## ANGRA-1
2019 Operating Experience
BR-1 | [8 empty] | ANGRA-1 | [26 empty] | BRAZIL
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ELETRONU (ELETROBRAS ELETRONUCLEAR, S.A.)
Owner | [7 empty] | : | ELETRONU (ELETROBRAS ELETRONUCLEAR, S.A.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-05-01
Thermal power | [12 empty] | : |  |  | 1882 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-04-01
Gross electrical power | [12 empty] | : |  |  | 640 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-01-01
Reference unit power (net) | [12 empty] | : |  |  | 609 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.71
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.32
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.0 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 35.1 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.47 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.05
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 19
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 5239.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.36 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.54 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.36 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.62 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.02 %
Load Factor (LF) | [18 empty] | : | 98.21 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.08 %
Operating Factor (OF) | [18 empty] | : | 98.94 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 93 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 450.25 | 408.69 |  |  |  | 390.92 |  | 438.38 | [8 empty] | 453.77 |  |  | 419.14 | [6 empty] | 456.45 |  | 456.85 |  |  |  | 441.88 |  |  | 430.22 |  |  | 440.41 | [9 empty] | 452.74 |  |  | 5239.68
EAF [%] |  |  |  |  | 99.37 | 99.71 |  |  |  | 100.00 |  | 99.98 | [8 empty] | 100.00 |  |  | 99.75 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 95.74 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.54
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.75 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 95.74 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.62
LF [%] |  |  |  |  | 99.37 | 99.71 |  |  |  | 86.28 |  | 99.98 | [8 empty] | 100.15 |  |  | 95.59 | [6 empty] | 100.74 |  | 100.83 |  |  |  | 100.77 |  |  | 94.95 |  |  | 100.44 | [9 empty] | 99.92 |  |  | 98.21
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 90.59 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 96.91 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.94
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 4.26 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.36
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 4.26 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.36
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.25 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
XUF [%] |  |  |  |  | 0.63 | 0.29 |  |  |  | 0.00 |  | 0.02 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.08
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 105482.68 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 16.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 62.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.61 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 67.39 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 55.07 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 5.09 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 69.44 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 3169.38 |  |  | 6847 |  |  |  | 626 | [10 empty] | 57.80 |  |  |  | 57.80 | [5 empty] | 57.80 |  |  | 78.16 |  |  |  | 37.49 |  | 34.66 | [8 empty] | 7.55 |  |  |  |  | 0.00
1986 |  |  |  | 132.36 |  |  | 512 |  |  |  | 626 | [10 empty] | 3.70 |  |  |  | 3.70 | [5 empty] | 2.41 |  |  | 5.84 |  |  |  | 89.62 |  | 31.97 | [8 empty] | 64.33 |  |  |  |  | 0.00
1987 |  |  |  | 910.56 |  |  | 1958 |  |  |  | 626 | [10 empty] | 19.72 |  |  |  | 19.72 | [5 empty] | 16.60 |  |  | 22.35 |  |  |  | 80.28 |  | 80.28 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 566.64 |  |  | 1488 |  |  |  | 626 | [10 empty] | 18.52 |  |  |  | 18.52 | [5 empty] | 10.30 |  |  | 16.94 |  |  |  | 81.48 |  | 81.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 1695.10 |  |  | 5362 |  |  |  | 626 | [10 empty] | 61.30 |  |  |  | 61.78 | [5 empty] | 30.91 |  |  | 61.21 |  |  |  | 6.96 |  | 4.62 | [8 empty] | 33.60 |  |  |  |  | 0.47
1990 |  |  |  | 2055.34 |  |  | 7400 |  |  |  | 626 | [10 empty] | 82.54 |  |  |  | 86.08 | [5 empty] | 37.48 |  |  | 84.47 |  |  |  | 10.13 |  | 9.71 | [8 empty] | 4.21 |  |  |  |  | 3.54
1991 |  |  |  | 1306.35 |  |  | 5046 |  |  |  | 626 | [10 empty] | 57.18 |  |  |  | 57.18 | [5 empty] | 23.82 |  |  | 57.60 |  |  |  | 1.56 |  | 0.91 | [8 empty] | 41.92 |  |  |  |  | 0.00
1992 |  |  |  | 1506.37 |  |  | 4275 |  |  |  | 626 | [10 empty] | 47.93 |  |  |  | 47.93 | [5 empty] | 27.39 |  |  | 48.67 |  |  |  | 16.27 |  | 9.31 | [8 empty] | 42.76 |  |  |  |  | 0.00
1993 |  |  |  | 402.70 |  |  | 1524 |  |  |  | 626 | [10 empty] | 17.17 |  |  |  | 17.17 | [5 empty] | 7.34 |  |  | 17.40 |  |  |  | 82.83 |  | 82.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 41.45 |  |  | 305 |  |  |  | 626 | [10 empty] | 3.48 |  |  |  | 83.84 | [5 empty] | 0.76 |  |  | 3.48 |  |  |  | 16.16 |  | 16.16 | [8 empty] | 0.00 |  |  |  |  | 80.35
1995 |  |  |  | 2333.64 |  |  | 8127 |  |  |  | 626 | [10 empty] | 42.56 |  |  |  | 92.77 | [5 empty] | 42.56 |  |  | 92.77 |  |  |  | 3.09 |  | 2.96 | [8 empty] | 4.27 |  |  |  |  | 50.22
1996 |  |  |  | 2288.84 |  |  | 5063 |  |  |  | 626 | [10 empty] | 55.23 |  |  |  | 66.99 | [5 empty] | 41.62 |  |  | 57.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.01 |  |  |  |  | 11.76
1997 |  |  |  | 2989.97 |  |  | 6219 |  |  |  | 626 | [10 empty] | 53.17 |  |  |  | 60.65 | [5 empty] | 54.52 |  |  | 70.99 |  |  |  | 0.75 |  | 0.46 | [8 empty] | 38.89 |  |  |  |  | 7.49
1998 |  |  |  | 3093.82 |  |  | 6976 |  |  |  | 626 | [10 empty] | 56.42 |  |  |  | 56.42 | [5 empty] | 56.42 |  |  | 79.63 |  |  |  | 6.39 |  | 3.85 | [8 empty] | 39.73 |  |  |  |  | 0.00
1999 |  |  |  | 3631.68 |  |  | 8429 |  |  |  | 626 | [10 empty] | 64.79 |  |  |  | 65.19 | [5 empty] | 66.23 |  |  | 96.22 |  |  |  | 4.69 |  | 3.21 | [8 empty] | 31.60 |  |  |  |  | 0.40
2000 |  |  |  | 3164.93 |  |  | 6514 |  |  |  | 626 | [10 empty] | 58.73 |  |  |  | 58.73 | [5 empty] | 57.56 |  |  | 74.16 |  |  |  | 15.27 |  | 10.59 | [8 empty] | 30.69 |  |  |  |  | 0.00
2001 |  |  |  | 3614.43 |  |  | 7295 |  |  |  | 626 | [10 empty] | 82.88 |  |  |  | 82.88 | [5 empty] | 65.91 |  |  | 83.28 |  |  |  | 4.94 |  | 4.31 | [8 empty] | 12.82 |  |  |  |  | 0.00
2002 |  |  |  | 3775.19 |  |  | 7595 |  |  |  | 626 | [10 empty] | 85.93 |  |  |  | 87.66 | [5 empty] | 68.84 |  |  | 86.70 |  |  |  | 0.64 |  | 0.56 | [8 empty] | 11.78 |  |  |  |  | 1.73
2003 |  |  |  | 3137.06 |  |  | 6551 |  |  |  | 626 | [10 empty] | 57.20 |  |  |  | 74.53 | [5 empty] | 57.21 |  |  | 74.78 |  |  |  | 9.74 |  | 8.04 | [8 empty] | 17.43 |  |  |  |  | 17.33
2004 |  |  |  | 3890.16 |  |  | 7968 |  |  |  | 626 | [10 empty] | 70.75 |  |  |  | 70.75 | [5 empty] | 70.75 |  |  | 90.71 |  |  |  | 0.35 |  | 0.25 | [8 empty] | 29.00 |  |  |  |  | 0.00
2005 |  |  |  | 3520.38 |  |  | 7275 |  |  |  | 626 | [10 empty] | 83.05 |  |  |  | 83.05 | [5 empty] | 64.20 |  |  | 83.05 |  |  |  | 0.85 |  | 0.71 | [8 empty] | 16.24 |  |  |  |  | 0.00
2006 |  |  |  | 3205.23 |  |  | 6743 |  |  |  | 626 | [10 empty] | 63.96 |  |  |  | 63.96 | [5 empty] | 58.45 |  |  | 76.97 |  |  |  | 20.91 |  | 16.91 | [8 empty] | 19.12 |  |  |  |  | 0.00
2007 |  |  |  | 2553.47 |  |  | 5481 |  |  |  | 520 | [10 empty] | 62.79 |  |  |  | 62.79 | [5 empty] | 56.06 |  |  | 62.57 |  |  |  | 8.97 |  | 16.59 | [8 empty] | 20.61 |  |  |  |  | 0.00
2008 |  |  |  | 3314.53 |  |  | 6967 |  |  |  | 491 | [10 empty] | 78.60 |  |  |  | 78.60 | [5 empty] | 76.85 |  |  | 79.31 |  |  |  | 5.95 |  | 4.98 | [8 empty] | 16.43 |  |  |  |  | 0.00
2009 |  |  |  | 2668.92 |  |  | 5256 |  |  |  | 609 | [10 empty] | 57.41 |  |  |  | 57.41 | [5 empty] | 50.87 |  |  | 60.00 |  |  |  | 7.83 |  | 4.88 | [8 empty] | 37.71 |  |  |  |  | 0.00
2010 |  |  |  | 4076.72 |  |  | 7055 |  |  |  | 609 | [10 empty] | 77.02 |  |  |  | 77.02 | [5 empty] | 76.42 |  |  | 80.54 |  |  |  | 3.94 |  | 3.16 | [8 empty] | 19.81 |  |  |  |  | 0.00
2011 |  |  |  | 4452.48 |  |  | 7789 |  |  |  | 609 | [10 empty] | 88.65 |  |  |  | 88.76 | [5 empty] | 83.46 |  |  | 88.92 |  |  |  | 1.93 |  | 1.75 | [8 empty] | 9.49 |  |  |  |  | 0.11
2012 |  |  |  | 5134.91 |  |  | 8734 |  |  |  | 609 | [10 empty] | 97.39 |  |  |  | 97.39 | [5 empty] | 95.99 |  |  | 99.43 |  |  |  | 0.58 |  | 0.57 | [8 empty] | 2.04 |  |  |  |  | 0.00
2013 |  |  |  | 3734.79 |  |  | 6765 |  |  |  | 609 | [10 empty] | 70.91 |  |  |  | 70.91 | [5 empty] | 70.01 |  |  | 77.23 |  |  |  | 11.56 |  | 9.27 | [8 empty] | 19.82 |  |  |  |  | 0.00
2014 |  |  |  | 4706.85 |  |  | 7857 |  |  |  | 609 | [10 empty] | 88.17 |  |  |  | 88.54 | [5 empty] | 88.23 |  |  | 89.69 |  |  |  | 1.43 |  | 1.28 | [8 empty] | 10.18 |  |  |  |  | 0.37
2015 |  |  |  | 3867.66 |  |  | 6619 |  |  |  | 609 | [10 empty] | 73.21 |  |  |  | 73.29 | [5 empty] | 72.50 |  |  | 75.56 |  |  |  | 11.77 |  | 15.33 | [8 empty] | 11.38 |  |  |  |  | 0.08
2016 |  |  |  | 4807.12 |  |  | 7951 |  |  |  | 609 | [10 empty] | 89.98 |  |  |  | 90.08 | [5 empty] | 89.86 |  |  | 90.52 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 9.89 |  |  |  |  | 0.10
2017 |  |  |  | 3966.79 |  |  | 6633 |  |  |  | 609 | [10 empty] | 74.22 |  |  |  | 74.34 | [5 empty] | 74.36 |  |  | 75.72 |  |  |  | 10.96 |  | 9.15 | [8 empty] | 16.51 |  |  |  |  | 0.12
2018 |  |  |  | 4695.30 |  |  | 7793 |  |  |  | 609 | [10 empty] | 88.12 |  |  |  | 88.61 | [5 empty] | 88.01 |  |  | 88.96 |  |  |  | 0.06 |  | 0.87 | [8 empty] | 10.52 |  |  |  |  | 0.49
2019 |  |  |  | 5239.68 |  |  | 8668 |  |  |  | 609 | [10 empty] | 99.54 |  |  |  | 99.62 | [5 empty] | 98.21 |  |  | 98.94 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.02 |  |  |  |  | 0.08
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1985 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 23 | [14 empty] | 1249
B. |  | Refuelling without maintenance | [35 empty] | 29
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1039
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 252
E. |  | Testing of plant systems or components | [35 empty] | 54 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 90
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 70 | [19 empty] | 13
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 7
L. |  | Human factor related | [39 empty] | 19
M. |  | Governmental requirements or court decisions | [51 empty] | 236
P. |  | Fire | [39 empty] | 0
Z. |  | Other | [39 empty] | 18 | [11 empty] | 2
Subtotal | [26 empty] | 23 | [6 empty] | 70 |  |  |  | 1464 |  |  |  | 1288 | [11 empty] | 258
Total | [22 empty] | 93 | [14 empty] | 3010
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1985 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 282
12. |  |  | Reactor I&C Systems | [34 empty] | 48
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 83
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
16. |  |  | Steam generation systems | [34 empty] | 31
31. |  |  | Turbine and auxiliaries | [34 empty] | 119
32. |  |  | Feedwater and Main Steam System | [19 empty] | 23 | [14 empty] | 45
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 369
42. |  |  | Electrical Power Supply Systems | [19 empty] | 70 | [14 empty] | 190
Total | [22 empty] | 93 | [14 empty] | 1187
Highlights (2019)
2019 stands out for having been the year with the highest production performance since the plant started operating. In 2019 Angra 1 had no refueling outage.

## ANGRA-2
2019 Operating Experience
BR-2 | [8 empty] | ANGRA-2 | [26 empty] | BRAZIL
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ELETRONU (ELETROBRAS ELETRONUCLEAR, S.A.)
Owner | [7 empty] | : | ELETRONU (ELETROBRAS ELETRONUCLEAR, S.A.)
Reactor Supplier | [7 empty] | : | KWU ( SIEMENS KRAFTWERK UNION, AG)
Turbine Supplier | [7 empty] | : | KWU ( SIEMENS KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / PRE KONVOI | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-01-01
Thermal power | [12 empty] | : |  |  | 3764 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2000-07-21
Gross electrical power | [12 empty] | : |  |  | 1350 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2001-02-01
Reference unit power (net) | [12 empty] | : |  |  | 1275 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 19 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.53
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.5 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 35000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.61 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.295
| Active core height/length [m] | [13 empty] | : |  |  | 3.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 25
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.79 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 8
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 9984.43 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.76 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.83 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.93 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.57 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.5 %
Load Factor (LF) | [18 empty] | : | 89.38 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.74 %
Operating Factor (OF) | [18 empty] | : | 90.12 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 866 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 887.31 | 854.78 |  |  |  | 819.43 |  | 568.26 | [8 empty] | 275.46 |  |  | 927.95 | [6 empty] | 950.59 |  | 960.48 |  |  |  | 927.93 |  |  | 943.26 |  |  | 924.86 | [9 empty] | 944.10 |  |  | 9984.43
EAF [%] |  |  |  |  | 93.54 | 99.62 |  |  |  | 86.38 |  | 61.90 | [8 empty] | 29.04 |  |  | 100.00 | [6 empty] | 99.06 |  | 100.00 |  |  |  | 100.00 |  |  | 98.79 |  |  | 100.00 | [9 empty] | 98.86 |  |  | 88.83
UCF [%] |  |  |  |  | 94.08 | 100.00 |  |  |  | 87.04 |  | 69.37 | [8 empty] | 29.04 |  |  | 100.00 | [6 empty] | 99.06 |  | 100.00 |  |  |  | 100.00 |  |  | 98.79 |  |  | 100.00 | [9 empty] | 98.86 |  |  | 89.57
LF [%] |  |  |  |  | 93.54 | 99.62 |  |  |  | 86.38 |  | 61.90 | [8 empty] | 29.04 |  |  | 101.08 | [6 empty] | 100.21 |  | 101.25 |  |  |  | 101.08 |  |  | 99.44 |  |  | 100.75 | [9 empty] | 99.53 |  |  | 89.38
OF [%] |  |  |  |  | 94.35 | 100.00 |  |  |  | 88.31 |  | 70.00 | [8 empty] | 29.97 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.12
FLR [%] |  |  |  |  | 5.92 | 0.00 |  |  |  | 12.96 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.76
UCL [%] |  |  |  |  | 5.92 | 0.00 |  |  |  | 12.96 |  | 0.00 | [8 empty] | 3.83 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.93
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 30.63 | [8 empty] | 67.13 |  |  | 0.00 | [6 empty] | 0.94 |  | 0.00 |  |  |  | 0.00 |  |  | 1.21 |  |  | 0.00 | [9 empty] | 1.14 |  |  | 8.50
XUF [%] |  |  |  |  | 0.54 | 0.38 |  |  |  | 0.66 |  | 7.47 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.74
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 182931.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.58 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.37 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.22 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.63 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.27 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.33 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2001 |  |  |  | 9904.99 |  |  | 8315 |  |  |  | 1350 | [10 empty] | 94.21 |  |  |  | 94.34 | [5 empty] | 85.69 |  |  | 97.27 |  |  |  | 3.11 |  | 3.02 | [8 empty] | 2.64 |  |  |  |  | 0.13
2002 |  |  |  | 9238.24 |  |  | 8060 |  |  |  | 1275 | [10 empty] | 83.33 |  |  |  | 91.26 | [5 empty] | 82.71 |  |  | 92.01 |  |  |  | 0.43 |  | 0.39 | [8 empty] | 8.35 |  |  |  |  | 7.93
2003 |  |  |  | 9418.97 |  |  | 8019 |  |  |  | 1275 | [10 empty] | 84.29 |  |  |  | 90.97 | [5 empty] | 84.33 |  |  | 91.54 |  |  |  | 1.91 |  | 1.77 | [8 empty] | 7.26 |  |  |  |  | 6.68
2004 |  |  |  | 6919.82 |  |  | 6497 |  |  |  | 1275 | [10 empty] | 72.76 |  |  |  | 72.76 | [5 empty] | 61.79 |  |  | 73.96 |  |  |  | 20.26 |  | 18.49 | [8 empty] | 8.74 |  |  |  |  | 0.00
2005 |  |  |  | 5676.66 |  |  | 5581 |  |  |  | 1275 | [10 empty] | 63.71 |  |  |  | 63.71 | [5 empty] | 50.83 |  |  | 63.71 |  |  |  | 4.70 |  | 9.17 | [8 empty] | 27.12 |  |  |  |  | 0.00
2006 |  |  |  | 9778.32 |  |  | 8014 |  |  |  | 1275 | [10 empty] | 89.34 |  |  |  | 89.34 | [5 empty] | 87.55 |  |  | 91.48 |  |  |  | 1.64 |  | 1.49 | [8 empty] | 9.17 |  |  |  |  | 0.00
2007 |  |  |  | 9096.95 |  |  | 7606 |  |  |  | 1275 | [10 empty] | 84.70 |  |  |  | 85.92 | [5 empty] | 81.45 |  |  | 86.83 |  |  |  | 4.68 |  | 6.68 | [8 empty] | 7.39 |  |  |  |  | 1.22
2008 |  |  |  | 9894.03 |  |  | 7924 |  |  |  | 1275 | [10 empty] | 89.12 |  |  |  | 90.06 | [5 empty] | 88.34 |  |  | 90.21 |  |  |  | 0.41 |  | 2.83 | [8 empty] | 7.10 |  |  |  |  | 0.94
2009 |  |  |  | 9554.65 |  |  | 8068 |  |  |  | 1275 | [10 empty] | 91.66 |  |  |  | 92.40 | [5 empty] | 85.55 |  |  | 92.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.60 |  |  |  |  | 0.73
2010 |  |  |  | 9697.44 |  |  | 7727 |  |  |  | 1275 | [10 empty] | 87.10 |  |  |  | 87.92 | [5 empty] | 86.82 |  |  | 88.21 |  |  |  | 2.89 |  | 2.62 | [8 empty] | 9.47 |  |  |  |  | 0.82
2011 |  |  |  | 10342.26 |  |  | 8682 |  |  |  | 1275 | [10 empty] | 99.04 |  |  |  | 99.11 | [5 empty] | 92.60 |  |  | 99.11 |  |  |  | 0.89 |  | 0.89 | [8 empty] | 0.00 |  |  |  |  | 0.07
2012 |  |  |  | 10035.50 |  |  | 8064 |  |  |  | 1275 | [10 empty] | 89.50 |  |  |  | 89.50 | [5 empty] | 89.61 |  |  | 91.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.50 |  |  |  |  | 0.00
2013 |  |  |  | 10045.27 |  |  | 7961 |  |  |  | 1275 | [10 empty] | 90.06 |  |  |  | 90.06 | [5 empty] | 89.94 |  |  | 90.88 |  |  |  | 1.74 |  | 2.19 | [8 empty] | 7.75 |  |  |  |  | 0.00
2014 |  |  |  | 9756.54 |  |  | 7754 |  |  |  | 1275 | [10 empty] | 86.57 |  |  |  | 88.61 | [5 empty] | 87.35 |  |  | 88.52 |  |  |  | 0.77 |  | 2.82 | [8 empty] | 8.57 |  |  |  |  | 2.04
2015 |  |  |  | 10023.96 |  |  | 7990 |  |  |  | 1275 | [10 empty] | 89.41 |  |  |  | 90.22 | [5 empty] | 89.75 |  |  | 91.21 |  |  |  | 1.18 |  | 1.56 | [8 empty] | 8.22 |  |  |  |  | 0.81
2016 |  |  |  | 10163.34 |  |  | 7939 |  |  |  | 1275 | [10 empty] | 90.05 |  |  |  | 90.20 | [5 empty] | 90.75 |  |  | 90.38 |  |  |  | 0.03 |  | 1.45 | [8 empty] | 8.35 |  |  |  |  | 0.16
2017 |  |  |  | 10887.54 |  |  | 8521 |  |  |  | 1275 | [10 empty] | 96.97 |  |  |  | 97.02 | [5 empty] | 97.48 |  |  | 97.27 |  |  |  | 2.95 |  | 2.95 | [8 empty] | 0.03 |  |  |  |  | 0.05
2018 |  |  |  | 10091.65 |  |  | 8011 |  |  |  | 1275 | [10 empty] | 89.53 |  |  |  | 91.22 | [5 empty] | 90.35 |  |  | 91.45 |  |  |  | 0.19 |  | 0.81 | [8 empty] | 7.97 |  |  |  |  | 1.69
2019 |  |  |  | 9984.43 |  |  | 7895 |  |  |  | 1275 | [10 empty] | 88.83 |  |  |  | 89.57 | [5 empty] | 89.38 |  |  | 90.12 |  |  |  | 1.76 |  | 1.93 | [8 empty] | 8.50 |  |  |  |  | 0.74
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2001 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 158 | [14 empty] | 205
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 709 | [14 empty] | 568 |  |  |  | 28
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 173
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 10
Subtotal | [22 empty] | 709 |  |  |  | 158 | [10 empty] | 744 |  |  |  | 244 | [11 empty] | 4
Total | [22 empty] | 867 | [14 empty] | 992
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2001 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 32
14. |  |  | Safety Systems | [19 empty] | 29 | [14 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 21
16. |  |  | Steam generation systems | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 6
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
33. |  |  | Circulating Water System | [34 empty] | 3
41. |  |  | Main Generator Systems | [19 empty] | 87 | [14 empty] | 63
42. |  |  | Electrical Power Supply Systems | [19 empty] | 42 | [14 empty] | 89
Total | [22 empty] | 158 | [14 empty] | 227
Highlights (2019)
The Plant was in power operation for 329 days in 2019. A refuelling outage was carried out between April and May and it took 30.6 days. The main unplanned power reductions during the year were: - Auto Reactor Scram in January due to a short circuit in a lightning arrester of one Main Transformer; - Manual shutdown in order to repair a hydrogen leak in the Hydrogen Cooler of the Main Generator; - Refuelling outage extension due to an unplanned HP Safety Injection Pump replacement. After the refuelling outage, at the end of May, it was found an indication of fuel failure in Angra 2 Reactor Core. However, the Tech Spec limits were not achieved and the Plant remained in operation since then. In the next refuelling outage (June 2020) the failed fuel assemblies will be replaced