## BRUCE-1
2019 Operating Experience
CA-8 | [8 empty] | BRUCE-1 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 791 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-06-01
Thermal power | [12 empty] | : |  |  | 2620 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-01-14
Gross electrical power | [12 empty] | : |  |  | 830 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-09-01
Reference unit power (net) | [12 empty] | : |  |  | 760 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8750 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.37
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 4 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6720.15 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.95 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.95 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.05 %
Load Factor (LF) | [18 empty] | : | 100.94 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 580.95 | 525.18 |  |  |  | 581.47 |  | 559.87 | [8 empty] | 555.82 |  |  | 509.91 | [6 empty] | 577.13 |  | 571.97 |  |  |  | 559.87 |  |  | 557.98 |  |  | 559.83 | [9 empty] | 580.18 |  |  | 6720.15
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 99.91 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.90 |  | 99.93 |  |  |  | 99.84 |  |  | 99.84 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 99.95
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 99.91 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.90 |  | 99.93 |  |  |  | 99.84 |  |  | 99.84 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 99.95
LF [%] |  |  |  |  | 102.74 | 102.83 |  |  |  | 102.84 |  | 102.32 | [8 empty] | 98.30 |  |  | 93.19 | [6 empty] | 102.07 |  | 101.15 |  |  |  | 102.32 |  |  | 98.68 |  |  | 102.31 | [9 empty] | 102.61 |  |  | 100.94
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.09 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.10 |  | 0.07 |  |  |  | 0.16 |  |  | 0.16 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 0.05
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 133717.85 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 19.99 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.05 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 17.89 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 71.54 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.57 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.42 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.49 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.94 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 1860.70 |  |  | 2698 |  |  |  | 740 | [10 empty] | 88.40 |  |  |  | 88.40 | [5 empty] | 88.04 |  |  | 94.47 |  |  |  | 11.60 |  | 11.60 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 4152.60 |  |  | 6649 |  |  |  | 740 | [10 empty] | 72.65 |  |  |  | 72.65 | [5 empty] | 64.24 |  |  | 76.11 |  |  |  | 15.38 |  | 13.20 | [8 empty] | 14.15 |  |  |  |  | 0.00
1979 |  |  |  | 5018.80 |  |  | 7334 |  |  |  | 740 | [10 empty] | 81.48 |  |  |  | 81.48 | [5 empty] | 76.58 |  |  | 82.81 |  |  |  | 18.52 |  | 18.52 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 5597.50 |  |  | 7902 |  |  |  | 740 | [10 empty] | 86.18 |  |  |  | 86.18 | [5 empty] | 86.11 |  |  | 89.96 |  |  |  | 7.87 |  | 7.36 | [8 empty] | 6.46 |  |  |  |  | 0.00
1981 |  |  |  | 6253.30 |  |  | 8486 |  |  |  | 740 | [10 empty] | 96.66 |  |  |  | 96.66 | [5 empty] | 96.47 |  |  | 96.87 |  |  |  | 3.34 |  | 3.34 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 5914.90 |  |  | 7884 |  |  |  | 740 | [10 empty] | 88.80 |  |  |  | 88.80 | [5 empty] | 91.25 |  |  | 90.00 |  |  |  | 11.20 |  | 11.20 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 5802.80 |  |  | 7590 |  |  |  | 740 | [10 empty] | 84.81 |  |  |  | 84.81 | [5 empty] | 89.52 |  |  | 86.64 |  |  |  | 15.04 |  | 15.01 | [8 empty] | 0.18 |  |  |  |  | 0.00
1984 |  |  |  | 6457.62 |  |  | 8546 |  |  |  | 740 | [10 empty] | 94.76 |  |  |  | 94.76 | [5 empty] | 99.35 |  |  | 97.29 |  |  |  | 5.10 |  | 5.09 | [8 empty] | 0.15 |  |  |  |  | 0.00
1985 |  |  |  | 6417.45 |  |  | 8349 |  |  |  | 772 | [10 empty] | 94.89 |  |  |  | 99.99 | [5 empty] | 94.78 |  |  | 95.31 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.00 |  |  |  |  | 5.10
1986 |  |  |  | 4398.02 |  |  | 5783 |  |  |  | 770 | [10 empty] | 65.33 |  |  |  | 65.97 | [5 empty] | 65.20 |  |  | 66.02 |  |  |  | 0.07 |  | 0.05 | [8 empty] | 33.98 |  |  |  |  | 0.64
1987 |  |  |  | 4087.07 |  |  | 5462 |  |  |  | 848 | [10 empty] | 60.73 |  |  |  | 63.26 | [5 empty] | 55.02 |  |  | 62.35 |  |  |  | 19.62 |  | 15.44 | [8 empty] | 21.29 |  |  |  |  | 2.54
1988 |  |  |  | 4642.66 |  |  | 6066 |  |  |  | 848 | [10 empty] | 65.95 |  |  |  | 66.85 | [5 empty] | 62.33 |  |  | 69.06 |  |  |  | 15.12 |  | 11.91 | [8 empty] | 21.24 |  |  |  |  | 0.89
1989 |  |  |  | 5094.78 |  |  | 7543 |  |  |  | 848 | [10 empty] | 68.74 |  |  |  | 69.91 | [5 empty] | 68.58 |  |  | 86.11 |  |  |  | 25.23 |  | 23.59 | [8 empty] | 6.50 |  |  |  |  | 1.16
1990 |  |  |  | 2451.13 |  |  | 4629 |  |  |  | 848 | [10 empty] | 32.98 |  |  |  | 33.58 | [5 empty] | 33.00 |  |  | 52.84 |  |  |  | 39.00 |  | 21.46 | [8 empty] | 44.96 |  |  |  |  | 0.60
1991 |  |  |  | 2394.45 |  |  | 3467 |  |  |  | 848 | [10 empty] | 32.22 |  |  |  | 34.08 | [5 empty] | 32.23 |  |  | 39.58 |  |  |  | 65.87 |  | 65.78 | [8 empty] | 0.14 |  |  |  |  | 1.87
1992 |  |  |  | 4546.54 |  |  | 7484 |  |  |  | 848 | [10 empty] | 61.04 |  |  |  | 61.04 | [5 empty] | 61.04 |  |  | 85.20 |  |  |  | 38.96 |  | 38.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 3389.20 |  |  | 6869 |  |  |  | 848 | [10 empty] | 45.67 |  |  |  | 45.67 | [5 empty] | 45.62 |  |  | 78.41 |  |  |  | 45.60 |  | 38.28 | [8 empty] | 16.06 |  |  |  |  | 0.00
1994 |  |  |  | 3849.03 |  |  | 7094 |  |  |  | 848 | [10 empty] | 51.81 |  |  |  | 51.81 | [5 empty] | 51.81 |  |  | 80.98 |  |  |  | 48.19 |  | 48.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 3531.45 |  |  | 5827 |  |  |  | 848 | [10 empty] | 47.54 |  |  |  | 47.54 | [5 empty] | 47.54 |  |  | 66.52 |  |  |  | 34.50 |  | 25.04 | [8 empty] | 27.42 |  |  |  |  | 0.00
1996 |  |  |  | 4326.40 |  |  | 7306 |  |  |  | 848 | [10 empty] | 58.09 |  |  |  | 58.09 | [5 empty] | 58.08 |  |  | 83.17 |  |  |  | 39.23 |  | 37.49 | [8 empty] | 4.42 |  |  |  |  | 0.00
1997 |  |  |  | 1383.58 |  |  | 2254 |  |  |  | 848 | [10 empty] | 23.52 |  |  |  | 23.52 | [5 empty] | 23.52 |  |  | 32.50 |  |  |  | 63.04 |  | 40.12 | [8 empty] | 36.35 |  |  |  |  | 0.00
1998 |  |  |  | Data not available - Long-term shutdown
1999 |  |  |  | "
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | "
2005 |  |  |  | "
2006 |  |  |  | "
2007 |  |  |  | "
2008 |  |  |  | "
2009 |  |  |  | "
2010 |  |  |  | "
2011 |  |  |  | "
2012 |  |  |  | 743.65 |  |  | 1365 |  |  |  | 772 | [10 empty] | 42.86 |  |  |  | 42.86 | [5 empty] | 42.87 |  |  | 57.11 |  |  |  | 14.46 |  | 7.25 | [8 empty] | 49.90 |  |  |  |  | 0.00
2013 |  |  |  | 5257.07 |  |  | 7883 |  |  |  | 772 | [10 empty] | 85.98 |  |  |  | 86.14 | [5 empty] | 77.74 |  |  | 89.99 |  |  |  | 5.31 |  | 4.83 | [8 empty] | 9.03 |  |  |  |  | 0.16
2014 |  |  |  | 5630.95 |  |  | 7540 |  |  |  | 772 | [10 empty] | 85.52 |  |  |  | 85.52 | [5 empty] | 83.26 |  |  | 86.07 |  |  |  | 14.48 |  | 14.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 5816.97 |  |  | 7711 |  |  |  | 760 | [10 empty] | 86.96 |  |  |  | 86.96 | [5 empty] | 87.37 |  |  | 88.03 |  |  |  | 2.37 |  | 2.11 | [8 empty] | 10.94 |  |  |  |  | 0.00
2016 |  |  |  | 6122.17 |  |  | 8004 |  |  |  | 760 | [10 empty] | 90.36 |  |  |  | 90.42 | [5 empty] | 91.71 |  |  | 91.12 |  |  |  | 1.55 |  | 1.69 | [8 empty] | 7.89 |  |  |  |  | 0.06
2017 |  |  |  | 6434.23 |  |  | 8412 |  |  |  | 760 | [10 empty] | 95.42 |  |  |  | 95.42 | [5 empty] | 96.64 |  |  | 96.03 |  |  |  | 3.40 |  | 3.59 | [8 empty] | 0.99 |  |  |  |  | 0.01
2018 |  |  |  | 5424.38 |  |  | 7046 |  |  |  | 760 | [10 empty] | 79.92 |  |  |  | 79.93 | [5 empty] | 81.48 |  |  | 80.43 |  |  |  | 7.03 |  | 6.04 | [8 empty] | 14.03 |  |  |  |  | 0.01
2019 |  |  |  | 6720.15 |  |  | 8760 |  |  |  | 760 | [10 empty] | 99.95 |  |  |  | 99.95 | [5 empty] | 100.94 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1977 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 838
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 775
E. |  | Testing of plant systems or components | [35 empty] | 83 |  |  |  | 3
H. |  | Nuclear regulatory requirements | [39 empty] | 19
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 6
P. |  | Fire | [39 empty] | 5
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 15
Z. |  | Other | [35 empty] | 12 |  |  |  | 3
Subtotal | [37 empty] | 870 |  |  |  | 874 | [11 empty] | 21
Total | [22 empty] | 0 | [14 empty] | 1765
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1977 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 53
12. |  |  | Reactor I&C Systems | [34 empty] | 78
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 89
14. |  |  | Safety Systems | [34 empty] | 63
15. |  |  | Reactor Cooling Systems | [34 empty] | 91
16. |  |  | Steam generation systems | [34 empty] | 235
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 29
31. |  |  | Turbine and auxiliaries | [34 empty] | 39
32. |  |  | Feedwater and Main Steam System | [34 empty] | 25
34. |  |  | Miscellaneous Systems | [34 empty] | 22
41. |  |  | Main Generator Systems | [34 empty] | 62
42. |  |  | Electrical Power Supply Systems | [34 empty] | 47
Total | [37 empty] | 833
Highlights (2019)
No planned outages, no forced outages occurred in Unit 1 in 2019.

## BRUCE-2
2019 Operating Experience
CA-9 | [8 empty] | BRUCE-2 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 791 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-12-01
Thermal power | [12 empty] | : |  |  | 2620 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-09-04
Gross electrical power | [12 empty] | : |  |  | 830 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-09-01
Reference unit power (net) | [12 empty] | : |  |  | 760 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8750 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.37
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 4 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 5766.96 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.92 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.27 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.57 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.27 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.16 %
Load Factor (LF) | [18 empty] | : | 86.62 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 85.91 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1234 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 584.65 | 529.01 |  |  |  | 585.41 |  | 558.50 | [8 empty] | 471.51 |  |  | 520.72 | [6 empty] | 510.69 |  | 581.63 |  |  |  | 553.36 |  |  | 498.23 |  |  | 0.00 | [9 empty] | 373.24 |  |  | 5766.96
EAF [%] |  |  |  |  | 99.97 | 100.00 |  |  |  | 100.00 |  | 99.82 | [8 empty] | 82.91 |  |  | 100.00 | [6 empty] | 89.33 |  | 99.88 |  |  |  | 99.95 |  |  | 87.38 |  |  | 0.00 | [9 empty] | 64.10 |  |  | 85.27
UCF [%] |  |  |  |  | 99.97 | 100.00 |  |  |  | 100.00 |  | 99.82 | [8 empty] | 82.91 |  |  | 100.00 | [6 empty] | 89.33 |  | 99.88 |  |  |  | 99.95 |  |  | 87.38 |  |  | 0.00 | [9 empty] | 64.10 |  |  | 85.27
LF [%] |  |  |  |  | 103.40 | 103.58 |  |  |  | 103.53 |  | 102.07 | [8 empty] | 83.39 |  |  | 95.16 | [6 empty] | 90.32 |  | 102.86 |  |  |  | 101.13 |  |  | 88.11 |  |  | 0.00 | [9 empty] | 66.01 |  |  | 86.62
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 86.83 |  |  | 100.00 | [6 empty] | 89.52 |  | 100.00 |  |  |  | 100.00 |  |  | 89.78 |  |  | 0.00 | [9 empty] | 64.78 |  |  | 85.91
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.18 | [8 empty] | 17.09 |  |  | 0.00 | [6 empty] | 10.67 |  | 0.00 |  |  |  | 0.00 |  |  | 2.56 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.92
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.18 | [8 empty] | 17.09 |  |  | 0.00 | [6 empty] | 10.67 |  | 0.00 |  |  |  | 0.00 |  |  | 2.29 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.57
PUF [%] |  |  |  |  | 0.03 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.12 |  |  |  | 0.05 |  |  | 10.32 |  |  | 100.00 | [9 empty] | 35.90 |  |  | 12.16
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 116727.66 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 22.09 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 67.69 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 19.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 68.18 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.29 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.05 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.49 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.64 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 1696.80 |  |  | 2481 |  |  |  | 740 | [10 empty] | 87.01 |  |  |  | 87.01 | [5 empty] | 80.29 |  |  | 86.87 |  |  |  | 12.99 |  | 12.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 3603.80 |  |  | 5946 |  |  |  | 740 | [10 empty] | 65.23 |  |  |  | 65.45 | [5 empty] | 55.75 |  |  | 68.06 |  |  |  | 22.17 |  | 18.65 | [8 empty] | 15.91 |  |  |  |  | 0.22
1979 |  |  |  | 4408.80 |  |  | 6534 |  |  |  | 740 | [10 empty] | 73.76 |  |  |  | 73.76 | [5 empty] | 67.27 |  |  | 73.78 |  |  |  | 19.40 |  | 17.75 | [8 empty] | 8.49 |  |  |  |  | 0.00
1980 |  |  |  | 6074.90 |  |  | 8463 |  |  |  | 740 | [10 empty] | 93.52 |  |  |  | 93.52 | [5 empty] | 93.46 |  |  | 96.35 |  |  |  | 6.48 |  | 6.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
1981 |  |  |  | 5795.10 |  |  | 7904 |  |  |  | 740 | [10 empty] | 89.57 |  |  |  | 89.57 | [5 empty] | 89.40 |  |  | 90.23 |  |  |  | 4.02 |  | 3.75 | [8 empty] | 6.67 |  |  |  |  | 0.00
1982 |  |  |  | 4432.40 |  |  | 6163 |  |  |  | 740 | [10 empty] | 68.00 |  |  |  | 68.00 | [5 empty] | 68.38 |  |  | 70.35 |  |  |  | 32.00 |  | 32.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 6112.80 |  |  | 7941 |  |  |  | 740 | [10 empty] | 89.51 |  |  |  | 89.51 | [5 empty] | 94.30 |  |  | 90.65 |  |  |  | 10.35 |  | 10.34 | [8 empty] | 0.15 |  |  |  |  | 0.00
1984 |  |  |  | 6223.90 |  |  | 8649 |  |  |  | 740 | [10 empty] | 91.03 |  |  |  | 91.03 | [5 empty] | 95.75 |  |  | 98.46 |  |  |  | 8.84 |  | 8.83 | [8 empty] | 0.15 |  |  |  |  | 0.00
1985 |  |  |  | 4979.30 |  |  | 6525 |  |  |  | 781 | [10 empty] | 73.54 |  |  |  | 77.95 | [5 empty] | 72.76 |  |  | 74.49 |  |  |  | 11.25 |  | 9.88 | [8 empty] | 12.17 |  |  |  |  | 4.41
1986 |  |  |  | 4257.63 |  |  | 5308 |  |  |  | 848 | [10 empty] | 56.97 |  |  |  | 59.21 | [5 empty] | 57.31 |  |  | 60.59 |  |  |  | 40.79 |  | 40.79 | [8 empty] | 0.00 |  |  |  |  | 2.24
1987 |  |  |  | 3781.40 |  |  | 4636 |  |  |  | 848 | [10 empty] | 50.56 |  |  |  | 52.18 | [5 empty] | 50.90 |  |  | 52.92 |  |  |  | 6.98 |  | 3.91 | [8 empty] | 43.91 |  |  |  |  | 1.62
1988 |  |  |  | 4971.25 |  |  | 7741 |  |  |  | 848 | [10 empty] | 71.70 |  |  |  | 71.70 | [5 empty] | 66.74 |  |  | 88.13 |  |  |  | 25.15 |  | 24.08 | [8 empty] | 4.22 |  |  |  |  | 0.00
1989 |  |  |  | 1316.31 |  |  | 2149 |  |  |  | 848 | [10 empty] | 17.72 |  |  |  | 17.82 | [5 empty] | 17.72 |  |  | 24.53 |  |  |  | 26.85 |  | 6.54 | [8 empty] | 75.64 |  |  |  |  | 0.10
1990 |  |  |  | 2578.32 |  |  | 3460 |  |  |  | 848 | [10 empty] | 35.22 |  |  |  | 35.48 | [5 empty] | 34.71 |  |  | 39.50 |  |  |  | 41.05 |  | 24.71 | [8 empty] | 39.81 |  |  |  |  | 0.26
1991 |  |  |  | 4483.48 |  |  | 5915 |  |  |  | 848 | [10 empty] | 60.25 |  |  |  | 63.20 | [5 empty] | 60.36 |  |  | 67.52 |  |  |  | 36.71 |  | 36.66 | [8 empty] | 0.15 |  |  |  |  | 2.95
1992 |  |  |  | 353.88 |  |  | 625 |  |  |  | 848 | [10 empty] | 4.73 |  |  |  | 4.73 | [5 empty] | 4.75 |  |  | 7.12 |  |  |  | 95.27 |  | 95.27 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 3016.81 |  |  | 6041 |  |  |  | 848 | [10 empty] | 40.75 |  |  |  | 40.75 | [5 empty] | 40.61 |  |  | 68.96 |  |  |  | 45.16 |  | 33.56 | [8 empty] | 25.69 |  |  |  |  | 0.00
1994 |  |  |  | 3882.47 |  |  | 7046 |  |  |  | 848 | [10 empty] | 52.26 |  |  |  | 52.26 | [5 empty] | 52.26 |  |  | 80.43 |  |  |  | 40.39 |  | 35.41 | [8 empty] | 12.32 |  |  |  |  | 0.00
1995 |  |  |  | 3791.00 |  |  | 6225 |  |  |  | 848 | [10 empty] | 66.34 |  |  |  | 66.34 | [5 empty] | 66.34 |  |  | 92.22 |  |  |  | 27.76 |  | 25.50 | [8 empty] | 8.16 |  |  |  |  | 0.00
1996 |  |  |  | Data not available - Long-term shutdown
1997 |  |  |  | "
1998 |  |  |  | "
1999 |  |  |  | "
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | "
2005 |  |  |  | "
2006 |  |  |  | "
2007 |  |  |  | "
2008 |  |  |  | "
2009 |  |  |  | "
2010 |  |  |  | "
2011 |  |  |  | "
2012 |  |  |  | 1039.20 |  |  | 1826 |  |  |  | 734 | [10 empty] | 85.69 |  |  |  | 85.71 | [5 empty] | 85.41 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.29 |  |  |  |  | 0.02
2013 |  |  |  | 5607.65 |  |  | 8190 |  |  |  | 734 | [10 empty] | 88.10 |  |  |  | 88.23 | [5 empty] | 87.21 |  |  | 93.49 |  |  |  | 7.18 |  | 6.82 | [8 empty] | 4.94 |  |  |  |  | 0.13
2014 |  |  |  | 4910.32 |  |  | 6984 |  |  |  | 734 | [10 empty] | 81.74 |  |  |  | 81.74 | [5 empty] | 76.37 |  |  | 79.73 |  |  |  | 18.26 |  | 18.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6365.71 |  |  | 8660 |  |  |  | 730 | [10 empty] | 98.65 |  |  |  | 98.65 | [5 empty] | 99.55 |  |  | 98.86 |  |  |  | 0.68 |  | 0.68 | [8 empty] | 0.68 |  |  |  |  | 0.00
2016 |  |  |  | 4804.60 |  |  | 6408 |  |  |  | 760 | [10 empty] | 73.21 |  |  |  | 73.23 | [5 empty] | 73.17 |  |  | 72.95 |  |  |  | 2.57 |  | 6.93 | [8 empty] | 19.84 |  |  |  |  | 0.02
2017 |  |  |  | 6482.56 |  |  | 8560 |  |  |  | 760 | [10 empty] | 97.35 |  |  |  | 97.35 | [5 empty] | 97.37 |  |  | 97.72 |  |  |  | 0.88 |  | 0.87 | [8 empty] | 1.78 |  |  |  |  | 0.00
2018 |  |  |  | 5989.71 |  |  | 7828 |  |  |  | 760 | [10 empty] | 88.11 |  |  |  | 88.12 | [5 empty] | 89.97 |  |  | 89.36 |  |  |  | 7.67 |  | 7.32 | [8 empty] | 4.55 |  |  |  |  | 0.01
2019 |  |  |  | 5766.96 |  |  | 7526 |  |  |  | 760 | [10 empty] | 85.27 |  |  |  | 85.27 | [5 empty] | 86.62 |  |  | 85.91 |  |  |  | 2.92 |  | 2.57 | [8 empty] | 12.16 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1977 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 176 | [14 empty] | 1087
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 1058 | [14 empty] | 986
E. |  | Testing of plant systems or components | [39 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 11
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 28
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 42
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 16
Z. |  | Other | [39 empty] | 35
Subtotal | [22 empty] | 1058 |  |  |  | 176 | [10 empty] | 986 |  |  |  | 1177 | [11 empty] | 46
Total | [22 empty] | 1234 | [14 empty] | 2209
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1977 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 137
12. |  |  | Reactor I&C Systems | [19 empty] | 54 | [14 empty] | 53
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 148
16. |  |  | Steam generation systems | [34 empty] | 491
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 30
31. |  |  | Turbine and auxiliaries | [34 empty] | 23
32. |  |  | Feedwater and Main Steam System | [34 empty] | 12
34. |  |  | Miscellaneous Systems | [34 empty] | 15
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 141
42. |  |  | Electrical Power Supply Systems | [19 empty] | 122 | [14 empty] | 31
Total | [22 empty] | 176 | [14 empty] | 1103

## BRUCE-3
2019 Operating Experience
CA-10 | [8 empty] | BRUCE-3 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750A | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-07-01
Thermal power | [12 empty] | : |  |  | 2550 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-12-12
Gross electrical power | [12 empty] | : |  |  | 830 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1978-02-01
Reference unit power (net) | [12 empty] | : |  |  | 750 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8750 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.37
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 4 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 4213.89 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.68 %
Energy Availability Factor (EAF) | [18 empty] | : | 62.4 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 24.63 %
Unit Capability Factor (UCF) | [18 empty] | : | 62.4 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.98 %
Load Factor (LF) | [18 empty] | : | 64.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 63.84 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3168 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 267.68 |  |  | 469.38 | [6 empty] | 587.24 |  | 575.80 |  |  |  | 561.49 |  |  | 581.01 |  |  | 571.76 | [9 empty] | 599.51 |  |  | 4213.89
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 50.00 |  |  | 94.59 | [6 empty] | 99.91 |  | 99.87 |  |  |  | 99.89 |  |  | 99.91 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 62.40
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 50.00 |  |  | 94.59 | [6 empty] | 99.91 |  | 99.87 |  |  |  | 99.89 |  |  | 99.91 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 62.40
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 47.97 |  |  | 86.92 | [6 empty] | 105.24 |  | 103.19 |  |  |  | 103.98 |  |  | 104.12 |  |  | 105.88 | [9 empty] | 107.44 |  |  | 64.14
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 61.29 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 63.84
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.76 |  |  | 5.41 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.68
UCL [%] |  |  |  |  | 0.00 | 46.43 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 46.02 |  |  | 5.41 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 24.63
PUF [%] |  |  |  |  | 100.00 | 53.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.98 |  |  | 0.00 | [6 empty] | 0.09 |  | 0.13 |  |  |  | 0.11 |  |  | 0.09 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.98
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 169811.77 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 14.53 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.98 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.98 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.58 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.44 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.88 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.6 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.71 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1978 |  |  |  | 4793.00 |  |  | 7361 |  |  |  | 740 | [10 empty] | 87.56 |  |  |  | 87.56 | [5 empty] | 82.03 |  |  | 93.22 |  |  |  | 12.44 |  | 12.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
1979 |  |  |  | 4797.90 |  |  | 6885 |  |  |  | 740 | [10 empty] | 77.78 |  |  |  | 77.78 | [5 empty] | 73.21 |  |  | 77.74 |  |  |  | 11.80 |  | 10.41 | [8 empty] | 11.82 |  |  |  |  | 0.00
1980 |  |  |  | 5939.80 |  |  | 8276 |  |  |  | 740 | [10 empty] | 91.44 |  |  |  | 91.44 | [5 empty] | 91.38 |  |  | 94.22 |  |  |  | 8.56 |  | 8.56 | [8 empty] | 0.00 |  |  |  |  | 0.00
1981 |  |  |  | 5795.00 |  |  | 7873 |  |  |  | 740 | [10 empty] | 89.48 |  |  |  | 89.48 | [5 empty] | 89.40 |  |  | 89.87 |  |  |  | 4.74 |  | 4.45 | [8 empty] | 6.07 |  |  |  |  | 0.00
1982 |  |  |  | 6381.90 |  |  | 8497 |  |  |  | 740 | [10 empty] | 96.72 |  |  |  | 96.72 | [5 empty] | 98.45 |  |  | 97.00 |  |  |  | 3.28 |  | 3.28 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 6091.10 |  |  | 7905 |  |  |  | 740 | [10 empty] | 89.23 |  |  |  | 89.23 | [5 empty] | 93.96 |  |  | 90.24 |  |  |  | 10.64 |  | 10.62 | [8 empty] | 0.15 |  |  |  |  | 0.00
1984 |  |  |  | 6148.73 |  |  | 8077 |  |  |  | 740 | [10 empty] | 91.19 |  |  |  | 91.19 | [5 empty] | 94.59 |  |  | 91.95 |  |  |  | 8.56 |  | 8.54 | [8 empty] | 0.27 |  |  |  |  | 0.00
1985 |  |  |  | 6015.13 |  |  | 8118 |  |  |  | 775 | [10 empty] | 88.59 |  |  |  | 93.91 | [5 empty] | 88.60 |  |  | 92.67 |  |  |  | 6.09 |  | 6.09 | [8 empty] | 0.00 |  |  |  |  | 5.32
1986 |  |  |  | 5891.24 |  |  | 7600 |  |  |  | 796 | [10 empty] | 84.18 |  |  |  | 86.94 | [5 empty] | 84.48 |  |  | 86.76 |  |  |  | 13.01 |  | 13.00 | [8 empty] | 0.06 |  |  |  |  | 2.76
1987 |  |  |  | 6073.27 |  |  | 7724 |  |  |  | 848 | [10 empty] | 81.91 |  |  |  | 85.78 | [5 empty] | 81.76 |  |  | 88.17 |  |  |  | 7.86 |  | 7.32 | [8 empty] | 6.90 |  |  |  |  | 3.87
1988 |  |  |  | 3310.57 |  |  | 4044 |  |  |  | 848 | [10 empty] | 45.61 |  |  |  | 45.61 | [5 empty] | 44.44 |  |  | 46.04 |  |  |  | 4.02 |  | 1.91 | [8 empty] | 52.48 |  |  |  |  | 0.00
1989 |  |  |  | 4031.74 |  |  | 5364 |  |  |  | 848 | [10 empty] | 54.79 |  |  |  | 57.43 | [5 empty] | 54.27 |  |  | 61.23 |  |  |  | 31.42 |  | 26.31 | [8 empty] | 16.26 |  |  |  |  | 2.64
1990 |  |  |  | 5652.68 |  |  | 7472 |  |  |  | 848 | [10 empty] | 76.30 |  |  |  | 76.77 | [5 empty] | 76.09 |  |  | 85.30 |  |  |  | 23.03 |  | 22.97 | [8 empty] | 0.26 |  |  |  |  | 0.48
1991 |  |  |  | 6126.29 |  |  | 7950 |  |  |  | 848 | [10 empty] | 82.38 |  |  |  | 84.29 | [5 empty] | 82.47 |  |  | 90.75 |  |  |  | 15.71 |  | 15.71 | [8 empty] | 0.00 |  |  |  |  | 1.90
1992 |  |  |  | 5800.97 |  |  | 7438 |  |  |  | 848 | [10 empty] | 77.89 |  |  |  | 77.89 | [5 empty] | 77.88 |  |  | 84.68 |  |  |  | 18.25 |  | 17.39 | [8 empty] | 4.72 |  |  |  |  | 0.00
1993 |  |  |  | 3158.23 |  |  | 6557 |  |  |  | 848 | [10 empty] | 42.99 |  |  |  | 42.99 | [5 empty] | 42.52 |  |  | 74.85 |  |  |  | 54.42 |  | 51.32 | [8 empty] | 5.69 |  |  |  |  | 0.00
1994 |  |  |  | 2737.62 |  |  | 5006 |  |  |  | 848 | [10 empty] | 36.85 |  |  |  | 36.85 | [5 empty] | 36.85 |  |  | 57.15 |  |  |  | 37.07 |  | 21.71 | [8 empty] | 41.44 |  |  |  |  | 0.00
1995 |  |  |  | 4225.82 |  |  | 7000 |  |  |  | 848 | [10 empty] | 56.89 |  |  |  | 56.89 | [5 empty] | 56.89 |  |  | 79.91 |  |  |  | 43.11 |  | 43.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 3321.48 |  |  | 5684 |  |  |  | 848 | [10 empty] | 44.59 |  |  |  | 44.59 | [5 empty] | 44.59 |  |  | 64.71 |  |  |  | 32.38 |  | 21.35 | [8 empty] | 34.06 |  |  |  |  | 0.00
1997 |  |  |  | 4214.82 |  |  | 6325 |  |  |  | 848 | [10 empty] | 56.76 |  |  |  | 56.76 | [5 empty] | 56.74 |  |  | 72.20 |  |  |  | 43.24 |  | 43.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 1642.52 |  |  | 2328 |  |  |  | 848 | [10 empty] | 81.45 |  |  |  | 81.45 | [5 empty] | 81.45 |  |  | 97.87 |  |  |  | 18.55 |  | 18.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | Data not available - Long-term shutdown
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | 4971.58 |  |  | 7154 |  |  |  | 750 | [10 empty] | 76.09 |  |  |  | 76.45 | [5 empty] | 75.30 |  |  | 81.44 |  |  |  | 22.51 |  | 22.21 | [8 empty] | 1.34 |  |  |  |  | 0.36
2005 |  |  |  | 4938.11 |  |  | 6782 |  |  |  | 750 | [10 empty] | 75.24 |  |  |  | 75.52 | [5 empty] | 75.16 |  |  | 77.42 |  |  |  | 8.92 |  | 7.40 | [8 empty] | 17.08 |  |  |  |  | 0.28
2006 |  |  |  | 5440.25 |  |  | 7435 |  |  |  | 750 | [10 empty] | 82.86 |  |  |  | 83.27 | [5 empty] | 82.80 |  |  | 84.87 |  |  |  | 8.75 |  | 8.05 | [8 empty] | 8.68 |  |  |  |  | 0.41
2007 |  |  |  | 4966.67 |  |  | 6911 |  |  |  | 750 | [10 empty] | 75.95 |  |  |  | 76.68 | [5 empty] | 75.60 |  |  | 78.89 |  |  |  | 3.18 |  | 3.34 | [8 empty] | 19.97 |  |  |  |  | 0.73
2008 |  |  |  | 5148.88 |  |  | 7125 |  |  |  | 734 | [10 empty] | 79.32 |  |  |  | 79.77 | [5 empty] | 79.86 |  |  | 81.11 |  |  |  | 3.51 |  | 2.90 | [8 empty] | 17.33 |  |  |  |  | 0.45
2009 |  |  |  | 5162.09 |  |  | 7148 |  |  |  | 730 | [10 empty] | 80.39 |  |  |  | 80.59 | [5 empty] | 80.72 |  |  | 81.60 |  |  |  | 2.07 |  | 10.14 | [8 empty] | 9.27 |  |  |  |  | 0.20
2010 |  |  |  | 4375.77 |  |  | 6198 |  |  |  | 730 | [10 empty] | 68.44 |  |  |  | 69.58 | [5 empty] | 68.43 |  |  | 70.75 |  |  |  | 16.32 |  | 13.57 | [8 empty] | 16.85 |  |  |  |  | 1.15
2011 |  |  |  | 5084.86 |  |  | 6959 |  |  |  | 730 | [10 empty] | 78.89 |  |  |  | 79.13 | [5 empty] | 79.52 |  |  | 79.44 |  |  |  | 4.24 |  | 3.50 | [8 empty] | 17.37 |  |  |  |  | 0.25
2012 |  |  |  | 3352.06 |  |  | 4617 |  |  |  | 730 | [10 empty] | 52.21 |  |  |  | 52.26 | [5 empty] | 52.28 |  |  | 52.56 |  |  |  | 5.80 |  | 9.96 | [8 empty] | 37.78 |  |  |  |  | 0.06
2013 |  |  |  | 5518.71 |  |  | 7914 |  |  |  | 730 | [10 empty] | 94.01 |  |  |  | 94.16 | [5 empty] | 86.30 |  |  | 90.34 |  |  |  | 4.71 |  | 4.66 | [8 empty] | 1.18 |  |  |  |  | 0.14
2014 |  |  |  | 4125.00 |  |  | 5718 |  |  |  | 730 | [10 empty] | 64.55 |  |  |  | 64.55 | [5 empty] | 64.51 |  |  | 65.27 |  |  |  | 3.30 |  | 2.20 | [8 empty] | 33.25 |  |  |  |  | 0.00
2015 |  |  |  | 5827.57 |  |  | 7831 |  |  |  | 750 | [10 empty] | 89.01 |  |  |  | 89.01 | [5 empty] | 88.90 |  |  | 89.39 |  |  |  | 10.00 |  | 9.89 | [8 empty] | 1.09 |  |  |  |  | 0.00
2016 |  |  |  | 4995.72 |  |  | 6579 |  |  |  | 750 | [10 empty] | 75.54 |  |  |  | 75.60 | [5 empty] | 75.83 |  |  | 74.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.40 |  |  |  |  | 0.06
2017 |  |  |  | 5502.68 |  |  | 7344 |  |  |  | 750 | [10 empty] | 83.22 |  |  |  | 83.22 | [5 empty] | 83.75 |  |  | 83.84 |  |  |  | 0.08 |  | 9.65 | [8 empty] | 7.13 |  |  |  |  | 0.00
2018 |  |  |  | 6268.88 |  |  | 8079 |  |  |  | 750 | [10 empty] | 92.18 |  |  |  | 92.21 | [5 empty] | 95.42 |  |  | 92.23 |  |  |  | 3.26 |  | 3.11 | [8 empty] | 4.68 |  |  |  |  | 0.03
2019 |  |  |  | 4213.89 |  |  | 5592 |  |  |  | 750 | [10 empty] | 62.40 |  |  |  | 62.40 | [5 empty] | 64.14 |  |  | 63.84 |  |  |  | 1.68 |  | 24.63 | [8 empty] | 12.98 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1978 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 2064 | [14 empty] | 747
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 38 |  |  |  | 0
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 1104 | [14 empty] | 848
E. |  | Testing of plant systems or components | [35 empty] | 15 |  |  |  | 1
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 80
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 18
L. |  | Human factor related | [39 empty] | 9
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 14
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 1104 |  |  |  | 2064 | [10 empty] | 981 |  |  |  | 758 | [11 empty] | 36
Total | [22 empty] | 3168 | [14 empty] | 1775
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1978 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 2064 | [14 empty] | 134
12. |  |  | Reactor I&C Systems | [34 empty] | 46
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 25
14. |  |  | Safety Systems | [34 empty] | 68
15. |  |  | Reactor Cooling Systems | [34 empty] | 89
16. |  |  | Steam generation systems | [34 empty] | 107
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 32
31. |  |  | Turbine and auxiliaries | [34 empty] | 97
32. |  |  | Feedwater and Main Steam System | [34 empty] | 36
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 7
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 84
42. |  |  | Electrical Power Supply Systems | [34 empty] | 19
Total | [22 empty] | 2064 | [14 empty] | 758
Highlights (2019)
A single fuel channel replacement was completed in Unit 3 in 2019.

## BRUCE-4
2019 Operating Experience
CA-11 | [8 empty] | BRUCE-4 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750A | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-09-01
Thermal power | [12 empty] | : |  |  | 2550 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-12-21
Gross electrical power | [12 empty] | : |  |  | 830 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-01-18
Reference unit power (net) | [12 empty] | : |  |  | 750 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [13 empty] | : | [14 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : | [14 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8750 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.37
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 4 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6115.21 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.71 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.93 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.58 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.93 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 3.49 %
Load Factor (LF) | [18 empty] | : | 93.08 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.24 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 592 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 548.92 | 492.77 |  |  |  | 420.14 |  | 290.91 | [8 empty] | 519.17 |  |  | 417.29 | [6 empty] | 572.88 |  | 570.48 |  |  |  | 550.37 |  |  | 579.44 |  |  | 565.06 | [9 empty] | 587.79 |  |  | 6115.21
EAF [%] |  |  |  |  | 98.37 | 97.77 |  |  |  | 75.29 |  | 51.54 | [8 empty] | 92.27 |  |  | 100.00 | [6 empty] | 99.95 |  | 99.92 |  |  |  | 99.94 |  |  | 99.92 |  |  | 100.00 | [9 empty] | 99.97 |  |  | 92.93
UCF [%] |  |  |  |  | 98.37 | 97.77 |  |  |  | 75.29 |  | 51.54 | [8 empty] | 92.27 |  |  | 100.00 | [6 empty] | 99.96 |  | 99.92 |  |  |  | 99.94 |  |  | 99.92 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.93
LF [%] |  |  |  |  | 98.37 | 97.77 |  |  |  | 75.29 |  | 53.87 | [8 empty] | 93.04 |  |  | 77.28 | [6 empty] | 102.67 |  | 102.24 |  |  |  | 101.92 |  |  | 103.84 |  |  | 104.64 | [9 empty] | 105.34 |  |  | 93.08
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 77.42 |  | 56.67 | [8 empty] | 95.56 |  |  | 89.03 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.24
FLR [%] |  |  |  |  | 1.63 | 2.23 |  |  |  | 2.75 |  | 36.54 | [8 empty] | 7.72 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.71
UCL [%] |  |  |  |  | 1.63 | 2.23 |  |  |  | 2.13 |  | 29.68 | [8 empty] | 7.72 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.58
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 22.58 |  | 18.78 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.04 |  | 0.08 |  |  |  | 0.06 |  |  | 0.08 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.49
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.03 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 168100.31 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 15.07 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.17 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 14.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.86 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.81 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.81 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.68 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.29 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 4966.40 |  |  | 7084 |  |  |  | 740 | [10 empty] | 84.17 |  |  |  | 84.17 | [5 empty] | 79.65 |  |  | 84.18 |  |  |  | 15.83 |  | 15.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 4945.10 |  |  | 6962 |  |  |  | 740 | [10 empty] | 76.12 |  |  |  | 76.12 | [5 empty] | 76.08 |  |  | 79.26 |  |  |  | 14.06 |  | 12.46 | [8 empty] | 11.42 |  |  |  |  | 0.00
1981 |  |  |  | 5753.50 |  |  | 7874 |  |  |  | 740 | [10 empty] | 89.10 |  |  |  | 89.10 | [5 empty] | 88.76 |  |  | 89.89 |  |  |  | 10.90 |  | 10.90 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 6050.20 |  |  | 8150 |  |  |  | 740 | [10 empty] | 92.18 |  |  |  | 92.18 | [5 empty] | 93.33 |  |  | 93.04 |  |  |  | 2.13 |  | 2.01 | [8 empty] | 5.81 |  |  |  |  | 0.00
1983 |  |  |  | 6407.40 |  |  | 8345 |  |  |  | 740 | [10 empty] | 94.25 |  |  |  | 94.25 | [5 empty] | 98.84 |  |  | 95.26 |  |  |  | 5.68 |  | 5.67 | [8 empty] | 0.07 |  |  |  |  | 0.00
1984 |  |  |  | 6664.64 |  |  | 8625 |  |  |  | 740 | [10 empty] | 97.85 |  |  |  | 97.85 | [5 empty] | 102.53 |  |  | 98.19 |  |  |  | 2.08 |  | 2.07 | [8 empty] | 0.08 |  |  |  |  | 0.00
1985 |  |  |  | 4995.16 |  |  | 6518 |  |  |  | 788 | [10 empty] | 73.24 |  |  |  | 78.99 | [5 empty] | 72.29 |  |  | 74.41 |  |  |  | 7.88 |  | 6.76 | [8 empty] | 14.26 |  |  |  |  | 5.75
1986 |  |  |  | 6891.57 |  |  | 8644 |  |  |  | 848 | [10 empty] | 92.85 |  |  |  | 95.51 | [5 empty] | 92.77 |  |  | 98.68 |  |  |  | 4.49 |  | 4.49 | [8 empty] | 0.00 |  |  |  |  | 2.67
1987 |  |  |  | 5044.99 |  |  | 6366 |  |  |  | 848 | [10 empty] | 67.90 |  |  |  | 71.54 | [5 empty] | 67.91 |  |  | 72.67 |  |  |  | 5.78 |  | 4.39 | [8 empty] | 24.07 |  |  |  |  | 3.64
1988 |  |  |  | 4663.68 |  |  | 5997 |  |  |  | 848 | [10 empty] | 65.71 |  |  |  | 66.92 | [5 empty] | 62.61 |  |  | 68.27 |  |  |  | 18.05 |  | 14.74 | [8 empty] | 18.34 |  |  |  |  | 1.21
1989 |  |  |  | 5584.21 |  |  | 7290 |  |  |  | 848 | [10 empty] | 75.29 |  |  |  | 77.00 | [5 empty] | 75.17 |  |  | 83.22 |  |  |  | 17.87 |  | 16.75 | [8 empty] | 6.25 |  |  |  |  | 1.71
1990 |  |  |  | 3533.03 |  |  | 4611 |  |  |  | 848 | [10 empty] | 47.54 |  |  |  | 48.29 | [5 empty] | 47.56 |  |  | 52.64 |  |  |  | 51.71 |  | 51.71 | [8 empty] | 0.00 |  |  |  |  | 0.75
1991 |  |  |  | 5940.70 |  |  | 7955 |  |  |  | 848 | [10 empty] | 79.91 |  |  |  | 81.65 | [5 empty] | 79.97 |  |  | 90.81 |  |  |  | 17.92 |  | 17.83 | [8 empty] | 0.52 |  |  |  |  | 1.74
1992 |  |  |  | 5843.37 |  |  | 8070 |  |  |  | 848 | [10 empty] | 78.37 |  |  |  | 80.08 | [5 empty] | 78.45 |  |  | 91.87 |  |  |  | 19.92 |  | 19.92 | [8 empty] | 0.00 |  |  |  |  | 1.71
1993 |  |  |  | 350.09 |  |  | 527 |  |  |  | 848 | [10 empty] | 4.71 |  |  |  | 4.71 | [5 empty] | 4.71 |  |  | 6.02 |  |  |  | 79.26 |  | 18.01 | [8 empty] | 77.27 |  |  |  |  | 0.00
1994 |  |  |  | 3655.98 |  |  | 7206 |  |  |  | 848 | [10 empty] | 49.30 |  |  |  | 49.30 | [5 empty] | 49.22 |  |  | 82.26 |  |  |  | 50.38 |  | 50.06 | [8 empty] | 0.64 |  |  |  |  | 0.00
1995 |  |  |  | 3034.92 |  |  | 5024 |  |  |  | 848 | [10 empty] | 40.87 |  |  |  | 40.87 | [5 empty] | 40.86 |  |  | 57.35 |  |  |  | 42.28 |  | 29.94 | [8 empty] | 29.19 |  |  |  |  | 0.00
1996 |  |  |  | 5296.28 |  |  | 8686 |  |  |  | 848 | [10 empty] | 71.17 |  |  |  | 71.17 | [5 empty] | 71.10 |  |  | 98.88 |  |  |  | 28.83 |  | 28.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 2923.05 |  |  | 4968 |  |  |  | 848 | [10 empty] | 39.36 |  |  |  | 39.36 | [5 empty] | 39.35 |  |  | 56.71 |  |  |  | 60.64 |  | 60.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 12.34 |  |  | 45 |  |  |  | 848 | [10 empty] | 0.81 |  |  |  | 0.81 | [5 empty] | 0.81 |  |  | 2.50 |  |  |  | 99.19 |  | 99.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | Data not available - Long-term shutdown
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | 934.47 |  |  | 802 |  |  |  | 769 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 55.01 |  |  | 36.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 5418.78 |  |  | 7469 |  |  |  | 769 | [10 empty] | 83.42 |  |  |  | 83.42 | [5 empty] | 82.08 |  |  | 85.03 |  |  |  | 6.58 |  | 6.45 | [8 empty] | 10.13 |  |  |  |  | 0.00
2005 |  |  |  | 5499.12 |  |  | 7469 |  |  |  | 750 | [10 empty] | 83.67 |  |  |  | 84.10 | [5 empty] | 83.70 |  |  | 85.26 |  |  |  | 3.21 |  | 2.79 | [8 empty] | 13.11 |  |  |  |  | 0.43
2006 |  |  |  | 5308.22 |  |  | 7261 |  |  |  | 750 | [10 empty] | 80.78 |  |  |  | 81.59 | [5 empty] | 80.79 |  |  | 82.89 |  |  |  | 2.28 |  | 4.12 | [8 empty] | 14.29 |  |  |  |  | 0.81
2007 |  |  |  | 5250.98 |  |  | 7298 |  |  |  | 750 | [10 empty] | 80.15 |  |  |  | 80.78 | [5 empty] | 79.92 |  |  | 83.31 |  |  |  | 4.27 |  | 3.60 | [8 empty] | 15.62 |  |  |  |  | 0.63
2008 |  |  |  | 5504.43 |  |  | 7603 |  |  |  | 734 | [10 empty] | 84.92 |  |  |  | 85.62 | [5 empty] | 85.37 |  |  | 86.56 |  |  |  | 2.17 |  | 2.35 | [8 empty] | 12.03 |  |  |  |  | 0.70
2009 |  |  |  | 4907.55 |  |  | 7014 |  |  |  | 730 | [10 empty] | 76.92 |  |  |  | 77.37 | [5 empty] | 76.74 |  |  | 80.07 |  |  |  | 5.42 |  | 9.91 | [8 empty] | 12.72 |  |  |  |  | 0.44
2010 |  |  |  | 5976.18 |  |  | 8360 |  |  |  | 730 | [10 empty] | 94.11 |  |  |  | 94.49 | [5 empty] | 93.45 |  |  | 95.43 |  |  |  | 5.50 |  | 5.50 | [8 empty] | 0.02 |  |  |  |  | 0.37
2011 |  |  |  | 6259.24 |  |  | 8670 |  |  |  | 730 | [10 empty] | 98.71 |  |  |  | 98.97 | [5 empty] | 97.88 |  |  | 98.97 |  |  |  | 1.03 |  | 1.03 | [8 empty] | 0.00 |  |  |  |  | 0.26
2012 |  |  |  | 3700.41 |  |  | 5137 |  |  |  | 730 | [10 empty] | 58.31 |  |  |  | 58.46 | [5 empty] | 57.71 |  |  | 58.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 41.54 |  |  |  |  | 0.15
2013 |  |  |  | 4131.32 |  |  | 5778 |  |  |  | 730 | [10 empty] | 63.44 |  |  |  | 63.55 | [5 empty] | 64.60 |  |  | 65.96 |  |  |  | 10.79 |  | 31.78 | [8 empty] | 4.67 |  |  |  |  | 0.11
2014 |  |  |  | 6027.76 |  |  | 8243 |  |  |  | 730 | [10 empty] | 99.39 |  |  |  | 99.39 | [5 empty] | 94.26 |  |  | 94.10 |  |  |  | 0.61 |  | 0.61 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 4503.60 |  |  | 6069 |  |  |  | 750 | [10 empty] | 68.26 |  |  |  | 68.26 | [5 empty] | 68.55 |  |  | 69.28 |  |  |  | 0.00 |  | 2.74 | [8 empty] | 29.00 |  |  |  |  | 0.00
2016 |  |  |  | 5731.38 |  |  | 7511 |  |  |  | 750 | [10 empty] | 85.23 |  |  |  | 85.25 | [5 empty] | 87.00 |  |  | 85.51 |  |  |  | 6.54 |  | 5.96 | [8 empty] | 8.78 |  |  |  |  | 0.02
2017 |  |  |  | 6188.10 |  |  | 8262 |  |  |  | 750 | [10 empty] | 93.76 |  |  |  | 93.77 | [5 empty] | 94.19 |  |  | 94.32 |  |  |  | 4.65 |  | 4.58 | [8 empty] | 1.65 |  |  |  |  | 0.02
2018 |  |  |  | 4638.81 |  |  | 6146 |  |  |  | 750 | [10 empty] | 69.12 |  |  |  | 69.13 | [5 empty] | 70.61 |  |  | 70.16 |  |  |  | 4.78 |  | 7.58 | [8 empty] | 23.30 |  |  |  |  | 0.00
2019 |  |  |  | 6115.21 |  |  | 8168 |  |  |  | 750 | [10 empty] | 92.93 |  |  |  | 92.93 | [5 empty] | 93.08 |  |  | 93.24 |  |  |  | 3.71 |  | 3.58 | [8 empty] | 3.49 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1979 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 225 | [14 empty] | 800
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 64
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 288 | [14 empty] | 809
E. |  | Testing of plant systems or components | [35 empty] | 43
H. |  | Nuclear regulatory requirements | [39 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 79 | [19 empty] | 17
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 14
Z. |  | Other | [39 empty] | 12 | [11 empty] | 2
Subtotal | [22 empty] | 288 |  |  |  | 225 | [6 empty] | 79 |  |  |  | 916 |  |  |  | 826 | [11 empty] | 38
Total | [22 empty] | 592 | [14 empty] | 1780
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1979 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 109
12. |  |  | Reactor I&C Systems | [34 empty] | 44
14. |  |  | Safety Systems | [34 empty] | 46
15. |  |  | Reactor Cooling Systems | [34 empty] | 72
16. |  |  | Steam generation systems | [19 empty] | 225 | [14 empty] | 177
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 19
31. |  |  | Turbine and auxiliaries | [34 empty] | 65
32. |  |  | Feedwater and Main Steam System | [34 empty] | 36
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 34
35. |  |  | All other I&C Systems | [34 empty] | 98
41. |  |  | Main Generator Systems | [34 empty] | 79
42. |  |  | Electrical Power Supply Systems | [34 empty] | 35
Total | [22 empty] | 225 | [14 empty] | 822

## BRUCE-5
2019 Operating Experience
CA-18 | [8 empty] | BRUCE-5 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-06-01
Thermal power | [12 empty] | : |  |  | 2832 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-12-02
Gross electrical power | [12 empty] | : |  |  | 872 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-03-01
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 4865.8 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.1 %
Energy Availability Factor (EAF) | [18 empty] | : | 69.74 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.5 %
Unit Capability Factor (UCF) | [18 empty] | : | 69.96 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 28.54 %
Load Factor (LF) | [18 empty] | : | 67.99 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.22 %
Operating Factor (OF) | [18 empty] | : | 70.47 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2587 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 607.72 | 549.60 |  |  |  | 607.70 |  | 524.09 | [8 empty] | 586.21 |  |  | 482.64 | [6 empty] | 591.02 |  | 302.83 |  |  |  | 0.00 |  |  | 0.00 |  |  | 46.90 | [9 empty] | 567.10 |  |  | 4865.80
EAF [%] |  |  |  |  | 99.83 | 99.90 |  |  |  | 99.89 |  | 88.47 | [8 empty] | 99.93 |  |  | 99.47 | [6 empty] | 98.93 |  | 49.82 |  |  |  | 0.00 |  |  | 0.00 |  |  | 7.97 | [9 empty] | 92.91 |  |  | 69.74
UCF [%] |  |  |  |  | 100.00 | 99.91 |  |  |  | 100.00 |  | 88.54 | [8 empty] | 99.99 |  |  | 99.99 | [6 empty] | 99.73 |  | 50.35 |  |  |  | 0.00 |  |  | 0.00 |  |  | 7.97 | [9 empty] | 93.20 |  |  | 69.96
LF [%] |  |  |  |  | 99.98 | 100.10 |  |  |  | 99.97 |  | 89.09 | [8 empty] | 96.44 |  |  | 82.05 | [6 empty] | 97.23 |  | 49.82 |  |  |  | 0.00 |  |  | 0.00 |  |  | 7.97 | [9 empty] | 93.30 |  |  | 67.99
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 88.47 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 50.94 |  |  |  | 0.00 |  |  | 0.00 |  |  | 11.11 | [9 empty] | 95.30 |  |  | 70.47
FLR [%] |  |  |  |  | 0.00 | 0.07 |  |  |  | 0.00 |  | 11.45 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 6.57 |  |  | 2.10
UCL [%] |  |  |  |  | 0.00 | 0.07 |  |  |  | 0.00 |  | 11.45 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 6.55 |  |  | 1.50
PUF [%] |  |  |  |  | 0.00 | 0.02 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.01 |  |  | 0.01 | [6 empty] | 0.27 |  | 49.65 |  |  |  | 100.00 |  |  | 100.00 |  |  | 92.03 | [9 empty] | 0.25 |  |  | 28.54
XUF [%] |  |  |  |  | 0.17 | 0.01 |  |  |  | 0.11 |  | 0.07 | [8 empty] | 0.07 |  |  | 0.52 | [6 empty] | 0.80 |  | 0.53 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.29 |  |  | 0.22
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 211953.1 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.02 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.25 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.93 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.73 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.34 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.5 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.48 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.82 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 5464.16 |  |  | 7163 |  |  |  | 805 | [10 empty] | 85.86 |  |  |  | 91.57 | [5 empty] | 84.23 |  |  | 86.11 |  |  |  | 8.43 |  | 8.43 | [8 empty] | 0.00 |  |  |  |  | 5.71
1986 |  |  |  | 7078.03 |  |  | 8675 |  |  |  | 835 | [10 empty] | 96.67 |  |  |  | 98.43 | [5 empty] | 96.77 |  |  | 99.03 |  |  |  | 1.57 |  | 1.57 | [8 empty] | 0.00 |  |  |  |  | 1.76
1987 |  |  |  | 5730.15 |  |  | 7197 |  |  |  | 835 | [10 empty] | 78.18 |  |  |  | 80.17 | [5 empty] | 78.34 |  |  | 82.16 |  |  |  | 8.82 |  | 7.76 | [8 empty] | 12.08 |  |  |  |  | 1.99
1988 |  |  |  | 6673.56 |  |  | 7824 |  |  |  | 860 | [10 empty] | 88.49 |  |  |  | 88.52 | [5 empty] | 88.34 |  |  | 89.07 |  |  |  | 6.14 |  | 5.79 | [8 empty] | 5.69 |  |  |  |  | 0.02
1989 |  |  |  | 7130.76 |  |  | 8589 |  |  |  | 860 | [10 empty] | 94.14 |  |  |  | 97.10 | [5 empty] | 94.65 |  |  | 98.05 |  |  |  | 2.28 |  | 2.26 | [8 empty] | 0.64 |  |  |  |  | 2.96
1990 |  |  |  | 5534.66 |  |  | 6656 |  |  |  | 860 | [10 empty] | 73.53 |  |  |  | 74.60 | [5 empty] | 73.47 |  |  | 75.98 |  |  |  | 10.83 |  | 9.06 | [8 empty] | 16.34 |  |  |  |  | 1.06
1991 |  |  |  | 6769.63 |  |  | 8130 |  |  |  | 860 | [10 empty] | 90.30 |  |  |  | 90.74 | [5 empty] | 89.86 |  |  | 92.81 |  |  |  | 2.14 |  | 1.98 | [8 empty] | 7.27 |  |  |  |  | 0.44
1992 |  |  |  | 6452.05 |  |  | 7636 |  |  |  | 860 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 85.41 |  |  | 86.93 |  |  |  | 4.20 |  | 3.76 | [8 empty] | 10.45 |  |  |  |  | 0.00
1993 |  |  |  | 5118.34 |  |  | 7457 |  |  |  | 860 | [10 empty] | 68.08 |  |  |  | 68.08 | [5 empty] | 67.94 |  |  | 85.13 |  |  |  | 21.44 |  | 18.58 | [8 empty] | 13.34 |  |  |  |  | 0.00
1994 |  |  |  | 5629.34 |  |  | 7671 |  |  |  | 860 | [10 empty] | 75.02 |  |  |  | 75.02 | [5 empty] | 74.72 |  |  | 87.57 |  |  |  | 15.74 |  | 14.02 | [8 empty] | 10.97 |  |  |  |  | 0.00
1995 |  |  |  | 6125.27 |  |  | 7859 |  |  |  | 860 | [10 empty] | 81.41 |  |  |  | 81.41 | [5 empty] | 81.31 |  |  | 89.71 |  |  |  | 18.59 |  | 18.59 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 5767.61 |  |  | 7153 |  |  |  | 860 | [10 empty] | 76.40 |  |  |  | 76.40 | [5 empty] | 76.35 |  |  | 81.43 |  |  |  | 8.58 |  | 7.17 | [8 empty] | 16.42 |  |  |  |  | 0.00
1997 |  |  |  | 6388.27 |  |  | 8148 |  |  |  | 860 | [10 empty] | 84.80 |  |  |  | 84.80 | [5 empty] | 84.80 |  |  | 93.01 |  |  |  | 13.20 |  | 12.89 | [8 empty] | 2.31 |  |  |  |  | 0.00
1998 |  |  |  | 5623.11 |  |  | 7305 |  |  |  | 785 | [10 empty] | 81.68 |  |  |  | 81.69 | [5 empty] | 81.77 |  |  | 83.39 |  |  |  | 10.74 |  | 9.83 | [8 empty] | 8.48 |  |  |  |  | 0.01
1999 |  |  |  | 5281.90 |  |  | 6719 |  |  |  | 785 | [10 empty] | 76.57 |  |  |  | 76.58 | [5 empty] | 76.81 |  |  | 76.70 |  |  |  | 4.27 |  | 3.42 | [8 empty] | 20.01 |  |  |  |  | 0.01
2000 |  |  |  | 6908.74 |  |  | 8719 |  |  |  | 785 | [10 empty] | 99.08 |  |  |  | 99.08 | [5 empty] | 100.19 |  |  | 99.26 |  |  |  | 0.92 |  | 0.92 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 4902.08 |  |  | 6220 |  |  |  | 790 | [10 empty] | 70.91 |  |  |  | 70.91 | [5 empty] | 70.84 |  |  | 71.00 |  |  |  | 2.07 |  | 1.50 | [8 empty] | 27.59 |  |  |  |  | 0.00
2002 |  |  |  | 5993.14 |  |  | 7630 |  |  |  | 790 | [10 empty] | 86.28 |  |  |  | 86.28 | [5 empty] | 86.60 |  |  | 87.10 |  |  |  | 3.85 |  | 3.86 | [8 empty] | 9.86 |  |  |  |  | 0.00
2003 |  |  |  | 5302.51 |  |  | 6783 |  |  |  | 790 | [10 empty] | 77.26 |  |  |  | 77.26 | [5 empty] | 76.62 |  |  | 77.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.74 |  |  |  |  | 0.00
2004 |  |  |  | 5889.11 |  |  | 7543 |  |  |  | 790 | [10 empty] | 85.13 |  |  |  | 85.13 | [5 empty] | 84.87 |  |  | 85.87 |  |  |  | 2.05 |  | 7.33 | [8 empty] | 7.54 |  |  |  |  | 0.00
2005 |  |  |  | 5109.63 |  |  | 6678 |  |  |  | 790 | [10 empty] | 74.14 |  |  |  | 74.64 | [5 empty] | 73.83 |  |  | 76.23 |  |  |  | 4.77 |  | 6.14 | [8 empty] | 19.22 |  |  |  |  | 0.50
2006 |  |  |  | 6723.49 |  |  | 8694 |  |  |  | 806 | [10 empty] | 96.79 |  |  |  | 97.18 | [5 empty] | 95.89 |  |  | 99.25 |  |  |  | 2.60 |  | 2.60 | [8 empty] | 0.22 |  |  |  |  | 0.38
2007 |  |  |  | 6710.89 |  |  | 8760 |  |  |  | 795 | [10 empty] | 97.23 |  |  |  | 97.69 | [5 empty] | 96.36 |  |  | 100.00 |  |  |  | 0.74 |  | 0.73 | [8 empty] | 1.58 |  |  |  |  | 0.46
2008 |  |  |  | 5596.97 |  |  | 6943 |  |  |  | 817 | [10 empty] | 78.05 |  |  |  | 78.30 | [5 empty] | 77.99 |  |  | 79.04 |  |  |  | 6.40 |  | 7.64 | [8 empty] | 14.05 |  |  |  |  | 0.25
2009 |  |  |  | 6826.70 |  |  | 8597 |  |  |  | 817 | [10 empty] | 97.91 |  |  |  | 98.00 | [5 empty] | 95.39 |  |  | 98.14 |  |  |  | 1.98 |  | 1.98 | [8 empty] | 0.01 |  |  |  |  | 0.10
2010 |  |  |  | 6699.69 |  |  | 8368 |  |  |  | 817 | [10 empty] | 93.97 |  |  |  | 94.15 | [5 empty] | 93.61 |  |  | 95.53 |  |  |  | 1.20 |  | 1.14 | [8 empty] | 4.71 |  |  |  |  | 0.18
2011 |  |  |  | 6149.76 |  |  | 7666 |  |  |  | 817 | [10 empty] | 86.78 |  |  |  | 86.86 | [5 empty] | 85.93 |  |  | 87.51 |  |  |  | 1.23 |  | 1.08 | [8 empty] | 12.06 |  |  |  |  | 0.08
2012 |  |  |  | 6927.64 |  |  | 8690 |  |  |  | 817 | [10 empty] | 98.24 |  |  |  | 98.38 | [5 empty] | 96.53 |  |  | 98.93 |  |  |  | 1.58 |  | 1.58 | [8 empty] | 0.03 |  |  |  |  | 0.14
2013 |  |  |  | 6421.79 |  |  | 8141 |  |  |  | 817 | [10 empty] | 92.04 |  |  |  | 92.11 | [5 empty] | 89.73 |  |  | 92.93 |  |  |  | 0.62 |  | 0.85 | [8 empty] | 7.04 |  |  |  |  | 0.07
2014 |  |  |  | 5859.11 |  |  | 7487 |  |  |  | 817 | [10 empty] | 84.64 |  |  |  | 84.76 | [5 empty] | 81.87 |  |  | 85.47 |  |  |  | 0.00 |  | 0.51 | [8 empty] | 14.73 |  |  |  |  | 0.11
2015 |  |  |  | 6180.84 |  |  | 7978 |  |  |  | 817 | [10 empty] | 90.60 |  |  |  | 90.70 | [5 empty] | 86.36 |  |  | 91.07 |  |  |  | 1.65 |  | 1.63 | [8 empty] | 7.66 |  |  |  |  | 0.10
2016 |  |  |  | 6742.40 |  |  | 8613 |  |  |  | 817 | [10 empty] | 97.45 |  |  |  | 97.86 | [5 empty] | 93.95 |  |  | 98.05 |  |  |  | 0.87 |  | 0.86 | [8 empty] | 1.28 |  |  |  |  | 0.41
2017 |  |  |  | 5034.08 |  |  | 6394 |  |  |  | 817 | [10 empty] | 72.35 |  |  |  | 72.75 | [5 empty] | 70.34 |  |  | 72.99 |  |  |  | 0.52 |  | 3.12 | [8 empty] | 24.13 |  |  |  |  | 0.40
2018 |  |  |  | 7076.65 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.38 |  |  |  | 99.64 | [5 empty] | 98.88 |  |  | 100.00 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.00 |  |  |  |  | 0.26
2019 |  |  |  | 4865.80 |  |  | 6173 |  |  |  | 817 | [10 empty] | 69.74 |  |  |  | 69.96 | [5 empty] | 67.99 |  |  | 70.47 |  |  |  | 2.10 |  | 1.50 | [8 empty] | 28.54 |  |  |  |  | 0.22
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1985 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 118 | [14 empty] | 233
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 19
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2469 | [14 empty] | 774 |  |  |  | 7
E. |  | Testing of plant systems or components | [35 empty] | 6 |  |  |  | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 4
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 14
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 2469 |  |  |  | 118 | [10 empty] | 799 |  |  |  | 245 | [11 empty] | 18
Total | [22 empty] | 2587 | [14 empty] | 1062
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1985 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 26
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 18
15. |  |  | Reactor Cooling Systems | [34 empty] | 78
16. |  |  | Steam generation systems | [34 empty] | 22
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 23
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [19 empty] | 35 | [14 empty] | 21
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 15
42. |  |  | Electrical Power Supply Systems | [19 empty] | 83 | [14 empty] | 11
Total | [22 empty] | 118 | [14 empty] | 247

## BRUCE-6
2019 Operating Experience
CA-19 | [8 empty] | BRUCE-6 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-01-01
Thermal power | [12 empty] | : |  |  | 2690 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-06-26
Gross electrical power | [12 empty] | : |  |  | 891 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-09-14
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6498.25 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 7.63 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.71 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.63 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.35 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.02 %
Load Factor (LF) | [18 empty] | : | 90.8 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.64 %
Operating Factor (OF) | [18 empty] | : | 93.88 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 536 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 577.48 | 544.30 |  |  |  | 602.63 |  | 577.36 | [8 empty] | 134.66 |  |  | 533.88 | [6 empty] | 585.15 |  | 593.41 |  |  |  | 578.06 |  |  | 596.04 |  |  | 576.15 | [9 empty] | 599.12 |  |  | 6498.25
EAF [%] |  |  |  |  | 95.00 | 99.17 |  |  |  | 99.14 |  | 99.20 | [8 empty] | 23.01 |  |  | 98.13 | [6 empty] | 97.45 |  | 97.62 |  |  |  | 98.28 |  |  | 98.42 |  |  | 98.20 | [9 empty] | 98.49 |  |  | 91.71
UCF [%] |  |  |  |  | 95.42 | 99.17 |  |  |  | 99.14 |  | 99.20 | [8 empty] | 23.01 |  |  | 98.96 | [6 empty] | 99.96 |  | 99.98 |  |  |  | 99.17 |  |  | 98.62 |  |  | 98.43 | [9 empty] | 98.63 |  |  | 92.35
LF [%] |  |  |  |  | 95.00 | 99.14 |  |  |  | 99.14 |  | 98.15 | [8 empty] | 22.15 |  |  | 90.76 | [6 empty] | 96.27 |  | 97.62 |  |  |  | 98.27 |  |  | 98.06 |  |  | 97.95 | [9 empty] | 98.56 |  |  | 90.80
OF [%] |  |  |  |  | 99.46 | 100.00 |  |  |  | 100.00 |  | 99.44 | [8 empty] | 29.03 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.88
FLR [%] |  |  |  |  | 4.58 | 0.81 |  |  |  | 0.86 |  | 0.79 | [8 empty] | 76.98 |  |  | 1.03 | [6 empty] | 0.03 |  | 0.01 |  |  |  | 0.82 |  |  | 1.37 |  |  | 1.44 | [9 empty] | 1.35 |  |  | 7.63
UCL [%] |  |  |  |  | 4.58 | 0.81 |  |  |  | 0.86 |  | 0.79 | [8 empty] | 76.95 |  |  | 1.03 | [6 empty] | 0.03 |  | 0.01 |  |  |  | 0.82 |  |  | 1.37 |  |  | 1.44 | [9 empty] | 1.35 |  |  | 7.63
PUF [%] |  |  |  |  | 0.01 | 0.02 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.05 |  |  | 0.01 | [6 empty] | 0.01 |  | 0.01 |  |  |  | 0.01 |  |  | 0.01 |  |  | 0.13 | [9 empty] | 0.01 |  |  | 0.02
XUF [%] |  |  |  |  | 0.41 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.84 | [6 empty] | 2.51 |  | 2.35 |  |  |  | 0.89 |  |  | 0.20 |  |  | 0.23 | [9 empty] | 0.14 |  |  | 0.64
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 204263.67 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.04 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.35 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.05 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.95 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.99 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.64 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.6 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 3068.32 |  |  | 4230 |  |  |  | 822 | [10 empty] | 98.80 |  |  |  | 99.38 | [5 empty] | 98.85 |  |  | 99.93 |  |  |  | 0.46 |  | 0.46 | [8 empty] | 0.17 |  |  |  |  | 0.58
1985 |  |  |  | 5900.13 |  |  | 7369 |  |  |  | 805 | [10 empty] | 84.04 |  |  |  | 88.69 | [5 empty] | 83.66 |  |  | 84.12 |  |  |  | 10.23 |  | 10.10 | [8 empty] | 1.20 |  |  |  |  | 4.65
1986 |  |  |  | 5716.03 |  |  | 7213 |  |  |  | 835 | [10 empty] | 77.78 |  |  |  | 81.71 | [5 empty] | 78.13 |  |  | 82.34 |  |  |  | 6.94 |  | 6.09 | [8 empty] | 12.20 |  |  |  |  | 3.93
1987 |  |  |  | 7017.10 |  |  | 8610 |  |  |  | 837 | [10 empty] | 95.33 |  |  |  | 97.85 | [5 empty] | 95.70 |  |  | 98.29 |  |  |  | 1.92 |  | 1.92 | [8 empty] | 0.23 |  |  |  |  | 2.52
1988 |  |  |  | 6139.49 |  |  | 7880 |  |  |  | 837 | [10 empty] | 89.10 |  |  |  | 89.22 | [5 empty] | 83.51 |  |  | 89.71 |  |  |  | 4.88 |  | 4.58 | [8 empty] | 6.20 |  |  |  |  | 0.12
1989 |  |  |  | 5386.17 |  |  | 7069 |  |  |  | 837 | [10 empty] | 73.43 |  |  |  | 78.94 | [5 empty] | 73.46 |  |  | 80.70 |  |  |  | 8.94 |  | 7.75 | [8 empty] | 13.32 |  |  |  |  | 5.50
1990 |  |  |  | 6213.64 |  |  | 7429 |  |  |  | 852 | [10 empty] | 82.31 |  |  |  | 83.85 | [5 empty] | 83.21 |  |  | 84.81 |  |  |  | 5.69 |  | 5.06 | [8 empty] | 11.09 |  |  |  |  | 1.54
1991 |  |  |  | 7013.36 |  |  | 8194 |  |  |  | 860 | [10 empty] | 93.03 |  |  |  | 93.31 | [5 empty] | 93.09 |  |  | 93.54 |  |  |  | 0.94 |  | 0.89 | [8 empty] | 5.81 |  |  |  |  | 0.27
1992 |  |  |  | 5328.20 |  |  | 6393 |  |  |  | 860 | [10 empty] | 70.51 |  |  |  | 70.55 | [5 empty] | 70.53 |  |  | 72.78 |  |  |  | 7.40 |  | 5.64 | [8 empty] | 23.82 |  |  |  |  | 0.04
1993 |  |  |  | 4351.00 |  |  | 6950 |  |  |  | 860 | [10 empty] | 58.03 |  |  |  | 58.03 | [5 empty] | 57.75 |  |  | 79.34 |  |  |  | 38.84 |  | 36.85 | [8 empty] | 5.12 |  |  |  |  | 0.00
1994 |  |  |  | 6451.71 |  |  | 8760 |  |  |  | 860 | [10 empty] | 85.75 |  |  |  | 85.75 | [5 empty] | 85.64 |  |  | 100.00 |  |  |  | 14.25 |  | 14.25 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 4671.57 |  |  | 6049 |  |  |  | 860 | [10 empty] | 62.10 |  |  |  | 62.10 | [5 empty] | 62.01 |  |  | 69.05 |  |  |  | 11.48 |  | 8.05 | [8 empty] | 29.85 |  |  |  |  | 0.00
1996 |  |  |  | 6822.75 |  |  | 8682 |  |  |  | 860 | [10 empty] | 90.38 |  |  |  | 90.39 | [5 empty] | 90.32 |  |  | 98.84 |  |  |  | 9.61 |  | 9.61 | [8 empty] | 0.00 |  |  |  |  | 0.01
1997 |  |  |  | 4796.41 |  |  | 6201 |  |  |  | 860 | [10 empty] | 63.70 |  |  |  | 63.70 | [5 empty] | 63.67 |  |  | 70.79 |  |  |  | 26.88 |  | 23.42 | [8 empty] | 12.88 |  |  |  |  | 0.00
1998 |  |  |  | 4678.62 |  |  | 6137 |  |  |  | 785 | [10 empty] | 68.04 |  |  |  | 68.11 | [5 empty] | 68.04 |  |  | 70.06 |  |  |  | 21.80 |  | 18.98 | [8 empty] | 12.91 |  |  |  |  | 0.07
1999 |  |  |  | 6860.15 |  |  | 8760 |  |  |  | 785 | [10 empty] | 99.32 |  |  |  | 99.44 | [5 empty] | 99.76 |  |  | 100.00 |  |  |  | 0.56 |  | 0.56 | [8 empty] | 0.00 |  |  |  |  | 0.12
2000 |  |  |  | 4668.21 |  |  | 5912 |  |  |  | 785 | [10 empty] | 66.81 |  |  |  | 66.81 | [5 empty] | 67.70 |  |  | 67.30 |  |  |  | 11.72 |  | 8.87 | [8 empty] | 24.32 |  |  |  |  | 0.00
2001 |  |  |  | 6840.06 |  |  | 8624 |  |  |  | 790 | [10 empty] | 98.32 |  |  |  | 98.32 | [5 empty] | 98.84 |  |  | 98.45 |  |  |  | 1.68 |  | 1.68 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 3522.45 |  |  | 4539 |  |  |  | 790 | [10 empty] | 50.64 |  |  |  | 50.64 | [5 empty] | 50.90 |  |  | 51.82 |  |  |  | 0.42 |  | 14.91 | [8 empty] | 34.45 |  |  |  |  | 0.00
2003 |  |  |  | 6750.85 |  |  | 8559 |  |  |  | 790 | [10 empty] | 98.18 |  |  |  | 98.18 | [5 empty] | 97.55 |  |  | 97.71 |  |  |  | 1.81 |  | 1.81 | [8 empty] | 0.01 |  |  |  |  | 0.00
2004 |  |  |  | 5379.09 |  |  | 6698 |  |  |  | 790 | [10 empty] | 76.65 |  |  |  | 76.65 | [5 empty] | 75.43 |  |  | 76.25 |  |  |  | 1.06 |  | 0.98 | [8 empty] | 22.37 |  |  |  |  | 0.00
2005 |  |  |  | 5721.10 |  |  | 7151 |  |  |  | 841 | [10 empty] | 79.56 |  |  |  | 79.56 | [5 empty] | 78.90 |  |  | 81.63 |  |  |  | 20.44 |  | 20.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 7104.45 |  |  | 8760 |  |  |  | 822 | [10 empty] | 99.32 |  |  |  | 99.45 | [5 empty] | 98.66 |  |  | 100.00 |  |  |  | 0.50 |  | 0.50 | [8 empty] | 0.06 |  |  |  |  | 0.12
2007 |  |  |  | 5145.02 |  |  | 6363 |  |  |  | 822 | [10 empty] | 71.77 |  |  |  | 71.77 | [5 empty] | 71.45 |  |  | 72.64 |  |  |  | 7.49 |  | 5.81 | [8 empty] | 22.42 |  |  |  |  | 0.00
2008 |  |  |  | 6857.25 |  |  | 8452 |  |  |  | 817 | [10 empty] | 95.35 |  |  |  | 95.52 | [5 empty] | 95.55 |  |  | 96.22 |  |  |  | 2.77 |  | 2.72 | [8 empty] | 1.77 |  |  |  |  | 0.17
2009 |  |  |  | 6063.07 |  |  | 7732 |  |  |  | 817 | [10 empty] | 91.32 |  |  |  | 91.36 | [5 empty] | 84.72 |  |  | 88.26 |  |  |  | 8.43 |  | 8.41 | [8 empty] | 0.23 |  |  |  |  | 0.04
2010 |  |  |  | 5471.91 |  |  | 6815 |  |  |  | 817 | [10 empty] | 76.54 |  |  |  | 76.67 | [5 empty] | 76.46 |  |  | 77.80 |  |  |  | 4.31 |  | 8.21 | [8 empty] | 15.12 |  |  |  |  | 0.13
2011 |  |  |  | 6552.52 |  |  | 8277 |  |  |  | 817 | [10 empty] | 94.00 |  |  |  | 94.07 | [5 empty] | 91.55 |  |  | 94.49 |  |  |  | 0.84 |  | 0.80 | [8 empty] | 5.13 |  |  |  |  | 0.07
2012 |  |  |  | 7125.32 |  |  | 8784 |  |  |  | 817 | [10 empty] | 99.58 |  |  |  | 99.72 | [5 empty] | 99.29 |  |  | 100.00 |  |  |  | 0.28 |  | 0.28 | [8 empty] | 0.00 |  |  |  |  | 0.14
2013 |  |  |  | 5684.00 |  |  | 7174 |  |  |  | 817 | [10 empty] | 81.00 |  |  |  | 81.07 | [5 empty] | 79.42 |  |  | 81.89 |  |  |  | 0.67 |  | 3.27 | [8 empty] | 15.66 |  |  |  |  | 0.07
2014 |  |  |  | 6768.62 |  |  | 8488 |  |  |  | 817 | [10 empty] | 97.74 |  |  |  | 97.85 | [5 empty] | 94.57 |  |  | 96.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.15 |  |  |  |  | 0.11
2015 |  |  |  | 5344.31 |  |  | 6694 |  |  |  | 817 | [10 empty] | 76.15 |  |  |  | 76.15 | [5 empty] | 74.67 |  |  | 76.42 |  |  |  | 0.74 |  | 0.57 | [8 empty] | 23.28 |  |  |  |  | 0.00
2016 |  |  |  | 6875.21 |  |  | 8613 |  |  |  | 817 | [10 empty] | 97.09 |  |  |  | 97.61 | [5 empty] | 95.80 |  |  | 98.05 |  |  |  | 2.39 |  | 2.39 | [8 empty] | 0.00 |  |  |  |  | 0.52
2017 |  |  |  | 5741.56 |  |  | 7164 |  |  |  | 817 | [10 empty] | 80.96 |  |  |  | 81.10 | [5 empty] | 80.22 |  |  | 81.78 |  |  |  | 0.19 |  | 2.89 | [8 empty] | 16.01 |  |  |  |  | 0.14
2018 |  |  |  | 7059.65 |  |  | 8718 |  |  |  | 817 | [10 empty] | 99.03 |  |  |  | 99.18 | [5 empty] | 98.64 |  |  | 99.52 |  |  |  | 0.80 |  | 0.80 | [8 empty] | 0.02 |  |  |  |  | 0.15
2019 |  |  |  | 6498.25 |  |  | 8224 |  |  |  | 817 | [10 empty] | 91.71 |  |  |  | 92.35 | [5 empty] | 90.80 |  |  | 93.88 |  |  |  | 7.63 |  | 7.63 | [8 empty] | 0.02 |  |  |  |  | 0.64
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1984 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 4 | [14 empty] | 365
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 94
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 679 |  |  |  | 4
E. |  | Testing of plant systems or components | [24 empty] | 532 | [10 empty] | 0 |  |  |  | 17
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 16
L. |  | Human factor related | [39 empty] | 17
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 12
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 11
Z. |  | Other | [39 empty] | 13
Subtotal | [26 empty] | 536 | [10 empty] | 773 |  |  |  | 427 | [11 empty] | 31
Total | [22 empty] | 536 | [14 empty] | 1231
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1984 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 532 | [14 empty] | 90
12. |  |  | Reactor I&C Systems | [34 empty] | 56
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 25
15. |  |  | Reactor Cooling Systems | [34 empty] | 101
16. |  |  | Steam generation systems | [34 empty] | 57
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [19 empty] | 4 | [14 empty] | 13
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
33. |  |  | Circulating Water System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [22 empty] | 536 | [14 empty] | 409
Highlights (2019)
Fuel channel inspections were completed in May 2019 as a pre-requisite to the Unit 6 Main Component Replacement -MCR6 commencing January 2020.

## BRUCE-7
2019 Operating Experience
CA-20 | [8 empty] | BRUCE-7 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-05-01
Thermal power | [12 empty] | : |  |  | 2832 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-02-22
Gross electrical power | [12 empty] | : |  |  | 872 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-04-10
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 4849.09 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.19 %
Energy Availability Factor (EAF) | [18 empty] | : | 68.32 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 6.15 %
Unit Capability Factor (UCF) | [18 empty] | : | 68.46 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.39 %
Load Factor (LF) | [18 empty] | : | 67.75 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.14 %
Operating Factor (OF) | [18 empty] | : | 68.9 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2724 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 611.06 | 152.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 494.06 | [6 empty] | 603.83 |  | 596.52 |  |  |  | 581.69 |  |  | 608.66 |  |  | 592.02 | [9 empty] | 608.75 |  |  | 4849.09
EAF [%] |  |  |  |  | 99.98 | 27.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 89.71 | [6 empty] | 99.73 |  | 99.59 |  |  |  | 99.79 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 99.98 |  |  | 68.32
UCF [%] |  |  |  |  | 100.00 | 27.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 90.56 | [6 empty] | 99.94 |  | 99.99 |  |  |  | 99.97 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 99.98 |  |  | 68.46
LF [%] |  |  |  |  | 100.53 | 27.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 83.99 | [6 empty] | 99.34 |  | 98.14 |  |  |  | 98.89 |  |  | 100.13 |  |  | 100.64 | [9 empty] | 100.15 |  |  | 67.75
OF [%] |  |  |  |  | 100.00 | 28.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 95.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 68.90
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.64 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.01 |  |  | 0.19
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 67.74 |  |  | 4.84 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.01 |  |  | 6.15
PUF [%] |  |  |  |  | 0.00 | 72.36 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 32.26 |  |  | 4.61 | [6 empty] | 0.06 |  | 0.01 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 25.39
XUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.84 | [6 empty] | 0.21 |  | 0.41 |  |  |  | 0.18 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.14
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 205386.04 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.27 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.15 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.32 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.44 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.7 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.42 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 5256.62 |  |  | 6957 |  |  |  | 838 | [10 empty] | 89.83 |  |  |  | 96.68 | [5 empty] | 89.66 |  |  | 97.55 |  |  |  | 3.31 |  | 3.30 | [8 empty] | 0.02 |  |  |  |  | 6.85
1987 |  |  |  | 6288.05 |  |  | 8489 |  |  |  | 837 | [10 empty] | 85.91 |  |  |  | 96.87 | [5 empty] | 85.76 |  |  | 96.91 |  |  |  | 2.80 |  | 2.79 | [8 empty] | 0.34 |  |  |  |  | 10.96
1988 |  |  |  | 4866.19 |  |  | 6636 |  |  |  | 846 | [10 empty] | 74.75 |  |  |  | 74.75 | [5 empty] | 65.44 |  |  | 75.55 |  |  |  | 9.46 |  | 7.81 | [8 empty] | 17.44 |  |  |  |  | 0.00
1989 |  |  |  | 7280.79 |  |  | 8632 |  |  |  | 860 | [10 empty] | 96.44 |  |  |  | 97.83 | [5 empty] | 96.64 |  |  | 98.54 |  |  |  | 1.83 |  | 1.82 | [8 empty] | 0.35 |  |  |  |  | 1.39
1990 |  |  |  | 6659.40 |  |  | 8065 |  |  |  | 860 | [10 empty] | 88.53 |  |  |  | 90.69 | [5 empty] | 88.40 |  |  | 92.07 |  |  |  | 4.64 |  | 4.41 | [8 empty] | 4.89 |  |  |  |  | 2.17
1991 |  |  |  | 5733.63 |  |  | 6835 |  |  |  | 860 | [10 empty] | 76.27 |  |  |  | 76.39 | [5 empty] | 76.11 |  |  | 78.03 |  |  |  | 8.22 |  | 6.84 | [8 empty] | 16.77 |  |  |  |  | 0.12
1992 |  |  |  | 6413.41 |  |  | 7589 |  |  |  | 860 | [10 empty] | 85.11 |  |  |  | 85.16 | [5 empty] | 84.90 |  |  | 86.40 |  |  |  | 1.64 |  | 1.42 | [8 empty] | 13.42 |  |  |  |  | 0.05
1993 |  |  |  | 5802.33 |  |  | 8760 |  |  |  | 860 | [10 empty] | 78.12 |  |  |  | 78.12 | [5 empty] | 77.02 |  |  | 100.00 |  |  |  | 21.87 |  | 21.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 5496.71 |  |  | 7577 |  |  |  | 860 | [10 empty] | 73.20 |  |  |  | 73.20 | [5 empty] | 72.96 |  |  | 86.50 |  |  |  | 17.13 |  | 15.13 | [8 empty] | 11.67 |  |  |  |  | 0.00
1995 |  |  |  | 6285.10 |  |  | 8092 |  |  |  | 860 | [10 empty] | 83.47 |  |  |  | 83.47 | [5 empty] | 83.43 |  |  | 92.37 |  |  |  | 16.53 |  | 16.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 5475.68 |  |  | 7000 |  |  |  | 860 | [10 empty] | 72.55 |  |  |  | 72.58 | [5 empty] | 72.48 |  |  | 79.69 |  |  |  | 16.16 |  | 13.98 | [8 empty] | 13.44 |  |  |  |  | 0.03
1997 |  |  |  | 6154.48 |  |  | 7874 |  |  |  | 860 | [10 empty] | 81.69 |  |  |  | 81.69 | [5 empty] | 81.69 |  |  | 89.89 |  |  |  | 18.31 |  | 18.31 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 4990.76 |  |  | 6474 |  |  |  | 785 | [10 empty] | 72.42 |  |  |  | 72.42 | [5 empty] | 72.58 |  |  | 73.90 |  |  |  | 6.83 |  | 5.31 | [8 empty] | 22.27 |  |  |  |  | 0.00
1999 |  |  |  | 6315.74 |  |  | 8208 |  |  |  | 785 | [10 empty] | 91.84 |  |  |  | 92.29 | [5 empty] | 91.84 |  |  | 93.70 |  |  |  | 7.71 |  | 7.71 | [8 empty] | 0.00 |  |  |  |  | 0.44
2000 |  |  |  | 5322.68 |  |  | 6790 |  |  |  | 785 | [10 empty] | 76.91 |  |  |  | 78.20 | [5 empty] | 77.19 |  |  | 77.30 |  |  |  | 1.57 |  | 1.25 | [8 empty] | 20.55 |  |  |  |  | 1.29
2001 |  |  |  | 7026.30 |  |  | 8760 |  |  |  | 790 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.53 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 4819.35 |  |  | 6121 |  |  |  | 790 | [10 empty] | 69.49 |  |  |  | 69.49 | [5 empty] | 69.64 |  |  | 69.87 |  |  |  | 1.46 |  | 3.67 | [8 empty] | 26.84 |  |  |  |  | 0.00
2003 |  |  |  | 6730.24 |  |  | 8592 |  |  |  | 790 | [10 empty] | 97.66 |  |  |  | 97.66 | [5 empty] | 97.25 |  |  | 98.08 |  |  |  | 2.20 |  | 2.20 | [8 empty] | 0.14 |  |  |  |  | 0.00
2004 |  |  |  | 6428.77 |  |  | 8188 |  |  |  | 790 | [10 empty] | 92.77 |  |  |  | 92.77 | [5 empty] | 92.64 |  |  | 93.21 |  |  |  | 0.00 |  | 0.03 | [8 empty] | 7.20 |  |  |  |  | 0.00
2005 |  |  |  | 4890.45 |  |  | 6310 |  |  |  | 790 | [10 empty] | 70.21 |  |  |  | 70.23 | [5 empty] | 70.07 |  |  | 72.03 |  |  |  | 3.28 |  | 5.70 | [8 empty] | 24.07 |  |  |  |  | 0.02
2006 |  |  |  | 6740.47 |  |  | 8486 |  |  |  | 806 | [10 empty] | 94.79 |  |  |  | 95.06 | [5 empty] | 94.37 |  |  | 96.87 |  |  |  | 4.30 |  | 4.27 | [8 empty] | 0.67 |  |  |  |  | 0.28
2007 |  |  |  | 6969.91 |  |  | 8570 |  |  |  | 822 | [10 empty] | 97.07 |  |  |  | 97.33 | [5 empty] | 96.79 |  |  | 97.83 |  |  |  | 2.49 |  | 2.48 | [8 empty] | 0.18 |  |  |  |  | 0.26
2008 |  |  |  | 5763.74 |  |  | 7101 |  |  |  | 817 | [10 empty] | 79.92 |  |  |  | 80.08 | [5 empty] | 80.31 |  |  | 80.84 |  |  |  | 3.49 |  | 5.99 | [8 empty] | 13.93 |  |  |  |  | 0.16
2009 |  |  |  | 6475.33 |  |  | 8144 |  |  |  | 817 | [10 empty] | 97.93 |  |  |  | 97.93 | [5 empty] | 90.48 |  |  | 92.97 |  |  |  | 1.99 |  | 1.98 | [8 empty] | 0.08 |  |  |  |  | 0.01
2010 |  |  |  | 6726.64 |  |  | 8610 |  |  |  | 817 | [10 empty] | 93.68 |  |  |  | 93.84 | [5 empty] | 93.99 |  |  | 98.29 |  |  |  | 5.98 |  | 5.97 | [8 empty] | 0.19 |  |  |  |  | 0.16
2011 |  |  |  | 5761.53 |  |  | 7137 |  |  |  | 817 | [10 empty] | 80.73 |  |  |  | 80.82 | [5 empty] | 80.50 |  |  | 81.47 |  |  |  | 0.17 |  | 4.98 | [8 empty] | 14.20 |  |  |  |  | 0.09
2012 |  |  |  | 7055.97 |  |  | 8731 |  |  |  | 817 | [10 empty] | 99.55 |  |  |  | 99.68 | [5 empty] | 98.32 |  |  | 99.40 |  |  |  | 0.24 |  | 0.24 | [8 empty] | 0.08 |  |  |  |  | 0.14
2013 |  |  |  | 7003.57 |  |  | 8758 |  |  |  | 817 | [10 empty] | 99.42 |  |  |  | 99.49 | [5 empty] | 97.86 |  |  | 99.98 |  |  |  | 0.51 |  | 0.51 | [8 empty] | 0.00 |  |  |  |  | 0.07
2014 |  |  |  | 5479.21 |  |  | 7113 |  |  |  | 817 | [10 empty] | 80.72 |  |  |  | 80.72 | [5 empty] | 76.56 |  |  | 81.20 |  |  |  | 1.04 |  | 4.01 | [8 empty] | 15.27 |  |  |  |  | 0.00
2015 |  |  |  | 6324.10 |  |  | 8029 |  |  |  | 817 | [10 empty] | 91.46 |  |  |  | 91.46 | [5 empty] | 88.36 |  |  | 91.66 |  |  |  | 1.35 |  | 1.26 | [8 empty] | 7.29 |  |  |  |  | 0.00
2016 |  |  |  | 4983.38 |  |  | 6332 |  |  |  | 817 | [10 empty] | 71.92 |  |  |  | 72.20 | [5 empty] | 69.44 |  |  | 72.09 |  |  |  | 0.00 |  | 2.23 | [8 empty] | 25.57 |  |  |  |  | 0.27
2017 |  |  |  | 6643.16 |  |  | 8431 |  |  |  | 817 | [10 empty] | 96.33 |  |  |  | 96.53 | [5 empty] | 92.82 |  |  | 96.24 |  |  |  | 3.28 |  | 3.27 | [8 empty] | 0.20 |  |  |  |  | 0.20
2018 |  |  |  | 7116.79 |  |  | 8715 |  |  |  | 817 | [10 empty] | 99.01 |  |  |  | 99.07 | [5 empty] | 99.44 |  |  | 99.49 |  |  |  | 0.91 |  | 0.91 | [8 empty] | 0.02 |  |  |  |  | 0.06
2019 |  |  |  | 4849.09 |  |  | 6036 |  |  |  | 817 | [10 empty] | 68.32 |  |  |  | 68.46 | [5 empty] | 67.75 |  |  | 68.90 |  |  |  | 0.19 |  | 6.15 | [8 empty] | 25.39 |  |  |  |  | 0.14
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1986 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 540 | [14 empty] | 251
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 19
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2184 | [14 empty] | 621 |  |  |  | 9
E. |  | Testing of plant systems or components | [35 empty] | 9
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 67
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 20
L. |  | Human factor related | [39 empty] | 4
Z. |  | Other | [39 empty] | 10 | [11 empty] | 3
Subtotal | [22 empty] | 2184 |  |  |  | 540 | [10 empty] | 716 |  |  |  | 274 | [11 empty] | 23
Total | [22 empty] | 2724 | [14 empty] | 1013
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1986 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 33
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 41
16. |  |  | Steam generation systems | [34 empty] | 25
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 28
31. |  |  | Turbine and auxiliaries | [19 empty] | 540 | [14 empty] | 32
32. |  |  | Feedwater and Main Steam System | [34 empty] | 31
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 31
41. |  |  | Main Generator Systems | [34 empty] | 7
42. |  |  | Electrical Power Supply Systems | [34 empty] | 17
Total | [22 empty] | 540 | [14 empty] | 272

## BRUCE-8
2019 Operating Experience
CA-21 | [8 empty] | BRUCE-8 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-08-01
Thermal power | [12 empty] | : |  |  | 2690 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-03-09
Gross electrical power | [12 empty] | : |  |  | 872 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-05-22
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 7082 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.18 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.75 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.18 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 98.95 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.07 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 613.20 | 553.47 |  |  |  | 612.29 |  | 580.82 | [8 empty] | 591.49 |  |  | 539.72 | [6 empty] | 596.50 |  | 600.19 |  |  |  | 585.44 |  |  | 601.75 |  |  | 593.25 | [9 empty] | 613.88 |  |  | 7082.00
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 98.50 | [8 empty] | 99.90 |  |  | 99.99 | [6 empty] | 99.10 |  | 99.58 |  |  |  | 99.94 |  |  | 99.96 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.75
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 98.50 | [8 empty] | 99.92 |  |  | 99.99 | [6 empty] | 99.43 |  | 99.99 |  |  |  | 99.99 |  |  | 99.96 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.82
LF [%] |  |  |  |  | 100.88 | 100.81 |  |  |  | 100.73 |  | 98.74 | [8 empty] | 97.31 |  |  | 91.75 | [6 empty] | 98.13 |  | 98.74 |  |  |  | 99.52 |  |  | 99.00 |  |  | 100.85 | [9 empty] | 100.99 |  |  | 98.95
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 1.49 | [8 empty] | 0.07 |  |  | 0.00 | [6 empty] | 0.52 |  | 0.00 |  |  |  | 0.01 |  |  | 0.03 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.18
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 1.49 | [8 empty] | 0.07 |  |  | 0.00 | [6 empty] | 0.52 |  | 0.00 |  |  |  | 0.01 |  |  | 0.03 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.18
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.01 |  |  | 0.01 | [6 empty] | 0.05 |  | 0.01 |  |  |  | 0.01 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.33 |  | 0.41 |  |  |  | 0.05 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.07
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 194077.38 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.97 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.23 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.77 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.19 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.89 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.28 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 3673.23 |  |  | 5849 |  |  |  | 844 | [10 empty] | 76.58 |  |  |  | 99.06 | [5 empty] | 76.45 |  |  | 99.90 |  |  |  | 0.69 |  | 0.69 | [8 empty] | 0.25 |  |  |  |  | 22.48
1988 |  |  |  | 5958.52 |  |  | 7659 |  |  |  | 837 | [10 empty] | 86.53 |  |  |  | 86.85 | [5 empty] | 81.04 |  |  | 87.19 |  |  |  | 8.74 |  | 8.32 | [8 empty] | 4.83 |  |  |  |  | 0.32
1989 |  |  |  | 6523.47 |  |  | 8661 |  |  |  | 837 | [10 empty] | 89.21 |  |  |  | 98.45 | [5 empty] | 88.97 |  |  | 98.87 |  |  |  | 1.29 |  | 1.29 | [8 empty] | 0.26 |  |  |  |  | 9.24
1990 |  |  |  | 5758.67 |  |  | 7186 |  |  |  | 842 | [10 empty] | 78.09 |  |  |  | 80.67 | [5 empty] | 78.00 |  |  | 82.03 |  |  |  | 7.58 |  | 6.62 | [8 empty] | 12.71 |  |  |  |  | 2.58
1991 |  |  |  | 6932.70 |  |  | 8213 |  |  |  | 860 | [10 empty] | 92.47 |  |  |  | 92.96 | [5 empty] | 92.02 |  |  | 93.76 |  |  |  | 1.65 |  | 1.56 | [8 empty] | 5.48 |  |  |  |  | 0.48
1992 |  |  |  | 5451.09 |  |  | 6587 |  |  |  | 860 | [10 empty] | 72.41 |  |  |  | 72.43 | [5 empty] | 72.16 |  |  | 74.99 |  |  |  | 11.73 |  | 9.63 | [8 empty] | 17.94 |  |  |  |  | 0.02
1993 |  |  |  | 4675.90 |  |  | 7064 |  |  |  | 860 | [10 empty] | 62.27 |  |  |  | 62.27 | [5 empty] | 62.07 |  |  | 80.64 |  |  |  | 28.79 |  | 25.18 | [8 empty] | 12.55 |  |  |  |  | 0.00
1994 |  |  |  | 6443.16 |  |  | 8760 |  |  |  | 860 | [10 empty] | 86.00 |  |  |  | 86.00 | [5 empty] | 85.53 |  |  | 100.00 |  |  |  | 13.88 |  | 13.86 | [8 empty] | 0.15 |  |  |  |  | 0.00
1995 |  |  |  | 6113.35 |  |  | 7876 |  |  |  | 860 | [10 empty] | 81.34 |  |  |  | 81.34 | [5 empty] | 81.15 |  |  | 89.91 |  |  |  | 9.36 |  | 8.40 | [8 empty] | 10.26 |  |  |  |  | 0.00
1996 |  |  |  | 6957.82 |  |  | 8783 |  |  |  | 860 | [10 empty] | 92.14 |  |  |  | 92.14 | [5 empty] | 92.10 |  |  | 99.99 |  |  |  | 7.86 |  | 7.86 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 6346.54 |  |  | 8003 |  |  |  | 860 | [10 empty] | 84.24 |  |  |  | 84.24 | [5 empty] | 84.24 |  |  | 91.36 |  |  |  | 15.73 |  | 15.72 | [8 empty] | 0.03 |  |  |  |  | 0.00
1998 |  |  |  | 4122.43 |  |  | 5368 |  |  |  | 785 | [10 empty] | 59.76 |  |  |  | 59.86 | [5 empty] | 59.95 |  |  | 61.28 |  |  |  | 18.78 |  | 13.84 | [8 empty] | 26.30 |  |  |  |  | 0.10
1999 |  |  |  | 4114.43 |  |  | 5414 |  |  |  | 785 | [10 empty] | 59.77 |  |  |  | 59.98 | [5 empty] | 59.83 |  |  | 61.80 |  |  |  | 15.23 |  | 10.77 | [8 empty] | 29.25 |  |  |  |  | 0.21
2000 |  |  |  | 6530.94 |  |  | 8293 |  |  |  | 785 | [10 empty] | 93.67 |  |  |  | 93.67 | [5 empty] | 94.71 |  |  | 94.41 |  |  |  | 4.25 |  | 4.16 | [8 empty] | 2.17 |  |  |  |  | 0.00
2001 |  |  |  | 5424.77 |  |  | 6852 |  |  |  | 790 | [10 empty] | 78.03 |  |  |  | 78.03 | [5 empty] | 78.39 |  |  | 78.22 |  |  |  | 4.50 |  | 3.67 | [8 empty] | 18.30 |  |  |  |  | 0.00
2002 |  |  |  | 6685.96 |  |  | 8543 |  |  |  | 790 | [10 empty] | 97.01 |  |  |  | 97.01 | [5 empty] | 96.61 |  |  | 97.52 |  |  |  | 2.99 |  | 2.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 4959.99 |  |  | 6301 |  |  |  | 790 | [10 empty] | 71.89 |  |  |  | 71.89 | [5 empty] | 71.67 |  |  | 71.93 |  |  |  | 0.08 |  | 11.29 | [8 empty] | 16.81 |  |  |  |  | 0.00
2004 |  |  |  | 5695.77 |  |  | 7374 |  |  |  | 790 | [10 empty] | 82.80 |  |  |  | 83.01 | [5 empty] | 82.08 |  |  | 83.95 |  |  |  | 11.13 |  | 10.39 | [8 empty] | 6.60 |  |  |  |  | 0.21
2005 |  |  |  | 6889.22 |  |  | 8745 |  |  |  | 790 | [10 empty] | 99.44 |  |  |  | 99.65 | [5 empty] | 99.55 |  |  | 99.83 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.01 |  |  |  |  | 0.22
2006 |  |  |  | 5283.88 |  |  | 6791 |  |  |  | 790 | [10 empty] | 76.37 |  |  |  | 76.58 | [5 empty] | 76.31 |  |  | 77.52 |  |  |  | 4.47 |  | 5.14 | [8 empty] | 18.28 |  |  |  |  | 0.20
2007 |  |  |  | 6485.25 |  |  | 8341 |  |  |  | 795 | [10 empty] | 93.39 |  |  |  | 94.04 | [5 empty] | 93.12 |  |  | 95.22 |  |  |  | 2.41 |  | 2.32 | [8 empty] | 3.64 |  |  |  |  | 0.65
2008 |  |  |  | 6514.39 |  |  | 8699 |  |  |  | 782 | [10 empty] | 94.30 |  |  |  | 94.52 | [5 empty] | 94.84 |  |  | 99.03 |  |  |  | 5.43 |  | 5.42 | [8 empty] | 0.06 |  |  |  |  | 0.22
2009 |  |  |  | 5266.44 |  |  | 6906 |  |  |  | 782 | [10 empty] | 80.58 |  |  |  | 80.58 | [5 empty] | 76.88 |  |  | 78.84 |  |  |  | 1.79 |  | 4.43 | [8 empty] | 14.99 |  |  |  |  | 0.00
2010 |  |  |  | 6930.19 |  |  | 8760 |  |  |  | 817 | [10 empty] | 98.61 |  |  |  | 98.78 | [5 empty] | 98.93 |  |  | 100.00 |  |  |  | 0.75 |  | 0.74 | [8 empty] | 0.48 |  |  |  |  | 0.16
2011 |  |  |  | 6453.40 |  |  | 8015 |  |  |  | 817 | [10 empty] | 91.37 |  |  |  | 91.44 | [5 empty] | 90.17 |  |  | 91.50 |  |  |  | 1.81 |  | 2.81 | [8 empty] | 5.75 |  |  |  |  | 0.07
2012 |  |  |  | 5682.67 |  |  | 7161 |  |  |  | 817 | [10 empty] | 85.48 |  |  |  | 85.62 | [5 empty] | 79.18 |  |  | 81.52 |  |  |  | 1.87 |  | 3.88 | [8 empty] | 10.51 |  |  |  |  | 0.14
2013 |  |  |  | 5656.62 |  |  | 7141 |  |  |  | 817 | [10 empty] | 80.58 |  |  |  | 80.64 | [5 empty] | 79.04 |  |  | 81.52 |  |  |  | 7.01 |  | 6.08 | [8 empty] | 13.28 |  |  |  |  | 0.07
2014 |  |  |  | 6873.54 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.87 |  |  |  | 99.87 | [5 empty] | 96.04 |  |  | 100.00 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6288.54 |  |  | 8001 |  |  |  | 817 | [10 empty] | 90.66 |  |  |  | 90.66 | [5 empty] | 87.87 |  |  | 91.34 |  |  |  | 2.36 |  | 2.19 | [8 empty] | 7.15 |  |  |  |  | 0.00
2016 |  |  |  | 5038.39 |  |  | 6291 |  |  |  | 817 | [10 empty] | 71.41 |  |  |  | 71.41 | [5 empty] | 70.21 |  |  | 71.62 |  |  |  | 1.17 |  | 0.84 | [8 empty] | 27.74 |  |  |  |  | 0.00
2017 |  |  |  | 6992.50 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.70 |  |  |  | 99.98 | [5 empty] | 97.70 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.28
2018 |  |  |  | 4816.88 |  |  | 6123 |  |  |  | 817 | [10 empty] | 67.07 |  |  |  | 67.14 | [5 empty] | 67.30 |  |  | 69.90 |  |  |  | 2.68 |  | 10.62 | [8 empty] | 22.25 |  |  |  |  | 0.07
2019 |  |  |  | 7082.00 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.75 |  |  |  | 99.82 | [5 empty] | 98.95 |  |  | 100.00 |  |  |  | 0.18 |  | 0.18 | [8 empty] | 0.01 |  |  |  |  | 0.07
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1987 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 303
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 116
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 640 |  |  |  | 30
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 23
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 1
Subtotal | [37 empty] | 756 |  |  |  | 340 | [11 empty] | 23
Total | [22 empty] | 0 | [14 empty] | 1119
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1987 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 34
12. |  |  | Reactor I&C Systems | [34 empty] | 9
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 19
15. |  |  | Reactor Cooling Systems | [34 empty] | 56
16. |  |  | Steam generation systems | [34 empty] | 145
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 6
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 18
Total | [37 empty] | 336

## DARLINGTON-1
2019 Operating Experience
CA-22 | [8 empty] | DARLINGTON-1 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-04-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-12-19
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1992-11-14
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 29 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 7619.17 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.29 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.13 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.29 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.7 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 99.06 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.57 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 649.09 | 592.54 |  |  |  | 655.03 |  | 630.31 | [8 empty] | 653.48 |  |  | 630.78 | [6 empty] | 645.90 |  | 634.46 |  |  |  | 612.84 |  |  | 642.10 |  |  | 625.51 | [9 empty] | 647.15 |  |  | 7619.17
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.96 |  | 99.54 | [8 empty] | 100.00 |  |  | 99.98 | [6 empty] | 99.15 |  | 97.22 |  |  |  | 97.05 |  |  | 98.30 |  |  | 99.35 | [9 empty] | 99.07 |  |  | 99.13
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.96 |  | 99.54 | [8 empty] | 100.00 |  |  | 99.98 | [6 empty] | 99.78 |  | 99.82 |  |  |  | 98.67 |  |  | 99.11 |  |  | 99.76 | [9 empty] | 99.82 |  |  | 99.70
LF [%] |  |  |  |  | 99.37 | 100.43 |  |  |  | 100.27 |  | 99.71 | [8 empty] | 100.04 |  |  | 99.78 | [6 empty] | 98.88 |  | 97.13 |  |  |  | 96.94 |  |  | 98.30 |  |  | 98.95 | [9 empty] | 99.07 |  |  | 99.06
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.46 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.22 |  | 0.18 |  |  |  | 1.33 |  |  | 0.89 |  |  | 0.19 | [9 empty] | 0.18 |  |  | 0.29
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.46 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.22 |  | 0.18 |  |  |  | 1.33 |  |  | 0.89 |  |  | 0.19 | [9 empty] | 0.18 |  |  | 0.29
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.04 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.06 | [9 empty] | 0.00 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.63 |  | 2.61 |  |  |  | 1.62 |  |  | 0.82 |  |  | 0.41 | [9 empty] | 0.75 |  |  | 0.57
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 181936 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.75 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.07 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.32 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.04 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.64 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.64 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.97 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.79 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1992 |  |  |  | 973.98 |  |  | 1152 |  |  |  | 881 | [10 empty] | 96.83 |  |  |  | 96.83 | [5 empty] | 75.51 |  |  | 78.69 |  |  |  | 3.17 |  | 3.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 6016.23 |  |  | 7213 |  |  |  | 881 | [10 empty] | 78.72 |  |  |  | 79.18 | [5 empty] | 77.96 |  |  | 82.34 |  |  |  | 9.34 |  | 8.16 | [8 empty] | 12.66 |  |  |  |  | 0.45
1994 |  |  |  | 6326.65 |  |  | 7446 |  |  |  | 881 | [10 empty] | 83.13 |  |  |  | 83.46 | [5 empty] | 81.98 |  |  | 85.00 |  |  |  | 10.94 |  | 10.25 | [8 empty] | 6.29 |  |  |  |  | 0.33
1995 |  |  |  | 6853.27 |  |  | 8046 |  |  |  | 881 | [10 empty] | 89.72 |  |  |  | 90.65 | [5 empty] | 88.80 |  |  | 91.85 |  |  |  | 4.41 |  | 4.19 | [8 empty] | 5.16 |  |  |  |  | 0.94
1996 |  |  |  | 5745.25 |  |  | 6827 |  |  |  | 881 | [10 empty] | 75.03 |  |  |  | 75.68 | [5 empty] | 74.24 |  |  | 77.72 |  |  |  | 20.47 |  | 19.48 | [8 empty] | 4.84 |  |  |  |  | 0.65
1997 |  |  |  | 4765.08 |  |  | 7236 |  |  |  | 881 | [10 empty] | 62.33 |  |  |  | 63.04 | [5 empty] | 61.74 |  |  | 82.60 |  |  |  | 31.33 |  | 28.76 | [8 empty] | 8.20 |  |  |  |  | 0.71
1998 |  |  |  | 6427.46 |  |  | 7717 |  |  |  | 881 | [10 empty] | 83.28 |  |  |  | 84.27 | [5 empty] | 83.28 |  |  | 88.09 |  |  |  | 6.58 |  | 5.94 | [8 empty] | 9.79 |  |  |  |  | 0.99
1999 |  |  |  | 7175.13 |  |  | 8705 |  |  |  | 881 | [10 empty] | 92.97 |  |  |  | 94.35 | [5 empty] | 92.97 |  |  | 99.37 |  |  |  | 5.65 |  | 5.65 | [8 empty] | 0.00 |  |  |  |  | 1.38
2000 |  |  |  | 6280.57 |  |  | 7615 |  |  |  | 881 | [10 empty] | 81.18 |  |  |  | 81.97 | [5 empty] | 81.16 |  |  | 86.69 |  |  |  | 5.20 |  | 4.49 | [8 empty] | 13.54 |  |  |  |  | 0.79
2001 |  |  |  | 6980.80 |  |  | 8502 |  |  |  | 881 | [10 empty] | 90.45 |  |  |  | 91.17 | [5 empty] | 90.45 |  |  | 97.05 |  |  |  | 5.81 |  | 5.62 | [8 empty] | 3.21 |  |  |  |  | 0.71
2002 |  |  |  | 6532.91 |  |  | 7887 |  |  |  | 881 | [10 empty] | 84.65 |  |  |  | 85.51 | [5 empty] | 84.65 |  |  | 90.03 |  |  |  | 7.89 |  | 7.32 | [8 empty] | 7.16 |  |  |  |  | 0.86
2003 |  |  |  | 6562.38 |  |  | 7846 |  |  |  | 881 | [10 empty] | 85.10 |  |  |  | 87.47 | [5 empty] | 85.03 |  |  | 89.57 |  |  |  | 5.14 |  | 4.74 | [8 empty] | 7.79 |  |  |  |  | 2.38
2004 |  |  |  | 5612.12 |  |  | 6540 |  |  |  | 881 | [10 empty] | 72.82 |  |  |  | 73.58 | [5 empty] | 72.52 |  |  | 74.45 |  |  |  | 9.72 |  | 7.92 | [8 empty] | 18.50 |  |  |  |  | 0.76
2005 |  |  |  | 7366.26 |  |  | 8553 |  |  |  | 881 | [10 empty] | 96.20 |  |  |  | 97.04 | [5 empty] | 95.69 |  |  | 97.64 |  |  |  | 2.96 |  | 2.96 | [8 empty] | 0.00 |  |  |  |  | 0.84
2006 |  |  |  | 6388.89 |  |  | 7520 |  |  |  | 878 | [10 empty] | 83.43 |  |  |  | 85.16 | [5 empty] | 83.07 |  |  | 85.84 |  |  |  | 1.85 |  | 2.36 | [8 empty] | 12.47 |  |  |  |  | 1.73
2007 |  |  |  | 7412.62 |  |  | 8647 |  |  |  | 878 | [10 empty] | 96.81 |  |  |  | 98.15 | [5 empty] | 96.38 |  |  | 98.71 |  |  |  | 1.74 |  | 1.74 | [8 empty] | 0.11 |  |  |  |  | 1.35
2008 |  |  |  | 6125.27 |  |  | 7125 |  |  |  | 878 | [10 empty] | 79.73 |  |  |  | 80.79 | [5 empty] | 79.42 |  |  | 81.11 |  |  |  | 0.08 |  | 0.06 | [8 empty] | 19.15 |  |  |  |  | 1.06
2009 |  |  |  | 6870.24 |  |  | 8038 |  |  |  | 878 | [10 empty] | 89.79 |  |  |  | 90.98 | [5 empty] | 89.33 |  |  | 91.76 |  |  |  | 0.66 |  | 0.60 | [8 empty] | 8.42 |  |  |  |  | 1.19
2010 |  |  |  | 7244.93 |  |  | 8660 |  |  |  | 878 | [10 empty] | 94.48 |  |  |  | 95.47 | [5 empty] | 94.20 |  |  | 98.86 |  |  |  | 4.48 |  | 4.48 | [8 empty] | 0.04 |  |  |  |  | 1.00
2011 |  |  |  | 6256.80 |  |  | 7313 |  |  |  | 878 | [10 empty] | 81.55 |  |  |  | 82.66 | [5 empty] | 81.35 |  |  | 83.48 |  |  |  | 0.44 |  | 0.36 | [8 empty] | 16.98 |  |  |  |  | 1.11
2012 |  |  |  | 7256.40 |  |  | 8468 |  |  |  | 878 | [10 empty] | 94.31 |  |  |  | 95.50 | [5 empty] | 94.09 |  |  | 96.40 |  |  |  | 4.44 |  | 4.44 | [8 empty] | 0.06 |  |  |  |  | 1.19
2013 |  |  |  | 7454.01 |  |  | 8760 |  |  |  | 878 | [10 empty] | 97.12 |  |  |  | 98.37 | [5 empty] | 96.92 |  |  | 100.00 |  |  |  | 1.37 |  | 1.37 | [8 empty] | 0.26 |  |  |  |  | 1.25
2014 |  |  |  | 5818.57 |  |  | 6848 |  |  |  | 878 | [10 empty] | 75.86 |  |  |  | 76.51 | [5 empty] | 75.65 |  |  | 78.17 |  |  |  | 2.22 |  | 1.74 | [8 empty] | 21.75 |  |  |  |  | 0.65
2015 |  |  |  | 5480.95 |  |  | 6449 |  |  |  | 878 | [10 empty] | 71.43 |  |  |  | 72.33 | [5 empty] | 71.26 |  |  | 73.62 |  |  |  | 8.35 |  | 7.09 | [8 empty] | 20.58 |  |  |  |  | 0.90
2016 |  |  |  | 7570.79 |  |  | 8784 |  |  |  | 878 | [10 empty] | 98.62 |  |  |  | 99.69 | [5 empty] | 98.16 |  |  | 100.00 |  |  |  | 0.25 |  | 0.25 | [8 empty] | 0.07 |  |  |  |  | 1.07
2017 |  |  |  | 4638.42 |  |  | 6181 |  |  |  | 878 | [10 empty] | 60.26 |  |  |  | 60.87 | [5 empty] | 60.31 |  |  | 70.56 |  |  |  | 3.49 |  | 2.20 | [8 empty] | 36.93 |  |  |  |  | 0.61
2018 |  |  |  | 7477.90 |  |  | 8606 |  |  |  | 878 | [10 empty] | 97.02 |  |  |  | 97.92 | [5 empty] | 97.23 |  |  | 98.24 |  |  |  | 0.69 |  | 1.43 | [8 empty] | 0.64 |  |  |  |  | 0.90
2019 |  |  |  | 7619.17 |  |  | 8760 |  |  |  | 878 | [10 empty] | 99.13 |  |  |  | 99.70 | [5 empty] | 99.06 |  |  | 100.00 |  |  |  | 0.29 |  | 0.29 | [8 empty] | 0.01 |  |  |  |  | 0.57
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1992 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 418
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 731
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 39
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 0
Z. |  | Other | [39 empty] | 1
Subtotal | [37 empty] | 770 |  |  |  | 419 | [11 empty] | 3
Total | [22 empty] | 0 | [14 empty] | 1192
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1992 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 31
12. |  |  | Reactor I&C Systems | [34 empty] | 28
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 185
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 25
31. |  |  | Turbine and auxiliaries | [34 empty] | 17
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 23
41. |  |  | Main Generator Systems | [34 empty] | 48
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [37 empty] | 395

## DARLINGTON-2
2019 Operating Experience
CA-23 | [8 empty] | DARLINGTON-2 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-09-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-01-15
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-10-09
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 29 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8760 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 161331 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 12.95 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.03 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.05 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 71.91 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.04 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.88 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 1153.47 |  |  | 1608 |  |  |  | 881 | [10 empty] | 64.94 |  |  |  | 64.94 | [5 empty] | 65.73 |  |  | 80.72 |  |  |  | 35.03 |  | 35.02 | [8 empty] | 0.04 |  |  |  |  | 0.00
1991 |  |  |  | 51.48 |  |  | 102 |  |  |  | 881 | [10 empty] | 0.67 |  |  |  | 0.67 | [5 empty] | 0.67 |  |  | 1.16 |  |  |  | 99.33 |  | 99.33 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 1290.16 |  |  | 2418 |  |  |  | 881 | [10 empty] | 16.68 |  |  |  | 16.68 | [5 empty] | 16.67 |  |  | 27.53 |  |  |  | 83.32 |  | 83.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 6370.16 |  |  | 7594 |  |  |  | 881 | [10 empty] | 82.74 |  |  |  | 83.28 | [5 empty] | 82.54 |  |  | 86.69 |  |  |  | 8.13 |  | 7.37 | [8 empty] | 9.34 |  |  |  |  | 0.54
1994 |  |  |  | 6750.76 |  |  | 8069 |  |  |  | 881 | [10 empty] | 88.52 |  |  |  | 88.90 | [5 empty] | 87.47 |  |  | 92.11 |  |  |  | 5.87 |  | 5.54 | [8 empty] | 5.56 |  |  |  |  | 0.38
1995 |  |  |  | 6952.96 |  |  | 8104 |  |  |  | 881 | [10 empty] | 90.65 |  |  |  | 91.30 | [5 empty] | 90.09 |  |  | 92.51 |  |  |  | 5.07 |  | 4.88 | [8 empty] | 3.82 |  |  |  |  | 0.65
1996 |  |  |  | 6705.75 |  |  | 7752 |  |  |  | 881 | [10 empty] | 87.22 |  |  |  | 87.76 | [5 empty] | 86.65 |  |  | 88.25 |  |  |  | 5.55 |  | 5.15 | [8 empty] | 7.09 |  |  |  |  | 0.53
1997 |  |  |  | 4710.39 |  |  | 7069 |  |  |  | 881 | [10 empty] | 61.53 |  |  |  | 61.73 | [5 empty] | 61.03 |  |  | 80.70 |  |  |  | 29.89 |  | 26.32 | [8 empty] | 11.95 |  |  |  |  | 0.20
1998 |  |  |  | 6227.93 |  |  | 7492 |  |  |  | 881 | [10 empty] | 80.70 |  |  |  | 81.91 | [5 empty] | 80.70 |  |  | 85.53 |  |  |  | 18.09 |  | 18.09 | [8 empty] | 0.00 |  |  |  |  | 1.21
1999 |  |  |  | 6469.08 |  |  | 7824 |  |  |  | 881 | [10 empty] | 83.82 |  |  |  | 85.13 | [5 empty] | 83.82 |  |  | 89.32 |  |  |  | 5.12 |  | 4.60 | [8 empty] | 10.27 |  |  |  |  | 1.31
2000 |  |  |  | 6885.42 |  |  | 8221 |  |  |  | 881 | [10 empty] | 88.97 |  |  |  | 90.14 | [5 empty] | 88.97 |  |  | 93.59 |  |  |  | 9.86 |  | 9.86 | [8 empty] | 0.00 |  |  |  |  | 1.17
2001 |  |  |  | 5826.45 |  |  | 7030 |  |  |  | 881 | [10 empty] | 75.50 |  |  |  | 76.30 | [5 empty] | 75.50 |  |  | 80.25 |  |  |  | 6.64 |  | 5.43 | [8 empty] | 18.27 |  |  |  |  | 0.81
2002 |  |  |  | 7268.93 |  |  | 8627 |  |  |  | 881 | [10 empty] | 94.19 |  |  |  | 95.43 | [5 empty] | 94.19 |  |  | 98.48 |  |  |  | 4.57 |  | 4.57 | [8 empty] | 0.00 |  |  |  |  | 1.25
2003 |  |  |  | 6084.10 |  |  | 7245 |  |  |  | 881 | [10 empty] | 79.29 |  |  |  | 81.59 | [5 empty] | 78.83 |  |  | 82.71 |  |  |  | 5.71 |  | 4.94 | [8 empty] | 13.47 |  |  |  |  | 2.30
2004 |  |  |  | 7038.38 |  |  | 8737 |  |  |  | 881 | [10 empty] | 91.42 |  |  |  | 96.71 | [5 empty] | 90.95 |  |  | 99.46 |  |  |  | 3.29 |  | 3.29 | [8 empty] | 0.00 |  |  |  |  | 5.29
2005 |  |  |  | 6056.21 |  |  | 7031 |  |  |  | 878 | [10 empty] | 78.93 |  |  |  | 79.75 | [5 empty] | 78.67 |  |  | 80.26 |  |  |  | 0.98 |  | 4.72 | [8 empty] | 15.53 |  |  |  |  | 0.82
2006 |  |  |  | 7548.39 |  |  | 8745 |  |  |  | 878 | [10 empty] | 98.59 |  |  |  | 99.38 | [5 empty] | 98.14 |  |  | 99.83 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.00 |  |  |  |  | 0.79
2007 |  |  |  | 6364.83 |  |  | 7327 |  |  |  | 878 | [10 empty] | 82.85 |  |  |  | 83.37 | [5 empty] | 82.75 |  |  | 83.64 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 16.62 |  |  |  |  | 0.52
2008 |  |  |  | 7560.94 |  |  | 8696 |  |  |  | 878 | [10 empty] | 98.15 |  |  |  | 98.82 | [5 empty] | 98.04 |  |  | 99.00 |  |  |  | 1.18 |  | 1.18 | [8 empty] | 0.00 |  |  |  |  | 0.67
2009 |  |  |  | 6745.27 |  |  | 7769 |  |  |  | 878 | [10 empty] | 87.67 |  |  |  | 88.37 | [5 empty] | 87.70 |  |  | 88.69 |  |  |  | 2.03 |  | 2.71 | [8 empty] | 8.91 |  |  |  |  | 0.70
2010 |  |  |  | 6234.30 |  |  | 7248 |  |  |  | 878 | [10 empty] | 81.14 |  |  |  | 82.48 | [5 empty] | 81.06 |  |  | 82.74 |  |  |  | 0.67 |  | 0.56 | [8 empty] | 16.96 |  |  |  |  | 1.34
2011 |  |  |  | 7503.51 |  |  | 8719 |  |  |  | 878 | [10 empty] | 97.74 |  |  |  | 98.90 | [5 empty] | 97.56 |  |  | 99.53 |  |  |  | 1.06 |  | 1.06 | [8 empty] | 0.04 |  |  |  |  | 1.16
2012 |  |  |  | 7157.95 |  |  | 8467 |  |  |  | 878 | [10 empty] | 92.97 |  |  |  | 93.92 | [5 empty] | 92.81 |  |  | 96.39 |  |  |  | 3.86 |  | 3.77 | [8 empty] | 2.30 |  |  |  |  | 0.96
2013 |  |  |  | 5138.76 |  |  | 6131 |  |  |  | 878 | [10 empty] | 66.97 |  |  |  | 67.33 | [5 empty] | 66.81 |  |  | 69.99 |  |  |  | 7.39 |  | 10.77 | [8 empty] | 21.91 |  |  |  |  | 0.36
2014 |  |  |  | 7412.53 |  |  | 8522 |  |  |  | 878 | [10 empty] | 96.38 |  |  |  | 96.90 | [5 empty] | 96.38 |  |  | 97.28 |  |  |  | 2.22 |  | 2.21 | [8 empty] | 0.89 |  |  |  |  | 0.52
2015 |  |  |  | 6405.95 |  |  | 7428 |  |  |  | 878 | [10 empty] | 83.41 |  |  |  | 84.28 | [5 empty] | 83.29 |  |  | 84.79 |  |  |  | 2.05 |  | 1.77 | [8 empty] | 13.95 |  |  |  |  | 0.87
2016 |  |  |  | 5728.84 |  |  | 6793 |  |  |  | 878 | [10 empty] | 74.41 |  |  |  | 75.73 | [5 empty] | 74.28 |  |  | 77.33 |  |  |  | 3.13 |  | 2.45 | [8 empty] | 21.82 |  |  |  |  | 1.32
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1990 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 517
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 518 |  |  |  | 12
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8760 | [14 empty] | 963
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
Z. |  | Other | [39 empty] | 224
Subtotal | [22 empty] | 8760 | [14 empty] | 1481 |  |  |  | 753 | [11 empty] | 3
Total | [22 empty] | 8760 | [14 empty] | 2237
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1990 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 38
12. |  |  | Reactor I&C Systems | [34 empty] | 28
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 322
16. |  |  | Steam generation systems | [34 empty] | 42
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 15
31. |  |  | Turbine and auxiliaries | [34 empty] | 20
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 6
35. |  |  | All other I&C Systems | [34 empty] | 11
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 11
Total | [37 empty] | 519
Highlights (2019)
The unit is in refurbishment and does not generate power.

## DARLINGTON-3
2019 Operating Experience
CA-24 | [8 empty] | DARLINGTON-3 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-09-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1992-12-07
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-02-14
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 7026.63 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 7.52 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.58 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.48 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.54 %
Load Factor (LF) | [18 empty] | : | 91.36 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.4 %
Operating Factor (OF) | [18 empty] | : | 93.36 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 582 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 643.98 | 588.15 |  |  |  | 644.62 |  | 630.62 | [8 empty] | 650.73 |  |  | 630.96 | [6 empty] | 238.39 |  | 583.41 |  |  |  | 618.46 |  |  | 649.52 |  |  | 485.91 | [9 empty] | 661.87 |  |  | 7026.63
EAF [%] |  |  |  |  | 99.99 | 99.99 |  |  |  | 99.98 |  | 99.42 | [8 empty] | 100.00 |  |  | 99.92 | [6 empty] | 36.56 |  | 89.37 |  |  |  | 98.06 |  |  | 99.23 |  |  | 77.57 | [9 empty] | 99.99 |  |  | 91.58
UCF [%] |  |  |  |  | 99.99 | 99.99 |  |  |  | 99.98 |  | 99.42 | [8 empty] | 100.00 |  |  | 99.92 | [6 empty] | 36.70 |  | 92.04 |  |  |  | 99.22 |  |  | 100.00 |  |  | 77.57 | [9 empty] | 99.99 |  |  | 91.98
LF [%] |  |  |  |  | 98.58 | 99.68 |  |  |  | 98.68 |  | 99.76 | [8 empty] | 99.62 |  |  | 99.81 | [6 empty] | 36.49 |  | 89.31 |  |  |  | 97.83 |  |  | 99.43 |  |  | 76.87 | [9 empty] | 101.32 |  |  | 91.36
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 38.17 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 83.06 | [9 empty] | 100.00 |  |  | 93.36
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.57 | [8 empty] | 0.00 |  |  | 0.03 | [6 empty] | 63.30 |  | 1.87 |  |  |  | 0.77 |  |  | 0.00 |  |  | 22.42 | [9 empty] | 0.00 |  |  | 7.52
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.57 | [8 empty] | 0.00 |  |  | 0.03 | [6 empty] | 63.30 |  | 1.75 |  |  |  | 0.77 |  |  | 0.00 |  |  | 22.42 | [9 empty] | 0.00 |  |  | 7.48
PUF [%] |  |  |  |  | 0.01 | 0.01 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.04 | [6 empty] | 0.00 |  | 6.20 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.01 |  |  | 0.54
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.14 |  | 2.68 |  |  |  | 1.17 |  |  | 0.77 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.40
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 178775 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.06 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.33 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.17 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.79 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.01 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.84 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.09 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 6003.39 |  |  | 7141 |  |  |  | 881 | [10 empty] | 89.24 |  |  |  | 89.81 | [5 empty] | 85.01 |  |  | 89.08 |  |  |  | 10.05 |  | 10.04 | [8 empty] | 0.15 |  |  |  |  | 0.57
1994 |  |  |  | 6528.54 |  |  | 7642 |  |  |  | 881 | [10 empty] | 85.26 |  |  |  | 85.64 | [5 empty] | 84.59 |  |  | 87.24 |  |  |  | 2.11 |  | 1.85 | [8 empty] | 12.51 |  |  |  |  | 0.38
1995 |  |  |  | 7061.53 |  |  | 8219 |  |  |  | 881 | [10 empty] | 92.22 |  |  |  | 92.93 | [5 empty] | 91.50 |  |  | 93.82 |  |  |  | 3.05 |  | 2.92 | [8 empty] | 4.15 |  |  |  |  | 0.71
1996 |  |  |  | 7391.57 |  |  | 8574 |  |  |  | 881 | [10 empty] | 96.66 |  |  |  | 97.34 | [5 empty] | 95.51 |  |  | 97.61 |  |  |  | 2.65 |  | 2.65 | [8 empty] | 0.01 |  |  |  |  | 0.68
1997 |  |  |  | 4010.78 |  |  | 6314 |  |  |  | 881 | [10 empty] | 52.10 |  |  |  | 52.35 | [5 empty] | 51.97 |  |  | 72.08 |  |  |  | 40.36 |  | 35.42 | [8 empty] | 12.22 |  |  |  |  | 0.25
1998 |  |  |  | 7244.91 |  |  | 8593 |  |  |  | 881 | [10 empty] | 93.88 |  |  |  | 94.68 | [5 empty] | 93.88 |  |  | 98.09 |  |  |  | 4.05 |  | 4.00 | [8 empty] | 1.32 |  |  |  |  | 0.80
1999 |  |  |  | 5629.08 |  |  | 6929 |  |  |  | 881 | [10 empty] | 72.94 |  |  |  | 75.09 | [5 empty] | 72.94 |  |  | 79.10 |  |  |  | 6.57 |  | 5.28 | [8 empty] | 19.63 |  |  |  |  | 2.15
2000 |  |  |  | 6517.02 |  |  | 7822 |  |  |  | 881 | [10 empty] | 84.22 |  |  |  | 85.10 | [5 empty] | 84.21 |  |  | 89.05 |  |  |  | 8.27 |  | 7.67 | [8 empty] | 7.23 |  |  |  |  | 0.88
2001 |  |  |  | 6577.97 |  |  | 7901 |  |  |  | 881 | [10 empty] | 85.23 |  |  |  | 86.30 | [5 empty] | 85.23 |  |  | 90.19 |  |  |  | 8.87 |  | 8.40 | [8 empty] | 5.30 |  |  |  |  | 1.07
2002 |  |  |  | 6371.77 |  |  | 7595 |  |  |  | 881 | [10 empty] | 82.58 |  |  |  | 83.68 | [5 empty] | 82.56 |  |  | 86.70 |  |  |  | 4.81 |  | 4.23 | [8 empty] | 12.09 |  |  |  |  | 1.10
2003 |  |  |  | 6827.19 |  |  | 8004 |  |  |  | 881 | [10 empty] | 88.62 |  |  |  | 89.45 | [5 empty] | 88.46 |  |  | 91.37 |  |  |  | 2.21 |  | 2.02 | [8 empty] | 8.53 |  |  |  |  | 0.83
2004 |  |  |  | 6601.58 |  |  | 7649 |  |  |  | 881 | [10 empty] | 85.59 |  |  |  | 86.88 | [5 empty] | 85.31 |  |  | 87.08 |  |  |  | 5.14 |  | 4.71 | [8 empty] | 8.41 |  |  |  |  | 1.29
2005 |  |  |  | 7562.05 |  |  | 8760 |  |  |  | 878 | [10 empty] | 98.26 |  |  |  | 99.08 | [5 empty] | 98.24 |  |  | 100.00 |  |  |  | 0.89 |  | 0.89 | [8 empty] | 0.02 |  |  |  |  | 0.83
2006 |  |  |  | 5573.10 |  |  | 6452 |  |  |  | 878 | [10 empty] | 72.50 |  |  |  | 73.12 | [5 empty] | 72.46 |  |  | 73.65 |  |  |  | 8.54 |  | 13.05 | [8 empty] | 13.84 |  |  |  |  | 0.62
2007 |  |  |  | 7221.13 |  |  | 8311 |  |  |  | 878 | [10 empty] | 93.90 |  |  |  | 94.75 | [5 empty] | 93.89 |  |  | 94.87 |  |  |  | 0.02 |  | 0.75 | [8 empty] | 4.49 |  |  |  |  | 0.85
2008 |  |  |  | 7654.59 |  |  | 8784 |  |  |  | 878 | [10 empty] | 99.15 |  |  |  | 99.93 | [5 empty] | 99.25 |  |  | 100.00 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.03 |  |  |  |  | 0.78
2009 |  |  |  | 5657.16 |  |  | 6590 |  |  |  | 878 | [10 empty] | 73.60 |  |  |  | 74.47 | [5 empty] | 73.55 |  |  | 75.23 |  |  |  | 2.00 |  | 3.62 | [8 empty] | 21.91 |  |  |  |  | 0.87
2010 |  |  |  | 7500.90 |  |  | 8643 |  |  |  | 878 | [10 empty] | 97.47 |  |  |  | 98.51 | [5 empty] | 97.52 |  |  | 98.66 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 1.43 |  |  |  |  | 1.04
2011 |  |  |  | 7558.56 |  |  | 8707 |  |  |  | 878 | [10 empty] | 98.37 |  |  |  | 99.17 | [5 empty] | 98.27 |  |  | 99.39 |  |  |  | 0.78 |  | 0.78 | [8 empty] | 0.04 |  |  |  |  | 0.81
2012 |  |  |  | 6377.61 |  |  | 7419 |  |  |  | 878 | [10 empty] | 83.03 |  |  |  | 83.97 | [5 empty] | 82.69 |  |  | 84.46 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 15.98 |  |  |  |  | 0.94
2013 |  |  |  | 7334.60 |  |  | 8470 |  |  |  | 878 | [10 empty] | 95.63 |  |  |  | 96.61 | [5 empty] | 95.36 |  |  | 96.69 |  |  |  | 3.35 |  | 3.35 | [8 empty] | 0.04 |  |  |  |  | 0.98
2014 |  |  |  | 7501.60 |  |  | 8708 |  |  |  | 878 | [10 empty] | 97.75 |  |  |  | 98.75 | [5 empty] | 97.53 |  |  | 99.41 |  |  |  | 1.23 |  | 1.23 | [8 empty] | 0.02 |  |  |  |  | 1.00
2015 |  |  |  | 4992.10 |  |  | 5787 |  |  |  | 878 | [10 empty] | 65.00 |  |  |  | 65.52 | [5 empty] | 64.91 |  |  | 66.06 |  |  |  | 8.58 |  | 7.75 | [8 empty] | 26.73 |  |  |  |  | 0.52
2016 |  |  |  | 6716.91 |  |  | 7832 |  |  |  | 878 | [10 empty] | 86.99 |  |  |  | 87.63 | [5 empty] | 87.09 |  |  | 89.16 |  |  |  | 5.93 |  | 5.53 | [8 empty] | 6.84 |  |  |  |  | 0.64
2017 |  |  |  | 7219.88 |  |  | 8442 |  |  |  | 878 | [10 empty] | 94.27 |  |  |  | 95.20 | [5 empty] | 93.87 |  |  | 96.37 |  |  |  | 1.42 |  | 1.37 | [8 empty] | 3.43 |  |  |  |  | 0.93
2018 |  |  |  | 5781.75 |  |  | 6718 |  |  |  | 878 | [10 empty] | 75.15 |  |  |  | 75.94 | [5 empty] | 75.17 |  |  | 76.69 |  |  |  | 1.62 |  | 1.25 | [8 empty] | 22.81 |  |  |  |  | 0.79
2019 |  |  |  | 7026.63 |  |  | 8178 |  |  |  | 878 | [10 empty] | 91.58 |  |  |  | 91.98 | [5 empty] | 91.36 |  |  | 93.36 |  |  |  | 7.52 |  | 7.48 | [8 empty] | 0.54 |  |  |  |  | 0.40
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1993 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 582 | [14 empty] | 270
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 74
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 590
E. |  | Testing of plant systems or components | [39 empty] | 5
L. |  | Human factor related | [39 empty] | 3
Subtotal | [26 empty] | 582 | [10 empty] | 664 |  |  |  | 278
Total | [22 empty] | 582 | [14 empty] | 942
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1993 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 122 | [14 empty] | 22
12. |  |  | Reactor I&C Systems | [34 empty] | 28
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 460 | [14 empty] | 32
14. |  |  | Safety Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 45
16. |  |  | Steam generation systems | [34 empty] | 15
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 20
31. |  |  | Turbine and auxiliaries | [34 empty] | 59
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
34. |  |  | Miscellaneous Systems | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 20
42. |  |  | Electrical Power Supply Systems | [34 empty] | 9
Total | [22 empty] | 582 | [14 empty] | 278

## DARLINGTON-4
2019 Operating Experience
CA-25 | [8 empty] | DARLINGTON-4 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-07-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-04-17
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-06-14
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 26 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 5423.69 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 7.34 %
Energy Availability Factor (EAF) | [18 empty] | : | 70.07 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.58 %
Unit Capability Factor (UCF) | [18 empty] | : | 70.44 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 23.99 %
Load Factor (LF) | [18 empty] | : | 70.52 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.37 %
Operating Factor (OF) | [18 empty] | : | 71.32 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2512 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 332.08 | 0.00 |  |  |  | 0.00 |  | 401.45 | [8 empty] | 660.91 |  |  | 640.14 | [6 empty] | 643.77 |  | 602.11 |  |  |  | 623.15 |  |  | 653.75 |  |  | 634.71 | [9 empty] | 231.62 |  |  | 5423.69
EAF [%] |  |  |  |  | 51.28 | 0.00 |  |  |  | 0.00 |  | 62.02 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 98.30 |  | 92.18 |  |  |  | 98.72 |  |  | 99.56 |  |  | 100.00 | [9 empty] | 34.54 |  |  | 70.07
UCF [%] |  |  |  |  | 51.46 | 0.00 |  |  |  | 0.00 |  | 62.02 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 98.56 |  | 94.69 |  |  |  | 99.85 |  |  | 99.86 |  |  | 100.00 | [9 empty] | 34.54 |  |  | 70.44
LF [%] |  |  |  |  | 50.84 | 0.00 |  |  |  | 0.00 |  | 63.50 | [8 empty] | 101.17 |  |  | 101.26 | [6 empty] | 98.55 |  | 92.17 |  |  |  | 98.57 |  |  | 100.08 |  |  | 100.40 | [9 empty] | 35.46 |  |  | 70.52
OF [%] |  |  |  |  | 52.02 | 0.00 |  |  |  | 0.00 |  | 63.19 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 36.29 |  |  | 71.32
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.07 |  |  | 0.14 |  |  | 0.00 | [9 empty] | 65.46 |  |  | 7.34
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.07 |  |  | 0.14 |  |  | 0.00 | [9 empty] | 65.46 |  |  | 5.58
PUF [%] |  |  |  |  | 48.54 | 100.00 |  |  |  | 100.00 |  | 37.98 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.44 |  | 5.31 |  |  |  | 0.08 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 23.99
XUF [%] |  |  |  |  | 0.18 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.26 |  | 2.51 |  |  |  | 1.13 |  |  | 0.30 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.37
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 175698 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.08 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.53 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.06 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.24 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.7 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.71 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.82 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 3528.78 |  |  | 4447 |  |  |  | 881 | [10 empty] | 73.87 |  |  |  | 74.02 | [5 empty] | 67.58 |  |  | 70.40 |  |  |  | 10.42 |  | 8.61 | [8 empty] | 17.37 |  |  |  |  | 0.15
1994 |  |  |  | 7038.67 |  |  | 8143 |  |  |  | 881 | [10 empty] | 91.85 |  |  |  | 92.19 | [5 empty] | 91.20 |  |  | 92.96 |  |  |  | 3.36 |  | 3.21 | [8 empty] | 4.60 |  |  |  |  | 0.35
1995 |  |  |  | 6750.56 |  |  | 7751 |  |  |  | 881 | [10 empty] | 87.72 |  |  |  | 88.14 | [5 empty] | 87.47 |  |  | 88.48 |  |  |  | 2.41 |  | 2.18 | [8 empty] | 9.68 |  |  |  |  | 0.43
1996 |  |  |  | 6105.35 |  |  | 7023 |  |  |  | 881 | [10 empty] | 79.14 |  |  |  | 79.37 | [5 empty] | 78.89 |  |  | 79.95 |  |  |  | 12.79 |  | 11.65 | [8 empty] | 8.98 |  |  |  |  | 0.23
1997 |  |  |  | 5069.64 |  |  | 7428 |  |  |  | 881 | [10 empty] | 65.71 |  |  |  | 65.97 | [5 empty] | 65.69 |  |  | 84.79 |  |  |  | 28.56 |  | 26.37 | [8 empty] | 7.65 |  |  |  |  | 0.27
1998 |  |  |  | 6520.88 |  |  | 7699 |  |  |  | 881 | [10 empty] | 84.49 |  |  |  | 85.32 | [5 empty] | 84.49 |  |  | 87.89 |  |  |  | 11.60 |  | 11.20 | [8 empty] | 3.48 |  |  |  |  | 0.83
1999 |  |  |  | 6216.13 |  |  | 7431 |  |  |  | 881 | [10 empty] | 80.55 |  |  |  | 81.60 | [5 empty] | 80.55 |  |  | 84.83 |  |  |  | 5.28 |  | 4.55 | [8 empty] | 13.85 |  |  |  |  | 1.05
2000 |  |  |  | 6975.02 |  |  | 8219 |  |  |  | 881 | [10 empty] | 90.13 |  |  |  | 90.78 | [5 empty] | 90.13 |  |  | 93.57 |  |  |  | 9.22 |  | 9.22 | [8 empty] | 0.00 |  |  |  |  | 0.65
2001 |  |  |  | 6836.35 |  |  | 8037 |  |  |  | 881 | [10 empty] | 88.58 |  |  |  | 89.62 | [5 empty] | 88.58 |  |  | 91.75 |  |  |  | 3.01 |  | 2.78 | [8 empty] | 7.59 |  |  |  |  | 1.04
2002 |  |  |  | 7449.79 |  |  | 8760 |  |  |  | 881 | [10 empty] | 96.53 |  |  |  | 97.33 | [5 empty] | 96.53 |  |  | 100.00 |  |  |  | 2.67 |  | 2.67 | [8 empty] | 0.00 |  |  |  |  | 0.80
2003 |  |  |  | 5428.86 |  |  | 6320 |  |  |  | 881 | [10 empty] | 70.64 |  |  |  | 72.28 | [5 empty] | 70.34 |  |  | 72.15 |  |  |  | 5.81 |  | 4.46 | [8 empty] | 23.26 |  |  |  |  | 1.64
2004 |  |  |  | 7321.13 |  |  | 8451 |  |  |  | 881 | [10 empty] | 94.60 |  |  |  | 95.25 | [5 empty] | 94.60 |  |  | 96.21 |  |  |  | 4.75 |  | 4.75 | [8 empty] | 0.00 |  |  |  |  | 0.65
2005 |  |  |  | 6569.70 |  |  | 7617 |  |  |  | 878 | [10 empty] | 85.63 |  |  |  | 86.47 | [5 empty] | 85.35 |  |  | 86.95 |  |  |  | 0.36 |  | 2.49 | [8 empty] | 11.04 |  |  |  |  | 0.84
2006 |  |  |  | 7449.44 |  |  | 8541 |  |  |  | 878 | [10 empty] | 96.54 |  |  |  | 97.08 | [5 empty] | 96.86 |  |  | 97.50 |  |  |  | 2.92 |  | 2.92 | [8 empty] | 0.00 |  |  |  |  | 0.54
2007 |  |  |  | 6210.23 |  |  | 7170 |  |  |  | 878 | [10 empty] | 80.77 |  |  |  | 81.44 | [5 empty] | 80.74 |  |  | 81.85 |  |  |  | 2.90 |  | 2.43 | [8 empty] | 16.13 |  |  |  |  | 0.67
2008 |  |  |  | 7525.46 |  |  | 8652 |  |  |  | 878 | [10 empty] | 97.35 |  |  |  | 98.39 | [5 empty] | 97.58 |  |  | 98.50 |  |  |  | 1.48 |  | 1.48 | [8 empty] | 0.13 |  |  |  |  | 1.05
2009 |  |  |  | 6836.15 |  |  | 7892 |  |  |  | 878 | [10 empty] | 88.71 |  |  |  | 89.71 | [5 empty] | 88.88 |  |  | 90.09 |  |  |  | 2.12 |  | 2.23 | [8 empty] | 8.06 |  |  |  |  | 1.00
2010 |  |  |  | 5633.65 |  |  | 6612 |  |  |  | 878 | [10 empty] | 73.26 |  |  |  | 73.62 | [5 empty] | 73.25 |  |  | 75.48 |  |  |  | 8.67 |  | 10.81 | [8 empty] | 15.57 |  |  |  |  | 0.36
2011 |  |  |  | 7617.80 |  |  | 8760 |  |  |  | 878 | [10 empty] | 98.89 |  |  |  | 99.73 | [5 empty] | 99.04 |  |  | 100.00 |  |  |  | 0.23 |  | 0.23 | [8 empty] | 0.04 |  |  |  |  | 0.85
2012 |  |  |  | 7557.72 |  |  | 8725 |  |  |  | 878 | [10 empty] | 97.88 |  |  |  | 98.99 | [5 empty] | 97.99 |  |  | 99.33 |  |  |  | 0.87 |  | 0.87 | [8 empty] | 0.14 |  |  |  |  | 1.11
2013 |  |  |  | 5237.45 |  |  | 6132 |  |  |  | 878 | [10 empty] | 68.25 |  |  |  | 68.83 | [5 empty] | 68.10 |  |  | 70.00 |  |  |  | 9.51 |  | 12.75 | [8 empty] | 18.42 |  |  |  |  | 0.58
2014 |  |  |  | 7302.71 |  |  | 8476 |  |  |  | 878 | [10 empty] | 95.24 |  |  |  | 95.97 | [5 empty] | 94.95 |  |  | 96.76 |  |  |  | 0.65 |  | 0.63 | [8 empty] | 3.40 |  |  |  |  | 0.73
2015 |  |  |  | 6532.11 |  |  | 7490 |  |  |  | 878 | [10 empty] | 84.72 |  |  |  | 85.13 | [5 empty] | 84.93 |  |  | 85.50 |  |  |  | 1.53 |  | 1.32 | [8 empty] | 13.55 |  |  |  |  | 0.40
2016 |  |  |  | 5774.65 |  |  | 6678 |  |  |  | 878 | [10 empty] | 74.66 |  |  |  | 75.46 | [5 empty] | 74.88 |  |  | 76.02 |  |  |  | 0.23 |  | 0.18 | [8 empty] | 24.36 |  |  |  |  | 0.80
2017 |  |  |  | 7593.09 |  |  | 8684 |  |  |  | 878 | [10 empty] | 98.10 |  |  |  | 98.77 | [5 empty] | 98.72 |  |  | 99.13 |  |  |  | 1.03 |  | 1.03 | [8 empty] | 0.20 |  |  |  |  | 0.67
2018 |  |  |  | 6993.41 |  |  | 8105 |  |  |  | 878 | [10 empty] | 90.71 |  |  |  | 91.56 | [5 empty] | 90.93 |  |  | 92.52 |  |  |  | 1.42 |  | 1.32 | [8 empty] | 7.12 |  |  |  |  | 0.85
2019 |  |  |  | 5423.69 |  |  | 6248 |  |  |  | 878 | [10 empty] | 70.07 |  |  |  | 70.44 | [5 empty] | 70.52 |  |  | 71.32 |  |  |  | 7.34 |  | 5.58 | [8 empty] | 23.99 |  |  |  |  | 0.37
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1993 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 474 | [14 empty] | 294
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2037 | [14 empty] | 99
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 638
E. |  | Testing of plant systems or components | [35 empty] | 13 |  |  |  | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 11
Subtotal | [22 empty] | 2037 |  |  |  | 474 | [10 empty] | 750 |  |  |  | 307 | [11 empty] | 4
Total | [22 empty] | 2511 | [14 empty] | 1061
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1993 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 42
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 89
16. |  |  | Steam generation systems | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 17
31. |  |  | Turbine and auxiliaries | [19 empty] | 474 | [14 empty] | 43
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 22
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 20
42. |  |  | Electrical Power Supply Systems | [34 empty] | 33
Total | [22 empty] | 474 | [14 empty] | 311

## PICKERING-1
2019 Operating Experience
CA-4 | [8 empty] | PICKERING-1 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500A | [11 empty] | Construction Date | [15 empty] | : |  |  | 1966-06-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1971-04-04
Gross electrical power | [12 empty] | : |  |  | 542 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1971-07-29
Reference unit power (net) | [12 empty] | : |  |  | 515 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 9080 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4680 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 26.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 6 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 4299.59 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.3 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.53 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.27 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.91 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.82 %
Load Factor (LF) | [18 empty] | : | 95.3 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.38 %
Operating Factor (OF) | [18 empty] | : | 97.98 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 177 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 373.60 | 330.43 |  |  |  | 363.42 |  | 369.51 | [8 empty] | 278.99 |  |  | 366.30 | [6 empty] | 377.51 |  | 371.34 |  |  |  | 354.38 |  |  | 373.33 |  |  | 361.63 | [9 empty] | 379.16 |  |  | 4299.59
EAF [%] |  |  |  |  | 97.73 | 95.48 |  |  |  | 94.87 |  | 99.76 | [8 empty] | 73.10 |  |  | 99.16 | [6 empty] | 98.77 |  | 97.07 |  |  |  | 95.74 |  |  | 97.64 |  |  | 97.99 | [9 empty] | 99.40 |  |  | 95.53
UCF [%] |  |  |  |  | 97.74 | 95.48 |  |  |  | 94.87 |  | 99.76 | [8 empty] | 73.10 |  |  | 99.16 | [6 empty] | 99.44 |  | 98.91 |  |  |  | 97.15 |  |  | 98.17 |  |  | 97.99 | [9 empty] | 99.40 |  |  | 95.91
LF [%] |  |  |  |  | 97.50 | 95.48 |  |  |  | 94.85 |  | 99.65 | [8 empty] | 72.81 |  |  | 98.79 | [6 empty] | 98.52 |  | 96.92 |  |  |  | 95.57 |  |  | 97.44 |  |  | 97.53 | [9 empty] | 98.96 |  |  | 95.30
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 76.21 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.98
FLR [%] |  |  |  |  | 2.26 | 4.52 |  |  |  | 0.00 |  | 0.24 | [8 empty] | 26.63 |  |  | 0.84 | [6 empty] | 0.56 |  | 1.09 |  |  |  | 1.16 |  |  | 1.83 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.30
UCL [%] |  |  |  |  | 2.26 | 4.52 |  |  |  | 0.00 |  | 0.24 | [8 empty] | 26.53 |  |  | 0.84 | [6 empty] | 0.56 |  | 1.09 |  |  |  | 1.14 |  |  | 1.83 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.27
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 5.13 |  | 0.00 | [8 empty] | 0.37 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 1.71 |  |  | 0.00 |  |  | 2.01 | [9 empty] | 0.60 |  |  | 0.82
XUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.67 |  | 1.85 |  |  |  | 1.41 |  |  | 0.53 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.38
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 121328 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 24.22 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 67.84 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 22.84 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 68.06 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.1 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.73 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.22 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 69.13 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1971 |  |  |  | 2302.30 |  |  | 4829 |  |  |  | 514 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 80.43 |  |  | 78.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1972 |  |  |  | 2207.90 |  |  | 4117 |  |  |  | 514 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 48.90 |  |  | 46.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 4222.40 |  |  | 8523 |  |  |  | 514 | [10 empty] | 93.98 |  |  |  | 93.98 | [5 empty] | 92.26 |  |  | 95.72 |  |  |  | 5.19 |  | 5.15 | [8 empty] | 0.88 |  |  |  |  | 0.00
1974 |  |  |  | 3232.00 |  |  | 6979 |  |  |  | 514 | [10 empty] | 71.92 |  |  |  | 71.92 | [5 empty] | 71.98 |  |  | 79.89 |  |  |  | 20.17 |  | 18.17 | [8 empty] | 9.91 |  |  |  |  | 0.00
1975 |  |  |  | 3592.80 |  |  | 7234 |  |  |  | 512 | [10 empty] | 80.17 |  |  |  | 80.17 | [5 empty] | 80.32 |  |  | 82.81 |  |  |  | 11.74 |  | 10.66 | [8 empty] | 9.17 |  |  |  |  | 0.00
1976 |  |  |  | 4169.70 |  |  | 8136 |  |  |  | 514 | [10 empty] | 92.73 |  |  |  | 92.73 | [5 empty] | 92.61 |  |  | 92.88 |  |  |  | 2.07 |  | 1.96 | [8 empty] | 5.31 |  |  |  |  | 0.00
1977 |  |  |  | 3852.80 |  |  | 7545 |  |  |  | 514 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 85.80 |  |  | 86.37 |  |  |  | 6.14 |  | 5.61 | [8 empty] | 8.59 |  |  |  |  | 0.00
1978 |  |  |  | 4273.70 |  |  | 8359 |  |  |  | 515 | [10 empty] | 95.09 |  |  |  | 95.09 | [5 empty] | 94.99 |  |  | 95.68 |  |  |  | 4.91 |  | 4.91 | [8 empty] | 0.00 |  |  |  |  | 0.00
1979 |  |  |  | 3781.40 |  |  | 7554 |  |  |  | 515 | [10 empty] | 85.29 |  |  |  | 85.29 | [5 empty] | 82.91 |  |  | 85.30 |  |  |  | 14.71 |  | 14.71 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 3356.90 |  |  | 6640 |  |  |  | 515 | [10 empty] | 73.68 |  |  |  | 73.68 | [5 empty] | 74.21 |  |  | 75.59 |  |  |  | 14.10 |  | 12.09 | [8 empty] | 14.23 |  |  |  |  | 0.00
1981 |  |  |  | 3947.70 |  |  | 7795 |  |  |  | 515 | [10 empty] | 88.05 |  |  |  | 88.05 | [5 empty] | 87.50 |  |  | 88.98 |  |  |  | 5.07 |  | 4.70 | [8 empty] | 7.25 |  |  |  |  | 0.00
1982 |  |  |  | 3499.30 |  |  | 6915 |  |  |  | 515 | [10 empty] | 77.80 |  |  |  | 77.80 | [5 empty] | 77.57 |  |  | 78.94 |  |  |  | 10.00 |  | 8.65 | [8 empty] | 13.55 |  |  |  |  | 0.00
1983 |  |  |  | 3070.80 |  |  | 6101 |  |  |  | 515 | [10 empty] | 68.11 |  |  |  | 68.11 | [5 empty] | 68.07 |  |  | 69.65 |  |  |  | 27.81 |  | 26.23 | [8 empty] | 5.66 |  |  |  |  | 0.00
1984 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 832.79 |  |  | 1981 |  |  |  | 515 | [10 empty] | 17.35 |  |  |  | 19.69 | [5 empty] | 18.46 |  |  | 22.61 |  |  |  | 78.69 |  | 72.71 | [8 empty] | 7.60 |  |  |  |  | 2.33
1988 |  |  |  | 3986.48 |  |  | 8224 |  |  |  | 515 | [10 empty] | 89.12 |  |  |  | 89.16 | [5 empty] | 88.12 |  |  | 93.62 |  |  |  | 10.81 |  | 10.81 | [8 empty] | 0.04 |  |  |  |  | 0.03
1989 |  |  |  | 3222.13 |  |  | 6943 |  |  |  | 515 | [10 empty] | 72.62 |  |  |  | 72.72 | [5 empty] | 71.42 |  |  | 79.26 |  |  |  | 20.54 |  | 18.80 | [8 empty] | 8.48 |  |  |  |  | 0.11
1990 |  |  |  | 3041.75 |  |  | 7435 |  |  |  | 515 | [10 empty] | 70.56 |  |  |  | 70.86 | [5 empty] | 67.42 |  |  | 84.87 |  |  |  | 22.19 |  | 20.21 | [8 empty] | 8.93 |  |  |  |  | 0.30
1991 |  |  |  | 3051.08 |  |  | 6525 |  |  |  | 515 | [10 empty] | 67.83 |  |  |  | 67.84 | [5 empty] | 67.63 |  |  | 74.49 |  |  |  | 18.36 |  | 15.26 | [8 empty] | 16.90 |  |  |  |  | 0.01
1992 |  |  |  | 2919.96 |  |  | 5798 |  |  |  | 515 | [10 empty] | 65.43 |  |  |  | 65.43 | [5 empty] | 64.55 |  |  | 66.01 |  |  |  | 22.58 |  | 19.09 | [8 empty] | 15.48 |  |  |  |  | 0.00
1993 |  |  |  | 3451.16 |  |  | 6908 |  |  |  | 515 | [10 empty] | 78.39 |  |  |  | 78.43 | [5 empty] | 76.50 |  |  | 78.86 |  |  |  | 8.82 |  | 7.59 | [8 empty] | 13.98 |  |  |  |  | 0.04
1994 |  |  |  | 897.64 |  |  | 1835 |  |  |  | 515 | [10 empty] | 20.12 |  |  |  | 20.12 | [5 empty] | 19.90 |  |  | 20.95 |  |  |  | 54.24 |  | 23.84 | [8 empty] | 56.04 |  |  |  |  | 0.00
1995 |  |  |  | 2013.23 |  |  | 4234 |  |  |  | 515 | [10 empty] | 44.85 |  |  |  | 45.71 | [5 empty] | 44.63 |  |  | 48.33 |  |  |  | 49.07 |  | 44.04 | [8 empty] | 10.25 |  |  |  |  | 0.86
1996 |  |  |  | 3011.76 |  |  | 6202 |  |  |  | 515 | [10 empty] | 66.83 |  |  |  | 66.83 | [5 empty] | 66.58 |  |  | 70.61 |  |  |  | 31.66 |  | 30.96 | [8 empty] | 2.22 |  |  |  |  | 0.00
1997 |  |  |  | 3950.80 |  |  | 8205 |  |  |  | 515 | [10 empty] | 89.68 |  |  |  | 89.68 | [5 empty] | 88.54 |  |  | 94.70 |  |  |  | 10.32 |  | 10.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | Data not available - Long-term shutdown
1999 |  |  |  | "
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | "
2005 |  |  |  | 584.96 |  |  | 1230 |  |  |  | 515 | [10 empty] | 95.88 |  |  |  | 95.88 | [5 empty] | 51.42 |  |  | 55.68 |  |  |  | 4.12 |  | 4.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 3470.49 |  |  | 7260 |  |  |  | 515 | [10 empty] | 77.02 |  |  |  | 77.22 | [5 empty] | 76.93 |  |  | 82.88 |  |  |  | 19.42 |  | 18.85 | [8 empty] | 3.92 |  |  |  |  | 0.21
2007 |  |  |  | 1750.26 |  |  | 3447 |  |  |  | 515 | [10 empty] | 38.91 |  |  |  | 38.94 | [5 empty] | 38.80 |  |  | 39.35 |  |  |  | 50.80 |  | 43.22 | [8 empty] | 17.84 |  |  |  |  | 0.04
2008 |  |  |  | 2792.10 |  |  | 6221 |  |  |  | 515 | [10 empty] | 61.72 |  |  |  | 61.78 | [5 empty] | 61.72 |  |  | 70.82 |  |  |  | 37.71 |  | 37.70 | [8 empty] | 0.52 |  |  |  |  | 0.06
2009 |  |  |  | 4108.77 |  |  | 8436 |  |  |  | 515 | [10 empty] | 91.15 |  |  |  | 91.45 | [5 empty] | 91.08 |  |  | 96.30 |  |  |  | 8.50 |  | 8.50 | [8 empty] | 0.05 |  |  |  |  | 0.30
2010 |  |  |  | 2376.13 |  |  | 4983 |  |  |  | 515 | [10 empty] | 52.73 |  |  |  | 52.90 | [5 empty] | 52.67 |  |  | 56.88 |  |  |  | 22.60 |  | 18.82 | [8 empty] | 28.28 |  |  |  |  | 0.17
2011 |  |  |  | 3669.17 |  |  | 7382 |  |  |  | 515 | [10 empty] | 81.49 |  |  |  | 81.79 | [5 empty] | 81.33 |  |  | 84.27 |  |  |  | 18.21 |  | 18.21 | [8 empty] | 0.00 |  |  |  |  | 0.30
2012 |  |  |  | 2912.37 |  |  | 5799 |  |  |  | 515 | [10 empty] | 64.48 |  |  |  | 65.11 | [5 empty] | 64.38 |  |  | 66.02 |  |  |  | 4.03 |  | 5.44 | [8 empty] | 29.45 |  |  |  |  | 0.64
2013 |  |  |  | 2074.98 |  |  | 4344 |  |  |  | 515 | [10 empty] | 45.99 |  |  |  | 46.20 | [5 empty] | 45.99 |  |  | 49.59 |  |  |  | 33.45 |  | 53.27 | [8 empty] | 0.53 |  |  |  |  | 0.21
2014 |  |  |  | 3871.29 |  |  | 7855 |  |  |  | 515 | [10 empty] | 86.08 |  |  |  | 87.40 | [5 empty] | 85.81 |  |  | 89.67 |  |  |  | 12.55 |  | 12.55 | [8 empty] | 0.05 |  |  |  |  | 1.32
2015 |  |  |  | 2599.85 |  |  | 5263 |  |  |  | 515 | [10 empty] | 57.80 |  |  |  | 57.92 | [5 empty] | 57.63 |  |  | 60.08 |  |  |  | 2.63 |  | 6.31 | [8 empty] | 35.77 |  |  |  |  | 0.12
2016 |  |  |  | 4212.67 |  |  | 8784 |  |  |  | 515 | [10 empty] | 93.41 |  |  |  | 94.28 | [5 empty] | 93.12 |  |  | 100.00 |  |  |  | 5.25 |  | 5.22 | [8 empty] | 0.50 |  |  |  |  | 0.87
2017 |  |  |  | 2608.49 |  |  | 5323 |  |  |  | 515 | [10 empty] | 57.91 |  |  |  | 58.07 | [5 empty] | 57.82 |  |  | 60.76 |  |  |  | 8.48 |  | 5.38 | [8 empty] | 36.56 |  |  |  |  | 0.16
2018 |  |  |  | 4206.18 |  |  | 8503 |  |  |  | 515 | [10 empty] | 93.41 |  |  |  | 94.09 | [5 empty] | 93.23 |  |  | 97.07 |  |  |  | 4.63 |  | 4.57 | [8 empty] | 1.34 |  |  |  |  | 0.68
2019 |  |  |  | 4299.59 |  |  | 8583 |  |  |  | 515 | [10 empty] | 95.53 |  |  |  | 95.91 | [5 empty] | 95.30 |  |  | 97.98 |  |  |  | 3.30 |  | 3.27 | [8 empty] | 0.82 |  |  |  |  | 0.38
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1971 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 177 | [14 empty] | 1686
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 808
E. |  | Testing of plant systems or components | [35 empty] | 5 |  |  |  | 6
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 57
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
P. |  | Fire | [39 empty] | 35
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 74
Z. |  | Other | [39 empty] | 11
Subtotal | [26 empty] | 177 | [10 empty] | 813 |  |  |  | 1795 | [11 empty] | 77
Total | [22 empty] | 177 | [14 empty] | 2685
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1971 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 884
12. |  |  | Reactor I&C Systems | [34 empty] | 71
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 62
14. |  |  | Safety Systems | [34 empty] | 61
15. |  |  | Reactor Cooling Systems | [34 empty] | 143
16. |  |  | Steam generation systems | [34 empty] | 61
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 74
31. |  |  | Turbine and auxiliaries | [34 empty] | 118
32. |  |  | Feedwater and Main Steam System | [34 empty] | 51
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 11
35. |  |  | All other I&C Systems | [19 empty] | 177 | [14 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 51
42. |  |  | Electrical Power Supply Systems | [34 empty] | 118
Total | [22 empty] | 177 | [14 empty] | 1714

## PICKERING-4
2019 Operating Experience
CA-7 | [8 empty] | PICKERING-4 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500A | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-05-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-05-21
Gross electrical power | [12 empty] | : |  |  | 542 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-06-17
Reference unit power (net) | [12 empty] | : |  |  | 515 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 9080 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 26.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 6 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 4421.44 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.21 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.17 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.2 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.52 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.27 %
Load Factor (LF) | [18 empty] | : | 98.01 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.36 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 379.68 | 342.22 |  |  |  | 378.55 |  | 368.96 | [8 empty] | 378.02 |  |  | 358.21 | [6 empty] | 366.14 |  | 373.65 |  |  |  | 358.80 |  |  | 375.39 |  |  | 365.28 | [9 empty] | 376.54 |  |  | 4421.44
EAF [%] |  |  |  |  | 99.88 | 98.88 |  |  |  | 99.17 |  | 99.92 | [8 empty] | 98.64 |  |  | 96.71 | [6 empty] | 95.63 |  | 97.53 |  |  |  | 96.90 |  |  | 97.97 |  |  | 98.51 | [9 empty] | 98.27 |  |  | 98.17
UCF [%] |  |  |  |  | 99.90 | 98.88 |  |  |  | 99.17 |  | 99.92 | [8 empty] | 98.64 |  |  | 96.71 | [6 empty] | 96.03 |  | 99.07 |  |  |  | 97.94 |  |  | 98.35 |  |  | 98.92 | [9 empty] | 98.77 |  |  | 98.52
LF [%] |  |  |  |  | 99.09 | 98.88 |  |  |  | 98.80 |  | 99.51 | [8 empty] | 98.66 |  |  | 96.60 | [6 empty] | 95.56 |  | 97.52 |  |  |  | 96.76 |  |  | 97.97 |  |  | 98.51 | [9 empty] | 98.27 |  |  | 98.01
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.10 | 1.12 |  |  |  | 0.83 |  | 0.08 | [8 empty] | 1.36 |  |  | 0.62 | [6 empty] | 3.97 |  | 0.93 |  |  |  | 2.06 |  |  | 1.60 |  |  | 1.07 | [9 empty] | 0.69 |  |  | 1.21
UCL [%] |  |  |  |  | 0.10 | 1.12 |  |  |  | 0.83 |  | 0.08 | [8 empty] | 1.36 |  |  | 0.60 | [6 empty] | 3.97 |  | 0.93 |  |  |  | 2.06 |  |  | 1.60 |  |  | 1.07 | [9 empty] | 0.69 |  |  | 1.20
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.68 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.05 |  |  | 0.01 | [9 empty] | 0.54 |  |  | 0.27
XUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.39 |  | 1.54 |  |  |  | 1.04 |  |  | 0.38 |  |  | 0.41 | [9 empty] | 0.50 |  |  | 0.36
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 124791 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 18.1 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 67.69 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 16.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 68.07 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.63 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.54 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.39 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 70.65 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 2226.60 |  |  | 4402 |  |  |  | 514 | [10 empty] | 90.59 |  |  |  | 90.59 | [5 empty] | 90.40 |  |  | 91.75 |  |  |  | 6.12 |  | 5.91 | [8 empty] | 3.50 |  |  |  |  | 0.00
1974 |  |  |  | 4221.00 |  |  | 8356 |  |  |  | 514 | [10 empty] | 94.00 |  |  |  | 94.00 | [5 empty] | 94.00 |  |  | 95.65 |  |  |  | 5.22 |  | 5.18 | [8 empty] | 0.82 |  |  |  |  | 0.00
1975 |  |  |  | 1094.20 |  |  | 2201 |  |  |  | 513 | [10 empty] | 24.24 |  |  |  | 24.24 | [5 empty] | 24.42 |  |  | 25.19 |  |  |  | 73.53 |  | 67.34 | [8 empty] | 8.42 |  |  |  |  | 0.00
1976 |  |  |  | 3089.00 |  |  | 6063 |  |  |  | 514 | [10 empty] | 68.23 |  |  |  | 68.23 | [5 empty] | 68.60 |  |  | 69.21 |  |  |  | 31.44 |  | 31.29 | [8 empty] | 0.49 |  |  |  |  | 0.00
1977 |  |  |  | 4107.20 |  |  | 7975 |  |  |  | 514 | [10 empty] | 90.30 |  |  |  | 90.30 | [5 empty] | 91.47 |  |  | 91.29 |  |  |  | 4.38 |  | 4.13 | [8 empty] | 5.57 |  |  |  |  | 0.00
1978 |  |  |  | 4033.90 |  |  | 7876 |  |  |  | 515 | [10 empty] | 89.70 |  |  |  | 89.70 | [5 empty] | 89.66 |  |  | 90.16 |  |  |  | 3.07 |  | 2.84 | [8 empty] | 7.46 |  |  |  |  | 0.00
1979 |  |  |  | 4102.20 |  |  | 8059 |  |  |  | 515 | [10 empty] | 91.00 |  |  |  | 91.00 | [5 empty] | 89.94 |  |  | 91.00 |  |  |  | 4.67 |  | 4.45 | [8 empty] | 4.55 |  |  |  |  | 0.00
1980 |  |  |  | 3700.50 |  |  | 7321 |  |  |  | 515 | [10 empty] | 81.76 |  |  |  | 81.76 | [5 empty] | 81.80 |  |  | 83.34 |  |  |  | 8.38 |  | 7.48 | [8 empty] | 10.77 |  |  |  |  | 0.00
1981 |  |  |  | 4142.00 |  |  | 8078 |  |  |  | 515 | [10 empty] | 91.65 |  |  |  | 91.65 | [5 empty] | 91.81 |  |  | 92.21 |  |  |  | 3.83 |  | 3.65 | [8 empty] | 4.70 |  |  |  |  | 0.00
1982 |  |  |  | 4137.90 |  |  | 8087 |  |  |  | 515 | [10 empty] | 91.76 |  |  |  | 91.76 | [5 empty] | 91.72 |  |  | 92.32 |  |  |  | 2.61 |  | 2.46 | [8 empty] | 5.78 |  |  |  |  | 0.00
1983 |  |  |  | 4170.20 |  |  | 8183 |  |  |  | 515 | [10 empty] | 92.32 |  |  |  | 92.32 | [5 empty] | 92.44 |  |  | 93.41 |  |  |  | 5.55 |  | 5.43 | [8 empty] | 2.25 |  |  |  |  | 0.00
1984 |  |  |  | 3733.30 |  |  | 7425 |  |  |  | 515 | [10 empty] | 82.75 |  |  |  | 82.75 | [5 empty] | 82.53 |  |  | 84.53 |  |  |  | 4.49 |  | 3.89 | [8 empty] | 13.36 |  |  |  |  | 0.00
1985 |  |  |  | 3438.86 |  |  | 6824 |  |  |  | 515 | [10 empty] | 77.47 |  |  |  | 83.50 | [5 empty] | 76.23 |  |  | 77.90 |  |  |  | 16.50 |  | 16.50 | [8 empty] | 0.00 |  |  |  |  | 6.03
1986 |  |  |  | 3687.37 |  |  | 7410 |  |  |  | 515 | [10 empty] | 83.16 |  |  |  | 83.16 | [5 empty] | 81.73 |  |  | 84.59 |  |  |  | 7.06 |  | 6.32 | [8 empty] | 10.52 |  |  |  |  | 0.00
1987 |  |  |  | 3770.41 |  |  | 7495 |  |  |  | 515 | [10 empty] | 83.96 |  |  |  | 84.33 | [5 empty] | 83.58 |  |  | 85.56 |  |  |  | 2.74 |  | 2.37 | [8 empty] | 13.29 |  |  |  |  | 0.37
1988 |  |  |  | 3166.17 |  |  | 6525 |  |  |  | 515 | [10 empty] | 70.11 |  |  |  | 70.11 | [5 empty] | 69.99 |  |  | 74.28 |  |  |  | 17.91 |  | 15.29 | [8 empty] | 14.60 |  |  |  |  | 0.00
1989 |  |  |  | 2255.49 |  |  | 5468 |  |  |  | 515 | [10 empty] | 50.00 |  |  |  | 50.00 | [5 empty] | 50.00 |  |  | 62.42 |  |  |  | 34.52 |  | 26.35 | [8 empty] | 23.65 |  |  |  |  | 0.00
1990 |  |  |  | 1070.83 |  |  | 2851 |  |  |  | 515 | [10 empty] | 23.74 |  |  |  | 23.74 | [5 empty] | 23.74 |  |  | 32.55 |  |  |  | 43.49 |  | 18.27 | [8 empty] | 58.00 |  |  |  |  | 0.00
1991 |  |  |  | 2130.76 |  |  | 5185 |  |  |  | 515 | [10 empty] | 47.34 |  |  |  | 47.34 | [5 empty] | 47.23 |  |  | 59.19 |  |  |  | 21.40 |  | 12.89 | [8 empty] | 39.77 |  |  |  |  | 0.00
1992 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1993 |  |  |  | 3309.63 |  |  | 6711 |  |  |  | 515 | [10 empty] | 73.76 |  |  |  | 74.21 | [5 empty] | 73.36 |  |  | 76.61 |  |  |  | 7.77 |  | 6.25 | [8 empty] | 19.55 |  |  |  |  | 0.45
1994 |  |  |  | 4009.64 |  |  | 7915 |  |  |  | 515 | [10 empty] | 89.51 |  |  |  | 89.71 | [5 empty] | 88.88 |  |  | 90.35 |  |  |  | 10.20 |  | 10.19 | [8 empty] | 0.09 |  |  |  |  | 0.21
1995 |  |  |  | 2806.96 |  |  | 5684 |  |  |  | 515 | [10 empty] | 63.33 |  |  |  | 63.84 | [5 empty] | 62.22 |  |  | 64.89 |  |  |  | 36.16 |  | 36.16 | [8 empty] | 0.00 |  |  |  |  | 0.50
1996 |  |  |  | 1134.91 |  |  | 2230 |  |  |  | 515 | [10 empty] | 25.13 |  |  |  | 25.13 | [5 empty] | 25.09 |  |  | 25.39 |  |  |  | 72.71 |  | 66.95 | [8 empty] | 7.92 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1998 |  |  |  | Data not provided
1999 |  |  |  | Data not available - Long-term shutdown
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | 844.81 |  |  | 1880 |  |  |  | 515 | [10 empty] | 72.27 |  |  |  | 72.27 | [5 empty] | 72.27 |  |  | 82.70 |  |  |  | 27.73 |  | 27.73 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 3266.76 |  |  | 6739 |  |  |  | 515 | [10 empty] | 72.10 |  |  |  | 75.58 | [5 empty] | 72.21 |  |  | 76.72 |  |  |  | 19.76 |  | 18.61 | [8 empty] | 5.81 |  |  |  |  | 3.48
2005 |  |  |  | 2996.45 |  |  | 5900 |  |  |  | 515 | [10 empty] | 66.40 |  |  |  | 66.52 | [5 empty] | 66.42 |  |  | 67.35 |  |  |  | 33.48 |  | 33.48 | [8 empty] | 0.00 |  |  |  |  | 0.13
2006 |  |  |  | 2976.54 |  |  | 6149 |  |  |  | 515 | [10 empty] | 65.96 |  |  |  | 66.30 | [5 empty] | 65.98 |  |  | 70.19 |  |  |  | 15.05 |  | 17.26 | [8 empty] | 16.44 |  |  |  |  | 0.34
2007 |  |  |  | 1959.14 |  |  | 4086 |  |  |  | 515 | [10 empty] | 43.44 |  |  |  | 43.44 | [5 empty] | 43.43 |  |  | 46.64 |  |  |  | 49.23 |  | 55.59 | [8 empty] | 0.96 |  |  |  |  | 0.00
2008 |  |  |  | 3656.45 |  |  | 7765 |  |  |  | 515 | [10 empty] | 80.83 |  |  |  | 80.91 | [5 empty] | 80.83 |  |  | 88.40 |  |  |  | 19.04 |  | 19.03 | [8 empty] | 0.07 |  |  |  |  | 0.08
2009 |  |  |  | 1620.17 |  |  | 3845 |  |  |  | 515 | [10 empty] | 35.91 |  |  |  | 36.15 | [5 empty] | 35.91 |  |  | 43.89 |  |  |  | 48.47 |  | 42.90 | [8 empty] | 20.95 |  |  |  |  | 0.24
2010 |  |  |  | 3203.51 |  |  | 6583 |  |  |  | 515 | [10 empty] | 71.13 |  |  |  | 71.37 | [5 empty] | 71.01 |  |  | 75.15 |  |  |  | 17.89 |  | 15.55 | [8 empty] | 13.08 |  |  |  |  | 0.24
2011 |  |  |  | 2401.12 |  |  | 4919 |  |  |  | 515 | [10 empty] | 53.28 |  |  |  | 53.66 | [5 empty] | 53.22 |  |  | 56.15 |  |  |  | 29.34 |  | 24.15 | [8 empty] | 22.18 |  |  |  |  | 0.38
2012 |  |  |  | 3310.83 |  |  | 6592 |  |  |  | 515 | [10 empty] | 73.42 |  |  |  | 73.73 | [5 empty] | 73.19 |  |  | 75.05 |  |  |  | 20.62 |  | 21.17 | [8 empty] | 5.10 |  |  |  |  | 0.31
2013 |  |  |  | 3884.54 |  |  | 7798 |  |  |  | 515 | [10 empty] | 86.29 |  |  |  | 86.60 | [5 empty] | 86.10 |  |  | 89.02 |  |  |  | 7.00 |  | 7.76 | [8 empty] | 5.64 |  |  |  |  | 0.31
2014 |  |  |  | 2853.53 |  |  | 5772 |  |  |  | 515 | [10 empty] | 63.30 |  |  |  | 63.49 | [5 empty] | 63.25 |  |  | 65.89 |  |  |  | 5.37 |  | 13.00 | [8 empty] | 23.51 |  |  |  |  | 0.19
2015 |  |  |  | 4266.31 |  |  | 8604 |  |  |  | 515 | [10 empty] | 94.66 |  |  |  | 95.12 | [5 empty] | 94.57 |  |  | 98.22 |  |  |  | 4.87 |  | 4.87 | [8 empty] | 0.01 |  |  |  |  | 0.47
2016 |  |  |  | 2455.22 |  |  | 5169 |  |  |  | 515 | [10 empty] | 54.32 |  |  |  | 54.91 | [5 empty] | 54.27 |  |  | 58.85 |  |  |  | 10.39 |  | 15.07 | [8 empty] | 30.01 |  |  |  |  | 0.60
2017 |  |  |  | 3961.10 |  |  | 7978 |  |  |  | 515 | [10 empty] | 87.94 |  |  |  | 88.20 | [5 empty] | 87.80 |  |  | 91.07 |  |  |  | 3.91 |  | 3.59 | [8 empty] | 8.20 |  |  |  |  | 0.27
2018 |  |  |  | 2792.32 |  |  | 5901 |  |  |  | 515 | [10 empty] | 62.06 |  |  |  | 62.92 | [5 empty] | 61.89 |  |  | 67.36 |  |  |  | 8.24 |  | 5.65 | [8 empty] | 31.43 |  |  |  |  | 0.87
2019 |  |  |  | 4421.44 |  |  | 8760 |  |  |  | 515 | [10 empty] | 98.17 |  |  |  | 98.52 | [5 empty] | 98.01 |  |  | 100.00 |  |  |  | 1.21 |  | 1.20 | [8 empty] | 0.27 |  |  |  |  | 0.36
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1973 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1174
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 65
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 1251
E. |  | Testing of plant systems or components | [35 empty] | 55
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 3
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 13
Z. |  | Other | [39 empty] | 7
Subtotal | [37 empty] | 1371 |  |  |  | 1184 | [11 empty] | 18
Total | [22 empty] | 0 | [14 empty] | 2573
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1973 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 59
12. |  |  | Reactor I&C Systems | [34 empty] | 139
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 155
14. |  |  | Safety Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 439
16. |  |  | Steam generation systems | [34 empty] | 40
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 106
32. |  |  | Feedwater and Main Steam System | [34 empty] | 28
34. |  |  | Miscellaneous Systems | [34 empty] | 17
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 46
42. |  |  | Electrical Power Supply Systems | [34 empty] | 109
Total | [37 empty] | 1170

## PICKERING-5
2019 Operating Experience
CA-13 | [8 empty] | PICKERING-5 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-11-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-12-19
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-05-10
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 2978.82 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.67 %
Energy Availability Factor (EAF) | [18 empty] | : | 66.3 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.13 %
Unit Capability Factor (UCF) | [18 empty] | : | 66.58 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 32.28 %
Load Factor (LF) | [18 empty] | : | 65.9 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.28 %
Operating Factor (OF) | [18 empty] | : | 67.74 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2826 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 374.38 | 343.05 |  |  |  | 377.08 |  | 364.91 | [8 empty] | 378.28 |  |  | 364.32 | [6 empty] | 373.56 |  | 371.49 |  |  |  | 26.80 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 4.95 |  |  | 2978.82
EAF [%] |  |  |  |  | 98.68 | 99.91 |  |  |  | 98.37 |  | 98.22 | [8 empty] | 99.10 |  |  | 98.98 | [6 empty] | 98.09 |  | 97.04 |  |  |  | 7.20 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 1.29 |  |  | 66.30
UCF [%] |  |  |  |  | 98.86 | 99.94 |  |  |  | 98.37 |  | 98.22 | [8 empty] | 99.10 |  |  | 98.98 | [6 empty] | 99.32 |  | 98.94 |  |  |  | 7.20 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 1.29 |  |  | 66.58
LF [%] |  |  |  |  | 97.52 | 98.93 |  |  |  | 98.22 |  | 98.22 | [8 empty] | 98.54 |  |  | 98.06 | [6 empty] | 97.30 |  | 96.77 |  |  |  | 7.21 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 1.29 |  |  | 65.90
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 8.47 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 5.51 |  |  | 67.74
FLR [%] |  |  |  |  | 1.14 | 0.06 |  |  |  | 1.63 |  | 1.78 | [8 empty] | 0.56 |  |  | 0.65 | [6 empty] | 0.68 |  | 1.06 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 81.99 |  |  | 1.67
UCL [%] |  |  |  |  | 1.14 | 0.06 |  |  |  | 1.63 |  | 1.78 | [8 empty] | 0.56 |  |  | 0.64 | [6 empty] | 0.68 |  | 1.06 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 5.87 |  |  | 1.13
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.35 |  |  | 0.37 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 92.80 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 92.84 |  |  | 32.28
XUF [%] |  |  |  |  | 0.18 | 0.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.23 |  | 1.90 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.28
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 123025 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 12.34 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.17 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 12.02 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.11 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.92 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.7 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.78 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 3202.40 |  |  | 6968 |  |  |  | 516 | [10 empty] | 90.29 |  |  |  | 90.29 | [5 empty] | 89.64 |  |  | 92.62 |  |  |  | 9.69 |  | 9.69 | [8 empty] | 0.02 |  |  |  |  | 0.00
1984 |  |  |  | 3517.52 |  |  | 7035 |  |  |  | 516 | [10 empty] | 77.75 |  |  |  | 77.75 | [5 empty] | 77.61 |  |  | 80.09 |  |  |  | 11.82 |  | 10.42 | [8 empty] | 11.83 |  |  |  |  | 0.00
1985 |  |  |  | 3366.50 |  |  | 6989 |  |  |  | 516 | [10 empty] | 77.74 |  |  |  | 83.10 | [5 empty] | 74.48 |  |  | 79.78 |  |  |  | 8.79 |  | 8.01 | [8 empty] | 8.89 |  |  |  |  | 5.36
1986 |  |  |  | 4068.64 |  |  | 8057 |  |  |  | 516 | [10 empty] | 90.70 |  |  |  | 91.16 | [5 empty] | 90.01 |  |  | 91.97 |  |  |  | 2.33 |  | 2.18 | [8 empty] | 6.66 |  |  |  |  | 0.46
1987 |  |  |  | 3600.10 |  |  | 7148 |  |  |  | 516 | [10 empty] | 79.56 |  |  |  | 80.33 | [5 empty] | 79.65 |  |  | 81.60 |  |  |  | 7.82 |  | 6.82 | [8 empty] | 12.85 |  |  |  |  | 0.77
1988 |  |  |  | 4397.16 |  |  | 8683 |  |  |  | 516 | [10 empty] | 97.52 |  |  |  | 97.55 | [5 empty] | 97.01 |  |  | 98.85 |  |  |  | 2.09 |  | 2.09 | [8 empty] | 0.37 |  |  |  |  | 0.03
1989 |  |  |  | 3400.76 |  |  | 6862 |  |  |  | 516 | [10 empty] | 75.42 |  |  |  | 75.67 | [5 empty] | 75.24 |  |  | 78.33 |  |  |  | 9.36 |  | 7.81 | [8 empty] | 16.52 |  |  |  |  | 0.25
1990 |  |  |  | 3885.00 |  |  | 7821 |  |  |  | 516 | [10 empty] | 86.36 |  |  |  | 86.44 | [5 empty] | 85.95 |  |  | 89.28 |  |  |  | 4.06 |  | 3.65 | [8 empty] | 9.90 |  |  |  |  | 0.08
1991 |  |  |  | 2887.06 |  |  | 5724 |  |  |  | 516 | [10 empty] | 64.36 |  |  |  | 64.56 | [5 empty] | 63.87 |  |  | 65.34 |  |  |  | 28.95 |  | 26.30 | [8 empty] | 9.14 |  |  |  |  | 0.20
1992 |  |  |  | 1345.25 |  |  | 2621 |  |  |  | 516 | [10 empty] | 29.76 |  |  |  | 29.76 | [5 empty] | 29.68 |  |  | 29.84 |  |  |  | 70.24 |  | 70.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 3841.81 |  |  | 8307 |  |  |  | 516 | [10 empty] | 85.40 |  |  |  | 85.57 | [5 empty] | 84.99 |  |  | 94.83 |  |  |  | 14.25 |  | 14.22 | [8 empty] | 0.22 |  |  |  |  | 0.16
1994 |  |  |  | 3074.41 |  |  | 6196 |  |  |  | 516 | [10 empty] | 68.53 |  |  |  | 68.53 | [5 empty] | 68.02 |  |  | 70.73 |  |  |  | 9.15 |  | 6.90 | [8 empty] | 24.57 |  |  |  |  | 0.00
1995 |  |  |  | 3372.87 |  |  | 7008 |  |  |  | 516 | [10 empty] | 74.76 |  |  |  | 75.01 | [5 empty] | 74.62 |  |  | 80.00 |  |  |  | 13.00 |  | 11.21 | [8 empty] | 13.77 |  |  |  |  | 0.25
1996 |  |  |  | 3042.63 |  |  | 6429 |  |  |  | 516 | [10 empty] | 67.13 |  |  |  | 67.13 | [5 empty] | 67.13 |  |  | 73.19 |  |  |  | 32.87 |  | 32.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 3924.89 |  |  | 7908 |  |  |  | 516 | [10 empty] | 86.83 |  |  |  | 86.83 | [5 empty] | 86.83 |  |  | 90.27 |  |  |  | 13.17 |  | 13.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 3490.58 |  |  | 7296 |  |  |  | 516 | [10 empty] | 77.22 |  |  |  | 77.22 | [5 empty] | 77.22 |  |  | 83.29 |  |  |  | 8.70 |  | 7.36 | [8 empty] | 15.42 |  |  |  |  | 0.00
1999 |  |  |  | 2511.57 |  |  | 5302 |  |  |  | 516 | [10 empty] | 55.56 |  |  |  | 55.63 | [5 empty] | 55.56 |  |  | 60.53 |  |  |  | 20.16 |  | 14.04 | [8 empty] | 30.33 |  |  |  |  | 0.06
2000 |  |  |  | 2631.49 |  |  | 5457 |  |  |  | 516 | [10 empty] | 58.03 |  |  |  | 58.12 | [5 empty] | 58.06 |  |  | 62.12 |  |  |  | 32.58 |  | 28.09 | [8 empty] | 13.79 |  |  |  |  | 0.09
2001 |  |  |  | 2980.21 |  |  | 5986 |  |  |  | 516 | [10 empty] | 65.87 |  |  |  | 66.57 | [5 empty] | 65.93 |  |  | 68.33 |  |  |  | 6.95 |  | 4.97 | [8 empty] | 28.46 |  |  |  |  | 0.71
2002 |  |  |  | 2655.74 |  |  | 5565 |  |  |  | 516 | [10 empty] | 58.75 |  |  |  | 59.17 | [5 empty] | 58.75 |  |  | 63.53 |  |  |  | 11.96 |  | 8.03 | [8 empty] | 32.80 |  |  |  |  | 0.41
2003 |  |  |  | 3294.96 |  |  | 6566 |  |  |  | 516 | [10 empty] | 69.14 |  |  |  | 71.14 | [5 empty] | 72.89 |  |  | 74.95 |  |  |  | 28.29 |  | 28.07 | [8 empty] | 0.79 |  |  |  |  | 2.00
2004 |  |  |  | 4159.81 |  |  | 8264 |  |  |  | 516 | [10 empty] | 92.16 |  |  |  | 92.60 | [5 empty] | 91.78 |  |  | 94.08 |  |  |  | 4.45 |  | 4.31 | [8 empty] | 3.09 |  |  |  |  | 0.44
2005 |  |  |  | 2352.79 |  |  | 4818 |  |  |  | 516 | [10 empty] | 52.63 |  |  |  | 53.56 | [5 empty] | 52.05 |  |  | 55.00 |  |  |  | 9.80 |  | 8.30 | [8 empty] | 38.14 |  |  |  |  | 0.93
2006 |  |  |  | 4010.87 |  |  | 8113 |  |  |  | 516 | [10 empty] | 88.95 |  |  |  | 89.66 | [5 empty] | 88.73 |  |  | 92.61 |  |  |  | 10.34 |  | 10.34 | [8 empty] | 0.00 |  |  |  |  | 0.71
2007 |  |  |  | 2567.59 |  |  | 5637 |  |  |  | 516 | [10 empty] | 56.96 |  |  |  | 57.51 | [5 empty] | 56.80 |  |  | 64.35 |  |  |  | 21.85 |  | 22.84 | [8 empty] | 19.66 |  |  |  |  | 0.55
2008 |  |  |  | 4026.82 |  |  | 8357 |  |  |  | 516 | [10 empty] | 88.86 |  |  |  | 89.80 | [5 empty] | 88.84 |  |  | 95.14 |  |  |  | 7.64 |  | 8.89 | [8 empty] | 1.31 |  |  |  |  | 0.94
2009 |  |  |  | 3140.88 |  |  | 6631 |  |  |  | 516 | [10 empty] | 69.60 |  |  |  | 70.12 | [5 empty] | 69.49 |  |  | 75.70 |  |  |  | 7.81 |  | 13.53 | [8 empty] | 16.35 |  |  |  |  | 0.51
2010 |  |  |  | 3769.85 |  |  | 7645 |  |  |  | 516 | [10 empty] | 83.73 |  |  |  | 84.08 | [5 empty] | 83.40 |  |  | 87.27 |  |  |  | 4.21 |  | 3.69 | [8 empty] | 12.23 |  |  |  |  | 0.36
2011 |  |  |  | 1973.46 |  |  | 4258 |  |  |  | 516 | [10 empty] | 43.87 |  |  |  | 44.83 | [5 empty] | 43.66 |  |  | 48.61 |  |  |  | 10.88 |  | 22.97 | [8 empty] | 32.20 |  |  |  |  | 0.96
2012 |  |  |  | 4347.31 |  |  | 8725 |  |  |  | 516 | [10 empty] | 96.34 |  |  |  | 98.24 | [5 empty] | 95.91 |  |  | 99.33 |  |  |  | 1.69 |  | 1.69 | [8 empty] | 0.07 |  |  |  |  | 1.89
2013 |  |  |  | 2603.23 |  |  | 5371 |  |  |  | 516 | [10 empty] | 58.06 |  |  |  | 58.57 | [5 empty] | 57.59 |  |  | 61.31 |  |  |  | 1.98 |  | 15.82 | [8 empty] | 25.61 |  |  |  |  | 0.51
2014 |  |  |  | 4255.09 |  |  | 8760 |  |  |  | 516 | [10 empty] | 94.57 |  |  |  | 95.35 | [5 empty] | 94.14 |  |  | 100.00 |  |  |  | 4.50 |  | 4.49 | [8 empty] | 0.15 |  |  |  |  | 0.78
2015 |  |  |  | 2932.28 |  |  | 5865 |  |  |  | 516 | [10 empty] | 65.29 |  |  |  | 65.91 | [5 empty] | 64.87 |  |  | 66.95 |  |  |  | 0.62 |  | 4.44 | [8 empty] | 29.66 |  |  |  |  | 0.62
2016 |  |  |  | 4352.12 |  |  | 8784 |  |  |  | 516 | [10 empty] | 96.56 |  |  |  | 98.79 | [5 empty] | 96.02 |  |  | 100.00 |  |  |  | 1.11 |  | 1.10 | [8 empty] | 0.10 |  |  |  |  | 2.23
2017 |  |  |  | 2883.68 |  |  | 5841 |  |  |  | 516 | [10 empty] | 64.14 |  |  |  | 64.82 | [5 empty] | 63.80 |  |  | 66.68 |  |  |  | 1.92 |  | 1.27 | [8 empty] | 33.91 |  |  |  |  | 0.69
2018 |  |  |  | 4255.38 |  |  | 8615 |  |  |  | 516 | [10 empty] | 94.81 |  |  |  | 97.08 | [5 empty] | 94.14 |  |  | 98.34 |  |  |  | 2.88 |  | 2.87 | [8 empty] | 0.04 |  |  |  |  | 2.28
2019 |  |  |  | 2978.82 |  |  | 5934 |  |  |  | 516 | [10 empty] | 66.30 |  |  |  | 66.58 | [5 empty] | 65.90 |  |  | 67.74 |  |  |  | 1.67 |  | 1.13 | [8 empty] | 32.28 |  |  |  |  | 0.28
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1983 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 44 | [14 empty] | 792
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2782 | [14 empty] | 1060
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 2
L. |  | Human factor related | [39 empty] | 52
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 6
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 15
Z. |  | Other | [35 empty] | 26 |  |  |  | 20
Subtotal | [22 empty] | 2782 |  |  |  | 44 | [10 empty] | 1086 |  |  |  | 866 | [11 empty] | 21
Total | [22 empty] | 2826 | [14 empty] | 1973
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1983 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 56
12. |  |  | Reactor I&C Systems | [34 empty] | 66
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 54
14. |  |  | Safety Systems | [34 empty] | 18
15. |  |  | Reactor Cooling Systems | [34 empty] | 115
16. |  |  | Steam generation systems | [34 empty] | 266
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [19 empty] | 44 | [14 empty] | 38
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 8
41. |  |  | Main Generator Systems | [34 empty] | 84
42. |  |  | Electrical Power Supply Systems | [34 empty] | 85
Total | [22 empty] | 44 | [14 empty] | 811

## PICKERING-6
2019 Operating Experience
CA-14 | [8 empty] | PICKERING-6 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-10-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-11-08
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-02-01
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 4461.28 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.59 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.59 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.4 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 98.7 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.12 %
Operating Factor (OF) | [18 empty] | : | 99.1 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 79 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 383.69 | 350.02 |  |  |  | 387.42 |  | 304.81 | [8 empty] | 387.33 |  |  | 373.71 | [6 empty] | 381.63 |  | 380.26 |  |  |  | 368.29 |  |  | 383.28 |  |  | 374.12 | [9 empty] | 386.72 |  |  | 4461.28
EAF [%] |  |  |  |  | 99.40 | 99.97 |  |  |  | 100.00 |  | 81.47 | [8 empty] | 99.99 |  |  | 99.93 | [6 empty] | 99.70 |  | 99.36 |  |  |  | 99.68 |  |  | 99.69 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 98.28
UCF [%] |  |  |  |  | 99.47 | 99.98 |  |  |  | 100.00 |  | 81.47 | [8 empty] | 99.99 |  |  | 99.93 | [6 empty] | 99.88 |  | 99.99 |  |  |  | 99.96 |  |  | 99.88 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 98.40
LF [%] |  |  |  |  | 99.94 | 100.94 |  |  |  | 100.92 |  | 82.04 | [8 empty] | 100.89 |  |  | 100.59 | [6 empty] | 99.41 |  | 99.05 |  |  |  | 99.13 |  |  | 99.84 |  |  | 100.70 | [9 empty] | 100.73 |  |  | 98.70
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 89.03 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.10
FLR [%] |  |  |  |  | 0.53 | 0.02 |  |  |  | 0.00 |  | 18.53 | [8 empty] | 0.01 |  |  | 0.01 | [6 empty] | 0.04 |  | 0.01 |  |  |  | 0.04 |  |  | 0.12 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 1.59
UCL [%] |  |  |  |  | 0.53 | 0.02 |  |  |  | 0.00 |  | 18.53 | [8 empty] | 0.01 |  |  | 0.01 | [6 empty] | 0.04 |  | 0.01 |  |  |  | 0.04 |  |  | 0.12 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 1.59
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.06 | [6 empty] | 0.08 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
XUF [%] |  |  |  |  | 0.07 | 0.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.19 |  | 0.64 |  |  |  | 0.28 |  |  | 0.20 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.12
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 127986 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.18 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.52 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.58 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.24 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.18 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.47 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.72 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.32 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 3816.08 |  |  | 7636 |  |  |  | 516 | [10 empty] | 86.09 |  |  |  | 86.09 | [5 empty] | 85.88 |  |  | 87.66 |  |  |  | 13.78 |  | 13.76 | [8 empty] | 0.16 |  |  |  |  | 0.00
1985 |  |  |  | 3289.09 |  |  | 6540 |  |  |  | 516 | [10 empty] | 73.11 |  |  |  | 79.48 | [5 empty] | 72.76 |  |  | 74.66 |  |  |  | 6.72 |  | 5.73 | [8 empty] | 14.80 |  |  |  |  | 6.37
1986 |  |  |  | 3395.22 |  |  | 6763 |  |  |  | 516 | [10 empty] | 75.84 |  |  |  | 76.11 | [5 empty] | 75.11 |  |  | 77.20 |  |  |  | 18.81 |  | 17.63 | [8 empty] | 6.25 |  |  |  |  | 0.28
1987 |  |  |  | 3949.93 |  |  | 7791 |  |  |  | 516 | [10 empty] | 86.60 |  |  |  | 88.53 | [5 empty] | 87.38 |  |  | 88.94 |  |  |  | 3.42 |  | 3.13 | [8 empty] | 8.33 |  |  |  |  | 1.94
1988 |  |  |  | 4496.76 |  |  | 8775 |  |  |  | 516 | [10 empty] | 98.42 |  |  |  | 98.49 | [5 empty] | 99.21 |  |  | 99.90 |  |  |  | 1.51 |  | 1.51 | [8 empty] | 0.00 |  |  |  |  | 0.07
1989 |  |  |  | 3950.21 |  |  | 7794 |  |  |  | 516 | [10 empty] | 87.57 |  |  |  | 87.89 | [5 empty] | 87.39 |  |  | 88.97 |  |  |  | 5.86 |  | 5.47 | [8 empty] | 6.64 |  |  |  |  | 0.31
1990 |  |  |  | 3473.45 |  |  | 7017 |  |  |  | 516 | [10 empty] | 76.92 |  |  |  | 77.74 | [5 empty] | 76.84 |  |  | 80.10 |  |  |  | 7.76 |  | 6.54 | [8 empty] | 15.72 |  |  |  |  | 0.82
1991 |  |  |  | 4469.68 |  |  | 8721 |  |  |  | 516 | [10 empty] | 98.97 |  |  |  | 99.21 | [5 empty] | 98.88 |  |  | 99.55 |  |  |  | 0.79 |  | 0.79 | [8 empty] | 0.00 |  |  |  |  | 0.24
1992 |  |  |  | 4050.47 |  |  | 7936 |  |  |  | 516 | [10 empty] | 89.29 |  |  |  | 89.32 | [5 empty] | 89.36 |  |  | 90.35 |  |  |  | 10.54 |  | 10.53 | [8 empty] | 0.15 |  |  |  |  | 0.03
1993 |  |  |  | 2689.19 |  |  | 5506 |  |  |  | 516 | [10 empty] | 59.88 |  |  |  | 60.38 | [5 empty] | 59.49 |  |  | 62.85 |  |  |  | 11.28 |  | 7.68 | [8 empty] | 31.94 |  |  |  |  | 0.50
1994 |  |  |  | 4043.00 |  |  | 8036 |  |  |  | 516 | [10 empty] | 90.14 |  |  |  | 90.15 | [5 empty] | 89.44 |  |  | 91.74 |  |  |  | 9.71 |  | 9.70 | [8 empty] | 0.15 |  |  |  |  | 0.01
1995 |  |  |  | 3493.34 |  |  | 6962 |  |  |  | 516 | [10 empty] | 77.19 |  |  |  | 77.51 | [5 empty] | 77.28 |  |  | 79.47 |  |  |  | 5.67 |  | 4.66 | [8 empty] | 17.83 |  |  |  |  | 0.32
1996 |  |  |  | 2591.65 |  |  | 5707 |  |  |  | 516 | [10 empty] | 57.18 |  |  |  | 57.18 | [5 empty] | 57.18 |  |  | 64.97 |  |  |  | 31.11 |  | 25.82 | [8 empty] | 17.00 |  |  |  |  | 0.00
1997 |  |  |  | 3386.16 |  |  | 6841 |  |  |  | 516 | [10 empty] | 74.91 |  |  |  | 74.91 | [5 empty] | 74.91 |  |  | 78.09 |  |  |  | 16.79 |  | 15.11 | [8 empty] | 9.98 |  |  |  |  | 0.00
1998 |  |  |  | 3130.15 |  |  | 6384 |  |  |  | 516 | [10 empty] | 69.25 |  |  |  | 69.73 | [5 empty] | 69.25 |  |  | 72.88 |  |  |  | 14.14 |  | 11.48 | [8 empty] | 18.78 |  |  |  |  | 0.49
1999 |  |  |  | 3353.71 |  |  | 6863 |  |  |  | 516 | [10 empty] | 74.18 |  |  |  | 74.42 | [5 empty] | 74.19 |  |  | 78.34 |  |  |  | 25.38 |  | 25.31 | [8 empty] | 0.27 |  |  |  |  | 0.24
2000 |  |  |  | 2738.74 |  |  | 6449 |  |  |  | 516 | [10 empty] | 60.46 |  |  |  | 60.60 | [5 empty] | 60.42 |  |  | 73.42 |  |  |  | 19.46 |  | 14.64 | [8 empty] | 24.76 |  |  |  |  | 0.14
2001 |  |  |  | 2618.08 |  |  | 5286 |  |  |  | 516 | [10 empty] | 57.68 |  |  |  | 57.68 | [5 empty] | 57.92 |  |  | 60.34 |  |  |  | 21.61 |  | 15.90 | [8 empty] | 26.42 |  |  |  |  | 0.00
2002 |  |  |  | 3982.31 |  |  | 7985 |  |  |  | 516 | [10 empty] | 88.29 |  |  |  | 88.90 | [5 empty] | 88.10 |  |  | 91.15 |  |  |  | 7.01 |  | 6.71 | [8 empty] | 4.39 |  |  |  |  | 0.61
2003 |  |  |  | 3267.37 |  |  | 6566 |  |  |  | 516 | [10 empty] | 72.46 |  |  |  | 74.27 | [5 empty] | 72.28 |  |  | 74.95 |  |  |  | 12.71 |  | 10.81 | [8 empty] | 14.92 |  |  |  |  | 1.81
2004 |  |  |  | 2780.80 |  |  | 5597 |  |  |  | 516 | [10 empty] | 61.51 |  |  |  | 61.68 | [5 empty] | 61.35 |  |  | 63.72 |  |  |  | 28.61 |  | 24.72 | [8 empty] | 13.60 |  |  |  |  | 0.17
2005 |  |  |  | 2850.13 |  |  | 5596 |  |  |  | 516 | [10 empty] | 63.14 |  |  |  | 64.25 | [5 empty] | 63.05 |  |  | 63.88 |  |  |  | 3.16 |  | 4.41 | [8 empty] | 31.34 |  |  |  |  | 1.12
2006 |  |  |  | 3899.46 |  |  | 7635 |  |  |  | 516 | [10 empty] | 86.05 |  |  |  | 86.14 | [5 empty] | 86.27 |  |  | 87.16 |  |  |  | 4.26 |  | 13.54 | [8 empty] | 0.32 |  |  |  |  | 0.10
2007 |  |  |  | 3216.52 |  |  | 6588 |  |  |  | 516 | [10 empty] | 70.75 |  |  |  | 71.26 | [5 empty] | 71.16 |  |  | 75.21 |  |  |  | 8.36 |  | 10.77 | [8 empty] | 17.97 |  |  |  |  | 0.51
2008 |  |  |  | 4323.78 |  |  | 8521 |  |  |  | 516 | [10 empty] | 95.64 |  |  |  | 95.79 | [5 empty] | 95.39 |  |  | 97.01 |  |  |  | 4.21 |  | 4.21 | [8 empty] | 0.00 |  |  |  |  | 0.15
2009 |  |  |  | 3493.23 |  |  | 7051 |  |  |  | 516 | [10 empty] | 77.60 |  |  |  | 77.97 | [5 empty] | 77.28 |  |  | 80.49 |  |  |  | 3.36 |  | 2.71 | [8 empty] | 19.32 |  |  |  |  | 0.36
2010 |  |  |  | 3865.26 |  |  | 7659 |  |  |  | 516 | [10 empty] | 85.83 |  |  |  | 86.01 | [5 empty] | 85.51 |  |  | 87.43 |  |  |  | 3.22 |  | 2.86 | [8 empty] | 11.12 |  |  |  |  | 0.19
2011 |  |  |  | 3195.82 |  |  | 6334 |  |  |  | 516 | [10 empty] | 70.96 |  |  |  | 71.33 | [5 empty] | 70.70 |  |  | 72.31 |  |  |  | 0.60 |  | 0.43 | [8 empty] | 28.24 |  |  |  |  | 0.38
2012 |  |  |  | 4333.57 |  |  | 8550 |  |  |  | 516 | [10 empty] | 95.50 |  |  |  | 97.08 | [5 empty] | 95.61 |  |  | 97.34 |  |  |  | 2.92 |  | 2.92 | [8 empty] | 0.00 |  |  |  |  | 1.58
2013 |  |  |  | 3027.43 |  |  | 6047 |  |  |  | 516 | [10 empty] | 67.19 |  |  |  | 67.42 | [5 empty] | 66.98 |  |  | 69.03 |  |  |  | 0.14 |  | 0.10 | [8 empty] | 32.49 |  |  |  |  | 0.23
2014 |  |  |  | 3979.30 |  |  | 8397 |  |  |  | 516 | [10 empty] | 87.91 |  |  |  | 88.18 | [5 empty] | 88.03 |  |  | 95.86 |  |  |  | 11.82 |  | 11.82 | [8 empty] | 0.00 |  |  |  |  | 0.27
2015 |  |  |  | 3037.96 |  |  | 6064 |  |  |  | 516 | [10 empty] | 67.32 |  |  |  | 67.86 | [5 empty] | 67.21 |  |  | 69.22 |  |  |  | 5.43 |  | 3.89 | [8 empty] | 28.25 |  |  |  |  | 0.54
2016 |  |  |  | 3995.28 |  |  | 8259 |  |  |  | 516 | [10 empty] | 88.20 |  |  |  | 91.33 | [5 empty] | 88.15 |  |  | 94.02 |  |  |  | 2.89 |  | 7.15 | [8 empty] | 1.52 |  |  |  |  | 3.13
2017 |  |  |  | 4434.18 |  |  | 8686 |  |  |  | 516 | [10 empty] | 98.31 |  |  |  | 98.57 | [5 empty] | 98.10 |  |  | 99.16 |  |  |  | 1.43 |  | 1.43 | [8 empty] | 0.00 |  |  |  |  | 0.27
2018 |  |  |  | 2652.58 |  |  | 5392 |  |  |  | 516 | [10 empty] | 58.68 |  |  |  | 61.18 | [5 empty] | 58.68 |  |  | 61.55 |  |  |  | 6.08 |  | 3.96 | [8 empty] | 34.87 |  |  |  |  | 2.49
2019 |  |  |  | 4461.28 |  |  | 8681 |  |  |  | 516 | [10 empty] | 98.28 |  |  |  | 98.40 | [5 empty] | 98.70 |  |  | 99.10 |  |  |  | 1.59 |  | 1.59 | [8 empty] | 0.01 |  |  |  |  | 0.12
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1984 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 79 | [14 empty] | 533
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 83
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 951
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 3
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 18
L. |  | Human factor related | [39 empty] | 37
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 9
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 17
Z. |  | Other | [39 empty] | 2
Subtotal | [26 empty] | 79 | [10 empty] | 1034 |  |  |  | 575 | [11 empty] | 44
Total | [22 empty] | 79 | [14 empty] | 1653
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1984 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 58
12. |  |  | Reactor I&C Systems | [34 empty] | 48
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 30
14. |  |  | Safety Systems | [34 empty] | 39
15. |  |  | Reactor Cooling Systems | [34 empty] | 48
16. |  |  | Steam generation systems | [34 empty] | 101
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 13
31. |  |  | Turbine and auxiliaries | [19 empty] | 79 | [14 empty] | 54
32. |  |  | Feedwater and Main Steam System | [34 empty] | 35
33. |  |  | Circulating Water System | [34 empty] | 13
34. |  |  | Miscellaneous Systems | [34 empty] | 20
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 66
42. |  |  | Electrical Power Supply Systems | [34 empty] | 23
Total | [22 empty] | 79 | [14 empty] | 553

## PICKERING-7
2019 Operating Experience
CA-15 | [8 empty] | PICKERING-7 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-03-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-11-17
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-01-01
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2/PuO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 3132.65 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 68.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.71 %
Unit Capability Factor (UCF) | [18 empty] | : | 68.53 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 30.76 %
Load Factor (LF) | [18 empty] | : | 69.3 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.01 %
Operating Factor (OF) | [18 empty] | : | 69.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2629 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 379.96 | 43.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.23 |  |  | 377.49 | [6 empty] | 387.02 |  | 385.40 |  |  |  | 373.75 |  |  | 387.31 |  |  | 374.07 | [9 empty] | 392.81 |  |  | 3132.65
EAF [%] |  |  |  |  | 98.06 | 12.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.16 |  |  | 99.99 | [6 empty] | 99.97 |  | 99.97 |  |  |  | 99.99 |  |  | 99.70 |  |  | 99.26 | [9 empty] | 100.00 |  |  | 68.52
UCF [%] |  |  |  |  | 98.09 | 12.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.16 |  |  | 99.99 | [6 empty] | 100.00 |  | 99.97 |  |  |  | 99.99 |  |  | 99.74 |  |  | 99.26 | [9 empty] | 100.00 |  |  | 68.53
LF [%] |  |  |  |  | 98.97 | 12.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.13 |  |  | 101.61 | [6 empty] | 100.81 |  | 100.39 |  |  |  | 100.60 |  |  | 100.89 |  |  | 100.69 | [9 empty] | 102.32 |  |  | 69.30
OF [%] |  |  |  |  | 100.00 | 19.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.73 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 69.99
FLR [%] |  |  |  |  | 1.91 | 35.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.03 |  |  |  | 0.00 |  |  | 0.26 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.03
UCL [%] |  |  |  |  | 1.91 | 6.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.03 |  |  |  | 0.00 |  |  | 0.26 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.71
PUF [%] |  |  |  |  | 0.00 | 80.58 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 91.84 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.74 | [9 empty] | 0.00 |  |  | 30.76
XUF [%] |  |  |  |  | 0.03 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.00 |  |  |  | 0.00 |  |  | 0.04 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 123312 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.91 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 10.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.54 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.13 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.66 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.62 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.75 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4093.95 |  |  | 8277 |  |  |  | 516 | [10 empty] | 92.65 |  |  |  | 99.03 | [5 empty] | 90.57 |  |  | 94.49 |  |  |  | 0.86 |  | 0.86 | [8 empty] | 0.11 |  |  |  |  | 6.39
1986 |  |  |  | 3373.30 |  |  | 7002 |  |  |  | 516 | [10 empty] | 75.20 |  |  |  | 75.45 | [5 empty] | 74.63 |  |  | 79.93 |  |  |  | 8.27 |  | 6.80 | [8 empty] | 17.75 |  |  |  |  | 0.25
1987 |  |  |  | 4339.89 |  |  | 8642 |  |  |  | 516 | [10 empty] | 95.99 |  |  |  | 97.44 | [5 empty] | 96.01 |  |  | 98.65 |  |  |  | 2.50 |  | 2.50 | [8 empty] | 0.05 |  |  |  |  | 1.45
1988 |  |  |  | 4340.42 |  |  | 8519 |  |  |  | 516 | [10 empty] | 95.39 |  |  |  | 95.94 | [5 empty] | 95.76 |  |  | 96.98 |  |  |  | 4.06 |  | 4.06 | [8 empty] | 0.00 |  |  |  |  | 0.55
1989 |  |  |  | 3408.69 |  |  | 6939 |  |  |  | 516 | [10 empty] | 75.37 |  |  |  | 77.13 | [5 empty] | 75.41 |  |  | 79.21 |  |  |  | 10.45 |  | 9.00 | [8 empty] | 13.87 |  |  |  |  | 1.76
1990 |  |  |  | 3500.80 |  |  | 7420 |  |  |  | 516 | [10 empty] | 77.73 |  |  |  | 78.35 | [5 empty] | 77.45 |  |  | 84.70 |  |  |  | 13.66 |  | 12.39 | [8 empty] | 9.25 |  |  |  |  | 0.62
1991 |  |  |  | 4258.77 |  |  | 8436 |  |  |  | 516 | [10 empty] | 94.52 |  |  |  | 94.93 | [5 empty] | 94.22 |  |  | 96.30 |  |  |  | 4.76 |  | 4.74 | [8 empty] | 0.33 |  |  |  |  | 0.42
1992 |  |  |  | 3727.45 |  |  | 7349 |  |  |  | 516 | [10 empty] | 82.40 |  |  |  | 82.41 | [5 empty] | 82.24 |  |  | 83.66 |  |  |  | 2.52 |  | 2.13 | [8 empty] | 15.46 |  |  |  |  | 0.01
1993 |  |  |  | 4415.95 |  |  | 8760 |  |  |  | 516 | [10 empty] | 99.01 |  |  |  | 99.88 | [5 empty] | 97.69 |  |  | 100.00 |  |  |  | 0.12 |  | 0.12 | [8 empty] | 0.00 |  |  |  |  | 0.87
1994 |  |  |  | 3709.91 |  |  | 7386 |  |  |  | 516 | [10 empty] | 83.40 |  |  |  | 83.40 | [5 empty] | 82.07 |  |  | 84.32 |  |  |  | 1.67 |  | 1.41 | [8 empty] | 15.18 |  |  |  |  | 0.00
1995 |  |  |  | 4056.79 |  |  | 8140 |  |  |  | 516 | [10 empty] | 90.05 |  |  |  | 90.43 | [5 empty] | 89.75 |  |  | 92.92 |  |  |  | 9.57 |  | 9.57 | [8 empty] | 0.00 |  |  |  |  | 0.38
1996 |  |  |  | 2050.69 |  |  | 4416 |  |  |  | 516 | [10 empty] | 45.37 |  |  |  | 45.37 | [5 empty] | 45.24 |  |  | 50.27 |  |  |  | 54.63 |  | 54.63 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 2936.16 |  |  | 6208 |  |  |  | 516 | [10 empty] | 64.96 |  |  |  | 64.96 | [5 empty] | 64.96 |  |  | 70.87 |  |  |  | 20.17 |  | 16.41 | [8 empty] | 18.63 |  |  |  |  | 0.00
1998 |  |  |  | 3084.73 |  |  | 6495 |  |  |  | 516 | [10 empty] | 68.24 |  |  |  | 68.87 | [5 empty] | 68.24 |  |  | 74.14 |  |  |  | 20.36 |  | 17.61 | [8 empty] | 13.52 |  |  |  |  | 0.63
1999 |  |  |  | 4433.82 |  |  | 8751 |  |  |  | 516 | [10 empty] | 98.04 |  |  |  | 98.82 | [5 empty] | 98.09 |  |  | 99.90 |  |  |  | 1.18 |  | 1.18 | [8 empty] | 0.00 |  |  |  |  | 0.78
2000 |  |  |  | 2099.00 |  |  | 4445 |  |  |  | 516 | [10 empty] | 46.29 |  |  |  | 46.37 | [5 empty] | 46.31 |  |  | 50.60 |  |  |  | 14.46 |  | 7.84 | [8 empty] | 45.79 |  |  |  |  | 0.08
2001 |  |  |  | 4020.78 |  |  | 7968 |  |  |  | 516 | [10 empty] | 88.71 |  |  |  | 89.03 | [5 empty] | 88.95 |  |  | 90.96 |  |  |  | 10.97 |  | 10.97 | [8 empty] | 0.00 |  |  |  |  | 0.32
2002 |  |  |  | 4246.89 |  |  | 8538 |  |  |  | 516 | [10 empty] | 93.85 |  |  |  | 94.45 | [5 empty] | 93.95 |  |  | 97.47 |  |  |  | 5.55 |  | 5.55 | [8 empty] | 0.00 |  |  |  |  | 0.59
2003 |  |  |  | 1790.66 |  |  | 3811 |  |  |  | 516 | [10 empty] | 39.66 |  |  |  | 39.81 | [5 empty] | 39.62 |  |  | 43.50 |  |  |  | 40.88 |  | 27.53 | [8 empty] | 32.67 |  |  |  |  | 0.15
2004 |  |  |  | 3116.06 |  |  | 6127 |  |  |  | 516 | [10 empty] | 68.86 |  |  |  | 68.93 | [5 empty] | 68.75 |  |  | 69.75 |  |  |  | 4.64 |  | 3.36 | [8 empty] | 27.72 |  |  |  |  | 0.07
2005 |  |  |  | 4390.76 |  |  | 8658 |  |  |  | 516 | [10 empty] | 97.44 |  |  |  | 97.79 | [5 empty] | 97.14 |  |  | 98.84 |  |  |  | 2.21 |  | 2.21 | [8 empty] | 0.00 |  |  |  |  | 0.34
2006 |  |  |  | 2652.57 |  |  | 5311 |  |  |  | 516 | [10 empty] | 59.06 |  |  |  | 59.11 | [5 empty] | 58.68 |  |  | 60.63 |  |  |  | 10.24 |  | 21.12 | [8 empty] | 19.77 |  |  |  |  | 0.05
2007 |  |  |  | 3667.91 |  |  | 7540 |  |  |  | 516 | [10 empty] | 81.69 |  |  |  | 82.04 | [5 empty] | 81.15 |  |  | 86.07 |  |  |  | 9.97 |  | 16.75 | [8 empty] | 1.21 |  |  |  |  | 0.35
2008 |  |  |  | 1530.27 |  |  | 3084 |  |  |  | 516 | [10 empty] | 33.98 |  |  |  | 33.99 | [5 empty] | 33.76 |  |  | 35.11 |  |  |  | 66.01 |  | 66.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 4229.46 |  |  | 8492 |  |  |  | 516 | [10 empty] | 94.10 |  |  |  | 94.53 | [5 empty] | 93.57 |  |  | 96.94 |  |  |  | 5.47 |  | 5.47 | [8 empty] | 0.00 |  |  |  |  | 0.43
2010 |  |  |  | 2920.66 |  |  | 5895 |  |  |  | 516 | [10 empty] | 64.78 |  |  |  | 65.13 | [5 empty] | 64.61 |  |  | 67.29 |  |  |  | 1.64 |  | 1.69 | [8 empty] | 33.18 |  |  |  |  | 0.35
2011 |  |  |  | 4337.70 |  |  | 8673 |  |  |  | 516 | [10 empty] | 96.58 |  |  |  | 96.83 | [5 empty] | 95.96 |  |  | 99.01 |  |  |  | 3.17 |  | 3.17 | [8 empty] | 0.00 |  |  |  |  | 0.25
2012 |  |  |  | 2920.02 |  |  | 5965 |  |  |  | 516 | [10 empty] | 64.76 |  |  |  | 66.28 | [5 empty] | 64.42 |  |  | 67.91 |  |  |  | 6.84 |  | 4.87 | [8 empty] | 28.85 |  |  |  |  | 1.52
2013 |  |  |  | 4264.55 |  |  | 8760 |  |  |  | 516 | [10 empty] | 94.44 |  |  |  | 94.92 | [5 empty] | 94.35 |  |  | 100.00 |  |  |  | 5.04 |  | 5.04 | [8 empty] | 0.04 |  |  |  |  | 0.48
2014 |  |  |  | 2783.08 |  |  | 5489 |  |  |  | 516 | [10 empty] | 61.95 |  |  |  | 62.18 | [5 empty] | 61.57 |  |  | 62.66 |  |  |  | 6.72 |  | 6.53 | [8 empty] | 31.30 |  |  |  |  | 0.23
2015 |  |  |  | 4171.04 |  |  | 8336 |  |  |  | 516 | [10 empty] | 92.57 |  |  |  | 93.11 | [5 empty] | 92.28 |  |  | 95.16 |  |  |  | 3.43 |  | 5.65 | [8 empty] | 1.25 |  |  |  |  | 0.54
2016 |  |  |  | 2803.59 |  |  | 5574 |  |  |  | 516 | [10 empty] | 61.97 |  |  |  | 62.32 | [5 empty] | 61.85 |  |  | 63.46 |  |  |  | 6.62 |  | 5.50 | [8 empty] | 32.18 |  |  |  |  | 0.35
2017 |  |  |  | 3751.37 |  |  | 7512 |  |  |  | 516 | [10 empty] | 83.14 |  |  |  | 83.35 | [5 empty] | 82.99 |  |  | 85.75 |  |  |  | 13.44 |  | 16.11 | [8 empty] | 0.55 |  |  |  |  | 0.20
2018 |  |  |  | 4377.16 |  |  | 8687 |  |  |  | 516 | [10 empty] | 96.67 |  |  |  | 98.11 | [5 empty] | 96.84 |  |  | 99.17 |  |  |  | 1.89 |  | 1.89 | [8 empty] | 0.00 |  |  |  |  | 1.45
2019 |  |  |  | 3132.65 |  |  | 6131 |  |  |  | 516 | [10 empty] | 68.52 |  |  |  | 68.53 | [5 empty] | 69.30 |  |  | 69.99 |  |  |  | 1.03 |  | 0.71 | [8 empty] | 30.76 |  |  |  |  | 0.01
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1985 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 570
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2629 | [14 empty] | 938
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 9
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 121
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 13
Z. |  | Other | [39 empty] | 34
Subtotal | [22 empty] | 2629 | [14 empty] | 939 |  |  |  | 734 | [11 empty] | 20
Total | [22 empty] | 2629 | [14 empty] | 1693
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1985 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 100
12. |  |  | Reactor I&C Systems | [34 empty] | 58
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 15
14. |  |  | Safety Systems | [34 empty] | 33
15. |  |  | Reactor Cooling Systems | [34 empty] | 89
16. |  |  | Steam generation systems | [34 empty] | 58
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 23
31. |  |  | Turbine and auxiliaries | [34 empty] | 35
32. |  |  | Feedwater and Main Steam System | [34 empty] | 19
33. |  |  | Circulating Water System | [34 empty] | 14
34. |  |  | Miscellaneous Systems | [34 empty] | 46
41. |  |  | Main Generator Systems | [34 empty] | 69
42. |  |  | Electrical Power Supply Systems | [34 empty] | 50
Total | [37 empty] | 609

## PICKERING-8
2019 Operating Experience
CA-16 | [8 empty] | PICKERING-8 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-09-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-01-21
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-02-28
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 4363.55 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.44 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.71 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.28 %
Load Factor (LF) | [18 empty] | : | 96.54 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.27 %
Operating Factor (OF) | [18 empty] | : | 97.84 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 189 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 344.38 | 344.62 |  |  |  | 278.22 |  | 374.24 | [8 empty] | 383.83 |  |  | 373.20 | [6 empty] | 383.65 |  | 378.03 |  |  |  | 367.22 |  |  | 381.26 |  |  | 367.95 | [9 empty] | 386.94 |  |  | 4363.55
EAF [%] |  |  |  |  | 89.61 | 99.86 |  |  |  | 73.03 |  | 99.99 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.80 |  | 98.81 |  |  |  | 99.13 |  |  | 99.29 |  |  | 98.53 | [9 empty] | 100.00 |  |  | 96.44
UCF [%] |  |  |  |  | 89.76 | 99.96 |  |  |  | 73.03 |  | 99.99 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.98 |  |  | 99.97 |  |  | 98.53 | [9 empty] | 100.00 |  |  | 96.71
LF [%] |  |  |  |  | 89.71 | 99.39 |  |  |  | 72.47 |  | 100.73 | [8 empty] | 99.98 |  |  | 100.45 | [6 empty] | 99.94 |  | 98.47 |  |  |  | 98.84 |  |  | 99.31 |  |  | 99.04 | [9 empty] | 100.79 |  |  | 96.54
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 74.60 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.84
FLR [%] |  |  |  |  | 10.24 | 0.04 |  |  |  | 0.15 |  | 0.01 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.02 |  |  | 0.03 |  |  | 1.47 | [9 empty] | 0.00 |  |  | 1.03
UCL [%] |  |  |  |  | 10.24 | 0.04 |  |  |  | 0.11 |  | 0.01 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.02 |  |  | 0.03 |  |  | 1.47 | [9 empty] | 0.00 |  |  | 1.01
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 26.86 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.28
XUF [%] |  |  |  |  | 0.15 | 0.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.20 |  | 1.19 |  |  |  | 0.85 |  |  | 0.68 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.27
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 115867 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.28 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.74 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.69 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.36 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.95 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.59 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.63 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.01 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 3792.31 |  |  | 8086 |  |  |  | 516 | [10 empty] | 96.32 |  |  |  | 96.67 | [5 empty] | 95.69 |  |  | 97.69 |  |  |  | 3.33 |  | 3.33 | [8 empty] | 0.00 |  |  |  |  | 0.35
1987 |  |  |  | 3759.36 |  |  | 7585 |  |  |  | 516 | [10 empty] | 83.31 |  |  |  | 84.70 | [5 empty] | 83.17 |  |  | 86.59 |  |  |  | 2.09 |  | 1.81 | [8 empty] | 13.49 |  |  |  |  | 1.38
1988 |  |  |  | 3710.38 |  |  | 7296 |  |  |  | 516 | [10 empty] | 82.25 |  |  |  | 82.50 | [5 empty] | 81.86 |  |  | 83.06 |  |  |  | 2.16 |  | 1.82 | [8 empty] | 15.68 |  |  |  |  | 0.25
1989 |  |  |  | 4295.19 |  |  | 8569 |  |  |  | 516 | [10 empty] | 95.37 |  |  |  | 96.61 | [5 empty] | 95.02 |  |  | 97.82 |  |  |  | 3.29 |  | 3.29 | [8 empty] | 0.10 |  |  |  |  | 1.24
1990 |  |  |  | 3014.65 |  |  | 6743 |  |  |  | 516 | [10 empty] | 66.63 |  |  |  | 66.72 | [5 empty] | 66.69 |  |  | 76.97 |  |  |  | 19.23 |  | 15.89 | [8 empty] | 17.39 |  |  |  |  | 0.09
1991 |  |  |  | 4484.97 |  |  | 8759 |  |  |  | 516 | [10 empty] | 98.89 |  |  |  | 99.52 | [5 empty] | 99.22 |  |  | 99.99 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.00 |  |  |  |  | 0.63
1992 |  |  |  | 4211.99 |  |  | 8280 |  |  |  | 516 | [10 empty] | 92.95 |  |  |  | 92.98 | [5 empty] | 92.93 |  |  | 94.26 |  |  |  | 6.81 |  | 6.79 | [8 empty] | 0.22 |  |  |  |  | 0.03
1993 |  |  |  | 3670.54 |  |  | 7233 |  |  |  | 516 | [10 empty] | 81.73 |  |  |  | 82.15 | [5 empty] | 81.20 |  |  | 82.57 |  |  |  | 2.50 |  | 2.11 | [8 empty] | 15.74 |  |  |  |  | 0.41
1994 |  |  |  | 4341.88 |  |  | 8579 |  |  |  | 516 | [10 empty] | 96.85 |  |  |  | 96.85 | [5 empty] | 96.06 |  |  | 97.93 |  |  |  | 3.14 |  | 3.14 | [8 empty] | 0.01 |  |  |  |  | 0.00
1995 |  |  |  | 4012.08 |  |  | 8066 |  |  |  | 516 | [10 empty] | 89.04 |  |  |  | 89.42 | [5 empty] | 88.76 |  |  | 92.08 |  |  |  | 10.58 |  | 10.58 | [8 empty] | 0.00 |  |  |  |  | 0.38
1996 |  |  |  | 1300.26 |  |  | 2597 |  |  |  | 516 | [10 empty] | 28.73 |  |  |  | 28.73 | [5 empty] | 28.69 |  |  | 29.57 |  |  |  | 68.79 |  | 63.34 | [8 empty] | 7.92 |  |  |  |  | 0.00
1997 |  |  |  | 360.81 |  |  | 995 |  |  |  | 516 | [10 empty] | 7.96 |  |  |  | 7.96 | [5 empty] | 7.96 |  |  | 11.33 |  |  |  | 44.06 |  | 6.27 | [8 empty] | 85.77 |  |  |  |  | 0.00
1998 |  |  |  | 3493.62 |  |  | 7009 |  |  |  | 516 | [10 empty] | 77.29 |  |  |  | 78.02 | [5 empty] | 77.29 |  |  | 80.01 |  |  |  | 10.55 |  | 9.20 | [8 empty] | 12.78 |  |  |  |  | 0.73
1999 |  |  |  | 3509.06 |  |  | 7077 |  |  |  | 516 | [10 empty] | 77.63 |  |  |  | 78.44 | [5 empty] | 77.63 |  |  | 80.79 |  |  |  | 2.49 |  | 2.00 | [8 empty] | 19.56 |  |  |  |  | 0.81
2000 |  |  |  | 2711.21 |  |  | 5508 |  |  |  | 516 | [10 empty] | 59.92 |  |  |  | 60.83 | [5 empty] | 59.82 |  |  | 62.70 |  |  |  | 16.52 |  | 12.04 | [8 empty] | 27.13 |  |  |  |  | 0.91
2001 |  |  |  | 3502.19 |  |  | 6999 |  |  |  | 516 | [10 empty] | 77.47 |  |  |  | 78.22 | [5 empty] | 77.48 |  |  | 79.90 |  |  |  | 8.46 |  | 7.23 | [8 empty] | 14.55 |  |  |  |  | 0.75
2002 |  |  |  | 3605.36 |  |  | 7244 |  |  |  | 516 | [10 empty] | 80.03 |  |  |  | 81.06 | [5 empty] | 79.76 |  |  | 82.69 |  |  |  | 9.27 |  | 8.28 | [8 empty] | 10.66 |  |  |  |  | 1.02
2003 |  |  |  | 3921.29 |  |  | 8026 |  |  |  | 516 | [10 empty] | 86.90 |  |  |  | 89.68 | [5 empty] | 86.75 |  |  | 91.62 |  |  |  | 10.32 |  | 10.32 | [8 empty] | 0.00 |  |  |  |  | 2.78
2004 |  |  |  | 2489.46 |  |  | 5182 |  |  |  | 516 | [10 empty] | 55.13 |  |  |  | 55.35 | [5 empty] | 54.92 |  |  | 58.99 |  |  |  | 23.42 |  | 16.93 | [8 empty] | 27.71 |  |  |  |  | 0.23
2005 |  |  |  | 4195.24 |  |  | 8431 |  |  |  | 516 | [10 empty] | 93.40 |  |  |  | 94.60 | [5 empty] | 92.81 |  |  | 96.24 |  |  |  | 5.40 |  | 5.40 | [8 empty] | 0.00 |  |  |  |  | 1.20
2006 |  |  |  | 2908.54 |  |  | 5853 |  |  |  | 516 | [10 empty] | 64.75 |  |  |  | 65.06 | [5 empty] | 64.35 |  |  | 66.82 |  |  |  | 3.38 |  | 11.22 | [8 empty] | 23.72 |  |  |  |  | 0.31
2007 |  |  |  | 3843.21 |  |  | 8015 |  |  |  | 516 | [10 empty] | 85.51 |  |  |  | 87.28 | [5 empty] | 85.02 |  |  | 91.50 |  |  |  | 12.72 |  | 12.72 | [8 empty] | 0.00 |  |  |  |  | 1.77
2008 |  |  |  | 2918.75 |  |  | 6116 |  |  |  | 516 | [10 empty] | 64.41 |  |  |  | 64.71 | [5 empty] | 64.40 |  |  | 69.63 |  |  |  | 18.42 |  | 18.21 | [8 empty] | 17.08 |  |  |  |  | 0.30
2009 |  |  |  | 4115.23 |  |  | 8520 |  |  |  | 516 | [10 empty] | 91.04 |  |  |  | 91.61 | [5 empty] | 91.04 |  |  | 97.26 |  |  |  | 8.39 |  | 8.39 | [8 empty] | 0.00 |  |  |  |  | 0.57
2010 |  |  |  | 3081.07 |  |  | 6427 |  |  |  | 516 | [10 empty] | 68.16 |  |  |  | 68.53 | [5 empty] | 68.16 |  |  | 73.37 |  |  |  | 9.60 |  | 9.19 | [8 empty] | 22.27 |  |  |  |  | 0.37
2011 |  |  |  | 4051.72 |  |  | 8345 |  |  |  | 516 | [10 empty] | 89.64 |  |  |  | 90.30 | [5 empty] | 89.64 |  |  | 95.26 |  |  |  | 9.61 |  | 9.60 | [8 empty] | 0.10 |  |  |  |  | 0.66
2012 |  |  |  | 2936.38 |  |  | 5967 |  |  |  | 516 | [10 empty] | 64.86 |  |  |  | 65.53 | [5 empty] | 64.78 |  |  | 67.93 |  |  |  | 6.71 |  | 7.15 | [8 empty] | 27.33 |  |  |  |  | 0.66
2013 |  |  |  | 3879.06 |  |  | 7979 |  |  |  | 516 | [10 empty] | 85.97 |  |  |  | 86.34 | [5 empty] | 85.82 |  |  | 91.08 |  |  |  | 13.57 |  | 13.55 | [8 empty] | 0.11 |  |  |  |  | 0.37
2014 |  |  |  | 2411.29 |  |  | 5223 |  |  |  | 516 | [10 empty] | 53.30 |  |  |  | 53.43 | [5 empty] | 53.35 |  |  | 59.62 |  |  |  | 26.12 |  | 22.62 | [8 empty] | 23.94 |  |  |  |  | 0.14
2015 |  |  |  | 4289.30 |  |  | 8440 |  |  |  | 516 | [10 empty] | 94.91 |  |  |  | 95.37 | [5 empty] | 94.89 |  |  | 96.35 |  |  |  | 0.76 |  | 0.73 | [8 empty] | 3.90 |  |  |  |  | 0.46
2016 |  |  |  | 2197.88 |  |  | 4367 |  |  |  | 516 | [10 empty] | 48.35 |  |  |  | 48.60 | [5 empty] | 48.49 |  |  | 49.72 |  |  |  | 0.61 |  | 11.62 | [8 empty] | 39.78 |  |  |  |  | 0.25
2017 |  |  |  | 3870.80 |  |  | 7787 |  |  |  | 516 | [10 empty] | 85.68 |  |  |  | 85.96 | [5 empty] | 85.63 |  |  | 88.89 |  |  |  | 2.90 |  | 2.57 | [8 empty] | 11.47 |  |  |  |  | 0.28
2018 |  |  |  | 2626.93 |  |  | 5427 |  |  |  | 516 | [10 empty] | 58.08 |  |  |  | 59.70 | [5 empty] | 58.12 |  |  | 61.95 |  |  |  | 13.69 |  | 9.47 | [8 empty] | 30.82 |  |  |  |  | 1.63
2019 |  |  |  | 4363.55 |  |  | 8571 |  |  |  | 516 | [10 empty] | 96.44 |  |  |  | 96.71 | [5 empty] | 96.54 |  |  | 97.84 |  |  |  | 1.03 |  | 1.01 | [8 empty] | 2.28 |  |  |  |  | 0.27
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1986 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 478
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 78
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 189 | [14 empty] | 956
E. |  | Testing of plant systems or components | [35 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 312
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 10
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 189 | [14 empty] | 1035 |  |  |  | 791 | [11 empty] | 14
Total | [22 empty] | 189 | [14 empty] | 1840
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1986 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 35
12. |  |  | Reactor I&C Systems | [34 empty] | 35
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 38
15. |  |  | Reactor Cooling Systems | [34 empty] | 88
16. |  |  | Steam generation systems | [34 empty] | 31
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 99
31. |  |  | Turbine and auxiliaries | [34 empty] | 49
32. |  |  | Feedwater and Main Steam System | [34 empty] | 28
33. |  |  | Circulating Water System | [34 empty] | 24
34. |  |  | Miscellaneous Systems | [34 empty] | 14
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 10
42. |  |  | Electrical Power Supply Systems | [34 empty] | 31
Total | [37 empty] | 486

## POINT LEPREAU
2019 Operating Experience
CA-17 | [8 empty] | POINT LEPREAU | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NBEPC (NEW BRUNSWICK ELECTRIC POWER COMMISSION)
Owner | [7 empty] | : | NBEPC (NEW BRUNSWICK ELECTRIC POWER COMMISSION)
Reactor Supplier | [7 empty] | : | AECL (ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI/PARS (NEI-PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-05-01
Thermal power | [12 empty] | : |  |  | 2180 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-09-11
Gross electrical power | [12 empty] | : |  |  | 705 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-02-01
Reference unit power (net) | [12 empty] | : |  |  | 660 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 11.55
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.3
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 6.28 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.64
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 59.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 5015.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.5 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.69 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.08 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.69 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.23 %
Load Factor (LF) | [18 empty] | : | 86.75 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 87.48 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1097 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 490.89 | 440.18 |  |  |  | 488.97 |  | 72.78 | [8 empty] | 260.17 |  |  | 477.44 | [6 empty] | 362.28 |  | 489.55 |  |  |  | 473.10 |  |  | 490.13 |  |  | 476.63 | [9 empty] | 493.55 |  |  | 5015.68
EAF [%] |  |  |  |  | 99.66 | 99.06 |  |  |  | 99.02 |  | 16.07 | [8 empty] | 52.98 |  |  | 99.99 | [6 empty] | 74.40 |  | 99.70 |  |  |  | 99.66 |  |  | 99.89 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.69
UCF [%] |  |  |  |  | 99.66 | 99.06 |  |  |  | 99.02 |  | 16.07 | [8 empty] | 52.98 |  |  | 99.99 | [6 empty] | 74.40 |  | 99.70 |  |  |  | 99.66 |  |  | 99.89 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.69
LF [%] |  |  |  |  | 99.97 | 99.25 |  |  |  | 99.58 |  | 15.32 | [8 empty] | 52.98 |  |  | 100.47 | [6 empty] | 73.78 |  | 99.70 |  |  |  | 99.56 |  |  | 99.81 |  |  | 100.30 | [9 empty] | 100.51 |  |  | 86.75
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 16.39 | [8 empty] | 57.53 |  |  | 100.00 | [6 empty] | 75.94 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.48
FLR [%] |  |  |  |  | 0.34 | 0.64 |  |  |  | 0.98 |  | 0.00 | [8 empty] | 28.20 |  |  | 0.00 | [6 empty] | 25.42 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.50
UCL [%] |  |  |  |  | 0.34 | 0.64 |  |  |  | 0.98 |  | 0.00 | [8 empty] | 20.81 |  |  | 0.00 | [6 empty] | 25.36 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.08
PUF [%] |  |  |  |  | 0.00 | 0.30 |  |  |  | 0.00 |  | 83.93 | [8 empty] | 26.21 |  |  | 0.01 | [6 empty] | 0.24 |  | 0.30 |  |  |  | 0.34 |  |  | 0.11 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.23
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 148073.85 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.01 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.49 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 72.79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.72 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.36 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.78 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.17 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 4742.90 |  |  | 7875 |  |  |  | 640 | [10 empty] | 86.03 |  |  |  | 86.03 | [5 empty] | 85.85 |  |  | 89.37 |  |  |  | 8.10 |  | 7.58 | [8 empty] | 6.39 |  |  |  |  | 0.00
1984 |  |  |  | 5000.94 |  |  | 7927 |  |  |  | 635 | [10 empty] | 88.94 |  |  |  | 88.97 | [5 empty] | 89.66 |  |  | 90.24 |  |  |  | 3.03 |  | 2.78 | [8 empty] | 8.25 |  |  |  |  | 0.03
1985 |  |  |  | 5421.91 |  |  | 8547 |  |  |  | 635 | [10 empty] | 96.87 |  |  |  | 96.93 | [5 empty] | 97.47 |  |  | 97.57 |  |  |  | 1.25 |  | 1.23 | [8 empty] | 1.84 |  |  |  |  | 0.06
1986 |  |  |  | 5223.09 |  |  | 8257 |  |  |  | 635 | [10 empty] | 93.41 |  |  |  | 94.00 | [5 empty] | 93.90 |  |  | 94.26 |  |  |  | 0.90 |  | 0.85 | [8 empty] | 5.15 |  |  |  |  | 0.59
1987 |  |  |  | 5107.73 |  |  | 8110 |  |  |  | 635 | [10 empty] | 91.23 |  |  |  | 91.25 | [5 empty] | 91.82 |  |  | 92.58 |  |  |  | 3.32 |  | 3.14 | [8 empty] | 5.61 |  |  |  |  | 0.02
1988 |  |  |  | 5338.25 |  |  | 8383 |  |  |  | 635 | [10 empty] | 94.85 |  |  |  | 94.85 | [5 empty] | 95.70 |  |  | 95.43 |  |  |  | 0.38 |  | 0.36 | [8 empty] | 4.79 |  |  |  |  | 0.00
1989 |  |  |  | 5266.67 |  |  | 8271 |  |  |  | 635 | [10 empty] | 93.60 |  |  |  | 93.81 | [5 empty] | 94.68 |  |  | 94.42 |  |  |  | 0.89 |  | 0.84 | [8 empty] | 5.34 |  |  |  |  | 0.22
1990 |  |  |  | 5333.71 |  |  | 8384 |  |  |  | 635 | [10 empty] | 94.70 |  |  |  | 94.99 | [5 empty] | 95.89 |  |  | 95.71 |  |  |  | 2.92 |  | 2.86 | [8 empty] | 2.15 |  |  |  |  | 0.29
1991 |  |  |  | 5437.17 |  |  | 8500 |  |  |  | 635 | [10 empty] | 96.68 |  |  |  | 96.72 | [5 empty] | 97.75 |  |  | 97.03 |  |  |  | 0.55 |  | 0.54 | [8 empty] | 2.74 |  |  |  |  | 0.04
1992 |  |  |  | 4829.78 |  |  | 7748 |  |  |  | 635 | [10 empty] | 85.76 |  |  |  | 85.76 | [5 empty] | 86.59 |  |  | 88.21 |  |  |  | 3.99 |  | 3.57 | [8 empty] | 10.67 |  |  |  |  | 0.00
1993 |  |  |  | 5320.00 |  |  | 8391 |  |  |  | 635 | [10 empty] | 95.09 |  |  |  | 95.09 | [5 empty] | 95.64 |  |  | 95.79 |  |  |  | 1.42 |  | 1.37 | [8 empty] | 3.54 |  |  |  |  | 0.00
1994 |  |  |  | 5230.10 |  |  | 8270 |  |  |  | 635 | [10 empty] | 93.46 |  |  |  | 93.46 | [5 empty] | 94.02 |  |  | 94.41 |  |  |  | 0.34 |  | 0.32 | [8 empty] | 6.22 |  |  |  |  | 0.00
1995 |  |  |  | 1611.40 |  |  | 2615 |  |  |  | 635 | [10 empty] | 28.98 |  |  |  | 28.98 | [5 empty] | 28.97 |  |  | 29.85 |  |  |  | 43.54 |  | 22.34 | [8 empty] | 48.68 |  |  |  |  | 0.00
1996 |  |  |  | 4587.83 |  |  | 7363 |  |  |  | 635 | [10 empty] | 81.41 |  |  |  | 81.41 | [5 empty] | 82.25 |  |  | 83.82 |  |  |  | 13.97 |  | 13.22 | [8 empty] | 5.37 |  |  |  |  | 0.00
1997 |  |  |  | 3455.59 |  |  | 5564 |  |  |  | 635 | [10 empty] | 61.60 |  |  |  | 62.19 | [5 empty] | 62.12 |  |  | 63.52 |  |  |  | 24.86 |  | 20.57 | [8 empty] | 17.24 |  |  |  |  | 0.59
1998 |  |  |  | 3782.35 |  |  | 6111 |  |  |  | 635 | [10 empty] | 66.04 |  |  |  | 67.11 | [5 empty] | 68.00 |  |  | 69.76 |  |  |  | 20.20 |  | 16.99 | [8 empty] | 15.90 |  |  |  |  | 1.06
1999 |  |  |  | 4082.74 |  |  | 6797 |  |  |  | 635 | [10 empty] | 71.99 |  |  |  | 75.52 | [5 empty] | 73.40 |  |  | 77.59 |  |  |  | 11.47 |  | 9.78 | [8 empty] | 14.70 |  |  |  |  | 3.53
2000 |  |  |  | 3966.85 |  |  | 6792 |  |  |  | 635 | [10 empty] | 70.52 |  |  |  | 77.64 | [5 empty] | 71.12 |  |  | 77.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.36 |  |  |  |  | 7.12
2001 |  |  |  | 4451.33 |  |  | 7418 |  |  |  | 635 | [10 empty] | 79.08 |  |  |  | 84.61 | [5 empty] | 80.02 |  |  | 84.68 |  |  |  | 15.33 |  | 15.31 | [8 empty] | 0.08 |  |  |  |  | 5.53
2002 |  |  |  | 3760.64 |  |  | 6107 |  |  |  | 635 | [10 empty] | 67.59 |  |  |  | 71.59 | [5 empty] | 67.61 |  |  | 69.71 |  |  |  | 6.62 |  | 10.30 | [8 empty] | 18.12 |  |  |  |  | 4.00
2003 |  |  |  | 4739.52 |  |  | 7869 |  |  |  | 635 | [10 empty] | 84.39 |  |  |  | 89.77 | [5 empty] | 85.20 |  |  | 89.83 |  |  |  | 0.70 |  | 4.18 | [8 empty] | 6.05 |  |  |  |  | 5.38
2004 |  |  |  | 4299.74 |  |  | 7310 |  |  |  | 635 | [10 empty] | 82.58 |  |  |  | 83.32 | [5 empty] | 77.09 |  |  | 83.22 |  |  |  | 6.13 |  | 6.56 | [8 empty] | 10.12 |  |  |  |  | 0.74
2005 |  |  |  | 4372.64 |  |  | 7632 |  |  |  | 635 | [10 empty] | 86.79 |  |  |  | 86.79 | [5 empty] | 78.61 |  |  | 87.12 |  |  |  | 2.13 |  | 6.68 | [8 empty] | 6.53 |  |  |  |  | 0.00
2006 |  |  |  | 4361.99 |  |  | 7755 |  |  |  | 635 | [10 empty] | 88.74 |  |  |  | 88.74 | [5 empty] | 78.42 |  |  | 88.53 |  |  |  | 0.88 |  | 1.59 | [8 empty] | 9.67 |  |  |  |  | 0.00
2007 |  |  |  | 4121.82 |  |  | 7511 |  |  |  | 635 | [10 empty] | 85.95 |  |  |  | 85.95 | [5 empty] | 74.10 |  |  | 85.74 |  |  |  | 7.79 |  | 8.02 | [8 empty] | 6.04 |  |  |  |  | 0.00
2008 |  |  |  | 1150.56 |  |  | 2111 |  |  |  | 635 | [10 empty] | 24.03 |  |  |  | 24.03 | [5 empty] | 20.63 |  |  | 24.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 75.97 |  |  |  |  | 0.00
2009 |  |  |  | 0.00 |  |  | 0 |  |  |  | 635 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2010 |  |  |  | 0.00 |  |  | 0 |  |  |  | 635 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2011 |  |  |  | 0.00 |  |  | 0 |  |  |  | 635 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2012 |  |  |  | 411.48 |  |  | 966 |  |  |  | 660 | [10 empty] | 7.53 |  |  |  | 7.53 | [5 empty] | 7.30 |  |  | 11.00 |  |  |  | 39.71 |  | 4.96 | [8 empty] | 87.51 |  |  |  |  | 0.00
2013 |  |  |  | 4111.15 |  |  | 7879 |  |  |  | 660 | [10 empty] | 70.80 |  |  |  | 70.80 | [5 empty] | 71.12 |  |  | 89.95 |  |  |  | 25.07 |  | 24.92 | [8 empty] | 4.28 |  |  |  |  | 0.00
2014 |  |  |  | 4724.62 |  |  | 7229 |  |  |  | 660 | [10 empty] | 81.86 |  |  |  | 81.86 | [5 empty] | 81.72 |  |  | 82.52 |  |  |  | 1.50 |  | 6.29 | [8 empty] | 11.85 |  |  |  |  | 0.00
2015 |  |  |  | 4277.04 |  |  | 6993 |  |  |  | 660 | [10 empty] | 74.61 |  |  |  | 74.61 | [5 empty] | 73.98 |  |  | 79.83 |  |  |  | 20.21 |  | 18.89 | [8 empty] | 6.50 |  |  |  |  | 0.00
2016 |  |  |  | 4548.99 |  |  | 6989 |  |  |  | 660 | [10 empty] | 78.20 |  |  |  | 78.20 | [5 empty] | 78.47 |  |  | 79.57 |  |  |  | 2.65 |  | 10.10 | [8 empty] | 11.71 |  |  |  |  | 0.00
2017 |  |  |  | 5151.32 |  |  | 7928 |  |  |  | 660 | [10 empty] | 89.25 |  |  |  | 89.25 | [5 empty] | 89.10 |  |  | 90.50 |  |  |  | 2.44 |  | 3.65 | [8 empty] | 7.10 |  |  |  |  | 0.00
2018 |  |  |  | 4894.15 |  |  | 7469 |  |  |  | 660 | [10 empty] | 84.46 |  |  |  | 84.46 | [5 empty] | 84.65 |  |  | 85.26 |  |  |  | 0.53 |  | 5.32 | [8 empty] | 10.22 |  |  |  |  | 0.00
2019 |  |  |  | 5015.68 |  |  | 7663 |  |  |  | 660 | [10 empty] | 86.69 |  |  |  | 86.69 | [5 empty] | 86.75 |  |  | 87.48 |  |  |  | 4.50 |  | 4.08 | [8 empty] | 9.23 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1983 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 306 | [14 empty] | 305
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 791 | [14 empty] | 76
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 425
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1099
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 24
H. |  | Nuclear regulatory requirements | [39 empty] | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 59
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
Z. |  | Other | [39 empty] | 24
Subtotal | [22 empty] | 791 |  |  |  | 306 | [10 empty] | 1624 |  |  |  | 391 | [11 empty] | 4
Total | [22 empty] | 1097 | [14 empty] | 2019
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1983 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 19
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 179 | [14 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 100
16. |  |  | Steam generation systems | [34 empty] | 42
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 4
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 25
31. |  |  | Turbine and auxiliaries | [19 empty] | 80 | [14 empty] | 57
32. |  |  | Feedwater and Main Steam System | [19 empty] | 47 | [14 empty] | 26
34. |  |  | Miscellaneous Systems | [34 empty] | 18
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [22 empty] | 306 | [14 empty] | 364
Highlights (2019)
Calendar Year 2019 was the second time since the unit's refurbishment that PLNGS produced in excess of 5 million net MWh. In addition to this, the station attained the highest Equipment Reliability Index amongst the CANDU fleet, while achieving INPO excellence. PLNGS is looking to build off these accomplishments in 2020 through continued investment in equipment reliability programs.