## BUSHEHR-1
2019 Operating Experience
IR-1 | [8 empty] | BUSHEHR-1 | [26 empty] | IRAN, ISLAMIC REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NPPDCO (Nuclear Power Production and Development Co. of Iran)
Owner | [7 empty] | : | NPPDCO (Nuclear Power Production and Development Co. of Iran)
Reactor Supplier | [7 empty] | : | JSC ASE (JSC "Atomstroyexport")
Turbine Supplier | [7 empty] | : | JSC ASE (JSC "Atomstroyexport")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-446 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-05-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2011-09-03
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2013-09-23
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 10 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.88
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.67 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 103 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 8
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 5865.73 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 11.36 %
Energy Availability Factor (EAF) | [18 empty] | : | 72.53 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 9.41 %
Unit Capability Factor (UCF) | [18 empty] | : | 73.41 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 17.18 %
Load Factor (LF) | [18 empty] | : | 73.18 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.88 %
Operating Factor (OF) | [18 empty] | : | 75.47 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2149 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 705.38 | 551.40 |  |  |  | 0.00 |  | 18.83 | [8 empty] | 653.57 |  |  | 637.88 | [6 empty] | 635.53 |  | 635.62 |  |  |  | 573.79 |  |  | 677.29 |  |  | 663.72 | [9 empty] | 112.71 |  |  | 5865.73
EAF [%] |  |  |  |  | 100.00 | 87.55 |  |  |  | 0.00 |  | 2.86 | [8 empty] | 94.86 |  |  | 96.82 | [6 empty] | 93.36 |  | 93.37 |  |  |  | 87.10 |  |  | 99.49 |  |  | 100.00 | [9 empty] | 16.30 |  |  | 72.53
UCF [%] |  |  |  |  | 100.00 | 87.55 |  |  |  | 0.00 |  | 2.86 | [8 empty] | 94.86 |  |  | 96.82 | [6 empty] | 93.36 |  | 99.47 |  |  |  | 90.98 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 16.30 |  |  | 73.41
LF [%] |  |  |  |  | 103.62 | 89.68 |  |  |  | 0.00 |  | 2.86 | [8 empty] | 96.01 |  |  | 96.82 | [6 empty] | 93.36 |  | 93.37 |  |  |  | 87.10 |  |  | 99.49 |  |  | 100.75 | [9 empty] | 16.56 |  |  | 73.18
OF [%] |  |  |  |  | 100.00 | 88.39 |  |  |  | 0.00 |  | 3.47 | [8 empty] | 95.43 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 95.14 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 24.33 |  |  | 75.47
FLR [%] |  |  |  |  | 0.00 | 3.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.14 |  |  | 3.18 | [6 empty] | 6.64 |  | 0.53 |  |  |  | 9.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 83.70 |  |  | 11.36
UCL [%] |  |  |  |  | 0.00 | 3.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.14 |  |  | 3.18 | [6 empty] | 6.64 |  | 0.53 |  |  |  | 9.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 83.70 |  |  | 9.41
PUF [%] |  |  |  |  | 0.00 | 9.12 |  |  |  | 100.00 |  | 97.14 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 17.18
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 6.10 |  |  |  | 3.88 |  |  | 0.51 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.88
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 36919.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.71 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.77 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 72.18 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.49 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 66.43 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.41 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 69.95 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2013 |  |  |  | 3893.67 |  |  | 4523 |  |  |  | 915 | [10 empty] | 95.11 |  |  |  | 95.11 | [5 empty] | 95.43 |  |  | 95.47 |  |  |  | 4.89 |  | 4.89 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 3723.60 |  |  | 5181 |  |  |  | 915 | [10 empty] | 56.36 |  |  |  | 56.40 | [5 empty] | 46.46 |  |  | 59.14 |  |  |  | 8.50 |  | 20.09 | [8 empty] | 23.50 |  |  |  |  | 0.04
2015 |  |  |  | 3198.24 |  |  | 3992 |  |  |  | 915 | [10 empty] | 64.42 |  |  |  | 64.85 | [5 empty] | 39.90 |  |  | 45.57 |  |  |  | 1.31 |  | 0.86 | [8 empty] | 34.29 |  |  |  |  | 0.44
2016 |  |  |  | 5923.97 |  |  | 6615 |  |  |  | 915 | [10 empty] | 73.91 |  |  |  | 74.64 | [5 empty] | 73.71 |  |  | 75.31 |  |  |  | 11.39 |  | 19.46 | [8 empty] | 5.90 |  |  |  |  | 0.72
2017 |  |  |  | 6366.21 |  |  | 6971 |  |  |  | 915 | [10 empty] | 80.03 |  |  |  | 80.37 | [5 empty] | 79.42 |  |  | 79.58 |  |  |  | 0.35 |  | 0.28 | [8 empty] | 19.35 |  |  |  |  | 0.34
2018 |  |  |  | 6300.12 |  |  | 6851 |  |  |  | 915 | [10 empty] | 77.50 |  |  |  | 77.63 | [5 empty] | 78.60 |  |  | 78.21 |  |  |  | 0.91 |  | 0.71 | [8 empty] | 21.65 |  |  |  |  | 0.14
2019 |  |  |  | 5865.73 |  |  | 6611 |  |  |  | 915 | [10 empty] | 72.53 |  |  |  | 73.41 | [5 empty] | 73.18 |  |  | 75.47 |  |  |  | 11.36 |  | 9.41 | [8 empty] | 17.18 |  |  |  |  | 0.88
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2013 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 649 | [14 empty] | 611
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1500 | [14 empty] | 1604
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 83
E. |  | Testing of plant systems or components | [35 empty] | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 15
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 299
L. |  | Human factor related | [39 empty] | 29
Subtotal | [22 empty] | 1500 |  |  |  | 649 | [10 empty] | 1689 |  |  |  | 640 | [11 empty] | 314
Total | [22 empty] | 2149 | [14 empty] | 2643
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2013 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [19 empty] | 0 | [14 empty] | 21
15. |  |  | Reactor Cooling Systems | [34 empty] | 124
16. |  |  | Steam generation systems | [19 empty] | 35 | [14 empty] | 14
31. |  |  | Turbine and auxiliaries | [19 empty] | 135 | [14 empty] | 98
32. |  |  | Feedwater and Main Steam System | [19 empty] | 51 | [14 empty] | 14
33. |  |  | Circulating Water System | [34 empty] | 200
34. |  |  | Miscellaneous Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [19 empty] | 428 | [14 empty] | 92
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [22 empty] | 649 | [14 empty] | 576