## HANBIT-1
2019 Operating Experience
KR-7 | [8 empty] | HANBIT-1 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH F | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-06-04
Thermal power | [12 empty] | : |  |  | 2787 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-03-05
Gross electrical power | [12 empty] | : |  |  | 1028 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-08-25
Reference unit power (net) | [12 empty] | : |  |  | 995 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.41
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.65 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 41 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 18190 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.54
| Active core height/length [m] | [13 empty] | : |  |  | 3.658 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.83 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 1440.24 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 16.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 63.06 %
Unit Capability Factor (UCF) | [18 empty] | : | 16.55 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.39 %
Load Factor (LF) | [18 empty] | : | 16.52 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.03 %
Operating Factor (OF) | [18 empty] | : | 16.8 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 7288 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.87 |  |  | 698.75 | [9 empty] | 740.63 |  |  | 1440.24
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.12 |  |  | 97.53 | [9 empty] | 99.99 |  |  | 16.52
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.12 |  |  | 97.94 | [9 empty] | 100.00 |  |  | 16.55
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.12 |  |  | 97.54 | [9 empty] | 100.05 |  |  | 16.52
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 1.08 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 16.80
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 52.82 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.29 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 63.06
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 47.18 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.59 |  |  | 2.06 | [9 empty] | 0.00 |  |  | 20.39
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.41 | [9 empty] | 0.01 |  |  | 0.03
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 233515.43 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.08 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.13 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.94 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.31 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.19 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.93 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 2467.92 |  |  | 2928 |  |  |  | 900 | [10 empty] | 94.44 |  |  |  | 94.67 | [5 empty] | 89.14 |  |  | 94.47 |  |  |  | 3.50 |  | 3.43 | [8 empty] | 1.89 |  |  |  |  | 0.23
1987 |  |  |  | 5973.92 |  |  | 6870 |  |  |  | 900 | [10 empty] | 78.77 |  |  |  | 78.77 | [5 empty] | 75.77 |  |  | 78.42 |  |  |  | 2.26 |  | 1.82 | [8 empty] | 19.41 |  |  |  |  | 0.00
1988 |  |  |  | 6199.62 |  |  | 6844 |  |  |  | 900 | [10 empty] | 77.91 |  |  |  | 77.91 | [5 empty] | 78.42 |  |  | 77.91 |  |  |  | 0.98 |  | 0.77 | [8 empty] | 21.31 |  |  |  |  | 0.00
1989 |  |  |  | 6451.79 |  |  | 7136 |  |  |  | 900 | [10 empty] | 81.46 |  |  |  | 81.46 | [5 empty] | 81.83 |  |  | 81.46 |  |  |  | 0.34 |  | 0.27 | [8 empty] | 18.26 |  |  |  |  | 0.00
1990 |  |  |  | 6897.48 |  |  | 7507 |  |  |  | 900 | [10 empty] | 85.70 |  |  |  | 85.70 | [5 empty] | 87.49 |  |  | 85.70 |  |  |  | 0.21 |  | 0.18 | [8 empty] | 14.12 |  |  |  |  | 0.00
1991 |  |  |  | 6695.62 |  |  | 7383 |  |  |  | 900 | [10 empty] | 84.27 |  |  |  | 84.27 | [5 empty] | 84.93 |  |  | 84.28 |  |  |  | 0.27 |  | 0.23 | [8 empty] | 15.50 |  |  |  |  | 0.00
1992 |  |  |  | 6947.35 |  |  | 7600 |  |  |  | 900 | [10 empty] | 86.52 |  |  |  | 86.52 | [5 empty] | 87.88 |  |  | 86.52 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 13.35 |  |  |  |  | 0.00
1993 |  |  |  | 6723.95 |  |  | 7603 |  |  |  | 900 | [10 empty] | 86.79 |  |  |  | 86.79 | [5 empty] | 85.29 |  |  | 86.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.21 |  |  |  |  | 0.00
1994 |  |  |  | 8230.12 |  |  | 8751 |  |  |  | 890 | [10 empty] | 99.45 |  |  |  | 99.45 | [5 empty] | 105.56 |  |  | 99.90 |  |  |  | 0.47 |  | 0.47 | [8 empty] | 0.08 |  |  |  |  | 0.00
1995 |  |  |  | 6094.64 |  |  | 6781 |  |  |  | 900 | [10 empty] | 74.94 |  |  |  | 74.94 | [5 empty] | 77.30 |  |  | 77.41 |  |  |  | 1.58 |  | 1.20 | [8 empty] | 23.85 |  |  |  |  | 0.00
1996 |  |  |  | 6755.47 |  |  | 7255 |  |  |  | 900 | [10 empty] | 81.35 |  |  |  | 81.37 | [5 empty] | 85.45 |  |  | 82.59 |  |  |  | 0.47 |  | 0.39 | [8 empty] | 18.24 |  |  |  |  | 0.02
1997 |  |  |  | 8236.06 |  |  | 8741 |  |  |  | 900 | [10 empty] | 99.39 |  |  |  | 99.39 | [5 empty] | 104.47 |  |  | 99.78 |  |  |  | 0.52 |  | 0.52 | [8 empty] | 0.09 |  |  |  |  | 0.01
1998 |  |  |  | 7104.49 |  |  | 7599 |  |  |  | 900 | [10 empty] | 85.49 |  |  |  | 85.49 | [5 empty] | 90.11 |  |  | 86.75 |  |  |  | 0.32 |  | 0.28 | [8 empty] | 14.23 |  |  |  |  | 0.00
1999 |  |  |  | 6729.98 |  |  | 7242 |  |  |  | 900 | [10 empty] | 81.07 |  |  |  | 81.07 | [5 empty] | 85.36 |  |  | 82.67 |  |  |  | 0.41 |  | 0.33 | [8 empty] | 18.60 |  |  |  |  | 0.00
2000 |  |  |  | 7215.09 |  |  | 7696 |  |  |  | 900 | [10 empty] | 87.51 |  |  |  | 87.51 | [5 empty] | 91.27 |  |  | 87.61 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 12.48 |  |  |  |  | 0.00
2001 |  |  |  | 8346.44 |  |  | 8760 |  |  |  | 900 | [10 empty] | 99.94 |  |  |  | 99.94 | [5 empty] | 105.87 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.06 |  |  |  |  | 0.00
2002 |  |  |  | 7419.03 |  |  | 7867 |  |  |  | 900 | [10 empty] | 88.81 |  |  |  | 88.81 | [5 empty] | 94.10 |  |  | 89.81 |  |  |  | 0.43 |  | 0.38 | [8 empty] | 10.81 |  |  |  |  | 0.00
2003 |  |  |  | 7074.39 |  |  | 7593 |  |  |  | 900 | [10 empty] | 86.32 |  |  |  | 86.34 | [5 empty] | 89.73 |  |  | 86.68 |  |  |  | 2.68 |  | 2.38 | [8 empty] | 11.28 |  |  |  |  | 0.02
2004 |  |  |  | 7207.19 |  |  | 7688 |  |  |  | 900 | [10 empty] | 86.69 |  |  |  | 86.69 | [5 empty] | 91.17 |  |  | 87.52 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 13.28 |  |  |  |  | 0.00
2005 |  |  |  | 8302.85 |  |  | 8760 |  |  |  | 900 | [10 empty] | 99.95 |  |  |  | 99.97 | [5 empty] | 105.31 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.02
2006 |  |  |  | 7545.07 |  |  | 8030 |  |  |  | 945 | [10 empty] | 91.06 |  |  |  | 91.06 | [5 empty] | 91.14 |  |  | 91.67 |  |  |  | 0.17 |  | 0.15 | [8 empty] | 8.78 |  |  |  |  | 0.00
2007 |  |  |  | 6466.51 |  |  | 6855 |  |  |  | 942 | [10 empty] | 77.26 |  |  |  | 77.62 | [5 empty] | 78.36 |  |  | 78.25 |  |  |  | 11.85 |  | 10.44 | [8 empty] | 11.95 |  |  |  |  | 0.36
2008 |  |  |  | 8434.70 |  |  | 8784 |  |  |  | 953 | [10 empty] | 99.86 |  |  |  | 99.99 | [5 empty] | 100.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.13
2009 |  |  |  | 7414.03 |  |  | 7785 |  |  |  | 953 | [10 empty] | 88.45 |  |  |  | 89.05 | [5 empty] | 88.81 |  |  | 88.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.95 |  |  |  |  | 0.60
2010 |  |  |  | 7791.08 |  |  | 8158 |  |  |  | 953 | [10 empty] | 92.41 |  |  |  | 92.68 | [5 empty] | 93.33 |  |  | 93.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.32 |  |  |  |  | 0.27
2011 |  |  |  | 8417.70 |  |  | 8760 |  |  |  | 953 | [10 empty] | 99.80 |  |  |  | 99.95 | [5 empty] | 100.83 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  |  |  | 0.16
2012 |  |  |  | 7733.46 |  |  | 8103 |  |  |  | 959 | [10 empty] | 91.31 |  |  |  | 91.76 | [5 empty] | 91.80 |  |  | 92.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.24 |  |  |  |  | 0.45
2013 |  |  |  | 6911.44 |  |  | 7204 |  |  |  | 997 | [10 empty] | 81.23 |  |  |  | 81.94 | [5 empty] | 81.66 |  |  | 82.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.06 |  |  |  |  | 0.71
2014 |  |  |  | 8729.35 |  |  | 8760 |  |  |  | 997 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.95 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 7184.07 |  |  | 7289 |  |  |  | 997 | [10 empty] | 82.02 |  |  |  | 82.65 | [5 empty] | 82.26 |  |  | 83.21 |  |  |  | 0.20 |  | 0.17 | [8 empty] | 17.18 |  |  |  |  | 0.63
2016 |  |  |  | 6417.05 |  |  | 6539 |  |  |  | 996 | [10 empty] | 73.15 |  |  |  | 74.13 | [5 empty] | 73.35 |  |  | 74.44 |  |  |  | 10.68 |  | 8.86 | [8 empty] | 17.01 |  |  |  |  | 0.97
2017 |  |  |  | 6374.24 |  |  | 6484 |  |  |  | 996 | [10 empty] | 72.97 |  |  |  | 73.78 | [5 empty] | 73.06 |  |  | 74.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.22 |  |  |  |  | 0.81
2018 |  |  |  | 5419.36 |  |  | 5506 |  |  |  | 995 | [10 empty] | 62.03 |  |  |  | 62.67 | [5 empty] | 62.18 |  |  | 62.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.33 |  |  |  |  | 0.64
2019 |  |  |  | 1440.24 |  |  | 1472 |  |  |  | 995 | [10 empty] | 16.52 |  |  |  | 16.55 | [5 empty] | 16.52 |  |  | 16.80 |  |  |  | 0.00 |  | 63.06 | [8 empty] | 20.39 |  |  |  |  | 0.03
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1986 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 73
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1767 | [14 empty] | 1074
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [24 empty] | 4173 | [14 empty] | 126
P. |  | Fire | [24 empty] | 1351 | [14 empty] | 41
Z. |  | Other | [51 empty] | 1
Subtotal | [22 empty] | 1767 |  |  |  | 5524 | [10 empty] | 1079 |  |  |  | 240 | [11 empty] | 1
Total | [22 empty] | 7291 | [14 empty] | 1320
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1986 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [19 empty] | 4173 | [14 empty] | 129
15. |  |  | Reactor Cooling Systems | [19 empty] | 1351 | [14 empty] | 41
16. |  |  | Steam generation systems | [34 empty] | 0
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 25
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 32
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [22 empty] | 5524 | [14 empty] | 235
Highlights (2019)
Refueling and maintenance(2018-8-18~2019-10-31) Manual scram(Human error occurred during a rod group reactivity worth measurement test, 2019-5-10)

## HANBIT-2
2019 Operating Experience
KR-8 | [8 empty] | HANBIT-2 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH F | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-12-01
Thermal power | [12 empty] | : |  |  | 2787 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-11-11
Gross electrical power | [12 empty] | : |  |  | 1025 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-06-10
Reference unit power (net) | [12 empty] | : |  |  | 988 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.41
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.65 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 41 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 17960 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.54
| Active core height/length [m] | [13 empty] | : |  |  | 3.658 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.83 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 7473.09 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.23 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 6.2 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.13 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.67 %
Load Factor (LF) | [18 empty] | : | 86.35 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.9 %
Operating Factor (OF) | [18 empty] | : | 87.41 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1103 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.27 | 287.61 |  |  |  | 737.79 |  | 713.10 | [8 empty] | 731.45 |  |  | 703.53 | [6 empty] | 721.39 |  | 710.84 |  |  |  | 694.04 |  |  | 724.02 |  |  | 711.27 | [9 empty] | 737.78 |  |  | 7473.09
EAF [%] |  |  |  |  | 0.04 | 43.15 |  |  |  | 100.00 |  | 99.94 | [8 empty] | 99.51 |  |  | 98.90 | [6 empty] | 98.14 |  | 96.70 |  |  |  | 97.57 |  |  | 98.50 |  |  | 99.87 | [9 empty] | 100.00 |  |  | 86.23
UCF [%] |  |  |  |  | 0.04 | 43.15 |  |  |  | 100.00 |  | 99.94 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.95 |  | 99.96 |  |  |  | 100.00 |  |  | 99.96 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.13
LF [%] |  |  |  |  | 0.04 | 43.32 |  |  |  | 100.37 |  | 100.24 | [8 empty] | 99.51 |  |  | 98.90 | [6 empty] | 98.14 |  | 96.70 |  |  |  | 97.57 |  |  | 98.50 |  |  | 99.99 | [9 empty] | 100.37 |  |  | 86.35
OF [%] |  |  |  |  | 0.27 | 46.28 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.41
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.03 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.04 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
UCL [%] |  |  |  |  | 24.14 | 53.99 |  |  |  | 0.00 |  | 0.03 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.04 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.20
PUF [%] |  |  |  |  | 75.82 | 2.86 |  |  |  | 0.00 |  | 0.03 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.05 |  | 0.00 |  |  |  | 0.00 |  |  | 0.04 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.67
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.49 |  |  | 1.10 | [6 empty] | 1.81 |  | 3.25 |  |  |  | 2.43 |  |  | 1.46 |  |  | 0.13 | [9 empty] | 0.00 |  |  | 0.90
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 225797.34 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.86 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.22 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.92 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.36 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.71 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.71 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.14 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.09 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 4297.03 |  |  | 4826 |  |  |  | 900 | [10 empty] | 98.15 |  |  |  | 98.15 | [5 empty] | 97.02 |  |  | 98.07 |  |  |  | 1.85 |  | 1.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 6280.88 |  |  | 7085 |  |  |  | 900 | [10 empty] | 80.65 |  |  |  | 80.65 | [5 empty] | 79.45 |  |  | 80.66 |  |  |  | 0.31 |  | 0.25 | [8 empty] | 19.10 |  |  |  |  | 0.00
1989 |  |  |  | 5703.24 |  |  | 6446 |  |  |  | 900 | [10 empty] | 73.60 |  |  |  | 73.60 | [5 empty] | 72.34 |  |  | 73.58 |  |  |  | 6.35 |  | 4.99 | [8 empty] | 21.42 |  |  |  |  | 0.00
1990 |  |  |  | 5964.51 |  |  | 6757 |  |  |  | 900 | [10 empty] | 77.13 |  |  |  | 77.13 | [5 empty] | 75.65 |  |  | 77.13 |  |  |  | 1.27 |  | 0.99 | [8 empty] | 21.87 |  |  |  |  | 0.00
1991 |  |  |  | 6714.99 |  |  | 7433 |  |  |  | 900 | [10 empty] | 84.85 |  |  |  | 84.85 | [5 empty] | 85.17 |  |  | 84.85 |  |  |  | 0.35 |  | 0.30 | [8 empty] | 14.85 |  |  |  |  | 0.00
1992 |  |  |  | 6434.62 |  |  | 7259 |  |  |  | 900 | [10 empty] | 82.64 |  |  |  | 82.64 | [5 empty] | 81.39 |  |  | 82.64 |  |  |  | 0.41 |  | 0.34 | [8 empty] | 17.02 |  |  |  |  | 0.00
1993 |  |  |  | 6930.49 |  |  | 7506 |  |  |  | 900 | [10 empty] | 85.69 |  |  |  | 85.83 | [5 empty] | 87.91 |  |  | 85.68 |  |  |  | 1.23 |  | 1.07 | [8 empty] | 13.10 |  |  |  |  | 0.15
1994 |  |  |  | 7132.86 |  |  | 7687 |  |  |  | 890 | [10 empty] | 85.55 |  |  |  | 85.55 | [5 empty] | 91.49 |  |  | 87.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.45 |  |  |  |  | 0.00
1995 |  |  |  | 6036.45 |  |  | 6696 |  |  |  | 900 | [10 empty] | 74.20 |  |  |  | 74.20 | [5 empty] | 76.57 |  |  | 76.44 |  |  |  | 1.06 |  | 0.80 | [8 empty] | 25.00 |  |  |  |  | 0.00
1996 |  |  |  | 7656.10 |  |  | 8189 |  |  |  | 900 | [10 empty] | 91.59 |  |  |  | 91.65 | [5 empty] | 96.84 |  |  | 93.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.35 |  |  |  |  | 0.06
1997 |  |  |  | 6657.34 |  |  | 7453 |  |  |  | 900 | [10 empty] | 81.21 |  |  |  | 81.21 | [5 empty] | 84.44 |  |  | 85.08 |  |  |  | 0.84 |  | 0.68 | [8 empty] | 18.11 |  |  |  |  | 0.00
1998 |  |  |  | 6010.35 |  |  | 6583 |  |  |  | 900 | [10 empty] | 74.39 |  |  |  | 74.50 | [5 empty] | 76.23 |  |  | 75.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.49 |  |  |  |  | 0.11
1999 |  |  |  | 6718.91 |  |  | 7301 |  |  |  | 900 | [10 empty] | 82.08 |  |  |  | 82.08 | [5 empty] | 85.22 |  |  | 83.34 |  |  |  | 1.66 |  | 1.38 | [8 empty] | 16.54 |  |  |  |  | 0.00
2000 |  |  |  | 7144.06 |  |  | 7753 |  |  |  | 900 | [10 empty] | 87.07 |  |  |  | 87.07 | [5 empty] | 90.37 |  |  | 88.26 |  |  |  | 0.31 |  | 0.27 | [8 empty] | 12.66 |  |  |  |  | 0.00
2001 |  |  |  | 7169.67 |  |  | 7726 |  |  |  | 900 | [10 empty] | 87.08 |  |  |  | 87.08 | [5 empty] | 90.94 |  |  | 88.20 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 12.91 |  |  |  |  | 0.00
2002 |  |  |  | 8194.23 |  |  | 8744 |  |  |  | 900 | [10 empty] | 99.61 |  |  |  | 99.90 | [5 empty] | 103.93 |  |  | 99.82 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 0.04 |  |  |  |  | 0.29
2003 |  |  |  | 7413.30 |  |  | 7931 |  |  |  | 900 | [10 empty] | 89.63 |  |  |  | 89.66 | [5 empty] | 94.03 |  |  | 90.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.34 |  |  |  |  | 0.03
2004 |  |  |  | 7242.94 |  |  | 7764 |  |  |  | 900 | [10 empty] | 87.51 |  |  |  | 87.51 | [5 empty] | 91.62 |  |  | 88.39 |  |  |  | 2.05 |  | 1.83 | [8 empty] | 10.66 |  |  |  |  | 0.00
2005 |  |  |  | 7302.40 |  |  | 7881 |  |  |  | 900 | [10 empty] | 88.62 |  |  |  | 88.64 | [5 empty] | 92.62 |  |  | 89.97 |  |  |  | 0.70 |  | 0.62 | [8 empty] | 10.74 |  |  |  |  | 0.02
2006 |  |  |  | 8195.68 |  |  | 8719 |  |  |  | 939 | [10 empty] | 99.92 |  |  |  | 99.99 | [5 empty] | 99.64 |  |  | 99.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.07
2007 |  |  |  | 7030.06 |  |  | 7523 |  |  |  | 936 | [10 empty] | 84.37 |  |  |  | 85.11 | [5 empty] | 85.74 |  |  | 85.88 |  |  |  | 0.62 |  | 0.53 | [8 empty] | 14.36 |  |  |  |  | 0.74
2008 |  |  |  | 7472.86 |  |  | 7850 |  |  |  | 947 | [10 empty] | 88.91 |  |  |  | 89.05 | [5 empty] | 89.83 |  |  | 89.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.95 |  |  |  |  | 0.13
2009 |  |  |  | 8376.93 |  |  | 8760 |  |  |  | 947 | [10 empty] | 99.94 |  |  |  | 99.99 | [5 empty] | 100.98 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.05
2010 |  |  |  | 7461.45 |  |  | 7830 |  |  |  | 947 | [10 empty] | 88.86 |  |  |  | 88.95 | [5 empty] | 89.94 |  |  | 89.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.05 |  |  |  |  | 0.09
2011 |  |  |  | 7600.63 |  |  | 7988 |  |  |  | 947 | [10 empty] | 90.38 |  |  |  | 90.67 | [5 empty] | 91.62 |  |  | 91.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.33 |  |  |  |  | 0.29
2012 |  |  |  | 8383.44 |  |  | 8784 |  |  |  | 958 | [10 empty] | 99.47 |  |  |  | 99.97 | [5 empty] | 99.62 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.01 |  |  |  |  | 0.50
2013 |  |  |  | 6277.11 |  |  | 6509 |  |  |  | 958 | [10 empty] | 73.22 |  |  |  | 73.25 | [5 empty] | 74.80 |  |  | 74.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.75 |  |  |  |  | 0.03
2014 |  |  |  | 6661.49 |  |  | 6789 |  |  |  | 977 | [10 empty] | 76.84 |  |  |  | 76.92 | [5 empty] | 77.83 |  |  | 77.50 |  |  |  | 2.91 |  | 2.30 | [8 empty] | 20.78 |  |  |  |  | 0.08
2015 |  |  |  | 7944.95 |  |  | 8060 |  |  |  | 984 | [10 empty] | 93.91 |  |  |  | 94.18 | [5 empty] | 92.17 |  |  | 92.01 |  |  |  | 5.82 |  | 5.82 | [8 empty] | 0.01 |  |  |  |  | 0.26
2016 |  |  |  | 2953.95 |  |  | 2986 |  |  |  | 988 | [10 empty] | 33.80 |  |  |  | 33.80 | [5 empty] | 34.04 |  |  | 33.99 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 66.19 |  |  |  |  | 0.00
2017 |  |  |  | 6669.35 |  |  | 6820 |  |  |  | 988 | [10 empty] | 76.91 |  |  |  | 77.54 | [5 empty] | 77.06 |  |  | 77.85 |  |  |  | 0.08 |  | 0.06 | [8 empty] | 22.40 |  |  |  |  | 0.63
2018 |  |  |  | 4643.92 |  |  | 4714 |  |  |  | 988 | [10 empty] | 53.42 |  |  |  | 53.54 | [5 empty] | 53.66 |  |  | 53.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 46.46 |  |  |  |  | 0.11
2019 |  |  |  | 7473.09 |  |  | 7657 |  |  |  | 988 | [10 empty] | 86.23 |  |  |  | 87.13 | [5 empty] | 86.35 |  |  | 87.41 |  |  |  | 0.01 |  | 6.20 | [8 empty] | 6.67 |  |  |  |  | 0.90
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1987 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 52
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 564 | [14 empty] | 1237
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 78
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 7
L. |  | Human factor related | [24 empty] | 543 | [14 empty] | 20
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
Subtotal | [22 empty] | 564 |  |  |  | 543 | [10 empty] | 1315 |  |  |  | 72 | [11 empty] | 7
Total | [22 empty] | 1107 | [14 empty] | 1394
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1987 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 17
16. |  |  | Steam generation systems | [19 empty] | 543 | [14 empty] | 28
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 12
42. |  |  | Electrical Power Supply Systems | [34 empty] | 6
Total | [22 empty] | 543 | [14 empty] | 72
Highlights (2019)
Refueling and maintenance(2018-7-16~2019-2-16) Automatic scram(SG LVL LO-LO during maintenance,2019-1-24)

## HANBIT-3
2019 Operating Experience
KR-11 | [8 empty] | HANBIT-3 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKAEC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA ATOMICENERGY RESEARCH INSTITUTE/COMBUSTION ENGINEERING )
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1989-12-23
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1994-10-30
Gross electrical power | [12 empty] | : |  |  | 1037 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1995-03-31
Reference unit power (net) | [12 empty] | : |  |  | 986 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 25 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.37
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 42700 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.124 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.26 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8760 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 174348.76 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.36 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.81 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.51 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.68 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.64 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.15 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.03 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1995 |  |  |  | 6430.28 |  |  | 6573 |  |  |  | 950 | [10 empty] | 99.19 |  |  |  | 99.19 | [5 empty] | 102.56 |  |  | 99.59 |  |  |  | 0.77 |  | 0.77 | [8 empty] | 0.04 |  |  |  |  | 0.00
1996 |  |  |  | 6366.17 |  |  | 6589 |  |  |  | 950 | [10 empty] | 73.97 |  |  |  | 73.98 | [5 empty] | 76.29 |  |  | 75.01 |  |  |  | 0.22 |  | 0.17 | [8 empty] | 25.85 |  |  |  |  | 0.01
1997 |  |  |  | 7229.61 |  |  | 7443 |  |  |  | 950 | [10 empty] | 84.03 |  |  |  | 84.03 | [5 empty] | 86.87 |  |  | 84.97 |  |  |  | 0.53 |  | 0.45 | [8 empty] | 15.52 |  |  |  |  | 0.00
1998 |  |  |  | 7400.78 |  |  | 7566 |  |  |  | 950 | [10 empty] | 85.47 |  |  |  | 85.47 | [5 empty] | 88.93 |  |  | 86.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.53 |  |  |  |  | 0.00
1999 |  |  |  | 7395.31 |  |  | 7678 |  |  |  | 950 | [10 empty] | 86.70 |  |  |  | 86.70 | [5 empty] | 88.86 |  |  | 87.65 |  |  |  | 0.83 |  | 0.73 | [8 empty] | 12.57 |  |  |  |  | 0.00
2000 |  |  |  | 7262.02 |  |  | 7568 |  |  |  | 950 | [10 empty] | 85.62 |  |  |  | 85.62 | [5 empty] | 87.02 |  |  | 86.16 |  |  |  | 0.17 |  | 0.15 | [8 empty] | 14.23 |  |  |  |  | 0.00
2001 |  |  |  | 8629.13 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.96 |  |  |  | 99.96 | [5 empty] | 103.69 |  |  | 100.00 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 7658.18 |  |  | 7831 |  |  |  | 950 | [10 empty] | 89.09 |  |  |  | 89.09 | [5 empty] | 92.02 |  |  | 89.39 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 10.84 |  |  |  |  | 0.00
2003 |  |  |  | 7818.09 |  |  | 7971 |  |  |  | 950 | [10 empty] | 90.08 |  |  |  | 90.08 | [5 empty] | 93.94 |  |  | 90.99 |  |  |  | 0.51 |  | 0.46 | [8 empty] | 9.46 |  |  |  |  | 0.00
2004 |  |  |  | 7654.72 |  |  | 7801 |  |  |  | 950 | [10 empty] | 90.35 |  |  |  | 90.35 | [5 empty] | 91.73 |  |  | 88.81 |  |  |  | 0.48 |  | 0.43 | [8 empty] | 9.22 |  |  |  |  | 0.00
2005 |  |  |  | 8675.55 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 104.25 |  |  | 100.00 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 0.00 |  |  |  |  | 0.01
2006 |  |  |  | 7556.77 |  |  | 7800 |  |  |  | 985 | [10 empty] | 87.34 |  |  |  | 87.40 | [5 empty] | 87.58 |  |  | 89.04 |  |  |  | 1.44 |  | 1.27 | [8 empty] | 11.32 |  |  |  |  | 0.06
2007 |  |  |  | 7778.30 |  |  | 7916 |  |  |  | 987 | [10 empty] | 90.18 |  |  |  | 90.81 | [5 empty] | 89.96 |  |  | 90.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.19 |  |  |  |  | 0.63
2008 |  |  |  | 7861.88 |  |  | 7967 |  |  |  | 997 | [10 empty] | 90.11 |  |  |  | 90.21 | [5 empty] | 89.77 |  |  | 90.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.79 |  |  |  |  | 0.10
2009 |  |  |  | 8737.18 |  |  | 8760 |  |  |  | 997 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.04 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 7953.95 |  |  | 8014 |  |  |  | 997 | [10 empty] | 90.68 |  |  |  | 91.13 | [5 empty] | 91.07 |  |  | 91.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.87 |  |  |  |  | 0.46
2011 |  |  |  | 7944.10 |  |  | 7973 |  |  |  | 997 | [10 empty] | 90.45 |  |  |  | 90.52 | [5 empty] | 90.96 |  |  | 91.02 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 9.43 |  |  |  |  | 0.07
2012 |  |  |  | 6961.94 |  |  | 6994 |  |  |  | 1000 | [10 empty] | 79.02 |  |  |  | 79.49 | [5 empty] | 79.26 |  |  | 79.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.51 |  |  |  |  | 0.47
2013 |  |  |  | 4719.06 |  |  | 4809 |  |  |  | 997 | [10 empty] | 53.98 |  |  |  | 54.28 | [5 empty] | 54.03 |  |  | 54.90 |  |  |  | 2.28 |  | 1.27 | [8 empty] | 44.45 |  |  |  |  | 0.30
2014 |  |  |  | 6882.52 |  |  | 6938 |  |  |  | 1000 | [10 empty] | 78.55 |  |  |  | 79.16 | [5 empty] | 78.57 |  |  | 79.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.84 |  |  |  |  | 0.61
2015 |  |  |  | 5012.19 |  |  | 5125 |  |  |  | 994 | [10 empty] | 57.44 |  |  |  | 57.63 | [5 empty] | 57.56 |  |  | 58.50 |  |  |  | 19.65 |  | 14.10 | [8 empty] | 28.27 |  |  |  |  | 0.19
2016 |  |  |  | 6965.40 |  |  | 7091 |  |  |  | 994 | [10 empty] | 79.59 |  |  |  | 80.08 | [5 empty] | 79.78 |  |  | 80.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.92 |  |  |  |  | 0.49
2017 |  |  |  | 8628.46 |  |  | 8760 |  |  |  | 986 | [10 empty] | 99.69 |  |  |  | 99.99 | [5 empty] | 99.90 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.30
2018 |  |  |  | 3078.30 |  |  | 3130 |  |  |  | 986 | [10 empty] | 35.54 |  |  |  | 35.54 | [5 empty] | 35.64 |  |  | 35.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 64.46 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 986 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1995 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 60
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 8760 | [14 empty] | 1598
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 5
E. |  | Testing of plant systems or components | [39 empty] | 0
L. |  | Human factor related | [39 empty] | 0
Subtotal | [22 empty] | 8760 | [14 empty] | 1603 |  |  |  | 60
Total | [22 empty] | 8760 | [14 empty] | 1663
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1995 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 48
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [37 empty] | 60
Highlights (2019)
Refueling and Maintenance(2018.05.11.~)

## HANBIT-4
2019 Operating Experience
KR-12 | [8 empty] | HANBIT-4 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKAEC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA ATOMICENERGY RESEARCH INSTITUTE/COMBUSTION ENGINEERING )
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1990-05-26
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1995-07-18
Gross electrical power | [12 empty] | : |  |  | 1022 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1996-01-01
Reference unit power (net) | [12 empty] | : |  |  | 970 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 24 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.37
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 42700 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.124 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.26 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8760 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 165873.43 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.38 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.87 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.36 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.05 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.59 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.18 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.55 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1996 |  |  |  | 7197.47 |  |  | 7565 |  |  |  | 950 | [10 empty] | 83.49 |  |  |  | 83.50 | [5 empty] | 86.25 |  |  | 86.12 |  |  |  | 1.71 |  | 1.45 | [8 empty] | 15.05 |  |  |  |  | 0.00
1997 |  |  |  | 6767.71 |  |  | 7125 |  |  |  | 950 | [10 empty] | 78.80 |  |  |  | 78.80 | [5 empty] | 81.32 |  |  | 81.34 |  |  |  | 3.24 |  | 2.64 | [8 empty] | 18.56 |  |  |  |  | 0.00
1998 |  |  |  | 8427.31 |  |  | 8591 |  |  |  | 950 | [10 empty] | 97.14 |  |  |  | 97.14 | [5 empty] | 101.27 |  |  | 98.07 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 2.78 |  |  |  |  | 0.00
1999 |  |  |  | 7627.93 |  |  | 7883 |  |  |  | 950 | [10 empty] | 89.03 |  |  |  | 89.03 | [5 empty] | 91.66 |  |  | 89.99 |  |  |  | 0.37 |  | 0.33 | [8 empty] | 10.64 |  |  |  |  | 0.00
2000 |  |  |  | 7252.26 |  |  | 7441 |  |  |  | 950 | [10 empty] | 84.65 |  |  |  | 84.65 | [5 empty] | 86.91 |  |  | 84.71 |  |  |  | 0.25 |  | 0.21 | [8 empty] | 15.14 |  |  |  |  | 0.00
2001 |  |  |  | 7237.24 |  |  | 7424 |  |  |  | 950 | [10 empty] | 84.76 |  |  |  | 84.76 | [5 empty] | 86.97 |  |  | 84.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.24 |  |  |  |  | 0.00
2002 |  |  |  | 7653.46 |  |  | 7808 |  |  |  | 950 | [10 empty] | 88.65 |  |  |  | 88.65 | [5 empty] | 91.97 |  |  | 89.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.35 |  |  |  |  | 0.00
2003 |  |  |  | 8576.76 |  |  | 8652 |  |  |  | 950 | [10 empty] | 98.68 |  |  |  | 98.68 | [5 empty] | 103.06 |  |  | 98.77 |  |  |  | 1.22 |  | 1.22 | [8 empty] | 0.10 |  |  |  |  | 0.00
2004 |  |  |  | 7624.86 |  |  | 7782 |  |  |  | 950 | [10 empty] | 88.28 |  |  |  | 88.28 | [5 empty] | 91.37 |  |  | 88.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.72 |  |  |  |  | 0.00
2005 |  |  |  | 7754.98 |  |  | 7879 |  |  |  | 950 | [10 empty] | 89.80 |  |  |  | 89.80 | [5 empty] | 93.19 |  |  | 89.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.20 |  |  |  |  | 0.01
2006 |  |  |  | 8646.19 |  |  | 8760 |  |  |  | 988 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 99.90 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2007 |  |  |  | 7651.07 |  |  | 7790 |  |  |  | 987 | [10 empty] | 87.78 |  |  |  | 88.37 | [5 empty] | 88.49 |  |  | 88.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.63 |  |  |  |  | 0.59
2008 |  |  |  | 7992.63 |  |  | 8084 |  |  |  | 994 | [10 empty] | 91.42 |  |  |  | 91.44 | [5 empty] | 91.54 |  |  | 92.03 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 8.52 |  |  |  |  | 0.02
2009 |  |  |  | 7694.28 |  |  | 7768 |  |  |  | 994 | [10 empty] | 88.07 |  |  |  | 88.07 | [5 empty] | 88.36 |  |  | 88.68 |  |  |  | 1.51 |  | 2.68 | [8 empty] | 9.25 |  |  |  |  | 0.00
2010 |  |  |  | 8760.58 |  |  | 8760 |  |  |  | 994 | [10 empty] | 99.91 |  |  |  | 99.97 | [5 empty] | 100.61 |  |  | 100.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.00 |  |  |  |  | 0.06
2011 |  |  |  | 7923.20 |  |  | 8005 |  |  |  | 994 | [10 empty] | 90.37 |  |  |  | 91.00 | [5 empty] | 90.99 |  |  | 91.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.00 |  |  |  |  | 0.64
2012 |  |  |  | 7705.11 |  |  | 7765 |  |  |  | 996 | [10 empty] | 87.65 |  |  |  | 87.83 | [5 empty] | 88.07 |  |  | 88.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.17 |  |  |  |  | 0.17
2013 |  |  |  | 7563.57 |  |  | 7618 |  |  |  | 997 | [10 empty] | 86.44 |  |  |  | 86.80 | [5 empty] | 86.60 |  |  | 86.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.20 |  |  |  |  | 0.36
2014 |  |  |  | 6796.58 |  |  | 6989 |  |  |  | 998 | [10 empty] | 77.74 |  |  |  | 79.30 | [5 empty] | 77.74 |  |  | 79.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.70 |  |  |  |  | 1.56
2015 |  |  |  | 5400.06 |  |  | 5584 |  |  |  | 980 | [10 empty] | 62.89 |  |  |  | 63.18 | [5 empty] | 62.90 |  |  | 63.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.82 |  |  |  |  | 0.29
2016 |  |  |  | 8487.73 |  |  | 8784 |  |  |  | 970 | [10 empty] | 99.54 |  |  |  | 99.99 | [5 empty] | 99.62 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.45
2017 |  |  |  | 3188.64 |  |  | 3298 |  |  |  | 970 | [10 empty] | 37.48 |  |  |  | 37.49 | [5 empty] | 37.53 |  |  | 37.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 62.51 |  |  |  |  | 0.01
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 970 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 970 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1996 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 25
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 8760 | [14 empty] | 1767
L. |  | Human factor related | [39 empty] | 0
Subtotal | [22 empty] | 8760 | [14 empty] | 1767 |  |  |  | 25
Total | [22 empty] | 8760 | [14 empty] | 1792
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1996 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 25
Highlights (2019)
Refueling and Maintenance(2017.05.18.~) Inspection & repair of air gaps between CLP(containment liner plate) and concrete of reactor building

## HANBIT-5
2019 Operating Experience
KR-17 | [8 empty] | HANBIT-5 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1997-06-29
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2001-12-19
Gross electrical power | [12 empty] | : |  |  | 1049 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-05-21
Reference unit power (net) | [12 empty] | : |  |  | 992 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 18 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 13820 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 4
| Active core diameter [m] | [13 empty] | : |  |  | 3.124 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19.68 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 8613.69 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.69 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.95 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.69 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.3 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 99.12 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.35 %
Operating Factor (OF) | [18 empty] | : | 99.42 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 51 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 741.46 | 668.89 |  |  |  | 680.99 |  | 717.21 | [8 empty] | 738.95 |  |  | 711.20 | [6 empty] | 730.96 |  | 724.93 |  |  |  | 708.17 |  |  | 736.74 |  |  | 715.06 | [9 empty] | 739.14 |  |  | 8613.69
EAF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 91.91 |  | 100.00 | [8 empty] | 99.96 |  |  | 99.57 | [6 empty] | 99.04 |  | 98.22 |  |  |  | 99.15 |  |  | 99.82 |  |  | 99.99 | [9 empty] | 99.99 |  |  | 98.95
UCF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 91.91 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.98 |  |  | 99.94 |  |  | 99.99 | [9 empty] | 99.99 |  |  | 99.30
LF [%] |  |  |  |  | 100.46 | 100.34 |  |  |  | 92.27 |  | 100.42 | [8 empty] | 100.12 |  |  | 99.57 | [6 empty] | 99.04 |  | 98.22 |  |  |  | 99.15 |  |  | 99.82 |  |  | 100.11 | [9 empty] | 100.15 |  |  | 99.12
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.15 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.42
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 8.09 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.06 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 0.69
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 8.09 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.06 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 0.69
PUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  | 0.42 | [6 empty] | 0.96 |  | 1.78 |  |  |  | 0.83 |  |  | 0.12 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.35
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 135007.83 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.69 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.02 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.27 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.87 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.21 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.75 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 5006.77 |  |  | 5095 |  |  |  | 950 | [10 empty] | 98.71 |  |  |  | 98.71 | [5 empty] | 102.59 |  |  | 99.18 |  |  |  | 1.25 |  | 1.25 | [8 empty] | 0.03 |  |  |  |  | 0.00
2003 |  |  |  | 6694.37 |  |  | 6856 |  |  |  | 950 | [10 empty] | 77.12 |  |  |  | 77.12 | [5 empty] | 80.44 |  |  | 78.26 |  |  |  | 1.14 |  | 0.89 | [8 empty] | 22.00 |  |  |  |  | 0.00
2004 |  |  |  | 5524.51 |  |  | 5611 |  |  |  | 950 | [10 empty] | 63.34 |  |  |  | 63.34 | [5 empty] | 66.20 |  |  | 63.88 |  |  |  | 3.63 |  | 2.39 | [8 empty] | 34.27 |  |  |  |  | 0.00
2005 |  |  |  | 7748.43 |  |  | 7873 |  |  |  | 950 | [10 empty] | 88.80 |  |  |  | 89.00 | [5 empty] | 93.11 |  |  | 89.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.00 |  |  |  |  | 0.20
2006 |  |  |  | 7688.25 |  |  | 7859 |  |  |  | 987 | [10 empty] | 88.80 |  |  |  | 88.83 | [5 empty] | 88.92 |  |  | 89.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.17 |  |  |  |  | 0.04
2007 |  |  |  | 8601.74 |  |  | 8725 |  |  |  | 990 | [10 empty] | 99.11 |  |  |  | 99.12 | [5 empty] | 99.19 |  |  | 99.60 |  |  |  | 0.88 |  | 0.88 | [8 empty] | 0.00 |  |  |  |  | 0.01
2008 |  |  |  | 7807.37 |  |  | 7972 |  |  |  | 988 | [10 empty] | 90.21 |  |  |  | 90.24 | [5 empty] | 89.96 |  |  | 90.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.76 |  |  |  |  | 0.03
2009 |  |  |  | 7857.49 |  |  | 7987 |  |  |  | 988 | [10 empty] | 90.56 |  |  |  | 90.58 | [5 empty] | 90.79 |  |  | 91.18 |  |  |  | 0.46 |  | 0.42 | [8 empty] | 9.00 |  |  |  |  | 0.02
2010 |  |  |  | 8457.74 |  |  | 8528 |  |  |  | 988 | [10 empty] | 97.12 |  |  |  | 97.27 | [5 empty] | 97.72 |  |  | 97.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.73 |  |  |  |  | 0.15
2011 |  |  |  | 8183.75 |  |  | 8283 |  |  |  | 988 | [10 empty] | 93.90 |  |  |  | 93.94 | [5 empty] | 94.56 |  |  | 94.55 |  |  |  | 1.65 |  | 1.58 | [8 empty] | 4.48 |  |  |  |  | 0.04
2012 |  |  |  | 6244.61 |  |  | 6428 |  |  |  | 993 | [10 empty] | 71.41 |  |  |  | 71.60 | [5 empty] | 71.59 |  |  | 73.18 |  |  |  | 20.53 |  | 18.50 | [8 empty] | 9.89 |  |  |  |  | 0.19
2013 |  |  |  | 8191.47 |  |  | 8290 |  |  |  | 997 | [10 empty] | 93.81 |  |  |  | 94.29 | [5 empty] | 93.79 |  |  | 94.63 |  |  |  | 0.19 |  | 0.18 | [8 empty] | 5.53 |  |  |  |  | 0.47
2014 |  |  |  | 6918.10 |  |  | 6984 |  |  |  | 994 | [10 empty] | 79.19 |  |  |  | 79.30 | [5 empty] | 79.45 |  |  | 79.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.70 |  |  |  |  | 0.12
2015 |  |  |  | 7004.72 |  |  | 7122 |  |  |  | 994 | [10 empty] | 80.16 |  |  |  | 80.74 | [5 empty] | 80.45 |  |  | 81.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.26 |  |  |  |  | 0.57
2016 |  |  |  | 8671.06 |  |  | 8784 |  |  |  | 994 | [10 empty] | 99.31 |  |  |  | 100.00 | [5 empty] | 99.31 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.69
2017 |  |  |  | 6655.11 |  |  | 6783 |  |  |  | 994 | [10 empty] | 76.41 |  |  |  | 76.79 | [5 empty] | 76.43 |  |  | 77.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.21 |  |  |  |  | 0.38
2018 |  |  |  | 7265.08 |  |  | 7387 |  |  |  | 992 | [10 empty] | 83.43 |  |  |  | 83.76 | [5 empty] | 83.60 |  |  | 84.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.24 |  |  |  |  | 0.33
2019 |  |  |  | 8613.69 |  |  | 8709 |  |  |  | 992 | [10 empty] | 98.95 |  |  |  | 99.30 | [5 empty] | 99.12 |  |  | 99.42 |  |  |  | 0.69 |  | 0.69 | [8 empty] | 0.00 |  |  |  |  | 0.35
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2002 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 51 | [14 empty] | 118
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 931
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 23
E. |  | Testing of plant systems or components | [39 empty] | 2
Subtotal | [26 empty] | 51 | [10 empty] | 954 |  |  |  | 120
Total | [22 empty] | 51 | [14 empty] | 1074
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2002 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 2
16. |  |  | Steam generation systems | [34 empty] | 12
35. |  |  | All other I&C Systems | [34 empty] | 14
42. |  |  | Electrical Power Supply Systems | [19 empty] | 51 | [14 empty] | 77
Total | [22 empty] | 51 | [14 empty] | 117
Highlights (2019)
Turbine trip due to main transformer protective relay malfunction caused by lightning(2019-03-15)

## HANBIT-6
2019 Operating Experience
KR-18 | [8 empty] | HANBIT-6 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1997-11-20
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-09-16
Gross electrical power | [12 empty] | : |  |  | 1051 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-12-24
Reference unit power (net) | [12 empty] | : |  |  | 993 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 17 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 13450 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.124 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19.68 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6367.31 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 72.99 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 73.01 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 26.99 %
Load Factor (LF) | [18 empty] | : | 73.2 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.01 %
Operating Factor (OF) | [18 empty] | : | 73.58 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2314 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 740.18 | 668.75 |  |  |  | 740.76 |  | 716.45 | [8 empty] | 686.84 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 611.35 |  |  | 741.34 |  |  | 718.86 | [9 empty] | 742.78 |  |  | 6367.31
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 92.88 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 85.43 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 72.99
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 92.89 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 85.60 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 73.01
LF [%] |  |  |  |  | 100.19 | 100.22 |  |  |  | 100.27 |  | 100.21 | [8 empty] | 92.97 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 85.51 |  |  | 100.34 |  |  | 100.55 | [9 empty] | 100.54 |  |  | 73.20
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 94.89 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 90.56 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 73.58
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 7.11 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 14.40 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 26.99
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.17 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 128498.73 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.4 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.95 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.35 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.19 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.47 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.26 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.23 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.66 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 1058.41 |  |  | 1461 |  |  |  | 996 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 7652.19 |  |  | 7728 |  |  |  | 950 | [10 empty] | 88.21 |  |  |  | 88.21 | [5 empty] | 91.95 |  |  | 88.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.79 |  |  |  |  | 0.00
2004 |  |  |  | 6354.49 |  |  | 6449 |  |  |  | 950 | [10 empty] | 72.78 |  |  |  | 72.78 | [5 empty] | 76.15 |  |  | 73.42 |  |  |  | 0.82 |  | 0.60 | [8 empty] | 26.61 |  |  |  |  | 0.00
2005 |  |  |  | 7137.13 |  |  | 7906 |  |  |  | 950 | [10 empty] | 88.78 |  |  |  | 89.13 | [5 empty] | 85.76 |  |  | 90.25 |  |  |  | 1.12 |  | 1.01 | [8 empty] | 9.87 |  |  |  |  | 0.35
2006 |  |  |  | 7988.59 |  |  | 8064 |  |  |  | 993 | [10 empty] | 91.48 |  |  |  | 91.52 | [5 empty] | 91.84 |  |  | 92.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.48 |  |  |  |  | 0.03
2007 |  |  |  | 7859.23 |  |  | 7957 |  |  |  | 993 | [10 empty] | 90.14 |  |  |  | 90.35 | [5 empty] | 90.35 |  |  | 90.83 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 9.63 |  |  |  |  | 0.21
2008 |  |  |  | 7914.57 |  |  | 8073 |  |  |  | 996 | [10 empty] | 90.90 |  |  |  | 91.13 | [5 empty] | 90.46 |  |  | 91.91 |  |  |  | 0.66 |  | 0.61 | [8 empty] | 8.27 |  |  |  |  | 0.23
2009 |  |  |  | 8501.44 |  |  | 8606 |  |  |  | 996 | [10 empty] | 97.56 |  |  |  | 97.90 | [5 empty] | 97.44 |  |  | 98.24 |  |  |  | 0.95 |  | 0.94 | [8 empty] | 1.16 |  |  |  |  | 0.34
2010 |  |  |  | 7961.42 |  |  | 8060 |  |  |  | 996 | [10 empty] | 91.19 |  |  |  | 91.48 | [5 empty] | 91.25 |  |  | 92.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.52 |  |  |  |  | 0.29
2011 |  |  |  | 8090.64 |  |  | 8179 |  |  |  | 996 | [10 empty] | 92.65 |  |  |  | 92.90 | [5 empty] | 92.73 |  |  | 93.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.10 |  |  |  |  | 0.24
2012 |  |  |  | 7231.21 |  |  | 7325 |  |  |  | 993 | [10 empty] | 82.72 |  |  |  | 82.96 | [5 empty] | 82.90 |  |  | 83.39 |  |  |  | 2.12 |  | 1.80 | [8 empty] | 15.24 |  |  |  |  | 0.24
2013 |  |  |  | 8531.74 |  |  | 8631 |  |  |  | 995 | [10 empty] | 97.74 |  |  |  | 98.04 | [5 empty] | 97.88 |  |  | 98.53 |  |  |  | 0.89 |  | 0.88 | [8 empty] | 1.08 |  |  |  |  | 0.31
2014 |  |  |  | 7110.37 |  |  | 7235 |  |  |  | 993 | [10 empty] | 81.59 |  |  |  | 81.73 | [5 empty] | 81.74 |  |  | 82.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.27 |  |  |  |  | 0.14
2015 |  |  |  | 8006.79 |  |  | 8122 |  |  |  | 993 | [10 empty] | 91.92 |  |  |  | 92.48 | [5 empty] | 92.05 |  |  | 92.72 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 7.46 |  |  |  |  | 0.56
2016 |  |  |  | 7559.26 |  |  | 7667 |  |  |  | 993 | [10 empty] | 86.50 |  |  |  | 86.88 | [5 empty] | 86.66 |  |  | 87.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.12 |  |  |  |  | 0.38
2017 |  |  |  | 4576.12 |  |  | 4642 |  |  |  | 993 | [10 empty] | 52.57 |  |  |  | 52.82 | [5 empty] | 52.61 |  |  | 52.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 47.18 |  |  |  |  | 0.25
2018 |  |  |  | 7934.90 |  |  | 8042 |  |  |  | 993 | [10 empty] | 91.06 |  |  |  | 91.41 | [5 empty] | 91.22 |  |  | 91.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.59 |  |  |  |  | 0.36
2019 |  |  |  | 6367.31 |  |  | 6446 |  |  |  | 993 | [10 empty] | 72.99 |  |  |  | 73.01 | [5 empty] | 73.20 |  |  | 73.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.99 |  |  |  |  | 0.01
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2002 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 24
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2313 | [14 empty] | 1140
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 5
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 0
Subtotal | [22 empty] | 2313 | [14 empty] | 1145 |  |  |  | 24 | [11 empty] | 0
Total | [22 empty] | 2313 | [14 empty] | 1169
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2002 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 4
12. |  |  | Reactor I&C Systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [37 empty] | 24
Highlights (2019)
The twelveth Refueling & Maintenance from 2019-05-30 to 2019-09-03

## HANUL-1
2019 Operating Experience
KR-9 | [8 empty] | HANUL-1 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / France CPI | [11 empty] | Construction Date | [15 empty] | : |  |  | 1983-01-26
Thermal power | [12 empty] | : |  |  | 2775 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-04-07
Gross electrical power | [12 empty] | : |  |  | 1008 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-09-10
Reference unit power (net) | [12 empty] | : |  |  | 966 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.2
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 38 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 42500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.53
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.83 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 7060.57 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.22 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.33 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.67 %
Load Factor (LF) | [18 empty] | : | 83.44 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.11 %
Operating Factor (OF) | [18 empty] | : | 83.58 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1438 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 679.20 |  | 698.99 | [8 empty] | 721.91 |  |  | 697.86 | [6 empty] | 717.76 |  | 714.26 |  |  |  | 693.57 |  |  | 717.53 |  |  | 697.71 | [9 empty] | 721.78 |  |  | 7060.57
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 94.09 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.80 |  | 99.37 |  |  |  | 99.68 |  |  | 99.83 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.22
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 94.09 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.97 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.33
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 94.50 |  | 100.50 | [8 empty] | 100.45 |  |  | 100.34 | [6 empty] | 99.87 |  | 99.38 |  |  |  | 99.72 |  |  | 99.84 |  |  | 100.31 | [9 empty] | 100.43 |  |  | 83.44
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 97.04 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.58
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.03 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.03 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 5.91 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.67
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.20 |  | 0.60 |  |  |  | 0.32 |  |  | 0.17 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.11
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 221045.02 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.54 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.5 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.23 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.76 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.01 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.76 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.26 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.03 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | Data not provided
1989 |  |  |  | 5205.36 |  |  | 5821 |  |  |  | 920 | [10 empty] | 66.45 |  |  |  | 66.45 | [5 empty] | 64.59 |  |  | 66.45 |  |  |  | 15.49 |  | 12.18 | [8 empty] | 21.37 |  |  |  |  | 0.00
1990 |  |  |  | 6166.21 |  |  | 7156 |  |  |  | 920 | [10 empty] | 81.69 |  |  |  | 81.69 | [5 empty] | 76.51 |  |  | 81.69 |  |  |  | 1.16 |  | 0.96 | [8 empty] | 17.35 |  |  |  |  | 0.00
1991 |  |  |  | 7244.32 |  |  | 7970 |  |  |  | 920 | [10 empty] | 90.98 |  |  |  | 90.98 | [5 empty] | 89.89 |  |  | 90.98 |  |  |  | 2.19 |  | 2.04 | [8 empty] | 6.99 |  |  |  |  | 0.00
1992 |  |  |  | 7020.77 |  |  | 7675 |  |  |  | 920 | [10 empty] | 87.37 |  |  |  | 87.37 | [5 empty] | 86.88 |  |  | 87.37 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 12.59 |  |  |  |  | 0.00
1993 |  |  |  | 6977.60 |  |  | 7651 |  |  |  | 920 | [10 empty] | 87.34 |  |  |  | 87.34 | [5 empty] | 86.58 |  |  | 87.34 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 12.48 |  |  |  |  | 0.00
1994 |  |  |  | 6878.53 |  |  | 7293 |  |  |  | 890 | [10 empty] | 82.02 |  |  |  | 82.02 | [5 empty] | 88.23 |  |  | 83.25 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 17.97 |  |  |  |  | 0.00
1995 |  |  |  | 7153.82 |  |  | 7698 |  |  |  | 920 | [10 empty] | 85.73 |  |  |  | 85.73 | [5 empty] | 88.77 |  |  | 87.88 |  |  |  | 0.31 |  | 0.27 | [8 empty] | 14.00 |  |  |  |  | 0.00
1996 |  |  |  | 7113.66 |  |  | 7631 |  |  |  | 920 | [10 empty] | 85.42 |  |  |  | 85.63 | [5 empty] | 88.03 |  |  | 86.87 |  |  |  | 0.93 |  | 0.81 | [8 empty] | 13.56 |  |  |  |  | 0.21
1997 |  |  |  | 6801.00 |  |  | 7323 |  |  |  | 920 | [10 empty] | 82.25 |  |  |  | 83.72 | [5 empty] | 84.39 |  |  | 83.60 |  |  |  | 2.57 |  | 2.21 | [8 empty] | 14.07 |  |  |  |  | 1.46
1998 |  |  |  | 7642.97 |  |  | 8256 |  |  |  | 920 | [10 empty] | 91.45 |  |  |  | 94.06 | [5 empty] | 94.84 |  |  | 94.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.94 |  |  |  |  | 2.61
1999 |  |  |  | 7161.55 |  |  | 7639 |  |  |  | 920 | [10 empty] | 86.12 |  |  |  | 86.12 | [5 empty] | 88.86 |  |  | 87.20 |  |  |  | 0.53 |  | 0.46 | [8 empty] | 13.42 |  |  |  |  | 0.00
2000 |  |  |  | 7230.77 |  |  | 7736 |  |  |  | 920 | [10 empty] | 86.34 |  |  |  | 86.75 | [5 empty] | 89.48 |  |  | 88.07 |  |  |  | 0.23 |  | 0.20 | [8 empty] | 13.05 |  |  |  |  | 0.41
2001 |  |  |  | 7022.30 |  |  | 7483 |  |  |  | 920 | [10 empty] | 84.48 |  |  |  | 85.14 | [5 empty] | 87.13 |  |  | 85.42 |  |  |  | 7.14 |  | 6.55 | [8 empty] | 8.31 |  |  |  |  | 0.66
2002 |  |  |  | 5462.40 |  |  | 6052 |  |  |  | 920 | [10 empty] | 75.98 |  |  |  | 75.98 | [5 empty] | 67.78 |  |  | 69.09 |  |  |  | 24.01 |  | 24.01 | [8 empty] | 0.01 |  |  |  |  | 0.00
2003 |  |  |  | 6371.56 |  |  | 7446 |  |  |  | 920 | [10 empty] | 85.20 |  |  |  | 85.21 | [5 empty] | 79.06 |  |  | 85.00 |  |  |  | 0.35 |  | 0.30 | [8 empty] | 14.49 |  |  |  |  | 0.01
2004 |  |  |  | 7420.13 |  |  | 7970 |  |  |  | 920 | [10 empty] | 89.27 |  |  |  | 89.48 | [5 empty] | 91.82 |  |  | 90.73 |  |  |  | 0.55 |  | 0.50 | [8 empty] | 10.02 |  |  |  |  | 0.21
2005 |  |  |  | 8245.04 |  |  | 8760 |  |  |  | 920 | [10 empty] | 99.80 |  |  |  | 99.88 | [5 empty] | 102.31 |  |  | 100.00 |  |  |  | 0.11 |  | 0.11 | [8 empty] | 0.00 |  |  |  |  | 0.08
2006 |  |  |  | 7212.78 |  |  | 7769 |  |  |  | 939 | [10 empty] | 87.50 |  |  |  | 88.06 | [5 empty] | 87.69 |  |  | 88.69 |  |  |  | 0.82 |  | 0.73 | [8 empty] | 11.21 |  |  |  |  | 0.56
2007 |  |  |  | 7262.21 |  |  | 7747 |  |  |  | 940 | [10 empty] | 87.97 |  |  |  | 87.97 | [5 empty] | 88.19 |  |  | 88.44 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 11.98 |  |  |  |  | 0.00
2008 |  |  |  | 8177.42 |  |  | 8747 |  |  |  | 945 | [10 empty] | 99.14 |  |  |  | 99.19 | [5 empty] | 98.51 |  |  | 99.58 |  |  |  | 0.80 |  | 0.80 | [8 empty] | 0.00 |  |  |  |  | 0.06
2009 |  |  |  | 7493.10 |  |  | 8024 |  |  |  | 945 | [10 empty] | 90.99 |  |  |  | 90.99 | [5 empty] | 90.52 |  |  | 91.60 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 8.70 |  |  |  |  | 0.00
2010 |  |  |  | 7437.82 |  |  | 7988 |  |  |  | 945 | [10 empty] | 89.84 |  |  |  | 90.16 | [5 empty] | 89.85 |  |  | 91.19 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 9.78 |  |  |  |  | 0.32
2011 |  |  |  | 8206.10 |  |  | 8730 |  |  |  | 945 | [10 empty] | 99.13 |  |  |  | 99.40 | [5 empty] | 99.13 |  |  | 99.66 |  |  |  | 0.53 |  | 0.53 | [8 empty] | 0.07 |  |  |  |  | 0.27
2012 |  |  |  | 6640.08 |  |  | 6988 |  |  |  | 960 | [10 empty] | 78.86 |  |  |  | 78.90 | [5 empty] | 79.15 |  |  | 79.55 |  |  |  | 1.71 |  | 1.37 | [8 empty] | 19.73 |  |  |  |  | 0.04
2013 |  |  |  | 7233.32 |  |  | 7545 |  |  |  | 960 | [10 empty] | 85.54 |  |  |  | 85.57 | [5 empty] | 86.01 |  |  | 86.13 |  |  |  | 3.53 |  | 3.13 | [8 empty] | 11.29 |  |  |  |  | 0.03
2014 |  |  |  | 7762.26 |  |  | 8033 |  |  |  | 963 | [10 empty] | 91.49 |  |  |  | 91.49 | [5 empty] | 92.01 |  |  | 91.70 |  |  |  | 8.51 |  | 8.51 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 7458.09 |  |  | 7747 |  |  |  | 966 | [10 empty] | 87.88 |  |  |  | 87.96 | [5 empty] | 88.13 |  |  | 88.44 |  |  |  | 0.15 |  | 0.13 | [8 empty] | 11.91 |  |  |  |  | 0.08
2016 |  |  |  | 6901.60 |  |  | 7171 |  |  |  | 968 | [10 empty] | 81.13 |  |  |  | 81.34 | [5 empty] | 81.17 |  |  | 81.64 |  |  |  | 3.69 |  | 3.12 | [8 empty] | 15.54 |  |  |  |  | 0.21
2017 |  |  |  | 6351.26 |  |  | 6622 |  |  |  | 968 | [10 empty] | 74.90 |  |  |  | 75.34 | [5 empty] | 74.90 |  |  | 75.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.66 |  |  |  |  | 0.44
2018 |  |  |  | 5547.64 |  |  | 5770 |  |  |  | 966 | [10 empty] | 65.55 |  |  |  | 65.79 | [5 empty] | 65.56 |  |  | 65.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 34.21 |  |  |  |  | 0.24
2019 |  |  |  | 7060.57 |  |  | 7322 |  |  |  | 966 | [10 empty] | 83.22 |  |  |  | 83.33 | [5 empty] | 83.44 |  |  | 83.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.67 |  |  |  |  | 0.11
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1988 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 156
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1438 | [14 empty] | 1005
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 86
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 7
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Z. |  | Other | [51 empty] | 2
Subtotal | [22 empty] | 1438 | [14 empty] | 1091 |  |  |  | 163 | [11 empty] | 5
Total | [22 empty] | 1438 | [14 empty] | 1259
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1988 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 31
15. |  |  | Reactor Cooling Systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
33. |  |  | Circulating Water System | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 101
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [37 empty] | 164
Highlights (2019)
22nd Refueling(2018.08.29 ~ 2019.03.01)

## HANUL-2
2019 Operating Experience
KR-10 | [8 empty] | HANUL-3 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / France CPI | [11 empty] | Construction Date | [15 empty] | : |  |  | 1983-07-05
Thermal power | [12 empty] | : |  |  | 2775 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1989-04-14
Gross electrical power | [12 empty] | : |  |  | 1010 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-09-30
Reference unit power (net) | [12 empty] | : |  |  | 967 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.2
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 38 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 42500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.53
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.83 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6629.49 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.13 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 78.38 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.62 %
Load Factor (LF) | [18 empty] | : | 78.26 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.25 %
Operating Factor (OF) | [18 empty] | : | 78.47 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1886 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 720.67 | 651.08 |  |  |  | 721.23 |  | 698.44 | [8 empty] | 720.42 |  |  | 698.08 | [6 empty] | 717.87 |  | 714.02 |  |  |  | 692.74 |  |  | 294.95 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6629.49
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.79 |  |  | 100.00 | [6 empty] | 99.75 |  | 99.24 |  |  |  | 99.49 |  |  | 41.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 78.13
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.79 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 42.38 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 78.38
LF [%] |  |  |  |  | 100.17 | 100.19 |  |  |  | 100.25 |  | 100.32 | [8 empty] | 100.13 |  |  | 100.26 | [6 empty] | 99.78 |  | 99.25 |  |  |  | 99.50 |  |  | 41.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 78.26
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 43.28 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 78.47
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.21 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 57.62 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 21.62
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.25 |  | 0.76 |  |  |  | 0.51 |  |  | 1.38 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.25
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 217915.53 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.12 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.74 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.06 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.92 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.03 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.7 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.17 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.62 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | Data not provided
1990 |  |  |  | 5547.29 |  |  | 6395 |  |  |  | 920 | [10 empty] | 73.00 |  |  |  | 73.00 | [5 empty] | 68.83 |  |  | 73.00 |  |  |  | 0.27 |  | 0.19 | [8 empty] | 26.80 |  |  |  |  | 0.00
1991 |  |  |  | 6671.16 |  |  | 7603 |  |  |  | 920 | [10 empty] | 86.79 |  |  |  | 86.79 | [5 empty] | 82.78 |  |  | 86.79 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 13.16 |  |  |  |  | 0.00
1992 |  |  |  | 7076.88 |  |  | 7686 |  |  |  | 920 | [10 empty] | 87.50 |  |  |  | 87.50 | [5 empty] | 87.57 |  |  | 87.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.50 |  |  |  |  | 0.00
1993 |  |  |  | 7230.22 |  |  | 7693 |  |  |  | 920 | [10 empty] | 87.82 |  |  |  | 87.82 | [5 empty] | 89.71 |  |  | 87.82 |  |  |  | 0.16 |  | 0.14 | [8 empty] | 12.04 |  |  |  |  | 0.00
1994 |  |  |  | 6889.67 |  |  | 7315 |  |  |  | 890 | [10 empty] | 81.47 |  |  |  | 81.47 | [5 empty] | 88.37 |  |  | 83.50 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 18.38 |  |  |  |  | 0.00
1995 |  |  |  | 7810.26 |  |  | 8223 |  |  |  | 920 | [10 empty] | 93.39 |  |  |  | 93.42 | [5 empty] | 96.91 |  |  | 93.87 |  |  |  | 0.34 |  | 0.32 | [8 empty] | 6.26 |  |  |  |  | 0.03
1996 |  |  |  | 7696.38 |  |  | 8151 |  |  |  | 920 | [10 empty] | 91.05 |  |  |  | 91.27 | [5 empty] | 95.24 |  |  | 92.79 |  |  |  | 0.45 |  | 0.41 | [8 empty] | 8.32 |  |  |  |  | 0.22
1997 |  |  |  | 7055.18 |  |  | 7534 |  |  |  | 920 | [10 empty] | 84.27 |  |  |  | 85.99 | [5 empty] | 87.54 |  |  | 86.00 |  |  |  | 0.52 |  | 0.45 | [8 empty] | 13.56 |  |  |  |  | 1.72
1998 |  |  |  | 7388.87 |  |  | 7947 |  |  |  | 920 | [10 empty] | 88.33 |  |  |  | 88.48 | [5 empty] | 91.68 |  |  | 90.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.52 |  |  |  |  | 0.15
1999 |  |  |  | 7815.17 |  |  | 8748 |  |  |  | 920 | [10 empty] | 94.53 |  |  |  | 94.58 | [5 empty] | 96.97 |  |  | 99.86 |  |  |  | 5.17 |  | 5.16 | [8 empty] | 0.27 |  |  |  |  | 0.05
2000 |  |  |  | 6836.81 |  |  | 7330 |  |  |  | 920 | [10 empty] | 82.34 |  |  |  | 82.49 | [5 empty] | 84.60 |  |  | 83.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.51 |  |  |  |  | 0.15
2001 |  |  |  | 7268.56 |  |  | 7848 |  |  |  | 920 | [10 empty] | 89.18 |  |  |  | 90.16 | [5 empty] | 90.19 |  |  | 89.59 |  |  |  | 0.94 |  | 0.85 | [8 empty] | 8.99 |  |  |  |  | 0.97
2002 |  |  |  | 6485.83 |  |  | 6939 |  |  |  | 920 | [10 empty] | 78.26 |  |  |  | 78.26 | [5 empty] | 80.48 |  |  | 79.21 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 21.73 |  |  |  |  | 0.00
2003 |  |  |  | 7253.75 |  |  | 7686 |  |  |  | 920 | [10 empty] | 87.12 |  |  |  | 87.12 | [5 empty] | 90.01 |  |  | 87.74 |  |  |  | 12.87 |  | 12.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 7253.74 |  |  | 7888 |  |  |  | 920 | [10 empty] | 88.64 |  |  |  | 88.64 | [5 empty] | 89.76 |  |  | 89.80 |  |  |  | 1.53 |  | 1.38 | [8 empty] | 9.98 |  |  |  |  | 0.00
2005 |  |  |  | 6582.35 |  |  | 7218 |  |  |  | 920 | [10 empty] | 80.66 |  |  |  | 80.75 | [5 empty] | 81.68 |  |  | 82.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.25 |  |  |  |  | 0.09
2006 |  |  |  | 7882.51 |  |  | 8510 |  |  |  | 937 | [10 empty] | 96.69 |  |  |  | 97.03 | [5 empty] | 96.03 |  |  | 97.15 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 2.94 |  |  |  |  | 0.33
2007 |  |  |  | 7391.65 |  |  | 7946 |  |  |  | 937 | [10 empty] | 90.02 |  |  |  | 90.02 | [5 empty] | 90.05 |  |  | 90.71 |  |  |  | 1.06 |  | 0.96 | [8 empty] | 9.01 |  |  |  |  | 0.00
2008 |  |  |  | 7264.19 |  |  | 7752 |  |  |  | 942 | [10 empty] | 87.94 |  |  |  | 87.95 | [5 empty] | 87.79 |  |  | 88.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.05 |  |  |  |  | 0.01
2009 |  |  |  | 8258.31 |  |  | 8760 |  |  |  | 942 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.08 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 7506.86 |  |  | 7991 |  |  |  | 942 | [10 empty] | 90.81 |  |  |  | 90.86 | [5 empty] | 90.97 |  |  | 91.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.14 |  |  |  |  | 0.05
2011 |  |  |  | 6571.07 |  |  | 7003 |  |  |  | 942 | [10 empty] | 79.26 |  |  |  | 79.30 | [5 empty] | 79.63 |  |  | 79.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.70 |  |  |  |  | 0.04
2012 |  |  |  | 8325.47 |  |  | 8661 |  |  |  | 961 | [10 empty] | 98.33 |  |  |  | 98.36 | [5 empty] | 98.63 |  |  | 98.60 |  |  |  | 1.64 |  | 1.64 | [8 empty] | 0.00 |  |  |  |  | 0.03
2013 |  |  |  | 7446.49 |  |  | 7740 |  |  |  | 962 | [10 empty] | 87.98 |  |  |  | 87.98 | [5 empty] | 88.36 |  |  | 88.36 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 12.01 |  |  |  |  | 0.00
2014 |  |  |  | 7161.63 |  |  | 7430 |  |  |  | 965 | [10 empty] | 84.39 |  |  |  | 84.41 | [5 empty] | 84.72 |  |  | 84.82 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 15.50 |  |  |  |  | 0.02
2015 |  |  |  | 8449.96 |  |  | 8760 |  |  |  | 967 | [10 empty] | 99.35 |  |  |  | 99.38 | [5 empty] | 99.75 |  |  | 100.00 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.00 |  |  |  |  | 0.03
2016 |  |  |  | 7373.63 |  |  | 7665 |  |  |  | 969 | [10 empty] | 86.55 |  |  |  | 86.84 | [5 empty] | 86.63 |  |  | 87.26 |  |  |  | 0.00 |  | 2.00 | [8 empty] | 11.16 |  |  |  |  | 0.29
2017 |  |  |  | 7535.86 |  |  | 7858 |  |  |  | 969 | [10 empty] | 88.78 |  |  |  | 89.39 | [5 empty] | 88.78 |  |  | 89.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.61 |  |  |  |  | 0.60
2018 |  |  |  | 5046.21 |  |  | 5271 |  |  |  | 967 | [10 empty] | 59.55 |  |  |  | 59.71 | [5 empty] | 59.57 |  |  | 60.17 |  |  |  | 6.97 |  | 4.47 | [8 empty] | 35.82 |  |  |  |  | 0.16
2019 |  |  |  | 6629.49 |  |  | 6874 |  |  |  | 967 | [10 empty] | 78.13 |  |  |  | 78.38 | [5 empty] | 78.26 |  |  | 78.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.62 |  |  |  |  | 0.25
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1989 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 103
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1886 | [14 empty] | 1013
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 43
E. |  | Testing of plant systems or components | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
Z. |  | Other | [51 empty] | 3
Subtotal | [22 empty] | 1886 | [14 empty] | 1056 |  |  |  | 104 | [11 empty] | 6
Total | [22 empty] | 1886 | [14 empty] | 1166
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1989 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 0
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 62
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
33. |  |  | Circulating Water System | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 36
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [37 empty] | 110
Highlights (2019)
22nd Refueling(2019.10.14 ~ )

## HANUL-3
2019 Operating Experience
KR-13 | [8 empty] | HANUL-3 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1993-07-21
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1998-01-06
Gross electrical power | [12 empty] | : |  |  | 1049 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1998-08-11
Reference unit power (net) | [12 empty] | : |  |  | 997 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 21 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36.7 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45800 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.122 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.136
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6616.04 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 75.7 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 75.76 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 24.24 %
Load Factor (LF) | [18 empty] | : | 75.75 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.06 %
Operating Factor (OF) | [18 empty] | : | 76.34 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2073 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 742.94 | 670.55 |  |  |  | 741.73 |  | 717.78 | [8 empty] | 742.27 |  |  | 718.10 | [6 empty] | 740.57 |  | 738.45 |  |  |  | 19.07 |  |  | 0.00 |  |  | 41.36 | [9 empty] | 743.22 |  |  | 6616.04
EAF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 99.96 |  | 99.97 | [8 empty] | 99.99 |  |  | 99.97 | [6 empty] | 99.83 |  | 99.55 |  |  |  | 2.66 |  |  | 0.00 |  |  | 5.76 | [9 empty] | 100.00 |  |  | 75.70
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 2.66 |  |  | 0.00 |  |  | 5.76 | [9 empty] | 100.00 |  |  | 75.76
LF [%] |  |  |  |  | 100.16 | 100.08 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 100.07 |  |  | 100.04 | [6 empty] | 99.84 |  | 99.55 |  |  |  | 2.66 |  |  | 0.00 |  |  | 5.76 | [9 empty] | 100.20 |  |  | 75.75
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 4.72 |  |  | 0.00 |  |  | 10.69 | [9 empty] | 100.00 |  |  | 76.34
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 97.34 |  |  | 100.00 |  |  | 94.24 | [9 empty] | 0.00 |  |  | 24.24
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 0.01 |  |  | 0.02 | [6 empty] | 0.17 |  | 0.45 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.06
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 160430.18 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.46 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.15 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.42 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.33 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.25 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.09 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.19 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.9 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1998 |  |  |  | 4822.23 |  |  | 5872 |  |  |  | 960 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 99.17 |  |  | 97.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
1999 |  |  |  | 6918.04 |  |  | 7149 |  |  |  | 960 | [10 empty] | 79.67 |  |  |  | 81.45 | [5 empty] | 82.26 |  |  | 81.61 |  |  |  | 0.68 |  | 0.56 | [8 empty] | 17.99 |  |  |  |  | 1.78
2000 |  |  |  | 7489.09 |  |  | 7734 |  |  |  | 960 | [10 empty] | 86.99 |  |  |  | 86.99 | [5 empty] | 88.81 |  |  | 88.05 |  |  |  | 0.65 |  | 0.57 | [8 empty] | 12.44 |  |  |  |  | 0.00
2001 |  |  |  | 7922.21 |  |  | 8025 |  |  |  | 960 | [10 empty] | 91.25 |  |  |  | 91.25 | [5 empty] | 94.20 |  |  | 91.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.75 |  |  |  |  | 0.00
2002 |  |  |  | 7031.29 |  |  | 7824 |  |  |  | 960 | [10 empty] | 88.96 |  |  |  | 88.96 | [5 empty] | 83.61 |  |  | 89.32 |  |  |  | 0.13 |  | 0.11 | [8 empty] | 10.93 |  |  |  |  | 0.00
2003 |  |  |  | 7984.26 |  |  | 8758 |  |  |  | 960 | [10 empty] | 99.56 |  |  |  | 99.56 | [5 empty] | 94.94 |  |  | 99.98 |  |  |  | 0.00 |  | 0.43 | [8 empty] | 0.01 |  |  |  |  | 0.00
2004 |  |  |  | 7187.59 |  |  | 7986 |  |  |  | 960 | [10 empty] | 90.05 |  |  |  | 90.05 | [5 empty] | 85.24 |  |  | 90.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.95 |  |  |  |  | 0.00
2005 |  |  |  | 7651.74 |  |  | 7834 |  |  |  | 960 | [10 empty] | 87.58 |  |  |  | 87.73 | [5 empty] | 90.99 |  |  | 89.43 |  |  |  | 2.99 |  | 2.70 | [8 empty] | 9.57 |  |  |  |  | 0.15
2006 |  |  |  | 8425.90 |  |  | 8501 |  |  |  | 994 | [10 empty] | 96.60 |  |  |  | 96.60 | [5 empty] | 96.77 |  |  | 97.04 |  |  |  | 3.38 |  | 3.38 | [8 empty] | 0.01 |  |  |  |  | 0.00
2007 |  |  |  | 7901.94 |  |  | 7970 |  |  |  | 995 | [10 empty] | 90.35 |  |  |  | 90.35 | [5 empty] | 90.66 |  |  | 90.98 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 9.54 |  |  |  |  | 0.00
2008 |  |  |  | 8034.73 |  |  | 8122 |  |  |  | 994 | [10 empty] | 91.67 |  |  |  | 91.69 | [5 empty] | 92.02 |  |  | 92.46 |  |  |  | 0.98 |  | 0.91 | [8 empty] | 7.40 |  |  |  |  | 0.02
2009 |  |  |  | 8149.75 |  |  | 8225 |  |  |  | 994 | [10 empty] | 93.15 |  |  |  | 93.26 | [5 empty] | 93.60 |  |  | 93.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.74 |  |  |  |  | 0.10
2010 |  |  |  | 8740.74 |  |  | 8760 |  |  |  | 994 | [10 empty] | 99.93 |  |  |  | 99.94 | [5 empty] | 100.38 |  |  | 100.00 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 0.00 |  |  |  |  | 0.01
2011 |  |  |  | 7873.04 |  |  | 7960 |  |  |  | 994 | [10 empty] | 90.04 |  |  |  | 90.45 | [5 empty] | 90.42 |  |  | 90.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.55 |  |  |  |  | 0.41
2012 |  |  |  | 6056.35 |  |  | 6130 |  |  |  | 994 | [10 empty] | 69.08 |  |  |  | 69.17 | [5 empty] | 69.36 |  |  | 69.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.83 |  |  |  |  | 0.09
2013 |  |  |  | 8731.76 |  |  | 8760 |  |  |  | 994 | [10 empty] | 99.94 |  |  |  | 99.99 | [5 empty] | 100.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.06
2014 |  |  |  | 3609.51 |  |  | 3739 |  |  |  | 997 | [10 empty] | 41.31 |  |  |  | 41.77 | [5 empty] | 41.33 |  |  | 42.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 58.23 |  |  |  |  | 0.46
2015 |  |  |  | 8717.66 |  |  | 8760 |  |  |  | 997 | [10 empty] | 99.80 |  |  |  | 100.00 | [5 empty] | 99.82 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.20
2016 |  |  |  | 4601.49 |  |  | 4708 |  |  |  | 997 | [10 empty] | 52.54 |  |  |  | 52.74 | [5 empty] | 52.54 |  |  | 53.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 47.26 |  |  |  |  | 0.20
2017 |  |  |  | 8047.45 |  |  | 8122 |  |  |  | 997 | [10 empty] | 92.14 |  |  |  | 92.52 | [5 empty] | 92.14 |  |  | 92.72 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 7.46 |  |  |  |  | 0.38
2018 |  |  |  | 5868.02 |  |  | 5935 |  |  |  | 997 | [10 empty] | 67.11 |  |  |  | 67.21 | [5 empty] | 67.19 |  |  | 67.75 |  |  |  | 0.15 |  | 0.10 | [8 empty] | 32.69 |  |  |  |  | 0.10
2019 |  |  |  | 6616.04 |  |  | 6687 |  |  |  | 997 | [10 empty] | 75.70 |  |  |  | 75.76 | [5 empty] | 75.75 |  |  | 76.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.24 |  |  |  |  | 0.06
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1998 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 27
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2073 | [14 empty] | 1231
Subtotal | [22 empty] | 2073 | [14 empty] | 1231 |  |  |  | 27
Total | [22 empty] | 2073 | [14 empty] | 1258
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1998 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 11
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 14
Total | [37 empty] | 28
Highlights (2019)
15th refueling(2019-9-2 ~ 2019-11-27)

## HANUL-4
2019 Operating Experience
KR-14 | [8 empty] | HANUL-4 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1993-11-01
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1998-12-28
Gross electrical power | [12 empty] | : |  |  | 1053 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1999-12-31
Reference unit power (net) | [12 empty] | : |  |  | 999 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 21 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.52502
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46603 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.122 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.136
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 8344.45 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.31 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.54 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.44 %
Load Factor (LF) | [18 empty] | : | 95.35 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.24 %
Operating Factor (OF) | [18 empty] | : | 95.73 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 374 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 742.90 | 670.63 |  |  |  | 742.50 |  | 719.12 | [8 empty] | 743.71 |  |  | 719.34 | [6 empty] | 741.82 |  | 738.66 |  |  |  | 714.98 |  |  | 739.71 |  |  | 716.87 | [9 empty] | 354.22 |  |  | 8344.45
EAF [%] |  |  |  |  | 99.94 | 99.85 |  |  |  | 99.88 |  | 99.95 | [8 empty] | 100.00 |  |  | 99.96 | [6 empty] | 99.80 |  | 99.38 |  |  |  | 99.40 |  |  | 99.52 |  |  | 99.33 | [9 empty] | 47.65 |  |  | 95.31
UCF [%] |  |  |  |  | 99.98 | 99.96 |  |  |  | 99.88 |  | 99.95 | [8 empty] | 100.00 |  |  | 99.98 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.98 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 47.80 |  |  | 95.54
LF [%] |  |  |  |  | 99.95 | 99.90 |  |  |  | 99.90 |  | 99.98 | [8 empty] | 100.06 |  |  | 100.01 | [6 empty] | 99.81 |  | 99.38 |  |  |  | 99.40 |  |  | 99.52 |  |  | 99.67 | [9 empty] | 47.66 |  |  | 95.35
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 49.73 |  |  | 95.73
FLR [%] |  |  |  |  | 0.00 | 0.04 |  |  |  | 0.11 |  | 0.05 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
UCL [%] |  |  |  |  | 0.00 | 0.04 |  |  |  | 0.11 |  | 0.05 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
PUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 52.20 |  |  | 4.44
XUF [%] |  |  |  |  | 0.04 | 0.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.20 |  | 0.62 |  |  |  | 0.58 |  |  | 0.48 |  |  | 0.67 | [9 empty] | 0.15 |  |  | 0.24
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 148054.22 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.8 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.56 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.65 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.68 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.67 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.52 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.12 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.85 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1999 |  |  |  | Data not provided
2000 |  |  |  | 7042.47 |  |  | 7229 |  |  |  | 960 | [10 empty] | 81.26 |  |  |  | 81.26 | [5 empty] | 83.51 |  |  | 82.30 |  |  |  | 0.50 |  | 0.40 | [8 empty] | 18.33 |  |  |  |  | 0.00
2001 |  |  |  | 7732.33 |  |  | 7880 |  |  |  | 960 | [10 empty] | 89.94 |  |  |  | 89.99 | [5 empty] | 91.95 |  |  | 89.95 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 9.74 |  |  |  |  | 0.04
2002 |  |  |  | 7311.29 |  |  | 7448 |  |  |  | 960 | [10 empty] | 83.82 |  |  |  | 84.02 | [5 empty] | 86.94 |  |  | 85.02 |  |  |  | 0.82 |  | 0.70 | [8 empty] | 15.28 |  |  |  |  | 0.20
2003 |  |  |  | 7922.45 |  |  | 8081 |  |  |  | 960 | [10 empty] | 91.62 |  |  |  | 91.63 | [5 empty] | 94.21 |  |  | 92.25 |  |  |  | 0.96 |  | 0.89 | [8 empty] | 7.48 |  |  |  |  | 0.01
2004 |  |  |  | 8623.08 |  |  | 8700 |  |  |  | 960 | [10 empty] | 98.66 |  |  |  | 98.66 | [5 empty] | 102.26 |  |  | 99.04 |  |  |  | 1.33 |  | 1.33 | [8 empty] | 0.01 |  |  |  |  | 0.00
2005 |  |  |  | 8003.01 |  |  | 8085 |  |  |  | 960 | [10 empty] | 91.33 |  |  |  | 91.54 | [5 empty] | 95.17 |  |  | 92.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.46 |  |  |  |  | 0.21
2006 |  |  |  | 7886.16 |  |  | 7938 |  |  |  | 993 | [10 empty] | 89.80 |  |  |  | 89.80 | [5 empty] | 90.66 |  |  | 90.62 |  |  |  | 1.00 |  | 0.90 | [8 empty] | 9.30 |  |  |  |  | 0.00
2007 |  |  |  | 7912.85 |  |  | 7998 |  |  |  | 992 | [10 empty] | 90.34 |  |  |  | 90.97 | [5 empty] | 91.06 |  |  | 91.30 |  |  |  | 0.99 |  | 0.91 | [8 empty] | 8.12 |  |  |  |  | 0.63
2008 |  |  |  | 8762.75 |  |  | 8784 |  |  |  | 998 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 99.96 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2009 |  |  |  | 7924.37 |  |  | 8047 |  |  |  | 998 | [10 empty] | 90.61 |  |  |  | 90.61 | [5 empty] | 90.64 |  |  | 91.86 |  |  |  | 2.36 |  | 2.19 | [8 empty] | 7.20 |  |  |  |  | 0.00
2010 |  |  |  | 8110.60 |  |  | 8149 |  |  |  | 998 | [10 empty] | 92.59 |  |  |  | 92.61 | [5 empty] | 92.77 |  |  | 93.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.39 |  |  |  |  | 0.02
2011 |  |  |  | 6023.71 |  |  | 6034 |  |  |  | 998 | [10 empty] | 68.73 |  |  |  | 68.75 | [5 empty] | 68.90 |  |  | 68.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.25 |  |  |  |  | 0.02
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 998 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 3307.10 |  |  | 3362 |  |  |  | 998 | [10 empty] | 37.77 |  |  |  | 37.78 | [5 empty] | 37.83 |  |  | 38.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 62.22 |  |  |  |  | 0.01
2014 |  |  |  | 8570.94 |  |  | 8606 |  |  |  | 999 | [10 empty] | 97.87 |  |  |  | 98.00 | [5 empty] | 97.94 |  |  | 98.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.00 |  |  |  |  | 0.13
2015 |  |  |  | 7322.33 |  |  | 7412 |  |  |  | 999 | [10 empty] | 83.64 |  |  |  | 84.16 | [5 empty] | 83.67 |  |  | 84.61 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 15.83 |  |  |  |  | 0.53
2016 |  |  |  | 5274.95 |  |  | 6298 |  |  |  | 999 | [10 empty] | 60.11 |  |  |  | 60.12 | [5 empty] | 60.11 |  |  | 71.70 |  |  |  | 0.22 |  | 0.13 | [8 empty] | 39.75 |  |  |  |  | 0.01
2017 |  |  |  | 8198.68 |  |  | 8266 |  |  |  | 999 | [10 empty] | 93.62 |  |  |  | 93.76 | [5 empty] | 93.69 |  |  | 94.36 |  |  |  | 0.10 |  | 0.10 | [8 empty] | 6.14 |  |  |  |  | 0.14
2018 |  |  |  | 6698.25 |  |  | 6802 |  |  |  | 999 | [10 empty] | 76.53 |  |  |  | 76.72 | [5 empty] | 76.54 |  |  | 77.65 |  |  |  | 6.27 |  | 5.14 | [8 empty] | 18.14 |  |  |  |  | 0.19
2019 |  |  |  | 8344.45 |  |  | 8386 |  |  |  | 999 | [10 empty] | 95.31 |  |  |  | 95.54 | [5 empty] | 95.35 |  |  | 95.73 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 4.44 |  |  |  |  | 0.24
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1999 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 43
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 374 | [14 empty] | 693
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 8
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 845
L. |  | Human factor related | [39 empty] | 0
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Subtotal | [22 empty] | 374 | [14 empty] | 1546 |  |  |  | 43 | [11 empty] | 2
Total | [22 empty] | 374 | [14 empty] | 1591
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1999 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 24
41. |  |  | Main Generator Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [37 empty] | 47
Highlights (2019)
14th refueling(2019-12-16 ~ )

## HANUL-5
2019 Operating Experience
KR-19 | [8 empty] | HANUL-5 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1999-10-01
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2003-12-18
Gross electrical power | [12 empty] | : |  |  | 1048 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2004-07-29
Reference unit power (net) | [12 empty] | : |  |  | 998 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 16 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 5 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36.15 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38723 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.12 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.69 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 180 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6467.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 73.98 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.5 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.5 %
Load Factor (LF) | [18 empty] | : | 73.98 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.52 %
Operating Factor (OF) | [18 empty] | : | 75.06 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2185 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 739.47 | 668.17 |  |  |  | 739.30 |  | 716.46 | [8 empty] | 739.96 |  |  | 715.57 | [6 empty] | 736.47 |  | 733.14 |  |  |  | 559.43 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 119.71 |  |  | 6467.68
EAF [%] |  |  |  |  | 99.59 | 99.63 |  |  |  | 99.57 |  | 99.71 | [8 empty] | 99.66 |  |  | 99.58 | [6 empty] | 99.19 |  | 98.74 |  |  |  | 77.85 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 16.12 |  |  | 73.98
UCF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 79.74 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 16.14 |  |  | 74.50
LF [%] |  |  |  |  | 99.59 | 99.63 |  |  |  | 99.57 |  | 99.71 | [8 empty] | 99.66 |  |  | 99.58 | [6 empty] | 99.19 |  | 98.74 |  |  |  | 77.85 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 16.12 |  |  | 73.98
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 81.39 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 21.10 |  |  | 75.06
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 20.26 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 83.86 |  |  | 25.50
XUF [%] |  |  |  |  | 0.41 | 0.36 |  |  |  | 0.43 |  | 0.29 | [8 empty] | 0.33 |  |  | 0.42 | [6 empty] | 0.81 |  | 1.25 |  |  |  | 1.89 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 0.52
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 120095.83 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.08 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.59 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.99 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.77 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.24 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.54 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.18 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.78 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2004 |  |  |  | 4415.65 |  |  | 4963 |  |  |  | 960 | [10 empty] | 97.88 |  |  |  | 97.88 | [5 empty] | 101.42 |  |  | 97.93 |  |  |  | 2.11 |  | 2.11 | [8 empty] | 0.01 |  |  |  |  | 0.00
2005 |  |  |  | 7321.60 |  |  | 7409 |  |  |  | 960 | [10 empty] | 83.79 |  |  |  | 83.79 | [5 empty] | 87.06 |  |  | 84.58 |  |  |  | 2.77 |  | 2.39 | [8 empty] | 13.82 |  |  |  |  | 0.00
2006 |  |  |  | 7882.81 |  |  | 7925 |  |  |  | 994 | [10 empty] | 90.56 |  |  |  | 90.56 | [5 empty] | 90.53 |  |  | 90.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.44 |  |  |  |  | 0.00
2007 |  |  |  | 8025.93 |  |  | 8115 |  |  |  | 995 | [10 empty] | 91.87 |  |  |  | 91.87 | [5 empty] | 92.08 |  |  | 92.64 |  |  |  | 0.27 |  | 0.25 | [8 empty] | 7.88 |  |  |  |  | 0.00
2008 |  |  |  | 8763.82 |  |  | 8784 |  |  |  | 1001 | [10 empty] | 99.93 |  |  |  | 99.96 | [5 empty] | 99.67 |  |  | 100.00 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.01 |  |  |  |  | 0.03
2009 |  |  |  | 7924.16 |  |  | 7988 |  |  |  | 1001 | [10 empty] | 90.75 |  |  |  | 90.75 | [5 empty] | 90.37 |  |  | 91.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.25 |  |  |  |  | 0.00
2010 |  |  |  | 8160.25 |  |  | 8245 |  |  |  | 997 | [10 empty] | 93.24 |  |  |  | 93.70 | [5 empty] | 93.43 |  |  | 94.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.30 |  |  |  |  | 0.46
2011 |  |  |  | 8052.72 |  |  | 8106 |  |  |  | 997 | [10 empty] | 92.00 |  |  |  | 92.07 | [5 empty] | 92.20 |  |  | 92.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.92 |  |  |  |  | 0.08
2012 |  |  |  | 8773.91 |  |  | 8784 |  |  |  | 998 | [10 empty] | 99.91 |  |  |  | 99.96 | [5 empty] | 100.09 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  |  |  | 0.05
2013 |  |  |  | 7476.53 |  |  | 7544 |  |  |  | 996 | [10 empty] | 85.42 |  |  |  | 85.45 | [5 empty] | 85.69 |  |  | 86.12 |  |  |  | 2.20 |  | 1.92 | [8 empty] | 12.63 |  |  |  |  | 0.02
2014 |  |  |  | 7349.72 |  |  | 7408 |  |  |  | 998 | [10 empty] | 83.98 |  |  |  | 84.26 | [5 empty] | 84.07 |  |  | 84.57 |  |  |  | 2.95 |  | 2.56 | [8 empty] | 13.17 |  |  |  |  | 0.28
2015 |  |  |  | 8687.64 |  |  | 8742 |  |  |  | 998 | [10 empty] | 99.10 |  |  |  | 99.19 | [5 empty] | 99.37 |  |  | 99.79 |  |  |  | 0.18 |  | 0.18 | [8 empty] | 0.64 |  |  |  |  | 0.08
2016 |  |  |  | 6877.61 |  |  | 6961 |  |  |  | 998 | [10 empty] | 78.43 |  |  |  | 78.72 | [5 empty] | 78.45 |  |  | 79.25 |  |  |  | 3.94 |  | 3.23 | [8 empty] | 18.04 |  |  |  |  | 0.29
2017 |  |  |  | 6663.73 |  |  | 6707 |  |  |  | 998 | [10 empty] | 82.31 |  |  |  | 82.42 | [5 empty] | 76.22 |  |  | 76.56 |  |  |  | 17.58 |  | 17.58 | [8 empty] | 0.00 |  |  |  |  | 0.11
2018 |  |  |  | 6962.42 |  |  | 7097 |  |  |  | 998 | [10 empty] | 79.62 |  |  |  | 80.39 | [5 empty] | 79.64 |  |  | 81.02 |  |  |  | 0.12 |  | 1.64 | [8 empty] | 17.97 |  |  |  |  | 0.77
2019 |  |  |  | 6467.68 |  |  | 6575 |  |  |  | 998 | [10 empty] | 73.98 |  |  |  | 74.50 | [5 empty] | 73.98 |  |  | 75.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.50 |  |  |  |  | 0.52
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2004 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 166
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2188 | [14 empty] | 783
M. |  | Governmental requirements or court decisions | [51 empty] | 35
Subtotal | [22 empty] | 2188 | [14 empty] | 783 |  |  |  | 166 | [11 empty] | 35
Total | [22 empty] | 2188 | [14 empty] | 984
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2004 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 4
12. |  |  | Reactor I&C Systems | [34 empty] | 94
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 44
Total | [37 empty] | 159
Highlights (2019)
Refueling and Maintenance (2019.09.25~2019.12.25)

## HANUL-6
2019 Operating Experience
KR-20 | [8 empty] | HANUL-6 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2000-09-29
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2005-01-07
Gross electrical power | [12 empty] | : |  |  | 1048 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2005-04-22
Reference unit power (net) | [12 empty] | : |  |  | 997 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 14 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 5 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36.15 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38829 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.124 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.69 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 180 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6739.28 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.67 %
Energy Availability Factor (EAF) | [18 empty] | : | 77.09 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.52 %
Unit Capability Factor (UCF) | [18 empty] | : | 77.2 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 22.28 %
Load Factor (LF) | [18 empty] | : | 77.16 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.11 %
Operating Factor (OF) | [18 empty] | : | 78.12 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1917 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 184.17 |  | 720.43 | [8 empty] | 743.12 |  |  | 718.35 | [6 empty] | 739.23 |  | 718.03 |  |  |  | 715.36 |  |  | 740.62 |  |  | 718.18 | [9 empty] | 741.79 |  |  | 6739.28
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 24.76 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.97 | [6 empty] | 99.66 |  | 96.80 |  |  |  | 99.64 |  |  | 99.84 |  |  | 99.99 | [9 empty] | 99.92 |  |  | 77.09
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 24.76 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.98 | [6 empty] | 99.85 |  | 97.26 |  |  |  | 99.99 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 77.20
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 24.83 |  | 100.36 | [8 empty] | 100.18 |  |  | 100.07 | [6 empty] | 99.66 |  | 96.80 |  |  |  | 99.65 |  |  | 99.85 |  |  | 100.05 | [9 empty] | 100.00 |  |  | 77.16
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 32.66 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.12
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 11.51 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.15 |  | 2.74 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.67
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 3.22 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.15 |  | 2.74 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.52
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 72.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 22.28
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.20 |  | 0.46 |  |  |  | 0.35 |  |  | 0.16 |  |  | 0.01 | [9 empty] | 0.07 |  |  | 0.11
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 115594.29 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.76 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.22 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.69 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.93 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.32 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.16 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.71 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2005 |  |  |  | 6010.96 |  |  | 6041 |  |  |  | 960 | [10 empty] | 98.82 |  |  |  | 98.82 | [5 empty] | 102.65 |  |  | 99.06 |  |  |  | 1.18 |  | 1.18 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 7409.91 |  |  | 7543 |  |  |  | 991 | [10 empty] | 86.65 |  |  |  | 86.65 | [5 empty] | 85.36 |  |  | 86.11 |  |  |  | 0.38 |  | 0.33 | [8 empty] | 13.02 |  |  |  |  | 0.00
2007 |  |  |  | 7911.30 |  |  | 8022 |  |  |  | 994 | [10 empty] | 90.88 |  |  |  | 91.59 | [5 empty] | 90.86 |  |  | 91.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.41 |  |  |  |  | 0.72
2008 |  |  |  | 8107.89 |  |  | 8168 |  |  |  | 1001 | [10 empty] | 92.58 |  |  |  | 92.58 | [5 empty] | 92.21 |  |  | 92.99 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 7.41 |  |  |  |  | 0.00
2009 |  |  |  | 8694.52 |  |  | 8724 |  |  |  | 1001 | [10 empty] | 99.47 |  |  |  | 99.47 | [5 empty] | 99.15 |  |  | 99.59 |  |  |  | 0.52 |  | 0.52 | [8 empty] | 0.01 |  |  |  |  | 0.00
2010 |  |  |  | 7991.04 |  |  | 8055 |  |  |  | 997 | [10 empty] | 91.44 |  |  |  | 91.54 | [5 empty] | 91.50 |  |  | 91.95 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 8.45 |  |  |  |  | 0.10
2011 |  |  |  | 8090.56 |  |  | 8168 |  |  |  | 997 | [10 empty] | 92.53 |  |  |  | 92.64 | [5 empty] | 92.64 |  |  | 93.24 |  |  |  | 0.82 |  | 0.77 | [8 empty] | 6.59 |  |  |  |  | 0.11
2012 |  |  |  | 7703.15 |  |  | 7763 |  |  |  | 997 | [10 empty] | 87.81 |  |  |  | 87.92 | [5 empty] | 87.96 |  |  | 88.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.08 |  |  |  |  | 0.11
2013 |  |  |  | 8716.35 |  |  | 8760 |  |  |  | 996 | [10 empty] | 99.78 |  |  |  | 99.94 | [5 empty] | 99.90 |  |  | 100.00 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 0.00 |  |  |  |  | 0.16
2014 |  |  |  | 7734.99 |  |  | 7810 |  |  |  | 997 | [10 empty] | 88.47 |  |  |  | 88.57 | [5 empty] | 88.56 |  |  | 89.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.43 |  |  |  |  | 0.10
2015 |  |  |  | 6465.70 |  |  | 6545 |  |  |  | 997 | [10 empty] | 73.98 |  |  |  | 74.16 | [5 empty] | 74.03 |  |  | 74.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.84 |  |  |  |  | 0.18
2016 |  |  |  | 8765.47 |  |  | 8784 |  |  |  | 997 | [10 empty] | 99.85 |  |  |  | 100.00 | [5 empty] | 100.09 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.14
2017 |  |  |  | 6830.58 |  |  | 6928 |  |  |  | 997 | [10 empty] | 78.19 |  |  |  | 78.55 | [5 empty] | 78.21 |  |  | 79.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.45 |  |  |  |  | 0.36
2018 |  |  |  | 7343.97 |  |  | 7419 |  |  |  | 997 | [10 empty] | 84.08 |  |  |  | 84.40 | [5 empty] | 84.09 |  |  | 84.69 |  |  |  | 7.76 |  | 7.10 | [8 empty] | 8.51 |  |  |  |  | 0.31
2019 |  |  |  | 6739.28 |  |  | 6843 |  |  |  | 997 | [10 empty] | 77.09 |  |  |  | 77.20 | [5 empty] | 77.16 |  |  | 78.12 |  |  |  | 0.67 |  | 0.52 | [8 empty] | 22.28 |  |  |  |  | 0.11
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2005 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 57
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1920 | [14 empty] | 843
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
Subtotal | [22 empty] | 1920 | [14 empty] | 843 |  |  |  | 57 | [11 empty] | 3
Total | [22 empty] | 1920 | [14 empty] | 903
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2005 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
35. |  |  | All other I&C Systems | [34 empty] | 40
41. |  |  | Main Generator Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 6
Total | [37 empty] | 59
Highlights (2019)
Refueling and Maintenance(2018.12.01 ~ 2019.03.21)

## KORI-2
2019 Operating Experience
KR-2 | [8 empty] | KORI-2 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH F | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-12-23
Thermal power | [12 empty] | : |  |  | 1882 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-04-22
Gross electrical power | [12 empty] | : |  |  | 681 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-07-25
Reference unit power (net) | [12 empty] | : |  |  | 640 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 324.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 3
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 36946 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.35
| Active core height/length [m] | [13 empty] | : |  |  | 3.658 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.04 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 5620.15 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.92 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 100.25 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.06 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 478.78 | 432.55 |  |  |  | 478.91 |  | 463.38 | [8 empty] | 478.15 |  |  | 461.45 | [6 empty] | 476.21 |  | 474.07 |  |  |  | 459.64 |  |  | 476.65 |  |  | 462.81 | [9 empty] | 477.54 |  |  | 5620.15
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 99.99 |  |  | 99.94 | [6 empty] | 99.87 |  | 99.54 |  |  |  | 99.75 |  |  | 99.98 |  |  | 100.00 | [9 empty] | 99.95 |  |  | 99.92
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 99.99 |  |  | 99.94 | [6 empty] | 99.91 |  | 100.00 |  |  |  | 99.95 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.95 |  |  | 99.98
LF [%] |  |  |  |  | 100.55 | 100.57 |  |  |  | 100.58 |  | 100.56 | [8 empty] | 100.42 |  |  | 100.14 | [6 empty] | 100.01 |  | 99.56 |  |  |  | 99.75 |  |  | 100.10 |  |  | 100.44 | [9 empty] | 100.29 |  |  | 100.25
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.04 | [6 empty] | 0.09 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.04 | [6 empty] | 0.09 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.05 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.05 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.04 |  | 0.46 |  |  |  | 0.21 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.06
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 172551.22 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.78 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.51 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.55 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.85 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.6 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.75 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.34 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.3 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | Data not provided
1984 |  |  |  | 4086.38 |  |  | 6876 |  |  |  | 605 | [10 empty] | 76.10 |  |  |  | 76.10 | [5 empty] | 76.89 |  |  | 78.28 |  |  |  | 10.44 |  | 8.87 | [8 empty] | 15.03 |  |  |  |  | 0.00
1985 |  |  |  | 3731.40 |  |  | 6641 |  |  |  | 605 | [10 empty] | 69.83 |  |  |  | 69.83 | [5 empty] | 70.41 |  |  | 75.81 |  |  |  | 16.53 |  | 13.82 | [8 empty] | 16.35 |  |  |  |  | 0.00
1986 |  |  |  | 3945.20 |  |  | 6555 |  |  |  | 605 | [10 empty] | 74.83 |  |  |  | 75.22 | [5 empty] | 74.44 |  |  | 74.83 |  |  |  | 13.85 |  | 12.10 | [8 empty] | 12.68 |  |  |  |  | 0.40
1987 |  |  |  | 4265.44 |  |  | 7251 |  |  |  | 605 | [10 empty] | 81.64 |  |  |  | 82.07 | [5 empty] | 80.48 |  |  | 82.77 |  |  |  | 0.60 |  | 0.49 | [8 empty] | 17.43 |  |  |  |  | 0.43
1988 |  |  |  | 4504.67 |  |  | 7275 |  |  |  | 605 | [10 empty] | 82.82 |  |  |  | 82.82 | [5 empty] | 84.76 |  |  | 82.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.18 |  |  |  |  | 0.00
1989 |  |  |  | 5062.77 |  |  | 8387 |  |  |  | 605 | [10 empty] | 95.74 |  |  |  | 95.74 | [5 empty] | 95.53 |  |  | 95.74 |  |  |  | 3.94 |  | 3.93 | [8 empty] | 0.33 |  |  |  |  | 0.00
1990 |  |  |  | 4349.88 |  |  | 7381 |  |  |  | 605 | [10 empty] | 84.26 |  |  |  | 84.26 | [5 empty] | 82.08 |  |  | 84.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.74 |  |  |  |  | 0.00
1991 |  |  |  | 4553.98 |  |  | 7512 |  |  |  | 605 | [10 empty] | 85.75 |  |  |  | 85.75 | [5 empty] | 85.93 |  |  | 85.75 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 14.17 |  |  |  |  | 0.00
1992 |  |  |  | 4517.20 |  |  | 7469 |  |  |  | 605 | [10 empty] | 85.03 |  |  |  | 85.03 | [5 empty] | 85.00 |  |  | 85.03 |  |  |  | 0.64 |  | 0.55 | [8 empty] | 14.42 |  |  |  |  | 0.00
1993 |  |  |  | 4186.98 |  |  | 7048 |  |  |  | 605 | [10 empty] | 80.46 |  |  |  | 80.46 | [5 empty] | 79.00 |  |  | 80.46 |  |  |  | 0.85 |  | 0.69 | [8 empty] | 18.85 |  |  |  |  | 0.00
1994 |  |  |  | 4693.89 |  |  | 7685 |  |  |  | 605 | [10 empty] | 86.50 |  |  |  | 86.50 | [5 empty] | 88.57 |  |  | 87.73 |  |  |  | 0.35 |  | 0.30 | [8 empty] | 13.20 |  |  |  |  | 0.00
1995 |  |  |  | 5106.61 |  |  | 8370 |  |  |  | 605 | [10 empty] | 94.71 |  |  |  | 94.78 | [5 empty] | 96.35 |  |  | 95.55 |  |  |  | 0.78 |  | 0.75 | [8 empty] | 4.48 |  |  |  |  | 0.07
1996 |  |  |  | 4673.92 |  |  | 7668 |  |  |  | 605 | [10 empty] | 86.03 |  |  |  | 86.06 | [5 empty] | 87.95 |  |  | 87.30 |  |  |  | 0.29 |  | 0.25 | [8 empty] | 13.69 |  |  |  |  | 0.03
1997 |  |  |  | 4620.33 |  |  | 7639 |  |  |  | 605 | [10 empty] | 86.62 |  |  |  | 86.75 | [5 empty] | 87.18 |  |  | 87.20 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 13.24 |  |  |  |  | 0.14
1998 |  |  |  | 4697.63 |  |  | 7541 |  |  |  | 605 | [10 empty] | 84.87 |  |  |  | 84.87 | [5 empty] | 88.64 |  |  | 86.08 |  |  |  | 1.30 |  | 1.12 | [8 empty] | 14.01 |  |  |  |  | 0.00
1999 |  |  |  | 4672.24 |  |  | 7472 |  |  |  | 605 | [10 empty] | 83.62 |  |  |  | 83.62 | [5 empty] | 88.16 |  |  | 85.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.38 |  |  |  |  | 0.00
2000 |  |  |  | 4914.70 |  |  | 7812 |  |  |  | 605 | [10 empty] | 90.14 |  |  |  | 90.14 | [5 empty] | 92.48 |  |  | 88.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.85 |  |  |  |  | 0.00
2001 |  |  |  | 4807.76 |  |  | 7650 |  |  |  | 605 | [10 empty] | 87.29 |  |  |  | 87.29 | [5 empty] | 90.72 |  |  | 87.33 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 12.69 |  |  |  |  | 0.00
2002 |  |  |  | 5051.22 |  |  | 7982 |  |  |  | 605 | [10 empty] | 90.63 |  |  |  | 90.63 | [5 empty] | 95.31 |  |  | 91.12 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 9.36 |  |  |  |  | 0.00
2003 |  |  |  | 4844.24 |  |  | 7709 |  |  |  | 605 | [10 empty] | 85.43 |  |  |  | 86.52 | [5 empty] | 91.40 |  |  | 88.00 |  |  |  | 1.24 |  | 1.09 | [8 empty] | 12.40 |  |  |  |  | 1.09
2004 |  |  |  | 5501.54 |  |  | 8602 |  |  |  | 605 | [10 empty] | 97.84 |  |  |  | 97.84 | [5 empty] | 103.52 |  |  | 97.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.16 |  |  |  |  | 0.00
2005 |  |  |  | 5151.51 |  |  | 8080 |  |  |  | 605 | [10 empty] | 92.05 |  |  |  | 92.05 | [5 empty] | 97.20 |  |  | 92.24 |  |  |  | 2.02 |  | 1.89 | [8 empty] | 6.06 |  |  |  |  | 0.00
2006 |  |  |  | 5099.16 |  |  | 7984 |  |  |  | 637 | [10 empty] | 90.79 |  |  |  | 90.79 | [5 empty] | 91.38 |  |  | 91.14 |  |  |  | 1.42 |  | 1.31 | [8 empty] | 7.90 |  |  |  |  | 0.00
2007 |  |  |  | 5011.02 |  |  | 7886 |  |  |  | 637 | [10 empty] | 89.21 |  |  |  | 89.23 | [5 empty] | 89.80 |  |  | 90.02 |  |  |  | 3.82 |  | 3.54 | [8 empty] | 7.23 |  |  |  |  | 0.01
2008 |  |  |  | 4933.94 |  |  | 7771 |  |  |  | 637 | [10 empty] | 87.64 |  |  |  | 87.64 | [5 empty] | 88.18 |  |  | 88.47 |  |  |  | 0.60 |  | 0.53 | [8 empty] | 11.83 |  |  |  |  | 0.00
2009 |  |  |  | 5176.87 |  |  | 8110 |  |  |  | 637 | [10 empty] | 92.18 |  |  |  | 92.18 | [5 empty] | 92.77 |  |  | 92.58 |  |  |  | 1.55 |  | 1.45 | [8 empty] | 6.37 |  |  |  |  | 0.00
2010 |  |  |  | 5025.59 |  |  | 7921 |  |  |  | 637 | [10 empty] | 90.04 |  |  |  | 90.04 | [5 empty] | 90.06 |  |  | 90.42 |  |  |  | 0.46 |  | 0.42 | [8 empty] | 9.55 |  |  |  |  | 0.00
2011 |  |  |  | 5497.79 |  |  | 8578 |  |  |  | 637 | [10 empty] | 97.78 |  |  |  | 97.78 | [5 empty] | 98.52 |  |  | 97.92 |  |  |  | 2.21 |  | 2.21 | [8 empty] | 0.01 |  |  |  |  | 0.00
2012 |  |  |  | 4703.69 |  |  | 7606 |  |  |  | 637 | [10 empty] | 84.03 |  |  |  | 84.03 | [5 empty] | 84.06 |  |  | 86.59 |  |  |  | 0.57 |  | 0.48 | [8 empty] | 15.49 |  |  |  |  | 0.00
2013 |  |  |  | 4501.64 |  |  | 7118 |  |  |  | 639 | [10 empty] | 80.28 |  |  |  | 80.31 | [5 empty] | 80.42 |  |  | 81.26 |  |  |  | 0.79 |  | 0.64 | [8 empty] | 19.05 |  |  |  |  | 0.03
2014 |  |  |  | 5127.37 |  |  | 8035 |  |  |  | 640 | [10 empty] | 91.22 |  |  |  | 99.99 | [5 empty] | 91.46 |  |  | 91.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 8.77
2015 |  |  |  | 4446.10 |  |  | 6923 |  |  |  | 640 | [10 empty] | 78.67 |  |  |  | 78.84 | [5 empty] | 79.30 |  |  | 79.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.16 |  |  |  |  | 0.16
2016 |  |  |  | 3769.97 |  |  | 5935 |  |  |  | 640 | [10 empty] | 66.84 |  |  |  | 67.22 | [5 empty] | 67.06 |  |  | 67.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.78 |  |  |  |  | 0.38
2017 |  |  |  | 5631.94 |  |  | 8760 |  |  |  | 640 | [10 empty] | 99.95 |  |  |  | 99.99 | [5 empty] | 100.46 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.04
2018 |  |  |  | 2694.13 |  |  | 4356 |  |  |  | 640 | [10 empty] | 47.84 |  |  |  | 48.12 | [5 empty] | 48.05 |  |  | 49.73 |  |  |  | 0.08 |  | 0.04 | [8 empty] | 51.84 |  |  |  |  | 0.28
2019 |  |  |  | 5620.15 |  |  | 8760 |  |  |  | 640 | [10 empty] | 99.92 |  |  |  | 99.98 | [5 empty] | 100.25 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.01 |  |  |  |  | 0.06
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1983 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 103
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1015
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 27
E. |  | Testing of plant systems or components | [39 empty] | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 20
Subtotal | [37 empty] | 1042 |  |  |  | 106 | [11 empty] | 24
Total | [22 empty] | 0 | [14 empty] | 1172
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1983 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 16
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 9
16. |  |  | Steam generation systems | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 31
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
33. |  |  | Circulating Water System | [34 empty] | 20
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 31
42. |  |  | Electrical Power Supply Systems | [34 empty] | 6
Total | [37 empty] | 125

## KORI-3
2019 Operating Experience
KR-5 | [8 empty] | KORI-3 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH F | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-10-01
Thermal power | [12 empty] | : |  |  | 2912 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-01-22
Gross electrical power | [12 empty] | : |  |  | 1045 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-09-30
Reference unit power (net) | [12 empty] | : |  |  | 1011 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.5 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 41 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 17910 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.53
| Active core height/length [m] | [13 empty] | : |  |  | 3.658 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 151 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.83 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6008.1 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 67.75 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 67.93 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 32.05 %
Load Factor (LF) | [18 empty] | : | 67.84 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.19 %
Operating Factor (OF) | [18 empty] | : | 68.06 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2798 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 753.79 | 680.30 |  |  |  | 754.00 |  | 728.88 | [8 empty] | 753.38 |  |  | 727.35 | [6 empty] | 750.53 |  | 744.59 |  |  |  | 115.28 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6008.10
EAF [%] |  |  |  |  | 99.98 | 99.91 |  |  |  | 100.00 |  | 99.91 | [8 empty] | 100.00 |  |  | 99.90 | [6 empty] | 99.77 |  | 98.99 |  |  |  | 15.84 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 67.75
UCF [%] |  |  |  |  | 99.98 | 99.91 |  |  |  | 100.00 |  | 99.91 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 16.71 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 67.93
LF [%] |  |  |  |  | 100.21 | 100.13 |  |  |  | 100.24 |  | 100.13 | [8 empty] | 100.16 |  |  | 99.92 | [6 empty] | 99.78 |  | 98.99 |  |  |  | 15.84 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 67.84
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 18.06 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 68.06
FLR [%] |  |  |  |  | 0.02 | 0.08 |  |  |  | 0.00 |  | 0.09 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
UCL [%] |  |  |  |  | 0.02 | 0.08 |  |  |  | 0.00 |  | 0.09 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 83.29 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 32.05
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.10 | [6 empty] | 0.23 |  | 1.01 |  |  |  | 0.88 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.19
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 240860.11 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.06 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.9 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.89 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.97 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.14 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.77 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.07 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.54 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | Data not provided
1986 |  |  |  | 5611.72 |  |  | 6529 |  |  |  | 895 | [10 empty] | 73.32 |  |  |  | 73.32 | [5 empty] | 71.58 |  |  | 74.53 |  |  |  | 5.41 |  | 4.20 | [8 empty] | 22.48 |  |  |  |  | 0.00
1987 |  |  |  | 5804.81 |  |  | 6665 |  |  |  | 895 | [10 empty] | 78.78 |  |  |  | 79.12 | [5 empty] | 74.04 |  |  | 76.08 |  |  |  | 2.13 |  | 1.72 | [8 empty] | 19.16 |  |  |  |  | 0.34
1988 |  |  |  | 6119.71 |  |  | 7005 |  |  |  | 895 | [10 empty] | 79.75 |  |  |  | 79.75 | [5 empty] | 77.84 |  |  | 79.75 |  |  |  | 0.38 |  | 0.31 | [8 empty] | 19.95 |  |  |  |  | 0.00
1989 |  |  |  | 6591.97 |  |  | 7206 |  |  |  | 895 | [10 empty] | 82.26 |  |  |  | 82.26 | [5 empty] | 84.08 |  |  | 82.26 |  |  |  | 1.89 |  | 1.59 | [8 empty] | 16.15 |  |  |  |  | 0.00
1990 |  |  |  | 6838.13 |  |  | 7923 |  |  |  | 895 | [10 empty] | 90.45 |  |  |  | 90.45 | [5 empty] | 87.22 |  |  | 90.45 |  |  |  | 1.57 |  | 1.44 | [8 empty] | 8.12 |  |  |  |  | 0.00
1991 |  |  |  | 5902.46 |  |  | 6578 |  |  |  | 895 | [10 empty] | 75.09 |  |  |  | 75.09 | [5 empty] | 75.28 |  |  | 75.09 |  |  |  | 10.59 |  | 8.89 | [8 empty] | 16.02 |  |  |  |  | 0.00
1992 |  |  |  | 6746.17 |  |  | 7349 |  |  |  | 895 | [10 empty] | 83.66 |  |  |  | 83.66 | [5 empty] | 85.81 |  |  | 83.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.34 |  |  |  |  | 0.00
1993 |  |  |  | 7121.81 |  |  | 7721 |  |  |  | 895 | [10 empty] | 88.14 |  |  |  | 88.14 | [5 empty] | 90.84 |  |  | 88.14 |  |  |  | 1.37 |  | 1.22 | [8 empty] | 10.63 |  |  |  |  | 0.00
1994 |  |  |  | 6545.31 |  |  | 7128 |  |  |  | 890 | [10 empty] | 79.18 |  |  |  | 79.35 | [5 empty] | 83.95 |  |  | 81.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.65 |  |  |  |  | 0.16
1995 |  |  |  | 6015.47 |  |  | 6863 |  |  |  | 895 | [10 empty] | 73.75 |  |  |  | 73.75 | [5 empty] | 76.73 |  |  | 78.34 |  |  |  | 0.66 |  | 0.49 | [8 empty] | 25.76 |  |  |  |  | 0.00
1996 |  |  |  | 7939.72 |  |  | 8431 |  |  |  | 895 | [10 empty] | 95.42 |  |  |  | 95.42 | [5 empty] | 100.99 |  |  | 95.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.58 |  |  |  |  | 0.00
1997 |  |  |  | 6051.91 |  |  | 6503 |  |  |  | 895 | [10 empty] | 73.82 |  |  |  | 73.82 | [5 empty] | 77.19 |  |  | 74.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.18 |  |  |  |  | 0.00
1998 |  |  |  | 6902.53 |  |  | 7325 |  |  |  | 895 | [10 empty] | 82.78 |  |  |  | 82.86 | [5 empty] | 88.04 |  |  | 83.62 |  |  |  | 3.30 |  | 2.83 | [8 empty] | 14.32 |  |  |  |  | 0.08
1999 |  |  |  | 7231.82 |  |  | 7615 |  |  |  | 895 | [10 empty] | 86.30 |  |  |  | 86.30 | [5 empty] | 92.24 |  |  | 86.93 |  |  |  | 0.21 |  | 0.18 | [8 empty] | 13.52 |  |  |  |  | 0.00
2000 |  |  |  | 8094.33 |  |  | 8399 |  |  |  | 895 | [10 empty] | 95.59 |  |  |  | 95.59 | [5 empty] | 102.96 |  |  | 95.62 |  |  |  | 0.32 |  | 0.31 | [8 empty] | 4.10 |  |  |  |  | 0.00
2001 |  |  |  | 7570.25 |  |  | 7881 |  |  |  | 895 | [10 empty] | 89.41 |  |  |  | 89.41 | [5 empty] | 96.56 |  |  | 89.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.59 |  |  |  |  | 0.00
2002 |  |  |  | 7684.80 |  |  | 8062 |  |  |  | 895 | [10 empty] | 90.93 |  |  |  | 90.93 | [5 empty] | 98.02 |  |  | 92.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.07 |  |  |  |  | 0.00
2003 |  |  |  | 8387.43 |  |  | 8689 |  |  |  | 895 | [10 empty] | 99.05 |  |  |  | 100.00 | [5 empty] | 106.98 |  |  | 99.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.95
2004 |  |  |  | 7312.46 |  |  | 7630 |  |  |  | 895 | [10 empty] | 86.55 |  |  |  | 86.55 | [5 empty] | 93.01 |  |  | 86.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.45 |  |  |  |  | 0.00
2005 |  |  |  | 7562.17 |  |  | 7885 |  |  |  | 895 | [10 empty] | 89.44 |  |  |  | 89.44 | [5 empty] | 96.45 |  |  | 90.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.56 |  |  |  |  | 0.00
2006 |  |  |  | 7461.77 |  |  | 7813 |  |  |  | 963 | [10 empty] | 88.28 |  |  |  | 88.28 | [5 empty] | 88.45 |  |  | 89.19 |  |  |  | 1.82 |  | 1.63 | [8 empty] | 10.08 |  |  |  |  | 0.00
2007 |  |  |  | 8214.16 |  |  | 8503 |  |  |  | 964 | [10 empty] | 96.40 |  |  |  | 96.40 | [5 empty] | 97.27 |  |  | 97.07 |  |  |  | 0.49 |  | 0.47 | [8 empty] | 3.12 |  |  |  |  | 0.00
2008 |  |  |  | 7564.39 |  |  | 7854 |  |  |  | 979 | [10 empty] | 88.80 |  |  |  | 88.88 | [5 empty] | 87.96 |  |  | 89.41 |  |  |  | 2.00 |  | 1.82 | [8 empty] | 9.30 |  |  |  |  | 0.08
2009 |  |  |  | 7599.62 |  |  | 7820 |  |  |  | 1007 | [10 empty] | 88.99 |  |  |  | 88.99 | [5 empty] | 88.40 |  |  | 89.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.00 |  |  |  |  | 0.00
2010 |  |  |  | 8799.70 |  |  | 8732 |  |  |  | 1007 | [10 empty] | 99.56 |  |  |  | 99.56 | [5 empty] | 99.75 |  |  | 99.68 |  |  |  | 0.44 |  | 0.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8025.13 |  |  | 7971 |  |  |  | 1011 | [10 empty] | 90.57 |  |  |  | 90.57 | [5 empty] | 90.61 |  |  | 90.99 |  |  |  | 2.77 |  | 2.58 | [8 empty] | 6.85 |  |  |  |  | 0.00
2012 |  |  |  | 6933.06 |  |  | 6875 |  |  |  | 1011 | [10 empty] | 77.89 |  |  |  | 77.97 | [5 empty] | 78.07 |  |  | 78.27 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 22.02 |  |  |  |  | 0.09
2013 |  |  |  | 8861.52 |  |  | 8760 |  |  |  | 1011 | [10 empty] | 99.93 |  |  |  | 100.00 | [5 empty] | 100.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.07
2014 |  |  |  | 7384.18 |  |  | 7332 |  |  |  | 1011 | [10 empty] | 83.33 |  |  |  | 83.39 | [5 empty] | 83.38 |  |  | 83.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.61 |  |  |  |  | 0.07
2015 |  |  |  | 7155.51 |  |  | 7119 |  |  |  | 1011 | [10 empty] | 80.70 |  |  |  | 80.74 | [5 empty] | 80.80 |  |  | 81.27 |  |  |  | 0.28 |  | 0.23 | [8 empty] | 19.04 |  |  |  |  | 0.04
2016 |  |  |  | 8860.96 |  |  | 8784 |  |  |  | 1011 | [10 empty] | 99.77 |  |  |  | 100.00 | [5 empty] | 99.78 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.23
2017 |  |  |  | 432.36 |  |  | 442 |  |  |  | 1011 | [10 empty] | 4.88 |  |  |  | 4.96 | [5 empty] | 4.88 |  |  | 5.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 95.04 |  |  |  |  | 0.07
2018 |  |  |  | 5606.18 |  |  | 5610 |  |  |  | 1011 | [10 empty] | 63.27 |  |  |  | 63.43 | [5 empty] | 63.30 |  |  | 64.04 |  |  |  | 0.61 |  | 0.39 | [8 empty] | 36.17 |  |  |  |  | 0.17
2019 |  |  |  | 6008.10 |  |  | 5962 |  |  |  | 1011 | [10 empty] | 67.75 |  |  |  | 67.93 | [5 empty] | 67.84 |  |  | 68.06 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 32.05 |  |  |  |  | 0.19
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1985 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 69
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2798 | [14 empty] | 1303
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 18
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 27
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 8
Subtotal | [22 empty] | 2798 | [14 empty] | 1348 |  |  |  | 81 | [11 empty] | 3
Total | [22 empty] | 2798 | [14 empty] | 1432
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1985 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 11
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
15. |  |  | Reactor Cooling Systems | [34 empty] | 2
16. |  |  | Steam generation systems | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 12
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 30
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 78
Highlights (2019)
25th Refueling and Maintenance(2019.9.6. ~ )

## KORI-4
2019 Operating Experience
KR-6 | [8 empty] | KORI-4 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH F | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-04-01
Thermal power | [12 empty] | : |  |  | 2912 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-12-31
Gross electrical power | [12 empty] | : |  |  | 1045 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-04-29
Reference unit power (net) | [12 empty] | : |  |  | 1012 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.5 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 41 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 18210 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.53
| Active core height/length [m] | [13 empty] | : |  |  | 3.658 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 151 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.83 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 4521.89 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.59 %
Energy Availability Factor (EAF) | [18 empty] | : | 50.96 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.82 %
Unit Capability Factor (UCF) | [18 empty] | : | 50.97 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 48.21 %
Load Factor (LF) | [18 empty] | : | 51.01 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 51.89 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4214 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 753.76 | 609.28 |  |  |  | 753.88 |  | 729.46 | [8 empty] | 753.34 |  |  | 726.89 | [6 empty] | 195.28 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4521.89
EAF [%] |  |  |  |  | 100.00 | 89.50 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.73 | [6 empty] | 25.93 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 50.96
UCF [%] |  |  |  |  | 100.00 | 89.50 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.78 | [6 empty] | 25.94 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 50.97
LF [%] |  |  |  |  | 100.11 | 89.59 |  |  |  | 100.13 |  | 100.11 | [8 empty] | 100.06 |  |  | 99.76 | [6 empty] | 25.94 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 51.01
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 27.15 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 51.89
FLR [%] |  |  |  |  | 0.00 | 10.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.22 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.59
UCL [%] |  |  |  |  | 0.00 | 10.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.22 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.82
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 74.06 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 48.21
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.05 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 241313.46 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.62 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.42 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.05 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.3 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.14 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.88 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | Data not provided
1987 |  |  |  | 5860.82 |  |  | 6707 |  |  |  | 895 | [10 empty] | 78.01 |  |  |  | 78.27 | [5 empty] | 74.75 |  |  | 76.56 |  |  |  | 0.53 |  | 0.42 | [8 empty] | 21.31 |  |  |  |  | 0.26
1988 |  |  |  | 5909.08 |  |  | 7006 |  |  |  | 895 | [10 empty] | 79.76 |  |  |  | 80.70 | [5 empty] | 75.16 |  |  | 79.76 |  |  |  | 0.34 |  | 0.27 | [8 empty] | 19.02 |  |  |  |  | 0.94
1989 |  |  |  | 6177.37 |  |  | 6763 |  |  |  | 895 | [10 empty] | 77.20 |  |  |  | 77.20 | [5 empty] | 78.79 |  |  | 77.20 |  |  |  | 0.19 |  | 0.15 | [8 empty] | 22.65 |  |  |  |  | 0.00
1990 |  |  |  | 6230.03 |  |  | 7140 |  |  |  | 895 | [10 empty] | 81.51 |  |  |  | 81.51 | [5 empty] | 79.46 |  |  | 81.51 |  |  |  | 1.08 |  | 0.89 | [8 empty] | 17.60 |  |  |  |  | 0.00
1991 |  |  |  | 6353.02 |  |  | 7011 |  |  |  | 895 | [10 empty] | 80.03 |  |  |  | 80.44 | [5 empty] | 81.03 |  |  | 80.03 |  |  |  | 1.18 |  | 0.96 | [8 empty] | 18.60 |  |  |  |  | 0.41
1992 |  |  |  | 6652.32 |  |  | 7266 |  |  |  | 895 | [10 empty] | 82.72 |  |  |  | 82.72 | [5 empty] | 84.62 |  |  | 82.72 |  |  |  | 0.68 |  | 0.57 | [8 empty] | 16.71 |  |  |  |  | 0.00
1993 |  |  |  | 6835.92 |  |  | 7456 |  |  |  | 895 | [10 empty] | 85.11 |  |  |  | 85.11 | [5 empty] | 87.19 |  |  | 85.11 |  |  |  | 1.51 |  | 1.30 | [8 empty] | 13.59 |  |  |  |  | 0.00
1994 |  |  |  | 7455.10 |  |  | 8160 |  |  |  | 890 | [10 empty] | 90.02 |  |  |  | 90.05 | [5 empty] | 95.62 |  |  | 93.15 |  |  |  | 0.50 |  | 0.46 | [8 empty] | 9.50 |  |  |  |  | 0.03
1995 |  |  |  | 6950.57 |  |  | 7824 |  |  |  | 890 | [10 empty] | 89.31 |  |  |  | 89.31 | [5 empty] | 89.15 |  |  | 89.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.69 |  |  |  |  | 0.01
1996 |  |  |  | 6678.43 |  |  | 7147 |  |  |  | 895 | [10 empty] | 80.04 |  |  |  | 80.04 | [5 empty] | 84.95 |  |  | 81.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.96 |  |  |  |  | 0.00
1997 |  |  |  | 7014.21 |  |  | 7450 |  |  |  | 895 | [10 empty] | 84.36 |  |  |  | 84.36 | [5 empty] | 89.46 |  |  | 85.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.64 |  |  |  |  | 0.00
1998 |  |  |  | 8433.70 |  |  | 8760 |  |  |  | 895 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 107.57 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 7128.95 |  |  | 7451 |  |  |  | 895 | [10 empty] | 84.56 |  |  |  | 84.56 | [5 empty] | 90.93 |  |  | 85.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.44 |  |  |  |  | 0.00
2000 |  |  |  | 7334.35 |  |  | 7578 |  |  |  | 895 | [10 empty] | 86.17 |  |  |  | 86.17 | [5 empty] | 93.29 |  |  | 86.27 |  |  |  | 0.45 |  | 0.39 | [8 empty] | 13.44 |  |  |  |  | 0.00
2001 |  |  |  | 7615.10 |  |  | 7929 |  |  |  | 895 | [10 empty] | 89.99 |  |  |  | 89.99 | [5 empty] | 97.13 |  |  | 90.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.01 |  |  |  |  | 0.00
2002 |  |  |  | 8495.50 |  |  | 8760 |  |  |  | 895 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 108.36 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 7596.96 |  |  | 7913 |  |  |  | 895 | [10 empty] | 89.58 |  |  |  | 90.47 | [5 empty] | 96.90 |  |  | 90.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.53 |  |  |  |  | 0.89
2004 |  |  |  | 7378.56 |  |  | 7669 |  |  |  | 895 | [10 empty] | 86.83 |  |  |  | 86.83 | [5 empty] | 93.85 |  |  | 87.31 |  |  |  | 0.95 |  | 0.83 | [8 empty] | 12.34 |  |  |  |  | 0.00
2005 |  |  |  | 8397.18 |  |  | 8695 |  |  |  | 895 | [10 empty] | 99.20 |  |  |  | 99.20 | [5 empty] | 107.10 |  |  | 99.26 |  |  |  | 0.80 |  | 0.80 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 7520.38 |  |  | 7824 |  |  |  | 967 | [10 empty] | 90.67 |  |  |  | 90.67 | [5 empty] | 88.78 |  |  | 89.32 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 9.19 |  |  |  |  | 0.00
2007 |  |  |  | 7500.92 |  |  | 7967 |  |  |  | 966 | [10 empty] | 88.04 |  |  |  | 88.04 | [5 empty] | 88.64 |  |  | 90.95 |  |  |  | 3.13 |  | 2.84 | [8 empty] | 9.11 |  |  |  |  | 0.00
2008 |  |  |  | 8348.25 |  |  | 8674 |  |  |  | 977 | [10 empty] | 97.62 |  |  |  | 98.76 | [5 empty] | 97.28 |  |  | 98.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.24 |  |  |  |  | 1.14
2009 |  |  |  | 7836.76 |  |  | 7779 |  |  |  | 1007 | [10 empty] | 89.02 |  |  |  | 89.02 | [5 empty] | 89.06 |  |  | 88.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.98 |  |  |  |  | 0.00
2010 |  |  |  | 8218.18 |  |  | 8217 |  |  |  | 1007 | [10 empty] | 93.55 |  |  |  | 93.56 | [5 empty] | 93.16 |  |  | 93.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.44 |  |  |  |  | 0.01
2011 |  |  |  | 8210.90 |  |  | 8227 |  |  |  | 1009 | [10 empty] | 92.77 |  |  |  | 92.83 | [5 empty] | 92.90 |  |  | 93.92 |  |  |  | 0.88 |  | 0.82 | [8 empty] | 6.35 |  |  |  |  | 0.06
2012 |  |  |  | 8871.96 |  |  | 8784 |  |  |  | 1007 | [10 empty] | 99.95 |  |  |  | 100.00 | [5 empty] | 100.30 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.05
2013 |  |  |  | 6681.28 |  |  | 6680 |  |  |  | 1010 | [10 empty] | 75.32 |  |  |  | 75.41 | [5 empty] | 75.52 |  |  | 76.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.59 |  |  |  |  | 0.09
2014 |  |  |  | 7635.09 |  |  | 7579 |  |  |  | 1010 | [10 empty] | 86.04 |  |  |  | 86.04 | [5 empty] | 86.30 |  |  | 86.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.96 |  |  |  |  | 0.00
2015 |  |  |  | 8566.93 |  |  | 8488 |  |  |  | 1012 | [10 empty] | 96.59 |  |  |  | 96.74 | [5 empty] | 96.64 |  |  | 96.89 |  |  |  | 3.26 |  | 3.26 | [8 empty] | 0.00 |  |  |  |  | 0.15
2016 |  |  |  | 7786.10 |  |  | 7746 |  |  |  | 1012 | [10 empty] | 87.57 |  |  |  | 87.87 | [5 empty] | 87.59 |  |  | 88.18 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 12.11 |  |  |  |  | 0.30
2017 |  |  |  | 2088.18 |  |  | 2069 |  |  |  | 1012 | [10 empty] | 23.55 |  |  |  | 23.59 | [5 empty] | 23.55 |  |  | 23.62 |  |  |  | 8.76 |  | 2.27 | [8 empty] | 74.14 |  |  |  |  | 0.03
2018 |  |  |  | 6320.55 |  |  | 6279 |  |  |  | 1012 | [10 empty] | 71.26 |  |  |  | 71.41 | [5 empty] | 71.30 |  |  | 71.68 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 28.57 |  |  |  |  | 0.15
2019 |  |  |  | 4521.89 |  |  | 4546 |  |  |  | 1012 | [10 empty] | 50.96 |  |  |  | 50.97 | [5 empty] | 51.01 |  |  | 51.89 |  |  |  | 1.59 |  | 0.82 | [8 empty] | 48.21 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1986 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 37
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 4214 | [14 empty] | 1210
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 17
E. |  | Testing of plant systems or components | [39 empty] | 0
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 32
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
Z. |  | Other | [51 empty] | 0
Subtotal | [22 empty] | 4214 | [14 empty] | 1259 |  |  |  | 38 | [11 empty] | 6
Total | [22 empty] | 4214 | [14 empty] | 1303
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1986 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 0
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 3
16. |  |  | Steam generation systems | [34 empty] | 6
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 8
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 10
Total | [37 empty] | 44
Highlights (2019)
25th Refeling and Maintenance(2019.7.9 ~ )

## SHIN-KORI-1
2019 Operating Experience
KR-21 | [8 empty] | SHIN-KORI-1 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2006-06-16
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2010-08-04
Gross electrical power | [12 empty] | : |  |  | 1046 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2011-02-28
Reference unit power (net) | [12 empty] | : |  |  | 996 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 17.237
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.9 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36.15 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38829 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.124 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.69 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 180 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6500.05 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.47 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.7 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.29 %
Load Factor (LF) | [18 empty] | : | 74.5 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.23 %
Operating Factor (OF) | [18 empty] | : | 75.37 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2158 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 739.92 | 669.89 |  |  |  | 742.01 |  | 717.76 | [8 empty] | 741.27 |  |  | 714.27 | [6 empty] | 18.95 |  | 0.00 |  |  |  | 2.09 |  |  | 705.56 |  |  | 710.55 | [9 empty] | 737.78 |  |  | 6500.05
EAF [%] |  |  |  |  | 99.84 | 100.00 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 99.97 |  |  | 99.60 | [6 empty] | 2.56 |  | 0.00 |  |  |  | 0.29 |  |  | 95.21 |  |  | 99.08 | [9 empty] | 99.56 |  |  | 74.47
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 2.56 |  | 0.00 |  |  |  | 0.29 |  |  | 96.19 |  |  | 99.86 | [9 empty] | 99.99 |  |  | 74.70
LF [%] |  |  |  |  | 99.85 | 100.09 |  |  |  | 100.13 |  | 100.09 | [8 empty] | 100.03 |  |  | 99.60 | [6 empty] | 2.56 |  | 0.00 |  |  |  | 0.29 |  |  | 95.21 |  |  | 99.08 | [9 empty] | 99.56 |  |  | 74.50
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 4.57 |  | 0.00 |  |  |  | 2.22 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 75.37
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.02 |  |  | 0.14 | [9 empty] | 0.00 |  |  | 0.02
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.02 |  |  | 0.14 | [9 empty] | 0.00 |  |  | 0.01
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 97.44 |  | 100.00 |  |  |  | 99.71 |  |  | 3.79 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 25.29
XUF [%] |  |  |  |  | 0.16 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  | 0.39 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.97 |  |  | 0.78 | [9 empty] | 0.43 |  |  | 0.23
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 56025.72 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.76 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.8 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 72.16 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.04 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.45 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.23 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 71.1 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2011 |  |  |  | 7867.03 |  |  | 8008 |  |  |  | 985 | [10 empty] | 99.61 |  |  |  | 99.98 | [5 empty] | 100.17 |  |  | 100.00 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 0.00 |  |  |  |  | 0.37
2012 |  |  |  | 7091.41 |  |  | 7220 |  |  |  | 997 | [10 empty] | 81.24 |  |  |  | 81.31 | [5 empty] | 80.97 |  |  | 82.19 |  |  |  | 5.45 |  | 4.69 | [8 empty] | 14.00 |  |  |  |  | 0.07
2013 |  |  |  | 2328.10 |  |  | 2338 |  |  |  | 1000 | [10 empty] | 26.49 |  |  |  | 26.49 | [5 empty] | 26.58 |  |  | 26.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 73.51 |  |  |  |  | 0.00
2014 |  |  |  | 7419.09 |  |  | 7497 |  |  |  | 999 | [10 empty] | 98.23 |  |  |  | 98.44 | [5 empty] | 84.78 |  |  | 85.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.56 |  |  |  |  | 0.21
2015 |  |  |  | 7565.55 |  |  | 7656 |  |  |  | 999 | [10 empty] | 86.45 |  |  |  | 86.75 | [5 empty] | 86.45 |  |  | 87.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.25 |  |  |  |  | 0.30
2016 |  |  |  | 8729.83 |  |  | 8784 |  |  |  | 997 | [10 empty] | 99.59 |  |  |  | 100.00 | [5 empty] | 99.68 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.41
2017 |  |  |  | 508.50 |  |  | 538 |  |  |  | 997 | [10 empty] | 5.82 |  |  |  | 5.99 | [5 empty] | 5.82 |  |  | 6.14 |  |  |  | 0.00 |  | 80.59 | [8 empty] | 13.42 |  |  |  |  | 0.17
2018 |  |  |  | 6997.79 |  |  | 7107 |  |  |  | 996 | [10 empty] | 80.17 |  |  |  | 80.49 | [5 empty] | 80.20 |  |  | 81.13 |  |  |  | 0.16 |  | 19.03 | [8 empty] | 0.48 |  |  |  |  | 0.32
2019 |  |  |  | 6500.05 |  |  | 6602 |  |  |  | 996 | [10 empty] | 74.47 |  |  |  | 74.70 | [5 empty] | 74.50 |  |  | 75.37 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 25.29 |  |  |  |  | 0.23
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2011 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1032
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2158 | [14 empty] | 1371
E. |  | Testing of plant systems or components | [35 empty] | 259
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 133
Subtotal | [22 empty] | 2158 | [14 empty] | 1630 |  |  |  | 1032 | [11 empty] | 133
Total | [22 empty] | 2158 | [14 empty] | 2795
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2011 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 42
15. |  |  | Reactor Cooling Systems | [34 empty] | 926
42. |  |  | Electrical Power Supply Systems | [34 empty] | 125
Total | [37 empty] | 1093
Highlights (2019)
Refueling and maintenance('19.07.02~'19.09.30)

## SHIN-KORI-2
2019 Operating Experience
KR-22 | [8 empty] | SHIN-KORI-2 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-06-05
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2012-01-28
Gross electrical power | [12 empty] | : |  |  | 1047 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2012-07-20
Reference unit power (net) | [12 empty] | : |  |  | 996 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 17.237
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.9 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36.15 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38829 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.124 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.69 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 180 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6889.15 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.27 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.95 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.21 %
Unit Capability Factor (UCF) | [18 empty] | : | 79.21 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.58 %
Load Factor (LF) | [18 empty] | : | 78.96 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.26 %
Operating Factor (OF) | [18 empty] | : | 80.07 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1746 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 736.87 | 666.82 |  |  |  | 738.65 |  | 714.55 | [8 empty] | 738.24 |  |  | 712.12 | [6 empty] | 733.23 |  | 728.30 |  |  |  | 65.88 |  |  | 0.00 |  |  | 313.06 | [9 empty] | 741.43 |  |  | 6889.15
EAF [%] |  |  |  |  | 99.44 | 99.63 |  |  |  | 99.68 |  | 99.64 | [8 empty] | 99.62 |  |  | 99.30 | [6 empty] | 98.95 |  | 98.28 |  |  |  | 9.19 |  |  | 0.00 |  |  | 43.64 | [9 empty] | 99.98 |  |  | 78.95
UCF [%] |  |  |  |  | 99.68 | 99.68 |  |  |  | 99.70 |  | 99.68 | [8 empty] | 99.68 |  |  | 99.68 | [6 empty] | 99.68 |  | 99.66 |  |  |  | 9.28 |  |  | 0.00 |  |  | 43.68 | [9 empty] | 100.00 |  |  | 79.21
LF [%] |  |  |  |  | 99.44 | 99.63 |  |  |  | 99.68 |  | 99.64 | [8 empty] | 99.62 |  |  | 99.30 | [6 empty] | 98.95 |  | 98.28 |  |  |  | 9.19 |  |  | 0.00 |  |  | 43.66 | [9 empty] | 100.05 |  |  | 78.96
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 11.39 |  |  | 0.00 |  |  | 49.44 | [9 empty] | 100.00 |  |  | 80.07
FLR [%] |  |  |  |  | 0.32 | 0.31 |  |  |  | 0.30 |  | 0.32 | [8 empty] | 0.31 |  |  | 0.32 | [6 empty] | 0.32 |  | 0.32 |  |  |  | 0.24 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.27
UCL [%] |  |  |  |  | 0.32 | 0.31 |  |  |  | 0.30 |  | 0.32 | [8 empty] | 0.31 |  |  | 0.32 | [6 empty] | 0.32 |  | 0.32 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.21
PUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.02 |  |  |  | 90.69 |  |  | 100.00 |  |  | 56.32 | [9 empty] | 0.00 |  |  | 20.58
XUF [%] |  |  |  |  | 0.24 | 0.05 |  |  |  | 0.02 |  | 0.04 | [8 empty] | 0.06 |  |  | 0.38 | [6 empty] | 0.73 |  | 1.38 |  |  |  | 0.10 |  |  | 0.00 |  |  | 0.03 | [9 empty] | 0.02 |  |  | 0.26
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 53734.17 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.31 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.31 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.25 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.61 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.14 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.09 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.3 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.31 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2012 |  |  |  | 5400.28 |  |  | 5897 |  |  |  | 997 | [10 empty] | 99.75 |  |  |  | 99.95 | [5 empty] | 98.04 |  |  | 99.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  |  |  | 0.19
2013 |  |  |  | 3560.31 |  |  | 3569 |  |  |  | 1000 | [10 empty] | 40.56 |  |  |  | 40.57 | [5 empty] | 40.64 |  |  | 40.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 59.43 |  |  |  |  | 0.01
2014 |  |  |  | 8304.89 |  |  | 8518 |  |  |  | 998 | [10 empty] | 96.01 |  |  |  | 96.24 | [5 empty] | 94.99 |  |  | 97.24 |  |  |  | 0.52 |  | 0.51 | [8 empty] | 3.26 |  |  |  |  | 0.23
2015 |  |  |  | 7405.24 |  |  | 7604 |  |  |  | 996 | [10 empty] | 84.87 |  |  |  | 85.20 | [5 empty] | 84.87 |  |  | 86.80 |  |  |  | 1.08 |  | 0.93 | [8 empty] | 13.87 |  |  |  |  | 0.33
2016 |  |  |  | 6627.86 |  |  | 6718 |  |  |  | 997 | [10 empty] | 75.68 |  |  |  | 75.87 | [5 empty] | 75.68 |  |  | 76.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.13 |  |  |  |  | 0.19
2017 |  |  |  | 8699.48 |  |  | 8760 |  |  |  | 997 | [10 empty] | 99.59 |  |  |  | 99.99 | [5 empty] | 99.61 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.41
2018 |  |  |  | 6847.68 |  |  | 7011 |  |  |  | 996 | [10 empty] | 78.48 |  |  |  | 79.21 | [5 empty] | 78.48 |  |  | 80.03 |  |  |  | 0.25 |  | 0.20 | [8 empty] | 20.60 |  |  |  |  | 0.72
2019 |  |  |  | 6889.15 |  |  | 7014 |  |  |  | 996 | [10 empty] | 78.95 |  |  |  | 79.21 | [5 empty] | 78.96 |  |  | 80.07 |  |  |  | 0.27 |  | 0.21 | [8 empty] | 20.58 |  |  |  |  | 0.26
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2012 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1746 | [14 empty] | 1639
E. |  | Testing of plant systems or components | [35 empty] | 297
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
Subtotal | [22 empty] | 1746 | [14 empty] | 1936 | [15 empty] | 0
Total | [22 empty] | 1746 | [14 empty] | 1936
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2012 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
42. |  |  | Electrical Power Supply Systems | [34 empty] | 0
Total | [37 empty] | 0
Highlights (2019)
Refueling and Maintenance('19.09.04~'19.11.16)

## SHIN-KORI-3
2019 Operating Experience
KR-25 | [8 empty] | SHIN-KORI-3 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / APR-1400 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-10-16
Thermal power | [12 empty] | : |  |  | 3983 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-01-15
Gross electrical power | [12 empty] | : |  |  | 1486 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-12-20
Reference unit power (net) | [12 empty] | : |  |  | 1416 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.41
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.66 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 41 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 53073 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.647 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.764
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.38 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 93 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 10939.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.08 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.44 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.56 %
Load Factor (LF) | [18 empty] | : | 88.19 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.35 %
Operating Factor (OF) | [18 empty] | : | 88.61 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 998 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1055.84 | 953.95 |  |  |  | 1054.49 |  | 1020.92 | [8 empty] | 1054.64 |  |  | 1020.21 | [6 empty] | 1053.36 |  | 1049.38 |  |  |  | 1017.00 |  |  | 1052.25 |  |  | 607.01 | [9 empty] | 0.00 |  |  | 10939.06
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.97 |  | 99.99 | [8 empty] | 100.00 |  |  | 99.95 | [6 empty] | 99.89 |  | 99.55 |  |  |  | 99.70 |  |  | 99.84 |  |  | 59.50 | [9 empty] | 0.00 |  |  | 88.08
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.98 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.98 |  |  | 100.00 |  |  | 62.69 | [9 empty] | 0.00 |  |  | 88.44
LF [%] |  |  |  |  | 100.22 | 100.25 |  |  |  | 100.09 |  | 100.14 | [8 empty] | 100.11 |  |  | 100.07 | [6 empty] | 99.99 |  | 99.61 |  |  |  | 99.75 |  |  | 99.88 |  |  | 59.54 | [9 empty] | 0.00 |  |  | 88.19
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 64.72 | [9 empty] | 0.00 |  |  | 88.61
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.02 |  |  | 0.00 |  |  | 37.31 | [9 empty] | 100.00 |  |  | 11.56
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.03 | [6 empty] | 0.11 |  | 0.45 |  |  |  | 0.28 |  |  | 0.16 |  |  | 3.20 | [9 empty] | 0.00 |  |  | 0.35
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 32222.92 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.76 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.81 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.25 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.02 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.73 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.93 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.22 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 2851.25 |  |  | 2956 |  |  |  | 1383 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 12405.61 |  |  | 8760 |  |  |  | 1416 | [10 empty] | 99.79 |  |  |  | 99.99 | [5 empty] | 100.01 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.21
2018 |  |  |  | 6027.00 |  |  | 4360 |  |  |  | 1416 | [10 empty] | 48.55 |  |  |  | 48.64 | [5 empty] | 48.59 |  |  | 49.77 |  |  |  | 12.16 |  | 6.74 | [8 empty] | 44.62 |  |  |  |  | 0.10
2019 |  |  |  | 10939.06 |  |  | 7762 |  |  |  | 1416 | [10 empty] | 88.08 |  |  |  | 88.44 | [5 empty] | 88.19 |  |  | 88.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.56 |  |  |  |  | 0.35
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2016 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 192
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 998 | [14 empty] | 1609
E. |  | Testing of plant systems or components | [35 empty] | 1826
Subtotal | [22 empty] | 998 | [14 empty] | 3435 |  |  |  | 192
Total | [22 empty] | 998 | [14 empty] | 3627
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2016 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 144
Total | [37 empty] | 144
Highlights (2019)
- Planned Outage : '19.11.20 ~

## SHIN-KORI-4
2019 Operating Experience
KR-26 | [7 empty] | SHIN-KORI-4 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [6 empty] | : | Operational
Operator | [6 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [6 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [6 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [6 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [26 empty] | Key Dates
Reactor type and model | [11 empty] | : |  |  | PWR / APR-1400 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-08-19
Thermal power | [11 empty] | : |  |  | 3983 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-04-22
Gross electrical power | [11 empty] | : |  |  | 1455 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2019-08-29
Reference unit power (net) | [11 empty] | : |  |  | 1418 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 0 years
Design Characteristics
| Primary Systems | [27 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [12 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.9
| Fuel material | [12 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [12 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [12 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.41
| Average fuel enrichment [% of U235] | [12 empty] | : |  |  | 2.66 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [12 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [12 empty] | : |  |  | 41 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [12 empty] | : |  |  | 53073 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [12 empty] | : |  |  | 3.647 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.764
| Active core height/length [m] | [12 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [12 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [12 empty] | : |  |  | 18.38 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [12 empty] | : |  |  | 93 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [12 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [12 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [17 empty] | : | 6107.4 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [17 empty] | : | 99.95 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [17 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [17 empty] | : | 100.34 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.05 %
Operating Factor (OF) | [17 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1222 hours
Annual Summary
|  |  |  | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | Aug |  |  | May | [6 empty] | Jun |  | Jul |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [35 empty] | 1021.93 |  |  | 1055.41 |  |  | 1026.69 | [9 empty] | 1061.95 |  |  | 4165.97
EAF [%] | [35 empty] | 99.90 |  |  | 99.90 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.95
UCF [%] | [35 empty] | 100.00 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] | [35 empty] | 100.09 |  |  | 100.04 |  |  | 100.56 | [9 empty] | 100.66 |  |  | 100.34
OF [%] | [35 empty] | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] | [35 empty] | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] | [35 empty] | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] | [35 empty] | 0.00 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] | [35 empty] | 0.10 |  |  | 0.09 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
Historical Summary
Lifetime energy generation | [12 empty] | : |  |  | 6107.4 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [12 empty] | : |  |  | 99.95 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [12 empty] | : |  |  | 100 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0 %
Cumulative Load Factor (LF) | [12 empty] | : |  |  | 100.34 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.05 %
Cumulative Operating Factor (OF) | [12 empty] | : |  |  | 100 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2019 |  |  | 6107.40 |  |  | 4874 |  |  |  | 1418 | [10 empty] | 99.95 |  |  |  | 100.00 | [5 empty] | 100.34 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.05
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[22 empty] | 2019 | [14 empty] | 2019 to 2019
Outage Cause | [21 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[22 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
E. |  | Testing of plant systems or components | [19 empty] | 1224 | [14 empty] | 3672
Subtotal | [21 empty] | 1224 | [14 empty] | 3672
Total | [21 empty] | 1224 | [14 empty] | 3672
Equipment Related Unplanned Full Outages, Analysis by System
System | [21 empty] | 2019 | [14 empty] | 2019 to 2019
[22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
Total
Highlights (2019)
Commercial Operation From August 29, 2019

## SHIN-WOLSONG-1
2019 Operating Experience
KR-23 | [8 empty] | SHIN-WOLSONG-1 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-11-20
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2012-01-27
Gross electrical power | [12 empty] | : |  |  | 1049 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2012-07-31
Reference unit power (net) | [12 empty] | : |  |  | 997 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 17.237
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.9 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36.15 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38829 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.124 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.69 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 180 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 7404.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.71 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.14 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 14.86 %
Load Factor (LF) | [18 empty] | : | 84.78 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.43 %
Operating Factor (OF) | [18 empty] | : | 85.74 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1249 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 743.41 | 671.51 |  |  |  | 742.93 |  | 718.53 | [8 empty] | 741.38 |  |  | 715.39 | [6 empty] | 737.71 |  | 732.84 |  |  |  | 706.07 |  |  | 678.93 |  |  | 0.00 | [9 empty] | 215.56 |  |  | 7404.26
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.98 |  | 99.99 | [8 empty] | 99.93 |  |  | 99.66 | [6 empty] | 99.45 |  | 98.80 |  |  |  | 98.36 |  |  | 91.53 |  |  | 0.00 | [9 empty] | 29.03 |  |  | 84.71
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.98 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.97 |  |  | 92.84 |  |  | 0.00 | [9 empty] | 29.03 |  |  | 85.14
LF [%] |  |  |  |  | 100.22 | 100.23 |  |  |  | 100.16 |  | 100.10 | [8 empty] | 99.95 |  |  | 99.66 | [6 empty] | 99.45 |  | 98.80 |  |  |  | 98.36 |  |  | 91.53 |  |  | 0.00 | [9 empty] | 29.06 |  |  | 84.78
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 94.89 |  |  | 0.00 | [9 empty] | 34.01 |  |  | 85.74
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.03 |  |  | 7.16 |  |  | 100.00 | [9 empty] | 70.97 |  |  | 14.86
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.07 |  |  | 0.32 | [6 empty] | 0.55 |  | 1.20 |  |  |  | 1.61 |  |  | 1.31 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.43
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 53443.3 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.85 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.69 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.4 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.91 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.29 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.08 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2012 |  |  |  | 4964.62 |  |  | 6256 |  |  |  | 997 | [10 empty] | 94.89 |  |  |  | 95.60 | [5 empty] | 94.90 |  |  | 97.03 |  |  |  | 3.56 |  | 3.53 | [8 empty] | 0.88 |  |  |  |  | 0.70
2013 |  |  |  | 3295.84 |  |  | 3353 |  |  |  | 991 | [10 empty] | 37.93 |  |  |  | 37.94 | [5 empty] | 37.97 |  |  | 38.28 |  |  |  | 6.51 |  | 2.64 | [8 empty] | 59.42 |  |  |  |  | 0.01
2014 |  |  |  | 8611.78 |  |  | 8677 |  |  |  | 1000 | [10 empty] | 98.27 |  |  |  | 98.54 | [5 empty] | 98.31 |  |  | 99.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.46 |  |  |  |  | 0.27
2015 |  |  |  | 6217.67 |  |  | 6354 |  |  |  | 997 | [10 empty] | 71.19 |  |  |  | 71.51 | [5 empty] | 71.19 |  |  | 72.53 |  |  |  | 0.51 |  | 0.36 | [8 empty] | 28.12 |  |  |  |  | 0.32
2016 |  |  |  | 7393.37 |  |  | 7522 |  |  |  | 997 | [10 empty] | 84.42 |  |  |  | 84.81 | [5 empty] | 84.42 |  |  | 85.63 |  |  |  | 0.76 |  | 0.65 | [8 empty] | 14.54 |  |  |  |  | 0.39
2017 |  |  |  | 8553.53 |  |  | 8640 |  |  |  | 997 | [10 empty] | 97.63 |  |  |  | 97.81 | [5 empty] | 97.94 |  |  | 98.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.19 |  |  |  |  | 0.18
2018 |  |  |  | 7002.14 |  |  | 7097 |  |  |  | 997 | [10 empty] | 80.08 |  |  |  | 80.35 | [5 empty] | 80.17 |  |  | 81.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.65 |  |  |  |  | 0.27
2019 |  |  |  | 7404.26 |  |  | 7511 |  |  |  | 997 | [10 empty] | 84.71 |  |  |  | 85.14 | [5 empty] | 84.78 |  |  | 85.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.86 |  |  |  |  | 0.43
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2012 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 44
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1253 | [14 empty] | 1616
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 243
Subtotal | [22 empty] | 1253 | [14 empty] | 1859 |  |  |  | 44
Total | [22 empty] | 1253 | [14 empty] | 1903
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2012 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 27
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
Total | [37 empty] | 41
Highlights (2019)
Refueling and Maintenance(2019.10.30~2019.12.21)

## SHIN-WOLSONG-2
2019 Operating Experience
KR-24 | [8 empty] | SHIN-WOLSONG-2 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | DHICKOPC (DOOSAN HEAVY INDUSTRIES AND CONSTRUCTION CO. LTD./KOREA POWER ENGINEERING COMPANY/COMBUSTION ENGINEERING)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / OPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-09-23
Thermal power | [12 empty] | : |  |  | 2825 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-02-26
Gross electrical power | [12 empty] | : |  |  | 1051 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-07-24
Reference unit power (net) | [12 empty] | : |  |  | 993 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 17.237
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.9 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 36.15 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38829 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.124 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.69 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : | [14 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 6544.76 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 10.97 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.85 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 9.22 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.89 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.89 %
Load Factor (LF) | [18 empty] | : | 75.24 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.03 %
Operating Factor (OF) | [18 empty] | : | 75.59 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2138 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 744.19 | 672.76 |  |  |  | 745.24 |  | 720.63 | [8 empty] | 743.23 |  |  | 716.83 | [6 empty] | 235.12 |  | 0.00 |  |  |  | 2.48 |  |  | 508.77 |  |  | 716.07 | [9 empty] | 739.43 |  |  | 6544.76
EAF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.99 |  |  | 99.99 | [6 empty] | 31.66 |  | 0.00 |  |  |  | 0.35 |  |  | 68.86 |  |  | 99.99 | [9 empty] | 99.88 |  |  | 74.85
UCF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 31.66 |  | 0.00 |  |  |  | 0.35 |  |  | 69.13 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 74.89
LF [%] |  |  |  |  | 100.73 | 100.82 |  |  |  | 100.87 |  | 100.79 | [8 empty] | 100.60 |  |  | 100.26 | [6 empty] | 31.83 |  | 0.00 |  |  |  | 0.35 |  |  | 68.86 |  |  | 100.16 | [9 empty] | 100.09 |  |  | 75.24
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 33.60 |  | 0.00 |  |  |  | 2.22 |  |  | 73.66 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 75.59
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 99.57 |  |  | 30.87 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.97
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 80.31 |  |  | 30.87 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.22
PUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 68.34 |  | 100.00 |  |  |  | 19.34 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 15.89
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.26 |  |  | 0.01 | [9 empty] | 0.10 |  |  | 0.03
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 31884.9 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.59 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.68 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.09 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.12 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.94 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.11 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.26 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 5169.24 |  |  | 5821 |  |  |  | 993 | [10 empty] | 99.83 |  |  |  | 99.98 | [5 empty] | 100.03 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.00 |  |  |  |  | 0.15
2016 |  |  |  | 7223.89 |  |  | 7328 |  |  |  | 993 | [10 empty] | 82.55 |  |  |  | 82.78 | [5 empty] | 82.82 |  |  | 83.42 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 17.20 |  |  |  |  | 0.22
2017 |  |  |  | 6234.20 |  |  | 6298 |  |  |  | 993 | [10 empty] | 71.59 |  |  |  | 71.71 | [5 empty] | 71.67 |  |  | 71.89 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 28.29 |  |  |  |  | 0.12
2018 |  |  |  | 6712.82 |  |  | 6783 |  |  |  | 993 | [10 empty] | 76.83 |  |  |  | 76.88 | [5 empty] | 77.17 |  |  | 77.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.12 |  |  |  |  | 0.05
2019 |  |  |  | 6544.76 |  |  | 6622 |  |  |  | 993 | [10 empty] | 74.85 |  |  |  | 74.89 | [5 empty] | 75.24 |  |  | 75.59 |  |  |  | 10.97 |  | 9.22 | [8 empty] | 15.89 |  |  |  |  | 0.03
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 2015 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 775 | [14 empty] | 175
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1367 | [14 empty] | 1646
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 367
Subtotal | [22 empty] | 1367 |  |  |  | 775 | [10 empty] | 2013 |  |  |  | 175
Total | [22 empty] | 2142 | [14 empty] | 2188
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 2015 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [19 empty] | 775 | [14 empty] | 158
Total | [22 empty] | 775 | [14 empty] | 158
Highlights (2019)
Refueling and Maintenance(2019.07.11~2019.10.09) Automatic reactor scram due to steam generator Level Lo(2019.09.06)

## WOLSONG-2
2019 Operating Experience
KR-4 | [8 empty] | WOLSONG-2 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | AECL/DHI (ATOMIC ENERGY OF CANADA LTD./DOOSAN HEAVY INDUSTRIES & CONSTRUCTION)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1992-09-25
Thermal power | [12 empty] | : |  |  | 2061 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1997-04-01
Gross electrical power | [12 empty] | : |  |  | 620 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1997-07-01
Reference unit power (net) | [12 empty] | : |  |  | 606 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 22 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.12
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.69 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.59
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 0.1615 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 4840.92 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.59 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.33 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.67 %
Load Factor (LF) | [18 empty] | : | 91.19 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.74 %
Operating Factor (OF) | [18 empty] | : | 90.41 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 840 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 461.56 | 418.32 |  |  |  | 462.34 |  | 446.48 | [8 empty] | 459.81 |  |  | 230.63 | [6 empty] | 147.75 |  | 446.16 |  |  |  | 433.65 |  |  | 451.00 |  |  | 435.14 | [9 empty] | 448.07 |  |  | 4840.92
EAF [%] |  |  |  |  | 99.38 | 99.58 |  |  |  | 99.47 |  | 99.44 | [8 empty] | 99.33 |  |  | 51.69 | [6 empty] | 32.29 |  | 98.47 |  |  |  | 99.03 |  |  | 99.17 |  |  | 99.01 | [9 empty] | 98.91 |  |  | 89.59
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 51.95 | [6 empty] | 32.61 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 99.99 |  |  | 90.33
LF [%] |  |  |  |  | 102.37 | 102.72 |  |  |  | 102.55 |  | 102.33 | [8 empty] | 101.99 |  |  | 52.86 | [6 empty] | 32.77 |  | 98.96 |  |  |  | 99.39 |  |  | 100.03 |  |  | 99.73 | [9 empty] | 99.38 |  |  | 91.19
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 52.22 | [6 empty] | 33.33 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.41
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.01 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.01 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 48.05 | [6 empty] | 67.39 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.67
XUF [%] |  |  |  |  | 0.62 | 0.42 |  |  |  | 0.53 |  | 0.56 | [8 empty] | 0.67 |  |  | 0.26 | [6 empty] | 0.32 |  | 1.53 |  |  |  | 0.97 |  |  | 0.83 |  |  | 0.98 | [9 empty] | 1.09 |  |  | 0.74
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 121400.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.26 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.01 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.24 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.14 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.62 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.94 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.13 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.18 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1997 |  |  |  | 3294.95 |  |  | 5296 |  |  |  | 650 | [10 empty] | 94.68 |  |  |  | 94.68 | [5 empty] | 97.70 |  |  | 95.09 |  |  |  | 5.20 |  | 5.19 | [8 empty] | 0.13 |  |  |  |  | 0.00
1998 |  |  |  | 4788.68 |  |  | 7144 |  |  |  | 650 | [10 empty] | 81.01 |  |  |  | 81.02 | [5 empty] | 84.10 |  |  | 81.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.98 |  |  |  |  | 0.00
1999 |  |  |  | 5211.77 |  |  | 7754 |  |  |  | 650 | [10 empty] | 88.12 |  |  |  | 88.13 | [5 empty] | 91.53 |  |  | 88.52 |  |  |  | 0.26 |  | 0.23 | [8 empty] | 11.65 |  |  |  |  | 0.00
2000 |  |  |  | 5346.81 |  |  | 7843 |  |  |  | 650 | [10 empty] | 91.49 |  |  |  | 91.49 | [5 empty] | 93.65 |  |  | 89.29 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 8.45 |  |  |  |  | 0.00
2001 |  |  |  | 5585.43 |  |  | 8188 |  |  |  | 650 | [10 empty] | 92.79 |  |  |  | 93.01 | [5 empty] | 98.09 |  |  | 93.47 |  |  |  | 0.34 |  | 0.32 | [8 empty] | 6.67 |  |  |  |  | 0.22
2002 |  |  |  | 5265.98 |  |  | 7717 |  |  |  | 650 | [10 empty] | 87.66 |  |  |  | 87.66 | [5 empty] | 92.48 |  |  | 88.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.34 |  |  |  |  | 0.00
2003 |  |  |  | 5480.58 |  |  | 8015 |  |  |  | 650 | [10 empty] | 91.22 |  |  |  | 91.22 | [5 empty] | 96.25 |  |  | 91.50 |  |  |  | 0.86 |  | 0.79 | [8 empty] | 7.99 |  |  |  |  | 0.00
2004 |  |  |  | 5465.46 |  |  | 8015 |  |  |  | 650 | [10 empty] | 90.88 |  |  |  | 90.91 | [5 empty] | 95.72 |  |  | 91.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.09 |  |  |  |  | 0.03
2005 |  |  |  | 5641.29 |  |  | 8243 |  |  |  | 650 | [10 empty] | 93.90 |  |  |  | 93.90 | [5 empty] | 99.07 |  |  | 94.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.10 |  |  |  |  | 0.00
2006 |  |  |  | 5975.85 |  |  | 8711 |  |  |  | 684 | [10 empty] | 99.34 |  |  |  | 99.34 | [5 empty] | 99.73 |  |  | 99.44 |  |  |  | 0.65 |  | 0.65 | [8 empty] | 0.01 |  |  |  |  | 0.00
2007 |  |  |  | 5618.82 |  |  | 7948 |  |  |  | 683 | [10 empty] | 90.58 |  |  |  | 90.58 | [5 empty] | 93.91 |  |  | 90.73 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 9.40 |  |  |  |  | 0.00
2008 |  |  |  | 5700.28 |  |  | 8081 |  |  |  | 710 | [10 empty] | 91.96 |  |  |  | 92.10 | [5 empty] | 91.40 |  |  | 92.00 |  |  |  | 0.56 |  | 0.52 | [8 empty] | 7.38 |  |  |  |  | 0.14
2009 |  |  |  | 5845.94 |  |  | 8265 |  |  |  | 710 | [10 empty] | 93.92 |  |  |  | 94.20 | [5 empty] | 93.99 |  |  | 94.35 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 5.77 |  |  |  |  | 0.29
2010 |  |  |  | 5774.27 |  |  | 8152 |  |  |  | 710 | [10 empty] | 92.67 |  |  |  | 92.96 | [5 empty] | 92.84 |  |  | 93.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.04 |  |  |  |  | 0.29
2011 |  |  |  | 6124.72 |  |  | 8760 |  |  |  | 710 | [10 empty] | 98.37 |  |  |  | 98.37 | [5 empty] | 98.47 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.63 |  |  |  |  | 0.00
2012 |  |  |  | 5572.93 |  |  | 8187 |  |  |  | 673 | [10 empty] | 92.76 |  |  |  | 92.76 | [5 empty] | 94.27 |  |  | 93.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.24 |  |  |  |  | 0.00
2013 |  |  |  | 4797.42 |  |  | 7207 |  |  |  | 655 | [10 empty] | 82.18 |  |  |  | 82.18 | [5 empty] | 82.86 |  |  | 82.27 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 17.66 |  |  |  |  | 0.01
2014 |  |  |  | 5194.82 |  |  | 7954 |  |  |  | 650 | [10 empty] | 90.78 |  |  |  | 90.78 | [5 empty] | 90.83 |  |  | 90.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.22 |  |  |  |  | 0.00
2015 |  |  |  | 5143.35 |  |  | 7921 |  |  |  | 652 | [10 empty] | 90.03 |  |  |  | 90.23 | [5 empty] | 90.14 |  |  | 90.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.77 |  |  |  |  | 0.20
2016 |  |  |  | 4219.27 |  |  | 6525 |  |  |  | 647 | [10 empty] | 73.90 |  |  |  | 97.43 | [5 empty] | 74.24 |  |  | 74.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.57 |  |  |  |  | 23.53
2017 |  |  |  | 4981.05 |  |  | 7947 |  |  |  | 632 | [10 empty] | 90.25 |  |  |  | 90.65 | [5 empty] | 89.97 |  |  | 90.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.35 |  |  |  |  | 0.40
2018 |  |  |  | 4449.94 |  |  | 7190 |  |  |  | 611 | [10 empty] | 81.97 |  |  |  | 82.00 | [5 empty] | 83.14 |  |  | 82.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.00 |  |  |  |  | 0.02
2019 |  |  |  | 4840.92 |  |  | 7920 |  |  |  | 606 | [10 empty] | 89.59 |  |  |  | 90.33 | [5 empty] | 91.19 |  |  | 90.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.67 |  |  |  |  | 0.74
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1997 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 13
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 189
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 840 | [14 empty] | 563
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 91
Subtotal | [22 empty] | 840 | [14 empty] | 752 |  |  |  | 15 | [11 empty] | 94
Total | [22 empty] | 840 | [14 empty] | 861
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1997 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 3
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
16. |  |  | Steam generation systems | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [37 empty] | 18
Highlights (2019)
18th Overhaul(Inspection and Maintenance, 2019-06-16~2019-07-21)

## WOLSONG-3
2019 Operating Experience
KR-15 | [8 empty] | WOLSONG-3 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | AECL/DHI (ATOMIC ENERGY OF CANADA LTD./DOOSAN HEAVY INDUSTRIES & CONSTRUCTION)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1994-03-17
Thermal power | [12 empty] | : |  |  | 2061 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1998-03-25
Gross electrical power | [12 empty] | : |  |  | 650 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1998-07-01
Reference unit power (net) | [12 empty] | : |  |  | 630 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 21 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.12
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.71 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 15 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 96 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7296 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.69 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.59
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 0.1615 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 3261.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 14.56 %
Energy Availability Factor (EAF) | [18 empty] | : | 58.19 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 28.61 %
Unit Capability Factor (UCF) | [18 empty] | : | 59.08 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.31 %
Load Factor (LF) | [18 empty] | : | 59.09 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.89 %
Operating Factor (OF) | [18 empty] | : | 59.18 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3576 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 312.54 | 27.95 |  |  |  | 472.59 |  | 456.76 | [8 empty] | 471.74 |  |  | 454.21 | [6 empty] | 465.93 |  | 459.79 |  |  |  | 139.75 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3261.26
EAF [%] |  |  |  |  | 65.02 | 6.53 |  |  |  | 98.71 |  | 98.67 | [8 empty] | 98.71 |  |  | 98.70 | [6 empty] | 98.35 |  | 97.70 |  |  |  | 30.72 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 58.19
UCF [%] |  |  |  |  | 65.73 | 6.68 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 31.31 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 59.08
LF [%] |  |  |  |  | 66.68 | 6.60 |  |  |  | 100.83 |  | 100.70 | [8 empty] | 100.64 |  |  | 100.14 | [6 empty] | 99.40 |  | 98.09 |  |  |  | 30.81 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 59.09
OF [%] |  |  |  |  | 65.73 | 7.74 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 31.53 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 59.18
FLR [%] |  |  |  |  | 34.27 | 93.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 14.56
UCL [%] |  |  |  |  | 34.27 | 93.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 21.51 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 28.61
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 68.69 |  |  | 78.49 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.31
XUF [%] |  |  |  |  | 0.70 | 0.15 |  |  |  | 1.29 |  | 1.33 | [8 empty] | 1.29 |  |  | 1.30 | [6 empty] | 1.65 |  | 2.30 |  |  |  | 0.59 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.89
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 112384.9 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.08 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.67 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.44 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.88 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.78 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.15 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.24 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1998 |  |  |  | 3460.26 |  |  | 5326 |  |  |  | 650 | [10 empty] | 96.11 |  |  |  | 96.11 | [5 empty] | 98.89 |  |  | 96.38 |  |  |  | 3.88 |  | 3.88 | [8 empty] | 0.01 |  |  |  |  | 0.00
1999 |  |  |  | 4696.65 |  |  | 7008 |  |  |  | 650 | [10 empty] | 80.23 |  |  |  | 80.24 | [5 empty] | 82.48 |  |  | 80.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.76 |  |  |  |  | 0.00
2000 |  |  |  | 5925.22 |  |  | 8784 |  |  |  | 650 | [10 empty] | 99.93 |  |  |  | 99.93 | [5 empty] | 103.78 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.07 |  |  |  |  | 0.00
2001 |  |  |  | 4923.93 |  |  | 7409 |  |  |  | 650 | [10 empty] | 85.32 |  |  |  | 85.32 | [5 empty] | 86.48 |  |  | 84.58 |  |  |  | 3.17 |  | 2.79 | [8 empty] | 11.89 |  |  |  |  | 0.00
2002 |  |  |  | 5043.33 |  |  | 8083 |  |  |  | 650 | [10 empty] | 91.79 |  |  |  | 91.79 | [5 empty] | 88.57 |  |  | 92.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.21 |  |  |  |  | 0.00
2003 |  |  |  | 5579.53 |  |  | 8176 |  |  |  | 650 | [10 empty] | 93.06 |  |  |  | 93.06 | [5 empty] | 97.99 |  |  | 93.33 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 6.88 |  |  |  |  | 0.00
2004 |  |  |  | 5540.29 |  |  | 8152 |  |  |  | 650 | [10 empty] | 92.24 |  |  |  | 92.47 | [5 empty] | 97.03 |  |  | 92.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.53 |  |  |  |  | 0.23
2005 |  |  |  | 5997.86 |  |  | 8760 |  |  |  | 650 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.34 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 5617.76 |  |  | 8205 |  |  |  | 682 | [10 empty] | 93.45 |  |  |  | 93.45 | [5 empty] | 94.03 |  |  | 93.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.55 |  |  |  |  | 0.00
2007 |  |  |  | 5826.59 |  |  | 8239 |  |  |  | 681 | [10 empty] | 93.78 |  |  |  | 93.78 | [5 empty] | 97.67 |  |  | 94.05 |  |  |  | 0.65 |  | 0.61 | [8 empty] | 5.61 |  |  |  |  | 0.00
2008 |  |  |  | 5761.08 |  |  | 8129 |  |  |  | 707 | [10 empty] | 92.63 |  |  |  | 92.71 | [5 empty] | 92.77 |  |  | 92.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.29 |  |  |  |  | 0.08
2009 |  |  |  | 5882.54 |  |  | 8287 |  |  |  | 707 | [10 empty] | 94.34 |  |  |  | 94.50 | [5 empty] | 94.98 |  |  | 94.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.50 |  |  |  |  | 0.15
2010 |  |  |  | 5986.43 |  |  | 8433 |  |  |  | 707 | [10 empty] | 96.19 |  |  |  | 96.25 | [5 empty] | 96.66 |  |  | 96.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.75 |  |  |  |  | 0.06
2011 |  |  |  | 6014.37 |  |  | 8477 |  |  |  | 707 | [10 empty] | 96.45 |  |  |  | 96.50 | [5 empty] | 97.11 |  |  | 96.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.50 |  |  |  |  | 0.05
2012 |  |  |  | 5460.60 |  |  | 7827 |  |  |  | 686 | [10 empty] | 88.70 |  |  |  | 88.70 | [5 empty] | 90.62 |  |  | 89.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.30 |  |  |  |  | 0.00
2013 |  |  |  | 5453.06 |  |  | 7937 |  |  |  | 684 | [10 empty] | 90.39 |  |  |  | 90.50 | [5 empty] | 91.01 |  |  | 90.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.50 |  |  |  |  | 0.11
2014 |  |  |  | 4968.56 |  |  | 7371 |  |  |  | 665 | [10 empty] | 83.99 |  |  |  | 83.99 | [5 empty] | 85.29 |  |  | 84.14 |  |  |  | 2.67 |  | 2.30 | [8 empty] | 13.71 |  |  |  |  | 0.00
2015 |  |  |  | 5528.96 |  |  | 8313 |  |  |  | 665 | [10 empty] | 94.72 |  |  |  | 94.88 | [5 empty] | 94.91 |  |  | 94.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.12 |  |  |  |  | 0.16
2016 |  |  |  | 4046.37 |  |  | 6216 |  |  |  | 651 | [10 empty] | 70.41 |  |  |  | 93.83 | [5 empty] | 70.76 |  |  | 70.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.17 |  |  |  |  | 23.42
2017 |  |  |  | 1857.46 |  |  | 2890 |  |  |  | 648 | [10 empty] | 32.82 |  |  |  | 32.87 | [5 empty] | 32.72 |  |  | 32.99 |  |  |  | 38.40 |  | 20.49 | [8 empty] | 46.64 |  |  |  |  | 0.06
2018 |  |  |  | 4116.18 |  |  | 6432 |  |  |  | 641 | [10 empty] | 73.18 |  |  |  | 73.19 | [5 empty] | 73.30 |  |  | 73.42 |  |  |  | 4.07 |  | 3.11 | [8 empty] | 23.70 |  |  |  |  | 0.01
2019 |  |  |  | 3261.26 |  |  | 5184 |  |  |  | 630 | [10 empty] | 58.19 |  |  |  | 59.08 | [5 empty] | 59.09 |  |  | 59.18 |  |  |  | 14.56 |  | 28.61 | [8 empty] | 12.31 |  |  |  |  | 0.89
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1998 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 2499 | [14 empty] | 240
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 235
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 1077 | [14 empty] | 651
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 98
Subtotal | [22 empty] | 1077 |  |  |  | 2499 | [10 empty] | 886 |  |  |  | 240 | [11 empty] | 99
Total | [22 empty] | 3576 | [14 empty] | 1225
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1998 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 99
15. |  |  | Reactor Cooling Systems | [19 empty] | 875 | [14 empty] | 42
16. |  |  | Steam generation systems | [19 empty] | 1624 | [14 empty] | 77
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 12
Total | [22 empty] | 2499 | [14 empty] | 241
Highlights (2019)
Reactor trip because of PHT pump trip(2019.01.21 ~ 2019.02.26) Inspection and Maintenance(2019.09.10 ~ )

## WOLSONG-4
2019 Operating Experience
KR-16 | [8 empty] | WOLSONG-4 | [26 empty] | KOREA, REPUBLIC OF
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Owner | [7 empty] | : | KHNP (Korea Hydro and Nuclear Power Co.)
Reactor Supplier | [7 empty] | : | AECL/DHI (ATOMIC ENERGY OF CANADA LTD./DOOSAN HEAVY INDUSTRIES & CONSTRUCTION)
Turbine Supplier | [7 empty] | : | DHICGE (Doosan Heavy Industry Co. & General Electric)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1994-07-22
Thermal power | [12 empty] | : |  |  | 2061 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1999-05-21
Gross electrical power | [12 empty] | : |  |  | 621 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1999-10-01
Reference unit power (net) | [12 empty] | : |  |  | 609 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 20 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.12
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.71 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 15 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 4
| Part of the core refuelled [%] | [13 empty] | : |  |  | 96 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7296 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.69 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.59
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 0.1615 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 4420.51 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.15 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.07 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.41 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.34 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.25 %
Load Factor (LF) | [18 empty] | : | 82.86 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.27 %
Operating Factor (OF) | [18 empty] | : | 83.45 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1450 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 454.44 | 412.40 |  |  |  | 456.36 |  | 310.86 | [8 empty] | 0.00 |  |  | 128.54 | [6 empty] | 450.19 |  | 444.52 |  |  |  | 430.91 |  |  | 446.42 |  |  | 435.03 | [9 empty] | 450.84 |  |  | 4420.51
EAF [%] |  |  |  |  | 98.56 | 98.96 |  |  |  | 98.91 |  | 70.05 | [8 empty] | 0.00 |  |  | 29.17 | [6 empty] | 98.39 |  | 97.78 |  |  |  | 98.19 |  |  | 98.32 |  |  | 98.46 | [9 empty] | 98.66 |  |  | 82.07
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 71.05 | [8 empty] | 0.00 |  |  | 29.57 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.34
LF [%] |  |  |  |  | 100.30 | 100.77 |  |  |  | 100.72 |  | 70.89 | [8 empty] | 0.00 |  |  | 29.32 | [6 empty] | 99.36 |  | 98.11 |  |  |  | 98.27 |  |  | 98.53 |  |  | 99.21 | [9 empty] | 99.50 |  |  | 82.86
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 71.25 | [8 empty] | 0.00 |  |  | 30.69 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.45
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 5.04 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.15
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 41.44 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.41
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 28.95 | [8 empty] | 100.00 |  |  | 28.98 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.25
XUF [%] |  |  |  |  | 1.44 | 1.04 |  |  |  | 1.09 |  | 1.00 | [8 empty] | 0.00 |  |  | 0.40 | [6 empty] | 1.61 |  | 2.22 |  |  |  | 1.81 |  |  | 1.68 |  |  | 1.54 | [9 empty] | 1.34 |  |  | 1.27
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 112583.18 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.11 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.2 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.25 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.02 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.73 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 93 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.82 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.4 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1999 |  |  |  | 1489.23 |  |  | 2208 |  |  |  | 650 | [10 empty] | 99.89 |  |  |  | 99.89 | [5 empty] | 103.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.11 |  |  |  |  | 0.00
2000 |  |  |  | 5423.32 |  |  | 8033 |  |  |  | 650 | [10 empty] | 91.36 |  |  |  | 91.36 | [5 empty] | 94.99 |  |  | 91.45 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 8.55 |  |  |  |  | 0.00
2001 |  |  |  | 5493.17 |  |  | 8110 |  |  |  | 650 | [10 empty] | 92.58 |  |  |  | 92.58 | [5 empty] | 96.47 |  |  | 92.58 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 7.33 |  |  |  |  | 0.00
2002 |  |  |  | 5448.11 |  |  | 7971 |  |  |  | 650 | [10 empty] | 90.80 |  |  |  | 90.80 | [5 empty] | 95.68 |  |  | 90.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.20 |  |  |  |  | 0.00
2003 |  |  |  | 5601.86 |  |  | 8225 |  |  |  | 650 | [10 empty] | 93.49 |  |  |  | 93.49 | [5 empty] | 98.38 |  |  | 93.89 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 6.40 |  |  |  |  | 0.00
2004 |  |  |  | 5620.95 |  |  | 8209 |  |  |  | 650 | [10 empty] | 93.17 |  |  |  | 93.17 | [5 empty] | 98.45 |  |  | 93.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.83 |  |  |  |  | 0.00
2005 |  |  |  | 5657.87 |  |  | 8254 |  |  |  | 650 | [10 empty] | 93.79 |  |  |  | 93.79 | [5 empty] | 99.37 |  |  | 94.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.21 |  |  |  |  | 0.00
2006 |  |  |  | 6028.31 |  |  | 8760 |  |  |  | 685 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.46 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 5770.36 |  |  | 8157 |  |  |  | 685 | [10 empty] | 92.80 |  |  |  | 92.80 | [5 empty] | 96.16 |  |  | 93.12 |  |  |  | 0.66 |  | 0.61 | [8 empty] | 6.59 |  |  |  |  | 0.00
2008 |  |  |  | 5861.40 |  |  | 8271 |  |  |  | 708 | [10 empty] | 94.15 |  |  |  | 94.23 | [5 empty] | 94.25 |  |  | 94.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.77 |  |  |  |  | 0.08
2009 |  |  |  | 5714.06 |  |  | 8079 |  |  |  | 708 | [10 empty] | 92.41 |  |  |  | 92.67 | [5 empty] | 92.13 |  |  | 92.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.33 |  |  |  |  | 0.26
2010 |  |  |  | 5831.20 |  |  | 8218 |  |  |  | 708 | [10 empty] | 93.70 |  |  |  | 93.76 | [5 empty] | 94.02 |  |  | 93.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.24 |  |  |  |  | 0.06
2011 |  |  |  | 5828.85 |  |  | 8215 |  |  |  | 708 | [10 empty] | 93.51 |  |  |  | 93.71 | [5 empty] | 93.98 |  |  | 93.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.29 |  |  |  |  | 0.20
2012 |  |  |  | 6105.67 |  |  | 8702 |  |  |  | 694 | [10 empty] | 98.60 |  |  |  | 98.60 | [5 empty] | 100.16 |  |  | 99.07 |  |  |  | 1.00 |  | 1.00 | [8 empty] | 0.40 |  |  |  |  | 0.00
2013 |  |  |  | 5364.39 |  |  | 7761 |  |  |  | 688 | [10 empty] | 88.30 |  |  |  | 88.47 | [5 empty] | 89.01 |  |  | 88.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.53 |  |  |  |  | 0.17
2014 |  |  |  | 4970.75 |  |  | 7307 |  |  |  | 669 | [10 empty] | 83.30 |  |  |  | 83.30 | [5 empty] | 84.82 |  |  | 83.41 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 16.68 |  |  |  |  | 0.00
2015 |  |  |  | 5117.75 |  |  | 7636 |  |  |  | 669 | [10 empty] | 87.07 |  |  |  | 87.07 | [5 empty] | 87.33 |  |  | 87.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.93 |  |  |  |  | 0.00
2016 |  |  |  | 4334.90 |  |  | 6720 |  |  |  | 653 | [10 empty] | 75.91 |  |  |  | 89.83 | [5 empty] | 75.57 |  |  | 76.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.17 |  |  |  |  | 13.92
2017 |  |  |  | 5517.85 |  |  | 8760 |  |  |  | 635 | [10 empty] | 99.63 |  |  |  | 100.00 | [5 empty] | 99.20 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.37
2018 |  |  |  | 4494.93 |  |  | 7354 |  |  |  | 622 | [10 empty] | 83.24 |  |  |  | 83.87 | [5 empty] | 82.50 |  |  | 83.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.13 |  |  |  |  | 0.62
2019 |  |  |  | 4420.51 |  |  | 7310 |  |  |  | 609 | [10 empty] | 82.07 |  |  |  | 83.34 | [5 empty] | 82.86 |  |  | 83.45 |  |  |  | 0.15 |  | 3.41 | [8 empty] | 13.25 |  |  |  |  | 1.27
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1999 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 299 | [14 empty] | 22
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 98
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 1151 | [14 empty] | 580
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 59
Subtotal | [22 empty] | 1151 |  |  |  | 299 | [10 empty] | 678 |  |  |  | 22 | [11 empty] | 61
Total | [22 empty] | 1450 | [14 empty] | 761
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1999 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [19 empty] | 288 | [14 empty] | 14
16. |  |  | Steam generation systems | [19 empty] | 11 | [14 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [22 empty] | 299 | [14 empty] | 23
Highlights (2019)
Inspection and Maintenance(2019.04.22 ~ 2019.06.21) Turbine trip because of steam generator high level(2019.06.21 ~ 2019.06.21)