## BORSSELE
2019 Operating Experience
NL-2 | [8 empty] | BORSSELE | [26 empty] | NETHERLANDS
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EPZ (N.V. ELEKTRICITEITS-PRODUKTIEMAATSCHAPPIJ ZUID-NEDERLAND)
Owner | [7 empty] | : | EPZ (N.V. ELEKTRICITEITS-PRODUKTIEMAATSCHAPPIJ ZUID-NEDERLAND)
Reactor Supplier | [7 empty] | : | S/KWU (SIEMENS/KRAFTWERK UNION, AG.)
Turbine Supplier | [7 empty] | : | S/KWU (SIEMENS/KRAFTWERK UNION, AG.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / KWU 2LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1969-07-01
Thermal power | [12 empty] | : |  |  | 1366 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-07-04
Gross electrical power | [12 empty] | : |  |  | 515 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-10-26
Reference unit power (net) | [12 empty] | : |  |  | 482 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 313
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.49
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 11 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 23 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 39000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 2.676 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.75
| Active core height/length [m] | [13 empty] | : |  |  | 2.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 21
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.26 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 5
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2019)
Net Energy Production | [18 empty] | : | 3700.71 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.64 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.84 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.39 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.05 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.56 %
Load Factor (LF) | [18 empty] | : | 87.66 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.22 %
Operating Factor (OF) | [18 empty] | : | 88.7 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 990 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 360.77 | 247.61 |  |  |  | 359.37 |  | 347.09 | [8 empty] | 329.66 |  |  | 31.74 | [6 empty] | 308.64 |  | 317.60 |  |  |  | 336.72 |  |  | 353.75 |  |  | 347.51 | [9 empty] | 360.24 |  |  | 3700.71
EAF [%] |  |  |  |  | 99.56 | 75.23 |  |  |  | 99.44 |  | 99.48 | [8 empty] | 91.13 |  |  | 8.98 | [6 empty] | 85.99 |  | 86.70 |  |  |  | 95.92 |  |  | 98.02 |  |  | 99.56 | [9 empty] | 99.55 |  |  | 86.84
UCF [%] |  |  |  |  | 99.56 | 75.42 |  |  |  | 99.44 |  | 99.48 | [8 empty] | 92.36 |  |  | 10.19 | [6 empty] | 88.90 |  | 91.28 |  |  |  | 98.89 |  |  | 99.37 |  |  | 99.56 | [9 empty] | 99.55 |  |  | 88.05
LF [%] |  |  |  |  | 100.60 | 76.45 |  |  |  | 100.35 |  | 100.01 | [8 empty] | 91.93 |  |  | 9.15 | [6 empty] | 86.07 |  | 88.56 |  |  |  | 97.03 |  |  | 98.65 |  |  | 100.14 | [9 empty] | 100.46 |  |  | 87.66
OF [%] |  |  |  |  | 100.00 | 76.64 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 92.74 |  |  | 10.28 | [6 empty] | 88.98 |  | 93.15 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.70
FLR [%] |  |  |  |  | 0.44 | 5.59 |  |  |  | 0.55 |  | 0.51 | [8 empty] | 0.41 |  |  | 0.00 | [6 empty] | 11.09 |  | 8.71 |  |  |  | 0.95 |  |  | 0.62 |  |  | 0.43 | [9 empty] | 0.45 |  |  | 2.64
UCL [%] |  |  |  |  | 0.44 | 4.46 |  |  |  | 0.55 |  | 0.51 | [8 empty] | 0.38 |  |  | 0.00 | [6 empty] | 11.09 |  | 8.71 |  |  |  | 0.95 |  |  | 0.62 |  |  | 0.43 | [9 empty] | 0.45 |  |  | 2.39
PUF [%] |  |  |  |  | 0.00 | 20.12 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 7.26 |  |  | 89.81 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.16 |  |  | 0.01 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 9.56
XUF [%] |  |  |  |  | 0.00 | 0.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.23 |  |  | 1.21 | [6 empty] | 2.91 |  | 4.58 |  |  |  | 2.98 |  |  | 1.35 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.22
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 156027 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.26 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.66 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.17 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.63 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.03 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.5 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.92 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 665.30 |  |  | 2682 |  |  |  | 448 | [10 empty] | 47.75 |  |  |  | 47.75 | [5 empty] | 47.72 |  |  | 71.31 |  |  |  | 52.25 |  | 52.25 | [8 empty] | 0.00 |  |  |  |  | 0.00
1974 |  |  |  | 2993.70 |  |  | 6840 |  |  |  | 477 | [10 empty] | 71.63 |  |  |  | 71.63 | [5 empty] | 71.64 |  |  | 78.08 |  |  |  | 12.52 |  | 10.25 | [8 empty] | 18.12 |  |  |  |  | 0.00
1975 |  |  |  | 2776.90 |  |  | 6494 |  |  |  | 447 | [10 empty] | 70.83 |  |  |  | 70.83 | [5 empty] | 70.92 |  |  | 74.13 |  |  |  | 4.64 |  | 3.45 | [8 empty] | 25.72 |  |  |  |  | 0.00
1976 |  |  |  | 3274.40 |  |  | 7521 |  |  |  | 450 | [10 empty] | 82.76 |  |  |  | 82.76 | [5 empty] | 82.84 |  |  | 85.62 |  |  |  | 6.12 |  | 5.40 | [8 empty] | 11.84 |  |  |  |  | 0.00
1977 |  |  |  | 3142.40 |  |  | 7318 |  |  |  | 450 | [10 empty] | 80.38 |  |  |  | 80.38 | [5 empty] | 79.72 |  |  | 83.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.62 |  |  |  |  | 0.00
1978 |  |  |  | 3424.10 |  |  | 7997 |  |  |  | 445 | [10 empty] | 88.37 |  |  |  | 88.37 | [5 empty] | 87.84 |  |  | 91.29 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 11.47 |  |  |  |  | 0.00
1979 |  |  |  | 2900.00 |  |  | 6785 |  |  |  | 445 | [10 empty] | 83.48 |  |  |  | 83.48 | [5 empty] | 74.39 |  |  | 77.45 |  |  |  | 4.96 |  | 4.36 | [8 empty] | 12.16 |  |  |  |  | 0.00
1980 |  |  |  | 3593.00 |  |  | 8496 |  |  |  | 447 | [10 empty] | 92.85 |  |  |  | 92.85 | [5 empty] | 91.51 |  |  | 96.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.15 |  |  |  |  | 0.00
1981 |  |  |  | 3048.30 |  |  | 7094 |  |  |  | 447 | [10 empty] | 78.79 |  |  |  | 78.79 | [5 empty] | 77.85 |  |  | 80.98 |  |  |  | 0.35 |  | 0.28 | [8 empty] | 20.93 |  |  |  |  | 0.00
1982 |  |  |  | 3315.90 |  |  | 7489 |  |  |  | 452 | [10 empty] | 83.86 |  |  |  | 83.86 | [5 empty] | 83.74 |  |  | 85.49 |  |  |  | 0.38 |  | 0.32 | [8 empty] | 15.83 |  |  |  |  | 0.00
1983 |  |  |  | 3050.00 |  |  | 6959 |  |  |  | 452 | [10 empty] | 76.92 |  |  |  | 76.92 | [5 empty] | 77.03 |  |  | 79.44 |  |  |  | 15.15 |  | 13.73 | [8 empty] | 9.35 |  |  |  |  | 0.00
1984 |  |  |  | 3062.00 |  |  | 6895 |  |  |  | 452 | [10 empty] | 76.65 |  |  |  | 76.65 | [5 empty] | 77.12 |  |  | 78.49 |  |  |  | 11.71 |  | 10.16 | [8 empty] | 13.19 |  |  |  |  | 0.00
1985 |  |  |  | 3261.15 |  |  | 7299 |  |  |  | 452 | [10 empty] | 81.94 |  |  |  | 83.28 | [5 empty] | 82.36 |  |  | 83.32 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 16.71 |  |  |  |  | 1.35
1986 |  |  |  | 3574.00 |  |  | 8053 |  |  |  | 452 | [10 empty] | 89.93 |  |  |  | 91.58 | [5 empty] | 90.26 |  |  | 91.93 |  |  |  | 0.69 |  | 0.64 | [8 empty] | 7.78 |  |  |  |  | 1.65
1987 |  |  |  | 2950.93 |  |  | 6756 |  |  |  | 452 | [10 empty] | 74.24 |  |  |  | 76.64 | [5 empty] | 74.53 |  |  | 77.12 |  |  |  | 5.35 |  | 4.33 | [8 empty] | 19.03 |  |  |  |  | 2.40
1988 |  |  |  | 3032.55 |  |  | 6763 |  |  |  | 452 | [10 empty] | 76.17 |  |  |  | 76.17 | [5 empty] | 76.38 |  |  | 76.99 |  |  |  | 0.69 |  | 0.53 | [8 empty] | 23.30 |  |  |  |  | 0.00
1989 |  |  |  | 3421.85 |  |  | 7711 |  |  |  | 481 | [10 empty] | 87.83 |  |  |  | 87.83 | [5 empty] | 81.21 |  |  | 88.03 |  |  |  | 0.78 |  | 0.69 | [8 empty] | 11.48 |  |  |  |  | 0.00
1990 |  |  |  | 2885.86 |  |  | 6636 |  |  |  | 481 | [10 empty] | 75.65 |  |  |  | 75.65 | [5 empty] | 68.49 |  |  | 75.75 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 24.35 |  |  |  |  | 0.00
1991 |  |  |  | 2728.53 |  |  | 6221 |  |  |  | 452 | [10 empty] | 69.24 |  |  |  | 69.29 | [5 empty] | 68.91 |  |  | 71.02 |  |  |  | 23.33 |  | 21.09 | [8 empty] | 9.62 |  |  |  |  | 0.05
1992 |  |  |  | 2830.34 |  |  | 6412 |  |  |  | 452 | [10 empty] | 80.59 |  |  |  | 82.86 | [5 empty] | 71.29 |  |  | 73.00 |  |  |  | 0.66 |  | 0.55 | [8 empty] | 16.59 |  |  |  |  | 2.27
1993 |  |  |  | 3328.15 |  |  | 7376 |  |  |  | 452 | [10 empty] | 83.59 |  |  |  | 84.27 | [5 empty] | 84.05 |  |  | 84.20 |  |  |  | 6.31 |  | 5.68 | [8 empty] | 10.05 |  |  |  |  | 0.68
1994 |  |  |  | 3321.97 |  |  | 7489 |  |  |  | 452 | [10 empty] | 84.10 |  |  |  | 84.75 | [5 empty] | 83.90 |  |  | 85.49 |  |  |  | 3.51 |  | 3.09 | [8 empty] | 12.16 |  |  |  |  | 0.65
1995 |  |  |  | 3386.75 |  |  | 7654 |  |  |  | 452 | [10 empty] | 86.84 |  |  |  | 87.08 | [5 empty] | 85.53 |  |  | 87.37 |  |  |  | 5.56 |  | 5.13 | [8 empty] | 7.79 |  |  |  |  | 0.25
1996 |  |  |  | 3520.28 |  |  | 7978 |  |  |  | 452 | [10 empty] | 88.15 |  |  |  | 88.27 | [5 empty] | 88.66 |  |  | 90.82 |  |  |  | 2.91 |  | 2.64 | [8 empty] | 9.09 |  |  |  |  | 0.12
1997 |  |  |  | Data not provided
1998 |  |  |  | "
1999 |  |  |  | 3604.20 |  |  | 8363 |  |  |  | 449 | [10 empty] | 94.19 |  |  |  | 94.19 | [5 empty] | 91.63 |  |  | 95.47 |  |  |  | 0.94 |  | 0.89 | [8 empty] | 4.91 |  |  |  |  | 0.00
2000 |  |  |  | 3698.96 |  |  | 8262 |  |  |  | 449 | [10 empty] | 93.09 |  |  |  | 93.89 | [5 empty] | 93.79 |  |  | 94.06 |  |  |  | 2.38 |  | 2.29 | [8 empty] | 3.82 |  |  |  |  | 0.80
2001 |  |  |  | 3746.67 |  |  | 8404 |  |  |  | 449 | [10 empty] | 94.61 |  |  |  | 94.61 | [5 empty] | 95.26 |  |  | 95.94 |  |  |  | 0.21 |  | 0.20 | [8 empty] | 5.19 |  |  |  |  | 0.00
2002 |  |  |  | 3686.89 |  |  | 8284 |  |  |  | 450 | [10 empty] | 93.36 |  |  |  | 93.80 | [5 empty] | 93.53 |  |  | 94.57 |  |  |  | 0.10 |  | 1.23 | [8 empty] | 4.97 |  |  |  |  | 0.44
2003 |  |  |  | 3788.31 |  |  | 8431 |  |  |  | 450 | [10 empty] | 95.31 |  |  |  | 95.31 | [5 empty] | 96.10 |  |  | 96.24 |  |  |  | 1.09 |  | 1.44 | [8 empty] | 3.25 |  |  |  |  | 0.00
2004 |  |  |  | 3604.69 |  |  | 8073 |  |  |  | 450 | [10 empty] | 91.09 |  |  |  | 91.09 | [5 empty] | 91.19 |  |  | 91.91 |  |  |  | 1.19 |  | 2.26 | [8 empty] | 6.65 |  |  |  |  | 0.00
2005 |  |  |  | 3771.93 |  |  | 8430 |  |  |  | 450 | [10 empty] | 95.49 |  |  |  | 95.92 | [5 empty] | 95.69 |  |  | 96.23 |  |  |  | 1.65 |  | 1.61 | [8 empty] | 2.47 |  |  |  |  | 0.43
2006 |  |  |  | 3272.61 |  |  | 7542 |  |  |  | 482 | [10 empty] | 84.57 |  |  |  | 85.70 | [5 empty] | 82.52 |  |  | 86.10 |  |  |  | 1.72 |  | 1.50 | [8 empty] | 12.80 |  |  |  |  | 1.14
2007 |  |  |  | 3993.87 |  |  | 8346 |  |  |  | 482 | [10 empty] | 95.12 |  |  |  | 95.23 | [5 empty] | 94.59 |  |  | 95.27 |  |  |  | 0.34 |  | 0.78 | [8 empty] | 3.99 |  |  |  |  | 0.11
2008 |  |  |  | 3933.64 |  |  | 8161 |  |  |  | 482 | [10 empty] | 92.55 |  |  |  | 92.55 | [5 empty] | 92.91 |  |  | 92.91 |  |  |  | 0.04 |  | 4.14 | [8 empty] | 3.31 |  |  |  |  | 0.00
2009 |  |  |  | 4017.67 |  |  | 8352 |  |  |  | 482 | [10 empty] | 95.08 |  |  |  | 95.13 | [5 empty] | 95.15 |  |  | 95.34 |  |  |  | 0.92 |  | 0.90 | [8 empty] | 3.96 |  |  |  |  | 0.05
2010 |  |  |  | 3754.88 |  |  | 7807 |  |  |  | 482 | [10 empty] | 88.86 |  |  |  | 89.09 | [5 empty] | 88.93 |  |  | 89.12 |  |  |  | 1.78 |  | 2.55 | [8 empty] | 8.36 |  |  |  |  | 0.23
2011 |  |  |  | 3917.24 |  |  | 8092 |  |  |  | 482 | [10 empty] | 92.08 |  |  |  | 92.86 | [5 empty] | 92.77 |  |  | 92.37 |  |  |  | 1.53 |  | 1.89 | [8 empty] | 5.25 |  |  |  |  | 0.78
2012 |  |  |  | 3706.68 |  |  | 7722 |  |  |  | 482 | [10 empty] | 86.89 |  |  |  | 87.43 | [5 empty] | 87.55 |  |  | 87.91 |  |  |  | 5.52 |  | 5.10 | [8 empty] | 7.47 |  |  |  |  | 0.54
2013 |  |  |  | 2736.93 |  |  | 5737 |  |  |  | 482 | [10 empty] | 63.71 |  |  |  | 64.84 | [5 empty] | 64.81 |  |  | 65.48 |  |  |  | 26.51 |  | 25.02 | [8 empty] | 10.15 |  |  |  |  | 1.12
2014 |  |  |  | 3873.51 |  |  | 8054 |  |  |  | 482 | [10 empty] | 91.18 |  |  |  | 91.95 | [5 empty] | 91.75 |  |  | 91.95 |  |  |  | 1.23 |  | 4.35 | [8 empty] | 3.70 |  |  |  |  | 0.77
2015 |  |  |  | 3861.63 |  |  | 8020 |  |  |  | 482 | [10 empty] | 90.48 |  |  |  | 91.27 | [5 empty] | 91.47 |  |  | 91.56 |  |  |  | 3.86 |  | 5.03 | [8 empty] | 3.70 |  |  |  |  | 0.78
2016 |  |  |  | 3749.81 |  |  | 7836 |  |  |  | 482 | [10 empty] | 87.85 |  |  |  | 89.11 | [5 empty] | 88.58 |  |  | 89.22 |  |  |  | 0.63 |  | 0.67 | [8 empty] | 10.22 |  |  |  |  | 1.26
2017 |  |  |  | 3263.18 |  |  | 6672 |  |  |  | 482 | [10 empty] | 75.60 |  |  |  | 77.23 | [5 empty] | 77.28 |  |  | 76.16 |  |  |  | 5.93 |  | 4.87 | [8 empty] | 17.90 |  |  |  |  | 1.63
2018 |  |  |  | 3340.53 |  |  | 6997 |  |  |  | 482 | [10 empty] | 78.30 |  |  |  | 79.70 | [5 empty] | 79.13 |  |  | 79.88 |  |  |  | 12.43 |  | 13.88 | [8 empty] | 6.41 |  |  |  |  | 1.41
2019 |  |  |  | 3700.71 |  |  | 7769 |  |  |  | 482 | [10 empty] | 86.84 |  |  |  | 88.05 | [5 empty] | 87.66 |  |  | 88.70 |  |  |  | 2.64 |  | 2.39 | [8 empty] | 9.56 |  |  |  |  | 1.22
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2019 | [14 empty] | 1973 to 2019
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 165 | [14 empty] | 232
B. |  | Refuelling without maintenance | [35 empty] | 23
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 700 | [14 empty] | 730 |  |  |  | 20
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 143 | [14 empty] | 41
E. |  | Testing of plant systems or components | [39 empty] | 19
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 22
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
Z. |  | Other | [35 empty] | 14 |  |  |  | 3
Subtotal | [22 empty] | 843 |  |  |  | 165 | [10 empty] | 830 |  |  |  | 277 | [11 empty] | 6
Total | [22 empty] | 1008 | [14 empty] | 1113
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2019 | [14 empty] | 1973 to 2019
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 32
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 29
15. |  |  | Reactor Cooling Systems | [34 empty] | 19
16. |  |  | Steam generation systems | [34 empty] | 29
31. |  |  | Turbine and auxiliaries | [19 empty] | 28 | [14 empty] | 19
32. |  |  | Feedwater and Main Steam System | [34 empty] | 27
33. |  |  | Circulating Water System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 24
41. |  |  | Main Generator Systems | [19 empty] | 137 | [14 empty] | 44
42. |  |  | Electrical Power Supply Systems | [34 empty] | 18
Total | [22 empty] | 165 | [14 empty] | 257
Highlights (2019)
TUSA caused by addressing turbine speed sensor TUSA caused by generator protection system RL-releb