## BRUCE-1
2020 Operating Experience
CA-8 | [9 empty] | BRUCE-1 | [28 empty] | CANADA
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | BRUCEPOW (Bruce Power)
Owner | [8 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [8 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [8 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PHWR / CANDU 791 | [12 empty] | Construction Date | [16 empty] | : |  |  | 1971-06-01
Thermal power | [14 empty] | : |  |  | 2620 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 1977-01-14
Gross electrical power | [14 empty] | : |  |  | 830 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 1977-09-01
Reference unit power (net) | [14 empty] | : |  |  | 774 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Horizontal | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 300
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 8
| Refuelling type | [15 empty] | : |  |  | ON-line | [12 empty] | Containment type | [16 empty] | : |  |  | -
| Moderator material | [15 empty] | : |  |  | D2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | - | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | - | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 1
| Part of the core refuelled [%] | [15 empty] | : |  |  | - | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | 8750 | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | -
| Active core diameter [m] | [15 empty] | : |  |  | 5.67 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 4.37
| Active core height/length [m] | [15 empty] | : |  |  | 5.94 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 6240 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 24.5 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | -
| Number of control rod assemblies | [15 empty] | : |  |  | 4 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | -
| Number of external reactor coolant loops | [15 empty] | : |  |  | - | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | -
| Coolant type | [15 empty] | : |  |  | D2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [20 empty] | : | 6658.49 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 0.76 %
Energy Availability Factor (EAF) | [20 empty] | : | 98.13 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 0.75 %
Unit Capability Factor (UCF) | [20 empty] | : | 98.15 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 1.1 %
Load Factor (LF) | [20 empty] | : | 97.94 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0.02 %
Operating Factor (OF) | [20 empty] | : | 98.25 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 154 hours
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 580.58 |  | 543.79 |  |  |  |  | 580.86 |  | 560.81 | [8 empty] | 580.36 |  |  |  | 555.83 | [6 empty] | 524.78 |  | 575.72 |  |  |  |  | 490.67 |  |  | 526.97 |  |  | 559.55 | [9 empty] | 578.57 |  |  | 6658.49
EAF [%] |  |  |  |  | 99.99 |  | 99.99 |  |  |  |  | 99.79 |  | 99.90 | [8 empty] | 99.85 |  |  |  | 99.77 | [6 empty] | 99.92 |  | 99.74 |  |  |  |  | 87.60 |  |  | 91.64 |  |  | 99.78 | [9 empty] | 99.47 |  |  | 98.13
UCF [%] |  |  |  |  | 99.99 |  | 99.99 |  |  |  |  | 99.79 |  | 99.90 | [8 empty] | 99.85 |  |  |  | 99.77 | [6 empty] | 100.00 |  | 99.93 |  |  |  |  | 87.61 |  |  | 91.64 |  |  | 99.78 | [9 empty] | 99.47 |  |  | 98.15
LF [%] |  |  |  |  | 100.82 |  | 100.94 |  |  |  |  | 100.87 |  | 100.63 | [8 empty] | 100.78 |  |  |  | 99.74 | [6 empty] | 91.13 |  | 99.98 |  |  |  |  | 88.05 |  |  | 91.51 |  |  | 100.41 | [9 empty] | 100.47 |  |  | 97.94
OF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  |  | 87.92 |  |  | 90.99 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.25
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.17 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.42 |  |  | 8.34 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.76
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.17 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.37 |  |  | 8.34 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.75
PUF [%] |  |  |  |  | 0.01 |  | 0.01 |  |  |  |  | 0.04 |  | 0.10 | [8 empty] | 0.15 |  |  |  | 0.23 | [6 empty] | 0.00 |  | 0.07 |  |  |  |  | 12.02 |  |  | 0.01 |  |  | 0.22 | [9 empty] | 0.53 |  |  | 1.10
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.08 |  | 0.19 |  |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 140376.33 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 19.26 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 71.99 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 17.3 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 72.46 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 10.24 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 71.38 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.47 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 80.59 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 1860.70 |  |  |  | 2698 |  |  |  |  | 740 | [10 empty] | 88.40 |  |  |  |  | 88.40 | [5 empty] | 88.04 |  |  | 94.47 |  |  |  |  | 11.60 |  | 11.60 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 4152.60 |  |  |  | 6649 |  |  |  |  | 740 | [10 empty] | 72.65 |  |  |  |  | 72.65 | [5 empty] | 64.24 |  |  | 76.11 |  |  |  |  | 15.38 |  | 13.20 | [8 empty] | 14.15 |  |  |  |  | 0.00
1979 |  |  |  | 5018.80 |  |  |  | 7334 |  |  |  |  | 740 | [10 empty] | 81.48 |  |  |  |  | 81.48 | [5 empty] | 76.58 |  |  | 82.81 |  |  |  |  | 18.52 |  | 18.52 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 5597.50 |  |  |  | 7902 |  |  |  |  | 740 | [10 empty] | 86.18 |  |  |  |  | 86.18 | [5 empty] | 86.11 |  |  | 89.96 |  |  |  |  | 7.87 |  | 7.36 | [8 empty] | 6.46 |  |  |  |  | 0.00
1981 |  |  |  | 6253.30 |  |  |  | 8486 |  |  |  |  | 740 | [10 empty] | 96.66 |  |  |  |  | 96.66 | [5 empty] | 96.47 |  |  | 96.87 |  |  |  |  | 3.34 |  | 3.34 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 5914.90 |  |  |  | 7884 |  |  |  |  | 740 | [10 empty] | 88.80 |  |  |  |  | 88.80 | [5 empty] | 91.25 |  |  | 90.00 |  |  |  |  | 11.20 |  | 11.20 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 5802.80 |  |  |  | 7590 |  |  |  |  | 740 | [10 empty] | 84.81 |  |  |  |  | 84.81 | [5 empty] | 89.52 |  |  | 86.64 |  |  |  |  | 15.04 |  | 15.01 | [8 empty] | 0.18 |  |  |  |  | 0.00
1984 |  |  |  | 6457.62 |  |  |  | 8546 |  |  |  |  | 740 | [10 empty] | 94.76 |  |  |  |  | 94.76 | [5 empty] | 99.35 |  |  | 97.29 |  |  |  |  | 5.10 |  | 5.09 | [8 empty] | 0.15 |  |  |  |  | 0.00
1985 |  |  |  | 6417.45 |  |  |  | 8349 |  |  |  |  | 772 | [10 empty] | 94.89 |  |  |  |  | 99.99 | [5 empty] | 94.78 |  |  | 95.31 |  |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.00 |  |  |  |  | 5.10
1986 |  |  |  | 4398.02 |  |  |  | 5783 |  |  |  |  | 770 | [10 empty] | 65.33 |  |  |  |  | 65.97 | [5 empty] | 65.20 |  |  | 66.02 |  |  |  |  | 0.07 |  | 0.05 | [8 empty] | 33.98 |  |  |  |  | 0.64
1987 |  |  |  | 4087.07 |  |  |  | 5462 |  |  |  |  | 848 | [10 empty] | 60.73 |  |  |  |  | 63.26 | [5 empty] | 55.02 |  |  | 62.35 |  |  |  |  | 19.62 |  | 15.44 | [8 empty] | 21.29 |  |  |  |  | 2.54
1988 |  |  |  | 4642.66 |  |  |  | 6066 |  |  |  |  | 848 | [10 empty] | 65.95 |  |  |  |  | 66.85 | [5 empty] | 62.33 |  |  | 69.06 |  |  |  |  | 15.12 |  | 11.91 | [8 empty] | 21.24 |  |  |  |  | 0.89
1989 |  |  |  | 5094.78 |  |  |  | 7543 |  |  |  |  | 848 | [10 empty] | 68.74 |  |  |  |  | 69.91 | [5 empty] | 68.58 |  |  | 86.11 |  |  |  |  | 25.23 |  | 23.59 | [8 empty] | 6.50 |  |  |  |  | 1.16
1990 |  |  |  | 2451.13 |  |  |  | 4629 |  |  |  |  | 848 | [10 empty] | 32.98 |  |  |  |  | 33.58 | [5 empty] | 33.00 |  |  | 52.84 |  |  |  |  | 39.00 |  | 21.46 | [8 empty] | 44.96 |  |  |  |  | 0.60
1991 |  |  |  | 2394.45 |  |  |  | 3467 |  |  |  |  | 848 | [10 empty] | 32.22 |  |  |  |  | 34.08 | [5 empty] | 32.23 |  |  | 39.58 |  |  |  |  | 65.87 |  | 65.78 | [8 empty] | 0.14 |  |  |  |  | 1.87
1992 |  |  |  | 4546.54 |  |  |  | 7484 |  |  |  |  | 848 | [10 empty] | 61.04 |  |  |  |  | 61.04 | [5 empty] | 61.04 |  |  | 85.20 |  |  |  |  | 38.96 |  | 38.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 3389.20 |  |  |  | 6869 |  |  |  |  | 848 | [10 empty] | 45.67 |  |  |  |  | 45.67 | [5 empty] | 45.62 |  |  | 78.41 |  |  |  |  | 45.60 |  | 38.28 | [8 empty] | 16.06 |  |  |  |  | 0.00
1994 |  |  |  | 3849.03 |  |  |  | 7094 |  |  |  |  | 848 | [10 empty] | 51.81 |  |  |  |  | 51.81 | [5 empty] | 51.81 |  |  | 80.98 |  |  |  |  | 48.19 |  | 48.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 3531.45 |  |  |  | 5827 |  |  |  |  | 848 | [10 empty] | 47.54 |  |  |  |  | 47.54 | [5 empty] | 47.54 |  |  | 66.52 |  |  |  |  | 34.50 |  | 25.04 | [8 empty] | 27.42 |  |  |  |  | 0.00
1996 |  |  |  | 4326.40 |  |  |  | 7306 |  |  |  |  | 848 | [10 empty] | 58.09 |  |  |  |  | 58.09 | [5 empty] | 58.08 |  |  | 83.17 |  |  |  |  | 39.23 |  | 37.49 | [8 empty] | 4.42 |  |  |  |  | 0.00
1997 |  |  |  | 1383.58 |  |  |  | 2254 |  |  |  |  | 848 | [10 empty] | 23.52 |  |  |  |  | 23.52 | [5 empty] | 23.52 |  |  | 32.50 |  |  |  |  | 63.04 |  | 40.12 | [8 empty] | 36.35 |  |  |  |  | 0.00
1998 |  |  |  | Data not available - Long-term shutdown
1999 |  |  |  | "
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | "
2005 |  |  |  | "
2006 |  |  |  | "
2007 |  |  |  | "
2008 |  |  |  | "
2009 |  |  |  | "
2010 |  |  |  | "
2011 |  |  |  | "
2012 |  |  |  | 743.65 |  |  |  | 1365 |  |  |  |  | 772 | [10 empty] | 42.86 |  |  |  |  | 42.86 | [5 empty] | 42.87 |  |  | 57.11 |  |  |  |  | 14.46 |  | 7.25 | [8 empty] | 49.90 |  |  |  |  | 0.00
2013 |  |  |  | 5257.07 |  |  |  | 7883 |  |  |  |  | 772 | [10 empty] | 85.98 |  |  |  |  | 86.14 | [5 empty] | 77.74 |  |  | 89.99 |  |  |  |  | 5.31 |  | 4.83 | [8 empty] | 9.03 |  |  |  |  | 0.16
2014 |  |  |  | 5630.95 |  |  |  | 7540 |  |  |  |  | 772 | [10 empty] | 85.52 |  |  |  |  | 85.52 | [5 empty] | 83.26 |  |  | 86.07 |  |  |  |  | 14.48 |  | 14.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 5816.97 |  |  |  | 7711 |  |  |  |  | 760 | [10 empty] | 86.96 |  |  |  |  | 86.96 | [5 empty] | 87.37 |  |  | 88.03 |  |  |  |  | 2.37 |  | 2.11 | [8 empty] | 10.94 |  |  |  |  | 0.00
2016 |  |  |  | 6122.17 |  |  |  | 8004 |  |  |  |  | 760 | [10 empty] | 90.36 |  |  |  |  | 90.42 | [5 empty] | 91.71 |  |  | 91.12 |  |  |  |  | 1.55 |  | 1.69 | [8 empty] | 7.89 |  |  |  |  | 0.06
2017 |  |  |  | 6434.23 |  |  |  | 8412 |  |  |  |  | 760 | [10 empty] | 95.42 |  |  |  |  | 95.42 | [5 empty] | 96.64 |  |  | 96.03 |  |  |  |  | 3.40 |  | 3.59 | [8 empty] | 0.99 |  |  |  |  | 0.01
2018 |  |  |  | 5424.38 |  |  |  | 7046 |  |  |  |  | 760 | [10 empty] | 79.92 |  |  |  |  | 79.93 | [5 empty] | 81.48 |  |  | 80.43 |  |  |  |  | 7.03 |  | 6.04 | [8 empty] | 14.03 |  |  |  |  | 0.01
2019 |  |  |  | 6720.15 |  |  |  | 8760 |  |  |  |  | 760 | [10 empty] | 99.95 |  |  |  |  | 99.95 | [5 empty] | 100.94 |  |  | 100.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  |  |  | 0.00
2020 |  |  |  | 6658.49 |  |  |  | 8630 |  |  |  |  | 774 | [10 empty] | 98.13 |  |  |  |  | 98.15 | [5 empty] | 97.94 |  |  | 98.25 |  |  |  |  | 0.76 |  | 0.75 | [8 empty] | 1.10 |  |  |  |  | 0.02
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2020 | [16 empty] | 1977 to 2020
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [27 empty] | 76 | [15 empty] | 811
D. |  | Inspection, maintenance or repair without refuelling | [22 empty] | 79 | [16 empty] | 751
E. |  | Testing of plant systems or components | [39 empty] | 80 |  |  |  | 3
H. |  | Nuclear regulatory requirements | [43 empty] | 18
J. |  | Grid limitation, failure or grid unavailability | [55 empty] | 5
L. |  | Human factor related | [43 empty] | 6
P. |  | Fire | [43 empty] | 5
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [55 empty] | 14
Z. |  | Other | [39 empty] | 12 |  |  |  | 3
Subtotal | [24 empty] | 79 |  |  |  |  | 76 | [11 empty] | 843 |  |  |  | 846 | [11 empty] | 19
Total | [24 empty] | 155 | [16 empty] | 1708
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2020 | [16 empty] | 1977 to 2020
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [38 empty] | 51
12. |  |  | Reactor I&C Systems | [21 empty] | 76 | [16 empty] | 78
13. |  |  | Reactor Auxiliary Systems | [38 empty] | 86
14. |  |  | Safety Systems | [38 empty] | 61
15. |  |  | Reactor Cooling Systems | [38 empty] | 88
16. |  |  | Steam generation systems | [38 empty] | 227
21. |  |  | Fuel Handling and Storage Facilities | [38 empty] | 28
31. |  |  | Turbine and auxiliaries | [38 empty] | 38
32. |  |  | Feedwater and Main Steam System | [38 empty] | 24
34. |  |  | Miscellaneous Systems | [38 empty] | 21
41. |  |  | Main Generator Systems | [38 empty] | 60
42. |  |  | Electrical Power Supply Systems | [38 empty] | 45
Total | [24 empty] | 76 | [16 empty] | 807
RUP revision during the year (2020) due to power uprate
RUP at the end of previous year : 760 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
January | [5 empty] | 774 |  |  |  |  | Stretch power uprate (2-7%) | [14 empty] | Balance of plant | [13 empty] | Reference Unit Power revised to 774MWs. Increase from 760MW (2019) due to engineering analysis of generator (previous limiting factor) which allowed increase in yearly net average output. Change in RUP retroactive to 1 Jan 2020.

## BRUCE-2
2020 Operating Experience
CA-9 | [9 empty] | BRUCE-2 | [28 empty] | CANADA
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | BRUCEPOW (Bruce Power)
Owner | [8 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [8 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [8 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PHWR / CANDU 791 | [12 empty] | Construction Date | [16 empty] | : |  |  | 1970-12-01
Thermal power | [14 empty] | : |  |  | 2620 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 1976-09-04
Gross electrical power | [14 empty] | : |  |  | 830 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 1977-09-01
Reference unit power (net) | [14 empty] | : |  |  | 777 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Horizontal | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 300
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 8
| Refuelling type | [15 empty] | : |  |  | ON-line | [12 empty] | Containment type | [16 empty] | : |  |  | -
| Moderator material | [15 empty] | : |  |  | D2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | - | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | - | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 1
| Part of the core refuelled [%] | [15 empty] | : |  |  | - | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | 8750 | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | -
| Active core diameter [m] | [15 empty] | : |  |  | 5.67 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 4.37
| Active core height/length [m] | [15 empty] | : |  |  | 5.94 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 6240 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 24.5 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | -
| Number of control rod assemblies | [15 empty] | : |  |  | 4 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | -
| Number of external reactor coolant loops | [15 empty] | : |  |  | - | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | -
| Coolant type | [15 empty] | : |  |  | D2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [20 empty] | : | 6717.44 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 1.69 %
Energy Availability Factor (EAF) | [20 empty] | : | 97.69 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 1.68 %
Unit Capability Factor (UCF) | [20 empty] | : | 97.69 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 0.63 %
Load Factor (LF) | [20 empty] | : | 98.42 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0 %
Operating Factor (OF) | [20 empty] | : | 97.72 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 200 hours
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 585.74 |  | 548.02 |  |  |  |  | 542.94 |  | 565.16 | [8 empty] | 515.12 |  |  |  | 555.03 | [6 empty] | 582.03 |  | 530.19 |  |  |  |  | 561.10 |  |  | 581.24 |  |  | 565.71 | [9 empty] | 585.17 |  |  | 6717.44
EAF [%] |  |  |  |  | 99.97 |  | 99.98 |  |  |  |  | 92.84 |  | 99.98 | [8 empty] | 88.77 |  |  |  | 99.89 | [6 empty] | 99.97 |  | 91.87 |  |  |  |  | 99.57 |  |  | 99.95 |  |  | 99.94 | [9 empty] | 99.95 |  |  | 97.69
UCF [%] |  |  |  |  | 99.97 |  | 99.98 |  |  |  |  | 92.84 |  | 99.98 | [8 empty] | 88.77 |  |  |  | 99.89 | [6 empty] | 99.97 |  | 91.87 |  |  |  |  | 99.57 |  |  | 99.95 |  |  | 99.94 | [9 empty] | 99.95 |  |  | 97.69
LF [%] |  |  |  |  | 101.32 |  | 101.34 |  |  |  |  | 93.92 |  | 101.02 | [8 empty] | 89.11 |  |  |  | 99.21 | [6 empty] | 100.68 |  | 91.71 |  |  |  |  | 100.30 |  |  | 100.55 |  |  | 101.12 | [9 empty] | 101.23 |  |  | 98.42
OF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 92.74 |  | 100.00 | [8 empty] | 88.71 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 91.67 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.72
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.23 |  |  |  | 0.06 | [6 empty] | 0.00 |  | 8.13 |  |  |  |  | 0.43 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.69
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.23 |  |  |  | 0.06 | [6 empty] | 0.00 |  | 8.13 |  |  |  |  | 0.43 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.68
PUF [%] |  |  |  |  | 0.03 |  | 0.02 |  |  |  |  | 7.16 |  | 0.02 | [8 empty] | 0.00 |  |  |  | 0.06 | [6 empty] | 0.03 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.05 |  |  | 0.06 | [9 empty] | 0.05 |  |  | 0.63
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 123445.1 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 21.22 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 68.82 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 18.85 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 69.3 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 11.85 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 68.24 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.48 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 75.52 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 1696.80 |  |  |  | 2481 |  |  |  |  | 740 | [10 empty] | 87.01 |  |  |  |  | 87.01 | [5 empty] | 80.29 |  |  | 86.87 |  |  |  |  | 12.99 |  | 12.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 3603.80 |  |  |  | 5946 |  |  |  |  | 740 | [10 empty] | 65.23 |  |  |  |  | 65.45 | [5 empty] | 55.75 |  |  | 68.06 |  |  |  |  | 22.17 |  | 18.65 | [8 empty] | 15.91 |  |  |  |  | 0.22
1979 |  |  |  | 4408.80 |  |  |  | 6534 |  |  |  |  | 740 | [10 empty] | 73.76 |  |  |  |  | 73.76 | [5 empty] | 67.27 |  |  | 73.78 |  |  |  |  | 19.40 |  | 17.75 | [8 empty] | 8.49 |  |  |  |  | 0.00
1980 |  |  |  | 6074.90 |  |  |  | 8463 |  |  |  |  | 740 | [10 empty] | 93.52 |  |  |  |  | 93.52 | [5 empty] | 93.46 |  |  | 96.35 |  |  |  |  | 6.48 |  | 6.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
1981 |  |  |  | 5795.10 |  |  |  | 7904 |  |  |  |  | 740 | [10 empty] | 89.57 |  |  |  |  | 89.57 | [5 empty] | 89.40 |  |  | 90.23 |  |  |  |  | 4.02 |  | 3.75 | [8 empty] | 6.67 |  |  |  |  | 0.00
1982 |  |  |  | 4432.40 |  |  |  | 6163 |  |  |  |  | 740 | [10 empty] | 68.00 |  |  |  |  | 68.00 | [5 empty] | 68.38 |  |  | 70.35 |  |  |  |  | 32.00 |  | 32.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 6112.80 |  |  |  | 7941 |  |  |  |  | 740 | [10 empty] | 89.51 |  |  |  |  | 89.51 | [5 empty] | 94.30 |  |  | 90.65 |  |  |  |  | 10.35 |  | 10.34 | [8 empty] | 0.15 |  |  |  |  | 0.00
1984 |  |  |  | 6223.90 |  |  |  | 8649 |  |  |  |  | 740 | [10 empty] | 91.03 |  |  |  |  | 91.03 | [5 empty] | 95.75 |  |  | 98.46 |  |  |  |  | 8.84 |  | 8.83 | [8 empty] | 0.15 |  |  |  |  | 0.00
1985 |  |  |  | 4979.30 |  |  |  | 6525 |  |  |  |  | 781 | [10 empty] | 73.54 |  |  |  |  | 77.95 | [5 empty] | 72.76 |  |  | 74.49 |  |  |  |  | 11.25 |  | 9.88 | [8 empty] | 12.17 |  |  |  |  | 4.41
1986 |  |  |  | 4257.63 |  |  |  | 5308 |  |  |  |  | 848 | [10 empty] | 56.97 |  |  |  |  | 59.21 | [5 empty] | 57.31 |  |  | 60.59 |  |  |  |  | 40.79 |  | 40.79 | [8 empty] | 0.00 |  |  |  |  | 2.24
1987 |  |  |  | 3781.40 |  |  |  | 4636 |  |  |  |  | 848 | [10 empty] | 50.56 |  |  |  |  | 52.18 | [5 empty] | 50.90 |  |  | 52.92 |  |  |  |  | 6.98 |  | 3.91 | [8 empty] | 43.91 |  |  |  |  | 1.62
1988 |  |  |  | 4971.25 |  |  |  | 7741 |  |  |  |  | 848 | [10 empty] | 71.70 |  |  |  |  | 71.70 | [5 empty] | 66.74 |  |  | 88.13 |  |  |  |  | 25.15 |  | 24.08 | [8 empty] | 4.22 |  |  |  |  | 0.00
1989 |  |  |  | 1316.31 |  |  |  | 2149 |  |  |  |  | 848 | [10 empty] | 17.72 |  |  |  |  | 17.82 | [5 empty] | 17.72 |  |  | 24.53 |  |  |  |  | 26.85 |  | 6.54 | [8 empty] | 75.64 |  |  |  |  | 0.10
1990 |  |  |  | 2578.32 |  |  |  | 3460 |  |  |  |  | 848 | [10 empty] | 35.22 |  |  |  |  | 35.48 | [5 empty] | 34.71 |  |  | 39.50 |  |  |  |  | 41.05 |  | 24.71 | [8 empty] | 39.81 |  |  |  |  | 0.26
1991 |  |  |  | 4483.48 |  |  |  | 5915 |  |  |  |  | 848 | [10 empty] | 60.25 |  |  |  |  | 63.20 | [5 empty] | 60.36 |  |  | 67.52 |  |  |  |  | 36.71 |  | 36.66 | [8 empty] | 0.15 |  |  |  |  | 2.95
1992 |  |  |  | 353.88 |  |  |  | 625 |  |  |  |  | 848 | [10 empty] | 4.73 |  |  |  |  | 4.73 | [5 empty] | 4.75 |  |  | 7.12 |  |  |  |  | 95.27 |  | 95.27 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 3016.81 |  |  |  | 6041 |  |  |  |  | 848 | [10 empty] | 40.75 |  |  |  |  | 40.75 | [5 empty] | 40.61 |  |  | 68.96 |  |  |  |  | 45.16 |  | 33.56 | [8 empty] | 25.69 |  |  |  |  | 0.00
1994 |  |  |  | 3882.47 |  |  |  | 7046 |  |  |  |  | 848 | [10 empty] | 52.26 |  |  |  |  | 52.26 | [5 empty] | 52.26 |  |  | 80.43 |  |  |  |  | 40.39 |  | 35.41 | [8 empty] | 12.32 |  |  |  |  | 0.00
1995 |  |  |  | 3791.00 |  |  |  | 6225 |  |  |  |  | 848 | [10 empty] | 66.34 |  |  |  |  | 66.34 | [5 empty] | 66.34 |  |  | 92.22 |  |  |  |  | 27.76 |  | 25.50 | [8 empty] | 8.16 |  |  |  |  | 0.00
1996 |  |  |  | Data not available - Long-term shutdown
1997 |  |  |  | "
1998 |  |  |  | "
1999 |  |  |  | "
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | "
2005 |  |  |  | "
2006 |  |  |  | "
2007 |  |  |  | "
2008 |  |  |  | "
2009 |  |  |  | "
2010 |  |  |  | "
2011 |  |  |  | "
2012 |  |  |  | 1039.20 |  |  |  | 1826 |  |  |  |  | 734 | [10 empty] | 85.69 |  |  |  |  | 85.71 | [5 empty] | 85.41 |  |  | 100.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.29 |  |  |  |  | 0.02
2013 |  |  |  | 5607.65 |  |  |  | 8190 |  |  |  |  | 734 | [10 empty] | 88.10 |  |  |  |  | 88.23 | [5 empty] | 87.21 |  |  | 93.49 |  |  |  |  | 7.18 |  | 6.82 | [8 empty] | 4.94 |  |  |  |  | 0.13
2014 |  |  |  | 4910.32 |  |  |  | 6984 |  |  |  |  | 734 | [10 empty] | 81.74 |  |  |  |  | 81.74 | [5 empty] | 76.37 |  |  | 79.73 |  |  |  |  | 18.26 |  | 18.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6365.71 |  |  |  | 8660 |  |  |  |  | 730 | [10 empty] | 98.65 |  |  |  |  | 98.65 | [5 empty] | 99.55 |  |  | 98.86 |  |  |  |  | 0.68 |  | 0.68 | [8 empty] | 0.68 |  |  |  |  | 0.00
2016 |  |  |  | 4804.60 |  |  |  | 6408 |  |  |  |  | 760 | [10 empty] | 73.21 |  |  |  |  | 73.23 | [5 empty] | 73.17 |  |  | 72.95 |  |  |  |  | 2.57 |  | 6.93 | [8 empty] | 19.84 |  |  |  |  | 0.02
2017 |  |  |  | 6482.56 |  |  |  | 8560 |  |  |  |  | 760 | [10 empty] | 97.35 |  |  |  |  | 97.35 | [5 empty] | 97.37 |  |  | 97.72 |  |  |  |  | 0.88 |  | 0.87 | [8 empty] | 1.78 |  |  |  |  | 0.00
2018 |  |  |  | 5989.70 |  |  |  | 7828 |  |  |  |  | 760 | [10 empty] | 88.11 |  |  |  |  | 88.12 | [5 empty] | 89.97 |  |  | 89.36 |  |  |  |  | 7.67 |  | 7.32 | [8 empty] | 4.55 |  |  |  |  | 0.01
2019 |  |  |  | 5766.96 |  |  |  | 7526 |  |  |  |  | 760 | [10 empty] | 85.27 |  |  |  |  | 85.27 | [5 empty] | 86.62 |  |  | 85.91 |  |  |  |  | 2.92 |  | 2.57 | [8 empty] | 12.16 |  |  |  |  | 0.00
2020 |  |  |  | 6717.44 |  |  |  | 8584 |  |  |  |  | 777 | [10 empty] | 97.69 |  |  |  |  | 97.69 | [5 empty] | 98.42 |  |  | 97.72 |  |  |  |  | 1.69 |  | 1.68 | [8 empty] | 0.63 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2020 | [16 empty] | 1977 to 2020
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [27 empty] | 140 | [15 empty] | 1051
D. |  | Inspection, maintenance or repair without refuelling | [22 empty] | 49 | [16 empty] | 950
E. |  | Testing of plant systems or components | [43 empty] | 2
H. |  | Nuclear regulatory requirements | [43 empty] | 10
J. |  | Grid limitation, failure or grid unavailability | [55 empty] | 27
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [55 empty] | 2
L. |  | Human factor related | [43 empty] | 41
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [55 empty] | 16
Z. |  | Other | [43 empty] | 34
Subtotal | [24 empty] | 49 |  |  |  |  | 140 | [11 empty] | 950 |  |  |  | 1138 | [11 empty] | 45
Total | [24 empty] | 189 | [16 empty] | 2133
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2020 | [16 empty] | 1977 to 2020
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [38 empty] | 132
12. |  |  | Reactor I&C Systems | [38 empty] | 51
13. |  |  | Reactor Auxiliary Systems | [38 empty] | 6
14. |  |  | Safety Systems | [38 empty] | 12
15. |  |  | Reactor Cooling Systems | [38 empty] | 142
16. |  |  | Steam generation systems | [38 empty] | 473
21. |  |  | Fuel Handling and Storage Facilities | [38 empty] | 29
31. |  |  | Turbine and auxiliaries | [38 empty] | 22
32. |  |  | Feedwater and Main Steam System | [21 empty] | 56 | [16 empty] | 13
34. |  |  | Miscellaneous Systems | [38 empty] | 15
35. |  |  | All other I&C Systems | [38 empty] | 2
41. |  |  | Main Generator Systems | [21 empty] | 84 | [16 empty] | 139
42. |  |  | Electrical Power Supply Systems | [38 empty] | 30
Total | [24 empty] | 140 | [16 empty] | 1066
RUP revision during the year (2020) due to power uprate
RUP at the end of previous year : 760 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
January | [5 empty] | 777 |  |  |  |  | Stretch power uprate (2-7%) | [14 empty] | Balance of plant | [13 empty] | Reference Unit Power revised to 777MWs. Increase from 760MW (2019) due to engineering analysis performed on Main Output Transformer limitations allowing net average output increase. Change in RUP retroactive to 1 Jan 2020.

## BRUCE-3
2020 Operating Experience
CA-10 | [9 empty] | BRUCE-3 | [28 empty] | CANADA
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | BRUCEPOW (Bruce Power)
Owner | [8 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [8 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [8 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PHWR / CANDU 750A | [12 empty] | Construction Date | [16 empty] | : |  |  | 1972-07-01
Thermal power | [14 empty] | : |  |  | 2550 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 1977-12-12
Gross electrical power | [14 empty] | : |  |  | 830 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 1978-02-01
Reference unit power (net) | [14 empty] | : |  |  | 770 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Horizontal | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 300
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 8
| Refuelling type | [15 empty] | : |  |  | ON-line | [12 empty] | Containment type | [16 empty] | : |  |  | -
| Moderator material | [15 empty] | : |  |  | D2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | - | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | - | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 1
| Part of the core refuelled [%] | [15 empty] | : |  |  | - | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | 8750 | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | -
| Active core diameter [m] | [15 empty] | : |  |  | 5.67 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 4.37
| Active core height/length [m] | [15 empty] | : |  |  | 5.94 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 6240 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 24.5 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | -
| Number of control rod assemblies | [15 empty] | : |  |  | 4 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | -
| Number of external reactor coolant loops | [15 empty] | : |  |  | - | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | -
| Coolant type | [15 empty] | : |  |  | D2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [20 empty] | : | 6776.48 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 1.35 %
Energy Availability Factor (EAF) | [20 empty] | : | 97.08 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 1.33 %
Unit Capability Factor (UCF) | [20 empty] | : | 97.12 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 1.54 %
Load Factor (LF) | [20 empty] | : | 100.19 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0.04 %
Operating Factor (OF) | [20 empty] | : | 97.61 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 210 hours
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 601.55 |  | 562.69 |  |  |  |  | 599.55 |  | 577.77 | [8 empty] | 590.25 |  |  |  | 417.18 | [6 empty] | 581.01 |  | 522.71 |  |  |  |  | 563.21 |  |  | 590.16 |  |  | 575.17 | [9 empty] | 595.23 |  |  | 6776.48
EAF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.98 |  |  |  | 74.77 | [6 empty] | 99.36 |  | 91.07 |  |  |  |  | 99.70 |  |  | 100.00 |  |  | 99.90 | [9 empty] | 99.96 |  |  | 97.08
UCF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.98 |  |  |  | 74.77 | [6 empty] | 99.36 |  | 91.36 |  |  |  |  | 99.87 |  |  | 100.00 |  |  | 99.90 | [9 empty] | 99.96 |  |  | 97.12
LF [%] |  |  |  |  | 105.00 |  | 105.00 |  |  |  |  | 104.66 |  | 104.22 | [8 empty] | 103.03 |  |  |  | 75.25 | [6 empty] | 101.42 |  | 91.24 |  |  |  |  | 101.59 |  |  | 103.02 |  |  | 103.75 | [9 empty] | 103.90 |  |  | 100.19
OF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 79.72 | [6 empty] | 100.00 |  | 91.40 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.61
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 8.14 | [6 empty] | 0.58 |  | 8.64 |  |  |  |  | 0.13 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.35
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 6.63 | [6 empty] | 0.58 |  | 8.64 |  |  |  |  | 0.13 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.33
PUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  | 18.61 | [6 empty] | 0.06 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.10 | [9 empty] | 0.04 |  |  | 1.54
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.30 |  |  |  |  | 0.18 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.04
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 176588.25 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 14.13 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 74.6 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 13.64 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 75.19 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 11.17 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 74.58 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.59 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 80.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1978 |  |  |  | 4793.00 |  |  |  | 7361 |  |  |  |  | 740 | [10 empty] | 87.56 |  |  |  |  | 87.56 | [5 empty] | 82.03 |  |  | 93.22 |  |  |  |  | 12.44 |  | 12.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
1979 |  |  |  | 4797.90 |  |  |  | 6885 |  |  |  |  | 740 | [10 empty] | 77.78 |  |  |  |  | 77.78 | [5 empty] | 73.21 |  |  | 77.74 |  |  |  |  | 11.80 |  | 10.41 | [8 empty] | 11.82 |  |  |  |  | 0.00
1980 |  |  |  | 5939.80 |  |  |  | 8276 |  |  |  |  | 740 | [10 empty] | 91.44 |  |  |  |  | 91.44 | [5 empty] | 91.38 |  |  | 94.22 |  |  |  |  | 8.56 |  | 8.56 | [8 empty] | 0.00 |  |  |  |  | 0.00
1981 |  |  |  | 5795.00 |  |  |  | 7873 |  |  |  |  | 740 | [10 empty] | 89.48 |  |  |  |  | 89.48 | [5 empty] | 89.40 |  |  | 89.87 |  |  |  |  | 4.74 |  | 4.45 | [8 empty] | 6.07 |  |  |  |  | 0.00
1982 |  |  |  | 6381.90 |  |  |  | 8497 |  |  |  |  | 740 | [10 empty] | 96.72 |  |  |  |  | 96.72 | [5 empty] | 98.45 |  |  | 97.00 |  |  |  |  | 3.28 |  | 3.28 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 6091.10 |  |  |  | 7905 |  |  |  |  | 740 | [10 empty] | 89.23 |  |  |  |  | 89.23 | [5 empty] | 93.96 |  |  | 90.24 |  |  |  |  | 10.64 |  | 10.62 | [8 empty] | 0.15 |  |  |  |  | 0.00
1984 |  |  |  | 6148.73 |  |  |  | 8077 |  |  |  |  | 740 | [10 empty] | 91.19 |  |  |  |  | 91.19 | [5 empty] | 94.59 |  |  | 91.95 |  |  |  |  | 8.56 |  | 8.54 | [8 empty] | 0.27 |  |  |  |  | 0.00
1985 |  |  |  | 6015.13 |  |  |  | 8118 |  |  |  |  | 775 | [10 empty] | 88.59 |  |  |  |  | 93.91 | [5 empty] | 88.60 |  |  | 92.67 |  |  |  |  | 6.09 |  | 6.09 | [8 empty] | 0.00 |  |  |  |  | 5.32
1986 |  |  |  | 5891.24 |  |  |  | 7600 |  |  |  |  | 796 | [10 empty] | 84.18 |  |  |  |  | 86.94 | [5 empty] | 84.48 |  |  | 86.76 |  |  |  |  | 13.01 |  | 13.00 | [8 empty] | 0.06 |  |  |  |  | 2.76
1987 |  |  |  | 6073.27 |  |  |  | 7724 |  |  |  |  | 848 | [10 empty] | 81.91 |  |  |  |  | 85.78 | [5 empty] | 81.76 |  |  | 88.17 |  |  |  |  | 7.86 |  | 7.32 | [8 empty] | 6.90 |  |  |  |  | 3.87
1988 |  |  |  | 3310.57 |  |  |  | 4044 |  |  |  |  | 848 | [10 empty] | 45.61 |  |  |  |  | 45.61 | [5 empty] | 44.44 |  |  | 46.04 |  |  |  |  | 4.02 |  | 1.91 | [8 empty] | 52.48 |  |  |  |  | 0.00
1989 |  |  |  | 4031.74 |  |  |  | 5364 |  |  |  |  | 848 | [10 empty] | 54.79 |  |  |  |  | 57.43 | [5 empty] | 54.27 |  |  | 61.23 |  |  |  |  | 31.42 |  | 26.31 | [8 empty] | 16.26 |  |  |  |  | 2.64
1990 |  |  |  | 5652.68 |  |  |  | 7472 |  |  |  |  | 848 | [10 empty] | 76.30 |  |  |  |  | 76.77 | [5 empty] | 76.09 |  |  | 85.30 |  |  |  |  | 23.03 |  | 22.97 | [8 empty] | 0.26 |  |  |  |  | 0.48
1991 |  |  |  | 6126.29 |  |  |  | 7950 |  |  |  |  | 848 | [10 empty] | 82.38 |  |  |  |  | 84.29 | [5 empty] | 82.47 |  |  | 90.75 |  |  |  |  | 15.71 |  | 15.71 | [8 empty] | 0.00 |  |  |  |  | 1.90
1992 |  |  |  | 5800.97 |  |  |  | 7438 |  |  |  |  | 848 | [10 empty] | 77.89 |  |  |  |  | 77.89 | [5 empty] | 77.88 |  |  | 84.68 |  |  |  |  | 18.25 |  | 17.39 | [8 empty] | 4.72 |  |  |  |  | 0.00
1993 |  |  |  | 3158.23 |  |  |  | 6557 |  |  |  |  | 848 | [10 empty] | 42.99 |  |  |  |  | 42.99 | [5 empty] | 42.52 |  |  | 74.85 |  |  |  |  | 54.42 |  | 51.32 | [8 empty] | 5.69 |  |  |  |  | 0.00
1994 |  |  |  | 2737.62 |  |  |  | 5006 |  |  |  |  | 848 | [10 empty] | 36.85 |  |  |  |  | 36.85 | [5 empty] | 36.85 |  |  | 57.15 |  |  |  |  | 37.07 |  | 21.71 | [8 empty] | 41.44 |  |  |  |  | 0.00
1995 |  |  |  | 4225.82 |  |  |  | 7000 |  |  |  |  | 848 | [10 empty] | 56.89 |  |  |  |  | 56.89 | [5 empty] | 56.89 |  |  | 79.91 |  |  |  |  | 43.11 |  | 43.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 3321.48 |  |  |  | 5684 |  |  |  |  | 848 | [10 empty] | 44.59 |  |  |  |  | 44.59 | [5 empty] | 44.59 |  |  | 64.71 |  |  |  |  | 32.38 |  | 21.35 | [8 empty] | 34.06 |  |  |  |  | 0.00
1997 |  |  |  | 4214.82 |  |  |  | 6325 |  |  |  |  | 848 | [10 empty] | 56.76 |  |  |  |  | 56.76 | [5 empty] | 56.74 |  |  | 72.20 |  |  |  |  | 43.24 |  | 43.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 1642.52 |  |  |  | 2328 |  |  |  |  | 848 | [10 empty] | 81.45 |  |  |  |  | 81.45 | [5 empty] | 81.45 |  |  | 97.87 |  |  |  |  | 18.55 |  | 18.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | Data not available - Long-term shutdown
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | 4971.58 |  |  |  | 7154 |  |  |  |  | 750 | [10 empty] | 76.09 |  |  |  |  | 76.45 | [5 empty] | 75.30 |  |  | 81.44 |  |  |  |  | 22.51 |  | 22.21 | [8 empty] | 1.34 |  |  |  |  | 0.36
2005 |  |  |  | 4938.11 |  |  |  | 6782 |  |  |  |  | 750 | [10 empty] | 75.24 |  |  |  |  | 75.52 | [5 empty] | 75.16 |  |  | 77.42 |  |  |  |  | 8.92 |  | 7.40 | [8 empty] | 17.08 |  |  |  |  | 0.28
2006 |  |  |  | 5440.25 |  |  |  | 7435 |  |  |  |  | 750 | [10 empty] | 82.86 |  |  |  |  | 83.27 | [5 empty] | 82.80 |  |  | 84.87 |  |  |  |  | 8.75 |  | 8.05 | [8 empty] | 8.68 |  |  |  |  | 0.41
2007 |  |  |  | 4966.67 |  |  |  | 6911 |  |  |  |  | 750 | [10 empty] | 75.95 |  |  |  |  | 76.68 | [5 empty] | 75.60 |  |  | 78.89 |  |  |  |  | 3.18 |  | 3.34 | [8 empty] | 19.97 |  |  |  |  | 0.73
2008 |  |  |  | 5148.88 |  |  |  | 7125 |  |  |  |  | 734 | [10 empty] | 79.32 |  |  |  |  | 79.77 | [5 empty] | 79.86 |  |  | 81.11 |  |  |  |  | 3.51 |  | 2.90 | [8 empty] | 17.33 |  |  |  |  | 0.45
2009 |  |  |  | 5162.09 |  |  |  | 7148 |  |  |  |  | 730 | [10 empty] | 80.39 |  |  |  |  | 80.59 | [5 empty] | 80.72 |  |  | 81.60 |  |  |  |  | 2.07 |  | 10.14 | [8 empty] | 9.27 |  |  |  |  | 0.20
2010 |  |  |  | 4375.77 |  |  |  | 6198 |  |  |  |  | 730 | [10 empty] | 68.44 |  |  |  |  | 69.58 | [5 empty] | 68.43 |  |  | 70.75 |  |  |  |  | 16.32 |  | 13.57 | [8 empty] | 16.85 |  |  |  |  | 1.15
2011 |  |  |  | 5084.86 |  |  |  | 6959 |  |  |  |  | 730 | [10 empty] | 78.89 |  |  |  |  | 79.13 | [5 empty] | 79.52 |  |  | 79.44 |  |  |  |  | 4.24 |  | 3.50 | [8 empty] | 17.37 |  |  |  |  | 0.25
2012 |  |  |  | 3352.06 |  |  |  | 4617 |  |  |  |  | 730 | [10 empty] | 52.21 |  |  |  |  | 52.26 | [5 empty] | 52.28 |  |  | 52.56 |  |  |  |  | 5.80 |  | 9.96 | [8 empty] | 37.78 |  |  |  |  | 0.06
2013 |  |  |  | 5518.71 |  |  |  | 7914 |  |  |  |  | 730 | [10 empty] | 94.01 |  |  |  |  | 94.16 | [5 empty] | 86.30 |  |  | 90.34 |  |  |  |  | 4.71 |  | 4.66 | [8 empty] | 1.18 |  |  |  |  | 0.14
2014 |  |  |  | 4125.00 |  |  |  | 5718 |  |  |  |  | 730 | [10 empty] | 64.55 |  |  |  |  | 64.55 | [5 empty] | 64.51 |  |  | 65.27 |  |  |  |  | 3.30 |  | 2.20 | [8 empty] | 33.25 |  |  |  |  | 0.00
2015 |  |  |  | 5827.57 |  |  |  | 7831 |  |  |  |  | 750 | [10 empty] | 89.01 |  |  |  |  | 89.01 | [5 empty] | 88.90 |  |  | 89.39 |  |  |  |  | 10.00 |  | 9.89 | [8 empty] | 1.09 |  |  |  |  | 0.00
2016 |  |  |  | 4995.72 |  |  |  | 6579 |  |  |  |  | 750 | [10 empty] | 75.54 |  |  |  |  | 75.60 | [5 empty] | 75.83 |  |  | 74.90 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.40 |  |  |  |  | 0.06
2017 |  |  |  | 5502.68 |  |  |  | 7344 |  |  |  |  | 750 | [10 empty] | 83.22 |  |  |  |  | 83.22 | [5 empty] | 83.75 |  |  | 83.84 |  |  |  |  | 0.08 |  | 9.65 | [8 empty] | 7.13 |  |  |  |  | 0.00
2018 |  |  |  | 6268.88 |  |  |  | 8079 |  |  |  |  | 750 | [10 empty] | 92.18 |  |  |  |  | 92.21 | [5 empty] | 95.42 |  |  | 92.23 |  |  |  |  | 3.26 |  | 3.11 | [8 empty] | 4.68 |  |  |  |  | 0.03
2019 |  |  |  | 4213.89 |  |  |  | 5592 |  |  |  |  | 750 | [10 empty] | 62.40 |  |  |  |  | 62.40 | [5 empty] | 64.14 |  |  | 63.84 |  |  |  |  | 1.68 |  | 24.63 | [8 empty] | 12.98 |  |  |  |  | 0.00
2020 |  |  |  | 6776.48 |  |  |  | 8574 |  |  |  |  | 770 | [10 empty] | 97.08 |  |  |  |  | 97.12 | [5 empty] | 100.19 |  |  | 97.61 |  |  |  |  | 1.35 |  | 1.33 | [8 empty] | 1.54 |  |  |  |  | 0.04
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2020 | [16 empty] | 1978 to 2020
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [27 empty] | 25 | [15 empty] | 728
C. |  | Inspection, maintenance or repair combined with refuelling | [22 empty] | 123 | [16 empty] | 40 |  |  |  | 0
D. |  | Inspection, maintenance or repair without refuelling | [39 empty] | 825
E. |  | Testing of plant systems or components | [39 empty] | 14 |  |  |  | 1
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [39 empty] | 78
J. |  | Grid limitation, failure or grid unavailability | [55 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [55 empty] | 17
L. |  | Human factor related | [27 empty] | 59 | [15 empty] | 11
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [55 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [55 empty] | 13
Z. |  | Other | [43 empty] | 1
Subtotal | [24 empty] | 123 |  |  |  |  | 84 | [11 empty] | 957 |  |  |  | 741 | [11 empty] | 34
Total | [24 empty] | 207 | [16 empty] | 1732
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2020 | [16 empty] | 1978 to 2020
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [38 empty] | 131
12. |  |  | Reactor I&C Systems | [38 empty] | 45
13. |  |  | Reactor Auxiliary Systems | [38 empty] | 24
14. |  |  | Safety Systems | [38 empty] | 66
15. |  |  | Reactor Cooling Systems | [38 empty] | 87
16. |  |  | Steam generation systems | [38 empty] | 104
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [38 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [38 empty] | 31
31. |  |  | Turbine and auxiliaries | [21 empty] | 59 | [16 empty] | 96
32. |  |  | Feedwater and Main Steam System | [38 empty] | 35
33. |  |  | Circulating Water System | [38 empty] | 5
34. |  |  | Miscellaneous Systems | [38 empty] | 7
35. |  |  | All other I&C Systems | [38 empty] | 6
41. |  |  | Main Generator Systems | [38 empty] | 81
42. |  |  | Electrical Power Supply Systems | [21 empty] | 25 | [16 empty] | 19
Total | [24 empty] | 84 | [16 empty] | 740
RUP revision during the year (2020) due to power uprate
RUP at the end of previous year : 750 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
January | [5 empty] | 770 |  |  |  |  | Stretch power uprate (2-7%) | [14 empty] | Balance of plant | [13 empty] | Reference Unit Power revised to 770MWs. Increase from 750MW (2019) due to secondary side equipment upgrades including: seal oil, generator rewind, condenser cooling water pump replacement and installation of HX5A/5B bypass project. Change in RUP r

## BRUCE-4
2020 Operating Experience
CA-11 | [9 empty] | BRUCE-4 | [28 empty] | CANADA
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | BRUCEPOW (Bruce Power)
Owner | [8 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [8 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [8 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PHWR / CANDU 750A | [12 empty] | Construction Date | [16 empty] | : |  |  | 1972-09-01
Thermal power | [14 empty] | : |  |  | 2550 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 1978-12-21
Gross electrical power | [14 empty] | : |  |  | 830 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 1979-01-18
Reference unit power (net) | [14 empty] | : |  |  | 769 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Horizontal | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 300
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 8
| Refuelling type | [15 empty] | : |  |  | ON-line | [12 empty] | Containment type | [16 empty] | : |  |  | -
| Moderator material | [15 empty] | : |  |  | D2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | - | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | NA | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 1
| Part of the core refuelled [%] | [15 empty] | : |  |  | - | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | 8750 | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | -
| Active core diameter [m] | [15 empty] | : |  |  | 5.67 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 4.37
| Active core height/length [m] | [15 empty] | : |  |  | 5.94 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 6240 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 24.5 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | -
| Number of control rod assemblies | [15 empty] | : |  |  | 4 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | -
| Number of external reactor coolant loops | [15 empty] | : |  |  | - | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | -
| Coolant type | [15 empty] | : |  |  | D2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [20 empty] | : | 4506.1 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 2.84 %
Energy Availability Factor (EAF) | [20 empty] | : | 65.21 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 1.91 %
Unit Capability Factor (UCF) | [20 empty] | : | 65.35 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 32.74 %
Load Factor (LF) | [20 empty] | : | 66.71 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0.14 %
Operating Factor (OF) | [20 empty] | : | 65.74 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 3009 hours
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 588.08 |  | 263.91 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 271.31 | [6 empty] | 576.62 |  | 566.77 |  |  |  |  | 561.32 |  |  | 589.80 |  |  | 576.65 | [9 empty] | 511.64 |  |  | 4506.10
EAF [%] |  |  |  |  | 100.00 |  | 47.99 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 48.67 | [6 empty] | 99.77 |  | 98.71 |  |  |  |  | 99.83 |  |  | 100.00 |  |  | 99.95 | [9 empty] | 86.02 |  |  | 65.21
UCF [%] |  |  |  |  | 100.00 |  | 47.99 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 48.67 | [6 empty] | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.95 | [9 empty] | 86.02 |  |  | 65.35
LF [%] |  |  |  |  | 102.79 |  | 49.31 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 49.00 | [6 empty] | 100.78 |  | 99.06 |  |  |  |  | 101.38 |  |  | 103.09 |  |  | 104.15 | [9 empty] | 89.43 |  |  | 66.71
OF [%] |  |  |  |  | 100.00 |  | 47.99 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 51.39 | [6 empty] | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 88.04 |  |  | 65.74
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 15.43 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 13.93 |  |  | 2.84
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 8.88 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 13.92 |  |  | 1.91
PUF [%] |  |  |  |  | 0.00 |  | 52.01 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 42.44 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.05 | [9 empty] | 0.05 |  |  | 32.74
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.23 |  | 1.29 |  |  |  |  | 0.17 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.14
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 172606.41 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 14.81 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 73.93 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 14 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 74.6 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 11.41 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 73.61 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.67 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 78.92 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 4966.40 |  |  |  | 7084 |  |  |  |  | 740 | [10 empty] | 84.17 |  |  |  |  | 84.17 | [5 empty] | 79.65 |  |  | 84.18 |  |  |  |  | 15.83 |  | 15.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 4945.10 |  |  |  | 6962 |  |  |  |  | 740 | [10 empty] | 76.12 |  |  |  |  | 76.12 | [5 empty] | 76.08 |  |  | 79.26 |  |  |  |  | 14.06 |  | 12.46 | [8 empty] | 11.42 |  |  |  |  | 0.00
1981 |  |  |  | 5753.50 |  |  |  | 7874 |  |  |  |  | 740 | [10 empty] | 89.10 |  |  |  |  | 89.10 | [5 empty] | 88.76 |  |  | 89.89 |  |  |  |  | 10.90 |  | 10.90 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 6050.20 |  |  |  | 8150 |  |  |  |  | 740 | [10 empty] | 92.18 |  |  |  |  | 92.18 | [5 empty] | 93.33 |  |  | 93.04 |  |  |  |  | 2.13 |  | 2.01 | [8 empty] | 5.81 |  |  |  |  | 0.00
1983 |  |  |  | 6407.40 |  |  |  | 8345 |  |  |  |  | 740 | [10 empty] | 94.25 |  |  |  |  | 94.25 | [5 empty] | 98.84 |  |  | 95.26 |  |  |  |  | 5.68 |  | 5.67 | [8 empty] | 0.07 |  |  |  |  | 0.00
1984 |  |  |  | 6664.64 |  |  |  | 8625 |  |  |  |  | 740 | [10 empty] | 97.85 |  |  |  |  | 97.85 | [5 empty] | 102.53 |  |  | 98.19 |  |  |  |  | 2.08 |  | 2.07 | [8 empty] | 0.08 |  |  |  |  | 0.00
1985 |  |  |  | 4995.16 |  |  |  | 6518 |  |  |  |  | 788 | [10 empty] | 73.24 |  |  |  |  | 78.99 | [5 empty] | 72.29 |  |  | 74.41 |  |  |  |  | 7.88 |  | 6.76 | [8 empty] | 14.26 |  |  |  |  | 5.75
1986 |  |  |  | 6891.57 |  |  |  | 8644 |  |  |  |  | 848 | [10 empty] | 92.85 |  |  |  |  | 95.51 | [5 empty] | 92.77 |  |  | 98.68 |  |  |  |  | 4.49 |  | 4.49 | [8 empty] | 0.00 |  |  |  |  | 2.67
1987 |  |  |  | 5044.99 |  |  |  | 6366 |  |  |  |  | 848 | [10 empty] | 67.90 |  |  |  |  | 71.54 | [5 empty] | 67.91 |  |  | 72.67 |  |  |  |  | 5.78 |  | 4.39 | [8 empty] | 24.07 |  |  |  |  | 3.64
1988 |  |  |  | 4663.68 |  |  |  | 5997 |  |  |  |  | 848 | [10 empty] | 65.71 |  |  |  |  | 66.92 | [5 empty] | 62.61 |  |  | 68.27 |  |  |  |  | 18.05 |  | 14.74 | [8 empty] | 18.34 |  |  |  |  | 1.21
1989 |  |  |  | 5584.21 |  |  |  | 7290 |  |  |  |  | 848 | [10 empty] | 75.29 |  |  |  |  | 77.00 | [5 empty] | 75.17 |  |  | 83.22 |  |  |  |  | 17.87 |  | 16.75 | [8 empty] | 6.25 |  |  |  |  | 1.71
1990 |  |  |  | 3533.03 |  |  |  | 4611 |  |  |  |  | 848 | [10 empty] | 47.54 |  |  |  |  | 48.29 | [5 empty] | 47.56 |  |  | 52.64 |  |  |  |  | 51.71 |  | 51.71 | [8 empty] | 0.00 |  |  |  |  | 0.75
1991 |  |  |  | 5940.70 |  |  |  | 7955 |  |  |  |  | 848 | [10 empty] | 79.91 |  |  |  |  | 81.65 | [5 empty] | 79.97 |  |  | 90.81 |  |  |  |  | 17.92 |  | 17.83 | [8 empty] | 0.52 |  |  |  |  | 1.74
1992 |  |  |  | 5843.37 |  |  |  | 8070 |  |  |  |  | 848 | [10 empty] | 78.37 |  |  |  |  | 80.08 | [5 empty] | 78.45 |  |  | 91.87 |  |  |  |  | 19.92 |  | 19.92 | [8 empty] | 0.00 |  |  |  |  | 1.71
1993 |  |  |  | 350.09 |  |  |  | 527 |  |  |  |  | 848 | [10 empty] | 4.71 |  |  |  |  | 4.71 | [5 empty] | 4.71 |  |  | 6.02 |  |  |  |  | 79.26 |  | 18.01 | [8 empty] | 77.27 |  |  |  |  | 0.00
1994 |  |  |  | 3655.98 |  |  |  | 7206 |  |  |  |  | 848 | [10 empty] | 49.30 |  |  |  |  | 49.30 | [5 empty] | 49.22 |  |  | 82.26 |  |  |  |  | 50.38 |  | 50.06 | [8 empty] | 0.64 |  |  |  |  | 0.00
1995 |  |  |  | 3034.92 |  |  |  | 5024 |  |  |  |  | 848 | [10 empty] | 40.87 |  |  |  |  | 40.87 | [5 empty] | 40.86 |  |  | 57.35 |  |  |  |  | 42.28 |  | 29.94 | [8 empty] | 29.19 |  |  |  |  | 0.00
1996 |  |  |  | 5296.28 |  |  |  | 8686 |  |  |  |  | 848 | [10 empty] | 71.17 |  |  |  |  | 71.17 | [5 empty] | 71.10 |  |  | 98.88 |  |  |  |  | 28.83 |  | 28.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 2923.05 |  |  |  | 4968 |  |  |  |  | 848 | [10 empty] | 39.36 |  |  |  |  | 39.36 | [5 empty] | 39.35 |  |  | 56.71 |  |  |  |  | 60.64 |  | 60.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 12.34 |  |  |  | 45 |  |  |  |  | 848 | [10 empty] | 0.81 |  |  |  |  | 0.81 | [5 empty] | 0.81 |  |  | 2.50 |  |  |  |  | 99.19 |  | 99.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | Data not available - Long-term shutdown
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | 934.47 |  |  |  | 802 |  |  |  |  | 769 | [10 empty] | 100.00 |  |  |  |  | 100.00 | [5 empty] | 55.01 |  |  | 36.31 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 5418.78 |  |  |  | 7469 |  |  |  |  | 769 | [10 empty] | 83.42 |  |  |  |  | 83.42 | [5 empty] | 82.08 |  |  | 85.03 |  |  |  |  | 6.58 |  | 6.45 | [8 empty] | 10.13 |  |  |  |  | 0.00
2005 |  |  |  | 5499.12 |  |  |  | 7469 |  |  |  |  | 750 | [10 empty] | 83.67 |  |  |  |  | 84.10 | [5 empty] | 83.70 |  |  | 85.26 |  |  |  |  | 3.21 |  | 2.79 | [8 empty] | 13.11 |  |  |  |  | 0.43
2006 |  |  |  | 5308.22 |  |  |  | 7261 |  |  |  |  | 750 | [10 empty] | 80.78 |  |  |  |  | 81.59 | [5 empty] | 80.79 |  |  | 82.89 |  |  |  |  | 2.28 |  | 4.12 | [8 empty] | 14.29 |  |  |  |  | 0.81
2007 |  |  |  | 5250.98 |  |  |  | 7298 |  |  |  |  | 750 | [10 empty] | 80.15 |  |  |  |  | 80.78 | [5 empty] | 79.92 |  |  | 83.31 |  |  |  |  | 4.27 |  | 3.60 | [8 empty] | 15.62 |  |  |  |  | 0.63
2008 |  |  |  | 5504.43 |  |  |  | 7603 |  |  |  |  | 734 | [10 empty] | 84.92 |  |  |  |  | 85.62 | [5 empty] | 85.37 |  |  | 86.56 |  |  |  |  | 2.17 |  | 2.35 | [8 empty] | 12.03 |  |  |  |  | 0.70
2009 |  |  |  | 4907.55 |  |  |  | 7014 |  |  |  |  | 730 | [10 empty] | 76.92 |  |  |  |  | 77.37 | [5 empty] | 76.74 |  |  | 80.07 |  |  |  |  | 5.42 |  | 9.91 | [8 empty] | 12.72 |  |  |  |  | 0.44
2010 |  |  |  | 5976.18 |  |  |  | 8360 |  |  |  |  | 730 | [10 empty] | 94.11 |  |  |  |  | 94.49 | [5 empty] | 93.45 |  |  | 95.43 |  |  |  |  | 5.50 |  | 5.50 | [8 empty] | 0.02 |  |  |  |  | 0.37
2011 |  |  |  | 6259.24 |  |  |  | 8670 |  |  |  |  | 730 | [10 empty] | 98.71 |  |  |  |  | 98.97 | [5 empty] | 97.88 |  |  | 98.97 |  |  |  |  | 1.03 |  | 1.03 | [8 empty] | 0.00 |  |  |  |  | 0.26
2012 |  |  |  | 3700.41 |  |  |  | 5137 |  |  |  |  | 730 | [10 empty] | 58.31 |  |  |  |  | 58.46 | [5 empty] | 57.71 |  |  | 58.48 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 41.54 |  |  |  |  | 0.15
2013 |  |  |  | 4131.32 |  |  |  | 5778 |  |  |  |  | 730 | [10 empty] | 63.44 |  |  |  |  | 63.55 | [5 empty] | 64.60 |  |  | 65.96 |  |  |  |  | 10.79 |  | 31.78 | [8 empty] | 4.67 |  |  |  |  | 0.11
2014 |  |  |  | 6027.76 |  |  |  | 8243 |  |  |  |  | 730 | [10 empty] | 99.39 |  |  |  |  | 99.39 | [5 empty] | 94.26 |  |  | 94.10 |  |  |  |  | 0.61 |  | 0.61 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 4503.60 |  |  |  | 6069 |  |  |  |  | 750 | [10 empty] | 68.26 |  |  |  |  | 68.26 | [5 empty] | 68.55 |  |  | 69.28 |  |  |  |  | 0.00 |  | 2.74 | [8 empty] | 29.00 |  |  |  |  | 0.00
2016 |  |  |  | 5731.38 |  |  |  | 7511 |  |  |  |  | 750 | [10 empty] | 85.23 |  |  |  |  | 85.25 | [5 empty] | 87.00 |  |  | 85.51 |  |  |  |  | 6.54 |  | 5.96 | [8 empty] | 8.78 |  |  |  |  | 0.02
2017 |  |  |  | 6188.10 |  |  |  | 8262 |  |  |  |  | 750 | [10 empty] | 93.76 |  |  |  |  | 93.77 | [5 empty] | 94.19 |  |  | 94.32 |  |  |  |  | 4.65 |  | 4.58 | [8 empty] | 1.65 |  |  |  |  | 0.02
2018 |  |  |  | 4638.81 |  |  |  | 6146 |  |  |  |  | 750 | [10 empty] | 69.12 |  |  |  |  | 69.13 | [5 empty] | 70.61 |  |  | 70.16 |  |  |  |  | 4.78 |  | 7.58 | [8 empty] | 23.30 |  |  |  |  | 0.00
2019 |  |  |  | 6115.21 |  |  |  | 8168 |  |  |  |  | 750 | [10 empty] | 92.93 |  |  |  |  | 92.93 | [5 empty] | 93.08 |  |  | 93.24 |  |  |  |  | 3.71 |  | 3.58 | [8 empty] | 3.49 |  |  |  |  | 0.00
2020 |  |  |  | 4506.10 |  |  |  | 5775 |  |  |  |  | 769 | [10 empty] | 65.21 |  |  |  |  | 65.35 | [5 empty] | 66.71 |  |  | 65.74 |  |  |  |  | 2.84 |  | 1.91 | [8 empty] | 32.74 |  |  |  |  | 0.14
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2020 | [16 empty] | 1979 to 2020
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [27 empty] | 135 | [15 empty] | 782
C. |  | Inspection, maintenance or repair combined with refuelling | [39 empty] | 62
D. |  | Inspection, maintenance or repair without refuelling | [22 empty] | 2856 | [16 empty] | 865
E. |  | Testing of plant systems or components | [39 empty] | 42
H. |  | Nuclear regulatory requirements | [43 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [55 empty] | 16
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [55 empty] | 3
L. |  | Human factor related | [43 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [55 empty] | 2
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [55 empty] | 14
Z. |  | Other | [43 empty] | 12 | [11 empty] | 2
Subtotal | [24 empty] | 2856 |  |  |  |  | 135 | [11 empty] | 969 |  |  |  | 808 | [11 empty] | 37
Total | [24 empty] | 2991 | [16 empty] | 1814
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2020 | [16 empty] | 1979 to 2020
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [38 empty] | 106
12. |  |  | Reactor I&C Systems | [38 empty] | 43
14. |  |  | Safety Systems | [38 empty] | 45
15. |  |  | Reactor Cooling Systems | [38 empty] | 70
16. |  |  | Steam generation systems | [38 empty] | 172
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [38 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [38 empty] | 19
31. |  |  | Turbine and auxiliaries | [21 empty] | 57 | [16 empty] | 65
32. |  |  | Feedwater and Main Steam System | [38 empty] | 35
33. |  |  | Circulating Water System | [38 empty] | 7
34. |  |  | Miscellaneous Systems | [38 empty] | 33
35. |  |  | All other I&C Systems | [38 empty] | 95
41. |  |  | Main Generator Systems | [21 empty] | 78 | [16 empty] | 79
42. |  |  | Electrical Power Supply Systems | [38 empty] | 34
Total | [24 empty] | 135 | [16 empty] | 804
RUP revision during the year (2020) due to power uprate
RUP at the end of previous year : 750 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
January | [5 empty] | 769 |  |  |  |  | Stretch power uprate (2-7%) | [14 empty] | Balance of plant | [13 empty] | Reference Unit Power revised to 769MWs. Increase from 750MW (2019) due to HX5A/5B bypass project and engineering analysis performed on conducted on excitation limitations allowing increase to net average output. Change in RUP retroactive to 1 Jan 2

## BRUCE-5
2020 Operating Experience
CA-18 | [8 empty] | BRUCE-5 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-06-01
Thermal power | [12 empty] | : |  |  | 2832 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-12-02
Gross electrical power | [12 empty] | : |  |  | 872 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-03-01
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6227.87 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.08 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.06 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.07 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.37 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.56 %
Load Factor (LF) | [18 empty] | : | 86.78 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.31 %
Operating Factor (OF) | [18 empty] | : | 87.45 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1102 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 596.51 | 569.57 |  |  |  | 610.19 |  | 590.27 | [8 empty] | 152.70 |  |  | 141.88 | [6 empty] | 600.47 |  | 588.24 |  |  |  | 581.68 |  |  | 599.45 |  |  | 587.63 | [9 empty] | 609.27 |  |  | 6227.87
EAF [%] |  |  |  |  | 99.79 | 99.95 |  |  |  | 99.97 |  | 99.98 | [8 empty] | 25.30 |  |  | 24.11 | [6 empty] | 99.16 |  | 98.34 |  |  |  | 98.88 |  |  | 99.45 |  |  | 99.82 | [9 empty] | 99.99 |  |  | 87.06
UCF [%] |  |  |  |  | 99.79 | 99.95 |  |  |  | 99.97 |  | 99.98 | [8 empty] | 25.30 |  |  | 24.11 | [6 empty] | 99.97 |  | 99.85 |  |  |  | 99.87 |  |  | 99.76 |  |  | 99.88 | [9 empty] | 99.99 |  |  | 87.37
LF [%] |  |  |  |  | 98.13 | 100.17 |  |  |  | 100.39 |  | 100.35 | [8 empty] | 25.12 |  |  | 24.12 | [6 empty] | 98.79 |  | 96.77 |  |  |  | 98.88 |  |  | 98.62 |  |  | 99.90 | [9 empty] | 100.23 |  |  | 86.78
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 25.27 |  |  | 24.17 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.45
FLR [%] |  |  |  |  | 0.16 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.28 | [6 empty] | 0.01 |  | 0.15 |  |  |  | 0.13 |  |  | 0.18 |  |  | 0.12 | [9 empty] | 0.00 |  |  | 0.08
UCL [%] |  |  |  |  | 0.16 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.07 | [6 empty] | 0.01 |  | 0.15 |  |  |  | 0.13 |  |  | 0.18 |  |  | 0.12 | [9 empty] | 0.00 |  |  | 0.07
PUF [%] |  |  |  |  | 0.05 | 0.05 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 74.70 |  |  | 75.82 | [6 empty] | 0.02 |  | 0.01 |  |  |  | 0.01 |  |  | 0.06 |  |  | 0.01 | [9 empty] | 0.01 |  |  | 12.56
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.81 |  | 1.50 |  |  |  | 0.98 |  |  | 0.31 |  |  | 0.05 | [9 empty] | 0.00 |  |  | 0.31
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 218180.96 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.89 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.8 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.77 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.56 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.48 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.81 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 5464.16 |  |  | 7163 |  |  |  | 805 | [10 empty] | 85.86 |  |  |  | 91.57 | [5 empty] | 84.23 |  |  | 86.11 |  |  |  | 8.43 |  | 8.43 | [8 empty] | 0.00 |  |  |  |  | 5.71
1986 |  |  |  | 7078.03 |  |  | 8675 |  |  |  | 835 | [10 empty] | 96.67 |  |  |  | 98.43 | [5 empty] | 96.77 |  |  | 99.03 |  |  |  | 1.57 |  | 1.57 | [8 empty] | 0.00 |  |  |  |  | 1.76
1987 |  |  |  | 5730.15 |  |  | 7197 |  |  |  | 835 | [10 empty] | 78.18 |  |  |  | 80.17 | [5 empty] | 78.34 |  |  | 82.16 |  |  |  | 8.82 |  | 7.76 | [8 empty] | 12.08 |  |  |  |  | 1.99
1988 |  |  |  | 6673.56 |  |  | 7824 |  |  |  | 860 | [10 empty] | 88.49 |  |  |  | 88.52 | [5 empty] | 88.34 |  |  | 89.07 |  |  |  | 6.14 |  | 5.79 | [8 empty] | 5.69 |  |  |  |  | 0.02
1989 |  |  |  | 7130.76 |  |  | 8589 |  |  |  | 860 | [10 empty] | 94.14 |  |  |  | 97.10 | [5 empty] | 94.65 |  |  | 98.05 |  |  |  | 2.28 |  | 2.26 | [8 empty] | 0.64 |  |  |  |  | 2.96
1990 |  |  |  | 5534.66 |  |  | 6656 |  |  |  | 860 | [10 empty] | 73.53 |  |  |  | 74.60 | [5 empty] | 73.47 |  |  | 75.98 |  |  |  | 10.83 |  | 9.06 | [8 empty] | 16.34 |  |  |  |  | 1.06
1991 |  |  |  | 6769.63 |  |  | 8130 |  |  |  | 860 | [10 empty] | 90.30 |  |  |  | 90.74 | [5 empty] | 89.86 |  |  | 92.81 |  |  |  | 2.14 |  | 1.98 | [8 empty] | 7.27 |  |  |  |  | 0.44
1992 |  |  |  | 6452.05 |  |  | 7636 |  |  |  | 860 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 85.41 |  |  | 86.93 |  |  |  | 4.20 |  | 3.76 | [8 empty] | 10.45 |  |  |  |  | 0.00
1993 |  |  |  | 5118.34 |  |  | 7457 |  |  |  | 860 | [10 empty] | 68.08 |  |  |  | 68.08 | [5 empty] | 67.94 |  |  | 85.13 |  |  |  | 21.44 |  | 18.58 | [8 empty] | 13.34 |  |  |  |  | 0.00
1994 |  |  |  | 5629.34 |  |  | 7671 |  |  |  | 860 | [10 empty] | 75.02 |  |  |  | 75.02 | [5 empty] | 74.72 |  |  | 87.57 |  |  |  | 15.74 |  | 14.02 | [8 empty] | 10.97 |  |  |  |  | 0.00
1995 |  |  |  | 6125.27 |  |  | 7859 |  |  |  | 860 | [10 empty] | 81.41 |  |  |  | 81.41 | [5 empty] | 81.31 |  |  | 89.71 |  |  |  | 18.59 |  | 18.59 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 5767.61 |  |  | 7153 |  |  |  | 860 | [10 empty] | 76.40 |  |  |  | 76.40 | [5 empty] | 76.35 |  |  | 81.43 |  |  |  | 8.58 |  | 7.17 | [8 empty] | 16.42 |  |  |  |  | 0.00
1997 |  |  |  | 6388.27 |  |  | 8148 |  |  |  | 860 | [10 empty] | 84.80 |  |  |  | 84.80 | [5 empty] | 84.80 |  |  | 93.01 |  |  |  | 13.20 |  | 12.89 | [8 empty] | 2.31 |  |  |  |  | 0.00
1998 |  |  |  | 5623.11 |  |  | 7305 |  |  |  | 785 | [10 empty] | 81.68 |  |  |  | 81.69 | [5 empty] | 81.77 |  |  | 83.39 |  |  |  | 10.74 |  | 9.83 | [8 empty] | 8.48 |  |  |  |  | 0.01
1999 |  |  |  | 5281.90 |  |  | 6719 |  |  |  | 785 | [10 empty] | 76.57 |  |  |  | 76.58 | [5 empty] | 76.81 |  |  | 76.70 |  |  |  | 4.27 |  | 3.42 | [8 empty] | 20.01 |  |  |  |  | 0.01
2000 |  |  |  | 6908.74 |  |  | 8719 |  |  |  | 785 | [10 empty] | 99.08 |  |  |  | 99.08 | [5 empty] | 100.19 |  |  | 99.26 |  |  |  | 0.92 |  | 0.92 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 4902.08 |  |  | 6220 |  |  |  | 790 | [10 empty] | 70.91 |  |  |  | 70.91 | [5 empty] | 70.84 |  |  | 71.00 |  |  |  | 2.07 |  | 1.50 | [8 empty] | 27.59 |  |  |  |  | 0.00
2002 |  |  |  | 5993.14 |  |  | 7630 |  |  |  | 790 | [10 empty] | 86.28 |  |  |  | 86.28 | [5 empty] | 86.60 |  |  | 87.10 |  |  |  | 3.85 |  | 3.86 | [8 empty] | 9.86 |  |  |  |  | 0.00
2003 |  |  |  | 5302.51 |  |  | 6783 |  |  |  | 790 | [10 empty] | 77.26 |  |  |  | 77.26 | [5 empty] | 76.62 |  |  | 77.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.74 |  |  |  |  | 0.00
2004 |  |  |  | 5889.11 |  |  | 7543 |  |  |  | 790 | [10 empty] | 85.13 |  |  |  | 85.13 | [5 empty] | 84.87 |  |  | 85.87 |  |  |  | 2.05 |  | 7.33 | [8 empty] | 7.54 |  |  |  |  | 0.00
2005 |  |  |  | 5109.63 |  |  | 6678 |  |  |  | 790 | [10 empty] | 74.14 |  |  |  | 74.64 | [5 empty] | 73.83 |  |  | 76.23 |  |  |  | 4.77 |  | 6.14 | [8 empty] | 19.22 |  |  |  |  | 0.50
2006 |  |  |  | 6723.49 |  |  | 8694 |  |  |  | 806 | [10 empty] | 96.79 |  |  |  | 97.18 | [5 empty] | 95.89 |  |  | 99.25 |  |  |  | 2.60 |  | 2.60 | [8 empty] | 0.22 |  |  |  |  | 0.38
2007 |  |  |  | 6710.89 |  |  | 8760 |  |  |  | 795 | [10 empty] | 97.23 |  |  |  | 97.69 | [5 empty] | 96.36 |  |  | 100.00 |  |  |  | 0.74 |  | 0.73 | [8 empty] | 1.58 |  |  |  |  | 0.46
2008 |  |  |  | 5596.97 |  |  | 6943 |  |  |  | 817 | [10 empty] | 78.05 |  |  |  | 78.30 | [5 empty] | 77.99 |  |  | 79.04 |  |  |  | 6.40 |  | 7.64 | [8 empty] | 14.05 |  |  |  |  | 0.25
2009 |  |  |  | 6826.70 |  |  | 8597 |  |  |  | 817 | [10 empty] | 97.91 |  |  |  | 98.00 | [5 empty] | 95.39 |  |  | 98.14 |  |  |  | 1.98 |  | 1.98 | [8 empty] | 0.01 |  |  |  |  | 0.10
2010 |  |  |  | 6699.69 |  |  | 8368 |  |  |  | 817 | [10 empty] | 93.97 |  |  |  | 94.15 | [5 empty] | 93.61 |  |  | 95.53 |  |  |  | 1.20 |  | 1.14 | [8 empty] | 4.71 |  |  |  |  | 0.18
2011 |  |  |  | 6149.76 |  |  | 7666 |  |  |  | 817 | [10 empty] | 86.78 |  |  |  | 86.86 | [5 empty] | 85.93 |  |  | 87.51 |  |  |  | 1.23 |  | 1.08 | [8 empty] | 12.06 |  |  |  |  | 0.08
2012 |  |  |  | 6927.64 |  |  | 8690 |  |  |  | 817 | [10 empty] | 98.24 |  |  |  | 98.38 | [5 empty] | 96.53 |  |  | 98.93 |  |  |  | 1.58 |  | 1.58 | [8 empty] | 0.03 |  |  |  |  | 0.14
2013 |  |  |  | 6421.79 |  |  | 8141 |  |  |  | 817 | [10 empty] | 92.04 |  |  |  | 92.11 | [5 empty] | 89.73 |  |  | 92.93 |  |  |  | 0.62 |  | 0.85 | [8 empty] | 7.04 |  |  |  |  | 0.07
2014 |  |  |  | 5859.11 |  |  | 7487 |  |  |  | 817 | [10 empty] | 84.64 |  |  |  | 84.76 | [5 empty] | 81.87 |  |  | 85.47 |  |  |  | 0.00 |  | 0.51 | [8 empty] | 14.73 |  |  |  |  | 0.11
2015 |  |  |  | 6180.84 |  |  | 7978 |  |  |  | 817 | [10 empty] | 90.60 |  |  |  | 90.70 | [5 empty] | 86.36 |  |  | 91.07 |  |  |  | 1.65 |  | 1.63 | [8 empty] | 7.66 |  |  |  |  | 0.10
2016 |  |  |  | 6742.40 |  |  | 8613 |  |  |  | 817 | [10 empty] | 97.45 |  |  |  | 97.86 | [5 empty] | 93.95 |  |  | 98.05 |  |  |  | 0.87 |  | 0.86 | [8 empty] | 1.28 |  |  |  |  | 0.41
2017 |  |  |  | 5034.08 |  |  | 6394 |  |  |  | 817 | [10 empty] | 72.35 |  |  |  | 72.75 | [5 empty] | 70.34 |  |  | 72.99 |  |  |  | 0.52 |  | 3.12 | [8 empty] | 24.13 |  |  |  |  | 0.40
2018 |  |  |  | 7076.65 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.38 |  |  |  | 99.64 | [5 empty] | 98.88 |  |  | 100.00 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.00 |  |  |  |  | 0.26
2019 |  |  |  | 4865.80 |  |  | 6173 |  |  |  | 817 | [10 empty] | 69.74 |  |  |  | 69.96 | [5 empty] | 67.99 |  |  | 70.47 |  |  |  | 2.10 |  | 1.50 | [8 empty] | 28.54 |  |  |  |  | 0.22
2020 |  |  |  | 6227.87 |  |  | 7682 |  |  |  | 817 | [10 empty] | 87.06 |  |  |  | 87.37 | [5 empty] | 86.78 |  |  | 87.45 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 12.56 |  |  |  |  | 0.31
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 226
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 18
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 1084 | [14 empty] | 783 |  |  |  | 7
E. |  | Testing of plant systems or components | [35 empty] | 6 |  |  |  | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 4
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 13
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 1084 | [14 empty] | 807 |  |  |  | 238 | [11 empty] | 17
Total | [22 empty] | 1084 | [14 empty] | 1062
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 25
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 76
16. |  |  | Steam generation systems | [34 empty] | 21
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 22
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 20
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 14
42. |  |  | Electrical Power Supply Systems | [34 empty] | 11
Total | [37 empty] | 238

## BRUCE-6
2020 Operating Experience
CA-19 | [8 empty] | BRUCE-6 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-01-01
Thermal power | [12 empty] | : |  |  | 2690 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-06-26
Gross electrical power | [12 empty] | : |  |  | 891 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-09-14
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 313.8 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.74 %
Energy Availability Factor (EAF) | [18 empty] | : | 4.74 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.04 %
Unit Capability Factor (UCF) | [18 empty] | : | 4.74 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 95.22 %
Load Factor (LF) | [18 empty] | : | 4.37 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 4.64 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8376 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 313.80 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 313.80
EAF [%] |  |  |  |  | 53.72 | 0.21 |  |  |  | 0.21 |  | 0.21 | [8 empty] | 0.21 |  |  | 0.21 | [6 empty] | 0.21 |  | 0.21 |  |  |  | 0.21 |  |  | 0.21 |  |  | 0.21 | [9 empty] | 0.21 |  |  | 4.74
UCF [%] |  |  |  |  | 53.72 | 0.21 |  |  |  | 0.21 |  | 0.21 | [8 empty] | 0.21 |  |  | 0.21 | [6 empty] | 0.21 |  | 0.21 |  |  |  | 0.21 |  |  | 0.21 |  |  | 0.21 | [9 empty] | 0.21 |  |  | 4.74
LF [%] |  |  |  |  | 51.63 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.37
OF [%] |  |  |  |  | 54.84 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.64
FLR [%] |  |  |  |  | 0.77 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.74
UCL [%] |  |  |  |  | 0.42 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.04
PUF [%] |  |  |  |  | 45.87 | 99.79 |  |  |  | 99.79 |  | 99.79 | [8 empty] | 99.79 |  |  | 99.79 | [6 empty] | 99.79 |  | 99.79 |  |  |  | 99.79 |  |  | 99.79 |  |  | 99.79 | [9 empty] | 99.79 |  |  | 95.22
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 204577.48 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.03 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.2 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.86 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.35 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.5 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.59 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.76 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 3068.32 |  |  | 4230 |  |  |  | 822 | [10 empty] | 98.80 |  |  |  | 99.38 | [5 empty] | 98.85 |  |  | 99.93 |  |  |  | 0.46 |  | 0.46 | [8 empty] | 0.17 |  |  |  |  | 0.58
1985 |  |  |  | 5900.13 |  |  | 7369 |  |  |  | 805 | [10 empty] | 84.04 |  |  |  | 88.69 | [5 empty] | 83.66 |  |  | 84.12 |  |  |  | 10.23 |  | 10.10 | [8 empty] | 1.20 |  |  |  |  | 4.65
1986 |  |  |  | 5716.03 |  |  | 7213 |  |  |  | 835 | [10 empty] | 77.78 |  |  |  | 81.71 | [5 empty] | 78.13 |  |  | 82.34 |  |  |  | 6.94 |  | 6.09 | [8 empty] | 12.20 |  |  |  |  | 3.93
1987 |  |  |  | 7017.10 |  |  | 8610 |  |  |  | 837 | [10 empty] | 95.33 |  |  |  | 97.85 | [5 empty] | 95.70 |  |  | 98.29 |  |  |  | 1.92 |  | 1.92 | [8 empty] | 0.23 |  |  |  |  | 2.52
1988 |  |  |  | 6139.49 |  |  | 7880 |  |  |  | 837 | [10 empty] | 89.10 |  |  |  | 89.22 | [5 empty] | 83.51 |  |  | 89.71 |  |  |  | 4.88 |  | 4.58 | [8 empty] | 6.20 |  |  |  |  | 0.12
1989 |  |  |  | 5386.17 |  |  | 7069 |  |  |  | 837 | [10 empty] | 73.43 |  |  |  | 78.94 | [5 empty] | 73.46 |  |  | 80.70 |  |  |  | 8.94 |  | 7.75 | [8 empty] | 13.32 |  |  |  |  | 5.50
1990 |  |  |  | 6213.64 |  |  | 7429 |  |  |  | 852 | [10 empty] | 82.31 |  |  |  | 83.85 | [5 empty] | 83.21 |  |  | 84.81 |  |  |  | 5.69 |  | 5.06 | [8 empty] | 11.09 |  |  |  |  | 1.54
1991 |  |  |  | 7013.36 |  |  | 8194 |  |  |  | 860 | [10 empty] | 93.03 |  |  |  | 93.31 | [5 empty] | 93.09 |  |  | 93.54 |  |  |  | 0.94 |  | 0.89 | [8 empty] | 5.81 |  |  |  |  | 0.27
1992 |  |  |  | 5328.20 |  |  | 6393 |  |  |  | 860 | [10 empty] | 70.51 |  |  |  | 70.55 | [5 empty] | 70.53 |  |  | 72.78 |  |  |  | 7.40 |  | 5.64 | [8 empty] | 23.82 |  |  |  |  | 0.04
1993 |  |  |  | 4351.00 |  |  | 6950 |  |  |  | 860 | [10 empty] | 58.03 |  |  |  | 58.03 | [5 empty] | 57.75 |  |  | 79.34 |  |  |  | 38.84 |  | 36.85 | [8 empty] | 5.12 |  |  |  |  | 0.00
1994 |  |  |  | 6451.71 |  |  | 8760 |  |  |  | 860 | [10 empty] | 85.75 |  |  |  | 85.75 | [5 empty] | 85.64 |  |  | 100.00 |  |  |  | 14.25 |  | 14.25 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 4671.57 |  |  | 6049 |  |  |  | 860 | [10 empty] | 62.10 |  |  |  | 62.10 | [5 empty] | 62.01 |  |  | 69.05 |  |  |  | 11.48 |  | 8.05 | [8 empty] | 29.85 |  |  |  |  | 0.00
1996 |  |  |  | 6822.75 |  |  | 8682 |  |  |  | 860 | [10 empty] | 90.38 |  |  |  | 90.39 | [5 empty] | 90.32 |  |  | 98.84 |  |  |  | 9.61 |  | 9.61 | [8 empty] | 0.00 |  |  |  |  | 0.01
1997 |  |  |  | 4796.41 |  |  | 6201 |  |  |  | 860 | [10 empty] | 63.70 |  |  |  | 63.70 | [5 empty] | 63.67 |  |  | 70.79 |  |  |  | 26.88 |  | 23.42 | [8 empty] | 12.88 |  |  |  |  | 0.00
1998 |  |  |  | 4678.62 |  |  | 6137 |  |  |  | 785 | [10 empty] | 68.04 |  |  |  | 68.11 | [5 empty] | 68.04 |  |  | 70.06 |  |  |  | 21.80 |  | 18.98 | [8 empty] | 12.91 |  |  |  |  | 0.07
1999 |  |  |  | 6860.15 |  |  | 8760 |  |  |  | 785 | [10 empty] | 99.32 |  |  |  | 99.44 | [5 empty] | 99.76 |  |  | 100.00 |  |  |  | 0.56 |  | 0.56 | [8 empty] | 0.00 |  |  |  |  | 0.12
2000 |  |  |  | 4668.21 |  |  | 5912 |  |  |  | 785 | [10 empty] | 66.81 |  |  |  | 66.81 | [5 empty] | 67.70 |  |  | 67.30 |  |  |  | 11.72 |  | 8.87 | [8 empty] | 24.32 |  |  |  |  | 0.00
2001 |  |  |  | 6840.06 |  |  | 8624 |  |  |  | 790 | [10 empty] | 98.32 |  |  |  | 98.32 | [5 empty] | 98.84 |  |  | 98.45 |  |  |  | 1.68 |  | 1.68 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 3522.45 |  |  | 4539 |  |  |  | 790 | [10 empty] | 50.64 |  |  |  | 50.64 | [5 empty] | 50.90 |  |  | 51.82 |  |  |  | 0.42 |  | 14.91 | [8 empty] | 34.45 |  |  |  |  | 0.00
2003 |  |  |  | 6750.85 |  |  | 8559 |  |  |  | 790 | [10 empty] | 98.18 |  |  |  | 98.18 | [5 empty] | 97.55 |  |  | 97.71 |  |  |  | 1.81 |  | 1.81 | [8 empty] | 0.01 |  |  |  |  | 0.00
2004 |  |  |  | 5379.09 |  |  | 6698 |  |  |  | 790 | [10 empty] | 76.65 |  |  |  | 76.65 | [5 empty] | 75.43 |  |  | 76.25 |  |  |  | 1.06 |  | 0.98 | [8 empty] | 22.37 |  |  |  |  | 0.00
2005 |  |  |  | 5721.10 |  |  | 7151 |  |  |  | 841 | [10 empty] | 79.56 |  |  |  | 79.56 | [5 empty] | 78.90 |  |  | 81.63 |  |  |  | 20.44 |  | 20.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 7104.45 |  |  | 8760 |  |  |  | 822 | [10 empty] | 99.32 |  |  |  | 99.45 | [5 empty] | 98.66 |  |  | 100.00 |  |  |  | 0.50 |  | 0.50 | [8 empty] | 0.06 |  |  |  |  | 0.12
2007 |  |  |  | 5145.02 |  |  | 6363 |  |  |  | 822 | [10 empty] | 71.77 |  |  |  | 71.77 | [5 empty] | 71.45 |  |  | 72.64 |  |  |  | 7.49 |  | 5.81 | [8 empty] | 22.42 |  |  |  |  | 0.00
2008 |  |  |  | 6857.25 |  |  | 8452 |  |  |  | 817 | [10 empty] | 95.35 |  |  |  | 95.52 | [5 empty] | 95.55 |  |  | 96.22 |  |  |  | 2.77 |  | 2.72 | [8 empty] | 1.77 |  |  |  |  | 0.17
2009 |  |  |  | 6063.07 |  |  | 7732 |  |  |  | 817 | [10 empty] | 91.32 |  |  |  | 91.36 | [5 empty] | 84.72 |  |  | 88.26 |  |  |  | 8.43 |  | 8.41 | [8 empty] | 0.23 |  |  |  |  | 0.04
2010 |  |  |  | 5471.91 |  |  | 6815 |  |  |  | 817 | [10 empty] | 76.54 |  |  |  | 76.67 | [5 empty] | 76.46 |  |  | 77.80 |  |  |  | 4.31 |  | 8.21 | [8 empty] | 15.12 |  |  |  |  | 0.13
2011 |  |  |  | 6552.52 |  |  | 8277 |  |  |  | 817 | [10 empty] | 94.00 |  |  |  | 94.07 | [5 empty] | 91.55 |  |  | 94.49 |  |  |  | 0.84 |  | 0.80 | [8 empty] | 5.13 |  |  |  |  | 0.07
2012 |  |  |  | 7125.32 |  |  | 8784 |  |  |  | 817 | [10 empty] | 99.58 |  |  |  | 99.72 | [5 empty] | 99.29 |  |  | 100.00 |  |  |  | 0.28 |  | 0.28 | [8 empty] | 0.00 |  |  |  |  | 0.14
2013 |  |  |  | 5684.00 |  |  | 7174 |  |  |  | 817 | [10 empty] | 81.00 |  |  |  | 81.07 | [5 empty] | 79.42 |  |  | 81.89 |  |  |  | 0.67 |  | 3.27 | [8 empty] | 15.66 |  |  |  |  | 0.07
2014 |  |  |  | 6768.62 |  |  | 8488 |  |  |  | 817 | [10 empty] | 97.74 |  |  |  | 97.85 | [5 empty] | 94.57 |  |  | 96.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.15 |  |  |  |  | 0.11
2015 |  |  |  | 5344.31 |  |  | 6694 |  |  |  | 817 | [10 empty] | 76.15 |  |  |  | 76.15 | [5 empty] | 74.67 |  |  | 76.42 |  |  |  | 0.74 |  | 0.57 | [8 empty] | 23.28 |  |  |  |  | 0.00
2016 |  |  |  | 6875.21 |  |  | 8613 |  |  |  | 817 | [10 empty] | 97.09 |  |  |  | 97.61 | [5 empty] | 95.80 |  |  | 98.05 |  |  |  | 2.39 |  | 2.39 | [8 empty] | 0.00 |  |  |  |  | 0.52
2017 |  |  |  | 5741.56 |  |  | 7164 |  |  |  | 817 | [10 empty] | 80.96 |  |  |  | 81.10 | [5 empty] | 80.22 |  |  | 81.78 |  |  |  | 0.19 |  | 2.89 | [8 empty] | 16.01 |  |  |  |  | 0.14
2018 |  |  |  | 7059.65 |  |  | 8718 |  |  |  | 817 | [10 empty] | 99.03 |  |  |  | 99.18 | [5 empty] | 98.64 |  |  | 99.52 |  |  |  | 0.80 |  | 0.80 | [8 empty] | 0.02 |  |  |  |  | 0.15
2019 |  |  |  | 6498.25 |  |  | 8224 |  |  |  | 817 | [10 empty] | 91.71 |  |  |  | 92.35 | [5 empty] | 90.80 |  |  | 93.88 |  |  |  | 7.63 |  | 7.63 | [8 empty] | 0.02 |  |  |  |  | 0.64
2020 |  |  |  | 313.80 |  |  | 408 |  |  |  | 817 | [10 empty] | 4.74 |  |  |  | 4.74 | [5 empty] | 4.37 |  |  | 4.64 |  |  |  | 0.74 |  | 0.04 | [8 empty] | 95.22 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 355
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 8040 | [14 empty] | 313
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 660 |  |  |  | 4
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 17
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [20 empty] | 342 | [14 empty] | 9
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 15
L. |  | Human factor related | [39 empty] | 17
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 12
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 11
Z. |  | Other | [39 empty] | 13
Subtotal | [22 empty] | 8382 | [14 empty] | 982 |  |  |  | 417 | [11 empty] | 30
Total | [22 empty] | 8382 | [14 empty] | 1429
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 87
12. |  |  | Reactor I&C Systems | [34 empty] | 55
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 24
15. |  |  | Reactor Cooling Systems | [34 empty] | 98
16. |  |  | Steam generation systems | [34 empty] | 55
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 13
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
33. |  |  | Circulating Water System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [37 empty] | 398
Highlights (2020)
Major component replacement outage start Jan 2020 (pressure tubes, steam generators, feeder piping, calendria tubes)

## BRUCE-7
2020 Operating Experience
CA-20 | [8 empty] | BRUCE-7 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-05-01
Thermal power | [12 empty] | : |  |  | 2832 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-02-22
Gross electrical power | [12 empty] | : |  |  | 872 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-04-10
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7036.81 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.71 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.96 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.71 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.04 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.25 %
Load Factor (LF) | [18 empty] | : | 98.05 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.08 %
Operating Factor (OF) | [18 empty] | : | 98.63 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 120 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 583.59 | 570.29 |  |  |  | 611.40 |  | 591.46 | [8 empty] | 609.95 |  |  | 586.33 | [6 empty] | 595.57 |  | 496.24 |  |  |  | 585.58 |  |  | 603.42 |  |  | 591.60 | [9 empty] | 611.39 |  |  | 7036.81
EAF [%] |  |  |  |  | 97.40 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.97 | [6 empty] | 98.04 |  | 81.46 |  |  |  | 99.43 |  |  | 99.58 |  |  | 99.98 | [9 empty] | 100.00 |  |  | 97.96
UCF [%] |  |  |  |  | 97.40 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.97 | [6 empty] | 98.62 |  | 81.70 |  |  |  | 99.57 |  |  | 99.59 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 98.04
LF [%] |  |  |  |  | 96.01 | 100.29 |  |  |  | 100.58 |  | 100.55 | [8 empty] | 100.35 |  |  | 99.68 | [6 empty] | 97.98 |  | 81.64 |  |  |  | 99.55 |  |  | 99.27 |  |  | 100.57 | [9 empty] | 100.58 |  |  | 98.05
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 83.87 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.63
FLR [%] |  |  |  |  | 0.08 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.38 |  | 18.29 |  |  |  | 0.29 |  |  | 0.13 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.71
UCL [%] |  |  |  |  | 0.08 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.38 |  | 18.29 |  |  |  | 0.28 |  |  | 0.13 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.71
PUF [%] |  |  |  |  | 2.52 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.03 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.15 |  |  | 0.28 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 0.25
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.58 |  | 0.24 |  |  |  | 0.14 |  |  | 0.01 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 0.08
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 212422.84 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.16 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.8 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.42 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.49 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.09 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.83 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.69 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 5256.62 |  |  | 6957 |  |  |  | 838 | [10 empty] | 89.83 |  |  |  | 96.68 | [5 empty] | 89.66 |  |  | 97.55 |  |  |  | 3.31 |  | 3.30 | [8 empty] | 0.02 |  |  |  |  | 6.85
1987 |  |  |  | 6288.05 |  |  | 8489 |  |  |  | 837 | [10 empty] | 85.91 |  |  |  | 96.87 | [5 empty] | 85.76 |  |  | 96.91 |  |  |  | 2.80 |  | 2.79 | [8 empty] | 0.34 |  |  |  |  | 10.96
1988 |  |  |  | 4866.19 |  |  | 6636 |  |  |  | 846 | [10 empty] | 74.75 |  |  |  | 74.75 | [5 empty] | 65.44 |  |  | 75.55 |  |  |  | 9.46 |  | 7.81 | [8 empty] | 17.44 |  |  |  |  | 0.00
1989 |  |  |  | 7280.79 |  |  | 8632 |  |  |  | 860 | [10 empty] | 96.44 |  |  |  | 97.83 | [5 empty] | 96.64 |  |  | 98.54 |  |  |  | 1.83 |  | 1.82 | [8 empty] | 0.35 |  |  |  |  | 1.39
1990 |  |  |  | 6659.40 |  |  | 8065 |  |  |  | 860 | [10 empty] | 88.53 |  |  |  | 90.69 | [5 empty] | 88.40 |  |  | 92.07 |  |  |  | 4.64 |  | 4.41 | [8 empty] | 4.89 |  |  |  |  | 2.17
1991 |  |  |  | 5733.63 |  |  | 6835 |  |  |  | 860 | [10 empty] | 76.27 |  |  |  | 76.39 | [5 empty] | 76.11 |  |  | 78.03 |  |  |  | 8.22 |  | 6.84 | [8 empty] | 16.77 |  |  |  |  | 0.12
1992 |  |  |  | 6413.41 |  |  | 7589 |  |  |  | 860 | [10 empty] | 85.11 |  |  |  | 85.16 | [5 empty] | 84.90 |  |  | 86.40 |  |  |  | 1.64 |  | 1.42 | [8 empty] | 13.42 |  |  |  |  | 0.05
1993 |  |  |  | 5802.33 |  |  | 8760 |  |  |  | 860 | [10 empty] | 78.12 |  |  |  | 78.12 | [5 empty] | 77.02 |  |  | 100.00 |  |  |  | 21.87 |  | 21.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 5496.71 |  |  | 7577 |  |  |  | 860 | [10 empty] | 73.20 |  |  |  | 73.20 | [5 empty] | 72.96 |  |  | 86.50 |  |  |  | 17.13 |  | 15.13 | [8 empty] | 11.67 |  |  |  |  | 0.00
1995 |  |  |  | 6285.10 |  |  | 8092 |  |  |  | 860 | [10 empty] | 83.47 |  |  |  | 83.47 | [5 empty] | 83.43 |  |  | 92.37 |  |  |  | 16.53 |  | 16.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 5475.68 |  |  | 7000 |  |  |  | 860 | [10 empty] | 72.55 |  |  |  | 72.58 | [5 empty] | 72.48 |  |  | 79.69 |  |  |  | 16.16 |  | 13.98 | [8 empty] | 13.44 |  |  |  |  | 0.03
1997 |  |  |  | 6154.48 |  |  | 7874 |  |  |  | 860 | [10 empty] | 81.69 |  |  |  | 81.69 | [5 empty] | 81.69 |  |  | 89.89 |  |  |  | 18.31 |  | 18.31 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 4990.76 |  |  | 6474 |  |  |  | 785 | [10 empty] | 72.42 |  |  |  | 72.42 | [5 empty] | 72.58 |  |  | 73.90 |  |  |  | 6.83 |  | 5.31 | [8 empty] | 22.27 |  |  |  |  | 0.00
1999 |  |  |  | 6315.74 |  |  | 8208 |  |  |  | 785 | [10 empty] | 91.84 |  |  |  | 92.29 | [5 empty] | 91.84 |  |  | 93.70 |  |  |  | 7.71 |  | 7.71 | [8 empty] | 0.00 |  |  |  |  | 0.44
2000 |  |  |  | 5322.68 |  |  | 6790 |  |  |  | 785 | [10 empty] | 76.91 |  |  |  | 78.20 | [5 empty] | 77.19 |  |  | 77.30 |  |  |  | 1.57 |  | 1.25 | [8 empty] | 20.55 |  |  |  |  | 1.29
2001 |  |  |  | 7026.30 |  |  | 8760 |  |  |  | 790 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.53 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 4819.35 |  |  | 6121 |  |  |  | 790 | [10 empty] | 69.49 |  |  |  | 69.49 | [5 empty] | 69.64 |  |  | 69.87 |  |  |  | 1.46 |  | 3.67 | [8 empty] | 26.84 |  |  |  |  | 0.00
2003 |  |  |  | 6730.24 |  |  | 8592 |  |  |  | 790 | [10 empty] | 97.66 |  |  |  | 97.66 | [5 empty] | 97.25 |  |  | 98.08 |  |  |  | 2.20 |  | 2.20 | [8 empty] | 0.14 |  |  |  |  | 0.00
2004 |  |  |  | 6428.77 |  |  | 8188 |  |  |  | 790 | [10 empty] | 92.77 |  |  |  | 92.77 | [5 empty] | 92.64 |  |  | 93.21 |  |  |  | 0.00 |  | 0.03 | [8 empty] | 7.20 |  |  |  |  | 0.00
2005 |  |  |  | 4890.45 |  |  | 6310 |  |  |  | 790 | [10 empty] | 70.21 |  |  |  | 70.23 | [5 empty] | 70.07 |  |  | 72.03 |  |  |  | 3.28 |  | 5.70 | [8 empty] | 24.07 |  |  |  |  | 0.02
2006 |  |  |  | 6740.47 |  |  | 8486 |  |  |  | 806 | [10 empty] | 94.79 |  |  |  | 95.06 | [5 empty] | 94.37 |  |  | 96.87 |  |  |  | 4.30 |  | 4.27 | [8 empty] | 0.67 |  |  |  |  | 0.28
2007 |  |  |  | 6969.91 |  |  | 8570 |  |  |  | 822 | [10 empty] | 97.07 |  |  |  | 97.33 | [5 empty] | 96.79 |  |  | 97.83 |  |  |  | 2.49 |  | 2.48 | [8 empty] | 0.18 |  |  |  |  | 0.26
2008 |  |  |  | 5763.74 |  |  | 7101 |  |  |  | 817 | [10 empty] | 79.92 |  |  |  | 80.08 | [5 empty] | 80.31 |  |  | 80.84 |  |  |  | 3.49 |  | 5.99 | [8 empty] | 13.93 |  |  |  |  | 0.16
2009 |  |  |  | 6475.33 |  |  | 8144 |  |  |  | 817 | [10 empty] | 97.93 |  |  |  | 97.93 | [5 empty] | 90.48 |  |  | 92.97 |  |  |  | 1.99 |  | 1.98 | [8 empty] | 0.08 |  |  |  |  | 0.01
2010 |  |  |  | 6726.64 |  |  | 8610 |  |  |  | 817 | [10 empty] | 93.68 |  |  |  | 93.84 | [5 empty] | 93.99 |  |  | 98.29 |  |  |  | 5.98 |  | 5.97 | [8 empty] | 0.19 |  |  |  |  | 0.16
2011 |  |  |  | 5761.53 |  |  | 7137 |  |  |  | 817 | [10 empty] | 80.73 |  |  |  | 80.82 | [5 empty] | 80.50 |  |  | 81.47 |  |  |  | 0.17 |  | 4.98 | [8 empty] | 14.20 |  |  |  |  | 0.09
2012 |  |  |  | 7055.97 |  |  | 8731 |  |  |  | 817 | [10 empty] | 99.55 |  |  |  | 99.68 | [5 empty] | 98.32 |  |  | 99.40 |  |  |  | 0.24 |  | 0.24 | [8 empty] | 0.08 |  |  |  |  | 0.14
2013 |  |  |  | 7003.57 |  |  | 8758 |  |  |  | 817 | [10 empty] | 99.42 |  |  |  | 99.49 | [5 empty] | 97.86 |  |  | 99.98 |  |  |  | 0.51 |  | 0.51 | [8 empty] | 0.00 |  |  |  |  | 0.07
2014 |  |  |  | 5479.21 |  |  | 7113 |  |  |  | 817 | [10 empty] | 80.72 |  |  |  | 80.72 | [5 empty] | 76.56 |  |  | 81.20 |  |  |  | 1.04 |  | 4.01 | [8 empty] | 15.27 |  |  |  |  | 0.00
2015 |  |  |  | 6324.10 |  |  | 8029 |  |  |  | 817 | [10 empty] | 91.46 |  |  |  | 91.46 | [5 empty] | 88.36 |  |  | 91.66 |  |  |  | 1.35 |  | 1.26 | [8 empty] | 7.29 |  |  |  |  | 0.00
2016 |  |  |  | 4983.38 |  |  | 6332 |  |  |  | 817 | [10 empty] | 71.92 |  |  |  | 72.20 | [5 empty] | 69.44 |  |  | 72.09 |  |  |  | 0.00 |  | 2.23 | [8 empty] | 25.57 |  |  |  |  | 0.27
2017 |  |  |  | 6643.16 |  |  | 8431 |  |  |  | 817 | [10 empty] | 96.33 |  |  |  | 96.53 | [5 empty] | 92.82 |  |  | 96.24 |  |  |  | 3.28 |  | 3.27 | [8 empty] | 0.20 |  |  |  |  | 0.20
2018 |  |  |  | 7116.79 |  |  | 8715 |  |  |  | 817 | [10 empty] | 99.01 |  |  |  | 99.07 | [5 empty] | 99.44 |  |  | 99.49 |  |  |  | 0.91 |  | 0.91 | [8 empty] | 0.02 |  |  |  |  | 0.06
2019 |  |  |  | 4849.09 |  |  | 6036 |  |  |  | 817 | [10 empty] | 68.32 |  |  |  | 68.46 | [5 empty] | 67.75 |  |  | 68.90 |  |  |  | 0.19 |  | 6.15 | [8 empty] | 25.39 |  |  |  |  | 0.14
2020 |  |  |  | 7036.81 |  |  | 8664 |  |  |  | 817 | [10 empty] | 97.96 |  |  |  | 98.04 | [5 empty] | 98.05 |  |  | 98.63 |  |  |  | 1.71 |  | 1.71 | [8 empty] | 0.25 |  |  |  |  | 0.08
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 117 | [14 empty] | 247
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 18
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 603 |  |  |  | 8
E. |  | Testing of plant systems or components | [35 empty] | 8
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 65
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 19
L. |  | Human factor related | [39 empty] | 4
Z. |  | Other | [39 empty] | 10 | [11 empty] | 3
Subtotal | [26 empty] | 117 | [10 empty] | 694 |  |  |  | 269 | [11 empty] | 22
Total | [22 empty] | 117 | [14 empty] | 985
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 32
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 40
16. |  |  | Steam generation systems | [34 empty] | 25
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 27
31. |  |  | Turbine and auxiliaries | [34 empty] | 31
32. |  |  | Feedwater and Main Steam System | [34 empty] | 30
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 30
41. |  |  | Main Generator Systems | [19 empty] | 117 | [14 empty] | 10
42. |  |  | Electrical Power Supply Systems | [34 empty] | 16
Total | [22 empty] | 117 | [14 empty] | 268

## BRUCE-8
2020 Operating Experience
CA-21 | [8 empty] | BRUCE-8 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-08-01
Thermal power | [12 empty] | : |  |  | 2690 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-03-09
Gross electrical power | [12 empty] | : |  |  | 872 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-05-22
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4936.59 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.4 %
Energy Availability Factor (EAF) | [18 empty] | : | 68.69 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.69 %
Unit Capability Factor (UCF) | [18 empty] | : | 68.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 29.49 %
Load Factor (LF) | [18 empty] | : | 68.79 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.13 %
Operating Factor (OF) | [18 empty] | : | 69.91 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2643 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 576.33 | 520.85 |  |  |  | 611.27 |  | 592.56 | [8 empty] | 612.57 |  |  | 582.66 | [6 empty] | 605.61 |  | 597.11 |  |  |  | 71.68 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 165.95 |  |  | 4936.59
EAF [%] |  |  |  |  | 95.08 | 91.05 |  |  |  | 99.96 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 99.48 |  | 98.69 |  |  |  | 12.19 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 27.30 |  |  | 68.69
UCF [%] |  |  |  |  | 95.08 | 91.05 |  |  |  | 99.96 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 99.94 |  | 99.59 |  |  |  | 12.35 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 27.30 |  |  | 68.82
LF [%] |  |  |  |  | 94.82 | 91.60 |  |  |  | 100.56 |  | 100.73 | [8 empty] | 100.78 |  |  | 99.05 | [6 empty] | 99.63 |  | 98.23 |  |  |  | 12.19 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 27.30 |  |  | 68.79
OF [%] |  |  |  |  | 95.83 | 99.57 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 12.92 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 30.38 |  |  | 69.91
FLR [%] |  |  |  |  | 4.61 | 8.85 |  |  |  | 0.04 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.05 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 20.40 |  |  | 2.40
UCL [%] |  |  |  |  | 4.60 | 8.84 |  |  |  | 0.04 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.05 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 6.99 |  |  | 1.69
PUF [%] |  |  |  |  | 0.32 | 0.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.41 |  |  |  | 87.65 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 65.70 |  |  | 29.49
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.46 |  | 0.90 |  |  |  | 0.17 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.13
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 199013.96 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.88 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.65 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.1 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.52 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.39 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.76 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.87 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.76 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 3673.23 |  |  | 5849 |  |  |  | 844 | [10 empty] | 76.58 |  |  |  | 99.06 | [5 empty] | 76.45 |  |  | 99.90 |  |  |  | 0.69 |  | 0.69 | [8 empty] | 0.25 |  |  |  |  | 22.48
1988 |  |  |  | 5958.52 |  |  | 7659 |  |  |  | 837 | [10 empty] | 86.53 |  |  |  | 86.85 | [5 empty] | 81.04 |  |  | 87.19 |  |  |  | 8.74 |  | 8.32 | [8 empty] | 4.83 |  |  |  |  | 0.32
1989 |  |  |  | 6523.47 |  |  | 8661 |  |  |  | 837 | [10 empty] | 89.21 |  |  |  | 98.45 | [5 empty] | 88.97 |  |  | 98.87 |  |  |  | 1.29 |  | 1.29 | [8 empty] | 0.26 |  |  |  |  | 9.24
1990 |  |  |  | 5758.67 |  |  | 7186 |  |  |  | 842 | [10 empty] | 78.09 |  |  |  | 80.67 | [5 empty] | 78.00 |  |  | 82.03 |  |  |  | 7.58 |  | 6.62 | [8 empty] | 12.71 |  |  |  |  | 2.58
1991 |  |  |  | 6932.70 |  |  | 8213 |  |  |  | 860 | [10 empty] | 92.47 |  |  |  | 92.96 | [5 empty] | 92.02 |  |  | 93.76 |  |  |  | 1.65 |  | 1.56 | [8 empty] | 5.48 |  |  |  |  | 0.48
1992 |  |  |  | 5451.09 |  |  | 6587 |  |  |  | 860 | [10 empty] | 72.41 |  |  |  | 72.43 | [5 empty] | 72.16 |  |  | 74.99 |  |  |  | 11.73 |  | 9.63 | [8 empty] | 17.94 |  |  |  |  | 0.02
1993 |  |  |  | 4675.90 |  |  | 7064 |  |  |  | 860 | [10 empty] | 62.27 |  |  |  | 62.27 | [5 empty] | 62.07 |  |  | 80.64 |  |  |  | 28.79 |  | 25.18 | [8 empty] | 12.55 |  |  |  |  | 0.00
1994 |  |  |  | 6443.16 |  |  | 8760 |  |  |  | 860 | [10 empty] | 86.00 |  |  |  | 86.00 | [5 empty] | 85.53 |  |  | 100.00 |  |  |  | 13.88 |  | 13.86 | [8 empty] | 0.15 |  |  |  |  | 0.00
1995 |  |  |  | 6113.35 |  |  | 7876 |  |  |  | 860 | [10 empty] | 81.34 |  |  |  | 81.34 | [5 empty] | 81.15 |  |  | 89.91 |  |  |  | 9.36 |  | 8.40 | [8 empty] | 10.26 |  |  |  |  | 0.00
1996 |  |  |  | 6957.82 |  |  | 8783 |  |  |  | 860 | [10 empty] | 92.14 |  |  |  | 92.14 | [5 empty] | 92.10 |  |  | 99.99 |  |  |  | 7.86 |  | 7.86 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 6346.54 |  |  | 8003 |  |  |  | 860 | [10 empty] | 84.24 |  |  |  | 84.24 | [5 empty] | 84.24 |  |  | 91.36 |  |  |  | 15.73 |  | 15.72 | [8 empty] | 0.03 |  |  |  |  | 0.00
1998 |  |  |  | 4122.43 |  |  | 5368 |  |  |  | 785 | [10 empty] | 59.76 |  |  |  | 59.86 | [5 empty] | 59.95 |  |  | 61.28 |  |  |  | 18.78 |  | 13.84 | [8 empty] | 26.30 |  |  |  |  | 0.10
1999 |  |  |  | 4114.43 |  |  | 5414 |  |  |  | 785 | [10 empty] | 59.77 |  |  |  | 59.98 | [5 empty] | 59.83 |  |  | 61.80 |  |  |  | 15.23 |  | 10.77 | [8 empty] | 29.25 |  |  |  |  | 0.21
2000 |  |  |  | 6530.94 |  |  | 8293 |  |  |  | 785 | [10 empty] | 93.67 |  |  |  | 93.67 | [5 empty] | 94.71 |  |  | 94.41 |  |  |  | 4.25 |  | 4.16 | [8 empty] | 2.17 |  |  |  |  | 0.00
2001 |  |  |  | 5424.77 |  |  | 6852 |  |  |  | 790 | [10 empty] | 78.03 |  |  |  | 78.03 | [5 empty] | 78.39 |  |  | 78.22 |  |  |  | 4.50 |  | 3.67 | [8 empty] | 18.30 |  |  |  |  | 0.00
2002 |  |  |  | 6685.96 |  |  | 8543 |  |  |  | 790 | [10 empty] | 97.01 |  |  |  | 97.01 | [5 empty] | 96.61 |  |  | 97.52 |  |  |  | 2.99 |  | 2.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 4959.99 |  |  | 6301 |  |  |  | 790 | [10 empty] | 71.89 |  |  |  | 71.89 | [5 empty] | 71.67 |  |  | 71.93 |  |  |  | 0.08 |  | 11.29 | [8 empty] | 16.81 |  |  |  |  | 0.00
2004 |  |  |  | 5695.77 |  |  | 7374 |  |  |  | 790 | [10 empty] | 82.80 |  |  |  | 83.01 | [5 empty] | 82.08 |  |  | 83.95 |  |  |  | 11.13 |  | 10.39 | [8 empty] | 6.60 |  |  |  |  | 0.21
2005 |  |  |  | 6889.22 |  |  | 8745 |  |  |  | 790 | [10 empty] | 99.44 |  |  |  | 99.65 | [5 empty] | 99.55 |  |  | 99.83 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.01 |  |  |  |  | 0.22
2006 |  |  |  | 5283.88 |  |  | 6791 |  |  |  | 790 | [10 empty] | 76.37 |  |  |  | 76.58 | [5 empty] | 76.31 |  |  | 77.52 |  |  |  | 4.47 |  | 5.14 | [8 empty] | 18.28 |  |  |  |  | 0.20
2007 |  |  |  | 6485.25 |  |  | 8341 |  |  |  | 795 | [10 empty] | 93.39 |  |  |  | 94.04 | [5 empty] | 93.12 |  |  | 95.22 |  |  |  | 2.41 |  | 2.32 | [8 empty] | 3.64 |  |  |  |  | 0.65
2008 |  |  |  | 6514.39 |  |  | 8699 |  |  |  | 782 | [10 empty] | 94.30 |  |  |  | 94.52 | [5 empty] | 94.84 |  |  | 99.03 |  |  |  | 5.43 |  | 5.42 | [8 empty] | 0.06 |  |  |  |  | 0.22
2009 |  |  |  | 5266.44 |  |  | 6906 |  |  |  | 782 | [10 empty] | 80.58 |  |  |  | 80.58 | [5 empty] | 76.88 |  |  | 78.84 |  |  |  | 1.79 |  | 4.43 | [8 empty] | 14.99 |  |  |  |  | 0.00
2010 |  |  |  | 6930.19 |  |  | 8760 |  |  |  | 817 | [10 empty] | 98.61 |  |  |  | 98.78 | [5 empty] | 98.93 |  |  | 100.00 |  |  |  | 0.75 |  | 0.74 | [8 empty] | 0.48 |  |  |  |  | 0.16
2011 |  |  |  | 6453.40 |  |  | 8015 |  |  |  | 817 | [10 empty] | 91.37 |  |  |  | 91.44 | [5 empty] | 90.17 |  |  | 91.50 |  |  |  | 1.81 |  | 2.81 | [8 empty] | 5.75 |  |  |  |  | 0.07
2012 |  |  |  | 5682.67 |  |  | 7161 |  |  |  | 817 | [10 empty] | 85.48 |  |  |  | 85.62 | [5 empty] | 79.18 |  |  | 81.52 |  |  |  | 1.87 |  | 3.88 | [8 empty] | 10.51 |  |  |  |  | 0.14
2013 |  |  |  | 5656.62 |  |  | 7141 |  |  |  | 817 | [10 empty] | 80.58 |  |  |  | 80.64 | [5 empty] | 79.04 |  |  | 81.52 |  |  |  | 7.01 |  | 6.08 | [8 empty] | 13.28 |  |  |  |  | 0.07
2014 |  |  |  | 6873.54 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.87 |  |  |  | 99.87 | [5 empty] | 96.04 |  |  | 100.00 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6288.54 |  |  | 8001 |  |  |  | 817 | [10 empty] | 90.66 |  |  |  | 90.66 | [5 empty] | 87.87 |  |  | 91.34 |  |  |  | 2.36 |  | 2.19 | [8 empty] | 7.15 |  |  |  |  | 0.00
2016 |  |  |  | 5038.39 |  |  | 6291 |  |  |  | 817 | [10 empty] | 71.41 |  |  |  | 71.41 | [5 empty] | 70.21 |  |  | 71.62 |  |  |  | 1.17 |  | 0.84 | [8 empty] | 27.74 |  |  |  |  | 0.00
2017 |  |  |  | 6992.50 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.70 |  |  |  | 99.98 | [5 empty] | 97.70 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.28
2018 |  |  |  | 4816.88 |  |  | 6123 |  |  |  | 817 | [10 empty] | 67.07 |  |  |  | 67.14 | [5 empty] | 67.30 |  |  | 69.90 |  |  |  | 2.68 |  | 10.62 | [8 empty] | 22.25 |  |  |  |  | 0.07
2019 |  |  |  | 7082.00 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.75 |  |  |  | 99.82 | [5 empty] | 98.95 |  |  | 100.00 |  |  |  | 0.18 |  | 0.18 | [8 empty] | 0.01 |  |  |  |  | 0.07
2020 |  |  |  | 4936.59 |  |  | 6141 |  |  |  | 817 | [10 empty] | 68.69 |  |  |  | 68.82 | [5 empty] | 68.79 |  |  | 69.91 |  |  |  | 2.40 |  | 1.69 | [8 empty] | 29.49 |  |  |  |  | 0.13
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 84 | [14 empty] | 296
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 112
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2568 | [14 empty] | 698 |  |  |  | 29
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 23
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 2568 |  |  |  | 84 | [10 empty] | 810 |  |  |  | 332 | [11 empty] | 23
Total | [22 empty] | 2652 | [14 empty] | 1165
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 33
12. |  |  | Reactor I&C Systems | [34 empty] | 9
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 18
15. |  |  | Reactor Cooling Systems | [34 empty] | 54
16. |  |  | Steam generation systems | [34 empty] | 141
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [19 empty] | 33 | [14 empty] | 17
32. |  |  | Feedwater and Main Steam System | [19 empty] | 51 | [14 empty] | 13
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 17
Total | [22 empty] | 84 | [14 empty] | 329

## DARLINGTON-1
2020 Operating Experience
CA-22 | [8 empty] | DARLINGTON-1 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-04-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-12-19
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1992-11-14
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7565.81 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.81 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.22 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.81 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.08 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.11 %
Load Factor (LF) | [18 empty] | : | 98.1 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.85 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 643.99 | 603.99 |  |  |  | 651.06 |  | 627.16 | [8 empty] | 649.54 |  |  | 603.53 | [6 empty] | 637.71 |  | 628.90 |  |  |  | 597.52 |  |  | 644.73 |  |  | 639.25 | [9 empty] | 638.42 |  |  | 7565.81
EAF [%] |  |  |  |  | 98.99 | 98.84 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.96 |  |  | 95.88 | [6 empty] | 97.76 |  | 96.27 |  |  |  | 94.57 |  |  | 98.67 |  |  | 100.00 | [9 empty] | 97.73 |  |  | 98.22
UCF [%] |  |  |  |  | 99.67 | 99.88 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.96 |  |  | 96.27 | [6 empty] | 99.74 |  | 98.62 |  |  |  | 97.32 |  |  | 99.23 |  |  | 100.00 | [9 empty] | 98.23 |  |  | 99.08
LF [%] |  |  |  |  | 98.59 | 98.84 |  |  |  | 99.67 |  | 99.21 | [8 empty] | 99.44 |  |  | 95.47 | [6 empty] | 97.62 |  | 96.27 |  |  |  | 94.52 |  |  | 98.70 |  |  | 101.12 | [9 empty] | 97.73 |  |  | 98.10
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.22 | 0.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  | 3.73 | [6 empty] | 0.26 |  | 1.38 |  |  |  | 2.68 |  |  | 0.77 |  |  | 0.00 | [9 empty] | 0.58 |  |  | 0.81
UCL [%] |  |  |  |  | 0.22 | 0.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  | 3.73 | [6 empty] | 0.26 |  | 1.38 |  |  |  | 2.68 |  |  | 0.77 |  |  | 0.00 | [9 empty] | 0.57 |  |  | 0.81
PUF [%] |  |  |  |  | 0.11 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 1.20 |  |  | 0.11
XUF [%] |  |  |  |  | 0.68 | 1.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.39 | [6 empty] | 1.98 |  | 2.35 |  |  |  | 2.75 |  |  | 0.56 |  |  | 0.00 | [9 empty] | 0.50 |  |  | 0.85
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 189501.45 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.56 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.54 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.16 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.51 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.33 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.12 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.97 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1992 |  |  |  | 973.98 |  |  | 1152 |  |  |  | 881 | [10 empty] | 96.83 |  |  |  | 96.83 | [5 empty] | 75.51 |  |  | 78.69 |  |  |  | 3.17 |  | 3.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 6016.23 |  |  | 7213 |  |  |  | 881 | [10 empty] | 78.72 |  |  |  | 79.18 | [5 empty] | 77.96 |  |  | 82.34 |  |  |  | 9.34 |  | 8.16 | [8 empty] | 12.66 |  |  |  |  | 0.45
1994 |  |  |  | 6326.65 |  |  | 7446 |  |  |  | 881 | [10 empty] | 83.13 |  |  |  | 83.46 | [5 empty] | 81.98 |  |  | 85.00 |  |  |  | 10.94 |  | 10.25 | [8 empty] | 6.29 |  |  |  |  | 0.33
1995 |  |  |  | 6853.27 |  |  | 8046 |  |  |  | 881 | [10 empty] | 89.72 |  |  |  | 90.65 | [5 empty] | 88.80 |  |  | 91.85 |  |  |  | 4.41 |  | 4.19 | [8 empty] | 5.16 |  |  |  |  | 0.94
1996 |  |  |  | 5745.25 |  |  | 6827 |  |  |  | 881 | [10 empty] | 75.03 |  |  |  | 75.68 | [5 empty] | 74.24 |  |  | 77.72 |  |  |  | 20.47 |  | 19.48 | [8 empty] | 4.84 |  |  |  |  | 0.65
1997 |  |  |  | 4765.08 |  |  | 7236 |  |  |  | 881 | [10 empty] | 62.33 |  |  |  | 63.04 | [5 empty] | 61.74 |  |  | 82.60 |  |  |  | 31.33 |  | 28.76 | [8 empty] | 8.20 |  |  |  |  | 0.71
1998 |  |  |  | 6427.46 |  |  | 7717 |  |  |  | 881 | [10 empty] | 83.28 |  |  |  | 84.27 | [5 empty] | 83.28 |  |  | 88.09 |  |  |  | 6.58 |  | 5.94 | [8 empty] | 9.79 |  |  |  |  | 0.99
1999 |  |  |  | 7175.13 |  |  | 8705 |  |  |  | 881 | [10 empty] | 92.97 |  |  |  | 94.35 | [5 empty] | 92.97 |  |  | 99.37 |  |  |  | 5.65 |  | 5.65 | [8 empty] | 0.00 |  |  |  |  | 1.38
2000 |  |  |  | 6280.57 |  |  | 7615 |  |  |  | 881 | [10 empty] | 81.18 |  |  |  | 81.97 | [5 empty] | 81.16 |  |  | 86.69 |  |  |  | 5.20 |  | 4.49 | [8 empty] | 13.54 |  |  |  |  | 0.79
2001 |  |  |  | 6980.80 |  |  | 8502 |  |  |  | 881 | [10 empty] | 90.45 |  |  |  | 91.17 | [5 empty] | 90.45 |  |  | 97.05 |  |  |  | 5.81 |  | 5.62 | [8 empty] | 3.21 |  |  |  |  | 0.71
2002 |  |  |  | 6532.91 |  |  | 7887 |  |  |  | 881 | [10 empty] | 84.65 |  |  |  | 85.51 | [5 empty] | 84.65 |  |  | 90.03 |  |  |  | 7.89 |  | 7.32 | [8 empty] | 7.16 |  |  |  |  | 0.86
2003 |  |  |  | 6562.38 |  |  | 7846 |  |  |  | 881 | [10 empty] | 85.10 |  |  |  | 87.47 | [5 empty] | 85.03 |  |  | 89.57 |  |  |  | 5.14 |  | 4.74 | [8 empty] | 7.79 |  |  |  |  | 2.38
2004 |  |  |  | 5612.12 |  |  | 6540 |  |  |  | 881 | [10 empty] | 72.82 |  |  |  | 73.58 | [5 empty] | 72.52 |  |  | 74.45 |  |  |  | 9.72 |  | 7.92 | [8 empty] | 18.50 |  |  |  |  | 0.76
2005 |  |  |  | 7366.26 |  |  | 8553 |  |  |  | 881 | [10 empty] | 96.20 |  |  |  | 97.04 | [5 empty] | 95.69 |  |  | 97.64 |  |  |  | 2.96 |  | 2.96 | [8 empty] | 0.00 |  |  |  |  | 0.84
2006 |  |  |  | 6388.89 |  |  | 7520 |  |  |  | 878 | [10 empty] | 83.43 |  |  |  | 85.16 | [5 empty] | 83.07 |  |  | 85.84 |  |  |  | 1.85 |  | 2.36 | [8 empty] | 12.47 |  |  |  |  | 1.73
2007 |  |  |  | 7412.62 |  |  | 8647 |  |  |  | 878 | [10 empty] | 96.81 |  |  |  | 98.15 | [5 empty] | 96.38 |  |  | 98.71 |  |  |  | 1.74 |  | 1.74 | [8 empty] | 0.11 |  |  |  |  | 1.35
2008 |  |  |  | 6125.27 |  |  | 7125 |  |  |  | 878 | [10 empty] | 79.73 |  |  |  | 80.79 | [5 empty] | 79.42 |  |  | 81.11 |  |  |  | 0.08 |  | 0.06 | [8 empty] | 19.15 |  |  |  |  | 1.06
2009 |  |  |  | 6870.24 |  |  | 8038 |  |  |  | 878 | [10 empty] | 89.79 |  |  |  | 90.98 | [5 empty] | 89.33 |  |  | 91.76 |  |  |  | 0.66 |  | 0.60 | [8 empty] | 8.42 |  |  |  |  | 1.19
2010 |  |  |  | 7244.93 |  |  | 8660 |  |  |  | 878 | [10 empty] | 94.48 |  |  |  | 95.47 | [5 empty] | 94.20 |  |  | 98.86 |  |  |  | 4.48 |  | 4.48 | [8 empty] | 0.04 |  |  |  |  | 1.00
2011 |  |  |  | 6256.80 |  |  | 7313 |  |  |  | 878 | [10 empty] | 81.55 |  |  |  | 82.66 | [5 empty] | 81.35 |  |  | 83.48 |  |  |  | 0.44 |  | 0.36 | [8 empty] | 16.98 |  |  |  |  | 1.11
2012 |  |  |  | 7256.40 |  |  | 8468 |  |  |  | 878 | [10 empty] | 94.31 |  |  |  | 95.50 | [5 empty] | 94.09 |  |  | 96.40 |  |  |  | 4.44 |  | 4.44 | [8 empty] | 0.06 |  |  |  |  | 1.19
2013 |  |  |  | 7454.01 |  |  | 8760 |  |  |  | 878 | [10 empty] | 97.12 |  |  |  | 98.37 | [5 empty] | 96.92 |  |  | 100.00 |  |  |  | 1.37 |  | 1.37 | [8 empty] | 0.26 |  |  |  |  | 1.25
2014 |  |  |  | 5818.57 |  |  | 6848 |  |  |  | 878 | [10 empty] | 75.86 |  |  |  | 76.51 | [5 empty] | 75.65 |  |  | 78.17 |  |  |  | 2.22 |  | 1.74 | [8 empty] | 21.75 |  |  |  |  | 0.65
2015 |  |  |  | 5480.95 |  |  | 6449 |  |  |  | 878 | [10 empty] | 71.43 |  |  |  | 72.33 | [5 empty] | 71.26 |  |  | 73.62 |  |  |  | 8.35 |  | 7.09 | [8 empty] | 20.58 |  |  |  |  | 0.90
2016 |  |  |  | 7570.79 |  |  | 8784 |  |  |  | 878 | [10 empty] | 98.62 |  |  |  | 99.69 | [5 empty] | 98.16 |  |  | 100.00 |  |  |  | 0.25 |  | 0.25 | [8 empty] | 0.07 |  |  |  |  | 1.07
2017 |  |  |  | 4638.42 |  |  | 6181 |  |  |  | 878 | [10 empty] | 60.26 |  |  |  | 60.87 | [5 empty] | 60.31 |  |  | 70.56 |  |  |  | 3.49 |  | 2.20 | [8 empty] | 36.93 |  |  |  |  | 0.61
2018 |  |  |  | 7477.90 |  |  | 8606 |  |  |  | 878 | [10 empty] | 97.02 |  |  |  | 97.92 | [5 empty] | 97.23 |  |  | 98.24 |  |  |  | 0.69 |  | 1.43 | [8 empty] | 0.64 |  |  |  |  | 0.90
2019 |  |  |  | 7619.17 |  |  | 8760 |  |  |  | 878 | [10 empty] | 99.13 |  |  |  | 99.70 | [5 empty] | 99.06 |  |  | 100.00 |  |  |  | 0.29 |  | 0.29 | [8 empty] | 0.01 |  |  |  |  | 0.57
2020 |  |  |  | 7565.81 |  |  | 8784 |  |  |  | 878 | [10 empty] | 98.22 |  |  |  | 99.08 | [5 empty] | 98.10 |  |  | 100.00 |  |  |  | 0.81 |  | 0.81 | [8 empty] | 0.11 |  |  |  |  | 0.85
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1992 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 403
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 705
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 38
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 0
Z. |  | Other | [39 empty] | 1
Subtotal | [37 empty] | 743 |  |  |  | 404 | [11 empty] | 3
Total | [22 empty] | 0 | [14 empty] | 1150
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1992 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 30
12. |  |  | Reactor I&C Systems | [34 empty] | 27
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 178
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 24
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 22
41. |  |  | Main Generator Systems | [34 empty] | 46
42. |  |  | Electrical Power Supply Systems | [34 empty] | 11
Total | [37 empty] | 380
Highlights (2020)
This Unit hit an international record of the longest CANDU run. It did so safely and reliably. It still continues this run into 2021.

## DARLINGTON-2
2020 Operating Experience
CA-23 | [8 empty] | DARLINGTON-2 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-09-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-01-15
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-10-09
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4218.91 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 5.06 %
Energy Availability Factor (EAF) | [18 empty] | : | 54.74 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.95 %
Unit Capability Factor (UCF) | [18 empty] | : | 55.41 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 41.64 %
Load Factor (LF) | [18 empty] | : | 54.7 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.67 %
Operating Factor (OF) | [18 empty] | : | 58.56 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3640 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 61.33 |  |  | 563.05 | [6 empty] | 622.50 |  | 626.55 |  |  |  | 605.54 |  |  | 648.77 |  |  | 612.22 | [9 empty] | 478.95 |  |  | 4218.91
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.39 |  |  | 88.89 | [6 empty] | 95.30 |  | 95.91 |  |  |  | 95.83 |  |  | 99.68 |  |  | 96.63 | [9 empty] | 73.67 |  |  | 54.74
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.39 |  |  | 89.14 | [6 empty] | 97.04 |  | 98.83 |  |  |  | 98.76 |  |  | 99.68 |  |  | 96.63 | [9 empty] | 73.84 |  |  | 55.41
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.39 |  |  | 89.07 | [6 empty] | 95.30 |  | 95.91 |  |  |  | 95.79 |  |  | 99.32 |  |  | 96.85 | [9 empty] | 73.32 |  |  | 54.70
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.31 |  |  | 94.31 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 93.28 |  |  | 58.56
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.14 | [6 empty] | 2.49 |  | 0.53 |  |  |  | 0.67 |  |  | 0.00 |  |  | 3.25 | [9 empty] | 26.16 |  |  | 5.06
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.95 | [6 empty] | 2.48 |  | 0.53 |  |  |  | 0.67 |  |  | 0.00 |  |  | 3.25 | [9 empty] | 26.16 |  |  | 2.95
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 90.61 |  |  | 8.91 | [6 empty] | 0.48 |  | 0.64 |  |  |  | 0.57 |  |  | 0.32 |  |  | 0.12 | [9 empty] | 0.00 |  |  | 41.64
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.25 | [6 empty] | 1.74 |  | 2.92 |  |  |  | 2.92 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.17 |  |  | 0.67
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 165550.04 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 12.77 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 70.49 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 10.78 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 71.37 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.85 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.32 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.87 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.93 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 1153.47 |  |  | 1608 |  |  |  | 881 | [10 empty] | 64.94 |  |  |  | 64.94 | [5 empty] | 65.73 |  |  | 80.72 |  |  |  | 35.03 |  | 35.02 | [8 empty] | 0.04 |  |  |  |  | 0.00
1991 |  |  |  | 51.48 |  |  | 102 |  |  |  | 881 | [10 empty] | 0.67 |  |  |  | 0.67 | [5 empty] | 0.67 |  |  | 1.16 |  |  |  | 99.33 |  | 99.33 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 1290.16 |  |  | 2418 |  |  |  | 881 | [10 empty] | 16.68 |  |  |  | 16.68 | [5 empty] | 16.67 |  |  | 27.53 |  |  |  | 83.32 |  | 83.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 6370.16 |  |  | 7594 |  |  |  | 881 | [10 empty] | 82.74 |  |  |  | 83.28 | [5 empty] | 82.54 |  |  | 86.69 |  |  |  | 8.13 |  | 7.37 | [8 empty] | 9.34 |  |  |  |  | 0.54
1994 |  |  |  | 6750.76 |  |  | 8069 |  |  |  | 881 | [10 empty] | 88.52 |  |  |  | 88.90 | [5 empty] | 87.47 |  |  | 92.11 |  |  |  | 5.87 |  | 5.54 | [8 empty] | 5.56 |  |  |  |  | 0.38
1995 |  |  |  | 6952.96 |  |  | 8104 |  |  |  | 881 | [10 empty] | 90.65 |  |  |  | 91.30 | [5 empty] | 90.09 |  |  | 92.51 |  |  |  | 5.07 |  | 4.88 | [8 empty] | 3.82 |  |  |  |  | 0.65
1996 |  |  |  | 6705.75 |  |  | 7752 |  |  |  | 881 | [10 empty] | 87.22 |  |  |  | 87.76 | [5 empty] | 86.65 |  |  | 88.25 |  |  |  | 5.55 |  | 5.15 | [8 empty] | 7.09 |  |  |  |  | 0.53
1997 |  |  |  | 4710.39 |  |  | 7069 |  |  |  | 881 | [10 empty] | 61.53 |  |  |  | 61.73 | [5 empty] | 61.03 |  |  | 80.70 |  |  |  | 29.89 |  | 26.32 | [8 empty] | 11.95 |  |  |  |  | 0.20
1998 |  |  |  | 6227.93 |  |  | 7492 |  |  |  | 881 | [10 empty] | 80.70 |  |  |  | 81.91 | [5 empty] | 80.70 |  |  | 85.53 |  |  |  | 18.09 |  | 18.09 | [8 empty] | 0.00 |  |  |  |  | 1.21
1999 |  |  |  | 6469.08 |  |  | 7824 |  |  |  | 881 | [10 empty] | 83.82 |  |  |  | 85.13 | [5 empty] | 83.82 |  |  | 89.32 |  |  |  | 5.12 |  | 4.60 | [8 empty] | 10.27 |  |  |  |  | 1.31
2000 |  |  |  | 6885.42 |  |  | 8221 |  |  |  | 881 | [10 empty] | 88.97 |  |  |  | 90.14 | [5 empty] | 88.97 |  |  | 93.59 |  |  |  | 9.86 |  | 9.86 | [8 empty] | 0.00 |  |  |  |  | 1.17
2001 |  |  |  | 5826.45 |  |  | 7030 |  |  |  | 881 | [10 empty] | 75.50 |  |  |  | 76.30 | [5 empty] | 75.50 |  |  | 80.25 |  |  |  | 6.64 |  | 5.43 | [8 empty] | 18.27 |  |  |  |  | 0.81
2002 |  |  |  | 7268.93 |  |  | 8627 |  |  |  | 881 | [10 empty] | 94.19 |  |  |  | 95.43 | [5 empty] | 94.19 |  |  | 98.48 |  |  |  | 4.57 |  | 4.57 | [8 empty] | 0.00 |  |  |  |  | 1.25
2003 |  |  |  | 6084.10 |  |  | 7245 |  |  |  | 881 | [10 empty] | 79.29 |  |  |  | 81.59 | [5 empty] | 78.83 |  |  | 82.71 |  |  |  | 5.71 |  | 4.94 | [8 empty] | 13.47 |  |  |  |  | 2.30
2004 |  |  |  | 7038.38 |  |  | 8737 |  |  |  | 881 | [10 empty] | 91.42 |  |  |  | 96.71 | [5 empty] | 90.95 |  |  | 99.46 |  |  |  | 3.29 |  | 3.29 | [8 empty] | 0.00 |  |  |  |  | 5.29
2005 |  |  |  | 6056.21 |  |  | 7031 |  |  |  | 878 | [10 empty] | 78.93 |  |  |  | 79.75 | [5 empty] | 78.67 |  |  | 80.26 |  |  |  | 0.98 |  | 4.72 | [8 empty] | 15.53 |  |  |  |  | 0.82
2006 |  |  |  | 7548.39 |  |  | 8745 |  |  |  | 878 | [10 empty] | 98.59 |  |  |  | 99.38 | [5 empty] | 98.14 |  |  | 99.83 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.00 |  |  |  |  | 0.79
2007 |  |  |  | 6364.83 |  |  | 7327 |  |  |  | 878 | [10 empty] | 82.85 |  |  |  | 83.37 | [5 empty] | 82.75 |  |  | 83.64 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 16.62 |  |  |  |  | 0.52
2008 |  |  |  | 7560.94 |  |  | 8696 |  |  |  | 878 | [10 empty] | 98.15 |  |  |  | 98.82 | [5 empty] | 98.04 |  |  | 99.00 |  |  |  | 1.18 |  | 1.18 | [8 empty] | 0.00 |  |  |  |  | 0.67
2009 |  |  |  | 6745.27 |  |  | 7769 |  |  |  | 878 | [10 empty] | 87.67 |  |  |  | 88.37 | [5 empty] | 87.70 |  |  | 88.69 |  |  |  | 2.03 |  | 2.71 | [8 empty] | 8.91 |  |  |  |  | 0.70
2010 |  |  |  | 6234.30 |  |  | 7248 |  |  |  | 878 | [10 empty] | 81.14 |  |  |  | 82.48 | [5 empty] | 81.06 |  |  | 82.74 |  |  |  | 0.67 |  | 0.56 | [8 empty] | 16.96 |  |  |  |  | 1.34
2011 |  |  |  | 7503.51 |  |  | 8719 |  |  |  | 878 | [10 empty] | 97.74 |  |  |  | 98.90 | [5 empty] | 97.56 |  |  | 99.53 |  |  |  | 1.06 |  | 1.06 | [8 empty] | 0.04 |  |  |  |  | 1.16
2012 |  |  |  | 7157.95 |  |  | 8467 |  |  |  | 878 | [10 empty] | 92.97 |  |  |  | 93.92 | [5 empty] | 92.81 |  |  | 96.39 |  |  |  | 3.86 |  | 3.77 | [8 empty] | 2.30 |  |  |  |  | 0.96
2013 |  |  |  | 5138.76 |  |  | 6131 |  |  |  | 878 | [10 empty] | 66.97 |  |  |  | 67.33 | [5 empty] | 66.81 |  |  | 69.99 |  |  |  | 7.39 |  | 10.77 | [8 empty] | 21.91 |  |  |  |  | 0.36
2014 |  |  |  | 7412.53 |  |  | 8522 |  |  |  | 878 | [10 empty] | 96.38 |  |  |  | 96.90 | [5 empty] | 96.38 |  |  | 97.28 |  |  |  | 2.22 |  | 2.21 | [8 empty] | 0.89 |  |  |  |  | 0.52
2015 |  |  |  | 6405.95 |  |  | 7428 |  |  |  | 878 | [10 empty] | 83.41 |  |  |  | 84.28 | [5 empty] | 83.29 |  |  | 84.79 |  |  |  | 2.05 |  | 1.77 | [8 empty] | 13.95 |  |  |  |  | 0.87
2016 |  |  |  | 5728.84 |  |  | 6793 |  |  |  | 878 | [10 empty] | 74.41 |  |  |  | 75.73 | [5 empty] | 74.28 |  |  | 77.33 |  |  |  | 3.13 |  | 2.45 | [8 empty] | 21.82 |  |  |  |  | 1.32
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 4218.91 |  |  | 5144 |  |  |  | 878 | [10 empty] | 54.74 |  |  |  | 55.41 | [5 empty] | 54.70 |  |  | 58.56 |  |  |  | 5.06 |  | 2.95 | [8 empty] | 41.64 |  |  |  |  | 0.67
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1990 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 50 | [14 empty] | 501
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 501 |  |  |  | 11
E. |  | Testing of plant systems or components | [20 empty] | 393 | [14 empty] | 13
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 3196 | [14 empty] | 1036
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
Z. |  | Other | [39 empty] | 217
Subtotal | [22 empty] | 3589 |  |  |  | 50 | [10 empty] | 1550 |  |  |  | 729 | [11 empty] | 2
Total | [22 empty] | 3639 | [14 empty] | 2281
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1990 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 36
12. |  |  | Reactor I&C Systems | [34 empty] | 27
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 312
16. |  |  | Steam generation systems | [34 empty] | 40
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [19 empty] | 50 | [14 empty] | 16
31. |  |  | Turbine and auxiliaries | [34 empty] | 20
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 6
35. |  |  | All other I&C Systems | [34 empty] | 11
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 11
Total | [22 empty] | 50 | [14 empty] | 503
Highlights (2020)
This unit was successfully returned to service after a multi-year refurbishment.

## DARLINGTON-3
2020 Operating Experience
CA-24 | [8 empty] | DARLINGTON-3 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-09-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1992-12-07
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-02-14
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 28 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4483.41 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.04 %
Energy Availability Factor (EAF) | [18 empty] | : | 57.75 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.37 %
Unit Capability Factor (UCF) | [18 empty] | : | 57.88 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 41.75 %
Load Factor (LF) | [18 empty] | : | 58.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.13 %
Operating Factor (OF) | [18 empty] | : | 57.91 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3697 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 661.15 | 613.91 |  |  |  | 657.38 |  | 636.79 | [8 empty] | 654.30 |  |  | 634.86 | [6 empty] | 625.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4483.41
EAF [%] |  |  |  |  | 99.99 | 99.99 |  |  |  | 99.91 |  | 100.00 | [8 empty] | 99.99 |  |  | 99.79 | [6 empty] | 95.06 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 57.75
UCF [%] |  |  |  |  | 99.99 | 99.99 |  |  |  | 99.91 |  | 100.00 | [8 empty] | 99.99 |  |  | 99.99 | [6 empty] | 96.40 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 57.88
LF [%] |  |  |  |  | 101.21 | 100.46 |  |  |  | 100.63 |  | 100.73 | [8 empty] | 100.16 |  |  | 100.43 | [6 empty] | 95.68 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 58.13
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 96.64 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 57.91
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.09 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.18 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.04
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.09 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.17 |  | 0.00 |  |  |  | 4.29 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.37
PUF [%] |  |  |  |  | 0.01 | 0.01 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.01 | [6 empty] | 3.43 |  | 100.00 |  |  |  | 95.71 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 41.75
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.20 | [6 empty] | 1.34 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.13
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 183258.61 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.94 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.87 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.12 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.01 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.02 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.82 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.97 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 6003.39 |  |  | 7141 |  |  |  | 881 | [10 empty] | 89.24 |  |  |  | 89.81 | [5 empty] | 85.01 |  |  | 89.08 |  |  |  | 10.05 |  | 10.04 | [8 empty] | 0.15 |  |  |  |  | 0.57
1994 |  |  |  | 6528.54 |  |  | 7642 |  |  |  | 881 | [10 empty] | 85.26 |  |  |  | 85.64 | [5 empty] | 84.59 |  |  | 87.24 |  |  |  | 2.11 |  | 1.85 | [8 empty] | 12.51 |  |  |  |  | 0.38
1995 |  |  |  | 7061.53 |  |  | 8219 |  |  |  | 881 | [10 empty] | 92.22 |  |  |  | 92.93 | [5 empty] | 91.50 |  |  | 93.82 |  |  |  | 3.05 |  | 2.92 | [8 empty] | 4.15 |  |  |  |  | 0.71
1996 |  |  |  | 7391.57 |  |  | 8574 |  |  |  | 881 | [10 empty] | 96.66 |  |  |  | 97.34 | [5 empty] | 95.51 |  |  | 97.61 |  |  |  | 2.65 |  | 2.65 | [8 empty] | 0.01 |  |  |  |  | 0.68
1997 |  |  |  | 4010.78 |  |  | 6314 |  |  |  | 881 | [10 empty] | 52.10 |  |  |  | 52.35 | [5 empty] | 51.97 |  |  | 72.08 |  |  |  | 40.36 |  | 35.42 | [8 empty] | 12.22 |  |  |  |  | 0.25
1998 |  |  |  | 7244.91 |  |  | 8593 |  |  |  | 881 | [10 empty] | 93.88 |  |  |  | 94.68 | [5 empty] | 93.88 |  |  | 98.09 |  |  |  | 4.05 |  | 4.00 | [8 empty] | 1.32 |  |  |  |  | 0.80
1999 |  |  |  | 5629.08 |  |  | 6929 |  |  |  | 881 | [10 empty] | 72.94 |  |  |  | 75.09 | [5 empty] | 72.94 |  |  | 79.10 |  |  |  | 6.57 |  | 5.28 | [8 empty] | 19.63 |  |  |  |  | 2.15
2000 |  |  |  | 6517.02 |  |  | 7822 |  |  |  | 881 | [10 empty] | 84.22 |  |  |  | 85.10 | [5 empty] | 84.21 |  |  | 89.05 |  |  |  | 8.27 |  | 7.67 | [8 empty] | 7.23 |  |  |  |  | 0.88
2001 |  |  |  | 6577.97 |  |  | 7901 |  |  |  | 881 | [10 empty] | 85.23 |  |  |  | 86.30 | [5 empty] | 85.23 |  |  | 90.19 |  |  |  | 8.87 |  | 8.40 | [8 empty] | 5.30 |  |  |  |  | 1.07
2002 |  |  |  | 6371.77 |  |  | 7595 |  |  |  | 881 | [10 empty] | 82.58 |  |  |  | 83.68 | [5 empty] | 82.56 |  |  | 86.70 |  |  |  | 4.81 |  | 4.23 | [8 empty] | 12.09 |  |  |  |  | 1.10
2003 |  |  |  | 6827.19 |  |  | 8004 |  |  |  | 881 | [10 empty] | 88.62 |  |  |  | 89.45 | [5 empty] | 88.46 |  |  | 91.37 |  |  |  | 2.21 |  | 2.02 | [8 empty] | 8.53 |  |  |  |  | 0.83
2004 |  |  |  | 6601.58 |  |  | 7649 |  |  |  | 881 | [10 empty] | 85.59 |  |  |  | 86.88 | [5 empty] | 85.31 |  |  | 87.08 |  |  |  | 5.14 |  | 4.71 | [8 empty] | 8.41 |  |  |  |  | 1.29
2005 |  |  |  | 7562.05 |  |  | 8760 |  |  |  | 878 | [10 empty] | 98.26 |  |  |  | 99.08 | [5 empty] | 98.24 |  |  | 100.00 |  |  |  | 0.89 |  | 0.89 | [8 empty] | 0.02 |  |  |  |  | 0.83
2006 |  |  |  | 5573.10 |  |  | 6452 |  |  |  | 878 | [10 empty] | 72.50 |  |  |  | 73.12 | [5 empty] | 72.46 |  |  | 73.65 |  |  |  | 8.54 |  | 13.05 | [8 empty] | 13.84 |  |  |  |  | 0.62
2007 |  |  |  | 7221.13 |  |  | 8311 |  |  |  | 878 | [10 empty] | 93.90 |  |  |  | 94.75 | [5 empty] | 93.89 |  |  | 94.87 |  |  |  | 0.02 |  | 0.75 | [8 empty] | 4.49 |  |  |  |  | 0.85
2008 |  |  |  | 7654.59 |  |  | 8784 |  |  |  | 878 | [10 empty] | 99.15 |  |  |  | 99.93 | [5 empty] | 99.25 |  |  | 100.00 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.03 |  |  |  |  | 0.78
2009 |  |  |  | 5657.16 |  |  | 6590 |  |  |  | 878 | [10 empty] | 73.60 |  |  |  | 74.47 | [5 empty] | 73.55 |  |  | 75.23 |  |  |  | 2.00 |  | 3.62 | [8 empty] | 21.91 |  |  |  |  | 0.87
2010 |  |  |  | 7500.90 |  |  | 8643 |  |  |  | 878 | [10 empty] | 97.47 |  |  |  | 98.51 | [5 empty] | 97.52 |  |  | 98.66 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 1.43 |  |  |  |  | 1.04
2011 |  |  |  | 7558.56 |  |  | 8707 |  |  |  | 878 | [10 empty] | 98.37 |  |  |  | 99.17 | [5 empty] | 98.27 |  |  | 99.39 |  |  |  | 0.78 |  | 0.78 | [8 empty] | 0.04 |  |  |  |  | 0.81
2012 |  |  |  | 6377.61 |  |  | 7419 |  |  |  | 878 | [10 empty] | 83.03 |  |  |  | 83.97 | [5 empty] | 82.69 |  |  | 84.46 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 15.98 |  |  |  |  | 0.94
2013 |  |  |  | 7334.60 |  |  | 8470 |  |  |  | 878 | [10 empty] | 95.63 |  |  |  | 96.61 | [5 empty] | 95.36 |  |  | 96.69 |  |  |  | 3.35 |  | 3.35 | [8 empty] | 0.04 |  |  |  |  | 0.98
2014 |  |  |  | 7501.60 |  |  | 8708 |  |  |  | 878 | [10 empty] | 97.75 |  |  |  | 98.75 | [5 empty] | 97.53 |  |  | 99.41 |  |  |  | 1.23 |  | 1.23 | [8 empty] | 0.02 |  |  |  |  | 1.00
2015 |  |  |  | 4992.10 |  |  | 5787 |  |  |  | 878 | [10 empty] | 65.00 |  |  |  | 65.52 | [5 empty] | 64.91 |  |  | 66.06 |  |  |  | 8.58 |  | 7.75 | [8 empty] | 26.73 |  |  |  |  | 0.52
2016 |  |  |  | 6716.91 |  |  | 7832 |  |  |  | 878 | [10 empty] | 86.99 |  |  |  | 87.63 | [5 empty] | 87.09 |  |  | 89.16 |  |  |  | 5.93 |  | 5.53 | [8 empty] | 6.84 |  |  |  |  | 0.64
2017 |  |  |  | 7219.88 |  |  | 8442 |  |  |  | 878 | [10 empty] | 94.27 |  |  |  | 95.20 | [5 empty] | 93.87 |  |  | 96.37 |  |  |  | 1.42 |  | 1.37 | [8 empty] | 3.43 |  |  |  |  | 0.93
2018 |  |  |  | 5781.75 |  |  | 6718 |  |  |  | 878 | [10 empty] | 75.15 |  |  |  | 75.94 | [5 empty] | 75.17 |  |  | 76.69 |  |  |  | 1.62 |  | 1.25 | [8 empty] | 22.81 |  |  |  |  | 0.79
2019 |  |  |  | 7026.63 |  |  | 8178 |  |  |  | 878 | [10 empty] | 91.58 |  |  |  | 91.98 | [5 empty] | 91.36 |  |  | 93.36 |  |  |  | 7.52 |  | 7.48 | [8 empty] | 0.54 |  |  |  |  | 0.40
2020 |  |  |  | 4483.41 |  |  | 5087 |  |  |  | 878 | [10 empty] | 57.75 |  |  |  | 57.88 | [5 empty] | 58.13 |  |  | 57.91 |  |  |  | 0.04 |  | 0.37 | [8 empty] | 41.75 |  |  |  |  | 0.13
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1993 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 31 | [14 empty] | 261
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 71
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 792 | [14 empty] | 597
E. |  | Testing of plant systems or components | [39 empty] | 5
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 2875 | [14 empty] | 103
L. |  | Human factor related | [39 empty] | 3
Subtotal | [22 empty] | 3667 |  |  |  | 31 | [10 empty] | 771 |  |  |  | 269
Total | [22 empty] | 3698 | [14 empty] | 1040
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1993 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 31 | [14 empty] | 23
12. |  |  | Reactor I&C Systems | [34 empty] | 27
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 31
14. |  |  | Safety Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 43
16. |  |  | Steam generation systems | [34 empty] | 14
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 19
31. |  |  | Turbine and auxiliaries | [34 empty] | 57
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
34. |  |  | Miscellaneous Systems | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 19
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [22 empty] | 31 | [14 empty] | 269
Highlights (2020)
This unit entered into a long term Refurbishment on September 2020.

## DARLINGTON-4
2020 Operating Experience
CA-25 | [8 empty] | DARLINGTON-4 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-07-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-04-17
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-06-14
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7294.39 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.46 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.26 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.41 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.87 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 3.72 %
Load Factor (LF) | [18 empty] | : | 94.58 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.61 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 648.43 | 580.80 |  |  |  | 658.09 |  | 634.47 | [8 empty] | 660.53 |  |  | 635.05 | [6 empty] | 643.25 |  | 566.85 |  |  |  | 610.45 |  |  | 653.50 |  |  | 610.18 | [9 empty] | 392.78 |  |  | 7294.39
EAF [%] |  |  |  |  | 99.18 | 94.74 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 100.00 |  |  | 99.78 | [6 empty] | 98.70 |  | 86.89 |  |  |  | 96.61 |  |  | 100.00 |  |  | 95.59 | [9 empty] | 60.13 |  |  | 94.26
UCF [%] |  |  |  |  | 99.18 | 94.74 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.95 |  | 89.35 |  |  |  | 100.00 |  |  | 100.00 |  |  | 95.59 | [9 empty] | 60.13 |  |  | 94.87
LF [%] |  |  |  |  | 99.27 | 95.04 |  |  |  | 100.74 |  | 100.37 | [8 empty] | 101.12 |  |  | 100.46 | [6 empty] | 98.47 |  | 86.78 |  |  |  | 96.57 |  |  | 100.04 |  |  | 96.52 | [9 empty] | 60.13 |  |  | 94.58
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.82 | 5.26 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.05 |  | 10.65 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.27 |  |  | 1.46
UCL [%] |  |  |  |  | 0.82 | 5.26 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.05 |  | 10.65 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.16 |  |  | 1.41
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 4.41 | [9 empty] | 39.71 |  |  | 3.72
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.22 | [6 empty] | 1.25 |  | 2.46 |  |  |  | 3.39 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.61
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 182991.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.94 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.85 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.92 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.55 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.52 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.74 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.7 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.26 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 3528.78 |  |  | 4447 |  |  |  | 881 | [10 empty] | 73.87 |  |  |  | 74.02 | [5 empty] | 67.58 |  |  | 70.40 |  |  |  | 10.42 |  | 8.61 | [8 empty] | 17.37 |  |  |  |  | 0.15
1994 |  |  |  | 7038.67 |  |  | 8143 |  |  |  | 881 | [10 empty] | 91.85 |  |  |  | 92.19 | [5 empty] | 91.20 |  |  | 92.96 |  |  |  | 3.36 |  | 3.21 | [8 empty] | 4.60 |  |  |  |  | 0.35
1995 |  |  |  | 6750.56 |  |  | 7751 |  |  |  | 881 | [10 empty] | 87.72 |  |  |  | 88.14 | [5 empty] | 87.47 |  |  | 88.48 |  |  |  | 2.41 |  | 2.18 | [8 empty] | 9.68 |  |  |  |  | 0.43
1996 |  |  |  | 6105.35 |  |  | 7023 |  |  |  | 881 | [10 empty] | 79.14 |  |  |  | 79.37 | [5 empty] | 78.89 |  |  | 79.95 |  |  |  | 12.79 |  | 11.65 | [8 empty] | 8.98 |  |  |  |  | 0.23
1997 |  |  |  | 5069.64 |  |  | 7428 |  |  |  | 881 | [10 empty] | 65.71 |  |  |  | 65.97 | [5 empty] | 65.69 |  |  | 84.79 |  |  |  | 28.56 |  | 26.37 | [8 empty] | 7.65 |  |  |  |  | 0.27
1998 |  |  |  | 6520.88 |  |  | 7699 |  |  |  | 881 | [10 empty] | 84.49 |  |  |  | 85.32 | [5 empty] | 84.49 |  |  | 87.89 |  |  |  | 11.60 |  | 11.20 | [8 empty] | 3.48 |  |  |  |  | 0.83
1999 |  |  |  | 6216.13 |  |  | 7431 |  |  |  | 881 | [10 empty] | 80.55 |  |  |  | 81.60 | [5 empty] | 80.55 |  |  | 84.83 |  |  |  | 5.28 |  | 4.55 | [8 empty] | 13.85 |  |  |  |  | 1.05
2000 |  |  |  | 6975.02 |  |  | 8219 |  |  |  | 881 | [10 empty] | 90.13 |  |  |  | 90.78 | [5 empty] | 90.13 |  |  | 93.57 |  |  |  | 9.22 |  | 9.22 | [8 empty] | 0.00 |  |  |  |  | 0.65
2001 |  |  |  | 6836.35 |  |  | 8037 |  |  |  | 881 | [10 empty] | 88.58 |  |  |  | 89.62 | [5 empty] | 88.58 |  |  | 91.75 |  |  |  | 3.01 |  | 2.78 | [8 empty] | 7.59 |  |  |  |  | 1.04
2002 |  |  |  | 7449.79 |  |  | 8760 |  |  |  | 881 | [10 empty] | 96.53 |  |  |  | 97.33 | [5 empty] | 96.53 |  |  | 100.00 |  |  |  | 2.67 |  | 2.67 | [8 empty] | 0.00 |  |  |  |  | 0.80
2003 |  |  |  | 5428.86 |  |  | 6320 |  |  |  | 881 | [10 empty] | 70.64 |  |  |  | 72.28 | [5 empty] | 70.34 |  |  | 72.15 |  |  |  | 5.81 |  | 4.46 | [8 empty] | 23.26 |  |  |  |  | 1.64
2004 |  |  |  | 7321.13 |  |  | 8451 |  |  |  | 881 | [10 empty] | 94.60 |  |  |  | 95.25 | [5 empty] | 94.60 |  |  | 96.21 |  |  |  | 4.75 |  | 4.75 | [8 empty] | 0.00 |  |  |  |  | 0.65
2005 |  |  |  | 6569.70 |  |  | 7617 |  |  |  | 878 | [10 empty] | 85.63 |  |  |  | 86.47 | [5 empty] | 85.35 |  |  | 86.95 |  |  |  | 0.36 |  | 2.49 | [8 empty] | 11.04 |  |  |  |  | 0.84
2006 |  |  |  | 7449.44 |  |  | 8541 |  |  |  | 878 | [10 empty] | 96.54 |  |  |  | 97.08 | [5 empty] | 96.86 |  |  | 97.50 |  |  |  | 2.92 |  | 2.92 | [8 empty] | 0.00 |  |  |  |  | 0.54
2007 |  |  |  | 6210.23 |  |  | 7170 |  |  |  | 878 | [10 empty] | 80.77 |  |  |  | 81.44 | [5 empty] | 80.74 |  |  | 81.85 |  |  |  | 2.90 |  | 2.43 | [8 empty] | 16.13 |  |  |  |  | 0.67
2008 |  |  |  | 7525.46 |  |  | 8652 |  |  |  | 878 | [10 empty] | 97.35 |  |  |  | 98.39 | [5 empty] | 97.58 |  |  | 98.50 |  |  |  | 1.48 |  | 1.48 | [8 empty] | 0.13 |  |  |  |  | 1.05
2009 |  |  |  | 6836.15 |  |  | 7892 |  |  |  | 878 | [10 empty] | 88.71 |  |  |  | 89.71 | [5 empty] | 88.88 |  |  | 90.09 |  |  |  | 2.12 |  | 2.23 | [8 empty] | 8.06 |  |  |  |  | 1.00
2010 |  |  |  | 5633.65 |  |  | 6612 |  |  |  | 878 | [10 empty] | 73.26 |  |  |  | 73.62 | [5 empty] | 73.25 |  |  | 75.48 |  |  |  | 8.67 |  | 10.81 | [8 empty] | 15.57 |  |  |  |  | 0.36
2011 |  |  |  | 7617.80 |  |  | 8760 |  |  |  | 878 | [10 empty] | 98.89 |  |  |  | 99.73 | [5 empty] | 99.04 |  |  | 100.00 |  |  |  | 0.23 |  | 0.23 | [8 empty] | 0.04 |  |  |  |  | 0.85
2012 |  |  |  | 7557.72 |  |  | 8725 |  |  |  | 878 | [10 empty] | 97.88 |  |  |  | 98.99 | [5 empty] | 97.99 |  |  | 99.33 |  |  |  | 0.87 |  | 0.87 | [8 empty] | 0.14 |  |  |  |  | 1.11
2013 |  |  |  | 5237.45 |  |  | 6132 |  |  |  | 878 | [10 empty] | 68.25 |  |  |  | 68.83 | [5 empty] | 68.10 |  |  | 70.00 |  |  |  | 9.51 |  | 12.75 | [8 empty] | 18.42 |  |  |  |  | 0.58
2014 |  |  |  | 7302.71 |  |  | 8476 |  |  |  | 878 | [10 empty] | 95.24 |  |  |  | 95.97 | [5 empty] | 94.95 |  |  | 96.76 |  |  |  | 0.65 |  | 0.63 | [8 empty] | 3.40 |  |  |  |  | 0.73
2015 |  |  |  | 6532.11 |  |  | 7490 |  |  |  | 878 | [10 empty] | 84.72 |  |  |  | 85.13 | [5 empty] | 84.93 |  |  | 85.50 |  |  |  | 1.53 |  | 1.32 | [8 empty] | 13.55 |  |  |  |  | 0.40
2016 |  |  |  | 5774.65 |  |  | 6678 |  |  |  | 878 | [10 empty] | 74.66 |  |  |  | 75.46 | [5 empty] | 74.88 |  |  | 76.02 |  |  |  | 0.23 |  | 0.18 | [8 empty] | 24.36 |  |  |  |  | 0.80
2017 |  |  |  | 7593.09 |  |  | 8684 |  |  |  | 878 | [10 empty] | 98.10 |  |  |  | 98.77 | [5 empty] | 98.72 |  |  | 99.13 |  |  |  | 1.03 |  | 1.03 | [8 empty] | 0.20 |  |  |  |  | 0.67
2018 |  |  |  | 6993.41 |  |  | 8105 |  |  |  | 878 | [10 empty] | 90.71 |  |  |  | 91.56 | [5 empty] | 90.93 |  |  | 92.52 |  |  |  | 1.42 |  | 1.32 | [8 empty] | 7.12 |  |  |  |  | 0.85
2019 |  |  |  | 5423.69 |  |  | 6248 |  |  |  | 878 | [10 empty] | 70.07 |  |  |  | 70.44 | [5 empty] | 70.52 |  |  | 71.32 |  |  |  | 7.34 |  | 5.58 | [8 empty] | 23.99 |  |  |  |  | 0.37
2020 |  |  |  | 7294.39 |  |  | 8784 |  |  |  | 878 | [10 empty] | 94.26 |  |  |  | 94.87 | [5 empty] | 94.58 |  |  | 100.00 |  |  |  | 1.46 |  | 1.41 | [8 empty] | 3.72 |  |  |  |  | 0.61
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1993 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 284
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 95
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 615
E. |  | Testing of plant systems or components | [35 empty] | 12 |  |  |  | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 10
Subtotal | [37 empty] | 722 |  |  |  | 296 | [11 empty] | 4
Total | [22 empty] | 0 | [14 empty] | 1022
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1993 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 40
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
14. |  |  | Safety Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 85
16. |  |  | Steam generation systems | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 16
31. |  |  | Turbine and auxiliaries | [34 empty] | 41
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 21
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 19
42. |  |  | Electrical Power Supply Systems | [34 empty] | 32
Total | [37 empty] | 297

## PICKERING-1
2020 Operating Experience
CA-4 | [8 empty] | PICKERING-1 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500A | [11 empty] | Construction Date | [15 empty] | : |  |  | 1966-06-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1971-04-04
Gross electrical power | [12 empty] | : |  |  | 542 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1971-07-29
Reference unit power (net) | [12 empty] | : |  |  | 515 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 9080 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4680 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 26.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 6 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2244.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 9.73 %
Energy Availability Factor (EAF) | [18 empty] | : | 49.73 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.4 %
Unit Capability Factor (UCF) | [18 empty] | : | 50.11 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 44.49 %
Load Factor (LF) | [18 empty] | : | 49.61 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.38 %
Operating Factor (OF) | [18 empty] | : | 53.05 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4124 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 108.75 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 48.59 | [6 empty] | 372.89 |  | 365.07 |  |  |  | 242.31 |  |  | 378.53 |  |  | 356.00 | [9 empty] | 371.92 |  |  | 2244.06
EAF [%] |  |  |  |  | 28.77 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 13.10 | [6 empty] | 97.45 |  | 95.34 |  |  |  | 65.35 |  |  | 99.18 |  |  | 96.29 | [9 empty] | 97.28 |  |  | 49.73
UCF [%] |  |  |  |  | 28.77 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 13.10 | [6 empty] | 98.59 |  | 97.60 |  |  |  | 66.50 |  |  | 99.18 |  |  | 96.29 | [9 empty] | 97.28 |  |  | 50.11
LF [%] |  |  |  |  | 28.38 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 13.10 | [6 empty] | 97.32 |  | 95.28 |  |  |  | 65.35 |  |  | 98.79 |  |  | 96.01 | [9 empty] | 97.07 |  |  | 49.61
OF [%] |  |  |  |  | 28.76 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 27.36 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 76.81 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 53.05
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 68.32 | [6 empty] | 1.41 |  | 0.04 |  |  |  | 33.50 |  |  | 0.82 |  |  | 1.65 | [9 empty] | 0.18 |  |  | 9.73
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 28.25 | [6 empty] | 1.41 |  | 0.04 |  |  |  | 33.50 |  |  | 0.82 |  |  | 1.62 | [9 empty] | 0.18 |  |  | 5.40
PUF [%] |  |  |  |  | 71.23 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 58.65 | [6 empty] | 0.00 |  | 2.37 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.09 | [9 empty] | 2.54 |  |  | 44.49
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.14 |  | 2.26 |  |  |  | 1.15 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.38
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 123572.37 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 24 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 67.4 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 22.42 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 67.63 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.95 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.34 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.23 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 68.74 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1971 |  |  |  | 2302.30 |  |  | 4829 |  |  |  | 514 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 80.43 |  |  | 78.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1972 |  |  |  | 2207.90 |  |  | 4117 |  |  |  | 514 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 48.90 |  |  | 46.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 4222.40 |  |  | 8523 |  |  |  | 514 | [10 empty] | 93.98 |  |  |  | 93.98 | [5 empty] | 92.26 |  |  | 95.72 |  |  |  | 5.19 |  | 5.15 | [8 empty] | 0.88 |  |  |  |  | 0.00
1974 |  |  |  | 3232.00 |  |  | 6979 |  |  |  | 514 | [10 empty] | 71.92 |  |  |  | 71.92 | [5 empty] | 71.98 |  |  | 79.89 |  |  |  | 20.17 |  | 18.17 | [8 empty] | 9.91 |  |  |  |  | 0.00
1975 |  |  |  | 3592.80 |  |  | 7234 |  |  |  | 512 | [10 empty] | 80.17 |  |  |  | 80.17 | [5 empty] | 80.32 |  |  | 82.81 |  |  |  | 11.74 |  | 10.66 | [8 empty] | 9.17 |  |  |  |  | 0.00
1976 |  |  |  | 4169.70 |  |  | 8136 |  |  |  | 514 | [10 empty] | 92.73 |  |  |  | 92.73 | [5 empty] | 92.61 |  |  | 92.88 |  |  |  | 2.07 |  | 1.96 | [8 empty] | 5.31 |  |  |  |  | 0.00
1977 |  |  |  | 3852.80 |  |  | 7545 |  |  |  | 514 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 85.80 |  |  | 86.37 |  |  |  | 6.14 |  | 5.61 | [8 empty] | 8.59 |  |  |  |  | 0.00
1978 |  |  |  | 4273.70 |  |  | 8359 |  |  |  | 515 | [10 empty] | 95.09 |  |  |  | 95.09 | [5 empty] | 94.99 |  |  | 95.68 |  |  |  | 4.91 |  | 4.91 | [8 empty] | 0.00 |  |  |  |  | 0.00
1979 |  |  |  | 3781.40 |  |  | 7554 |  |  |  | 515 | [10 empty] | 85.29 |  |  |  | 85.29 | [5 empty] | 82.91 |  |  | 85.30 |  |  |  | 14.71 |  | 14.71 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 3356.90 |  |  | 6640 |  |  |  | 515 | [10 empty] | 73.68 |  |  |  | 73.68 | [5 empty] | 74.21 |  |  | 75.59 |  |  |  | 14.10 |  | 12.09 | [8 empty] | 14.23 |  |  |  |  | 0.00
1981 |  |  |  | 3947.70 |  |  | 7795 |  |  |  | 515 | [10 empty] | 88.05 |  |  |  | 88.05 | [5 empty] | 87.50 |  |  | 88.98 |  |  |  | 5.07 |  | 4.70 | [8 empty] | 7.25 |  |  |  |  | 0.00
1982 |  |  |  | 3499.30 |  |  | 6915 |  |  |  | 515 | [10 empty] | 77.80 |  |  |  | 77.80 | [5 empty] | 77.57 |  |  | 78.94 |  |  |  | 10.00 |  | 8.65 | [8 empty] | 13.55 |  |  |  |  | 0.00
1983 |  |  |  | 3070.80 |  |  | 6101 |  |  |  | 515 | [10 empty] | 68.11 |  |  |  | 68.11 | [5 empty] | 68.07 |  |  | 69.65 |  |  |  | 27.81 |  | 26.23 | [8 empty] | 5.66 |  |  |  |  | 0.00
1984 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 832.79 |  |  | 1981 |  |  |  | 515 | [10 empty] | 17.35 |  |  |  | 19.69 | [5 empty] | 18.46 |  |  | 22.61 |  |  |  | 78.69 |  | 72.71 | [8 empty] | 7.60 |  |  |  |  | 2.33
1988 |  |  |  | 3986.48 |  |  | 8224 |  |  |  | 515 | [10 empty] | 89.12 |  |  |  | 89.16 | [5 empty] | 88.12 |  |  | 93.62 |  |  |  | 10.81 |  | 10.81 | [8 empty] | 0.04 |  |  |  |  | 0.03
1989 |  |  |  | 3222.13 |  |  | 6943 |  |  |  | 515 | [10 empty] | 72.62 |  |  |  | 72.72 | [5 empty] | 71.42 |  |  | 79.26 |  |  |  | 20.54 |  | 18.80 | [8 empty] | 8.48 |  |  |  |  | 0.11
1990 |  |  |  | 3041.75 |  |  | 7435 |  |  |  | 515 | [10 empty] | 70.56 |  |  |  | 70.86 | [5 empty] | 67.42 |  |  | 84.87 |  |  |  | 22.19 |  | 20.21 | [8 empty] | 8.93 |  |  |  |  | 0.30
1991 |  |  |  | 3051.08 |  |  | 6525 |  |  |  | 515 | [10 empty] | 67.83 |  |  |  | 67.84 | [5 empty] | 67.63 |  |  | 74.49 |  |  |  | 18.36 |  | 15.26 | [8 empty] | 16.90 |  |  |  |  | 0.01
1992 |  |  |  | 2919.96 |  |  | 5798 |  |  |  | 515 | [10 empty] | 65.43 |  |  |  | 65.43 | [5 empty] | 64.55 |  |  | 66.01 |  |  |  | 22.58 |  | 19.09 | [8 empty] | 15.48 |  |  |  |  | 0.00
1993 |  |  |  | 3451.16 |  |  | 6908 |  |  |  | 515 | [10 empty] | 78.39 |  |  |  | 78.43 | [5 empty] | 76.50 |  |  | 78.86 |  |  |  | 8.82 |  | 7.59 | [8 empty] | 13.98 |  |  |  |  | 0.04
1994 |  |  |  | 897.64 |  |  | 1835 |  |  |  | 515 | [10 empty] | 20.12 |  |  |  | 20.12 | [5 empty] | 19.90 |  |  | 20.95 |  |  |  | 54.24 |  | 23.84 | [8 empty] | 56.04 |  |  |  |  | 0.00
1995 |  |  |  | 2013.23 |  |  | 4234 |  |  |  | 515 | [10 empty] | 44.85 |  |  |  | 45.71 | [5 empty] | 44.63 |  |  | 48.33 |  |  |  | 49.07 |  | 44.04 | [8 empty] | 10.25 |  |  |  |  | 0.86
1996 |  |  |  | 3011.76 |  |  | 6202 |  |  |  | 515 | [10 empty] | 66.83 |  |  |  | 66.83 | [5 empty] | 66.58 |  |  | 70.61 |  |  |  | 31.66 |  | 30.96 | [8 empty] | 2.22 |  |  |  |  | 0.00
1997 |  |  |  | 3950.80 |  |  | 8205 |  |  |  | 515 | [10 empty] | 89.68 |  |  |  | 89.68 | [5 empty] | 88.54 |  |  | 94.70 |  |  |  | 10.32 |  | 10.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | Data not available - Long-term shutdown
1999 |  |  |  | "
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | "
2005 |  |  |  | 584.96 |  |  | 1230 |  |  |  | 515 | [10 empty] | 95.88 |  |  |  | 95.88 | [5 empty] | 51.42 |  |  | 55.68 |  |  |  | 4.12 |  | 4.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 3470.49 |  |  | 7260 |  |  |  | 515 | [10 empty] | 77.02 |  |  |  | 77.22 | [5 empty] | 76.93 |  |  | 82.88 |  |  |  | 19.42 |  | 18.85 | [8 empty] | 3.92 |  |  |  |  | 0.21
2007 |  |  |  | 1750.26 |  |  | 3447 |  |  |  | 515 | [10 empty] | 38.91 |  |  |  | 38.94 | [5 empty] | 38.80 |  |  | 39.35 |  |  |  | 50.80 |  | 43.22 | [8 empty] | 17.84 |  |  |  |  | 0.04
2008 |  |  |  | 2792.10 |  |  | 6221 |  |  |  | 515 | [10 empty] | 61.72 |  |  |  | 61.78 | [5 empty] | 61.72 |  |  | 70.82 |  |  |  | 37.71 |  | 37.70 | [8 empty] | 0.52 |  |  |  |  | 0.06
2009 |  |  |  | 4108.77 |  |  | 8436 |  |  |  | 515 | [10 empty] | 91.15 |  |  |  | 91.45 | [5 empty] | 91.08 |  |  | 96.30 |  |  |  | 8.50 |  | 8.50 | [8 empty] | 0.05 |  |  |  |  | 0.30
2010 |  |  |  | 2376.13 |  |  | 4983 |  |  |  | 515 | [10 empty] | 52.73 |  |  |  | 52.90 | [5 empty] | 52.67 |  |  | 56.88 |  |  |  | 22.60 |  | 18.82 | [8 empty] | 28.28 |  |  |  |  | 0.17
2011 |  |  |  | 3669.17 |  |  | 7382 |  |  |  | 515 | [10 empty] | 81.49 |  |  |  | 81.79 | [5 empty] | 81.33 |  |  | 84.27 |  |  |  | 18.21 |  | 18.21 | [8 empty] | 0.00 |  |  |  |  | 0.30
2012 |  |  |  | 2912.37 |  |  | 5799 |  |  |  | 515 | [10 empty] | 64.48 |  |  |  | 65.11 | [5 empty] | 64.38 |  |  | 66.02 |  |  |  | 4.03 |  | 5.44 | [8 empty] | 29.45 |  |  |  |  | 0.64
2013 |  |  |  | 2074.98 |  |  | 4344 |  |  |  | 515 | [10 empty] | 45.99 |  |  |  | 46.20 | [5 empty] | 45.99 |  |  | 49.59 |  |  |  | 33.45 |  | 53.27 | [8 empty] | 0.53 |  |  |  |  | 0.21
2014 |  |  |  | 3871.29 |  |  | 7855 |  |  |  | 515 | [10 empty] | 86.08 |  |  |  | 87.40 | [5 empty] | 85.81 |  |  | 89.67 |  |  |  | 12.55 |  | 12.55 | [8 empty] | 0.05 |  |  |  |  | 1.32
2015 |  |  |  | 2599.85 |  |  | 5263 |  |  |  | 515 | [10 empty] | 57.80 |  |  |  | 57.92 | [5 empty] | 57.63 |  |  | 60.08 |  |  |  | 2.63 |  | 6.31 | [8 empty] | 35.77 |  |  |  |  | 0.12
2016 |  |  |  | 4212.67 |  |  | 8784 |  |  |  | 515 | [10 empty] | 93.41 |  |  |  | 94.28 | [5 empty] | 93.12 |  |  | 100.00 |  |  |  | 5.25 |  | 5.22 | [8 empty] | 0.50 |  |  |  |  | 0.87
2017 |  |  |  | 2608.49 |  |  | 5323 |  |  |  | 515 | [10 empty] | 57.91 |  |  |  | 58.07 | [5 empty] | 57.82 |  |  | 60.76 |  |  |  | 8.48 |  | 5.38 | [8 empty] | 36.56 |  |  |  |  | 0.16
2018 |  |  |  | 4206.18 |  |  | 8503 |  |  |  | 515 | [10 empty] | 93.41 |  |  |  | 94.09 | [5 empty] | 93.23 |  |  | 97.07 |  |  |  | 4.63 |  | 4.57 | [8 empty] | 1.34 |  |  |  |  | 0.68
2019 |  |  |  | 4299.59 |  |  | 8583 |  |  |  | 515 | [10 empty] | 95.53 |  |  |  | 95.91 | [5 empty] | 95.30 |  |  | 97.98 |  |  |  | 3.30 |  | 3.27 | [8 empty] | 0.82 |  |  |  |  | 0.38
2020 |  |  |  | 2244.06 |  |  | 4660 |  |  |  | 515 | [10 empty] | 49.73 |  |  |  | 50.11 | [5 empty] | 49.61 |  |  | 53.05 |  |  |  | 9.73 |  | 5.40 | [8 empty] | 44.49 |  |  |  |  | 0.38
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1971 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 335 | [14 empty] | 1654
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 3789 | [14 empty] | 880
E. |  | Testing of plant systems or components | [35 empty] | 5 |  |  |  | 6
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 56
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
P. |  | Fire | [39 empty] | 34
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 72
Z. |  | Other | [39 empty] | 11
Subtotal | [22 empty] | 3789 |  |  |  | 335 | [10 empty] | 885 |  |  |  | 1761 | [11 empty] | 75
Total | [22 empty] | 4124 | [14 empty] | 2721
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1971 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 863
12. |  |  | Reactor I&C Systems | [34 empty] | 70
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 61
14. |  |  | Safety Systems | [34 empty] | 59
15. |  |  | Reactor Cooling Systems | [34 empty] | 140
16. |  |  | Steam generation systems | [34 empty] | 60
21. |  |  | Fuel Handling and Storage Facilities | [19 empty] | 167 | [14 empty] | 76
31. |  |  | Turbine and auxiliaries | [19 empty] | 168 | [14 empty] | 119
32. |  |  | Feedwater and Main Steam System | [34 empty] | 50
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 50
42. |  |  | Electrical Power Supply Systems | [34 empty] | 116
Total | [22 empty] | 335 | [14 empty] | 1683

## PICKERING-4
2020 Operating Experience
CA-7 | [8 empty] | PICKERING-4 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500A | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-05-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-05-21
Gross electrical power | [12 empty] | : |  |  | 542 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-06-17
Reference unit power (net) | [12 empty] | : |  |  | 515 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 9080 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 26.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 6 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2755.54 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.2 %
Energy Availability Factor (EAF) | [18 empty] | : | 60.92 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.29 %
Unit Capability Factor (UCF) | [18 empty] | : | 61.42 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 34.29 %
Load Factor (LF) | [18 empty] | : | 60.91 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.5 %
Operating Factor (OF) | [18 empty] | : | 63.24 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3229 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 377.15 | 352.81 |  |  |  | 358.01 |  | 363.69 | [8 empty] | 373.62 |  |  | 362.01 | [6 empty] | 365.70 |  | 111.20 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 91.36 |  |  | 2755.54
EAF [%] |  |  |  |  | 98.43 | 98.43 |  |  |  | 93.44 |  | 98.08 | [8 empty] | 97.51 |  |  | 97.63 | [6 empty] | 95.44 |  | 29.02 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 23.97 |  |  | 60.92
UCF [%] |  |  |  |  | 98.90 | 98.95 |  |  |  | 93.95 |  | 98.45 | [8 empty] | 98.04 |  |  | 98.65 | [6 empty] | 97.26 |  | 29.77 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 23.97 |  |  | 61.42
LF [%] |  |  |  |  | 98.43 | 98.43 |  |  |  | 93.44 |  | 98.08 | [8 empty] | 97.51 |  |  | 97.63 | [6 empty] | 95.44 |  | 29.02 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 23.84 |  |  | 60.91
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 32.12 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 27.42 |  |  | 63.24
FLR [%] |  |  |  |  | 1.10 | 1.05 |  |  |  | 0.61 |  | 1.55 | [8 empty] | 1.87 |  |  | 1.04 | [6 empty] | 1.13 |  | 2.08 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.31 |  |  | 1.20
UCL [%] |  |  |  |  | 1.10 | 1.05 |  |  |  | 0.58 |  | 1.55 | [8 empty] | 1.86 |  |  | 1.03 | [6 empty] | 1.11 |  | 0.63 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 41.85 |  |  | 4.29
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 5.48 |  | 0.00 | [8 empty] | 0.09 |  |  | 0.31 | [6 empty] | 1.63 |  | 69.60 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 34.18 |  |  | 34.29
XUF [%] |  |  |  |  | 0.47 | 0.52 |  |  |  | 0.51 |  | 0.37 | [8 empty] | 0.53 |  |  | 1.03 | [6 empty] | 1.81 |  | 0.75 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.50
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 127546.68 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 17.79 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 67.52 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 16.01 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 67.91 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.08 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.38 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.39 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 70.47 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 2226.60 |  |  | 4402 |  |  |  | 514 | [10 empty] | 90.59 |  |  |  | 90.59 | [5 empty] | 90.40 |  |  | 91.75 |  |  |  | 6.12 |  | 5.91 | [8 empty] | 3.50 |  |  |  |  | 0.00
1974 |  |  |  | 4221.00 |  |  | 8356 |  |  |  | 514 | [10 empty] | 94.00 |  |  |  | 94.00 | [5 empty] | 94.00 |  |  | 95.65 |  |  |  | 5.22 |  | 5.18 | [8 empty] | 0.82 |  |  |  |  | 0.00
1975 |  |  |  | 1094.20 |  |  | 2201 |  |  |  | 513 | [10 empty] | 24.24 |  |  |  | 24.24 | [5 empty] | 24.42 |  |  | 25.19 |  |  |  | 73.53 |  | 67.34 | [8 empty] | 8.42 |  |  |  |  | 0.00
1976 |  |  |  | 3089.00 |  |  | 6063 |  |  |  | 514 | [10 empty] | 68.23 |  |  |  | 68.23 | [5 empty] | 68.60 |  |  | 69.21 |  |  |  | 31.44 |  | 31.29 | [8 empty] | 0.49 |  |  |  |  | 0.00
1977 |  |  |  | 4107.20 |  |  | 7975 |  |  |  | 514 | [10 empty] | 90.30 |  |  |  | 90.30 | [5 empty] | 91.47 |  |  | 91.29 |  |  |  | 4.38 |  | 4.13 | [8 empty] | 5.57 |  |  |  |  | 0.00
1978 |  |  |  | 4033.90 |  |  | 7876 |  |  |  | 515 | [10 empty] | 89.70 |  |  |  | 89.70 | [5 empty] | 89.66 |  |  | 90.16 |  |  |  | 3.07 |  | 2.84 | [8 empty] | 7.46 |  |  |  |  | 0.00
1979 |  |  |  | 4102.20 |  |  | 8059 |  |  |  | 515 | [10 empty] | 91.00 |  |  |  | 91.00 | [5 empty] | 89.94 |  |  | 91.00 |  |  |  | 4.67 |  | 4.45 | [8 empty] | 4.55 |  |  |  |  | 0.00
1980 |  |  |  | 3700.50 |  |  | 7321 |  |  |  | 515 | [10 empty] | 81.76 |  |  |  | 81.76 | [5 empty] | 81.80 |  |  | 83.34 |  |  |  | 8.38 |  | 7.48 | [8 empty] | 10.77 |  |  |  |  | 0.00
1981 |  |  |  | 4142.00 |  |  | 8078 |  |  |  | 515 | [10 empty] | 91.65 |  |  |  | 91.65 | [5 empty] | 91.81 |  |  | 92.21 |  |  |  | 3.83 |  | 3.65 | [8 empty] | 4.70 |  |  |  |  | 0.00
1982 |  |  |  | 4137.90 |  |  | 8087 |  |  |  | 515 | [10 empty] | 91.76 |  |  |  | 91.76 | [5 empty] | 91.72 |  |  | 92.32 |  |  |  | 2.61 |  | 2.46 | [8 empty] | 5.78 |  |  |  |  | 0.00
1983 |  |  |  | 4170.20 |  |  | 8183 |  |  |  | 515 | [10 empty] | 92.32 |  |  |  | 92.32 | [5 empty] | 92.44 |  |  | 93.41 |  |  |  | 5.55 |  | 5.43 | [8 empty] | 2.25 |  |  |  |  | 0.00
1984 |  |  |  | 3733.30 |  |  | 7425 |  |  |  | 515 | [10 empty] | 82.75 |  |  |  | 82.75 | [5 empty] | 82.53 |  |  | 84.53 |  |  |  | 4.49 |  | 3.89 | [8 empty] | 13.36 |  |  |  |  | 0.00
1985 |  |  |  | 3438.86 |  |  | 6824 |  |  |  | 515 | [10 empty] | 77.47 |  |  |  | 83.50 | [5 empty] | 76.23 |  |  | 77.90 |  |  |  | 16.50 |  | 16.50 | [8 empty] | 0.00 |  |  |  |  | 6.03
1986 |  |  |  | 3687.37 |  |  | 7410 |  |  |  | 515 | [10 empty] | 83.16 |  |  |  | 83.16 | [5 empty] | 81.73 |  |  | 84.59 |  |  |  | 7.06 |  | 6.32 | [8 empty] | 10.52 |  |  |  |  | 0.00
1987 |  |  |  | 3770.41 |  |  | 7495 |  |  |  | 515 | [10 empty] | 83.96 |  |  |  | 84.33 | [5 empty] | 83.58 |  |  | 85.56 |  |  |  | 2.74 |  | 2.37 | [8 empty] | 13.29 |  |  |  |  | 0.37
1988 |  |  |  | 3166.17 |  |  | 6525 |  |  |  | 515 | [10 empty] | 70.11 |  |  |  | 70.11 | [5 empty] | 69.99 |  |  | 74.28 |  |  |  | 17.91 |  | 15.29 | [8 empty] | 14.60 |  |  |  |  | 0.00
1989 |  |  |  | 2255.49 |  |  | 5468 |  |  |  | 515 | [10 empty] | 50.00 |  |  |  | 50.00 | [5 empty] | 50.00 |  |  | 62.42 |  |  |  | 34.52 |  | 26.35 | [8 empty] | 23.65 |  |  |  |  | 0.00
1990 |  |  |  | 1070.83 |  |  | 2851 |  |  |  | 515 | [10 empty] | 23.74 |  |  |  | 23.74 | [5 empty] | 23.74 |  |  | 32.55 |  |  |  | 43.49 |  | 18.27 | [8 empty] | 58.00 |  |  |  |  | 0.00
1991 |  |  |  | 2130.76 |  |  | 5185 |  |  |  | 515 | [10 empty] | 47.34 |  |  |  | 47.34 | [5 empty] | 47.23 |  |  | 59.19 |  |  |  | 21.40 |  | 12.89 | [8 empty] | 39.77 |  |  |  |  | 0.00
1992 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1993 |  |  |  | 3309.63 |  |  | 6711 |  |  |  | 515 | [10 empty] | 73.76 |  |  |  | 74.21 | [5 empty] | 73.36 |  |  | 76.61 |  |  |  | 7.77 |  | 6.25 | [8 empty] | 19.55 |  |  |  |  | 0.45
1994 |  |  |  | 4009.64 |  |  | 7915 |  |  |  | 515 | [10 empty] | 89.51 |  |  |  | 89.71 | [5 empty] | 88.88 |  |  | 90.35 |  |  |  | 10.20 |  | 10.19 | [8 empty] | 0.09 |  |  |  |  | 0.21
1995 |  |  |  | 2806.96 |  |  | 5684 |  |  |  | 515 | [10 empty] | 63.33 |  |  |  | 63.84 | [5 empty] | 62.22 |  |  | 64.89 |  |  |  | 36.16 |  | 36.16 | [8 empty] | 0.00 |  |  |  |  | 0.50
1996 |  |  |  | 1134.91 |  |  | 2230 |  |  |  | 515 | [10 empty] | 25.13 |  |  |  | 25.13 | [5 empty] | 25.09 |  |  | 25.39 |  |  |  | 72.71 |  | 66.95 | [8 empty] | 7.92 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1998 |  |  |  | Data not provided
1999 |  |  |  | Data not available - Long-term shutdown
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | 844.81 |  |  | 1880 |  |  |  | 515 | [10 empty] | 72.27 |  |  |  | 72.27 | [5 empty] | 72.27 |  |  | 82.70 |  |  |  | 27.73 |  | 27.73 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 3266.76 |  |  | 6739 |  |  |  | 515 | [10 empty] | 72.10 |  |  |  | 75.58 | [5 empty] | 72.21 |  |  | 76.72 |  |  |  | 19.76 |  | 18.61 | [8 empty] | 5.81 |  |  |  |  | 3.48
2005 |  |  |  | 2996.45 |  |  | 5900 |  |  |  | 515 | [10 empty] | 66.40 |  |  |  | 66.52 | [5 empty] | 66.42 |  |  | 67.35 |  |  |  | 33.48 |  | 33.48 | [8 empty] | 0.00 |  |  |  |  | 0.13
2006 |  |  |  | 2976.54 |  |  | 6149 |  |  |  | 515 | [10 empty] | 65.96 |  |  |  | 66.30 | [5 empty] | 65.98 |  |  | 70.19 |  |  |  | 15.05 |  | 17.26 | [8 empty] | 16.44 |  |  |  |  | 0.34
2007 |  |  |  | 1959.14 |  |  | 4086 |  |  |  | 515 | [10 empty] | 43.44 |  |  |  | 43.44 | [5 empty] | 43.43 |  |  | 46.64 |  |  |  | 49.23 |  | 55.59 | [8 empty] | 0.96 |  |  |  |  | 0.00
2008 |  |  |  | 3656.45 |  |  | 7765 |  |  |  | 515 | [10 empty] | 80.83 |  |  |  | 80.91 | [5 empty] | 80.83 |  |  | 88.40 |  |  |  | 19.04 |  | 19.03 | [8 empty] | 0.07 |  |  |  |  | 0.08
2009 |  |  |  | 1620.17 |  |  | 3845 |  |  |  | 515 | [10 empty] | 35.91 |  |  |  | 36.15 | [5 empty] | 35.91 |  |  | 43.89 |  |  |  | 48.47 |  | 42.90 | [8 empty] | 20.95 |  |  |  |  | 0.24
2010 |  |  |  | 3203.51 |  |  | 6583 |  |  |  | 515 | [10 empty] | 71.13 |  |  |  | 71.37 | [5 empty] | 71.01 |  |  | 75.15 |  |  |  | 17.89 |  | 15.55 | [8 empty] | 13.08 |  |  |  |  | 0.24
2011 |  |  |  | 2401.12 |  |  | 4919 |  |  |  | 515 | [10 empty] | 53.28 |  |  |  | 53.66 | [5 empty] | 53.22 |  |  | 56.15 |  |  |  | 29.34 |  | 24.15 | [8 empty] | 22.18 |  |  |  |  | 0.38
2012 |  |  |  | 3310.83 |  |  | 6592 |  |  |  | 515 | [10 empty] | 73.42 |  |  |  | 73.73 | [5 empty] | 73.19 |  |  | 75.05 |  |  |  | 20.62 |  | 21.17 | [8 empty] | 5.10 |  |  |  |  | 0.31
2013 |  |  |  | 3884.54 |  |  | 7798 |  |  |  | 515 | [10 empty] | 86.29 |  |  |  | 86.60 | [5 empty] | 86.10 |  |  | 89.02 |  |  |  | 7.00 |  | 7.76 | [8 empty] | 5.64 |  |  |  |  | 0.31
2014 |  |  |  | 2853.53 |  |  | 5772 |  |  |  | 515 | [10 empty] | 63.30 |  |  |  | 63.49 | [5 empty] | 63.25 |  |  | 65.89 |  |  |  | 5.37 |  | 13.00 | [8 empty] | 23.51 |  |  |  |  | 0.19
2015 |  |  |  | 4266.31 |  |  | 8604 |  |  |  | 515 | [10 empty] | 94.66 |  |  |  | 95.12 | [5 empty] | 94.57 |  |  | 98.22 |  |  |  | 4.87 |  | 4.87 | [8 empty] | 0.01 |  |  |  |  | 0.47
2016 |  |  |  | 2455.22 |  |  | 5169 |  |  |  | 515 | [10 empty] | 54.32 |  |  |  | 54.91 | [5 empty] | 54.27 |  |  | 58.85 |  |  |  | 10.39 |  | 15.07 | [8 empty] | 30.01 |  |  |  |  | 0.60
2017 |  |  |  | 3961.10 |  |  | 7978 |  |  |  | 515 | [10 empty] | 87.94 |  |  |  | 88.20 | [5 empty] | 87.80 |  |  | 91.07 |  |  |  | 3.91 |  | 3.59 | [8 empty] | 8.20 |  |  |  |  | 0.27
2018 |  |  |  | 2792.32 |  |  | 5901 |  |  |  | 515 | [10 empty] | 62.06 |  |  |  | 62.92 | [5 empty] | 61.89 |  |  | 67.36 |  |  |  | 8.24 |  | 5.65 | [8 empty] | 31.43 |  |  |  |  | 0.87
2019 |  |  |  | 4421.44 |  |  | 8760 |  |  |  | 515 | [10 empty] | 98.17 |  |  |  | 98.52 | [5 empty] | 98.01 |  |  | 100.00 |  |  |  | 1.21 |  | 1.20 | [8 empty] | 0.27 |  |  |  |  | 0.36
2020 |  |  |  | 2755.54 |  |  | 5555 |  |  |  | 515 | [10 empty] | 60.92 |  |  |  | 61.42 | [5 empty] | 60.91 |  |  | 63.24 |  |  |  | 1.20 |  | 4.29 | [8 empty] | 34.29 |  |  |  |  | 0.50
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1973 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 311 | [14 empty] | 1153
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 63
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2919 | [14 empty] | 1291
E. |  | Testing of plant systems or components | [35 empty] | 54
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 3
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 12
Z. |  | Other | [39 empty] | 7
Subtotal | [22 empty] | 2919 |  |  |  | 311 | [10 empty] | 1408 |  |  |  | 1163 | [11 empty] | 17
Total | [22 empty] | 3230 | [14 empty] | 2588
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1973 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 57
12. |  |  | Reactor I&C Systems | [34 empty] | 135
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 151
14. |  |  | Safety Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 429
16. |  |  | Steam generation systems | [34 empty] | 39
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [19 empty] | 311 | [14 empty] | 111
32. |  |  | Feedwater and Main Steam System | [34 empty] | 28
34. |  |  | Miscellaneous Systems | [34 empty] | 16
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 45
42. |  |  | Electrical Power Supply Systems | [34 empty] | 106
Total | [22 empty] | 311 | [14 empty] | 1148

## PICKERING-5
2020 Operating Experience
CA-13 | [8 empty] | PICKERING-5 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-11-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-12-19
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-05-10
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4215.36 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 5.72 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.12 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.7 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.85 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.45 %
Load Factor (LF) | [18 empty] | : | 93 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.73 %
Operating Factor (OF) | [18 empty] | : | 96.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 264 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 326.61 | 357.91 |  |  |  | 382.47 |  | 370.70 | [8 empty] | 384.25 |  |  | 368.55 | [6 empty] | 194.52 |  | 372.04 |  |  |  | 361.03 |  |  | 355.56 |  |  | 360.30 | [9 empty] | 381.42 |  |  | 4215.36
EAF [%] |  |  |  |  | 85.11 | 99.93 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.55 | [6 empty] | 50.69 |  | 96.99 |  |  |  | 97.35 |  |  | 92.85 |  |  | 96.38 | [9 empty] | 99.71 |  |  | 93.12
UCF [%] |  |  |  |  | 85.11 | 99.93 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 51.91 |  | 99.96 |  |  |  | 99.40 |  |  | 94.86 |  |  | 96.38 | [9 empty] | 99.71 |  |  | 93.85
LF [%] |  |  |  |  | 85.08 | 99.66 |  |  |  | 99.63 |  | 99.78 | [8 empty] | 100.09 |  |  | 99.20 | [6 empty] | 50.67 |  | 96.91 |  |  |  | 97.18 |  |  | 92.62 |  |  | 96.98 | [9 empty] | 99.35 |  |  | 93.00
OF [%] |  |  |  |  | 92.74 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 71.77 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 96.99
FLR [%] |  |  |  |  | 10.32 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 48.09 |  | 0.04 |  |  |  | 0.59 |  |  | 5.14 |  |  | 3.62 | [9 empty] | 0.10 |  |  | 5.72
UCL [%] |  |  |  |  | 9.79 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 48.08 |  | 0.04 |  |  |  | 0.59 |  |  | 5.14 |  |  | 3.62 | [9 empty] | 0.10 |  |  | 5.70
PUF [%] |  |  |  |  | 5.10 | 0.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.19 |  |  | 0.45
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.45 | [6 empty] | 1.21 |  | 2.97 |  |  |  | 2.05 |  |  | 2.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.73
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 127240.42 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 12.13 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.67 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.85 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.37 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.78 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.43 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.7 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.29 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 3202.40 |  |  | 6968 |  |  |  | 516 | [10 empty] | 90.29 |  |  |  | 90.29 | [5 empty] | 89.64 |  |  | 92.62 |  |  |  | 9.69 |  | 9.69 | [8 empty] | 0.02 |  |  |  |  | 0.00
1984 |  |  |  | 3517.52 |  |  | 7035 |  |  |  | 516 | [10 empty] | 77.75 |  |  |  | 77.75 | [5 empty] | 77.61 |  |  | 80.09 |  |  |  | 11.82 |  | 10.42 | [8 empty] | 11.83 |  |  |  |  | 0.00
1985 |  |  |  | 3366.50 |  |  | 6989 |  |  |  | 516 | [10 empty] | 77.74 |  |  |  | 83.10 | [5 empty] | 74.48 |  |  | 79.78 |  |  |  | 8.79 |  | 8.01 | [8 empty] | 8.89 |  |  |  |  | 5.36
1986 |  |  |  | 4068.64 |  |  | 8057 |  |  |  | 516 | [10 empty] | 90.70 |  |  |  | 91.16 | [5 empty] | 90.01 |  |  | 91.97 |  |  |  | 2.33 |  | 2.18 | [8 empty] | 6.66 |  |  |  |  | 0.46
1987 |  |  |  | 3600.10 |  |  | 7148 |  |  |  | 516 | [10 empty] | 79.56 |  |  |  | 80.33 | [5 empty] | 79.65 |  |  | 81.60 |  |  |  | 7.82 |  | 6.82 | [8 empty] | 12.85 |  |  |  |  | 0.77
1988 |  |  |  | 4397.16 |  |  | 8683 |  |  |  | 516 | [10 empty] | 97.52 |  |  |  | 97.55 | [5 empty] | 97.01 |  |  | 98.85 |  |  |  | 2.09 |  | 2.09 | [8 empty] | 0.37 |  |  |  |  | 0.03
1989 |  |  |  | 3400.76 |  |  | 6862 |  |  |  | 516 | [10 empty] | 75.42 |  |  |  | 75.67 | [5 empty] | 75.24 |  |  | 78.33 |  |  |  | 9.36 |  | 7.81 | [8 empty] | 16.52 |  |  |  |  | 0.25
1990 |  |  |  | 3885.00 |  |  | 7821 |  |  |  | 516 | [10 empty] | 86.36 |  |  |  | 86.44 | [5 empty] | 85.95 |  |  | 89.28 |  |  |  | 4.06 |  | 3.65 | [8 empty] | 9.90 |  |  |  |  | 0.08
1991 |  |  |  | 2887.06 |  |  | 5724 |  |  |  | 516 | [10 empty] | 64.36 |  |  |  | 64.56 | [5 empty] | 63.87 |  |  | 65.34 |  |  |  | 28.95 |  | 26.30 | [8 empty] | 9.14 |  |  |  |  | 0.20
1992 |  |  |  | 1345.25 |  |  | 2621 |  |  |  | 516 | [10 empty] | 29.76 |  |  |  | 29.76 | [5 empty] | 29.68 |  |  | 29.84 |  |  |  | 70.24 |  | 70.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 3841.81 |  |  | 8307 |  |  |  | 516 | [10 empty] | 85.40 |  |  |  | 85.57 | [5 empty] | 84.99 |  |  | 94.83 |  |  |  | 14.25 |  | 14.22 | [8 empty] | 0.22 |  |  |  |  | 0.16
1994 |  |  |  | 3074.41 |  |  | 6196 |  |  |  | 516 | [10 empty] | 68.53 |  |  |  | 68.53 | [5 empty] | 68.02 |  |  | 70.73 |  |  |  | 9.15 |  | 6.90 | [8 empty] | 24.57 |  |  |  |  | 0.00
1995 |  |  |  | 3372.87 |  |  | 7008 |  |  |  | 516 | [10 empty] | 74.76 |  |  |  | 75.01 | [5 empty] | 74.62 |  |  | 80.00 |  |  |  | 13.00 |  | 11.21 | [8 empty] | 13.77 |  |  |  |  | 0.25
1996 |  |  |  | 3042.63 |  |  | 6429 |  |  |  | 516 | [10 empty] | 67.13 |  |  |  | 67.13 | [5 empty] | 67.13 |  |  | 73.19 |  |  |  | 32.87 |  | 32.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 3924.89 |  |  | 7908 |  |  |  | 516 | [10 empty] | 86.83 |  |  |  | 86.83 | [5 empty] | 86.83 |  |  | 90.27 |  |  |  | 13.17 |  | 13.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 3490.58 |  |  | 7296 |  |  |  | 516 | [10 empty] | 77.22 |  |  |  | 77.22 | [5 empty] | 77.22 |  |  | 83.29 |  |  |  | 8.70 |  | 7.36 | [8 empty] | 15.42 |  |  |  |  | 0.00
1999 |  |  |  | 2511.57 |  |  | 5302 |  |  |  | 516 | [10 empty] | 55.56 |  |  |  | 55.63 | [5 empty] | 55.56 |  |  | 60.53 |  |  |  | 20.16 |  | 14.04 | [8 empty] | 30.33 |  |  |  |  | 0.06
2000 |  |  |  | 2631.49 |  |  | 5457 |  |  |  | 516 | [10 empty] | 58.03 |  |  |  | 58.12 | [5 empty] | 58.06 |  |  | 62.12 |  |  |  | 32.58 |  | 28.09 | [8 empty] | 13.79 |  |  |  |  | 0.09
2001 |  |  |  | 2980.21 |  |  | 5986 |  |  |  | 516 | [10 empty] | 65.87 |  |  |  | 66.57 | [5 empty] | 65.93 |  |  | 68.33 |  |  |  | 6.95 |  | 4.97 | [8 empty] | 28.46 |  |  |  |  | 0.71
2002 |  |  |  | 2655.74 |  |  | 5565 |  |  |  | 516 | [10 empty] | 58.75 |  |  |  | 59.17 | [5 empty] | 58.75 |  |  | 63.53 |  |  |  | 11.96 |  | 8.03 | [8 empty] | 32.80 |  |  |  |  | 0.41
2003 |  |  |  | 3294.96 |  |  | 6566 |  |  |  | 516 | [10 empty] | 69.14 |  |  |  | 71.14 | [5 empty] | 72.89 |  |  | 74.95 |  |  |  | 28.29 |  | 28.07 | [8 empty] | 0.79 |  |  |  |  | 2.00
2004 |  |  |  | 4159.81 |  |  | 8264 |  |  |  | 516 | [10 empty] | 92.16 |  |  |  | 92.60 | [5 empty] | 91.78 |  |  | 94.08 |  |  |  | 4.45 |  | 4.31 | [8 empty] | 3.09 |  |  |  |  | 0.44
2005 |  |  |  | 2352.79 |  |  | 4818 |  |  |  | 516 | [10 empty] | 52.63 |  |  |  | 53.56 | [5 empty] | 52.05 |  |  | 55.00 |  |  |  | 9.80 |  | 8.30 | [8 empty] | 38.14 |  |  |  |  | 0.93
2006 |  |  |  | 4010.87 |  |  | 8113 |  |  |  | 516 | [10 empty] | 88.95 |  |  |  | 89.66 | [5 empty] | 88.73 |  |  | 92.61 |  |  |  | 10.34 |  | 10.34 | [8 empty] | 0.00 |  |  |  |  | 0.71
2007 |  |  |  | 2567.59 |  |  | 5637 |  |  |  | 516 | [10 empty] | 56.96 |  |  |  | 57.51 | [5 empty] | 56.80 |  |  | 64.35 |  |  |  | 21.85 |  | 22.84 | [8 empty] | 19.66 |  |  |  |  | 0.55
2008 |  |  |  | 4026.82 |  |  | 8357 |  |  |  | 516 | [10 empty] | 88.86 |  |  |  | 89.80 | [5 empty] | 88.84 |  |  | 95.14 |  |  |  | 7.64 |  | 8.89 | [8 empty] | 1.31 |  |  |  |  | 0.94
2009 |  |  |  | 3140.88 |  |  | 6631 |  |  |  | 516 | [10 empty] | 69.60 |  |  |  | 70.12 | [5 empty] | 69.49 |  |  | 75.70 |  |  |  | 7.81 |  | 13.53 | [8 empty] | 16.35 |  |  |  |  | 0.51
2010 |  |  |  | 3769.85 |  |  | 7645 |  |  |  | 516 | [10 empty] | 83.73 |  |  |  | 84.08 | [5 empty] | 83.40 |  |  | 87.27 |  |  |  | 4.21 |  | 3.69 | [8 empty] | 12.23 |  |  |  |  | 0.36
2011 |  |  |  | 1973.46 |  |  | 4258 |  |  |  | 516 | [10 empty] | 43.87 |  |  |  | 44.83 | [5 empty] | 43.66 |  |  | 48.61 |  |  |  | 10.88 |  | 22.97 | [8 empty] | 32.20 |  |  |  |  | 0.96
2012 |  |  |  | 4347.31 |  |  | 8725 |  |  |  | 516 | [10 empty] | 96.34 |  |  |  | 98.24 | [5 empty] | 95.91 |  |  | 99.33 |  |  |  | 1.69 |  | 1.69 | [8 empty] | 0.07 |  |  |  |  | 1.89
2013 |  |  |  | 2603.23 |  |  | 5371 |  |  |  | 516 | [10 empty] | 58.06 |  |  |  | 58.57 | [5 empty] | 57.59 |  |  | 61.31 |  |  |  | 1.98 |  | 15.82 | [8 empty] | 25.61 |  |  |  |  | 0.51
2014 |  |  |  | 4255.09 |  |  | 8760 |  |  |  | 516 | [10 empty] | 94.57 |  |  |  | 95.35 | [5 empty] | 94.14 |  |  | 100.00 |  |  |  | 4.50 |  | 4.49 | [8 empty] | 0.15 |  |  |  |  | 0.78
2015 |  |  |  | 2932.28 |  |  | 5865 |  |  |  | 516 | [10 empty] | 65.29 |  |  |  | 65.91 | [5 empty] | 64.87 |  |  | 66.95 |  |  |  | 0.62 |  | 4.44 | [8 empty] | 29.66 |  |  |  |  | 0.62
2016 |  |  |  | 4352.12 |  |  | 8784 |  |  |  | 516 | [10 empty] | 96.56 |  |  |  | 98.79 | [5 empty] | 96.02 |  |  | 100.00 |  |  |  | 1.11 |  | 1.10 | [8 empty] | 0.10 |  |  |  |  | 2.23
2017 |  |  |  | 2883.68 |  |  | 5841 |  |  |  | 516 | [10 empty] | 64.14 |  |  |  | 64.82 | [5 empty] | 63.80 |  |  | 66.68 |  |  |  | 1.92 |  | 1.27 | [8 empty] | 33.91 |  |  |  |  | 0.69
2018 |  |  |  | 4255.38 |  |  | 8615 |  |  |  | 516 | [10 empty] | 94.81 |  |  |  | 97.08 | [5 empty] | 94.14 |  |  | 98.34 |  |  |  | 2.88 |  | 2.87 | [8 empty] | 0.04 |  |  |  |  | 2.28
2019 |  |  |  | 2978.82 |  |  | 5934 |  |  |  | 516 | [10 empty] | 66.30 |  |  |  | 66.58 | [5 empty] | 65.90 |  |  | 67.74 |  |  |  | 1.67 |  | 1.13 | [8 empty] | 32.28 |  |  |  |  | 0.28
2020 |  |  |  | 4215.36 |  |  | 8520 |  |  |  | 516 | [10 empty] | 93.12 |  |  |  | 93.85 | [5 empty] | 93.00 |  |  | 96.99 |  |  |  | 5.72 |  | 5.70 | [8 empty] | 0.45 |  |  |  |  | 0.73
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 264 | [14 empty] | 778
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 1031
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 2
L. |  | Human factor related | [39 empty] | 50
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 6
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 15
Z. |  | Other | [35 empty] | 25 |  |  |  | 20
Subtotal | [26 empty] | 264 | [10 empty] | 1056 |  |  |  | 850 | [11 empty] | 21
Total | [22 empty] | 264 | [14 empty] | 1927
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 55
12. |  |  | Reactor I&C Systems | [34 empty] | 64
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 52
14. |  |  | Safety Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 112
16. |  |  | Steam generation systems | [34 empty] | 259
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [19 empty] | 264 | [14 empty] | 44
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 82
42. |  |  | Electrical Power Supply Systems | [34 empty] | 82
Total | [22 empty] | 264 | [14 empty] | 795

## PICKERING-6
2020 Operating Experience
CA-14 | [8 empty] | PICKERING-6 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-10-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-11-08
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-02-01
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3027.01 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.07 %
Energy Availability Factor (EAF) | [18 empty] | : | 66.72 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.05 %
Unit Capability Factor (UCF) | [18 empty] | : | 67.1 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 32.85 %
Load Factor (LF) | [18 empty] | : | 66.78 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.39 %
Operating Factor (OF) | [18 empty] | : | 67.37 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2866 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 386.36 | 361.46 |  |  |  | 378.65 |  | 372.44 | [8 empty] | 383.89 |  |  | 368.29 | [6 empty] | 375.06 |  | 372.83 |  |  |  | 28.03 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3027.01
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 98.31 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.44 | [6 empty] | 98.23 |  | 97.29 |  |  |  | 7.54 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 66.72
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 98.31 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 99.47 |  | 100.00 |  |  |  | 7.63 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 67.10
LF [%] |  |  |  |  | 100.64 | 100.65 |  |  |  | 98.63 |  | 100.25 | [8 empty] | 100.00 |  |  | 99.13 | [6 empty] | 97.70 |  | 97.11 |  |  |  | 7.54 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 66.78
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 8.61 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 67.37
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.53 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.07
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.53 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.68 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 92.37 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 32.85
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.55 | [6 empty] | 1.24 |  | 2.71 |  |  |  | 0.09 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.39
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 131013.02 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 8.99 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.2 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.35 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.91 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.15 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.71 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.94 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 3816.08 |  |  | 7636 |  |  |  | 516 | [10 empty] | 86.09 |  |  |  | 86.09 | [5 empty] | 85.88 |  |  | 87.66 |  |  |  | 13.78 |  | 13.76 | [8 empty] | 0.16 |  |  |  |  | 0.00
1985 |  |  |  | 3289.09 |  |  | 6540 |  |  |  | 516 | [10 empty] | 73.11 |  |  |  | 79.48 | [5 empty] | 72.76 |  |  | 74.66 |  |  |  | 6.72 |  | 5.73 | [8 empty] | 14.80 |  |  |  |  | 6.37
1986 |  |  |  | 3395.22 |  |  | 6763 |  |  |  | 516 | [10 empty] | 75.84 |  |  |  | 76.11 | [5 empty] | 75.11 |  |  | 77.20 |  |  |  | 18.81 |  | 17.63 | [8 empty] | 6.25 |  |  |  |  | 0.28
1987 |  |  |  | 3949.93 |  |  | 7791 |  |  |  | 516 | [10 empty] | 86.60 |  |  |  | 88.53 | [5 empty] | 87.38 |  |  | 88.94 |  |  |  | 3.42 |  | 3.13 | [8 empty] | 8.33 |  |  |  |  | 1.94
1988 |  |  |  | 4496.76 |  |  | 8775 |  |  |  | 516 | [10 empty] | 98.42 |  |  |  | 98.49 | [5 empty] | 99.21 |  |  | 99.90 |  |  |  | 1.51 |  | 1.51 | [8 empty] | 0.00 |  |  |  |  | 0.07
1989 |  |  |  | 3950.21 |  |  | 7794 |  |  |  | 516 | [10 empty] | 87.57 |  |  |  | 87.89 | [5 empty] | 87.39 |  |  | 88.97 |  |  |  | 5.86 |  | 5.47 | [8 empty] | 6.64 |  |  |  |  | 0.31
1990 |  |  |  | 3473.45 |  |  | 7017 |  |  |  | 516 | [10 empty] | 76.92 |  |  |  | 77.74 | [5 empty] | 76.84 |  |  | 80.10 |  |  |  | 7.76 |  | 6.54 | [8 empty] | 15.72 |  |  |  |  | 0.82
1991 |  |  |  | 4469.68 |  |  | 8721 |  |  |  | 516 | [10 empty] | 98.97 |  |  |  | 99.21 | [5 empty] | 98.88 |  |  | 99.55 |  |  |  | 0.79 |  | 0.79 | [8 empty] | 0.00 |  |  |  |  | 0.24
1992 |  |  |  | 4050.47 |  |  | 7936 |  |  |  | 516 | [10 empty] | 89.29 |  |  |  | 89.32 | [5 empty] | 89.36 |  |  | 90.35 |  |  |  | 10.54 |  | 10.53 | [8 empty] | 0.15 |  |  |  |  | 0.03
1993 |  |  |  | 2689.19 |  |  | 5506 |  |  |  | 516 | [10 empty] | 59.88 |  |  |  | 60.38 | [5 empty] | 59.49 |  |  | 62.85 |  |  |  | 11.28 |  | 7.68 | [8 empty] | 31.94 |  |  |  |  | 0.50
1994 |  |  |  | 4043.00 |  |  | 8036 |  |  |  | 516 | [10 empty] | 90.14 |  |  |  | 90.15 | [5 empty] | 89.44 |  |  | 91.74 |  |  |  | 9.71 |  | 9.70 | [8 empty] | 0.15 |  |  |  |  | 0.01
1995 |  |  |  | 3493.34 |  |  | 6962 |  |  |  | 516 | [10 empty] | 77.19 |  |  |  | 77.51 | [5 empty] | 77.28 |  |  | 79.47 |  |  |  | 5.67 |  | 4.66 | [8 empty] | 17.83 |  |  |  |  | 0.32
1996 |  |  |  | 2591.65 |  |  | 5707 |  |  |  | 516 | [10 empty] | 57.18 |  |  |  | 57.18 | [5 empty] | 57.18 |  |  | 64.97 |  |  |  | 31.11 |  | 25.82 | [8 empty] | 17.00 |  |  |  |  | 0.00
1997 |  |  |  | 3386.16 |  |  | 6841 |  |  |  | 516 | [10 empty] | 74.91 |  |  |  | 74.91 | [5 empty] | 74.91 |  |  | 78.09 |  |  |  | 16.79 |  | 15.11 | [8 empty] | 9.98 |  |  |  |  | 0.00
1998 |  |  |  | 3130.15 |  |  | 6384 |  |  |  | 516 | [10 empty] | 69.25 |  |  |  | 69.73 | [5 empty] | 69.25 |  |  | 72.88 |  |  |  | 14.14 |  | 11.48 | [8 empty] | 18.78 |  |  |  |  | 0.49
1999 |  |  |  | 3353.71 |  |  | 6863 |  |  |  | 516 | [10 empty] | 74.18 |  |  |  | 74.42 | [5 empty] | 74.19 |  |  | 78.34 |  |  |  | 25.38 |  | 25.31 | [8 empty] | 0.27 |  |  |  |  | 0.24
2000 |  |  |  | 2738.74 |  |  | 6449 |  |  |  | 516 | [10 empty] | 60.46 |  |  |  | 60.60 | [5 empty] | 60.42 |  |  | 73.42 |  |  |  | 19.46 |  | 14.64 | [8 empty] | 24.76 |  |  |  |  | 0.14
2001 |  |  |  | 2618.08 |  |  | 5286 |  |  |  | 516 | [10 empty] | 57.68 |  |  |  | 57.68 | [5 empty] | 57.92 |  |  | 60.34 |  |  |  | 21.61 |  | 15.90 | [8 empty] | 26.42 |  |  |  |  | 0.00
2002 |  |  |  | 3982.31 |  |  | 7985 |  |  |  | 516 | [10 empty] | 88.29 |  |  |  | 88.90 | [5 empty] | 88.10 |  |  | 91.15 |  |  |  | 7.01 |  | 6.71 | [8 empty] | 4.39 |  |  |  |  | 0.61
2003 |  |  |  | 3267.37 |  |  | 6566 |  |  |  | 516 | [10 empty] | 72.46 |  |  |  | 74.27 | [5 empty] | 72.28 |  |  | 74.95 |  |  |  | 12.71 |  | 10.81 | [8 empty] | 14.92 |  |  |  |  | 1.81
2004 |  |  |  | 2780.80 |  |  | 5597 |  |  |  | 516 | [10 empty] | 61.51 |  |  |  | 61.68 | [5 empty] | 61.35 |  |  | 63.72 |  |  |  | 28.61 |  | 24.72 | [8 empty] | 13.60 |  |  |  |  | 0.17
2005 |  |  |  | 2850.13 |  |  | 5596 |  |  |  | 516 | [10 empty] | 63.14 |  |  |  | 64.25 | [5 empty] | 63.05 |  |  | 63.88 |  |  |  | 3.16 |  | 4.41 | [8 empty] | 31.34 |  |  |  |  | 1.12
2006 |  |  |  | 3899.46 |  |  | 7635 |  |  |  | 516 | [10 empty] | 86.05 |  |  |  | 86.14 | [5 empty] | 86.27 |  |  | 87.16 |  |  |  | 4.26 |  | 13.54 | [8 empty] | 0.32 |  |  |  |  | 0.10
2007 |  |  |  | 3216.52 |  |  | 6588 |  |  |  | 516 | [10 empty] | 70.75 |  |  |  | 71.26 | [5 empty] | 71.16 |  |  | 75.21 |  |  |  | 8.36 |  | 10.77 | [8 empty] | 17.97 |  |  |  |  | 0.51
2008 |  |  |  | 4323.78 |  |  | 8521 |  |  |  | 516 | [10 empty] | 95.64 |  |  |  | 95.79 | [5 empty] | 95.39 |  |  | 97.01 |  |  |  | 4.21 |  | 4.21 | [8 empty] | 0.00 |  |  |  |  | 0.15
2009 |  |  |  | 3493.23 |  |  | 7051 |  |  |  | 516 | [10 empty] | 77.60 |  |  |  | 77.97 | [5 empty] | 77.28 |  |  | 80.49 |  |  |  | 3.36 |  | 2.71 | [8 empty] | 19.32 |  |  |  |  | 0.36
2010 |  |  |  | 3865.26 |  |  | 7659 |  |  |  | 516 | [10 empty] | 85.83 |  |  |  | 86.01 | [5 empty] | 85.51 |  |  | 87.43 |  |  |  | 3.22 |  | 2.86 | [8 empty] | 11.12 |  |  |  |  | 0.19
2011 |  |  |  | 3195.82 |  |  | 6334 |  |  |  | 516 | [10 empty] | 70.96 |  |  |  | 71.33 | [5 empty] | 70.70 |  |  | 72.31 |  |  |  | 0.60 |  | 0.43 | [8 empty] | 28.24 |  |  |  |  | 0.38
2012 |  |  |  | 4333.57 |  |  | 8550 |  |  |  | 516 | [10 empty] | 95.50 |  |  |  | 97.08 | [5 empty] | 95.61 |  |  | 97.34 |  |  |  | 2.92 |  | 2.92 | [8 empty] | 0.00 |  |  |  |  | 1.58
2013 |  |  |  | 3027.43 |  |  | 6047 |  |  |  | 516 | [10 empty] | 67.19 |  |  |  | 67.42 | [5 empty] | 66.98 |  |  | 69.03 |  |  |  | 0.14 |  | 0.10 | [8 empty] | 32.49 |  |  |  |  | 0.23
2014 |  |  |  | 3979.30 |  |  | 8397 |  |  |  | 516 | [10 empty] | 87.91 |  |  |  | 88.18 | [5 empty] | 88.03 |  |  | 95.86 |  |  |  | 11.82 |  | 11.82 | [8 empty] | 0.00 |  |  |  |  | 0.27
2015 |  |  |  | 3037.96 |  |  | 6064 |  |  |  | 516 | [10 empty] | 67.32 |  |  |  | 67.86 | [5 empty] | 67.21 |  |  | 69.22 |  |  |  | 5.43 |  | 3.89 | [8 empty] | 28.25 |  |  |  |  | 0.54
2016 |  |  |  | 3995.28 |  |  | 8259 |  |  |  | 516 | [10 empty] | 88.20 |  |  |  | 91.33 | [5 empty] | 88.15 |  |  | 94.02 |  |  |  | 2.89 |  | 7.15 | [8 empty] | 1.52 |  |  |  |  | 3.13
2017 |  |  |  | 4434.18 |  |  | 8686 |  |  |  | 516 | [10 empty] | 98.31 |  |  |  | 98.57 | [5 empty] | 98.10 |  |  | 99.16 |  |  |  | 1.43 |  | 1.43 | [8 empty] | 0.00 |  |  |  |  | 0.27
2018 |  |  |  | 2652.58 |  |  | 5392 |  |  |  | 516 | [10 empty] | 58.68 |  |  |  | 61.18 | [5 empty] | 58.68 |  |  | 61.55 |  |  |  | 6.08 |  | 3.96 | [8 empty] | 34.87 |  |  |  |  | 2.49
2019 |  |  |  | 4461.28 |  |  | 8681 |  |  |  | 516 | [10 empty] | 98.28 |  |  |  | 98.40 | [5 empty] | 98.70 |  |  | 99.10 |  |  |  | 1.59 |  | 1.59 | [8 empty] | 0.01 |  |  |  |  | 0.12
2020 |  |  |  | 3027.01 |  |  | 5918 |  |  |  | 516 | [10 empty] | 66.72 |  |  |  | 67.10 | [5 empty] | 66.78 |  |  | 67.37 |  |  |  | 0.07 |  | 0.05 | [8 empty] | 32.85 |  |  |  |  | 0.39
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 518
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 81
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2866 | [14 empty] | 1002
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 3
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 17
L. |  | Human factor related | [39 empty] | 36
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 9
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 16
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 2866 | [14 empty] | 1083 |  |  |  | 559 | [11 empty] | 42
Total | [22 empty] | 2866 | [14 empty] | 1684
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 56
12. |  |  | Reactor I&C Systems | [34 empty] | 47
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 29
14. |  |  | Safety Systems | [34 empty] | 38
15. |  |  | Reactor Cooling Systems | [34 empty] | 47
16. |  |  | Steam generation systems | [34 empty] | 99
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 13
31. |  |  | Turbine and auxiliaries | [34 empty] | 53
32. |  |  | Feedwater and Main Steam System | [34 empty] | 34
33. |  |  | Circulating Water System | [34 empty] | 13
34. |  |  | Miscellaneous Systems | [34 empty] | 20
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 64
42. |  |  | Electrical Power Supply Systems | [34 empty] | 22
Total | [37 empty] | 540

## PICKERING-7
2020 Operating Experience
CA-15 | [8 empty] | PICKERING-7 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-03-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-11-17
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-01-01
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2/PuO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4316.41 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.35 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.04 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.33 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.2 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.47 %
Load Factor (LF) | [18 empty] | : | 95.23 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.15 %
Operating Factor (OF) | [18 empty] | : | 94.73 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 463 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 390.56 | 122.16 |  |  |  | 385.42 |  | 377.68 | [8 empty] | 391.06 |  |  | 372.15 | [6 empty] | 378.98 |  | 369.76 |  |  |  | 370.89 |  |  | 387.33 |  |  | 382.48 | [9 empty] | 387.95 |  |  | 4316.41
EAF [%] |  |  |  |  | 100.00 | 33.34 |  |  |  | 98.05 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.30 | [6 empty] | 98.55 |  | 96.73 |  |  |  | 99.98 |  |  | 99.44 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 94.04
UCF [%] |  |  |  |  | 100.00 | 33.34 |  |  |  | 98.05 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.64 | [6 empty] | 99.14 |  | 97.06 |  |  |  | 99.98 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 94.20
LF [%] |  |  |  |  | 101.73 | 34.01 |  |  |  | 100.39 |  | 101.66 | [8 empty] | 101.86 |  |  | 100.17 | [6 empty] | 98.72 |  | 96.32 |  |  |  | 99.83 |  |  | 100.89 |  |  | 102.95 | [9 empty] | 101.05 |  |  | 95.23
OF [%] |  |  |  |  | 100.00 | 33.48 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.73
FLR [%] |  |  |  |  | 0.00 | 0.02 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.86 |  | 2.94 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 0.35
UCL [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.86 |  | 2.94 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 0.33
PUF [%] |  |  |  |  | 0.00 | 66.66 |  |  |  | 1.93 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.35 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.47
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.34 | [6 empty] | 0.59 |  | 0.33 |  |  |  | 0.00 |  |  | 0.56 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.15
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 127628.6 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.42 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.36 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 10.05 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.97 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.97 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.15 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.61 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.14 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4093.95 |  |  | 8277 |  |  |  | 516 | [10 empty] | 92.65 |  |  |  | 99.03 | [5 empty] | 90.57 |  |  | 94.49 |  |  |  | 0.86 |  | 0.86 | [8 empty] | 0.11 |  |  |  |  | 6.39
1986 |  |  |  | 3373.30 |  |  | 7002 |  |  |  | 516 | [10 empty] | 75.20 |  |  |  | 75.45 | [5 empty] | 74.63 |  |  | 79.93 |  |  |  | 8.27 |  | 6.80 | [8 empty] | 17.75 |  |  |  |  | 0.25
1987 |  |  |  | 4339.89 |  |  | 8642 |  |  |  | 516 | [10 empty] | 95.99 |  |  |  | 97.44 | [5 empty] | 96.01 |  |  | 98.65 |  |  |  | 2.50 |  | 2.50 | [8 empty] | 0.05 |  |  |  |  | 1.45
1988 |  |  |  | 4340.42 |  |  | 8519 |  |  |  | 516 | [10 empty] | 95.39 |  |  |  | 95.94 | [5 empty] | 95.76 |  |  | 96.98 |  |  |  | 4.06 |  | 4.06 | [8 empty] | 0.00 |  |  |  |  | 0.55
1989 |  |  |  | 3408.69 |  |  | 6939 |  |  |  | 516 | [10 empty] | 75.37 |  |  |  | 77.13 | [5 empty] | 75.41 |  |  | 79.21 |  |  |  | 10.45 |  | 9.00 | [8 empty] | 13.87 |  |  |  |  | 1.76
1990 |  |  |  | 3500.80 |  |  | 7420 |  |  |  | 516 | [10 empty] | 77.73 |  |  |  | 78.35 | [5 empty] | 77.45 |  |  | 84.70 |  |  |  | 13.66 |  | 12.39 | [8 empty] | 9.25 |  |  |  |  | 0.62
1991 |  |  |  | 4258.77 |  |  | 8436 |  |  |  | 516 | [10 empty] | 94.52 |  |  |  | 94.93 | [5 empty] | 94.22 |  |  | 96.30 |  |  |  | 4.76 |  | 4.74 | [8 empty] | 0.33 |  |  |  |  | 0.42
1992 |  |  |  | 3727.45 |  |  | 7349 |  |  |  | 516 | [10 empty] | 82.40 |  |  |  | 82.41 | [5 empty] | 82.24 |  |  | 83.66 |  |  |  | 2.52 |  | 2.13 | [8 empty] | 15.46 |  |  |  |  | 0.01
1993 |  |  |  | 4415.95 |  |  | 8760 |  |  |  | 516 | [10 empty] | 99.01 |  |  |  | 99.88 | [5 empty] | 97.69 |  |  | 100.00 |  |  |  | 0.12 |  | 0.12 | [8 empty] | 0.00 |  |  |  |  | 0.87
1994 |  |  |  | 3709.91 |  |  | 7386 |  |  |  | 516 | [10 empty] | 83.40 |  |  |  | 83.40 | [5 empty] | 82.07 |  |  | 84.32 |  |  |  | 1.67 |  | 1.41 | [8 empty] | 15.18 |  |  |  |  | 0.00
1995 |  |  |  | 4056.79 |  |  | 8140 |  |  |  | 516 | [10 empty] | 90.05 |  |  |  | 90.43 | [5 empty] | 89.75 |  |  | 92.92 |  |  |  | 9.57 |  | 9.57 | [8 empty] | 0.00 |  |  |  |  | 0.38
1996 |  |  |  | 2050.69 |  |  | 4416 |  |  |  | 516 | [10 empty] | 45.37 |  |  |  | 45.37 | [5 empty] | 45.24 |  |  | 50.27 |  |  |  | 54.63 |  | 54.63 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 2936.16 |  |  | 6208 |  |  |  | 516 | [10 empty] | 64.96 |  |  |  | 64.96 | [5 empty] | 64.96 |  |  | 70.87 |  |  |  | 20.17 |  | 16.41 | [8 empty] | 18.63 |  |  |  |  | 0.00
1998 |  |  |  | 3084.73 |  |  | 6495 |  |  |  | 516 | [10 empty] | 68.24 |  |  |  | 68.87 | [5 empty] | 68.24 |  |  | 74.14 |  |  |  | 20.36 |  | 17.61 | [8 empty] | 13.52 |  |  |  |  | 0.63
1999 |  |  |  | 4433.82 |  |  | 8751 |  |  |  | 516 | [10 empty] | 98.04 |  |  |  | 98.82 | [5 empty] | 98.09 |  |  | 99.90 |  |  |  | 1.18 |  | 1.18 | [8 empty] | 0.00 |  |  |  |  | 0.78
2000 |  |  |  | 2099.00 |  |  | 4445 |  |  |  | 516 | [10 empty] | 46.29 |  |  |  | 46.37 | [5 empty] | 46.31 |  |  | 50.60 |  |  |  | 14.46 |  | 7.84 | [8 empty] | 45.79 |  |  |  |  | 0.08
2001 |  |  |  | 4020.78 |  |  | 7968 |  |  |  | 516 | [10 empty] | 88.71 |  |  |  | 89.03 | [5 empty] | 88.95 |  |  | 90.96 |  |  |  | 10.97 |  | 10.97 | [8 empty] | 0.00 |  |  |  |  | 0.32
2002 |  |  |  | 4246.89 |  |  | 8538 |  |  |  | 516 | [10 empty] | 93.85 |  |  |  | 94.45 | [5 empty] | 93.95 |  |  | 97.47 |  |  |  | 5.55 |  | 5.55 | [8 empty] | 0.00 |  |  |  |  | 0.59
2003 |  |  |  | 1790.66 |  |  | 3811 |  |  |  | 516 | [10 empty] | 39.66 |  |  |  | 39.81 | [5 empty] | 39.62 |  |  | 43.50 |  |  |  | 40.88 |  | 27.53 | [8 empty] | 32.67 |  |  |  |  | 0.15
2004 |  |  |  | 3116.06 |  |  | 6127 |  |  |  | 516 | [10 empty] | 68.86 |  |  |  | 68.93 | [5 empty] | 68.75 |  |  | 69.75 |  |  |  | 4.64 |  | 3.36 | [8 empty] | 27.72 |  |  |  |  | 0.07
2005 |  |  |  | 4390.76 |  |  | 8658 |  |  |  | 516 | [10 empty] | 97.44 |  |  |  | 97.79 | [5 empty] | 97.14 |  |  | 98.84 |  |  |  | 2.21 |  | 2.21 | [8 empty] | 0.00 |  |  |  |  | 0.34
2006 |  |  |  | 2652.57 |  |  | 5311 |  |  |  | 516 | [10 empty] | 59.06 |  |  |  | 59.11 | [5 empty] | 58.68 |  |  | 60.63 |  |  |  | 10.24 |  | 21.12 | [8 empty] | 19.77 |  |  |  |  | 0.05
2007 |  |  |  | 3667.91 |  |  | 7540 |  |  |  | 516 | [10 empty] | 81.69 |  |  |  | 82.04 | [5 empty] | 81.15 |  |  | 86.07 |  |  |  | 9.97 |  | 16.75 | [8 empty] | 1.21 |  |  |  |  | 0.35
2008 |  |  |  | 1530.27 |  |  | 3084 |  |  |  | 516 | [10 empty] | 33.98 |  |  |  | 33.99 | [5 empty] | 33.76 |  |  | 35.11 |  |  |  | 66.01 |  | 66.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 4229.46 |  |  | 8492 |  |  |  | 516 | [10 empty] | 94.10 |  |  |  | 94.53 | [5 empty] | 93.57 |  |  | 96.94 |  |  |  | 5.47 |  | 5.47 | [8 empty] | 0.00 |  |  |  |  | 0.43
2010 |  |  |  | 2920.66 |  |  | 5895 |  |  |  | 516 | [10 empty] | 64.78 |  |  |  | 65.13 | [5 empty] | 64.61 |  |  | 67.29 |  |  |  | 1.64 |  | 1.69 | [8 empty] | 33.18 |  |  |  |  | 0.35
2011 |  |  |  | 4337.70 |  |  | 8673 |  |  |  | 516 | [10 empty] | 96.58 |  |  |  | 96.83 | [5 empty] | 95.96 |  |  | 99.01 |  |  |  | 3.17 |  | 3.17 | [8 empty] | 0.00 |  |  |  |  | 0.25
2012 |  |  |  | 2920.02 |  |  | 5965 |  |  |  | 516 | [10 empty] | 64.76 |  |  |  | 66.28 | [5 empty] | 64.42 |  |  | 67.91 |  |  |  | 6.84 |  | 4.87 | [8 empty] | 28.85 |  |  |  |  | 1.52
2013 |  |  |  | 4264.55 |  |  | 8760 |  |  |  | 516 | [10 empty] | 94.44 |  |  |  | 94.92 | [5 empty] | 94.35 |  |  | 100.00 |  |  |  | 5.04 |  | 5.04 | [8 empty] | 0.04 |  |  |  |  | 0.48
2014 |  |  |  | 2783.08 |  |  | 5489 |  |  |  | 516 | [10 empty] | 61.95 |  |  |  | 62.18 | [5 empty] | 61.57 |  |  | 62.66 |  |  |  | 6.72 |  | 6.53 | [8 empty] | 31.30 |  |  |  |  | 0.23
2015 |  |  |  | 4171.04 |  |  | 8336 |  |  |  | 516 | [10 empty] | 92.57 |  |  |  | 93.11 | [5 empty] | 92.28 |  |  | 95.16 |  |  |  | 3.43 |  | 5.65 | [8 empty] | 1.25 |  |  |  |  | 0.54
2016 |  |  |  | 2803.59 |  |  | 5574 |  |  |  | 516 | [10 empty] | 61.97 |  |  |  | 62.32 | [5 empty] | 61.85 |  |  | 63.46 |  |  |  | 6.62 |  | 5.50 | [8 empty] | 32.18 |  |  |  |  | 0.35
2017 |  |  |  | 3751.37 |  |  | 7512 |  |  |  | 516 | [10 empty] | 83.14 |  |  |  | 83.35 | [5 empty] | 82.99 |  |  | 85.75 |  |  |  | 13.44 |  | 16.11 | [8 empty] | 0.55 |  |  |  |  | 0.20
2018 |  |  |  | 4377.16 |  |  | 8687 |  |  |  | 516 | [10 empty] | 96.67 |  |  |  | 98.11 | [5 empty] | 96.84 |  |  | 99.17 |  |  |  | 1.89 |  | 1.89 | [8 empty] | 0.00 |  |  |  |  | 1.45
2019 |  |  |  | 3132.65 |  |  | 6131 |  |  |  | 516 | [10 empty] | 68.52 |  |  |  | 68.53 | [5 empty] | 69.30 |  |  | 69.99 |  |  |  | 1.03 |  | 0.71 | [8 empty] | 30.76 |  |  |  |  | 0.01
2020 |  |  |  | 4316.41 |  |  | 8321 |  |  |  | 516 | [10 empty] | 94.04 |  |  |  | 94.20 | [5 empty] | 95.23 |  |  | 94.73 |  |  |  | 0.35 |  | 0.33 | [8 empty] | 5.47 |  |  |  |  | 0.15
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 554
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 463 | [14 empty] | 925
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 9
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 118
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 13
Z. |  | Other | [39 empty] | 33
Subtotal | [22 empty] | 463 | [14 empty] | 926 |  |  |  | 714 | [11 empty] | 20
Total | [22 empty] | 463 | [14 empty] | 1660
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 98
12. |  |  | Reactor I&C Systems | [34 empty] | 56
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 14
14. |  |  | Safety Systems | [34 empty] | 32
15. |  |  | Reactor Cooling Systems | [34 empty] | 87
16. |  |  | Steam generation systems | [34 empty] | 56
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 22
31. |  |  | Turbine and auxiliaries | [34 empty] | 34
32. |  |  | Feedwater and Main Steam System | [34 empty] | 19
33. |  |  | Circulating Water System | [34 empty] | 13
34. |  |  | Miscellaneous Systems | [34 empty] | 45
41. |  |  | Main Generator Systems | [34 empty] | 67
42. |  |  | Electrical Power Supply Systems | [34 empty] | 49
Total | [37 empty] | 592

## PICKERING-8
2020 Operating Experience
CA-16 | [8 empty] | PICKERING-8 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-09-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-01-21
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-02-28
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4070.63 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.65 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.87 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.59 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.41 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9 %
Load Factor (LF) | [18 empty] | : | 89.81 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.54 %
Operating Factor (OF) | [18 empty] | : | 91.33 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 762 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 384.77 | 361.79 |  |  |  | 385.27 |  | 162.03 | [8 empty] | 330.72 |  |  | 367.10 | [6 empty] | 229.15 |  | 375.00 |  |  |  | 364.78 |  |  | 367.16 |  |  | 358.76 | [9 empty] | 384.09 |  |  | 4070.63
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.99 |  | 43.64 | [8 empty] | 86.73 |  |  | 99.23 | [6 empty] | 60.23 |  | 97.81 |  |  |  | 98.44 |  |  | 95.74 |  |  | 96.55 | [9 empty] | 99.98 |  |  | 89.87
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.99 |  | 43.64 | [8 empty] | 86.73 |  |  | 100.00 | [6 empty] | 61.27 |  | 99.99 |  |  |  | 99.96 |  |  | 96.71 |  |  | 96.55 | [9 empty] | 99.98 |  |  | 90.41
LF [%] |  |  |  |  | 100.23 | 100.74 |  |  |  | 100.36 |  | 43.61 | [8 empty] | 86.15 |  |  | 98.81 | [6 empty] | 59.69 |  | 97.68 |  |  |  | 98.19 |  |  | 95.64 |  |  | 96.56 | [9 empty] | 100.05 |  |  | 89.81
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 43.61 | [8 empty] | 89.25 |  |  | 100.00 | [6 empty] | 62.90 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.33
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.25 |  |  | 0.00 | [6 empty] | 0.06 |  | 0.01 |  |  |  | 0.04 |  |  | 3.29 |  |  | 3.45 | [9 empty] | 0.02 |  |  | 0.65
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.21 |  |  | 0.00 | [6 empty] | 0.04 |  | 0.01 |  |  |  | 0.04 |  |  | 3.29 |  |  | 3.45 | [9 empty] | 0.02 |  |  | 0.59
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 56.36 | [8 empty] | 13.06 |  |  | 0.00 | [6 empty] | 38.69 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.77 | [6 empty] | 1.04 |  | 2.18 |  |  |  | 1.53 |  |  | 0.97 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.54
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 119937.68 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.98 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.14 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.43 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.77 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.8 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.62 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.37 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 3792.31 |  |  | 8086 |  |  |  | 516 | [10 empty] | 96.32 |  |  |  | 96.67 | [5 empty] | 95.69 |  |  | 97.69 |  |  |  | 3.33 |  | 3.33 | [8 empty] | 0.00 |  |  |  |  | 0.35
1987 |  |  |  | 3759.36 |  |  | 7585 |  |  |  | 516 | [10 empty] | 83.31 |  |  |  | 84.70 | [5 empty] | 83.17 |  |  | 86.59 |  |  |  | 2.09 |  | 1.81 | [8 empty] | 13.49 |  |  |  |  | 1.38
1988 |  |  |  | 3710.38 |  |  | 7296 |  |  |  | 516 | [10 empty] | 82.25 |  |  |  | 82.50 | [5 empty] | 81.86 |  |  | 83.06 |  |  |  | 2.16 |  | 1.82 | [8 empty] | 15.68 |  |  |  |  | 0.25
1989 |  |  |  | 4295.19 |  |  | 8569 |  |  |  | 516 | [10 empty] | 95.37 |  |  |  | 96.61 | [5 empty] | 95.02 |  |  | 97.82 |  |  |  | 3.29 |  | 3.29 | [8 empty] | 0.10 |  |  |  |  | 1.24
1990 |  |  |  | 3014.65 |  |  | 6743 |  |  |  | 516 | [10 empty] | 66.63 |  |  |  | 66.72 | [5 empty] | 66.69 |  |  | 76.97 |  |  |  | 19.23 |  | 15.89 | [8 empty] | 17.39 |  |  |  |  | 0.09
1991 |  |  |  | 4484.97 |  |  | 8759 |  |  |  | 516 | [10 empty] | 98.89 |  |  |  | 99.52 | [5 empty] | 99.22 |  |  | 99.99 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.00 |  |  |  |  | 0.63
1992 |  |  |  | 4211.99 |  |  | 8280 |  |  |  | 516 | [10 empty] | 92.95 |  |  |  | 92.98 | [5 empty] | 92.93 |  |  | 94.26 |  |  |  | 6.81 |  | 6.79 | [8 empty] | 0.22 |  |  |  |  | 0.03
1993 |  |  |  | 3670.54 |  |  | 7233 |  |  |  | 516 | [10 empty] | 81.73 |  |  |  | 82.15 | [5 empty] | 81.20 |  |  | 82.57 |  |  |  | 2.50 |  | 2.11 | [8 empty] | 15.74 |  |  |  |  | 0.41
1994 |  |  |  | 4341.88 |  |  | 8579 |  |  |  | 516 | [10 empty] | 96.85 |  |  |  | 96.85 | [5 empty] | 96.06 |  |  | 97.93 |  |  |  | 3.14 |  | 3.14 | [8 empty] | 0.01 |  |  |  |  | 0.00
1995 |  |  |  | 4012.08 |  |  | 8066 |  |  |  | 516 | [10 empty] | 89.04 |  |  |  | 89.42 | [5 empty] | 88.76 |  |  | 92.08 |  |  |  | 10.58 |  | 10.58 | [8 empty] | 0.00 |  |  |  |  | 0.38
1996 |  |  |  | 1300.26 |  |  | 2597 |  |  |  | 516 | [10 empty] | 28.73 |  |  |  | 28.73 | [5 empty] | 28.69 |  |  | 29.57 |  |  |  | 68.79 |  | 63.34 | [8 empty] | 7.92 |  |  |  |  | 0.00
1997 |  |  |  | 360.81 |  |  | 995 |  |  |  | 516 | [10 empty] | 7.96 |  |  |  | 7.96 | [5 empty] | 7.96 |  |  | 11.33 |  |  |  | 44.06 |  | 6.27 | [8 empty] | 85.77 |  |  |  |  | 0.00
1998 |  |  |  | 3493.62 |  |  | 7009 |  |  |  | 516 | [10 empty] | 77.29 |  |  |  | 78.02 | [5 empty] | 77.29 |  |  | 80.01 |  |  |  | 10.55 |  | 9.20 | [8 empty] | 12.78 |  |  |  |  | 0.73
1999 |  |  |  | 3509.06 |  |  | 7077 |  |  |  | 516 | [10 empty] | 77.63 |  |  |  | 78.44 | [5 empty] | 77.63 |  |  | 80.79 |  |  |  | 2.49 |  | 2.00 | [8 empty] | 19.56 |  |  |  |  | 0.81
2000 |  |  |  | 2711.21 |  |  | 5508 |  |  |  | 516 | [10 empty] | 59.92 |  |  |  | 60.83 | [5 empty] | 59.82 |  |  | 62.70 |  |  |  | 16.52 |  | 12.04 | [8 empty] | 27.13 |  |  |  |  | 0.91
2001 |  |  |  | 3502.19 |  |  | 6999 |  |  |  | 516 | [10 empty] | 77.47 |  |  |  | 78.22 | [5 empty] | 77.48 |  |  | 79.90 |  |  |  | 8.46 |  | 7.23 | [8 empty] | 14.55 |  |  |  |  | 0.75
2002 |  |  |  | 3605.36 |  |  | 7244 |  |  |  | 516 | [10 empty] | 80.03 |  |  |  | 81.06 | [5 empty] | 79.76 |  |  | 82.69 |  |  |  | 9.27 |  | 8.28 | [8 empty] | 10.66 |  |  |  |  | 1.02
2003 |  |  |  | 3921.29 |  |  | 8026 |  |  |  | 516 | [10 empty] | 86.90 |  |  |  | 89.68 | [5 empty] | 86.75 |  |  | 91.62 |  |  |  | 10.32 |  | 10.32 | [8 empty] | 0.00 |  |  |  |  | 2.78
2004 |  |  |  | 2489.46 |  |  | 5182 |  |  |  | 516 | [10 empty] | 55.13 |  |  |  | 55.35 | [5 empty] | 54.92 |  |  | 58.99 |  |  |  | 23.42 |  | 16.93 | [8 empty] | 27.71 |  |  |  |  | 0.23
2005 |  |  |  | 4195.24 |  |  | 8431 |  |  |  | 516 | [10 empty] | 93.40 |  |  |  | 94.60 | [5 empty] | 92.81 |  |  | 96.24 |  |  |  | 5.40 |  | 5.40 | [8 empty] | 0.00 |  |  |  |  | 1.20
2006 |  |  |  | 2908.54 |  |  | 5853 |  |  |  | 516 | [10 empty] | 64.75 |  |  |  | 65.06 | [5 empty] | 64.35 |  |  | 66.82 |  |  |  | 3.38 |  | 11.22 | [8 empty] | 23.72 |  |  |  |  | 0.31
2007 |  |  |  | 3843.21 |  |  | 8015 |  |  |  | 516 | [10 empty] | 85.51 |  |  |  | 87.28 | [5 empty] | 85.02 |  |  | 91.50 |  |  |  | 12.72 |  | 12.72 | [8 empty] | 0.00 |  |  |  |  | 1.77
2008 |  |  |  | 2918.75 |  |  | 6116 |  |  |  | 516 | [10 empty] | 64.41 |  |  |  | 64.71 | [5 empty] | 64.40 |  |  | 69.63 |  |  |  | 18.42 |  | 18.21 | [8 empty] | 17.08 |  |  |  |  | 0.30
2009 |  |  |  | 4115.23 |  |  | 8520 |  |  |  | 516 | [10 empty] | 91.04 |  |  |  | 91.61 | [5 empty] | 91.04 |  |  | 97.26 |  |  |  | 8.39 |  | 8.39 | [8 empty] | 0.00 |  |  |  |  | 0.57
2010 |  |  |  | 3081.07 |  |  | 6427 |  |  |  | 516 | [10 empty] | 68.16 |  |  |  | 68.53 | [5 empty] | 68.16 |  |  | 73.37 |  |  |  | 9.60 |  | 9.19 | [8 empty] | 22.27 |  |  |  |  | 0.37
2011 |  |  |  | 4051.72 |  |  | 8345 |  |  |  | 516 | [10 empty] | 89.64 |  |  |  | 90.30 | [5 empty] | 89.64 |  |  | 95.26 |  |  |  | 9.61 |  | 9.60 | [8 empty] | 0.10 |  |  |  |  | 0.66
2012 |  |  |  | 2936.38 |  |  | 5967 |  |  |  | 516 | [10 empty] | 64.86 |  |  |  | 65.53 | [5 empty] | 64.78 |  |  | 67.93 |  |  |  | 6.71 |  | 7.15 | [8 empty] | 27.33 |  |  |  |  | 0.66
2013 |  |  |  | 3879.06 |  |  | 7979 |  |  |  | 516 | [10 empty] | 85.97 |  |  |  | 86.34 | [5 empty] | 85.82 |  |  | 91.08 |  |  |  | 13.57 |  | 13.55 | [8 empty] | 0.11 |  |  |  |  | 0.37
2014 |  |  |  | 2411.29 |  |  | 5223 |  |  |  | 516 | [10 empty] | 53.30 |  |  |  | 53.43 | [5 empty] | 53.35 |  |  | 59.62 |  |  |  | 26.12 |  | 22.62 | [8 empty] | 23.94 |  |  |  |  | 0.14
2015 |  |  |  | 4289.30 |  |  | 8440 |  |  |  | 516 | [10 empty] | 94.91 |  |  |  | 95.37 | [5 empty] | 94.89 |  |  | 96.35 |  |  |  | 0.76 |  | 0.73 | [8 empty] | 3.90 |  |  |  |  | 0.46
2016 |  |  |  | 2197.88 |  |  | 4367 |  |  |  | 516 | [10 empty] | 48.35 |  |  |  | 48.60 | [5 empty] | 48.49 |  |  | 49.72 |  |  |  | 0.61 |  | 11.62 | [8 empty] | 39.78 |  |  |  |  | 0.25
2017 |  |  |  | 3870.80 |  |  | 7787 |  |  |  | 516 | [10 empty] | 85.68 |  |  |  | 85.96 | [5 empty] | 85.63 |  |  | 88.89 |  |  |  | 2.90 |  | 2.57 | [8 empty] | 11.47 |  |  |  |  | 0.28
2018 |  |  |  | 2626.93 |  |  | 5427 |  |  |  | 516 | [10 empty] | 58.08 |  |  |  | 59.70 | [5 empty] | 58.12 |  |  | 61.95 |  |  |  | 13.69 |  | 9.47 | [8 empty] | 30.82 |  |  |  |  | 1.63
2019 |  |  |  | 4363.55 |  |  | 8571 |  |  |  | 516 | [10 empty] | 96.44 |  |  |  | 96.71 | [5 empty] | 96.54 |  |  | 97.84 |  |  |  | 1.03 |  | 1.01 | [8 empty] | 2.28 |  |  |  |  | 0.27
2020 |  |  |  | 4070.63 |  |  | 8022 |  |  |  | 516 | [10 empty] | 89.87 |  |  |  | 90.41 | [5 empty] | 89.81 |  |  | 91.33 |  |  |  | 0.65 |  | 0.59 | [8 empty] | 9.00 |  |  |  |  | 0.54
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 464
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 76
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 762 | [14 empty] | 950
E. |  | Testing of plant systems or components | [35 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 303
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 9
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 762 | [14 empty] | 1027 |  |  |  | 768 | [11 empty] | 13
Total | [22 empty] | 762 | [14 empty] | 1808
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 34
12. |  |  | Reactor I&C Systems | [34 empty] | 34
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 37
15. |  |  | Reactor Cooling Systems | [34 empty] | 85
16. |  |  | Steam generation systems | [34 empty] | 30
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 96
31. |  |  | Turbine and auxiliaries | [34 empty] | 48
32. |  |  | Feedwater and Main Steam System | [34 empty] | 27
33. |  |  | Circulating Water System | [34 empty] | 23
34. |  |  | Miscellaneous Systems | [34 empty] | 13
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 10
42. |  |  | Electrical Power Supply Systems | [34 empty] | 30
Total | [37 empty] | 471

## POINT LEPREAU
2020 Operating Experience
CA-17 | [8 empty] | POINT LEPREAU | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NBEPC (NEW BRUNSWICK ELECTRIC POWER COMMISSION)
Owner | [7 empty] | : | NBEPC (NEW BRUNSWICK ELECTRIC POWER COMMISSION)
Reactor Supplier | [7 empty] | : | AECL (ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI/PARS (NEI-PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-05-01
Thermal power | [12 empty] | : |  |  | 2180 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-09-11
Gross electrical power | [12 empty] | : |  |  | 705 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-02-01
Reference unit power (net) | [12 empty] | : |  |  | 660 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 11.55
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.3
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 6.28 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.64
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 59.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4801 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.23 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.46 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.08 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.46 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 14.45 %
Load Factor (LF) | [18 empty] | : | 82.81 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 83.13 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1482 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 495.10 | 464.18 |  |  |  | 491.97 |  | 477.90 | [8 empty] | 493.41 |  |  | 474.95 | [6 empty] | 491.83 |  | 484.75 |  |  |  | 60.72 |  |  | 0.00 |  |  | 376.56 | [9 empty] | 489.63 |  |  | 4801.00
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.39 |  | 99.68 | [8 empty] | 100.00 |  |  | 99.95 | [6 empty] | 100.00 |  | 98.72 |  |  |  | 12.78 |  |  | 0.00 |  |  | 79.24 | [9 empty] | 99.71 |  |  | 82.46
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.39 |  | 99.68 | [8 empty] | 100.00 |  |  | 99.95 | [6 empty] | 100.00 |  | 98.72 |  |  |  | 12.78 |  |  | 0.00 |  |  | 79.24 | [9 empty] | 99.71 |  |  | 82.46
LF [%] |  |  |  |  | 100.83 | 101.05 |  |  |  | 100.19 |  | 100.57 | [8 empty] | 100.48 |  |  | 99.95 | [6 empty] | 100.16 |  | 98.72 |  |  |  | 12.78 |  |  | 0.00 |  |  | 79.24 | [9 empty] | 99.71 |  |  | 82.81
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 12.78 |  |  | 0.00 |  |  | 84.72 | [9 empty] | 100.00 |  |  | 83.13
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.61 |  | 0.18 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.46 |  |  |  | 0.00 |  |  | 0.00 |  |  | 1.27 | [9 empty] | 0.00 |  |  | 0.23
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.61 |  | 0.18 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.46 |  |  |  | 0.00 |  |  | 19.35 |  |  | 16.30 | [9 empty] | 0.00 |  |  | 3.08
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.14 | [8 empty] | 0.00 |  |  | 0.05 | [6 empty] | 0.00 |  | 0.82 |  |  |  | 87.22 |  |  | 80.65 |  |  | 4.46 | [9 empty] | 0.29 |  |  | 14.45
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 152874.84 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.81 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 73.06 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.67 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.76 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.41 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 4742.90 |  |  | 7875 |  |  |  | 640 | [10 empty] | 86.03 |  |  |  | 86.03 | [5 empty] | 85.85 |  |  | 89.37 |  |  |  | 8.10 |  | 7.58 | [8 empty] | 6.39 |  |  |  |  | 0.00
1984 |  |  |  | 5000.94 |  |  | 7927 |  |  |  | 635 | [10 empty] | 88.94 |  |  |  | 88.97 | [5 empty] | 89.66 |  |  | 90.24 |  |  |  | 3.03 |  | 2.78 | [8 empty] | 8.25 |  |  |  |  | 0.03
1985 |  |  |  | 5421.91 |  |  | 8547 |  |  |  | 635 | [10 empty] | 96.87 |  |  |  | 96.93 | [5 empty] | 97.47 |  |  | 97.57 |  |  |  | 1.25 |  | 1.23 | [8 empty] | 1.84 |  |  |  |  | 0.06
1986 |  |  |  | 5223.09 |  |  | 8257 |  |  |  | 635 | [10 empty] | 93.41 |  |  |  | 94.00 | [5 empty] | 93.90 |  |  | 94.26 |  |  |  | 0.90 |  | 0.85 | [8 empty] | 5.15 |  |  |  |  | 0.59
1987 |  |  |  | 5107.73 |  |  | 8110 |  |  |  | 635 | [10 empty] | 91.23 |  |  |  | 91.25 | [5 empty] | 91.82 |  |  | 92.58 |  |  |  | 3.32 |  | 3.14 | [8 empty] | 5.61 |  |  |  |  | 0.02
1988 |  |  |  | 5338.25 |  |  | 8383 |  |  |  | 635 | [10 empty] | 94.85 |  |  |  | 94.85 | [5 empty] | 95.70 |  |  | 95.43 |  |  |  | 0.38 |  | 0.36 | [8 empty] | 4.79 |  |  |  |  | 0.00
1989 |  |  |  | 5266.67 |  |  | 8271 |  |  |  | 635 | [10 empty] | 93.60 |  |  |  | 93.81 | [5 empty] | 94.68 |  |  | 94.42 |  |  |  | 0.89 |  | 0.84 | [8 empty] | 5.34 |  |  |  |  | 0.22
1990 |  |  |  | 5333.71 |  |  | 8384 |  |  |  | 635 | [10 empty] | 94.70 |  |  |  | 94.99 | [5 empty] | 95.89 |  |  | 95.71 |  |  |  | 2.92 |  | 2.86 | [8 empty] | 2.15 |  |  |  |  | 0.29
1991 |  |  |  | 5437.17 |  |  | 8500 |  |  |  | 635 | [10 empty] | 96.68 |  |  |  | 96.72 | [5 empty] | 97.75 |  |  | 97.03 |  |  |  | 0.55 |  | 0.54 | [8 empty] | 2.74 |  |  |  |  | 0.04
1992 |  |  |  | 4829.78 |  |  | 7748 |  |  |  | 635 | [10 empty] | 85.76 |  |  |  | 85.76 | [5 empty] | 86.59 |  |  | 88.21 |  |  |  | 3.99 |  | 3.57 | [8 empty] | 10.67 |  |  |  |  | 0.00
1993 |  |  |  | 5320.00 |  |  | 8391 |  |  |  | 635 | [10 empty] | 95.09 |  |  |  | 95.09 | [5 empty] | 95.64 |  |  | 95.79 |  |  |  | 1.42 |  | 1.37 | [8 empty] | 3.54 |  |  |  |  | 0.00
1994 |  |  |  | 5230.10 |  |  | 8270 |  |  |  | 635 | [10 empty] | 93.46 |  |  |  | 93.46 | [5 empty] | 94.02 |  |  | 94.41 |  |  |  | 0.34 |  | 0.32 | [8 empty] | 6.22 |  |  |  |  | 0.00
1995 |  |  |  | 1611.40 |  |  | 2615 |  |  |  | 635 | [10 empty] | 28.98 |  |  |  | 28.98 | [5 empty] | 28.97 |  |  | 29.85 |  |  |  | 43.54 |  | 22.34 | [8 empty] | 48.68 |  |  |  |  | 0.00
1996 |  |  |  | 4587.83 |  |  | 7363 |  |  |  | 635 | [10 empty] | 81.41 |  |  |  | 81.41 | [5 empty] | 82.25 |  |  | 83.82 |  |  |  | 13.97 |  | 13.22 | [8 empty] | 5.37 |  |  |  |  | 0.00
1997 |  |  |  | 3455.59 |  |  | 5564 |  |  |  | 635 | [10 empty] | 61.60 |  |  |  | 62.19 | [5 empty] | 62.12 |  |  | 63.52 |  |  |  | 24.86 |  | 20.57 | [8 empty] | 17.24 |  |  |  |  | 0.59
1998 |  |  |  | 3782.35 |  |  | 6111 |  |  |  | 635 | [10 empty] | 66.04 |  |  |  | 67.11 | [5 empty] | 68.00 |  |  | 69.76 |  |  |  | 20.20 |  | 16.99 | [8 empty] | 15.90 |  |  |  |  | 1.06
1999 |  |  |  | 4082.74 |  |  | 6797 |  |  |  | 635 | [10 empty] | 71.99 |  |  |  | 75.52 | [5 empty] | 73.40 |  |  | 77.59 |  |  |  | 11.47 |  | 9.78 | [8 empty] | 14.70 |  |  |  |  | 3.53
2000 |  |  |  | 3966.85 |  |  | 6792 |  |  |  | 635 | [10 empty] | 70.52 |  |  |  | 77.64 | [5 empty] | 71.12 |  |  | 77.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.36 |  |  |  |  | 7.12
2001 |  |  |  | 4451.33 |  |  | 7418 |  |  |  | 635 | [10 empty] | 79.08 |  |  |  | 84.61 | [5 empty] | 80.02 |  |  | 84.68 |  |  |  | 15.33 |  | 15.31 | [8 empty] | 0.08 |  |  |  |  | 5.53
2002 |  |  |  | 3760.64 |  |  | 6107 |  |  |  | 635 | [10 empty] | 67.59 |  |  |  | 71.59 | [5 empty] | 67.61 |  |  | 69.71 |  |  |  | 6.62 |  | 10.30 | [8 empty] | 18.12 |  |  |  |  | 4.00
2003 |  |  |  | 4739.52 |  |  | 7869 |  |  |  | 635 | [10 empty] | 84.39 |  |  |  | 89.77 | [5 empty] | 85.20 |  |  | 89.83 |  |  |  | 0.70 |  | 4.18 | [8 empty] | 6.05 |  |  |  |  | 5.38
2004 |  |  |  | 4299.74 |  |  | 7310 |  |  |  | 635 | [10 empty] | 82.58 |  |  |  | 83.32 | [5 empty] | 77.09 |  |  | 83.22 |  |  |  | 6.13 |  | 6.56 | [8 empty] | 10.12 |  |  |  |  | 0.74
2005 |  |  |  | 4372.64 |  |  | 7632 |  |  |  | 635 | [10 empty] | 86.79 |  |  |  | 86.79 | [5 empty] | 78.61 |  |  | 87.12 |  |  |  | 2.13 |  | 6.68 | [8 empty] | 6.53 |  |  |  |  | 0.00
2006 |  |  |  | 4361.99 |  |  | 7755 |  |  |  | 635 | [10 empty] | 88.74 |  |  |  | 88.74 | [5 empty] | 78.42 |  |  | 88.53 |  |  |  | 0.88 |  | 1.59 | [8 empty] | 9.67 |  |  |  |  | 0.00
2007 |  |  |  | 4121.82 |  |  | 7511 |  |  |  | 635 | [10 empty] | 85.95 |  |  |  | 85.95 | [5 empty] | 74.10 |  |  | 85.74 |  |  |  | 7.79 |  | 8.02 | [8 empty] | 6.04 |  |  |  |  | 0.00
2008 |  |  |  | 1150.56 |  |  | 2111 |  |  |  | 635 | [10 empty] | 24.03 |  |  |  | 24.03 | [5 empty] | 20.63 |  |  | 24.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 75.97 |  |  |  |  | 0.00
2009 |  |  |  | 0.00 |  |  | 0 |  |  |  | 635 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2010 |  |  |  | 0.00 |  |  | 0 |  |  |  | 635 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2011 |  |  |  | 0.00 |  |  | 0 |  |  |  | 635 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2012 |  |  |  | 411.48 |  |  | 966 |  |  |  | 660 | [10 empty] | 7.53 |  |  |  | 7.53 | [5 empty] | 7.30 |  |  | 11.00 |  |  |  | 39.71 |  | 4.96 | [8 empty] | 87.51 |  |  |  |  | 0.00
2013 |  |  |  | 4111.15 |  |  | 7879 |  |  |  | 660 | [10 empty] | 70.80 |  |  |  | 70.80 | [5 empty] | 71.12 |  |  | 89.95 |  |  |  | 25.07 |  | 24.92 | [8 empty] | 4.28 |  |  |  |  | 0.00
2014 |  |  |  | 4724.62 |  |  | 7229 |  |  |  | 660 | [10 empty] | 81.86 |  |  |  | 81.86 | [5 empty] | 81.72 |  |  | 82.52 |  |  |  | 1.50 |  | 6.29 | [8 empty] | 11.85 |  |  |  |  | 0.00
2015 |  |  |  | 4277.04 |  |  | 6993 |  |  |  | 660 | [10 empty] | 74.61 |  |  |  | 74.61 | [5 empty] | 73.98 |  |  | 79.83 |  |  |  | 20.21 |  | 18.89 | [8 empty] | 6.50 |  |  |  |  | 0.00
2016 |  |  |  | 4548.99 |  |  | 6989 |  |  |  | 660 | [10 empty] | 78.20 |  |  |  | 78.20 | [5 empty] | 78.47 |  |  | 79.57 |  |  |  | 2.65 |  | 10.10 | [8 empty] | 11.71 |  |  |  |  | 0.00
2017 |  |  |  | 5151.32 |  |  | 7928 |  |  |  | 660 | [10 empty] | 89.25 |  |  |  | 89.25 | [5 empty] | 89.10 |  |  | 90.50 |  |  |  | 2.44 |  | 3.65 | [8 empty] | 7.10 |  |  |  |  | 0.00
2018 |  |  |  | 4894.15 |  |  | 7469 |  |  |  | 660 | [10 empty] | 84.46 |  |  |  | 84.46 | [5 empty] | 84.65 |  |  | 85.26 |  |  |  | 0.53 |  | 5.32 | [8 empty] | 10.22 |  |  |  |  | 0.00
2019 |  |  |  | 5015.68 |  |  | 7663 |  |  |  | 660 | [10 empty] | 86.69 |  |  |  | 86.69 | [5 empty] | 86.75 |  |  | 87.48 |  |  |  | 4.50 |  | 4.08 | [8 empty] | 9.23 |  |  |  |  | 0.00
2020 |  |  |  | 4801.00 |  |  | 7302 |  |  |  | 660 | [10 empty] | 82.46 |  |  |  | 82.46 | [5 empty] | 82.81 |  |  | 83.13 |  |  |  | 0.23 |  | 3.08 | [8 empty] | 14.45 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 297
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 74
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 414
E. |  | Testing of plant systems or components | [20 empty] | 1228 |  |  |  | 254 | [10 empty] | 32 |  |  |  | 8
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1070
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 23
H. |  | Nuclear regulatory requirements | [39 empty] | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 57
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
Z. |  | Other | [39 empty] | 24
Subtotal | [22 empty] | 1228 |  |  |  | 254 | [10 empty] | 1613 |  |  |  | 388 | [11 empty] | 4
Total | [22 empty] | 1482 | [14 empty] | 2005
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 254 | [14 empty] | 20
12. |  |  | Reactor I&C Systems | [34 empty] | 18
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 98
16. |  |  | Steam generation systems | [34 empty] | 41
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 4
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 24
31. |  |  | Turbine and auxiliaries | [34 empty] | 56
32. |  |  | Feedwater and Main Steam System | [34 empty] | 25
34. |  |  | Miscellaneous Systems | [34 empty] | 17
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 19
Total | [22 empty] | 254 | [14 empty] | 361
Highlights (2020)
Due to Covid-19 our station's Outage had been pushed from April 2020 to September 2020. During this time, our station further proved it's reliability as there were minimal forced losses and no forced outages. This allowed us to have at total of 417 consecutive days online which was the first time the station has done this in multiple decades.