## DUKOVANY-1
2020 Operating Experience
CZ-4 | [8 empty] | DUKOVANY-1 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-01-01
Thermal power | [12 empty] | : |  |  | 1444 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-02-24
Gross electrical power | [12 empty] | : |  |  | 500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-05-03
Reference unit power (net) | [12 empty] | : |  |  | 468 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.26
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 297
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.3
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3526.21 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.48 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.67 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.33 %
Load Factor (LF) | [18 empty] | : | 85.78 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.19 %
Operating Factor (OF) | [18 empty] | : | 86.75 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1164 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 351.31 | 325.77 |  |  |  | 349.26 |  | 336.05 | [8 empty] | 345.29 |  |  | 329.13 | [6 empty] | 338.10 |  | 335.22 |  |  |  | 328.86 |  |  | 348.69 |  |  | 138.53 | [9 empty] | 0.00 |  |  | 3526.21
EAF [%] |  |  |  |  | 99.97 | 99.43 |  |  |  | 99.80 |  | 99.34 | [8 empty] | 98.92 |  |  | 97.39 | [6 empty] | 97.00 |  | 96.42 |  |  |  | 97.54 |  |  | 99.70 |  |  | 40.98 | [9 empty] | 0.00 |  |  | 85.48
UCF [%] |  |  |  |  | 100.00 | 99.58 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.91 |  |  | 100.00 |  |  | 41.20 | [9 empty] | 0.00 |  |  | 86.67
LF [%] |  |  |  |  | 100.89 | 100.01 |  |  |  | 100.31 |  | 99.73 | [8 empty] | 99.17 |  |  | 97.68 | [6 empty] | 97.10 |  | 96.27 |  |  |  | 97.60 |  |  | 100.14 |  |  | 41.11 | [9 empty] | 0.00 |  |  | 85.78
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 41.67 | [9 empty] | 0.00 |  |  | 86.75
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.09 |  |  | 0.00 |  |  | 58.80 | [9 empty] | 100.00 |  |  | 13.33
XUF [%] |  |  |  |  | 0.03 | 0.15 |  |  |  | 0.20 |  | 0.66 | [8 empty] | 1.08 |  |  | 2.61 | [6 empty] | 3.00 |  | 3.58 |  |  |  | 2.37 |  |  | 0.30 |  |  | 0.22 | [9 empty] | 0.00 |  |  | 1.19
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 111960.15 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.02 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.18 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.86 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.97 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.89 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.84 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.35 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 1993.92 |  |  | 5418 |  |  |  | 396 | [10 empty] | 88.11 |  |  |  | 88.11 | [5 empty] | 86.73 |  |  | 88.06 |  |  |  | 2.36 |  | 2.13 | [8 empty] | 9.77 |  |  |  |  | 0.00
1986 |  |  |  | 2658.35 |  |  | 7094 |  |  |  | 403 | [10 empty] | 76.12 |  |  |  | 76.15 | [5 empty] | 75.30 |  |  | 80.98 |  |  |  | 1.22 |  | 0.94 | [8 empty] | 22.91 |  |  |  |  | 0.03
1987 |  |  |  | 2575.95 |  |  | 6867 |  |  |  | 408 | [10 empty] | 70.74 |  |  |  | 74.73 | [5 empty] | 72.07 |  |  | 78.39 |  |  |  | 0.79 |  | 0.60 | [8 empty] | 24.68 |  |  |  |  | 3.99
1988 |  |  |  | 2523.99 |  |  | 6996 |  |  |  | 408 | [10 empty] | 71.53 |  |  |  | 74.17 | [5 empty] | 70.43 |  |  | 79.64 |  |  |  | 1.48 |  | 1.11 | [8 empty] | 24.72 |  |  |  |  | 2.64
1989 |  |  |  | 2940.57 |  |  | 7579 |  |  |  | 408 | [10 empty] | 82.01 |  |  |  | 82.60 | [5 empty] | 82.27 |  |  | 86.52 |  |  |  | 2.05 |  | 1.72 | [8 empty] | 15.68 |  |  |  |  | 0.59
1990 |  |  |  | 2965.55 |  |  | 7658 |  |  |  | 408 | [10 empty] | 82.49 |  |  |  | 84.34 | [5 empty] | 82.97 |  |  | 87.42 |  |  |  | 3.02 |  | 2.62 | [8 empty] | 13.04 |  |  |  |  | 1.85
1991 |  |  |  | 2581.09 |  |  | 6751 |  |  |  | 408 | [10 empty] | 70.50 |  |  |  | 70.68 | [5 empty] | 72.22 |  |  | 77.07 |  |  |  | 9.25 |  | 7.20 | [8 empty] | 22.12 |  |  |  |  | 0.18
1992 |  |  |  | 3172.77 |  |  | 7537 |  |  |  | 408 | [10 empty] | 80.45 |  |  |  | 80.90 | [5 empty] | 88.53 |  |  | 85.80 |  |  |  | 3.16 |  | 2.64 | [8 empty] | 16.46 |  |  |  |  | 0.44
1993 |  |  |  | 3239.65 |  |  | 7649 |  |  |  | 442 | [10 empty] | 83.67 |  |  |  | 83.67 | [5 empty] | 83.67 |  |  | 87.32 |  |  |  | 2.87 |  | 2.47 | [8 empty] | 13.86 |  |  |  |  | 0.00
1994 |  |  |  | 3278.54 |  |  | 7656 |  |  |  | 442 | [10 empty] | 84.64 |  |  |  | 84.64 | [5 empty] | 84.67 |  |  | 87.40 |  |  |  | 3.15 |  | 2.76 | [8 empty] | 12.60 |  |  |  |  | 0.00
1995 |  |  |  | 2966.06 |  |  | 7022 |  |  |  | 442 | [10 empty] | 76.78 |  |  |  | 76.78 | [5 empty] | 76.60 |  |  | 80.16 |  |  |  | 4.40 |  | 3.53 | [8 empty] | 19.69 |  |  |  |  | 0.00
1996 |  |  |  | 3144.62 |  |  | 7592 |  |  |  | 412 | [10 empty] | 85.36 |  |  |  | 86.01 | [5 empty] | 86.89 |  |  | 86.43 |  |  |  | 2.73 |  | 2.42 | [8 empty] | 11.57 |  |  |  |  | 0.65
1997 |  |  |  | 3295.57 |  |  | 7678 |  |  |  | 440 | [10 empty] | 85.26 |  |  |  | 86.76 | [5 empty] | 85.50 |  |  | 87.65 |  |  |  | 1.01 |  | 0.88 | [8 empty] | 12.36 |  |  |  |  | 1.50
1998 |  |  |  | 2973.35 |  |  | 7518 |  |  |  | 412 | [10 empty] | 82.62 |  |  |  | 85.44 | [5 empty] | 82.38 |  |  | 85.82 |  |  |  | 3.29 |  | 2.91 | [8 empty] | 11.65 |  |  |  |  | 2.82
1999 |  |  |  | 2901.08 |  |  | 7034 |  |  |  | 412 | [10 empty] | 79.23 |  |  |  | 79.75 | [5 empty] | 80.38 |  |  | 80.30 |  |  |  | 0.46 |  | 0.37 | [8 empty] | 19.88 |  |  |  |  | 0.52
2000 |  |  |  | 3327.93 |  |  | 7934 |  |  |  | 412 | [10 empty] | 89.73 |  |  |  | 89.84 | [5 empty] | 91.96 |  |  | 90.32 |  |  |  | 0.48 |  | 0.44 | [8 empty] | 9.72 |  |  |  |  | 0.11
2001 |  |  |  | 3328.90 |  |  | 7996 |  |  |  | 412 | [10 empty] | 90.16 |  |  |  | 90.57 | [5 empty] | 92.24 |  |  | 91.28 |  |  |  | 0.77 |  | 0.70 | [8 empty] | 8.73 |  |  |  |  | 0.42
2002 |  |  |  | 3267.45 |  |  | 7926 |  |  |  | 412 | [10 empty] | 88.92 |  |  |  | 89.63 | [5 empty] | 90.53 |  |  | 90.48 |  |  |  | 1.03 |  | 0.94 | [8 empty] | 9.43 |  |  |  |  | 0.71
2003 |  |  |  | 3032.00 |  |  | 7261 |  |  |  | 412 | [10 empty] | 82.63 |  |  |  | 82.89 | [5 empty] | 84.01 |  |  | 82.89 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 17.06 |  |  |  |  | 0.25
2004 |  |  |  | 3035.50 |  |  | 7349 |  |  |  | 412 | [10 empty] | 82.91 |  |  |  | 83.65 | [5 empty] | 83.88 |  |  | 83.66 |  |  |  | 0.01 |  | 1.17 | [8 empty] | 15.18 |  |  |  |  | 0.73
2005 |  |  |  | 3324.55 |  |  | 8015 |  |  |  | 412 | [10 empty] | 90.62 |  |  |  | 91.26 | [5 empty] | 92.12 |  |  | 91.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.74 |  |  |  |  | 0.64
2006 |  |  |  | 3271.63 |  |  | 8014 |  |  |  | 412 | [10 empty] | 89.73 |  |  |  | 91.20 | [5 empty] | 90.65 |  |  | 91.48 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.79 |  |  |  |  | 1.46
2007 |  |  |  | 2967.32 |  |  | 7198 |  |  |  | 427 | [10 empty] | 80.92 |  |  |  | 81.36 | [5 empty] | 81.72 |  |  | 82.17 |  |  |  | 1.23 |  | 1.01 | [8 empty] | 17.63 |  |  |  |  | 0.45
2008 |  |  |  | 3485.30 |  |  | 8090 |  |  |  | 427 | [10 empty] | 91.59 |  |  |  | 91.80 | [5 empty] | 92.92 |  |  | 92.10 |  |  |  | 1.66 |  | 1.55 | [8 empty] | 6.65 |  |  |  |  | 0.21
2009 |  |  |  | 3518.64 |  |  | 8186 |  |  |  | 427 | [10 empty] | 92.48 |  |  |  | 92.68 | [5 empty] | 94.07 |  |  | 93.45 |  |  |  | 0.49 |  | 0.68 | [8 empty] | 6.65 |  |  |  |  | 0.20
2010 |  |  |  | 3573.83 |  |  | 8256 |  |  |  | 427 | [10 empty] | 93.76 |  |  |  | 93.98 | [5 empty] | 95.54 |  |  | 94.25 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 5.96 |  |  |  |  | 0.21
2011 |  |  |  | 2939.01 |  |  | 6877 |  |  |  | 468 | [10 empty] | 76.93 |  |  |  | 77.28 | [5 empty] | 77.94 |  |  | 78.50 |  |  |  | 0.43 |  | 0.33 | [8 empty] | 22.39 |  |  |  |  | 0.35
2012 |  |  |  | 3733.44 |  |  | 8049 |  |  |  | 468 | [10 empty] | 90.24 |  |  |  | 91.13 | [5 empty] | 90.82 |  |  | 91.63 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 8.82 |  |  |  |  | 0.89
2013 |  |  |  | 3778.58 |  |  | 8142 |  |  |  | 468 | [10 empty] | 91.72 |  |  |  | 92.63 | [5 empty] | 92.17 |  |  | 92.95 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 7.27 |  |  |  |  | 0.91
2014 |  |  |  | 3785.47 |  |  | 8141 |  |  |  | 468 | [10 empty] | 91.74 |  |  |  | 92.55 | [5 empty] | 92.34 |  |  | 92.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.45 |  |  |  |  | 0.80
2015 |  |  |  | 2655.64 |  |  | 5753 |  |  |  | 468 | [10 empty] | 64.66 |  |  |  | 65.63 | [5 empty] | 64.78 |  |  | 65.67 |  |  |  | 0.00 |  | 17.81 | [8 empty] | 16.56 |  |  |  |  | 0.97
2016 |  |  |  | 3579.05 |  |  | 7721 |  |  |  | 468 | [10 empty] | 86.69 |  |  |  | 87.58 | [5 empty] | 87.07 |  |  | 87.91 |  |  |  | 0.00 |  | 12.35 | [8 empty] | 0.07 |  |  |  |  | 0.89
2017 |  |  |  | 2642.46 |  |  | 5780 |  |  |  | 468 | [10 empty] | 64.32 |  |  |  | 65.46 | [5 empty] | 64.46 |  |  | 65.98 |  |  |  | 0.30 |  | 0.19 | [8 empty] | 34.35 |  |  |  |  | 1.13
2018 |  |  |  | 3370.83 |  |  | 7305 |  |  |  | 468 | [10 empty] | 81.91 |  |  |  | 82.82 | [5 empty] | 82.22 |  |  | 83.39 |  |  |  | 2.36 |  | 2.00 | [8 empty] | 15.18 |  |  |  |  | 0.91
2019 |  |  |  | 3430.94 |  |  | 7462 |  |  |  | 468 | [10 empty] | 83.62 |  |  |  | 84.83 | [5 empty] | 83.69 |  |  | 85.18 |  |  |  | 0.18 |  | 2.68 | [8 empty] | 12.50 |  |  |  |  | 1.21
2020 |  |  |  | 3526.21 |  |  | 7620 |  |  |  | 468 | [10 empty] | 85.48 |  |  |  | 86.67 | [5 empty] | 85.78 |  |  | 86.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.33 |  |  |  |  | 1.19
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 54
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1164 | [14 empty] | 1115
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 76
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 74
Subtotal | [22 empty] | 1164 | [14 empty] | 1191 |  |  |  | 128 | [11 empty] | 5
Total | [22 empty] | 1164 | [14 empty] | 1324
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 13
16. |  |  | Steam generation systems | [34 empty] | 14
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [34 empty] | 13
Total | [37 empty] | 53

## DUKOVANY-2
2020 Operating Experience
CZ-5 | [8 empty] | DUKOVANY-2 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-01-01
Thermal power | [12 empty] | : |  |  | 1444 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-01-30
Gross electrical power | [12 empty] | : |  |  | 500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-03-21
Reference unit power (net) | [12 empty] | : |  |  | 471 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.26
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 297
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.3
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3346.78 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.8 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.25 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.21 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.83 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.95 %
Load Factor (LF) | [18 empty] | : | 80.89 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.58 %
Operating Factor (OF) | [18 empty] | : | 83.78 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1425 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 348.09 | 323.95 |  |  |  | 346.90 |  | 333.86 | [8 empty] | 343.88 |  |  | 326.29 | [6 empty] | 327.34 |  | 332.14 |  |  |  | 266.80 |  |  | 0.00 |  |  | 58.15 | [9 empty] | 339.40 |  |  | 3346.78
EAF [%] |  |  |  |  | 99.68 | 99.19 |  |  |  | 99.40 |  | 98.82 | [8 empty] | 98.38 |  |  | 96.64 | [6 empty] | 93.85 |  | 95.33 |  |  |  | 79.11 |  |  | 0.00 |  |  | 17.87 | [9 empty] | 96.85 |  |  | 81.25
UCF [%] |  |  |  |  | 99.81 | 99.69 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 97.88 |  | 100.00 |  |  |  | 81.96 |  |  | 0.00 |  |  | 17.87 | [9 empty] | 96.88 |  |  | 82.83
LF [%] |  |  |  |  | 99.33 | 98.82 |  |  |  | 98.99 |  | 98.45 | [8 empty] | 98.13 |  |  | 96.22 | [6 empty] | 93.41 |  | 94.78 |  |  |  | 78.67 |  |  | 0.00 |  |  | 17.15 | [9 empty] | 96.85 |  |  | 80.89
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.19 |  | 100.00 |  |  |  | 82.64 |  |  | 0.00 |  |  | 23.61 | [9 empty] | 100.00 |  |  | 83.78
FLR [%] |  |  |  |  | 0.09 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 2.12 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 14.00 | [9 empty] | 2.85 |  |  | 0.80
UCL [%] |  |  |  |  | 0.09 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 2.12 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 9.57 | [9 empty] | 2.85 |  |  | 1.21
PUF [%] |  |  |  |  | 0.10 | 0.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 18.04 |  |  | 100.00 |  |  | 72.56 | [9 empty] | 0.27 |  |  | 15.95
XUF [%] |  |  |  |  | 0.13 | 0.50 |  |  |  | 0.60 |  | 1.18 | [8 empty] | 1.62 |  |  | 3.36 | [6 empty] | 4.02 |  | 4.67 |  |  |  | 2.85 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.03 |  |  | 1.58
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 107357.78 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.69 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.56 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.35 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.49 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.16 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.32 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.92 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.09 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 2792.72 |  |  | 7615 |  |  |  | 408 | [10 empty] | 93.71 |  |  |  | 93.71 | [5 empty] | 93.32 |  |  | 96.65 |  |  |  | 0.83 |  | 0.78 | [8 empty] | 5.50 |  |  |  |  | 0.00
1987 |  |  |  | 2668.61 |  |  | 6997 |  |  |  | 408 | [10 empty] | 71.57 |  |  |  | 76.57 | [5 empty] | 74.67 |  |  | 79.87 |  |  |  | 0.21 |  | 0.16 | [8 empty] | 23.28 |  |  |  |  | 5.00
1988 |  |  |  | 2771.27 |  |  | 6963 |  |  |  | 408 | [10 empty] | 74.59 |  |  |  | 74.89 | [5 empty] | 77.33 |  |  | 79.27 |  |  |  | 5.14 |  | 4.06 | [8 empty] | 21.06 |  |  |  |  | 0.30
1989 |  |  |  | 3011.03 |  |  | 7713 |  |  |  | 408 | [10 empty] | 82.23 |  |  |  | 82.68 | [5 empty] | 84.25 |  |  | 88.05 |  |  |  | 1.71 |  | 1.43 | [8 empty] | 15.89 |  |  |  |  | 0.45
1990 |  |  |  | 2822.65 |  |  | 7566 |  |  |  | 408 | [10 empty] | 76.46 |  |  |  | 80.06 | [5 empty] | 78.98 |  |  | 86.37 |  |  |  | 5.38 |  | 4.55 | [8 empty] | 15.39 |  |  |  |  | 3.60
1991 |  |  |  | 2901.44 |  |  | 7600 |  |  |  | 408 | [10 empty] | 81.18 |  |  |  | 81.60 | [5 empty] | 81.18 |  |  | 86.76 |  |  |  | 3.41 |  | 2.88 | [8 empty] | 15.52 |  |  |  |  | 0.42
1992 |  |  |  | 2830.61 |  |  | 6551 |  |  |  | 408 | [10 empty] | 71.42 |  |  |  | 71.59 | [5 empty] | 78.98 |  |  | 74.58 |  |  |  | 0.74 |  | 0.53 | [8 empty] | 27.88 |  |  |  |  | 0.16
1993 |  |  |  | 3256.93 |  |  | 7496 |  |  |  | 440 | [10 empty] | 84.16 |  |  |  | 84.16 | [5 empty] | 84.50 |  |  | 85.57 |  |  |  | 1.34 |  | 1.14 | [8 empty] | 14.70 |  |  |  |  | 0.00
1994 |  |  |  | 3094.32 |  |  | 7315 |  |  |  | 440 | [10 empty] | 79.64 |  |  |  | 80.75 | [5 empty] | 80.28 |  |  | 83.50 |  |  |  | 6.29 |  | 5.42 | [8 empty] | 13.82 |  |  |  |  | 1.11
1995 |  |  |  | 3263.35 |  |  | 7720 |  |  |  | 440 | [10 empty] | 84.35 |  |  |  | 85.52 | [5 empty] | 84.67 |  |  | 88.13 |  |  |  | 3.54 |  | 3.13 | [8 empty] | 11.34 |  |  |  |  | 1.17
1996 |  |  |  | 2831.01 |  |  | 6917 |  |  |  | 412 | [10 empty] | 77.31 |  |  |  | 78.32 | [5 empty] | 78.23 |  |  | 78.75 |  |  |  | 1.82 |  | 1.45 | [8 empty] | 20.22 |  |  |  |  | 1.02
1997 |  |  |  | 3144.83 |  |  | 7179 |  |  |  | 440 | [10 empty] | 81.11 |  |  |  | 81.11 | [5 empty] | 81.59 |  |  | 81.95 |  |  |  | 0.89 |  | 0.73 | [8 empty] | 18.16 |  |  |  |  | 0.00
1998 |  |  |  | 3209.23 |  |  | 7803 |  |  |  | 412 | [10 empty] | 87.73 |  |  |  | 88.24 | [5 empty] | 88.92 |  |  | 89.08 |  |  |  | 0.63 |  | 0.56 | [8 empty] | 11.20 |  |  |  |  | 0.51
1999 |  |  |  | 3198.15 |  |  | 7812 |  |  |  | 412 | [10 empty] | 87.81 |  |  |  | 88.44 | [5 empty] | 88.61 |  |  | 89.18 |  |  |  | 2.04 |  | 1.84 | [8 empty] | 9.71 |  |  |  |  | 0.63
2000 |  |  |  | 2954.10 |  |  | 7223 |  |  |  | 412 | [10 empty] | 81.18 |  |  |  | 81.80 | [5 empty] | 81.63 |  |  | 82.23 |  |  |  | 0.78 |  | 0.64 | [8 empty] | 17.56 |  |  |  |  | 0.62
2001 |  |  |  | 3121.12 |  |  | 7646 |  |  |  | 412 | [10 empty] | 86.35 |  |  |  | 86.92 | [5 empty] | 86.48 |  |  | 87.28 |  |  |  | 0.71 |  | 0.62 | [8 empty] | 12.46 |  |  |  |  | 0.56
2002 |  |  |  | 3159.64 |  |  | 7716 |  |  |  | 412 | [10 empty] | 87.83 |  |  |  | 88.30 | [5 empty] | 87.55 |  |  | 88.08 |  |  |  | 0.40 |  | 0.35 | [8 empty] | 11.35 |  |  |  |  | 0.47
2003 |  |  |  | 3252.55 |  |  | 7939 |  |  |  | 412 | [10 empty] | 89.20 |  |  |  | 89.85 | [5 empty] | 90.12 |  |  | 90.63 |  |  |  | 1.01 |  | 0.92 | [8 empty] | 9.23 |  |  |  |  | 0.65
2004 |  |  |  | 3087.75 |  |  | 7439 |  |  |  | 412 | [10 empty] | 84.19 |  |  |  | 84.36 | [5 empty] | 85.31 |  |  | 84.68 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 15.48 |  |  |  |  | 0.16
2005 |  |  |  | 3313.22 |  |  | 8048 |  |  |  | 412 | [10 empty] | 90.75 |  |  |  | 91.25 | [5 empty] | 91.80 |  |  | 91.87 |  |  |  | 0.49 |  | 0.45 | [8 empty] | 8.30 |  |  |  |  | 0.50
2006 |  |  |  | 3294.69 |  |  | 8017 |  |  |  | 412 | [10 empty] | 90.59 |  |  |  | 91.15 | [5 empty] | 91.29 |  |  | 91.52 |  |  |  | 0.29 |  | 0.27 | [8 empty] | 8.58 |  |  |  |  | 0.56
2007 |  |  |  | 3274.74 |  |  | 7983 |  |  |  | 412 | [10 empty] | 90.12 |  |  |  | 90.88 | [5 empty] | 90.74 |  |  | 91.13 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 9.07 |  |  |  |  | 0.77
2008 |  |  |  | 3040.36 |  |  | 7228 |  |  |  | 427 | [10 empty] | 81.60 |  |  |  | 82.08 | [5 empty] | 82.01 |  |  | 82.29 |  |  |  | 0.49 |  | 0.40 | [8 empty] | 17.52 |  |  |  |  | 0.48
2009 |  |  |  | 3507.86 |  |  | 8209 |  |  |  | 427 | [10 empty] | 92.78 |  |  |  | 93.15 | [5 empty] | 93.78 |  |  | 93.71 |  |  |  | 0.41 |  | 0.61 | [8 empty] | 6.24 |  |  |  |  | 0.38
2010 |  |  |  | 3535.93 |  |  | 8250 |  |  |  | 427 | [10 empty] | 93.39 |  |  |  | 93.81 | [5 empty] | 94.53 |  |  | 94.18 |  |  |  | 0.00 |  | 0.06 | [8 empty] | 6.14 |  |  |  |  | 0.42
2011 |  |  |  | 3254.83 |  |  | 7676 |  |  |  | 427 | [10 empty] | 86.33 |  |  |  | 86.73 | [5 empty] | 87.04 |  |  | 87.65 |  |  |  | 0.66 |  | 1.04 | [8 empty] | 12.23 |  |  |  |  | 0.40
2012 |  |  |  | 3047.28 |  |  | 6918 |  |  |  | 471 | [10 empty] | 76.80 |  |  |  | 78.31 | [5 empty] | 76.63 |  |  | 78.76 |  |  |  | 0.82 |  | 0.65 | [8 empty] | 21.04 |  |  |  |  | 1.51
2013 |  |  |  | 3690.57 |  |  | 7984 |  |  |  | 471 | [10 empty] | 89.75 |  |  |  | 90.61 | [5 empty] | 89.45 |  |  | 91.14 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 9.28 |  |  |  |  | 0.85
2014 |  |  |  | 3672.64 |  |  | 8033 |  |  |  | 471 | [10 empty] | 89.25 |  |  |  | 91.15 | [5 empty] | 89.01 |  |  | 91.70 |  |  |  | 0.34 |  | 0.32 | [8 empty] | 8.54 |  |  |  |  | 1.90
2015 |  |  |  | 2495.87 |  |  | 5426 |  |  |  | 471 | [10 empty] | 60.74 |  |  |  | 61.63 | [5 empty] | 60.49 |  |  | 61.94 |  |  |  | 31.80 |  | 32.58 | [8 empty] | 5.79 |  |  |  |  | 0.89
2016 |  |  |  | 2361.31 |  |  | 5194 |  |  |  | 471 | [10 empty] | 57.39 |  |  |  | 58.80 | [5 empty] | 57.07 |  |  | 59.13 |  |  |  | 17.04 |  | 12.08 | [8 empty] | 29.12 |  |  |  |  | 1.41
2017 |  |  |  | 3089.36 |  |  | 6782 |  |  |  | 471 | [10 empty] | 75.20 |  |  |  | 76.32 | [5 empty] | 74.88 |  |  | 77.42 |  |  |  | 3.04 |  | 2.90 | [8 empty] | 20.78 |  |  |  |  | 1.12
2018 |  |  |  | 3384.99 |  |  | 7359 |  |  |  | 471 | [10 empty] | 82.35 |  |  |  | 83.55 | [5 empty] | 82.04 |  |  | 84.01 |  |  |  | 1.80 |  | 1.53 | [8 empty] | 14.92 |  |  |  |  | 1.20
2019 |  |  |  | 2636.32 |  |  | 5751 |  |  |  | 471 | [10 empty] | 64.14 |  |  |  | 65.15 | [5 empty] | 63.90 |  |  | 65.65 |  |  |  | 27.32 |  | 24.94 | [8 empty] | 9.91 |  |  |  |  | 1.01
2020 |  |  |  | 3346.78 |  |  | 7359 |  |  |  | 471 | [10 empty] | 81.25 |  |  |  | 82.83 | [5 empty] | 80.89 |  |  | 83.78 |  |  |  | 0.80 |  | 1.21 | [8 empty] | 15.95 |  |  |  |  | 1.58
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 13 | [14 empty] | 100
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1359 | [14 empty] | 998
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 68
E. |  | Testing of plant systems or components | [24 empty] | 48 | [14 empty] | 3
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 125
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [24 empty] | 6 | [14 empty] | 121
Subtotal | [22 empty] | 1359 |  |  |  | 67 | [10 empty] | 1191 |  |  |  | 224 | [11 empty] | 4
Total | [22 empty] | 1426 | [14 empty] | 1419
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 10
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [19 empty] | 48 | [14 empty] | 67
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [19 empty] | 13 | [14 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [19 empty] | 6 | [14 empty] | 6
Total | [22 empty] | 67 | [14 empty] | 110

## DUKOVANY-3
2020 Operating Experience
CZ-8 | [8 empty] | DUKOVANY-3 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-03-01
Thermal power | [12 empty] | : |  |  | 1444 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-11-14
Gross electrical power | [12 empty] | : |  |  | 500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-12-20
Reference unit power (net) | [12 empty] | : |  |  | 468 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.26
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 297
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.3
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2919.55 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 5.75 %
Energy Availability Factor (EAF) | [18 empty] | : | 70.76 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 16.72 %
Unit Capability Factor (UCF) | [18 empty] | : | 72.5 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.78 %
Load Factor (LF) | [18 empty] | : | 71.02 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.74 %
Operating Factor (OF) | [18 empty] | : | 73.45 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2332 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 267.23 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 333.37 |  |  | 327.22 | [6 empty] | 336.80 |  | 310.13 |  |  |  | 327.12 |  |  | 343.69 |  |  | 329.74 | [9 empty] | 344.24 |  |  | 2919.55
EAF [%] |  |  |  |  | 76.54 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 95.24 |  |  | 96.89 | [6 empty] | 96.57 |  | 89.06 |  |  |  | 96.77 |  |  | 98.11 |  |  | 97.46 | [9 empty] | 98.13 |  |  | 70.76
UCF [%] |  |  |  |  | 76.85 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 96.54 |  |  | 100.00 | [6 empty] | 100.00 |  | 92.68 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.51 | [9 empty] | 100.00 |  |  | 72.50
LF [%] |  |  |  |  | 76.75 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 95.74 |  |  | 97.11 | [6 empty] | 96.73 |  | 89.07 |  |  |  | 97.08 |  |  | 98.71 |  |  | 97.86 | [9 empty] | 98.87 |  |  | 71.02
OF [%] |  |  |  |  | 77.96 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 98.92 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 73.45
FLR [%] |  |  |  |  | 23.15 | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 7.32 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.75
UCL [%] |  |  |  |  | 23.15 | 23.28 |  |  |  | 48.39 |  | 100.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 7.32 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.72
PUF [%] |  |  |  |  | 0.00 | 76.72 |  |  |  | 51.61 |  | 0.00 | [8 empty] | 3.46 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.49 | [9 empty] | 0.00 |  |  | 10.78
XUF [%] |  |  |  |  | 0.31 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.30 |  |  | 3.11 | [6 empty] | 3.43 |  | 3.63 |  |  |  | 3.23 |  |  | 1.89 |  |  | 2.05 | [9 empty] | 1.87 |  |  | 1.74
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 106197.55 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.08 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.18 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.3 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.67 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.03 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.13 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.48 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.18 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 280.19 |  |  | 1356 |  |  |  | 408 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 3109.91 |  |  | 7644 |  |  |  | 408 | [10 empty] | 84.32 |  |  |  | 86.35 | [5 empty] | 87.01 |  |  | 87.26 |  |  |  | 0.46 |  | 0.40 | [8 empty] | 13.25 |  |  |  |  | 2.03
1988 |  |  |  | 2988.88 |  |  | 7672 |  |  |  | 408 | [10 empty] | 79.96 |  |  |  | 81.44 | [5 empty] | 83.40 |  |  | 87.34 |  |  |  | 0.40 |  | 0.33 | [8 empty] | 18.22 |  |  |  |  | 1.48
1989 |  |  |  | 2685.66 |  |  | 6678 |  |  |  | 408 | [10 empty] | 71.04 |  |  |  | 71.39 | [5 empty] | 75.14 |  |  | 76.23 |  |  |  | 1.53 |  | 1.11 | [8 empty] | 27.50 |  |  |  |  | 0.35
1990 |  |  |  | 2981.97 |  |  | 7763 |  |  |  | 408 | [10 empty] | 80.32 |  |  |  | 84.97 | [5 empty] | 83.43 |  |  | 88.62 |  |  |  | 2.80 |  | 2.44 | [8 empty] | 12.58 |  |  |  |  | 4.65
1991 |  |  |  | 2987.03 |  |  | 7784 |  |  |  | 408 | [10 empty] | 81.28 |  |  |  | 81.59 | [5 empty] | 83.57 |  |  | 88.86 |  |  |  | 6.94 |  | 6.09 | [8 empty] | 12.33 |  |  |  |  | 0.31
1992 |  |  |  | 2917.94 |  |  | 6678 |  |  |  | 408 | [10 empty] | 72.27 |  |  |  | 72.59 | [5 empty] | 81.42 |  |  | 76.02 |  |  |  | 8.86 |  | 7.06 | [8 empty] | 20.36 |  |  |  |  | 0.32
1993 |  |  |  | 3190.49 |  |  | 7259 |  |  |  | 452 | [10 empty] | 80.51 |  |  |  | 80.51 | [5 empty] | 80.58 |  |  | 82.87 |  |  |  | 3.63 |  | 3.03 | [8 empty] | 16.46 |  |  |  |  | 0.00
1994 |  |  |  | 3343.93 |  |  | 7870 |  |  |  | 452 | [10 empty] | 84.45 |  |  |  | 84.45 | [5 empty] | 84.45 |  |  | 89.84 |  |  |  | 13.39 |  | 13.05 | [8 empty] | 2.49 |  |  |  |  | 0.00
1995 |  |  |  | 2689.63 |  |  | 7788 |  |  |  | 452 | [10 empty] | 70.02 |  |  |  | 87.40 | [5 empty] | 67.93 |  |  | 88.90 |  |  |  | 1.70 |  | 1.51 | [8 empty] | 11.08 |  |  |  |  | 17.38
1996 |  |  |  | 2871.23 |  |  | 7114 |  |  |  | 412 | [10 empty] | 78.29 |  |  |  | 80.39 | [5 empty] | 79.34 |  |  | 80.99 |  |  |  | 2.57 |  | 2.12 | [8 empty] | 17.48 |  |  |  |  | 2.10
1997 |  |  |  | 2904.58 |  |  | 6774 |  |  |  | 440 | [10 empty] | 74.88 |  |  |  | 75.46 | [5 empty] | 75.36 |  |  | 77.33 |  |  |  | 2.29 |  | 1.77 | [8 empty] | 22.77 |  |  |  |  | 0.57
1998 |  |  |  | 3090.14 |  |  | 7564 |  |  |  | 412 | [10 empty] | 85.02 |  |  |  | 85.70 | [5 empty] | 85.62 |  |  | 86.35 |  |  |  | 3.01 |  | 2.66 | [8 empty] | 11.64 |  |  |  |  | 0.67
1999 |  |  |  | 3246.18 |  |  | 7849 |  |  |  | 412 | [10 empty] | 89.28 |  |  |  | 89.86 | [5 empty] | 89.94 |  |  | 89.60 |  |  |  | 0.39 |  | 0.35 | [8 empty] | 9.79 |  |  |  |  | 0.58
2000 |  |  |  | 3187.89 |  |  | 7776 |  |  |  | 412 | [10 empty] | 87.40 |  |  |  | 88.75 | [5 empty] | 88.09 |  |  | 88.52 |  |  |  | 0.42 |  | 0.37 | [8 empty] | 10.88 |  |  |  |  | 1.35
2001 |  |  |  | 3005.99 |  |  | 7309 |  |  |  | 412 | [10 empty] | 82.67 |  |  |  | 83.78 | [5 empty] | 83.29 |  |  | 83.44 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 16.16 |  |  |  |  | 1.12
2002 |  |  |  | 3259.39 |  |  | 7880 |  |  |  | 412 | [10 empty] | 89.56 |  |  |  | 89.89 | [5 empty] | 90.31 |  |  | 89.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.11 |  |  |  |  | 0.33
2003 |  |  |  | 3280.09 |  |  | 7934 |  |  |  | 412 | [10 empty] | 89.83 |  |  |  | 90.50 | [5 empty] | 90.88 |  |  | 90.57 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 9.47 |  |  |  |  | 0.68
2004 |  |  |  | 3302.47 |  |  | 7957 |  |  |  | 412 | [10 empty] | 90.17 |  |  |  | 90.27 | [5 empty] | 91.24 |  |  | 90.57 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 9.64 |  |  |  |  | 0.10
2005 |  |  |  | 2964.87 |  |  | 7034 |  |  |  | 427 | [10 empty] | 79.55 |  |  |  | 80.00 | [5 empty] | 80.19 |  |  | 80.30 |  |  |  | 0.85 |  | 0.68 | [8 empty] | 19.32 |  |  |  |  | 0.45
2006 |  |  |  | 3396.20 |  |  | 8004 |  |  |  | 427 | [10 empty] | 90.01 |  |  |  | 90.83 | [5 empty] | 90.79 |  |  | 91.37 |  |  |  | 0.41 |  | 0.38 | [8 empty] | 8.79 |  |  |  |  | 0.82
2007 |  |  |  | 3427.86 |  |  | 8068 |  |  |  | 427 | [10 empty] | 90.90 |  |  |  | 91.41 | [5 empty] | 91.64 |  |  | 92.10 |  |  |  | 0.49 |  | 0.45 | [8 empty] | 8.13 |  |  |  |  | 0.51
2008 |  |  |  | 3548.84 |  |  | 8273 |  |  |  | 427 | [10 empty] | 93.15 |  |  |  | 93.66 | [5 empty] | 94.62 |  |  | 94.18 |  |  |  | 0.02 |  | 0.37 | [8 empty] | 5.97 |  |  |  |  | 0.50
2009 |  |  |  | 2944.75 |  |  | 6688 |  |  |  | 468 | [10 empty] | 73.96 |  |  |  | 74.69 | [5 empty] | 73.96 |  |  | 76.35 |  |  |  | 0.99 |  | 0.80 | [8 empty] | 24.51 |  |  |  |  | 0.74
2010 |  |  |  | 3283.52 |  |  | 7146 |  |  |  | 468 | [10 empty] | 79.93 |  |  |  | 80.87 | [5 empty] | 80.09 |  |  | 81.58 |  |  |  | 1.99 |  | 3.01 | [8 empty] | 16.13 |  |  |  |  | 0.94
2011 |  |  |  | 3643.88 |  |  | 7940 |  |  |  | 468 | [10 empty] | 89.03 |  |  |  | 89.93 | [5 empty] | 88.88 |  |  | 90.64 |  |  |  | 0.60 |  | 1.10 | [8 empty] | 8.97 |  |  |  |  | 0.90
2012 |  |  |  | 3691.31 |  |  | 8040 |  |  |  | 468 | [10 empty] | 89.82 |  |  |  | 91.09 | [5 empty] | 89.79 |  |  | 91.53 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 8.84 |  |  |  |  | 1.28
2013 |  |  |  | 3542.84 |  |  | 7714 |  |  |  | 468 | [10 empty] | 86.36 |  |  |  | 87.37 | [5 empty] | 86.42 |  |  | 88.06 |  |  |  | 0.31 |  | 0.68 | [8 empty] | 11.95 |  |  |  |  | 1.01
2014 |  |  |  | 3500.03 |  |  | 7639 |  |  |  | 468 | [10 empty] | 85.15 |  |  |  | 86.61 | [5 empty] | 85.37 |  |  | 87.20 |  |  |  | 5.52 |  | 5.81 | [8 empty] | 7.59 |  |  |  |  | 1.46
2015 |  |  |  | 2673.32 |  |  | 5870 |  |  |  | 468 | [10 empty] | 65.48 |  |  |  | 66.71 | [5 empty] | 65.21 |  |  | 67.01 |  |  |  | 29.23 |  | 27.65 | [8 empty] | 5.64 |  |  |  |  | 1.23
2016 |  |  |  | 2336.18 |  |  | 5021 |  |  |  | 468 | [10 empty] | 56.57 |  |  |  | 56.75 | [5 empty] | 56.83 |  |  | 57.16 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 43.24 |  |  |  |  | 0.18
2017 |  |  |  | 2813.49 |  |  | 6072 |  |  |  | 468 | [10 empty] | 68.37 |  |  |  | 68.86 | [5 empty] | 68.63 |  |  | 69.32 |  |  |  | 0.07 |  | 1.68 | [8 empty] | 29.47 |  |  |  |  | 0.48
2018 |  |  |  | 3630.68 |  |  | 7947 |  |  |  | 468 | [10 empty] | 88.45 |  |  |  | 90.37 | [5 empty] | 88.56 |  |  | 90.72 |  |  |  | 3.09 |  | 2.88 | [8 empty] | 6.75 |  |  |  |  | 1.92
2019 |  |  |  | 3521.99 |  |  | 7691 |  |  |  | 468 | [10 empty] | 85.94 |  |  |  | 87.65 | [5 empty] | 85.91 |  |  | 87.80 |  |  |  | 0.04 |  | 3.86 | [8 empty] | 8.49 |  |  |  |  | 1.71
2020 |  |  |  | 2919.55 |  |  | 6452 |  |  |  | 468 | [10 empty] | 70.76 |  |  |  | 72.50 | [5 empty] | 71.02 |  |  | 73.45 |  |  |  | 5.75 |  | 16.72 | [8 empty] | 10.78 |  |  |  |  | 1.74
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 334 | [14 empty] | 110
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 918 | [14 empty] | 1034
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 36
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 111
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [24 empty] | 1080 | [14 empty] | 106
Z. |  | Other | [39 empty] | 5
Subtotal | [22 empty] | 918 |  |  |  | 1414 | [10 empty] | 1181 |  |  |  | 221 | [11 empty] | 3
Total | [22 empty] | 2332 | [14 empty] | 1405
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [19 empty] | 326 | [14 empty] | 45
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
33. |  |  | Circulating Water System | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 24
42. |  |  | Electrical Power Supply Systems | [19 empty] | 8 | [14 empty] | 3
Total | [22 empty] | 334 | [14 empty] | 114

## DUKOVANY-4
2020 Operating Experience
CZ-9 | [8 empty] | DUKOVANY-4 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-03-01
Thermal power | [12 empty] | : |  |  | 1444 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-06-11
Gross electrical power | [12 empty] | : |  |  | 500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-07-19
Reference unit power (net) | [12 empty] | : |  |  | 471 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.26
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 297
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.3
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3624.27 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.66 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.73 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.53 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.73 %
Load Factor (LF) | [18 empty] | : | 87.6 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.88 %
Operating Factor (OF) | [18 empty] | : | 88.8 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 984 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 204.87 |  |  |  | 352.56 |  | 339.03 | [8 empty] | 348.31 |  |  | 331.18 | [6 empty] | 341.06 |  | 339.74 |  |  |  | 332.93 |  |  | 349.62 |  |  | 336.33 | [9 empty] | 348.65 |  |  | 3624.27
EAF [%] |  |  |  |  | 0.00 | 62.61 |  |  |  | 99.99 |  | 99.62 | [8 empty] | 99.42 |  |  | 98.05 | [6 empty] | 97.68 |  | 97.40 |  |  |  | 98.56 |  |  | 99.62 |  |  | 99.36 | [9 empty] | 99.41 |  |  | 87.66
UCF [%] |  |  |  |  | 0.00 | 62.62 |  |  |  | 99.99 |  | 99.65 | [8 empty] | 100.00 |  |  | 99.96 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.53
LF [%] |  |  |  |  | 0.00 | 62.49 |  |  |  | 100.61 |  | 99.97 | [8 empty] | 99.40 |  |  | 97.66 | [6 empty] | 97.33 |  | 96.95 |  |  |  | 98.18 |  |  | 99.77 |  |  | 99.18 | [9 empty] | 99.49 |  |  | 87.60
OF [%] |  |  |  |  | 0.00 | 65.52 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.80
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 21.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.73
PUF [%] |  |  |  |  | 100.00 | 15.54 |  |  |  | 0.01 |  | 0.35 | [8 empty] | 0.00 |  |  | 0.04 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.73
XUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.02 | [8 empty] | 0.58 |  |  | 1.90 | [6 empty] | 2.32 |  | 2.60 |  |  |  | 1.44 |  |  | 0.38 |  |  | 0.64 | [9 empty] | 0.59 |  |  | 0.88
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 107399.27 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.19 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.54 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.02 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.43 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.68 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.89 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.08 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 1624.94 |  |  | 4643 |  |  |  | 408 | [10 empty] | 97.85 |  |  |  | 99.92 | [5 empty] | 90.09 |  |  | 94.34 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 0.00 |  |  |  |  | 2.08
1988 |  |  |  | 2764.01 |  |  | 7092 |  |  |  | 408 | [10 empty] | 73.78 |  |  |  | 74.45 | [5 empty] | 77.12 |  |  | 80.74 |  |  |  | 3.05 |  | 2.34 | [8 empty] | 23.20 |  |  |  |  | 0.67
1989 |  |  |  | 2984.55 |  |  | 7314 |  |  |  | 408 | [10 empty] | 80.41 |  |  |  | 80.81 | [5 empty] | 83.51 |  |  | 83.49 |  |  |  | 0.54 |  | 0.44 | [8 empty] | 18.74 |  |  |  |  | 0.41
1990 |  |  |  | 2995.30 |  |  | 7836 |  |  |  | 408 | [10 empty] | 79.96 |  |  |  | 82.75 | [5 empty] | 83.81 |  |  | 89.45 |  |  |  | 2.21 |  | 1.87 | [8 empty] | 15.38 |  |  |  |  | 2.79
1991 |  |  |  | 2671.99 |  |  | 7301 |  |  |  | 408 | [10 empty] | 77.93 |  |  |  | 78.03 | [5 empty] | 74.76 |  |  | 83.34 |  |  |  | 4.57 |  | 3.74 | [8 empty] | 18.23 |  |  |  |  | 0.10
1992 |  |  |  | 3328.41 |  |  | 7614 |  |  |  | 408 | [10 empty] | 83.66 |  |  |  | 84.48 | [5 empty] | 92.87 |  |  | 86.68 |  |  |  | 2.81 |  | 2.45 | [8 empty] | 13.07 |  |  |  |  | 0.82
1993 |  |  |  | 2939.81 |  |  | 6859 |  |  |  | 448 | [10 empty] | 62.05 |  |  |  | 62.05 | [5 empty] | 74.91 |  |  | 78.30 |  |  |  | 21.40 |  | 16.90 | [8 empty] | 21.05 |  |  |  |  | 0.00
1994 |  |  |  | 3259.81 |  |  | 7538 |  |  |  | 448 | [10 empty] | 83.06 |  |  |  | 84.51 | [5 empty] | 83.06 |  |  | 86.05 |  |  |  | 2.85 |  | 2.48 | [8 empty] | 13.01 |  |  |  |  | 1.45
1995 |  |  |  | 3311.14 |  |  | 7712 |  |  |  | 448 | [10 empty] | 85.35 |  |  |  | 85.46 | [5 empty] | 84.37 |  |  | 88.04 |  |  |  | 3.74 |  | 3.32 | [8 empty] | 11.23 |  |  |  |  | 0.11
1996 |  |  |  | 3202.13 |  |  | 7762 |  |  |  | 412 | [10 empty] | 87.13 |  |  |  | 88.19 | [5 empty] | 88.48 |  |  | 88.37 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 11.64 |  |  |  |  | 1.06
1997 |  |  |  | 3149.15 |  |  | 7202 |  |  |  | 440 | [10 empty] | 80.89 |  |  |  | 80.89 | [5 empty] | 81.70 |  |  | 82.21 |  |  |  | 0.50 |  | 0.41 | [8 empty] | 18.70 |  |  |  |  | 0.00
1998 |  |  |  | 3078.56 |  |  | 7536 |  |  |  | 412 | [10 empty] | 83.85 |  |  |  | 85.66 | [5 empty] | 85.30 |  |  | 86.03 |  |  |  | 0.28 |  | 0.24 | [8 empty] | 14.09 |  |  |  |  | 1.81
1999 |  |  |  | 3179.42 |  |  | 7792 |  |  |  | 412 | [10 empty] | 86.60 |  |  |  | 88.64 | [5 empty] | 88.09 |  |  | 88.95 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 11.20 |  |  |  |  | 2.04
2000 |  |  |  | 3234.52 |  |  | 7839 |  |  |  | 412 | [10 empty] | 88.12 |  |  |  | 89.46 | [5 empty] | 89.38 |  |  | 89.24 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 10.45 |  |  |  |  | 1.34
2001 |  |  |  | 3258.06 |  |  | 7946 |  |  |  | 412 | [10 empty] | 89.25 |  |  |  | 90.40 | [5 empty] | 90.27 |  |  | 90.71 |  |  |  | 0.24 |  | 0.21 | [8 empty] | 9.39 |  |  |  |  | 1.15
2002 |  |  |  | 2748.24 |  |  | 6745 |  |  |  | 412 | [10 empty] | 75.57 |  |  |  | 77.29 | [5 empty] | 76.15 |  |  | 77.00 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 22.68 |  |  |  |  | 1.72
2003 |  |  |  | 3309.80 |  |  | 8009 |  |  |  | 412 | [10 empty] | 90.66 |  |  |  | 91.35 | [5 empty] | 91.71 |  |  | 91.43 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 8.63 |  |  |  |  | 0.70
2004 |  |  |  | 3335.38 |  |  | 8029 |  |  |  | 412 | [10 empty] | 90.87 |  |  |  | 91.09 | [5 empty] | 92.16 |  |  | 91.40 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 8.85 |  |  |  |  | 0.23
2005 |  |  |  | 3267.00 |  |  | 8008 |  |  |  | 412 | [10 empty] | 89.62 |  |  |  | 90.27 | [5 empty] | 90.52 |  |  | 91.42 |  |  |  | 0.98 |  | 0.89 | [8 empty] | 8.83 |  |  |  |  | 0.66
2006 |  |  |  | 3159.49 |  |  | 7704 |  |  |  | 412 | [10 empty] | 86.92 |  |  |  | 87.79 | [5 empty] | 87.54 |  |  | 87.95 |  |  |  | 0.16 |  | 0.14 | [8 empty] | 12.07 |  |  |  |  | 0.88
2007 |  |  |  | 3318.99 |  |  | 7854 |  |  |  | 427 | [10 empty] | 88.05 |  |  |  | 88.70 | [5 empty] | 88.73 |  |  | 89.66 |  |  |  | 0.37 |  | 0.33 | [8 empty] | 10.96 |  |  |  |  | 0.65
2008 |  |  |  | 3438.67 |  |  | 8010 |  |  |  | 427 | [10 empty] | 90.35 |  |  |  | 90.74 | [5 empty] | 91.68 |  |  | 91.19 |  |  |  | 0.62 |  | 0.56 | [8 empty] | 8.70 |  |  |  |  | 0.39
2009 |  |  |  | 3100.50 |  |  | 7247 |  |  |  | 427 | [10 empty] | 81.82 |  |  |  | 81.99 | [5 empty] | 82.89 |  |  | 82.73 |  |  |  | 0.31 |  | 0.25 | [8 empty] | 17.75 |  |  |  |  | 0.18
2010 |  |  |  | 2895.11 |  |  | 6846 |  |  |  | 427 | [10 empty] | 76.74 |  |  |  | 77.31 | [5 empty] | 77.40 |  |  | 78.15 |  |  |  | 0.32 |  | 0.24 | [8 empty] | 22.44 |  |  |  |  | 0.57
2011 |  |  |  | 3630.71 |  |  | 8001 |  |  |  | 471 | [10 empty] | 88.78 |  |  |  | 89.87 | [5 empty] | 88.00 |  |  | 91.34 |  |  |  | 4.28 |  | 4.02 | [8 empty] | 6.11 |  |  |  |  | 1.09
2012 |  |  |  | 3620.96 |  |  | 7850 |  |  |  | 471 | [10 empty] | 87.65 |  |  |  | 88.75 | [5 empty] | 87.52 |  |  | 89.37 |  |  |  | 0.14 |  | 2.37 | [8 empty] | 8.87 |  |  |  |  | 1.11
2013 |  |  |  | 3727.91 |  |  | 8009 |  |  |  | 471 | [10 empty] | 90.45 |  |  |  | 91.36 | [5 empty] | 90.35 |  |  | 91.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.63 |  |  |  |  | 0.91
2014 |  |  |  | 3494.80 |  |  | 7591 |  |  |  | 471 | [10 empty] | 84.79 |  |  |  | 86.06 | [5 empty] | 84.70 |  |  | 86.66 |  |  |  | 4.68 |  | 4.23 | [8 empty] | 9.71 |  |  |  |  | 1.27
2015 |  |  |  | 4004.79 |  |  | 8623 |  |  |  | 471 | [10 empty] | 97.05 |  |  |  | 98.00 | [5 empty] | 97.06 |  |  | 98.44 |  |  |  | 1.89 |  | 1.89 | [8 empty] | 0.11 |  |  |  |  | 0.96
2016 |  |  |  | 2936.27 |  |  | 6423 |  |  |  | 471 | [10 empty] | 71.26 |  |  |  | 72.43 | [5 empty] | 70.97 |  |  | 73.12 |  |  |  | 0.44 |  | 0.32 | [8 empty] | 27.25 |  |  |  |  | 1.17
2017 |  |  |  | 2576.88 |  |  | 5542 |  |  |  | 471 | [10 empty] | 62.47 |  |  |  | 62.75 | [5 empty] | 62.46 |  |  | 63.26 |  |  |  | 6.37 |  | 4.27 | [8 empty] | 32.98 |  |  |  |  | 0.28
2018 |  |  |  | 2979.28 |  |  | 6498 |  |  |  | 471 | [10 empty] | 72.22 |  |  |  | 72.99 | [5 empty] | 72.22 |  |  | 74.19 |  |  |  | 10.97 |  | 8.99 | [8 empty] | 18.01 |  |  |  |  | 0.77
2019 |  |  |  | 4009.33 |  |  | 8576 |  |  |  | 471 | [10 empty] | 96.97 |  |  |  | 97.73 | [5 empty] | 97.17 |  |  | 97.90 |  |  |  | 0.21 |  | 0.20 | [8 empty] | 2.07 |  |  |  |  | 0.76
2020 |  |  |  | 3624.27 |  |  | 7800 |  |  |  | 471 | [10 empty] | 87.66 |  |  |  | 88.53 | [5 empty] | 87.60 |  |  | 88.80 |  |  |  | 0.00 |  | 1.73 | [8 empty] | 9.73 |  |  |  |  | 0.88
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 72
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 832 | [14 empty] | 971
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 56
E. |  | Testing of plant systems or components | [24 empty] | 152 | [14 empty] | 5
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 71
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 7
Subtotal | [22 empty] | 832 |  |  |  | 152 | [10 empty] | 1098 |  |  |  | 84 | [11 empty] | 7
Total | [22 empty] | 984 | [14 empty] | 1189
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
16. |  |  | Steam generation systems | [19 empty] | 152 | [14 empty] | 18
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
33. |  |  | Circulating Water System | [34 empty] | 11
35. |  |  | All other I&C Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 152 | [14 empty] | 78

## TEMELIN-1
2020 Operating Experience
CZ-23 | [8 empty] | TEMELIN-1 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1987-02-01
Thermal power | [12 empty] | : |  |  | 3120 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2000-12-21
Gross electrical power | [12 empty] | : |  |  | 1082 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-06-10
Reference unit power (net) | [12 empty] | : |  |  | 1027 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 20 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.6 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25.7 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.2
| Active core height/length [m] | [13 empty] | : |  |  | 3.63 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7294.1 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.08 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.89 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.58 %
Unit Capability Factor (UCF) | [18 empty] | : | 81.08 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.34 %
Load Factor (LF) | [18 empty] | : | 80.86 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.19 %
Operating Factor (OF) | [18 empty] | : | 81.72 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1606 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 105 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 675.43 | 712.00 |  |  |  | 315.40 |  | 0.00 | [8 empty] | 374.91 |  |  | 734.26 | [6 empty] | 756.81 |  | 755.71 |  |  |  | 695.10 |  |  | 760.80 |  |  | 743.32 | [9 empty] | 770.35 |  |  | 7294.10
EAF [%] |  |  |  |  | 88.39 | 99.45 |  |  |  | 41.45 |  | 0.00 | [8 empty] | 50.14 |  |  | 99.55 | [6 empty] | 99.32 |  | 99.17 |  |  |  | 94.17 |  |  | 99.34 |  |  | 99.98 | [9 empty] | 100.00 |  |  | 80.89
UCF [%] |  |  |  |  | 88.39 | 99.45 |  |  |  | 41.45 |  | 0.00 | [8 empty] | 50.15 |  |  | 99.95 | [6 empty] | 99.97 |  | 99.91 |  |  |  | 94.57 |  |  | 99.36 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.08
LF [%] |  |  |  |  | 88.40 | 99.61 |  |  |  | 41.28 |  | 0.00 | [8 empty] | 49.07 |  |  | 99.30 | [6 empty] | 99.05 |  | 98.90 |  |  |  | 94.00 |  |  | 99.57 |  |  | 100.52 | [9 empty] | 100.82 |  |  | 80.86
OF [%] |  |  |  |  | 89.25 | 100.00 |  |  |  | 41.53 |  | 0.00 | [8 empty] | 54.84 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 95.14 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.72
FLR [%] |  |  |  |  | 11.49 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 20.69 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 5.42 |  |  | 0.63 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.08
UCL [%] |  |  |  |  | 11.48 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.08 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 5.42 |  |  | 0.63 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.58
PUF [%] |  |  |  |  | 0.13 | 0.55 |  |  |  | 58.55 |  | 100.00 | [8 empty] | 36.77 |  |  | 0.05 | [6 empty] | 0.03 |  | 0.09 |  |  |  | 0.01 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.34
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.40 | [6 empty] | 0.65 |  | 0.74 |  |  |  | 0.40 |  |  | 0.02 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 0.19
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 123249.1 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.59 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.32 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.49 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.6 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.92 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.58 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.28 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.09 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 5147.87 |  |  | 5961 |  |  |  | 930 | [10 empty] | 76.06 |  |  |  | 76.06 | [5 empty] | 76.96 |  |  | 82.42 |  |  |  | 5.17 |  | 4.15 | [8 empty] | 19.80 |  |  |  |  | 0.00
2003 |  |  |  | 5455.32 |  |  | 5861 |  |  |  | 912 | [10 empty] | 65.30 |  |  |  | 65.30 | [5 empty] | 68.28 |  |  | 66.91 |  |  |  | 4.15 |  | 4.71 | [8 empty] | 29.99 |  |  |  |  | 0.00
2004 |  |  |  | 5715.82 |  |  | 6029 |  |  |  | 950 | [10 empty] | 68.01 |  |  |  | 68.09 | [5 empty] | 68.50 |  |  | 68.64 |  |  |  | 7.98 |  | 6.07 | [8 empty] | 25.84 |  |  |  |  | 0.08
2005 |  |  |  | 5443.97 |  |  | 5846 |  |  |  | 950 | [10 empty] | 66.30 |  |  |  | 66.33 | [5 empty] | 66.35 |  |  | 66.74 |  |  |  | 16.34 |  | 20.25 | [8 empty] | 13.42 |  |  |  |  | 0.03
2006 |  |  |  | 6124.86 |  |  | 6731 |  |  |  | 930 | [10 empty] | 75.68 |  |  |  | 75.69 | [5 empty] | 75.18 |  |  | 76.84 |  |  |  | 4.39 |  | 3.48 | [8 empty] | 20.83 |  |  |  |  | 0.01
2007 |  |  |  | 4901.35 |  |  | 5282 |  |  |  | 963 | [10 empty] | 60.02 |  |  |  | 60.02 | [5 empty] | 59.63 |  |  | 60.30 |  |  |  | 4.05 |  | 8.54 | [8 empty] | 31.44 |  |  |  |  | 0.01
2008 |  |  |  | 4526.45 |  |  | 4745 |  |  |  | 963 | [10 empty] | 53.50 |  |  |  | 53.57 | [5 empty] | 53.51 |  |  | 54.02 |  |  |  | 11.75 |  | 25.06 | [8 empty] | 21.36 |  |  |  |  | 0.07
2009 |  |  |  | 6229.78 |  |  | 6527 |  |  |  | 963 | [10 empty] | 73.81 |  |  |  | 73.88 | [5 empty] | 73.85 |  |  | 74.51 |  |  |  | 4.22 |  | 6.00 | [8 empty] | 20.12 |  |  |  |  | 0.07
2010 |  |  |  | 6305.63 |  |  | 6594 |  |  |  | 963 | [10 empty] | 74.50 |  |  |  | 74.83 | [5 empty] | 74.75 |  |  | 75.27 |  |  |  | 0.65 |  | 6.49 | [8 empty] | 18.68 |  |  |  |  | 0.33
2011 |  |  |  | 6915.59 |  |  | 7205 |  |  |  | 963 | [10 empty] | 81.80 |  |  |  | 81.82 | [5 empty] | 81.98 |  |  | 82.25 |  |  |  | 0.53 |  | 0.44 | [8 empty] | 17.75 |  |  |  |  | 0.02
2012 |  |  |  | 7159.77 |  |  | 7515 |  |  |  | 963 | [10 empty] | 84.68 |  |  |  | 84.99 | [5 empty] | 84.64 |  |  | 85.55 |  |  |  | 1.59 |  | 1.38 | [8 empty] | 13.63 |  |  |  |  | 0.31
2013 |  |  |  | 7018.65 |  |  | 7252 |  |  |  | 1003 | [10 empty] | 82.22 |  |  |  | 82.26 | [5 empty] | 82.06 |  |  | 82.79 |  |  |  | 1.18 |  | 4.07 | [8 empty] | 13.68 |  |  |  |  | 0.04
2014 |  |  |  | 7194.59 |  |  | 7092 |  |  |  | 1023 | [10 empty] | 80.85 |  |  |  | 80.85 | [5 empty] | 81.34 |  |  | 80.96 |  |  |  | 0.02 |  | 0.10 | [8 empty] | 19.04 |  |  |  |  | 0.01
2015 |  |  |  | 7581.24 |  |  | 7400 |  |  |  | 1026 | [10 empty] | 83.88 |  |  |  | 84.22 | [5 empty] | 84.35 |  |  | 84.47 |  |  |  | 3.28 |  | 2.86 | [8 empty] | 12.92 |  |  |  |  | 0.34
2016 |  |  |  | 5786.94 |  |  | 5868 |  |  |  | 1026 | [10 empty] | 64.07 |  |  |  | 66.48 | [5 empty] | 64.21 |  |  | 66.80 |  |  |  | 0.59 |  | 5.72 | [8 empty] | 27.79 |  |  |  |  | 2.42
2017 |  |  |  | 8410.14 |  |  | 8205 |  |  |  | 1026 | [10 empty] | 93.27 |  |  |  | 93.60 | [5 empty] | 93.57 |  |  | 93.66 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 6.37 |  |  |  |  | 0.33
2018 |  |  |  | 7487.60 |  |  | 7321 |  |  |  | 1027 | [10 empty] | 83.11 |  |  |  | 83.34 | [5 empty] | 83.24 |  |  | 83.57 |  |  |  | 0.11 |  | 0.09 | [8 empty] | 16.57 |  |  |  |  | 0.23
2019 |  |  |  | 7169.40 |  |  | 7088 |  |  |  | 1027 | [10 empty] | 79.65 |  |  |  | 80.21 | [5 empty] | 79.69 |  |  | 80.91 |  |  |  | 4.17 |  | 3.49 | [8 empty] | 16.30 |  |  |  |  | 0.56
2020 |  |  |  | 7294.10 |  |  | 7178 |  |  |  | 1027 | [10 empty] | 80.89 |  |  |  | 81.08 | [5 empty] | 80.86 |  |  | 81.72 |  |  |  | 3.08 |  | 2.58 | [8 empty] | 16.34 |  |  |  |  | 0.19
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2002 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 195 | [14 empty] | 460
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1411 | [14 empty] | 1384
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 57
E. |  | Testing of plant systems or components | [35 empty] | 34 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 131
L. |  | Human factor related | [39 empty] | 83
M. |  | Governmental requirements or court decisions | [39 empty] | 36
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 72
Subtotal | [22 empty] | 1411 |  |  |  | 195 | [10 empty] | 1678 |  |  |  | 580
Total | [22 empty] | 1606 | [14 empty] | 2258
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2002 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 68
12. |  |  | Reactor I&C Systems | [19 empty] | 80 | [14 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 77
16. |  |  | Steam generation systems | [34 empty] | 12
31. |  |  | Turbine and auxiliaries | [19 empty] | 55 | [14 empty] | 190
32. |  |  | Feedwater and Main Steam System | [34 empty] | 32
33. |  |  | Circulating Water System | [34 empty] | 3
41. |  |  | Main Generator Systems | [19 empty] | 60 | [14 empty] | 56
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 195 | [14 empty] | 456

## TEMELIN-2
2020 Operating Experience
CZ-24 | [8 empty] | TEMELIN-2 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1987-02-01
Thermal power | [12 empty] | : |  |  | 3120 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-12-29
Gross electrical power | [12 empty] | : |  |  | 1082 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2003-04-18
Reference unit power (net) | [12 empty] | : |  |  | 1029 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 18 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.6 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25.7 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.2
| Active core height/length [m] | [13 empty] | : |  |  | 3.63 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7660.96 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.98 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.19 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.03 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.78 %
Load Factor (LF) | [18 empty] | : | 84.89 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.05 %
Operating Factor (OF) | [18 empty] | : | 84.22 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1386 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 776.02 | 725.31 |  |  |  | 771.90 |  | 743.76 | [8 empty] | 760.78 |  |  | 287.89 | [6 empty] | 0.00 |  | 534.84 |  |  |  | 746.44 |  |  | 778.36 |  |  | 754.72 | [9 empty] | 780.94 |  |  | 7660.96
EAF [%] |  |  |  |  | 99.95 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.84 |  |  | 38.91 | [6 empty] | 0.00 |  | 70.14 |  |  |  | 99.98 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.98
UCF [%] |  |  |  |  | 99.95 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.84 |  |  | 39.46 | [6 empty] | 0.00 |  | 70.18 |  |  |  | 99.99 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.03
LF [%] |  |  |  |  | 101.56 | 101.47 |  |  |  | 101.02 |  | 100.58 | [8 empty] | 99.57 |  |  | 38.93 | [6 empty] | 0.00 |  | 70.00 |  |  |  | 100.95 |  |  | 101.87 |  |  | 101.87 | [9 empty] | 102.01 |  |  | 84.89
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 39.58 | [6 empty] | 0.00 |  | 72.18 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.22
FLR [%] |  |  |  |  | 0.04 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.14 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.02 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
UCL [%] |  |  |  |  | 0.04 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.14 |  |  | 0.00 | [6 empty] | 0.00 |  | 2.03 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.19
PUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  | 60.54 | [6 empty] | 100.00 |  | 27.79 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.78
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.55 | [6 empty] | 0.00 |  | 0.04 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 119174.96 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.94 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.46 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.45 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.68 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.87 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.93 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.22 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.31 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2003 |  |  |  | 6033.03 |  |  | 6934 |  |  |  | 930 | [10 empty] | 84.23 |  |  |  | 84.23 | [5 empty] | 86.59 |  |  | 86.52 |  |  |  | 15.60 |  | 15.57 | [8 empty] | 0.21 |  |  |  |  | 0.00
2004 |  |  |  | 6340.09 |  |  | 6678 |  |  |  | 950 | [10 empty] | 75.22 |  |  |  | 75.22 | [5 empty] | 75.98 |  |  | 76.02 |  |  |  | 8.49 |  | 6.98 | [8 empty] | 17.80 |  |  |  |  | 0.00
2005 |  |  |  | 4941.36 |  |  | 6135 |  |  |  | 780 | [10 empty] | 65.10 |  |  |  | 65.25 | [5 empty] | 65.27 |  |  | 70.03 |  |  |  | 6.34 |  | 10.21 | [8 empty] | 24.54 |  |  |  |  | 0.15
2006 |  |  |  | 5251.85 |  |  | 5765 |  |  |  | 930 | [10 empty] | 65.28 |  |  |  | 65.82 | [5 empty] | 65.36 |  |  | 65.81 |  |  |  | 3.01 |  | 8.85 | [8 empty] | 25.33 |  |  |  |  | 0.54
2007 |  |  |  | 6745.10 |  |  | 7051 |  |  |  | 963 | [10 empty] | 79.93 |  |  |  | 80.05 | [5 empty] | 80.50 |  |  | 80.49 |  |  |  | 0.85 |  | 2.44 | [8 empty] | 17.50 |  |  |  |  | 0.12
2008 |  |  |  | 6978.75 |  |  | 7420 |  |  |  | 963 | [10 empty] | 82.65 |  |  |  | 83.23 | [5 empty] | 82.50 |  |  | 84.47 |  |  |  | 3.05 |  | 2.62 | [8 empty] | 14.15 |  |  |  |  | 0.58
2009 |  |  |  | 6363.18 |  |  | 6756 |  |  |  | 963 | [10 empty] | 75.39 |  |  |  | 76.80 | [5 empty] | 75.43 |  |  | 77.12 |  |  |  | 0.25 |  | 0.19 | [8 empty] | 23.00 |  |  |  |  | 1.41
2010 |  |  |  | 6847.34 |  |  | 7135 |  |  |  | 963 | [10 empty] | 80.95 |  |  |  | 81.10 | [5 empty] | 81.18 |  |  | 81.46 |  |  |  | 1.55 |  | 2.78 | [8 empty] | 16.12 |  |  |  |  | 0.15
2011 |  |  |  | 6311.62 |  |  | 6589 |  |  |  | 963 | [10 empty] | 74.77 |  |  |  | 74.85 | [5 empty] | 74.82 |  |  | 75.22 |  |  |  | 3.32 |  | 9.69 | [8 empty] | 15.46 |  |  |  |  | 0.08
2012 |  |  |  | 7349.91 |  |  | 7656 |  |  |  | 963 | [10 empty] | 86.84 |  |  |  | 86.91 | [5 empty] | 86.89 |  |  | 87.16 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 13.05 |  |  |  |  | 0.06
2013 |  |  |  | 7246.82 |  |  | 7448 |  |  |  | 1003 | [10 empty] | 84.48 |  |  |  | 84.79 | [5 empty] | 84.43 |  |  | 85.02 |  |  |  | 1.06 |  | 1.92 | [8 empty] | 13.29 |  |  |  |  | 0.31
2014 |  |  |  | 6989.25 |  |  | 6980 |  |  |  | 1003 | [10 empty] | 79.32 |  |  |  | 79.33 | [5 empty] | 79.55 |  |  | 79.68 |  |  |  | 8.27 |  | 7.15 | [8 empty] | 13.52 |  |  |  |  | 0.01
2015 |  |  |  | 5926.47 |  |  | 5813 |  |  |  | 1026 | [10 empty] | 66.23 |  |  |  | 66.24 | [5 empty] | 66.84 |  |  | 66.36 |  |  |  | 7.35 |  | 17.25 | [8 empty] | 16.51 |  |  |  |  | 0.00
2016 |  |  |  | 5730.12 |  |  | 5617 |  |  |  | 1026 | [10 empty] | 62.87 |  |  |  | 62.87 | [5 empty] | 63.58 |  |  | 63.95 |  |  |  | 14.72 |  | 14.93 | [8 empty] | 22.20 |  |  |  |  | 0.00
2017 |  |  |  | 7252.35 |  |  | 7024 |  |  |  | 1026 | [10 empty] | 79.85 |  |  |  | 79.87 | [5 empty] | 80.69 |  |  | 80.18 |  |  |  | 0.08 |  | 0.06 | [8 empty] | 20.07 |  |  |  |  | 0.01
2018 |  |  |  | 7402.41 |  |  | 7208 |  |  |  | 1027 | [10 empty] | 81.65 |  |  |  | 82.00 | [5 empty] | 82.34 |  |  | 82.29 |  |  |  | 1.30 |  | 1.37 | [8 empty] | 16.63 |  |  |  |  | 0.35
2019 |  |  |  | 7813.14 |  |  | 7555 |  |  |  | 1027 | [10 empty] | 85.98 |  |  |  | 86.04 | [5 empty] | 86.85 |  |  | 86.24 |  |  |  | 0.16 |  | 0.13 | [8 empty] | 13.82 |  |  |  |  | 0.06
2020 |  |  |  | 7660.96 |  |  | 7398 |  |  |  | 1029 | [10 empty] | 83.98 |  |  |  | 84.03 | [5 empty] | 84.89 |  |  | 84.22 |  |  |  | 0.02 |  | 0.19 | [8 empty] | 15.78 |  |  |  |  | 0.05
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2003 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 15 | [14 empty] | 435
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1371 | [14 empty] | 1290
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 51
E. |  | Testing of plant systems or components | [35 empty] | 23 |  |  |  | 3
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 109
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 53
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Subtotal | [22 empty] | 1371 |  |  |  | 15 | [10 empty] | 1473 |  |  |  | 491 | [11 empty] | 1
Total | [22 empty] | 1386 | [14 empty] | 1965
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2003 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 93
12. |  |  | Reactor I&C Systems | [34 empty] | 11
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 16
15. |  |  | Reactor Cooling Systems | [34 empty] | 20
16. |  |  | Steam generation systems | [34 empty] | 77
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 110
32. |  |  | Feedwater and Main Steam System | [19 empty] | 15 | [14 empty] | 24
33. |  |  | Circulating Water System | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 33
41. |  |  | Main Generator Systems | [34 empty] | 35
42. |  |  | Electrical Power Supply Systems | [34 empty] | 27
Total | [22 empty] | 15 | [14 empty] | 456