## LOVIISA-1
2020 Operating Experience
FI-1 | [8 empty] | LOVIISA-1 | [26 empty] | FINLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FORTUMPH (FORTUM POWER AND HEAT OY (former IVO))
Owner | [7 empty] | : | FORTUMPH (FORTUM POWER AND HEAT OY (former IVO))
Reactor Supplier | [7 empty] | : | AEE (ATOMENERGOEXPORT)
Turbine Supplier | [7 empty] | : | AEE (ATOMENERGOEXPORT)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-05-01
Thermal power | [12 empty] | : |  |  | 1500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-02-08
Gross electrical power | [12 empty] | : |  |  | 531 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-05-09
Reference unit power (net) | [12 empty] | : |  |  | 507 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.25
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 301
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.07
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.73 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.42 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 313 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3709.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.08 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.47 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.57 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.86 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.56 %
Load Factor (LF) | [18 empty] | : | 83.29 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.39 %
Operating Factor (OF) | [18 empty] | : | 85.19 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1301 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 375.93 | 351.88 |  |  |  | 375.62 |  | 363.11 | [8 empty] | 372.88 |  |  | 353.27 | [6 empty] | 367.33 |  | 314.71 |  |  |  | 0.00 |  |  | 100.33 |  |  | 360.02 | [9 empty] | 374.02 |  |  | 3709.12
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.96 |  | 100.00 | [8 empty] | 98.85 |  |  | 96.78 | [6 empty] | 97.38 |  | 83.43 |  |  |  | 0.00 |  |  | 26.46 |  |  | 98.62 | [9 empty] | 99.98 |  |  | 83.47
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.96 |  | 100.00 | [8 empty] | 99.70 |  |  | 100.00 | [6 empty] | 99.85 |  | 91.43 |  |  |  | 0.00 |  |  | 27.14 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 84.86
LF [%] |  |  |  |  | 99.66 | 99.72 |  |  |  | 99.58 |  | 99.47 | [8 empty] | 98.85 |  |  | 96.78 | [6 empty] | 97.38 |  | 83.43 |  |  |  | 0.00 |  |  | 26.60 |  |  | 98.62 | [9 empty] | 99.16 |  |  | 83.29
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 92.07 |  |  |  | 0.00 |  |  | 29.97 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.19
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.04 |  | 0.00 | [8 empty] | 0.30 |  |  | 0.00 | [6 empty] | 0.15 |  | 0.33 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 0.08
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.04 |  | 0.00 | [8 empty] | 0.30 |  |  | 0.00 | [6 empty] | 0.15 |  | 0.31 |  |  |  | 0.00 |  |  | 29.57 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 2.57
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 8.26 |  |  |  | 100.00 |  |  | 43.29 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.56
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.85 |  |  | 3.22 | [6 empty] | 2.47 |  | 8.00 |  |  |  | 0.00 |  |  | 0.68 |  |  | 1.38 | [9 empty] | 0.00 |  |  | 1.39
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 157499.83 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.51 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.88 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.46 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.84 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.64 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.59 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.67 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 2505.50 |  |  | 7192 |  |  |  | 431 | [10 empty] | 83.79 |  |  |  | 83.79 | [5 empty] | 83.79 |  |  | 95.09 |  |  |  | 12.65 |  | 12.13 | [8 empty] | 4.08 |  |  |  |  | 0.00
1978 |  |  |  | 2975.80 |  |  | 7531 |  |  |  | 430 | [10 empty] | 78.93 |  |  |  | 78.93 | [5 empty] | 79.00 |  |  | 85.97 |  |  |  | 9.27 |  | 8.06 | [8 empty] | 13.01 |  |  |  |  | 0.00
1979 |  |  |  | 2901.70 |  |  | 7404 |  |  |  | 405 | [10 empty] | 81.76 |  |  |  | 81.76 | [5 empty] | 81.79 |  |  | 84.52 |  |  |  | 9.09 |  | 8.17 | [8 empty] | 10.07 |  |  |  |  | 0.00
1980 |  |  |  | 1407.80 |  |  | 3482 |  |  |  | 445 | [10 empty] | 36.65 |  |  |  | 36.65 | [5 empty] | 36.02 |  |  | 39.64 |  |  |  | 55.36 |  | 45.45 | [8 empty] | 17.90 |  |  |  |  | 0.00
1981 |  |  |  | 3105.10 |  |  | 7642 |  |  |  | 440 | [10 empty] | 81.94 |  |  |  | 81.94 | [5 empty] | 80.56 |  |  | 87.24 |  |  |  | 2.74 |  | 2.31 | [8 empty] | 15.75 |  |  |  |  | 0.00
1982 |  |  |  | 3245.40 |  |  | 7576 |  |  |  | 440 | [10 empty] | 84.19 |  |  |  | 84.19 | [5 empty] | 84.20 |  |  | 86.48 |  |  |  | 4.46 |  | 3.93 | [8 empty] | 11.88 |  |  |  |  | 0.00
1983 |  |  |  | 3337.40 |  |  | 7982 |  |  |  | 445 | [10 empty] | 86.68 |  |  |  | 86.68 | [5 empty] | 85.61 |  |  | 91.12 |  |  |  | 3.01 |  | 2.69 | [8 empty] | 10.63 |  |  |  |  | 0.00
1984 |  |  |  | 3343.86 |  |  | 7653 |  |  |  | 445 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 85.55 |  |  | 87.12 |  |  |  | 0.31 |  | 0.27 | [8 empty] | 13.94 |  |  |  |  | 0.00
1985 |  |  |  | 3599.97 |  |  | 8248 |  |  |  | 440 | [10 empty] | 92.54 |  |  |  | 92.54 | [5 empty] | 93.40 |  |  | 94.16 |  |  |  | 0.45 |  | 0.42 | [8 empty] | 7.05 |  |  |  |  | 0.00
1986 |  |  |  | 3522.37 |  |  | 8093 |  |  |  | 445 | [10 empty] | 91.10 |  |  |  | 91.10 | [5 empty] | 90.36 |  |  | 92.39 |  |  |  | 2.67 |  | 2.49 | [8 empty] | 6.40 |  |  |  |  | 0.00
1987 |  |  |  | 3600.36 |  |  | 8257 |  |  |  | 445 | [10 empty] | 94.55 |  |  |  | 94.55 | [5 empty] | 92.36 |  |  | 94.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.45 |  |  |  |  | 0.00
1988 |  |  |  | 3354.63 |  |  | 7678 |  |  |  | 445 | [10 empty] | 87.03 |  |  |  | 87.03 | [5 empty] | 85.82 |  |  | 87.41 |  |  |  | 1.21 |  | 1.07 | [8 empty] | 11.90 |  |  |  |  | 0.00
1989 |  |  |  | 3575.75 |  |  | 8183 |  |  |  | 445 | [10 empty] | 92.61 |  |  |  | 92.80 | [5 empty] | 91.73 |  |  | 93.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.20 |  |  |  |  | 0.19
1990 |  |  |  | 3271.13 |  |  | 7605 |  |  |  | 445 | [10 empty] | 85.48 |  |  |  | 85.50 | [5 empty] | 83.91 |  |  | 86.82 |  |  |  | 4.46 |  | 3.99 | [8 empty] | 10.50 |  |  |  |  | 0.03
1991 |  |  |  | 3360.90 |  |  | 7927 |  |  |  | 445 | [10 empty] | 88.58 |  |  |  | 88.84 | [5 empty] | 86.22 |  |  | 90.49 |  |  |  | 2.52 |  | 2.29 | [8 empty] | 8.86 |  |  |  |  | 0.26
1992 |  |  |  | 3108.41 |  |  | 7186 |  |  |  | 445 | [10 empty] | 80.19 |  |  |  | 80.30 | [5 empty] | 79.52 |  |  | 81.81 |  |  |  | 0.44 |  | 0.35 | [8 empty] | 19.35 |  |  |  |  | 0.11
1993 |  |  |  | 3443.16 |  |  | 8052 |  |  |  | 445 | [10 empty] | 89.47 |  |  |  | 89.49 | [5 empty] | 88.40 |  |  | 91.99 |  |  |  | 1.77 |  | 1.61 | [8 empty] | 8.91 |  |  |  |  | 0.02
1994 |  |  |  | 3497.57 |  |  | 8017 |  |  |  | 445 | [10 empty] | 90.70 |  |  |  | 90.76 | [5 empty] | 89.72 |  |  | 91.52 |  |  |  | 2.31 |  | 2.15 | [8 empty] | 7.09 |  |  |  |  | 0.06
1995 |  |  |  | 3389.06 |  |  | 7834 |  |  |  | 445 | [10 empty] | 87.66 |  |  |  | 88.50 | [5 empty] | 86.94 |  |  | 89.43 |  |  |  | 6.50 |  | 6.16 | [8 empty] | 5.34 |  |  |  |  | 0.84
1996 |  |  |  | 3203.49 |  |  | 7281 |  |  |  | 445 | [10 empty] | 82.04 |  |  |  | 82.51 | [5 empty] | 81.95 |  |  | 82.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.49 |  |  |  |  | 0.47
1997 |  |  |  | 3794.83 |  |  | 8309 |  |  |  | 445 | [10 empty] | 93.02 |  |  |  | 93.87 | [5 empty] | 97.35 |  |  | 94.85 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 6.11 |  |  |  |  | 0.86
1998 |  |  |  | 3852.35 |  |  | 8234 |  |  |  | 488 | [10 empty] | 91.35 |  |  |  | 93.39 | [5 empty] | 90.12 |  |  | 94.00 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 6.56 |  |  |  |  | 2.04
1999 |  |  |  | 3883.28 |  |  | 8304 |  |  |  | 488 | [10 empty] | 91.63 |  |  |  | 92.37 | [5 empty] | 90.84 |  |  | 94.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.63 |  |  |  |  | 0.74
2000 |  |  |  | 3618.00 |  |  | 7720 |  |  |  | 488 | [10 empty] | 84.91 |  |  |  | 86.50 | [5 empty] | 84.40 |  |  | 87.89 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 13.45 |  |  |  |  | 1.59
2001 |  |  |  | 3920.99 |  |  | 8233 |  |  |  | 488 | [10 empty] | 92.38 |  |  |  | 93.41 | [5 empty] | 91.72 |  |  | 93.98 |  |  |  | 0.67 |  | 0.63 | [8 empty] | 5.97 |  |  |  |  | 1.02
2002 |  |  |  | 3790.07 |  |  | 8095 |  |  |  | 488 | [10 empty] | 89.27 |  |  |  | 91.40 | [5 empty] | 88.66 |  |  | 92.41 |  |  |  | 0.72 |  | 0.66 | [8 empty] | 7.94 |  |  |  |  | 2.13
2003 |  |  |  | 3938.98 |  |  | 8194 |  |  |  | 488 | [10 empty] | 92.40 |  |  |  | 93.22 | [5 empty] | 92.14 |  |  | 93.54 |  |  |  | 0.16 |  | 2.01 | [8 empty] | 4.77 |  |  |  |  | 0.83
2004 |  |  |  | 3715.03 |  |  | 7647 |  |  |  | 488 | [10 empty] | 86.51 |  |  |  | 86.91 | [5 empty] | 86.66 |  |  | 87.05 |  |  |  | 0.24 |  | 1.55 | [8 empty] | 11.54 |  |  |  |  | 0.40
2005 |  |  |  | 4062.43 |  |  | 8351 |  |  |  | 488 | [10 empty] | 94.61 |  |  |  | 95.02 | [5 empty] | 95.03 |  |  | 95.33 |  |  |  | 0.28 |  | 0.27 | [8 empty] | 4.71 |  |  |  |  | 0.41
2006 |  |  |  | 3964.84 |  |  | 8138 |  |  |  | 488 | [10 empty] | 92.08 |  |  |  | 92.63 | [5 empty] | 92.74 |  |  | 92.89 |  |  |  | 0.18 |  | 0.95 | [8 empty] | 6.42 |  |  |  |  | 0.55
2007 |  |  |  | 4028.12 |  |  | 8285 |  |  |  | 488 | [10 empty] | 93.49 |  |  |  | 94.00 | [5 empty] | 94.23 |  |  | 94.58 |  |  |  | 0.32 |  | 1.19 | [8 empty] | 4.82 |  |  |  |  | 0.50
2008 |  |  |  | 3671.84 |  |  | 7571 |  |  |  | 488 | [10 empty] | 84.51 |  |  |  | 84.87 | [5 empty] | 85.66 |  |  | 86.19 |  |  |  | 0.09 |  | 3.25 | [8 empty] | 11.88 |  |  |  |  | 0.36
2009 |  |  |  | 4084.91 |  |  | 8345 |  |  |  | 488 | [10 empty] | 94.80 |  |  |  | 94.83 | [5 empty] | 95.56 |  |  | 95.26 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 5.14 |  |  |  |  | 0.03
2010 |  |  |  | 3955.59 |  |  | 8123 |  |  |  | 488 | [10 empty] | 91.95 |  |  |  | 92.33 | [5 empty] | 92.53 |  |  | 92.73 |  |  |  | 0.53 |  | 0.61 | [8 empty] | 7.07 |  |  |  |  | 0.38
2011 |  |  |  | 4026.87 |  |  | 8295 |  |  |  | 488 | [10 empty] | 93.82 |  |  |  | 94.32 | [5 empty] | 94.20 |  |  | 94.69 |  |  |  | 0.80 |  | 0.76 | [8 empty] | 4.92 |  |  |  |  | 0.51
2012 |  |  |  | 3653.04 |  |  | 7473 |  |  |  | 496 | [10 empty] | 84.08 |  |  |  | 84.86 | [5 empty] | 83.86 |  |  | 85.08 |  |  |  | 0.00 |  | 3.32 | [8 empty] | 11.82 |  |  |  |  | 0.78
2013 |  |  |  | 4000.24 |  |  | 8219 |  |  |  | 496 | [10 empty] | 92.00 |  |  |  | 93.02 | [5 empty] | 92.07 |  |  | 93.82 |  |  |  | 1.33 |  | 1.25 | [8 empty] | 5.73 |  |  |  |  | 1.02
2014 |  |  |  | 4010.58 |  |  | 8262 |  |  |  | 496 | [10 empty] | 92.60 |  |  |  | 93.38 | [5 empty] | 92.30 |  |  | 94.32 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 6.57 |  |  |  |  | 0.78
2015 |  |  |  | 4025.96 |  |  | 8248 |  |  |  | 496 | [10 empty] | 92.68 |  |  |  | 93.76 | [5 empty] | 92.66 |  |  | 94.16 |  |  |  | 0.07 |  | 0.99 | [8 empty] | 5.25 |  |  |  |  | 1.08
2016 |  |  |  | 3862.81 |  |  | 7873 |  |  |  | 502 | [10 empty] | 88.45 |  |  |  | 89.43 | [5 empty] | 88.48 |  |  | 89.63 |  |  |  | 0.07 |  | 1.58 | [8 empty] | 8.99 |  |  |  |  | 0.98
2017 |  |  |  | 4087.37 |  |  | 8246 |  |  |  | 507 | [10 empty] | 92.71 |  |  |  | 93.85 | [5 empty] | 92.71 |  |  | 94.13 |  |  |  | 0.15 |  | 0.55 | [8 empty] | 5.59 |  |  |  |  | 1.15
2018 |  |  |  | 4021.00 |  |  | 8124 |  |  |  | 507 | [10 empty] | 90.64 |  |  |  | 92.47 | [5 empty] | 90.54 |  |  | 92.74 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 7.43 |  |  |  |  | 1.82
2019 |  |  |  | 4109.79 |  |  | 8270 |  |  |  | 507 | [10 empty] | 92.90 |  |  |  | 94.10 | [5 empty] | 92.54 |  |  | 94.41 |  |  |  | 0.05 |  | 0.71 | [8 empty] | 5.19 |  |  |  |  | 1.20
2020 |  |  |  | 3709.11 |  |  | 7483 |  |  |  | 507 | [10 empty] | 83.47 |  |  |  | 84.86 | [5 empty] | 83.29 |  |  | 85.19 |  |  |  | 0.08 |  | 2.57 | [8 empty] | 12.56 |  |  |  |  | 1.39
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1977 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 174
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1080 | [14 empty] | 705 |  |  |  | 8
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 15
E. |  | Testing of plant systems or components | [35 empty] | 2
L. |  | Human factor related | [39 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 4
Z. |  | Other | [24 empty] | 220 | [14 empty] | 13
Subtotal | [22 empty] | 1080 |  |  |  | 220 | [10 empty] | 722 |  |  |  | 196 | [11 empty] | 4
Total | [22 empty] | 1300 | [14 empty] | 922
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1977 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 12
14. |  |  | Safety Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 126
16. |  |  | Steam generation systems | [34 empty] | 5
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 13
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 172

## LOVIISA-2
2020 Operating Experience
FI-2 | [8 empty] | LOVIISA-2 | [26 empty] | FINLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FORTUMPH (FORTUM POWER AND HEAT OY (former IVO))
Owner | [7 empty] | : | FORTUMPH (FORTUM POWER AND HEAT OY (former IVO))
Reactor Supplier | [7 empty] | : | AEE (ATOMENERGOEXPORT)
Turbine Supplier | [7 empty] | : | AEE (ATOMENERGOEXPORT)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-08-01
Thermal power | [12 empty] | : |  |  | 1500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-11-04
Gross electrical power | [12 empty] | : |  |  | 531 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-01-05
Reference unit power (net) | [12 empty] | : |  |  | 507 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.25
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.07
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.73 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.42 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 313 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.7 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4058.51 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.11 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.22 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.52 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.53 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.96 %
Load Factor (LF) | [18 empty] | : | 91.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.3 %
Operating Factor (OF) | [18 empty] | : | 93.02 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 613 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 376.77 | 352.47 |  |  |  | 376.56 |  | 363.75 | [8 empty] | 374.34 |  |  | 352.31 | [6 empty] | 364.73 |  | 46.80 |  |  |  | 348.38 |  |  | 366.28 |  |  | 361.21 | [9 empty] | 374.91 |  |  | 4058.51
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.24 |  |  | 96.51 | [6 empty] | 96.69 |  | 12.29 |  |  |  | 95.44 |  |  | 96.97 |  |  | 98.95 | [9 empty] | 99.98 |  |  | 91.22
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.92 |  |  | 99.75 | [6 empty] | 99.96 |  | 13.01 |  |  |  | 99.09 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 92.53
LF [%] |  |  |  |  | 99.88 | 99.89 |  |  |  | 99.83 |  | 99.65 | [8 empty] | 99.24 |  |  | 96.51 | [6 empty] | 96.69 |  | 12.41 |  |  |  | 95.44 |  |  | 97.10 |  |  | 98.95 | [9 empty] | 99.39 |  |  | 91.13
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 17.74 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.02
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.08 |  |  | 0.25 | [6 empty] | 0.04 |  | 0.00 |  |  |  | 0.91 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 0.11
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.08 |  |  | 0.25 | [6 empty] | 0.04 |  | 4.84 |  |  |  | 0.91 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 0.52
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 82.15 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.96
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.68 |  |  | 3.24 | [6 empty] | 3.27 |  | 0.72 |  |  |  | 3.65 |  |  | 3.03 |  |  | 1.05 | [9 empty] | 0.00 |  |  | 1.30
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 148215.35 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.41 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.44 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.52 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.25 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.36 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.79 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.22 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 2714.20 |  |  | 7062 |  |  |  | 440 | [10 empty] | 72.18 |  |  |  | 72.18 | [5 empty] | 70.42 |  |  | 80.62 |  |  |  | 9.96 |  | 7.99 | [8 empty] | 19.83 |  |  |  |  | 0.00
1982 |  |  |  | 2997.40 |  |  | 7046 |  |  |  | 440 | [10 empty] | 78.00 |  |  |  | 78.00 | [5 empty] | 77.77 |  |  | 80.43 |  |  |  | 0.30 |  | 0.23 | [8 empty] | 21.76 |  |  |  |  | 0.00
1983 |  |  |  | 3474.50 |  |  | 8063 |  |  |  | 445 | [10 empty] | 90.09 |  |  |  | 90.09 | [5 empty] | 89.13 |  |  | 92.04 |  |  |  | 0.72 |  | 0.66 | [8 empty] | 9.25 |  |  |  |  | 0.00
1984 |  |  |  | 3608.63 |  |  | 8251 |  |  |  | 445 | [10 empty] | 92.57 |  |  |  | 92.57 | [5 empty] | 92.32 |  |  | 93.93 |  |  |  | 0.93 |  | 0.87 | [8 empty] | 6.56 |  |  |  |  | 0.00
1985 |  |  |  | 3549.84 |  |  | 8162 |  |  |  | 440 | [10 empty] | 92.15 |  |  |  | 92.15 | [5 empty] | 92.10 |  |  | 93.17 |  |  |  | 1.79 |  | 1.68 | [8 empty] | 6.17 |  |  |  |  | 0.00
1986 |  |  |  | 3174.87 |  |  | 7273 |  |  |  | 445 | [10 empty] | 81.46 |  |  |  | 81.46 | [5 empty] | 81.44 |  |  | 83.03 |  |  |  | 3.74 |  | 3.17 | [8 empty] | 15.37 |  |  |  |  | 0.00
1987 |  |  |  | 3572.08 |  |  | 8242 |  |  |  | 445 | [10 empty] | 93.37 |  |  |  | 93.37 | [5 empty] | 91.63 |  |  | 94.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.63 |  |  |  |  | 0.00
1988 |  |  |  | 3602.27 |  |  | 8305 |  |  |  | 445 | [10 empty] | 94.69 |  |  |  | 94.69 | [5 empty] | 92.16 |  |  | 94.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.31 |  |  |  |  | 0.00
1989 |  |  |  | 3550.96 |  |  | 8128 |  |  |  | 445 | [10 empty] | 91.69 |  |  |  | 91.76 | [5 empty] | 91.09 |  |  | 92.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.24 |  |  |  |  | 0.07
1990 |  |  |  | 3251.05 |  |  | 7584 |  |  |  | 445 | [10 empty] | 85.28 |  |  |  | 85.32 | [5 empty] | 83.40 |  |  | 86.58 |  |  |  | 4.24 |  | 3.78 | [8 empty] | 10.90 |  |  |  |  | 0.04
1991 |  |  |  | 3442.19 |  |  | 7941 |  |  |  | 445 | [10 empty] | 88.98 |  |  |  | 89.85 | [5 empty] | 88.30 |  |  | 90.65 |  |  |  | 0.25 |  | 0.22 | [8 empty] | 9.93 |  |  |  |  | 0.87
1992 |  |  |  | 3468.45 |  |  | 7931 |  |  |  | 445 | [10 empty] | 89.10 |  |  |  | 89.53 | [5 empty] | 88.73 |  |  | 90.29 |  |  |  | 0.66 |  | 0.60 | [8 empty] | 9.88 |  |  |  |  | 0.43
1993 |  |  |  | 3550.79 |  |  | 8050 |  |  |  | 445 | [10 empty] | 91.25 |  |  |  | 91.29 | [5 empty] | 91.16 |  |  | 91.97 |  |  |  | 2.29 |  | 2.14 | [8 empty] | 6.57 |  |  |  |  | 0.04
1994 |  |  |  | 3124.71 |  |  | 7170 |  |  |  | 445 | [10 empty] | 80.50 |  |  |  | 81.20 | [5 empty] | 80.16 |  |  | 81.85 |  |  |  | 1.87 |  | 1.55 | [8 empty] | 17.25 |  |  |  |  | 0.70
1995 |  |  |  | 3060.25 |  |  | 7064 |  |  |  | 445 | [10 empty] | 77.57 |  |  |  | 78.41 | [5 empty] | 78.50 |  |  | 80.64 |  |  |  | 17.16 |  | 16.25 | [8 empty] | 5.34 |  |  |  |  | 0.84
1996 |  |  |  | 3621.33 |  |  | 8227 |  |  |  | 445 | [10 empty] | 92.73 |  |  |  | 93.08 | [5 empty] | 92.64 |  |  | 93.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.92 |  |  |  |  | 0.35
1997 |  |  |  | 3804.70 |  |  | 8267 |  |  |  | 445 | [10 empty] | 91.96 |  |  |  | 92.87 | [5 empty] | 97.60 |  |  | 94.37 |  |  |  | 2.30 |  | 2.19 | [8 empty] | 4.94 |  |  |  |  | 0.91
1998 |  |  |  | 3687.90 |  |  | 7892 |  |  |  | 488 | [10 empty] | 86.41 |  |  |  | 88.55 | [5 empty] | 86.27 |  |  | 90.09 |  |  |  | 0.70 |  | 0.63 | [8 empty] | 10.82 |  |  |  |  | 2.14
1999 |  |  |  | 3974.34 |  |  | 8281 |  |  |  | 488 | [10 empty] | 93.53 |  |  |  | 94.19 | [5 empty] | 92.97 |  |  | 94.53 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 5.69 |  |  |  |  | 0.65
2000 |  |  |  | 3885.10 |  |  | 8314 |  |  |  | 488 | [10 empty] | 90.90 |  |  |  | 94.11 | [5 empty] | 90.63 |  |  | 94.65 |  |  |  | 0.25 |  | 0.23 | [8 empty] | 5.66 |  |  |  |  | 3.21
2001 |  |  |  | 3781.06 |  |  | 8149 |  |  |  | 488 | [10 empty] | 89.58 |  |  |  | 92.30 | [5 empty] | 88.45 |  |  | 93.03 |  |  |  | 1.25 |  | 1.17 | [8 empty] | 6.53 |  |  |  |  | 2.72
2002 |  |  |  | 3498.66 |  |  | 7463 |  |  |  | 488 | [10 empty] | 82.56 |  |  |  | 84.51 | [5 empty] | 81.84 |  |  | 85.19 |  |  |  | 1.54 |  | 4.75 | [8 empty] | 10.74 |  |  |  |  | 1.94
2003 |  |  |  | 3736.65 |  |  | 8358 |  |  |  | 488 | [10 empty] | 90.00 |  |  |  | 90.14 | [5 empty] | 87.41 |  |  | 95.41 |  |  |  | 0.08 |  | 0.20 | [8 empty] | 9.66 |  |  |  |  | 0.14
2004 |  |  |  | 4009.18 |  |  | 8231 |  |  |  | 488 | [10 empty] | 93.11 |  |  |  | 93.59 | [5 empty] | 93.53 |  |  | 93.70 |  |  |  | 0.25 |  | 0.23 | [8 empty] | 6.18 |  |  |  |  | 0.47
2005 |  |  |  | 4076.12 |  |  | 8376 |  |  |  | 488 | [10 empty] | 94.55 |  |  |  | 95.36 | [5 empty] | 95.35 |  |  | 95.62 |  |  |  | 0.16 |  | 0.15 | [8 empty] | 4.49 |  |  |  |  | 0.81
2006 |  |  |  | 3766.55 |  |  | 7863 |  |  |  | 488 | [10 empty] | 87.47 |  |  |  | 88.49 | [5 empty] | 88.11 |  |  | 89.76 |  |  |  | 0.51 |  | 0.45 | [8 empty] | 11.06 |  |  |  |  | 1.01
2007 |  |  |  | 4090.87 |  |  | 8403 |  |  |  | 488 | [10 empty] | 94.85 |  |  |  | 95.47 | [5 empty] | 95.70 |  |  | 95.92 |  |  |  | 0.24 |  | 0.23 | [8 empty] | 4.30 |  |  |  |  | 0.61
2008 |  |  |  | 3997.95 |  |  | 8240 |  |  |  | 488 | [10 empty] | 92.52 |  |  |  | 93.47 | [5 empty] | 93.27 |  |  | 93.81 |  |  |  | 0.02 |  | 0.22 | [8 empty] | 6.32 |  |  |  |  | 0.95
2009 |  |  |  | 4063.83 |  |  | 8318 |  |  |  | 488 | [10 empty] | 94.26 |  |  |  | 94.59 | [5 empty] | 95.06 |  |  | 94.95 |  |  |  | 0.18 |  | 0.17 | [8 empty] | 5.24 |  |  |  |  | 0.33
2010 |  |  |  | 3789.14 |  |  | 7797 |  |  |  | 488 | [10 empty] | 88.09 |  |  |  | 88.80 | [5 empty] | 88.64 |  |  | 89.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.20 |  |  |  |  | 0.70
2011 |  |  |  | 4035.30 |  |  | 8290 |  |  |  | 488 | [10 empty] | 93.70 |  |  |  | 94.48 | [5 empty] | 94.40 |  |  | 94.63 |  |  |  | 0.07 |  | 0.77 | [8 empty] | 4.75 |  |  |  |  | 0.77
2012 |  |  |  | 3959.19 |  |  | 8141 |  |  |  | 496 | [10 empty] | 91.02 |  |  |  | 92.04 | [5 empty] | 90.87 |  |  | 92.68 |  |  |  | 2.12 |  | 1.99 | [8 empty] | 5.97 |  |  |  |  | 1.02
2013 |  |  |  | 4040.04 |  |  | 8250 |  |  |  | 496 | [10 empty] | 92.40 |  |  |  | 93.69 | [5 empty] | 92.98 |  |  | 94.18 |  |  |  | 1.58 |  | 1.50 | [8 empty] | 4.81 |  |  |  |  | 1.29
2014 |  |  |  | 3872.75 |  |  | 7912 |  |  |  | 496 | [10 empty] | 88.91 |  |  |  | 89.73 | [5 empty] | 89.13 |  |  | 90.32 |  |  |  | 0.29 |  | 0.64 | [8 empty] | 9.63 |  |  |  |  | 0.82
2015 |  |  |  | 4039.11 |  |  | 8276 |  |  |  | 496 | [10 empty] | 92.60 |  |  |  | 93.20 | [5 empty] | 92.96 |  |  | 94.47 |  |  |  | 2.07 |  | 1.97 | [8 empty] | 4.84 |  |  |  |  | 0.60
2016 |  |  |  | 4068.96 |  |  | 8304 |  |  |  | 502 | [10 empty] | 92.94 |  |  |  | 93.97 | [5 empty] | 93.30 |  |  | 94.54 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 5.94 |  |  |  |  | 1.04
2017 |  |  |  | 4071.92 |  |  | 8255 |  |  |  | 502 | [10 empty] | 92.51 |  |  |  | 93.96 | [5 empty] | 92.60 |  |  | 94.24 |  |  |  | 1.16 |  | 1.10 | [8 empty] | 4.94 |  |  |  |  | 1.45
2018 |  |  |  | 3770.71 |  |  | 7639 |  |  |  | 507 | [10 empty] | 85.52 |  |  |  | 86.92 | [5 empty] | 85.60 |  |  | 87.20 |  |  |  | 0.26 |  | 1.44 | [8 empty] | 11.64 |  |  |  |  | 1.41
2019 |  |  |  | 4053.97 |  |  | 8142 |  |  |  | 507 | [10 empty] | 91.58 |  |  |  | 92.48 | [5 empty] | 91.28 |  |  | 92.95 |  |  |  | 0.19 |  | 2.56 | [8 empty] | 4.96 |  |  |  |  | 0.91
2020 |  |  |  | 4058.51 |  |  | 8171 |  |  |  | 507 | [10 empty] | 91.22 |  |  |  | 92.53 | [5 empty] | 91.13 |  |  | 93.02 |  |  |  | 0.11 |  | 0.52 | [8 empty] | 6.96 |  |  |  |  | 1.30
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 86
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 576 | [14 empty] | 650 |  |  |  | 2
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 30
Z. |  | Other | [24 empty] | 36 | [10 empty] | 1 |  |  |  | 6
Subtotal | [22 empty] | 576 |  |  |  | 36 | [10 empty] | 681 |  |  |  | 94
Total | [22 empty] | 612 | [14 empty] | 775
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
12. |  |  | Reactor I&C Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 44
16. |  |  | Steam generation systems | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
34. |  |  | Miscellaneous Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 1
Total | [37 empty] | 86

## OLKILUOTO-1
2020 Operating Experience
FI-3 | [8 empty] | OLKILUOTO-1 | [26 empty] | FINLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVO (TEOLLISUUDEN VOIMA OYJ)
Owner | [7 empty] | : | TVO (TEOLLISUUDEN VOIMA OYJ)
Reactor Supplier | [7 empty] | : | ASEASTAL (ASEA-ATOM / STAL-LAVAL)
Turbine Supplier | [7 empty] | : | ASEASTAL (ASEA-ATOM / STAL-LAVAL)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / AA-III, BWR-2500 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-02-01
Thermal power | [12 empty] | : |  |  | 2500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-09-02
Gross electrical power | [12 empty] | : |  |  | 920 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-10-10
Reference unit power (net) | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.12
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.8
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.85 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 4
| Active core diameter [m] | [13 empty] | : |  |  | 3.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.7
| Active core height/length [m] | [13 empty] | : |  |  | 3.68 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 500 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 121 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7310.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.12 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.25 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.3 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.75 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 3.94 %
Load Factor (LF) | [18 empty] | : | 93.51 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.5 %
Operating Factor (OF) | [18 empty] | : | 95.53 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 393 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 666.79 | 622.32 |  |  |  | 615.42 |  | 570.00 | [8 empty] | 468.70 |  |  | 461.05 | [6 empty] | 651.17 |  | 647.20 |  |  |  | 636.06 |  |  | 662.10 |  |  | 643.75 | [9 empty] | 665.50 |  |  | 7310.06
EAF [%] |  |  |  |  | 100.00 | 99.76 |  |  |  | 92.50 |  | 88.95 | [8 empty] | 70.78 |  |  | 71.96 | [6 empty] | 98.35 |  | 97.75 |  |  |  | 99.28 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 99.80 |  |  | 93.25
UCF [%] |  |  |  |  | 100.00 | 99.76 |  |  |  | 92.50 |  | 88.95 | [8 empty] | 71.55 |  |  | 72.61 | [6 empty] | 100.00 |  | 99.93 |  |  |  | 99.99 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 99.80 |  |  | 93.75
LF [%] |  |  |  |  | 100.70 | 100.46 |  |  |  | 93.07 |  | 88.95 | [8 empty] | 70.78 |  |  | 71.95 | [6 empty] | 98.34 |  | 97.74 |  |  |  | 99.26 |  |  | 99.86 |  |  | 100.46 | [9 empty] | 100.51 |  |  | 93.51
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 97.17 |  | 97.08 | [8 empty] | 76.61 |  |  | 75.42 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.53
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 7.50 |  | 11.05 | [8 empty] | 6.35 |  |  | 1.23 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.01 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.12
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 7.50 |  | 11.05 | [8 empty] | 4.85 |  |  | 4.29 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.01 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.30
PUF [%] |  |  |  |  | 0.00 | 0.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.60 |  |  | 23.10 | [6 empty] | 0.00 |  | 0.07 |  |  |  | 0.00 |  |  | 0.12 |  |  | 0.00 | [9 empty] | 0.20 |  |  | 3.94
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.77 |  |  | 0.66 | [6 empty] | 1.65 |  | 2.17 |  |  |  | 0.72 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.50
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 267098.66 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.43 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.72 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.59 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.16 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 5.24 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 92.55 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.45 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 93.75 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 3465.00 |  |  | 5614 |  |  |  | 660 | [10 empty] | 86.85 |  |  |  | 86.85 | [5 empty] | 86.82 |  |  | 90.40 |  |  |  | 12.45 |  | 12.35 | [8 empty] | 0.80 |  |  |  |  | 0.00
1980 |  |  |  | 4280.80 |  |  | 6849 |  |  |  | 658 | [10 empty] | 76.31 |  |  |  | 76.31 | [5 empty] | 74.06 |  |  | 77.97 |  |  |  | 3.12 |  | 2.46 | [8 empty] | 21.23 |  |  |  |  | 0.00
1981 |  |  |  | 4549.20 |  |  | 7353 |  |  |  | 660 | [10 empty] | 80.80 |  |  |  | 80.80 | [5 empty] | 78.68 |  |  | 83.94 |  |  |  | 8.82 |  | 7.82 | [8 empty] | 11.38 |  |  |  |  | 0.00
1982 |  |  |  | 4997.50 |  |  | 7903 |  |  |  | 658 | [10 empty] | 86.68 |  |  |  | 86.68 | [5 empty] | 86.70 |  |  | 90.22 |  |  |  | 3.90 |  | 3.51 | [8 empty] | 9.81 |  |  |  |  | 0.00
1983 |  |  |  | 4808.30 |  |  | 7651 |  |  |  | 669 | [10 empty] | 81.86 |  |  |  | 81.86 | [5 empty] | 82.01 |  |  | 87.34 |  |  |  | 0.96 |  | 0.79 | [8 empty] | 17.35 |  |  |  |  | 0.00
1984 |  |  |  | 5505.61 |  |  | 8247 |  |  |  | 694 | [10 empty] | 91.94 |  |  |  | 91.94 | [5 empty] | 90.30 |  |  | 93.89 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 7.76 |  |  |  |  | 0.00
1985 |  |  |  | 5414.51 |  |  | 8180 |  |  |  | 710 | [10 empty] | 88.75 |  |  |  | 88.75 | [5 empty] | 87.06 |  |  | 93.38 |  |  |  | 2.58 |  | 2.35 | [8 empty] | 8.90 |  |  |  |  | 0.00
1986 |  |  |  | 5463.21 |  |  | 8008 |  |  |  | 710 | [10 empty] | 90.08 |  |  |  | 90.08 | [5 empty] | 87.84 |  |  | 91.42 |  |  |  | 0.72 |  | 0.65 | [8 empty] | 9.27 |  |  |  |  | 0.00
1987 |  |  |  | 5636.46 |  |  | 8142 |  |  |  | 710 | [10 empty] | 92.05 |  |  |  | 92.05 | [5 empty] | 90.62 |  |  | 92.95 |  |  |  | 2.64 |  | 2.49 | [8 empty] | 5.45 |  |  |  |  | 0.00
1988 |  |  |  | 5778.87 |  |  | 8248 |  |  |  | 710 | [10 empty] | 94.07 |  |  |  | 94.29 | [5 empty] | 92.66 |  |  | 93.90 |  |  |  | 1.20 |  | 1.15 | [8 empty] | 4.56 |  |  |  |  | 0.22
1989 |  |  |  | 5056.20 |  |  | 7278 |  |  |  | 710 | [10 empty] | 83.18 |  |  |  | 83.18 | [5 empty] | 81.29 |  |  | 83.08 |  |  |  | 13.17 |  | 12.62 | [8 empty] | 4.20 |  |  |  |  | 0.00
1990 |  |  |  | 5857.31 |  |  | 8356 |  |  |  | 710 | [10 empty] | 95.60 |  |  |  | 95.60 | [5 empty] | 94.17 |  |  | 95.39 |  |  |  | 0.57 |  | 0.55 | [8 empty] | 3.86 |  |  |  |  | 0.00
1991 |  |  |  | 5873.22 |  |  | 8373 |  |  |  | 710 | [10 empty] | 94.85 |  |  |  | 95.72 | [5 empty] | 94.43 |  |  | 95.58 |  |  |  | 0.13 |  | 0.12 | [8 empty] | 4.16 |  |  |  |  | 0.87
1992 |  |  |  | 5803.04 |  |  | 8251 |  |  |  | 710 | [10 empty] | 93.23 |  |  |  | 93.72 | [5 empty] | 93.05 |  |  | 93.93 |  |  |  | 0.44 |  | 0.42 | [8 empty] | 5.87 |  |  |  |  | 0.49
1993 |  |  |  | 5944.92 |  |  | 8433 |  |  |  | 710 | [10 empty] | 95.33 |  |  |  | 95.78 | [5 empty] | 95.58 |  |  | 96.27 |  |  |  | 0.28 |  | 0.27 | [8 empty] | 3.95 |  |  |  |  | 0.45
1994 |  |  |  | 5978.04 |  |  | 8485 |  |  |  | 710 | [10 empty] | 96.01 |  |  |  | 96.50 | [5 empty] | 96.12 |  |  | 96.86 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 3.45 |  |  |  |  | 0.49
1995 |  |  |  | 5931.50 |  |  | 8427 |  |  |  | 710 | [10 empty] | 95.50 |  |  |  | 96.11 | [5 empty] | 95.37 |  |  | 96.20 |  |  |  | 0.84 |  | 0.81 | [8 empty] | 3.08 |  |  |  |  | 0.61
1996 |  |  |  | 5938.60 |  |  | 8212 |  |  |  | 710 | [10 empty] | 92.08 |  |  |  | 92.19 | [5 empty] | 95.22 |  |  | 93.49 |  |  |  | 1.22 |  | 1.14 | [8 empty] | 6.67 |  |  |  |  | 0.11
1997 |  |  |  | 6374.15 |  |  | 8254 |  |  |  | 772 | [10 empty] | 93.83 |  |  |  | 93.86 | [5 empty] | 94.18 |  |  | 94.22 |  |  |  | 1.24 |  | 1.18 | [8 empty] | 4.96 |  |  |  |  | 0.03
1998 |  |  |  | 6807.01 |  |  | 8384 |  |  |  | 840 | [10 empty] | 94.95 |  |  |  | 95.57 | [5 empty] | 92.51 |  |  | 95.71 |  |  |  | 0.22 |  | 0.21 | [8 empty] | 4.22 |  |  |  |  | 0.62
1999 |  |  |  | 7111.82 |  |  | 8542 |  |  |  | 840 | [10 empty] | 96.39 |  |  |  | 97.24 | [5 empty] | 96.65 |  |  | 97.51 |  |  |  | 0.26 |  | 0.25 | [8 empty] | 2.51 |  |  |  |  | 0.84
2000 |  |  |  | 7043.10 |  |  | 8448 |  |  |  | 840 | [10 empty] | 95.17 |  |  |  | 95.81 | [5 empty] | 95.45 |  |  | 96.17 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 4.06 |  |  |  |  | 0.65
2001 |  |  |  | 7163.80 |  |  | 8561 |  |  |  | 840 | [10 empty] | 97.16 |  |  |  | 97.64 | [5 empty] | 97.36 |  |  | 97.73 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 2.35 |  |  |  |  | 0.48
2002 |  |  |  | 6997.54 |  |  | 8377 |  |  |  | 840 | [10 empty] | 95.05 |  |  |  | 95.51 | [5 empty] | 95.09 |  |  | 95.62 |  |  |  | 0.65 |  | 0.63 | [8 empty] | 3.86 |  |  |  |  | 0.46
2003 |  |  |  | 7127.43 |  |  | 8515 |  |  |  | 840 | [10 empty] | 96.46 |  |  |  | 97.08 | [5 empty] | 96.86 |  |  | 97.20 |  |  |  | 0.18 |  | 0.51 | [8 empty] | 2.41 |  |  |  |  | 0.61
2004 |  |  |  | 7009.02 |  |  | 8329 |  |  |  | 840 | [10 empty] | 94.70 |  |  |  | 94.70 | [5 empty] | 94.99 |  |  | 94.82 |  |  |  | 0.80 |  | 1.19 | [8 empty] | 4.11 |  |  |  |  | 0.00
2005 |  |  |  | 7221.07 |  |  | 8588 |  |  |  | 840 | [10 empty] | 97.73 |  |  |  | 97.85 | [5 empty] | 98.13 |  |  | 98.04 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 2.13 |  |  |  |  | 0.12
2006 |  |  |  | 6973.38 |  |  | 8206 |  |  |  | 860 | [10 empty] | 92.64 |  |  |  | 93.34 | [5 empty] | 93.64 |  |  | 93.68 |  |  |  | 0.35 |  | 0.60 | [8 empty] | 6.06 |  |  |  |  | 0.71
2007 |  |  |  | 7334.94 |  |  | 8554 |  |  |  | 860 | [10 empty] | 96.75 |  |  |  | 97.37 | [5 empty] | 97.36 |  |  | 97.65 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 2.59 |  |  |  |  | 0.63
2008 |  |  |  | 7066.02 |  |  | 8288 |  |  |  | 860 | [10 empty] | 93.14 |  |  |  | 93.59 | [5 empty] | 93.54 |  |  | 94.35 |  |  |  | 0.78 |  | 2.09 | [8 empty] | 4.32 |  |  |  |  | 0.44
2009 |  |  |  | 7295.77 |  |  | 8548 |  |  |  | 860 | [10 empty] | 96.69 |  |  |  | 97.22 | [5 empty] | 96.84 |  |  | 97.58 |  |  |  | 0.30 |  | 0.37 | [8 empty] | 2.41 |  |  |  |  | 0.53
2010 |  |  |  | 6976.89 |  |  | 8120 |  |  |  | 880 | [10 empty] | 91.41 |  |  |  | 92.00 | [5 empty] | 91.54 |  |  | 92.69 |  |  |  | 0.65 |  | 0.90 | [8 empty] | 7.11 |  |  |  |  | 0.59
2011 |  |  |  | 7289.82 |  |  | 8410 |  |  |  | 880 | [10 empty] | 94.80 |  |  |  | 95.55 | [5 empty] | 94.56 |  |  | 96.00 |  |  |  | 1.91 |  | 2.38 | [8 empty] | 2.07 |  |  |  |  | 0.76
2012 |  |  |  | 6973.36 |  |  | 8013 |  |  |  | 880 | [10 empty] | 90.08 |  |  |  | 90.91 | [5 empty] | 90.21 |  |  | 91.22 |  |  |  | 2.52 |  | 2.35 | [8 empty] | 6.74 |  |  |  |  | 0.83
2013 |  |  |  | 7470.41 |  |  | 8555 |  |  |  | 880 | [10 empty] | 96.37 |  |  |  | 97.41 | [5 empty] | 96.91 |  |  | 97.66 |  |  |  | 0.36 |  | 0.58 | [8 empty] | 2.01 |  |  |  |  | 1.04
2014 |  |  |  | 7266.09 |  |  | 8337 |  |  |  | 880 | [10 empty] | 94.00 |  |  |  | 94.81 | [5 empty] | 94.26 |  |  | 95.17 |  |  |  | 0.38 |  | 0.89 | [8 empty] | 4.30 |  |  |  |  | 0.81
2015 |  |  |  | 7396.91 |  |  | 8506 |  |  |  | 880 | [10 empty] | 95.68 |  |  |  | 96.75 | [5 empty] | 95.95 |  |  | 97.10 |  |  |  | 0.24 |  | 0.66 | [8 empty] | 2.59 |  |  |  |  | 1.07
2016 |  |  |  | 7047.81 |  |  | 8146 |  |  |  | 880 | [10 empty] | 90.90 |  |  |  | 91.84 | [5 empty] | 91.18 |  |  | 92.74 |  |  |  | 2.29 |  | 3.46 | [8 empty] | 4.70 |  |  |  |  | 0.93
2017 |  |  |  | 7158.27 |  |  | 8289 |  |  |  | 880 | [10 empty] | 92.65 |  |  |  | 93.67 | [5 empty] | 92.86 |  |  | 94.62 |  |  |  | 3.26 |  | 3.82 | [8 empty] | 2.51 |  |  |  |  | 1.02
2018 |  |  |  | 6755.36 |  |  | 7731 |  |  |  | 880 | [10 empty] | 87.55 |  |  |  | 87.67 | [5 empty] | 87.63 |  |  | 88.25 |  |  |  | 0.65 |  | 2.73 | [8 empty] | 9.60 |  |  |  |  | 0.12
2019 |  |  |  | 7542.04 |  |  | 8539 |  |  |  | 890 | [10 empty] | 96.52 |  |  |  | 96.96 | [5 empty] | 96.74 |  |  | 97.48 |  |  |  | 0.27 |  | 0.32 | [8 empty] | 2.72 |  |  |  |  | 0.44
2020 |  |  |  | 7310.06 |  |  | 8391 |  |  |  | 890 | [10 empty] | 93.25 |  |  |  | 93.75 | [5 empty] | 93.51 |  |  | 95.53 |  |  |  | 2.12 |  | 2.30 | [8 empty] | 3.94 |  |  |  |  | 0.50
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1979 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 43 | [14 empty] | 99
B. |  | Refuelling without maintenance | [35 empty] | 39
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 327 |  |  |  | 24 | [10 empty] | 372 |  |  |  | 1
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 13
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 5
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 19
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
L. |  | Human factor related | [24 empty] | 3 | [14 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
Z. |  | Other | [39 empty] | 25
Subtotal | [22 empty] | 327 |  |  |  | 70 | [10 empty] | 443 |  |  |  | 131 | [11 empty] | 12
Total | [22 empty] | 397 | [14 empty] | 586
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1979 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 15
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 24
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [19 empty] | 1 | [14 empty] | 15
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 17
32. |  |  | Feedwater and Main Steam System | [19 empty] | 42 | [14 empty] | 5
33. |  |  | Circulating Water System | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 37
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [22 empty] | 43 | [14 empty] | 127
Highlights (2020)
The plant units operated safely. OL1's net production was 7,310 (7,542) GWh and load factor 93.7 (96.9)%. OL2's net production was 7,277 (7,209) GWh and load factor 93.3 (92.7)%. The 2020 annual outages of the Olkiluoto nuclear power plant were started with a refuelling outage at the OL2 plant unit on 10 May. The refueling outage was completed on 21 May. The annual outage carried out at the OL1 plant unit was a maintenance outage, which started on 24 May and was completed on 8 June. The duration of the plant unit's annual outage was shortened in March from the planned 25 days to 14 days due to the COVID-19 pandemic. Numerous special procedures and arrangements were put in place during the annual outages to protect people's health in Olkiluoto and prevent the possible spread of the virus, as well as to ensure a safe and high-quality annual outage. Modernizations and repair work with safety and availability significance were completed during the annual outages. Other planned modernizations were transferred to be completed in upcoming outages. Preventive maintenance was carried out normally according to the preventive maintenance programme. A significant task was the modernization of the bushing modules of one containment, which was completed for the first time. Other significant tasks were the modernization of the valve actuator in the cooling system of the shut down reactor as well as the changing of two valves, the connection of the recirculation line to one subsystem in auxiliary feed water systems, as well as repair works, preventive maintenance, inspections, and testing. The annual outages were carried out successfully despite special arrangements due to COVID-19.

## OLKILUOTO-2
2020 Operating Experience
FI-4 | [8 empty] | OLKILUOTO-2 | [26 empty] | FINLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVO (TEOLLISUUDEN VOIMA OYJ)
Owner | [7 empty] | : | TVO (TEOLLISUUDEN VOIMA OYJ)
Reactor Supplier | [7 empty] | : | ASEASTAL (ASEA-ATOM / STAL-LAVAL)
Turbine Supplier | [7 empty] | : | ASEASTAL (ASEA-ATOM / STAL-LAVAL)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / AA-III, BWR-2500 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-11-01
Thermal power | [12 empty] | : |  |  | 2500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-02-18
Gross electrical power | [12 empty] | : |  |  | 920 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1982-07-10
Reference unit power (net) | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.12
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.8
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.66 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 21 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 4
| Active core diameter [m] | [13 empty] | : |  |  | 4.00 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.7
| Active core height/length [m] | [13 empty] | : |  |  | 3.68 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 500 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.0 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 121 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7276.55 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.87 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.13 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.58 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.97 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.45 %
Load Factor (LF) | [18 empty] | : | 93.08 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.84 %
Operating Factor (OF) | [18 empty] | : | 94.36 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 495 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 665.46 | 622.68 |  |  |  | 663.91 |  | 629.78 | [8 empty] | 399.57 |  |  | 627.54 | [6 empty] | 643.86 |  | 643.98 |  |  |  | 633.46 |  |  | 661.26 |  |  | 634.78 | [9 empty] | 450.26 |  |  | 7276.55
EAF [%] |  |  |  |  | 99.92 | 100.00 |  |  |  | 99.90 |  | 99.16 | [8 empty] | 60.43 |  |  | 98.55 | [6 empty] | 97.92 |  | 97.27 |  |  |  | 98.87 |  |  | 100.00 |  |  | 98.94 | [9 empty] | 67.78 |  |  | 93.13
UCF [%] |  |  |  |  | 99.92 | 100.00 |  |  |  | 99.90 |  | 99.49 | [8 empty] | 62.10 |  |  | 100.00 | [6 empty] | 99.93 |  | 99.94 |  |  |  | 99.93 |  |  | 100.00 |  |  | 99.79 | [9 empty] | 67.78 |  |  | 93.97
LF [%] |  |  |  |  | 100.50 | 100.52 |  |  |  | 100.40 |  | 98.28 | [8 empty] | 60.34 |  |  | 97.93 | [6 empty] | 97.24 |  | 97.25 |  |  |  | 98.85 |  |  | 99.73 |  |  | 99.06 | [9 empty] | 68.00 |  |  | 93.08
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 63.98 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 69.49 |  |  | 94.36
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.51 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.06 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 32.22 |  |  | 2.87
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.51 | [8 empty] | 9.54 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.06 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 32.22 |  |  | 3.58
PUF [%] |  |  |  |  | 0.08 | 0.00 |  |  |  | 0.10 |  | 0.00 | [8 empty] | 28.36 |  |  | 0.00 | [6 empty] | 0.07 |  | 0.00 |  |  |  | 0.07 |  |  | 0.00 |  |  | 0.21 | [9 empty] | 0.00 |  |  | 2.45
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.34 | [8 empty] | 1.66 |  |  | 1.45 | [6 empty] | 2.01 |  | 2.67 |  |  |  | 1.06 |  |  | 0.00 |  |  | 0.85 | [9 empty] | 0.00 |  |  | 0.84
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 257523.89 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.24 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 93.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.56 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.66 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 4.78 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 93 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.54 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 94.2 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1982 |  |  |  | 4587.10 |  |  | 7269 |  |  |  | 658 | [10 empty] | 77.65 |  |  |  | 77.65 | [5 empty] | 77.64 |  |  | 79.53 |  |  |  | 2.38 |  | 1.89 | [8 empty] | 20.45 |  |  |  |  | 0.00
1983 |  |  |  | 5087.20 |  |  | 8221 |  |  |  | 657 | [10 empty] | 86.75 |  |  |  | 86.75 | [5 empty] | 88.39 |  |  | 93.85 |  |  |  | 5.00 |  | 4.57 | [8 empty] | 8.69 |  |  |  |  | 0.00
1984 |  |  |  | 5341.30 |  |  | 8031 |  |  |  | 696 | [10 empty] | 89.57 |  |  |  | 89.57 | [5 empty] | 87.28 |  |  | 91.43 |  |  |  | 1.96 |  | 1.79 | [8 empty] | 8.64 |  |  |  |  | 0.00
1985 |  |  |  | 5415.79 |  |  | 7912 |  |  |  | 710 | [10 empty] | 88.16 |  |  |  | 88.16 | [5 empty] | 87.08 |  |  | 90.32 |  |  |  | 1.98 |  | 1.78 | [8 empty] | 10.06 |  |  |  |  | 0.00
1986 |  |  |  | 5840.21 |  |  | 8437 |  |  |  | 710 | [10 empty] | 95.07 |  |  |  | 95.07 | [5 empty] | 93.90 |  |  | 96.31 |  |  |  | 0.32 |  | 0.30 | [8 empty] | 4.63 |  |  |  |  | 0.00
1987 |  |  |  | 5725.03 |  |  | 8379 |  |  |  | 710 | [10 empty] | 93.71 |  |  |  | 93.71 | [5 empty] | 92.05 |  |  | 95.65 |  |  |  | 1.41 |  | 1.34 | [8 empty] | 4.95 |  |  |  |  | 0.00
1988 |  |  |  | 5713.20 |  |  | 8220 |  |  |  | 710 | [10 empty] | 92.73 |  |  |  | 92.73 | [5 empty] | 91.61 |  |  | 93.58 |  |  |  | 2.89 |  | 2.76 | [8 empty] | 4.51 |  |  |  |  | 0.00
1989 |  |  |  | 5827.02 |  |  | 8363 |  |  |  | 710 | [10 empty] | 94.94 |  |  |  | 94.94 | [5 empty] | 93.69 |  |  | 95.47 |  |  |  | 0.39 |  | 0.37 | [8 empty] | 4.69 |  |  |  |  | 0.00
1990 |  |  |  | 5749.87 |  |  | 8265 |  |  |  | 710 | [10 empty] | 93.78 |  |  |  | 93.78 | [5 empty] | 92.45 |  |  | 94.35 |  |  |  | 1.20 |  | 1.14 | [8 empty] | 5.09 |  |  |  |  | 0.00
1991 |  |  |  | 5730.95 |  |  | 8216 |  |  |  | 710 | [10 empty] | 92.96 |  |  |  | 93.67 | [5 empty] | 92.14 |  |  | 93.79 |  |  |  | 2.10 |  | 2.01 | [8 empty] | 4.32 |  |  |  |  | 0.71
1992 |  |  |  | 5790.44 |  |  | 8306 |  |  |  | 710 | [10 empty] | 93.31 |  |  |  | 94.54 | [5 empty] | 92.85 |  |  | 94.56 |  |  |  | 1.63 |  | 1.57 | [8 empty] | 3.89 |  |  |  |  | 1.23
1993 |  |  |  | 5861.56 |  |  | 8327 |  |  |  | 710 | [10 empty] | 94.38 |  |  |  | 95.14 | [5 empty] | 94.24 |  |  | 95.06 |  |  |  | 0.16 |  | 0.15 | [8 empty] | 4.71 |  |  |  |  | 0.76
1994 |  |  |  | 5732.63 |  |  | 8130 |  |  |  | 710 | [10 empty] | 92.30 |  |  |  | 93.15 | [5 empty] | 92.17 |  |  | 92.81 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 6.76 |  |  |  |  | 0.85
1995 |  |  |  | 5747.24 |  |  | 8236 |  |  |  | 710 | [10 empty] | 92.47 |  |  |  | 93.71 | [5 empty] | 92.42 |  |  | 94.03 |  |  |  | 1.88 |  | 1.79 | [8 empty] | 4.50 |  |  |  |  | 1.24
1996 |  |  |  | 5915.41 |  |  | 8413 |  |  |  | 710 | [10 empty] | 94.96 |  |  |  | 95.29 | [5 empty] | 94.85 |  |  | 95.78 |  |  |  | 1.49 |  | 1.44 | [8 empty] | 3.27 |  |  |  |  | 0.33
1997 |  |  |  | 6077.04 |  |  | 8258 |  |  |  | 736 | [10 empty] | 93.74 |  |  |  | 94.56 | [5 empty] | 94.14 |  |  | 94.27 |  |  |  | 0.22 |  | 0.21 | [8 empty] | 5.23 |  |  |  |  | 0.82
1998 |  |  |  | 6628.46 |  |  | 8207 |  |  |  | 840 | [10 empty] | 93.23 |  |  |  | 94.29 | [5 empty] | 90.08 |  |  | 93.69 |  |  |  | 0.51 |  | 0.48 | [8 empty] | 5.22 |  |  |  |  | 1.06
1999 |  |  |  | 7091.21 |  |  | 8505 |  |  |  | 840 | [10 empty] | 96.43 |  |  |  | 96.86 | [5 empty] | 96.37 |  |  | 97.09 |  |  |  | 0.17 |  | 0.17 | [8 empty] | 2.97 |  |  |  |  | 0.43
2000 |  |  |  | 7028.90 |  |  | 8457 |  |  |  | 840 | [10 empty] | 95.31 |  |  |  | 95.93 | [5 empty] | 95.26 |  |  | 96.28 |  |  |  | 0.15 |  | 0.15 | [8 empty] | 3.92 |  |  |  |  | 0.61
2001 |  |  |  | 6988.00 |  |  | 8387 |  |  |  | 840 | [10 empty] | 95.12 |  |  |  | 95.12 | [5 empty] | 94.97 |  |  | 95.74 |  |  |  | 0.52 |  | 0.49 | [8 empty] | 4.39 |  |  |  |  | 0.00
2002 |  |  |  | 7108.51 |  |  | 8472 |  |  |  | 840 | [10 empty] | 96.79 |  |  |  | 96.96 | [5 empty] | 96.59 |  |  | 96.70 |  |  |  | 0.47 |  | 0.46 | [8 empty] | 2.58 |  |  |  |  | 0.16
2003 |  |  |  | 7026.86 |  |  | 8378 |  |  |  | 840 | [10 empty] | 95.16 |  |  |  | 95.48 | [5 empty] | 95.49 |  |  | 95.64 |  |  |  | 0.39 |  | 0.62 | [8 empty] | 3.90 |  |  |  |  | 0.33
2004 |  |  |  | 7080.70 |  |  | 8485 |  |  |  | 840 | [10 empty] | 95.81 |  |  |  | 95.81 | [5 empty] | 95.96 |  |  | 96.60 |  |  |  | 1.23 |  | 1.55 | [8 empty] | 2.64 |  |  |  |  | 0.00
2005 |  |  |  | 6996.68 |  |  | 8248 |  |  |  | 860 | [10 empty] | 93.80 |  |  |  | 93.82 | [5 empty] | 93.96 |  |  | 94.16 |  |  |  | 0.05 |  | 0.41 | [8 empty] | 5.77 |  |  |  |  | 0.01
2006 |  |  |  | 7294.36 |  |  | 8562 |  |  |  | 860 | [10 empty] | 96.37 |  |  |  | 97.43 | [5 empty] | 96.82 |  |  | 97.74 |  |  |  | 0.21 |  | 0.28 | [8 empty] | 2.29 |  |  |  |  | 1.06
2007 |  |  |  | 7051.32 |  |  | 8258 |  |  |  | 860 | [10 empty] | 93.21 |  |  |  | 94.01 | [5 empty] | 93.60 |  |  | 94.27 |  |  |  | 1.01 |  | 1.53 | [8 empty] | 4.45 |  |  |  |  | 0.81
2008 |  |  |  | 7313.82 |  |  | 8579 |  |  |  | 860 | [10 empty] | 96.29 |  |  |  | 96.94 | [5 empty] | 96.82 |  |  | 97.67 |  |  |  | 0.80 |  | 0.85 | [8 empty] | 2.21 |  |  |  |  | 0.65
2009 |  |  |  | 7156.34 |  |  | 8365 |  |  |  | 860 | [10 empty] | 94.53 |  |  |  | 95.20 | [5 empty] | 94.99 |  |  | 95.49 |  |  |  | 0.14 |  | 0.58 | [8 empty] | 4.23 |  |  |  |  | 0.66
2010 |  |  |  | 7167.34 |  |  | 8386 |  |  |  | 860 | [10 empty] | 94.59 |  |  |  | 95.29 | [5 empty] | 95.14 |  |  | 95.73 |  |  |  | 1.45 |  | 2.03 | [8 empty] | 2.67 |  |  |  |  | 0.70
2011 |  |  |  | 6913.53 |  |  | 7987 |  |  |  | 880 | [10 empty] | 89.88 |  |  |  | 90.69 | [5 empty] | 90.71 |  |  | 91.18 |  |  |  | 0.39 |  | 1.31 | [8 empty] | 8.00 |  |  |  |  | 0.81
2012 |  |  |  | 7477.19 |  |  | 8561 |  |  |  | 880 | [10 empty] | 95.85 |  |  |  | 97.30 | [5 empty] | 96.73 |  |  | 97.46 |  |  |  | 0.00 |  | 0.37 | [8 empty] | 2.32 |  |  |  |  | 1.46
2013 |  |  |  | 7162.81 |  |  | 8171 |  |  |  | 880 | [10 empty] | 92.03 |  |  |  | 93.11 | [5 empty] | 92.92 |  |  | 93.28 |  |  |  | 1.98 |  | 2.15 | [8 empty] | 4.74 |  |  |  |  | 1.09
2014 |  |  |  | 7496.54 |  |  | 8567 |  |  |  | 880 | [10 empty] | 96.75 |  |  |  | 97.61 | [5 empty] | 97.25 |  |  | 97.80 |  |  |  | 0.15 |  | 0.20 | [8 empty] | 2.19 |  |  |  |  | 0.86
2015 |  |  |  | 6863.99 |  |  | 7856 |  |  |  | 880 | [10 empty] | 88.52 |  |  |  | 89.08 | [5 empty] | 89.04 |  |  | 89.68 |  |  |  | 6.32 |  | 6.70 | [8 empty] | 4.22 |  |  |  |  | 0.56
2016 |  |  |  | 7300.52 |  |  | 8381 |  |  |  | 880 | [10 empty] | 93.78 |  |  |  | 94.58 | [5 empty] | 94.45 |  |  | 95.41 |  |  |  | 2.81 |  | 3.03 | [8 empty] | 2.39 |  |  |  |  | 0.80
2017 |  |  |  | 6256.41 |  |  | 7132 |  |  |  | 880 | [10 empty] | 80.36 |  |  |  | 80.53 | [5 empty] | 81.16 |  |  | 81.42 |  |  |  | 1.89 |  | 7.84 | [8 empty] | 11.63 |  |  |  |  | 0.17
2018 |  |  |  | 7333.77 |  |  | 8350 |  |  |  | 890 | [10 empty] | 95.01 |  |  |  | 95.65 | [5 empty] | 94.07 |  |  | 95.32 |  |  |  | 0.45 |  | 1.27 | [8 empty] | 3.09 |  |  |  |  | 0.64
2019 |  |  |  | 7209.08 |  |  | 8162 |  |  |  | 890 | [10 empty] | 92.33 |  |  |  | 92.95 | [5 empty] | 92.47 |  |  | 93.17 |  |  |  | 1.16 |  | 1.16 | [8 empty] | 5.88 |  |  |  |  | 0.63
2020 |  |  |  | 7276.55 |  |  | 8289 |  |  |  | 890 | [10 empty] | 93.13 |  |  |  | 93.97 | [5 empty] | 93.08 |  |  | 94.36 |  |  |  | 2.87 |  | 3.58 | [8 empty] | 2.45 |  |  |  |  | 0.84
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1982 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 299 | [14 empty] | 312
B. |  | Refuelling without maintenance | [35 empty] | 35
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 197 | [14 empty] | 355
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 8
E. |  | Testing of plant systems or components | [35 empty] | 18 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 26
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 12
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
P. |  | Fire | [39 empty] | 0
Z. |  | Other | [39 empty] | 1 | [11 empty] | 0
Subtotal | [22 empty] | 197 |  |  |  | 299 | [10 empty] | 442 |  |  |  | 322 | [11 empty] | 16
Total | [22 empty] | 496 | [14 empty] | 780
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1982 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 22
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [19 empty] | 228 | [14 empty] | 21
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
32. |  |  | Feedwater and Main Steam System | [19 empty] | 71 | [14 empty] | 10
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 224
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [22 empty] | 299 | [14 empty] | 296
Highlights (2020)
The plant units operated safely. OL1's net production was 7,310 (7,542) GWh and load factor 93.7 (96.9)%. OL2's net production was 7,277 (7,209) GWh and load factor 93.3 (92.7)%. There was a disturbance at the OL2 plant unit in December, when the plant unit was suddenly disconnected from the grid, and a site area emergency was declared at the unit. The disturbance soon proved to be less serious than a site area emergency, and the plant unit was driven into a cold shutdown state. The situation was caused due to hot water moving into the filters of the reactor water clean-up system. The plant's safety systems operated as planned, and the disturbance did not cause harm to people or the environment. The 2020 annual outages of the Olkiluoto nuclear power plant were started with a refuelling outage at the OL2 plant unit on 10 May. The refueling outage was completed on 21 May. The annual outage carried out at the OL1 plant unit was a maintenance outage, which started on 24 May and was completed on 8 June. The duration of the plant unit's annual outage was shortened in March from the planned 25 days to 14 days due to the COVID-19 pandemic. Numerous special procedures and arrangements were put in place during the annual outages to protect people's health in Olkiluoto and prevent the possible spread of the virus, as well as to ensure a safe and high-quality annual outage. Modernizations and repair work with safety and availability significance were completed during the annual outages. Other planned modernizations were transferred to be completed in upcoming outages. Preventive maintenance was carried out normally according to the preventive maintenance programme. A significant task was the modernization of the bushing modules of one containment, which was completed for the first time. Other significant tasks were the modernization of the valve actuator in the cooling system of the shut down reactor as well as the changing of two valves, the connection of the recirculation line to one subsystem in auxiliary feed water systems, as well as repair works, preventive maintenance, inspections, and testing.