## BELLEVILLE-1
2020 Operating Experience
FR-54 | [8 empty] | BELLEVILLE-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-05-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-10-14
Gross electrical power | [12 empty] | : |  |  | 1363 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-06-01
Reference unit power (net) | [12 empty] | : |  |  | 1310 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.25 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 51 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4590.82 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.46 %
Energy Availability Factor (EAF) | [18 empty] | : | 39.9 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.22 %
Unit Capability Factor (UCF) | [18 empty] | : | 48.36 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 51.42 %
Load Factor (LF) | [18 empty] | : | 39.9 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 8.46 %
Operating Factor (OF) | [18 empty] | : | 42.88 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 5017 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 969.94 | 907.48 |  |  |  | 968.19 |  | 842.37 | [8 empty] | 788.51 |  |  | 114.34 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4590.82
EAF [%] |  |  |  |  | 99.48 | 99.51 |  |  |  | 99.45 |  | 89.34 | [8 empty] | 80.92 |  |  | 12.14 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 39.90
UCF [%] |  |  |  |  | 99.89 | 100.00 |  |  |  | 99.91 |  | 97.45 | [8 empty] | 100.00 |  |  | 16.42 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 67.48 |  |  | 48.36
LF [%] |  |  |  |  | 99.52 | 99.53 |  |  |  | 99.47 |  | 89.31 | [8 empty] | 80.90 |  |  | 12.12 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 39.90
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 16.67 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 42.88
FLR [%] |  |  |  |  | 0.09 | 0.00 |  |  |  | 0.08 |  | 2.55 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.46
UCL [%] |  |  |  |  | 0.09 | 0.00 |  |  |  | 0.08 |  | 2.55 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.22
PUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 83.58 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 32.52 |  |  | 51.42
XUF [%] |  |  |  |  | 0.41 | 0.49 |  |  |  | 0.46 |  | 8.11 | [8 empty] | 19.08 |  |  | 4.28 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 67.47 |  |  | 8.46
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 267598.41 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.42 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.48 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.45 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.04 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.51 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.66 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.56 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.59 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 6283.00 |  |  | 6478 |  |  |  | 1310 | [10 empty] | 85.78 |  |  |  | 86.06 | [5 empty] | 64.40 |  |  | 86.06 |  |  |  | 13.94 |  | 13.94 | [8 empty] | 0.00 |  |  |  |  | 0.28
1989 |  |  |  | 5152.56 |  |  | 4244 |  |  |  | 1310 | [10 empty] | 45.97 |  |  |  | 46.53 | [5 empty] | 44.90 |  |  | 48.45 |  |  |  | 30.63 |  | 20.55 | [8 empty] | 32.93 |  |  |  |  | 0.55
1990 |  |  |  | 7914.26 |  |  | 6408 |  |  |  | 1310 | [10 empty] | 71.15 |  |  |  | 71.43 | [5 empty] | 68.97 |  |  | 73.15 |  |  |  | 12.19 |  | 9.92 | [8 empty] | 18.66 |  |  |  |  | 0.27
1991 |  |  |  | 8660.21 |  |  | 7092 |  |  |  | 1310 | [10 empty] | 79.28 |  |  |  | 80.80 | [5 empty] | 75.47 |  |  | 80.96 |  |  |  | 5.38 |  | 4.59 | [8 empty] | 14.61 |  |  |  |  | 1.51
1992 |  |  |  | 8494.33 |  |  | 7600 |  |  |  | 1310 | [10 empty] | 91.19 |  |  |  | 91.82 | [5 empty] | 73.82 |  |  | 86.52 |  |  |  | 6.07 |  | 5.94 | [8 empty] | 2.25 |  |  |  |  | 0.63
1993 |  |  |  | 7921.46 |  |  | 6873 |  |  |  | 1310 | [10 empty] | 71.25 |  |  |  | 77.46 | [5 empty] | 69.03 |  |  | 78.46 |  |  |  | 7.73 |  | 6.49 | [8 empty] | 16.05 |  |  |  |  | 6.21
1994 |  |  |  | 6575.76 |  |  | 5848 |  |  |  | 1310 | [10 empty] | 63.98 |  |  |  | 65.16 | [5 empty] | 57.30 |  |  | 66.76 |  |  |  | 24.97 |  | 21.69 | [8 empty] | 13.15 |  |  |  |  | 1.18
1995 |  |  |  | 7740.91 |  |  | 6796 |  |  |  | 1310 | [10 empty] | 73.44 |  |  |  | 76.23 | [5 empty] | 67.46 |  |  | 77.58 |  |  |  | 8.01 |  | 6.64 | [8 empty] | 17.14 |  |  |  |  | 2.79
1996 |  |  |  | 7365.06 |  |  | 6002 |  |  |  | 1310 | [10 empty] | 76.49 |  |  |  | 76.80 | [5 empty] | 64.00 |  |  | 68.33 |  |  |  | 12.12 |  | 10.59 | [8 empty] | 12.61 |  |  |  |  | 0.30
1997 |  |  |  | 9785.27 |  |  | 8294 |  |  |  | 1310 | [10 empty] | 93.24 |  |  |  | 93.41 | [5 empty] | 85.27 |  |  | 94.68 |  |  |  | 5.22 |  | 5.14 | [8 empty] | 1.44 |  |  |  |  | 0.18
1998 |  |  |  | 5740.91 |  |  | 4865 |  |  |  | 1310 | [10 empty] | 51.18 |  |  |  | 53.72 | [5 empty] | 50.03 |  |  | 55.54 |  |  |  | 38.57 |  | 33.73 | [8 empty] | 12.56 |  |  |  |  | 2.54
1999 |  |  |  | 9580.49 |  |  | 7957 |  |  |  | 1310 | [10 empty] | 90.43 |  |  |  | 91.97 | [5 empty] | 83.49 |  |  | 90.83 |  |  |  | 1.39 |  | 1.30 | [8 empty] | 6.73 |  |  |  |  | 1.54
2000 |  |  |  | 4238.57 |  |  | 3459 |  |  |  | 1310 | [10 empty] | 37.89 |  |  |  | 37.99 | [5 empty] | 36.83 |  |  | 39.38 |  |  |  | 9.13 |  | 3.82 | [8 empty] | 58.19 |  |  |  |  | 0.10
2001 |  |  |  | 9564.53 |  |  | 7774 |  |  |  | 1310 | [10 empty] | 86.79 |  |  |  | 87.31 | [5 empty] | 83.35 |  |  | 88.74 |  |  |  | 2.17 |  | 1.94 | [8 empty] | 10.75 |  |  |  |  | 0.52
2002 |  |  |  | 9567.30 |  |  | 8447 |  |  |  | 1310 | [10 empty] | 98.94 |  |  |  | 99.55 | [5 empty] | 83.37 |  |  | 96.43 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 0.32 |  |  |  |  | 0.62
2003 |  |  |  | 8401.73 |  |  | 6871 |  |  |  | 1310 | [10 empty] | 75.45 |  |  |  | 77.63 | [5 empty] | 73.21 |  |  | 78.44 |  |  |  | 8.55 |  | 7.26 | [8 empty] | 15.11 |  |  |  |  | 2.19
2004 |  |  |  | 9291.01 |  |  | 7645 |  |  |  | 1310 | [10 empty] | 88.02 |  |  |  | 88.59 | [5 empty] | 80.73 |  |  | 87.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.41 |  |  |  |  | 0.57
2005 |  |  |  | 10236.41 |  |  | 8646 |  |  |  | 1310 | [10 empty] | 97.11 |  |  |  | 98.77 | [5 empty] | 89.19 |  |  | 98.69 |  |  |  | 1.21 |  | 1.21 | [8 empty] | 0.02 |  |  |  |  | 1.66
2006 |  |  |  | 7926.72 |  |  | 6870 |  |  |  | 1310 | [10 empty] | 74.83 |  |  |  | 77.06 | [5 empty] | 69.07 |  |  | 78.42 |  |  |  | 2.85 |  | 2.54 | [8 empty] | 20.41 |  |  |  |  | 2.23
2007 |  |  |  | 8512.07 |  |  | 7213 |  |  |  | 1310 | [10 empty] | 75.83 |  |  |  | 77.52 | [5 empty] | 74.18 |  |  | 82.34 |  |  |  | 7.36 |  | 14.23 | [8 empty] | 8.25 |  |  |  |  | 1.69
2008 |  |  |  | 6304.96 |  |  | 5615 |  |  |  | 1310 | [10 empty] | 55.20 |  |  |  | 55.31 | [5 empty] | 54.79 |  |  | 63.92 |  |  |  | 21.25 |  | 25.63 | [8 empty] | 19.05 |  |  |  |  | 0.11
2009 |  |  |  | 10402.30 |  |  | 8350 |  |  |  | 1310 | [10 empty] | 92.08 |  |  |  | 93.04 | [5 empty] | 90.65 |  |  | 95.32 |  |  |  | 6.93 |  | 6.92 | [8 empty] | 0.04 |  |  |  |  | 0.96
2010 |  |  |  | 6650.30 |  |  | 5370 |  |  |  | 1310 | [10 empty] | 58.15 |  |  |  | 59.20 | [5 empty] | 57.95 |  |  | 61.30 |  |  |  | 3.94 |  | 10.48 | [8 empty] | 30.32 |  |  |  |  | 1.04
2011 |  |  |  | 7876.28 |  |  | 6525 |  |  |  | 1310 | [10 empty] | 71.77 |  |  |  | 73.05 | [5 empty] | 68.63 |  |  | 74.49 |  |  |  | 2.44 |  | 8.05 | [8 empty] | 18.90 |  |  |  |  | 1.28
2012 |  |  |  | 10483.62 |  |  | 8691 |  |  |  | 1310 | [10 empty] | 97.02 |  |  |  | 98.09 | [5 empty] | 91.11 |  |  | 98.94 |  |  |  | 1.82 |  | 1.82 | [8 empty] | 0.09 |  |  |  |  | 1.07
2013 |  |  |  | 8658.64 |  |  | 7309 |  |  |  | 1310 | [10 empty] | 80.18 |  |  |  | 82.02 | [5 empty] | 75.45 |  |  | 83.44 |  |  |  | 1.60 |  | 7.40 | [8 empty] | 10.59 |  |  |  |  | 1.84
2014 |  |  |  | 7723.74 |  |  | 6391 |  |  |  | 1310 | [10 empty] | 70.68 |  |  |  | 71.19 | [5 empty] | 67.31 |  |  | 72.96 |  |  |  | 7.15 |  | 7.79 | [8 empty] | 21.01 |  |  |  |  | 0.51
2015 |  |  |  | 10451.61 |  |  | 8660 |  |  |  | 1310 | [10 empty] | 98.29 |  |  |  | 99.02 | [5 empty] | 91.08 |  |  | 98.86 |  |  |  | 0.96 |  | 0.96 | [8 empty] | 0.02 |  |  |  |  | 0.74
2016 |  |  |  | 8593.89 |  |  | 7106 |  |  |  | 1310 | [10 empty] | 75.60 |  |  |  | 78.78 | [5 empty] | 74.68 |  |  | 80.90 |  |  |  | 4.70 |  | 5.82 | [8 empty] | 15.39 |  |  |  |  | 3.19
2017 |  |  |  | 6191.21 |  |  | 4991 |  |  |  | 1310 | [10 empty] | 54.88 |  |  |  | 55.44 | [5 empty] | 53.95 |  |  | 56.97 |  |  |  | 4.33 |  | 25.13 | [8 empty] | 19.43 |  |  |  |  | 0.56
2018 |  |  |  | 9375.77 |  |  | 7412 |  |  |  | 1310 | [10 empty] | 82.19 |  |  |  | 84.49 | [5 empty] | 81.70 |  |  | 84.61 |  |  |  | 1.42 |  | 2.29 | [8 empty] | 13.21 |  |  |  |  | 2.30
2019 |  |  |  | 10111.20 |  |  | 8130 |  |  |  | 1310 | [10 empty] | 91.04 |  |  |  | 92.33 | [5 empty] | 88.11 |  |  | 92.81 |  |  |  | 0.30 |  | 7.09 | [8 empty] | 0.58 |  |  |  |  | 1.29
2020 |  |  |  | 4590.82 |  |  | 3767 |  |  |  | 1310 | [10 empty] | 39.90 |  |  |  | 48.36 | [5 empty] | 39.90 |  |  | 42.88 |  |  |  | 0.46 |  | 0.22 | [8 empty] | 51.42 |  |  |  |  | 8.46
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 552
B. |  | Refuelling without maintenance | [35 empty] | 101
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 4513 | [14 empty] | 1118 |  |  |  | 7
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 6
E. |  | Testing of plant systems or components | [35 empty] | 39 |  |  |  | 2 | [11 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 72
L. |  | Human factor related | [39 empty] | 16
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [31 empty] | 481 | [19 empty] | 16
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [31 empty] | 21 | [7 empty] | 2 | [11 empty] | 46
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 1
Z. |  | Other | [39 empty] | 18
Subtotal | [22 empty] | 4513 | [10 empty] | 502 |  |  |  | 1264 |  |  |  | 669 | [11 empty] | 64
Total | [22 empty] | 5015 | [14 empty] | 1997
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 21
12. |  |  | Reactor I&C Systems | [34 empty] | 55
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 41
14. |  |  | Safety Systems | [34 empty] | 28
15. |  |  | Reactor Cooling Systems | [34 empty] | 29
16. |  |  | Steam generation systems | [34 empty] | 42
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 57
32. |  |  | Feedwater and Main Steam System | [34 empty] | 62
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 143
35. |  |  | All other I&C Systems | [34 empty] | 10
41. |  |  | Main Generator Systems | [34 empty] | 33
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [37 empty] | 544

## BELLEVILLE-2
2020 Operating Experience
FR-55 | [8 empty] | BELLEVILLE-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-08-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-07-06
Gross electrical power | [12 empty] | : |  |  | 1363 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-01-01
Reference unit power (net) | [12 empty] | : |  |  | 1310 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.25 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10421.33 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.34 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.84 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.33 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.41 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.26 %
Load Factor (LF) | [18 empty] | : | 90.56 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.57 %
Operating Factor (OF) | [18 empty] | : | 97.96 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 179 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 920.96 | 785.44 |  |  |  | 829.39 |  | 770.37 | [8 empty] | 809.06 |  |  | 816.76 | [6 empty] | 853.82 |  | 900.71 |  |  |  | 921.78 |  |  | 939.00 |  |  | 915.52 | [9 empty] | 958.53 |  |  | 10421.33
EAF [%] |  |  |  |  | 94.50 | 95.14 |  |  |  | 97.67 |  | 99.62 | [8 empty] | 96.67 |  |  | 90.87 | [6 empty] | 87.62 |  | 92.44 |  |  |  | 97.82 |  |  | 98.81 |  |  | 99.35 | [9 empty] | 99.73 |  |  | 95.84
UCF [%] |  |  |  |  | 94.65 | 99.89 |  |  |  | 99.68 |  | 99.97 | [8 empty] | 97.50 |  |  | 92.34 | [6 empty] | 90.51 |  | 95.19 |  |  |  | 99.91 |  |  | 99.74 |  |  | 99.88 | [9 empty] | 99.93 |  |  | 97.41
LF [%] |  |  |  |  | 94.49 | 86.15 |  |  |  | 85.21 |  | 81.68 | [8 empty] | 83.01 |  |  | 86.59 | [6 empty] | 87.60 |  | 92.41 |  |  |  | 97.73 |  |  | 96.21 |  |  | 97.07 | [9 empty] | 98.35 |  |  | 90.56
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 96.91 |  |  | 92.50 | [6 empty] | 90.73 |  | 95.83 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.96
FLR [%] |  |  |  |  | 3.00 | 0.02 |  |  |  | 0.26 |  | 0.03 | [8 empty] | 2.44 |  |  | 7.64 | [6 empty] | 9.39 |  | 4.77 |  |  |  | 0.00 |  |  | 0.23 |  |  | 0.08 | [9 empty] | 0.00 |  |  | 2.34
UCL [%] |  |  |  |  | 2.93 | 0.02 |  |  |  | 0.26 |  | 0.03 | [8 empty] | 2.43 |  |  | 7.64 | [6 empty] | 9.38 |  | 4.77 |  |  |  | 0.00 |  |  | 0.23 |  |  | 0.08 | [9 empty] | 0.00 |  |  | 2.33
PUF [%] |  |  |  |  | 2.42 | 0.08 |  |  |  | 0.06 |  | 0.01 | [8 empty] | 0.07 |  |  | 0.02 | [6 empty] | 0.11 |  | 0.05 |  |  |  | 0.09 |  |  | 0.02 |  |  | 0.04 | [9 empty] | 0.07 |  |  | 0.26
XUF [%] |  |  |  |  | 0.16 | 4.75 |  |  |  | 2.01 |  | 0.35 | [8 empty] | 0.83 |  |  | 1.47 | [6 empty] | 2.90 |  | 2.75 |  |  |  | 2.09 |  |  | 0.93 |  |  | 0.53 | [9 empty] | 0.20 |  |  | 1.57
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 266620.39 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.05 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.1 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.85 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.94 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.21 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.05 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.84 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.26 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 8505.66 |  |  | 7419 |  |  |  | 1310 | [10 empty] | 86.64 |  |  |  | 86.97 | [5 empty] | 74.12 |  |  | 84.69 |  |  |  | 12.32 |  | 12.23 | [8 empty] | 0.80 |  |  |  |  | 0.33
1990 |  |  |  | 6323.98 |  |  | 5350 |  |  |  | 1310 | [10 empty] | 56.88 |  |  |  | 58.44 | [5 empty] | 55.11 |  |  | 61.07 |  |  |  | 15.85 |  | 11.01 | [8 empty] | 30.55 |  |  |  |  | 1.56
1991 |  |  |  | 7876.29 |  |  | 6578 |  |  |  | 1310 | [10 empty] | 70.27 |  |  |  | 73.35 | [5 empty] | 68.64 |  |  | 75.09 |  |  |  | 11.31 |  | 9.35 | [8 empty] | 17.30 |  |  |  |  | 3.08
1992 |  |  |  | 8262.05 |  |  | 6904 |  |  |  | 1310 | [10 empty] | 75.27 |  |  |  | 75.86 | [5 empty] | 71.80 |  |  | 78.60 |  |  |  | 8.44 |  | 7.00 | [8 empty] | 17.15 |  |  |  |  | 0.59
1993 |  |  |  | 8871.34 |  |  | 7435 |  |  |  | 1310 | [10 empty] | 80.13 |  |  |  | 83.38 | [5 empty] | 77.31 |  |  | 84.87 |  |  |  | 1.52 |  | 1.28 | [8 empty] | 15.33 |  |  |  |  | 3.25
1994 |  |  |  | 8241.32 |  |  | 7122 |  |  |  | 1310 | [10 empty] | 76.93 |  |  |  | 80.38 | [5 empty] | 71.82 |  |  | 81.30 |  |  |  | 4.04 |  | 3.39 | [8 empty] | 16.23 |  |  |  |  | 3.45
1995 |  |  |  | 7960.50 |  |  | 7438 |  |  |  | 1310 | [10 empty] | 97.53 |  |  |  | 99.26 | [5 empty] | 69.37 |  |  | 84.91 |  |  |  | 0.58 |  | 0.58 | [8 empty] | 0.16 |  |  |  |  | 1.73
1996 |  |  |  | 7229.81 |  |  | 6666 |  |  |  | 1310 | [10 empty] | 71.15 |  |  |  | 74.45 | [5 empty] | 62.83 |  |  | 75.89 |  |  |  | 13.79 |  | 11.91 | [8 empty] | 13.64 |  |  |  |  | 3.30
1997 |  |  |  | 8508.10 |  |  | 7339 |  |  |  | 1310 | [10 empty] | 82.04 |  |  |  | 84.87 | [5 empty] | 74.14 |  |  | 83.78 |  |  |  | 1.24 |  | 1.07 | [8 empty] | 14.07 |  |  |  |  | 2.83
1998 |  |  |  | 5068.01 |  |  | 4239 |  |  |  | 1310 | [10 empty] | 45.03 |  |  |  | 45.03 | [5 empty] | 44.16 |  |  | 48.39 |  |  |  | 54.74 |  | 54.45 | [8 empty] | 0.51 |  |  |  |  | 0.01
1999 |  |  |  | 4899.26 |  |  | 4040 |  |  |  | 1310 | [10 empty] | 43.32 |  |  |  | 44.82 | [5 empty] | 42.69 |  |  | 46.12 |  |  |  | 7.10 |  | 3.43 | [8 empty] | 51.75 |  |  |  |  | 1.50
2000 |  |  |  | 9882.48 |  |  | 8271 |  |  |  | 1310 | [10 empty] | 96.68 |  |  |  | 97.43 | [5 empty] | 85.88 |  |  | 94.16 |  |  |  | 2.11 |  | 2.10 | [8 empty] | 0.47 |  |  |  |  | 0.75
2001 |  |  |  | 8457.97 |  |  | 6935 |  |  |  | 1310 | [10 empty] | 78.58 |  |  |  | 79.16 | [5 empty] | 73.70 |  |  | 79.17 |  |  |  | 8.87 |  | 7.71 | [8 empty] | 13.14 |  |  |  |  | 0.57
2002 |  |  |  | 9378.75 |  |  | 7687 |  |  |  | 1310 | [10 empty] | 84.29 |  |  |  | 86.15 | [5 empty] | 81.73 |  |  | 87.75 |  |  |  | 2.17 |  | 1.91 | [8 empty] | 11.94 |  |  |  |  | 1.86
2003 |  |  |  | 8624.72 |  |  | 7135 |  |  |  | 1310 | [10 empty] | 79.44 |  |  |  | 80.37 | [5 empty] | 75.16 |  |  | 81.45 |  |  |  | 7.22 |  | 6.25 | [8 empty] | 13.37 |  |  |  |  | 0.93
2004 |  |  |  | 10202.59 |  |  | 8621 |  |  |  | 1310 | [10 empty] | 97.05 |  |  |  | 98.01 | [5 empty] | 88.66 |  |  | 98.14 |  |  |  | 1.97 |  | 1.97 | [8 empty] | 0.03 |  |  |  |  | 0.95
2005 |  |  |  | 9242.31 |  |  | 7767 |  |  |  | 1310 | [10 empty] | 84.39 |  |  |  | 86.90 | [5 empty] | 80.53 |  |  | 88.65 |  |  |  | 0.73 |  | 3.01 | [8 empty] | 10.09 |  |  |  |  | 2.51
2006 |  |  |  | 8743.63 |  |  | 7309 |  |  |  | 1310 | [10 empty] | 79.06 |  |  |  | 81.71 | [5 empty] | 76.19 |  |  | 83.44 |  |  |  | 1.88 |  | 2.91 | [8 empty] | 15.38 |  |  |  |  | 2.65
2007 |  |  |  | 9516.03 |  |  | 7895 |  |  |  | 1310 | [10 empty] | 88.63 |  |  |  | 89.44 | [5 empty] | 82.92 |  |  | 90.13 |  |  |  | 2.27 |  | 2.63 | [8 empty] | 7.94 |  |  |  |  | 0.81
2008 |  |  |  | 9734.88 |  |  | 8327 |  |  |  | 1310 | [10 empty] | 92.36 |  |  |  | 92.61 | [5 empty] | 84.60 |  |  | 94.80 |  |  |  | 1.98 |  | 6.39 | [8 empty] | 1.00 |  |  |  |  | 0.25
2009 |  |  |  | 6310.85 |  |  | 5166 |  |  |  | 1310 | [10 empty] | 55.55 |  |  |  | 62.73 | [5 empty] | 54.99 |  |  | 58.97 |  |  |  | 1.45 |  | 10.48 | [8 empty] | 26.79 |  |  |  |  | 7.18
2010 |  |  |  | 7869.74 |  |  | 6361 |  |  |  | 1310 | [10 empty] | 70.02 |  |  |  | 73.51 | [5 empty] | 68.58 |  |  | 72.61 |  |  |  | 2.31 |  | 4.98 | [8 empty] | 21.51 |  |  |  |  | 3.49
2011 |  |  |  | 10390.88 |  |  | 8727 |  |  |  | 1310 | [10 empty] | 96.07 |  |  |  | 98.36 | [5 empty] | 90.55 |  |  | 99.62 |  |  |  | 1.07 |  | 1.07 | [8 empty] | 0.58 |  |  |  |  | 2.28
2012 |  |  |  | 8959.34 |  |  | 7456 |  |  |  | 1310 | [10 empty] | 81.86 |  |  |  | 84.76 | [5 empty] | 77.86 |  |  | 84.88 |  |  |  | 1.03 |  | 6.41 | [8 empty] | 8.83 |  |  |  |  | 2.89
2013 |  |  |  | 7480.48 |  |  | 6273 |  |  |  | 1310 | [10 empty] | 69.44 |  |  |  | 71.15 | [5 empty] | 65.19 |  |  | 71.61 |  |  |  | 3.40 |  | 9.79 | [8 empty] | 19.06 |  |  |  |  | 1.71
2014 |  |  |  | 10177.69 |  |  | 8753 |  |  |  | 1310 | [10 empty] | 98.91 |  |  |  | 99.44 | [5 empty] | 88.69 |  |  | 99.92 |  |  |  | 0.53 |  | 0.53 | [8 empty] | 0.03 |  |  |  |  | 0.54
2015 |  |  |  | 9264.45 |  |  | 7444 |  |  |  | 1310 | [10 empty] | 81.50 |  |  |  | 84.06 | [5 empty] | 80.73 |  |  | 84.98 |  |  |  | 2.65 |  | 2.29 | [8 empty] | 13.65 |  |  |  |  | 2.56
2016 |  |  |  | 8068.56 |  |  | 6779 |  |  |  | 1310 | [10 empty] | 72.65 |  |  |  | 73.67 | [5 empty] | 70.12 |  |  | 77.17 |  |  |  | 2.11 |  | 5.83 | [8 empty] | 20.50 |  |  |  |  | 1.03
2017 |  |  |  | 8376.52 |  |  | 6633 |  |  |  | 1310 | [10 empty] | 75.05 |  |  |  | 75.51 | [5 empty] | 72.99 |  |  | 75.72 |  |  |  | 1.17 |  | 12.12 | [8 empty] | 12.36 |  |  |  |  | 0.47
2018 |  |  |  | 7508.77 |  |  | 6173 |  |  |  | 1310 | [10 empty] | 65.77 |  |  |  | 67.09 | [5 empty] | 65.43 |  |  | 70.47 |  |  |  | 5.52 |  | 31.75 | [8 empty] | 1.16 |  |  |  |  | 1.32
2019 |  |  |  | 4402.58 |  |  | 3481 |  |  |  | 1310 | [10 empty] | 38.58 |  |  |  | 39.65 | [5 empty] | 38.36 |  |  | 39.74 |  |  |  | 5.69 |  | 13.16 | [8 empty] | 47.19 |  |  |  |  | 1.07
2020 |  |  |  | 10421.33 |  |  | 8605 |  |  |  | 1310 | [10 empty] | 95.84 |  |  |  | 97.41 | [5 empty] | 90.56 |  |  | 97.96 |  |  |  | 2.34 |  | 2.33 | [8 empty] | 0.26 |  |  |  |  | 1.57
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 466
B. |  | Refuelling without maintenance | [35 empty] | 68
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1012
E. |  | Testing of plant systems or components | [35 empty] | 32
H. |  | Nuclear regulatory requirements | [39 empty] | 97
L. |  | Human factor related | [39 empty] | 17
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 2 | [11 empty] | 33
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 3
Z. |  | Other | [39 empty] | 38 | [11 empty] | 1
Subtotal | [37 empty] | 1112 |  |  |  | 620 | [11 empty] | 38
Total | [22 empty] | 0 | [14 empty] | 1770
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 29
12. |  |  | Reactor I&C Systems | [34 empty] | 45
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 33
16. |  |  | Steam generation systems | [34 empty] | 28
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 7
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 11
31. |  |  | Turbine and auxiliaries | [34 empty] | 35
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 203
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [37 empty] | 457

## BLAYAIS-1
2020 Operating Experience
FR-32 | [8 empty] | BLAYAIS-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-01-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-06-12
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-12-01
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4983.14 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 11.21 %
Energy Availability Factor (EAF) | [18 empty] | : | 64.34 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 12.39 %
Unit Capability Factor (UCF) | [18 empty] | : | 66.26 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.35 %
Load Factor (LF) | [18 empty] | : | 62.34 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.92 %
Operating Factor (OF) | [18 empty] | : | 65.87 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2998 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 668.33 | 610.71 |  |  |  | 620.08 |  | 583.13 | [8 empty] | 645.50 |  |  | 473.23 | [6 empty] | 163.85 |  | 416.02 |  |  |  | 0.00 |  |  | 0.00 |  |  | 116.19 | [9 empty] | 686.10 |  |  | 4983.14
EAF [%] |  |  |  |  | 98.81 | 99.94 |  |  |  | 95.97 |  | 99.63 | [8 empty] | 99.84 |  |  | 72.62 | [6 empty] | 26.36 |  | 61.46 |  |  |  | 0.00 |  |  | 0.00 |  |  | 17.73 | [9 empty] | 99.93 |  |  | 64.34
UCF [%] |  |  |  |  | 100.00 | 99.94 |  |  |  | 99.90 |  | 99.64 | [8 empty] | 99.91 |  |  | 73.40 | [6 empty] | 27.33 |  | 67.56 |  |  |  | 0.00 |  |  | 0.00 |  |  | 27.72 | [9 empty] | 99.93 |  |  | 66.26
LF [%] |  |  |  |  | 98.71 | 96.42 |  |  |  | 91.71 |  | 89.00 | [8 empty] | 95.34 |  |  | 72.23 | [6 empty] | 24.20 |  | 61.45 |  |  |  | 0.00 |  |  | 0.00 |  |  | 17.73 | [9 empty] | 101.34 |  |  | 62.34
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 96.37 |  | 100.00 | [8 empty] | 100.00 |  |  | 73.47 | [6 empty] | 25.54 |  | 67.88 |  |  |  | 0.00 |  |  | 0.00 |  |  | 27.50 | [9 empty] | 100.00 |  |  | 65.87
FLR [%] |  |  |  |  | 0.00 | 0.02 |  |  |  | 0.10 |  | 0.20 | [8 empty] | 0.06 |  |  | 26.60 | [6 empty] | 72.67 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 11.21
UCL [%] |  |  |  |  | 0.00 | 0.02 |  |  |  | 0.10 |  | 0.20 | [8 empty] | 0.06 |  |  | 26.59 | [6 empty] | 72.67 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 49.10 | [9 empty] | 0.00 |  |  | 12.39
PUF [%] |  |  |  |  | 0.00 | 0.05 |  |  |  | 0.00 |  | 0.16 | [8 empty] | 0.02 |  |  | 0.00 | [6 empty] | 0.00 |  | 32.44 |  |  |  | 100.00 |  |  | 100.00 |  |  | 23.18 | [9 empty] | 0.07 |  |  | 21.35
XUF [%] |  |  |  |  | 1.19 | 0.00 |  |  |  | 3.93 |  | 0.01 | [8 empty] | 0.07 |  |  | 0.78 | [6 empty] | 0.97 |  | 6.10 |  |  |  | 0.00 |  |  | 0.00 |  |  | 9.99 | [9 empty] | 0.00 |  |  | 1.92
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 227797.83 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.55 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.39 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.61 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.73 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.85 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 1636.20 |  |  | 2584 |  |  |  | 915 | [10 empty] | 65.60 |  |  |  | 65.60 | [5 empty] | 65.60 |  |  | 70.16 |  |  |  | 7.37 |  | 5.22 | [8 empty] | 29.18 |  |  |  |  | 0.00
1982 |  |  |  | 6129.80 |  |  | 7588 |  |  |  | 910 | [10 empty] | 81.46 |  |  |  | 81.46 | [5 empty] | 76.90 |  |  | 86.62 |  |  |  | 18.54 |  | 18.54 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 3453.00 |  |  | 4285 |  |  |  | 910 | [10 empty] | 43.92 |  |  |  | 43.92 | [5 empty] | 43.32 |  |  | 48.92 |  |  |  | 31.78 |  | 20.46 | [8 empty] | 35.62 |  |  |  |  | 0.00
1984 |  |  |  | 6509.00 |  |  | 7536 |  |  |  | 910 | [10 empty] | 84.55 |  |  |  | 84.55 | [5 empty] | 81.43 |  |  | 85.79 |  |  |  | 7.30 |  | 6.66 | [8 empty] | 8.79 |  |  |  |  | 0.00
1985 |  |  |  | 6225.20 |  |  | 7348 |  |  |  | 910 | [10 empty] | 82.83 |  |  |  | 82.96 | [5 empty] | 78.09 |  |  | 83.88 |  |  |  | 3.26 |  | 2.79 | [8 empty] | 14.24 |  |  |  |  | 0.14
1986 |  |  |  | 6460.60 |  |  | 7754 |  |  |  | 910 | [10 empty] | 86.95 |  |  |  | 87.82 | [5 empty] | 81.05 |  |  | 88.52 |  |  |  | 2.13 |  | 1.91 | [8 empty] | 10.26 |  |  |  |  | 0.87
1987 |  |  |  | 5586.60 |  |  | 6793 |  |  |  | 910 | [10 empty] | 76.23 |  |  |  | 78.16 | [5 empty] | 70.08 |  |  | 77.55 |  |  |  | 6.57 |  | 5.50 | [8 empty] | 16.35 |  |  |  |  | 1.92
1988 |  |  |  | 5730.00 |  |  | 7069 |  |  |  | 910 | [10 empty] | 81.27 |  |  |  | 82.09 | [5 empty] | 71.68 |  |  | 80.48 |  |  |  | 6.23 |  | 5.45 | [8 empty] | 12.46 |  |  |  |  | 0.81
1989 |  |  |  | 6222.43 |  |  | 7419 |  |  |  | 910 | [10 empty] | 83.31 |  |  |  | 84.25 | [5 empty] | 78.06 |  |  | 84.69 |  |  |  | 3.77 |  | 3.30 | [8 empty] | 12.46 |  |  |  |  | 0.94
1990 |  |  |  | 5822.59 |  |  | 6834 |  |  |  | 910 | [10 empty] | 76.90 |  |  |  | 77.20 | [5 empty] | 73.04 |  |  | 78.01 |  |  |  | 5.32 |  | 4.34 | [8 empty] | 18.47 |  |  |  |  | 0.30
1991 |  |  |  | 6379.04 |  |  | 7400 |  |  |  | 910 | [10 empty] | 83.31 |  |  |  | 83.76 | [5 empty] | 80.02 |  |  | 84.47 |  |  |  | 4.09 |  | 3.57 | [8 empty] | 12.67 |  |  |  |  | 0.45
1992 |  |  |  | 4349.17 |  |  | 5079 |  |  |  | 910 | [10 empty] | 56.60 |  |  |  | 57.49 | [5 empty] | 54.41 |  |  | 57.82 |  |  |  | 20.87 |  | 15.16 | [8 empty] | 27.35 |  |  |  |  | 0.89
1993 |  |  |  | 5979.16 |  |  | 7253 |  |  |  | 910 | [10 empty] | 78.32 |  |  |  | 83.74 | [5 empty] | 75.01 |  |  | 82.80 |  |  |  | 5.60 |  | 4.97 | [8 empty] | 11.29 |  |  |  |  | 5.42
1994 |  |  |  | 3474.92 |  |  | 5119 |  |  |  | 910 | [10 empty] | 85.78 |  |  |  | 86.60 | [5 empty] | 43.59 |  |  | 58.44 |  |  |  | 2.06 |  | 1.82 | [8 empty] | 11.58 |  |  |  |  | 0.82
1995 |  |  |  | 6075.80 |  |  | 7206 |  |  |  | 910 | [10 empty] | 84.28 |  |  |  | 87.09 | [5 empty] | 76.22 |  |  | 82.26 |  |  |  | 0.91 |  | 0.80 | [8 empty] | 12.11 |  |  |  |  | 2.81
1996 |  |  |  | 6639.15 |  |  | 7798 |  |  |  | 910 | [10 empty] | 85.56 |  |  |  | 88.50 | [5 empty] | 83.06 |  |  | 88.78 |  |  |  | 1.49 |  | 1.34 | [8 empty] | 10.17 |  |  |  |  | 2.94
1997 |  |  |  | 6196.60 |  |  | 7621 |  |  |  | 910 | [10 empty] | 84.56 |  |  |  | 90.12 | [5 empty] | 77.73 |  |  | 87.00 |  |  |  | 0.52 |  | 0.47 | [8 empty] | 9.41 |  |  |  |  | 5.56
1998 |  |  |  | 5917.56 |  |  | 7078 |  |  |  | 910 | [10 empty] | 78.22 |  |  |  | 81.11 | [5 empty] | 74.23 |  |  | 80.80 |  |  |  | 7.37 |  | 6.46 | [8 empty] | 12.43 |  |  |  |  | 2.89
1999 |  |  |  | 6046.81 |  |  | 7082 |  |  |  | 910 | [10 empty] | 77.91 |  |  |  | 80.86 | [5 empty] | 75.85 |  |  | 80.84 |  |  |  | 11.17 |  | 10.17 | [8 empty] | 8.97 |  |  |  |  | 2.96
2000 |  |  |  | 2854.09 |  |  | 3602 |  |  |  | 910 | [10 empty] | 36.56 |  |  |  | 53.42 | [5 empty] | 35.71 |  |  | 41.01 |  |  |  | 35.61 |  | 29.54 | [8 empty] | 17.04 |  |  |  |  | 16.86
2001 |  |  |  | 4881.50 |  |  | 5768 |  |  |  | 910 | [10 empty] | 64.02 |  |  |  | 66.25 | [5 empty] | 61.24 |  |  | 65.84 |  |  |  | 27.08 |  | 24.61 | [8 empty] | 9.15 |  |  |  |  | 2.23
2002 |  |  |  | 6861.10 |  |  | 8251 |  |  |  | 910 | [10 empty] | 92.98 |  |  |  | 95.04 | [5 empty] | 86.07 |  |  | 94.19 |  |  |  | 1.80 |  | 1.74 | [8 empty] | 3.22 |  |  |  |  | 2.06
2003 |  |  |  | 4541.69 |  |  | 5321 |  |  |  | 910 | [10 empty] | 58.11 |  |  |  | 61.76 | [5 empty] | 56.97 |  |  | 60.74 |  |  |  | 17.16 |  | 12.79 | [8 empty] | 25.45 |  |  |  |  | 3.65
2004 |  |  |  | 6144.26 |  |  | 7217 |  |  |  | 910 | [10 empty] | 79.22 |  |  |  | 81.48 | [5 empty] | 76.87 |  |  | 82.16 |  |  |  | 2.45 |  | 2.05 | [8 empty] | 16.47 |  |  |  |  | 2.26
2005 |  |  |  | 6883.56 |  |  | 7841 |  |  |  | 910 | [10 empty] | 86.82 |  |  |  | 87.72 | [5 empty] | 86.34 |  |  | 89.50 |  |  |  | 2.13 |  | 3.67 | [8 empty] | 8.60 |  |  |  |  | 0.90
2006 |  |  |  | 6507.99 |  |  | 7440 |  |  |  | 910 | [10 empty] | 81.57 |  |  |  | 84.05 | [5 empty] | 81.64 |  |  | 84.93 |  |  |  | 3.56 |  | 4.99 | [8 empty] | 10.96 |  |  |  |  | 2.48
2007 |  |  |  | 6891.00 |  |  | 7791 |  |  |  | 910 | [10 empty] | 86.39 |  |  |  | 88.34 | [5 empty] | 86.43 |  |  | 88.93 |  |  |  | 3.05 |  | 3.94 | [8 empty] | 7.72 |  |  |  |  | 1.94
2008 |  |  |  | 6678.68 |  |  | 7651 |  |  |  | 910 | [10 empty] | 83.66 |  |  |  | 86.10 | [5 empty] | 83.55 |  |  | 87.10 |  |  |  | 0.82 |  | 2.98 | [8 empty] | 10.93 |  |  |  |  | 2.44
2009 |  |  |  | 4604.59 |  |  | 5461 |  |  |  | 910 | [10 empty] | 58.38 |  |  |  | 71.43 | [5 empty] | 57.76 |  |  | 62.34 |  |  |  | 0.51 |  | 4.54 | [8 empty] | 24.02 |  |  |  |  | 13.05
2010 |  |  |  | 6634.72 |  |  | 7679 |  |  |  | 910 | [10 empty] | 86.10 |  |  |  | 87.01 | [5 empty] | 83.23 |  |  | 87.66 |  |  |  | 0.42 |  | 1.68 | [8 empty] | 11.31 |  |  |  |  | 0.91
2011 |  |  |  | 6465.19 |  |  | 7370 |  |  |  | 910 | [10 empty] | 82.66 |  |  |  | 83.46 | [5 empty] | 81.10 |  |  | 84.13 |  |  |  | 0.67 |  | 9.26 | [8 empty] | 7.28 |  |  |  |  | 0.80
2012 |  |  |  | 4170.62 |  |  | 4690 |  |  |  | 910 | [10 empty] | 52.22 |  |  |  | 53.05 | [5 empty] | 52.18 |  |  | 53.39 |  |  |  | 14.15 |  | 19.44 | [8 empty] | 27.52 |  |  |  |  | 0.83
2013 |  |  |  | 6809.65 |  |  | 7659 |  |  |  | 910 | [10 empty] | 85.90 |  |  |  | 86.91 | [5 empty] | 85.42 |  |  | 87.43 |  |  |  | 0.67 |  | 5.01 | [8 empty] | 8.08 |  |  |  |  | 1.02
2014 |  |  |  | 6245.02 |  |  | 7214 |  |  |  | 910 | [10 empty] | 81.80 |  |  |  | 82.57 | [5 empty] | 78.34 |  |  | 82.35 |  |  |  | 0.54 |  | 2.04 | [8 empty] | 15.39 |  |  |  |  | 0.77
2015 |  |  |  | 6874.30 |  |  | 7961 |  |  |  | 910 | [10 empty] | 89.68 |  |  |  | 90.19 | [5 empty] | 86.23 |  |  | 90.88 |  |  |  | 1.74 |  | 1.60 | [8 empty] | 8.21 |  |  |  |  | 0.51
2016 |  |  |  | 3996.76 |  |  | 4637 |  |  |  | 910 | [10 empty] | 50.28 |  |  |  | 74.65 | [5 empty] | 50.00 |  |  | 52.79 |  |  |  | 1.07 |  | 8.30 | [8 empty] | 17.04 |  |  |  |  | 24.37
2017 |  |  |  | 6916.74 |  |  | 7783 |  |  |  | 910 | [10 empty] | 87.06 |  |  |  | 87.77 | [5 empty] | 86.77 |  |  | 88.85 |  |  |  | 0.68 |  | 3.52 | [8 empty] | 8.70 |  |  |  |  | 0.72
2018 |  |  |  | 6345.55 |  |  | 7164 |  |  |  | 910 | [10 empty] | 80.08 |  |  |  | 81.21 | [5 empty] | 79.60 |  |  | 81.78 |  |  |  | 0.73 |  | 1.73 | [8 empty] | 17.07 |  |  |  |  | 1.13
2019 |  |  |  | 6840.40 |  |  | 7698 |  |  |  | 910 | [10 empty] | 86.68 |  |  |  | 87.34 | [5 empty] | 85.81 |  |  | 87.88 |  |  |  | 1.01 |  | 3.51 | [8 empty] | 9.16 |  |  |  |  | 0.66
2020 |  |  |  | 4983.14 |  |  | 5786 |  |  |  | 910 | [10 empty] | 64.34 |  |  |  | 66.26 | [5 empty] | 62.34 |  |  | 65.87 |  |  |  | 11.21 |  | 12.39 | [8 empty] | 21.35 |  |  |  |  | 1.92
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 404 | [11 empty] | 0
B. |  | Refuelling without maintenance | [35 empty] | 172
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 893 |  |  |  | 4
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 31
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 55
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 11 | [11 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 45
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 17 | [11 empty] | 78
Z. |  | Other | [39 empty] | 16
Subtotal | [37 empty] | 1097 |  |  |  | 508 | [11 empty] | 126
Total | [22 empty] | 0 | [14 empty] | 1731
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 23
12. |  |  | Reactor I&C Systems | [34 empty] | 56
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 23
15. |  |  | Reactor Cooling Systems | [34 empty] | 55
16. |  |  | Steam generation systems | [34 empty] | 61
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 4
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 38
31. |  |  | Turbine and auxiliaries | [34 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 35
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 57
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 65
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 460

## BLAYAIS-2
2020 Operating Experience
FR-33 | [8 empty] | BLAYAIS-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | FRAM (FRAMATOME)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-01-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-07-17
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-02-01
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.44 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6716.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.07 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.49 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.81 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.37 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.82 %
Load Factor (LF) | [18 empty] | : | 84.03 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.88 %
Operating Factor (OF) | [18 empty] | : | 85.02 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1316 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 654.77 | 656.18 |  |  |  | 703.63 |  | 631.53 | [8 empty] | 153.83 |  |  | 0.22 | [6 empty] | 651.29 |  | 574.83 |  |  |  | 658.76 |  |  | 672.83 |  |  | 662.33 | [9 empty] | 696.48 |  |  | 6716.68
EAF [%] |  |  |  |  | 92.41 | 99.94 |  |  |  | 100.00 |  | 96.00 | [8 empty] | 22.73 |  |  | 0.04 | [6 empty] | 95.25 |  | 84.95 |  |  |  | 99.29 |  |  | 99.38 |  |  | 99.93 | [9 empty] | 99.96 |  |  | 82.49
UCF [%] |  |  |  |  | 93.07 | 99.94 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 25.65 |  |  | 0.04 | [6 empty] | 95.25 |  | 87.34 |  |  |  | 99.90 |  |  | 99.38 |  |  | 99.93 | [9 empty] | 99.96 |  |  | 83.37
LF [%] |  |  |  |  | 96.71 | 103.60 |  |  |  | 104.07 |  | 96.39 | [8 empty] | 22.72 |  |  | 0.03 | [6 empty] | 96.20 |  | 84.90 |  |  |  | 100.54 |  |  | 99.24 |  |  | 101.09 | [9 empty] | 102.87 |  |  | 84.03
OF [%] |  |  |  |  | 93.55 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 25.94 |  |  | 0.56 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.02
FLR [%] |  |  |  |  | 6.93 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.51 |  | 12.65 |  |  |  | 0.05 |  |  | 0.60 |  |  | 0.07 | [9 empty] | 0.04 |  |  | 2.07
UCL [%] |  |  |  |  | 6.93 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 49.31 | [6 empty] | 0.49 |  | 12.65 |  |  |  | 0.05 |  |  | 0.60 |  |  | 0.07 | [9 empty] | 0.04 |  |  | 5.81
PUF [%] |  |  |  |  | 0.00 | 0.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 74.35 |  |  | 50.64 | [6 empty] | 4.26 |  | 0.01 |  |  |  | 0.04 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.82
XUF [%] |  |  |  |  | 0.65 | 0.00 |  |  |  | 0.00 |  | 4.00 | [8 empty] | 2.93 |  |  | 0.00 | [6 empty] | 0.00 |  | 2.40 |  |  |  | 0.62 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.88
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 236094.02 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.76 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.42 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.57 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.47 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.96 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.35 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.05 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.98 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 5094.00 |  |  | 5817 |  |  |  | 910 | [10 empty] | 62.33 |  |  |  | 62.33 | [5 empty] | 61.55 |  |  | 63.87 |  |  |  | 9.70 |  | 6.69 | [8 empty] | 30.98 |  |  |  |  | 0.00
1984 |  |  |  | 6645.00 |  |  | 7716 |  |  |  | 910 | [10 empty] | 85.54 |  |  |  | 85.54 | [5 empty] | 83.13 |  |  | 87.84 |  |  |  | 4.07 |  | 3.63 | [8 empty] | 10.83 |  |  |  |  | 0.00
1985 |  |  |  | 6819.70 |  |  | 7937 |  |  |  | 910 | [10 empty] | 89.90 |  |  |  | 90.00 | [5 empty] | 85.55 |  |  | 90.61 |  |  |  | 1.61 |  | 1.47 | [8 empty] | 8.53 |  |  |  |  | 0.11
1986 |  |  |  | 6048.40 |  |  | 7142 |  |  |  | 910 | [10 empty] | 82.86 |  |  |  | 83.21 | [5 empty] | 75.87 |  |  | 81.53 |  |  |  | 3.13 |  | 2.68 | [8 empty] | 14.10 |  |  |  |  | 0.36
1987 |  |  |  | 5987.10 |  |  | 7218 |  |  |  | 910 | [10 empty] | 84.20 |  |  |  | 84.82 | [5 empty] | 75.11 |  |  | 82.40 |  |  |  | 4.93 |  | 4.40 | [8 empty] | 10.78 |  |  |  |  | 0.63
1988 |  |  |  | 4162.00 |  |  | 5718 |  |  |  | 910 | [10 empty] | 90.75 |  |  |  | 91.17 | [5 empty] | 52.07 |  |  | 65.10 |  |  |  | 4.68 |  | 4.48 | [8 empty] | 4.35 |  |  |  |  | 0.41
1989 |  |  |  | 5560.97 |  |  | 6720 |  |  |  | 910 | [10 empty] | 73.44 |  |  |  | 76.95 | [5 empty] | 69.76 |  |  | 76.71 |  |  |  | 3.25 |  | 2.59 | [8 empty] | 20.46 |  |  |  |  | 3.51
1990 |  |  |  | 5656.42 |  |  | 7381 |  |  |  | 910 | [10 empty] | 85.73 |  |  |  | 87.37 | [5 empty] | 70.96 |  |  | 84.26 |  |  |  | 2.33 |  | 2.08 | [8 empty] | 10.54 |  |  |  |  | 1.65
1991 |  |  |  | 5326.54 |  |  | 6789 |  |  |  | 910 | [10 empty] | 75.13 |  |  |  | 78.33 | [5 empty] | 66.82 |  |  | 77.50 |  |  |  | 3.66 |  | 2.98 | [8 empty] | 18.69 |  |  |  |  | 3.20
1992 |  |  |  | 5953.25 |  |  | 7505 |  |  |  | 910 | [10 empty] | 83.74 |  |  |  | 86.89 | [5 empty] | 74.48 |  |  | 85.44 |  |  |  | 0.72 |  | 0.63 | [8 empty] | 12.48 |  |  |  |  | 3.16
1993 |  |  |  | 5253.21 |  |  | 6203 |  |  |  | 910 | [10 empty] | 67.00 |  |  |  | 71.03 | [5 empty] | 65.90 |  |  | 70.81 |  |  |  | 1.73 |  | 1.25 | [8 empty] | 27.72 |  |  |  |  | 4.02
1994 |  |  |  | 6692.60 |  |  | 7658 |  |  |  | 910 | [10 empty] | 88.12 |  |  |  | 88.74 | [5 empty] | 83.96 |  |  | 87.42 |  |  |  | 0.21 |  | 0.19 | [8 empty] | 11.07 |  |  |  |  | 0.62
1995 |  |  |  | 6725.49 |  |  | 7775 |  |  |  | 910 | [10 empty] | 85.61 |  |  |  | 87.94 | [5 empty] | 84.37 |  |  | 88.76 |  |  |  | 1.75 |  | 1.57 | [8 empty] | 10.49 |  |  |  |  | 2.33
1996 |  |  |  | 6709.81 |  |  | 7587 |  |  |  | 910 | [10 empty] | 85.04 |  |  |  | 87.36 | [5 empty] | 83.94 |  |  | 86.37 |  |  |  | 0.45 |  | 0.40 | [8 empty] | 12.24 |  |  |  |  | 2.32
1997 |  |  |  | 6769.92 |  |  | 7681 |  |  |  | 910 | [10 empty] | 84.77 |  |  |  | 88.67 | [5 empty] | 84.93 |  |  | 87.68 |  |  |  | 1.95 |  | 1.77 | [8 empty] | 9.56 |  |  |  |  | 3.90
1998 |  |  |  | 6974.32 |  |  | 7883 |  |  |  | 910 | [10 empty] | 87.20 |  |  |  | 90.03 | [5 empty] | 87.49 |  |  | 89.99 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 9.87 |  |  |  |  | 2.83
1999 |  |  |  | 5836.20 |  |  | 6544 |  |  |  | 910 | [10 empty] | 73.05 |  |  |  | 75.10 | [5 empty] | 73.21 |  |  | 74.70 |  |  |  | 12.55 |  | 10.78 | [8 empty] | 14.12 |  |  |  |  | 2.05
2000 |  |  |  | 4941.11 |  |  | 5592 |  |  |  | 910 | [10 empty] | 63.00 |  |  |  | 75.24 | [5 empty] | 61.81 |  |  | 63.66 |  |  |  | 5.56 |  | 4.43 | [8 empty] | 20.33 |  |  |  |  | 12.24
2001 |  |  |  | 6547.95 |  |  | 7358 |  |  |  | 910 | [10 empty] | 81.93 |  |  |  | 83.56 | [5 empty] | 82.14 |  |  | 84.00 |  |  |  | 4.64 |  | 4.06 | [8 empty] | 12.38 |  |  |  |  | 1.63
2002 |  |  |  | 5971.95 |  |  | 7357 |  |  |  | 910 | [10 empty] | 82.72 |  |  |  | 84.35 | [5 empty] | 74.92 |  |  | 83.98 |  |  |  | 7.27 |  | 6.61 | [8 empty] | 9.05 |  |  |  |  | 1.62
2003 |  |  |  | 5181.16 |  |  | 5784 |  |  |  | 910 | [10 empty] | 63.69 |  |  |  | 66.03 | [5 empty] | 65.00 |  |  | 66.03 |  |  |  | 2.06 |  | 1.39 | [8 empty] | 32.58 |  |  |  |  | 2.34
2004 |  |  |  | 6734.56 |  |  | 7346 |  |  |  | 910 | [10 empty] | 81.47 |  |  |  | 82.57 | [5 empty] | 84.25 |  |  | 83.63 |  |  |  | 6.55 |  | 5.78 | [8 empty] | 11.65 |  |  |  |  | 1.09
2005 |  |  |  | 6918.75 |  |  | 7513 |  |  |  | 910 | [10 empty] | 84.65 |  |  |  | 84.96 | [5 empty] | 86.78 |  |  | 85.76 |  |  |  | 0.15 |  | 4.32 | [8 empty] | 10.71 |  |  |  |  | 0.32
2006 |  |  |  | 6786.69 |  |  | 7599 |  |  |  | 910 | [10 empty] | 85.44 |  |  |  | 86.03 | [5 empty] | 85.14 |  |  | 86.75 |  |  |  | 0.92 |  | 0.80 | [8 empty] | 13.17 |  |  |  |  | 0.59
2007 |  |  |  | 6035.60 |  |  | 6686 |  |  |  | 910 | [10 empty] | 74.27 |  |  |  | 75.83 | [5 empty] | 75.71 |  |  | 76.32 |  |  |  | 0.19 |  | 13.19 | [8 empty] | 10.99 |  |  |  |  | 1.56
2008 |  |  |  | 7191.21 |  |  | 7977 |  |  |  | 910 | [10 empty] | 89.67 |  |  |  | 90.28 | [5 empty] | 89.96 |  |  | 90.81 |  |  |  | 0.04 |  | 2.58 | [8 empty] | 7.15 |  |  |  |  | 0.60
2009 |  |  |  | 6050.55 |  |  | 6736 |  |  |  | 910 | [10 empty] | 75.02 |  |  |  | 83.55 | [5 empty] | 75.90 |  |  | 76.89 |  |  |  | 1.67 |  | 5.01 | [8 empty] | 11.44 |  |  |  |  | 8.53
2010 |  |  |  | 6341.07 |  |  | 6919 |  |  |  | 910 | [10 empty] | 78.18 |  |  |  | 79.08 | [5 empty] | 79.55 |  |  | 78.98 |  |  |  | 12.48 |  | 13.07 | [8 empty] | 7.85 |  |  |  |  | 0.90
2011 |  |  |  | 6516.19 |  |  | 7156 |  |  |  | 910 | [10 empty] | 80.96 |  |  |  | 81.16 | [5 empty] | 81.74 |  |  | 81.69 |  |  |  | 0.19 |  | 3.54 | [8 empty] | 15.30 |  |  |  |  | 0.20
2012 |  |  |  | 6486.49 |  |  | 7345 |  |  |  | 910 | [10 empty] | 81.81 |  |  |  | 85.65 | [5 empty] | 81.15 |  |  | 83.62 |  |  |  | 0.53 |  | 5.29 | [8 empty] | 9.06 |  |  |  |  | 3.84
2013 |  |  |  | 4891.24 |  |  | 5591 |  |  |  | 910 | [10 empty] | 61.69 |  |  |  | 64.21 | [5 empty] | 61.36 |  |  | 63.82 |  |  |  | 0.19 |  | 0.13 | [8 empty] | 35.67 |  |  |  |  | 2.52
2014 |  |  |  | 6064.42 |  |  | 7030 |  |  |  | 910 | [10 empty] | 87.12 |  |  |  | 88.54 | [5 empty] | 76.08 |  |  | 80.25 |  |  |  | 0.53 |  | 4.12 | [8 empty] | 7.34 |  |  |  |  | 1.41
2015 |  |  |  | 6278.21 |  |  | 7227 |  |  |  | 910 | [10 empty] | 81.02 |  |  |  | 81.87 | [5 empty] | 78.76 |  |  | 82.50 |  |  |  | 1.19 |  | 2.32 | [8 empty] | 15.81 |  |  |  |  | 0.85
2016 |  |  |  | 6937.64 |  |  | 8106 |  |  |  | 910 | [10 empty] | 89.90 |  |  |  | 90.40 | [5 empty] | 86.79 |  |  | 92.28 |  |  |  | 1.02 |  | 0.95 | [8 empty] | 8.65 |  |  |  |  | 0.50
2017 |  |  |  | 6376.49 |  |  | 6972 |  |  |  | 910 | [10 empty] | 78.39 |  |  |  | 80.73 | [5 empty] | 79.99 |  |  | 79.59 |  |  |  | 0.05 |  | 2.93 | [8 empty] | 16.34 |  |  |  |  | 2.34
2018 |  |  |  | 7003.89 |  |  | 7825 |  |  |  | 910 | [10 empty] | 87.94 |  |  |  | 89.08 | [5 empty] | 87.86 |  |  | 89.33 |  |  |  | 0.10 |  | 0.36 | [8 empty] | 10.55 |  |  |  |  | 1.14
2019 |  |  |  | 6366.21 |  |  | 7008 |  |  |  | 910 | [10 empty] | 78.57 |  |  |  | 80.19 | [5 empty] | 79.86 |  |  | 80.00 |  |  |  | 0.63 |  | 1.57 | [8 empty] | 18.23 |  |  |  |  | 1.62
2020 |  |  |  | 6716.68 |  |  | 7468 |  |  |  | 910 | [10 empty] | 82.49 |  |  |  | 83.37 | [5 empty] | 84.03 |  |  | 85.02 |  |  |  | 2.07 |  | 5.81 | [8 empty] | 10.82 |  |  |  |  | 0.88
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 217
B. |  | Refuelling without maintenance | [35 empty] | 124
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1026 |  |  |  | 2
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 18
E. |  | Testing of plant systems or components | [35 empty] | 54 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 13
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 22
L. |  | Human factor related | [39 empty] | 6
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 48
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 16
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 7
Z. |  | Other | [39 empty] | 20
Subtotal | [37 empty] | 1222 |  |  |  | 258 | [11 empty] | 96
Total | [22 empty] | 0 | [14 empty] | 1576
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 18
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 22
16. |  |  | Steam generation systems | [34 empty] | 30
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 39
33. |  |  | Circulating Water System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 29
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 7
42. |  |  | Electrical Power Supply Systems | [34 empty] | 16
Total | [37 empty] | 218

## BLAYAIS-3
2020 Operating Experience
FR-34 | [8 empty] | BLAYAIS-3 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-04-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-08-17
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-11-14
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.44 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5093.2 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.49 %
Energy Availability Factor (EAF) | [18 empty] | : | 63.21 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 13.45 %
Unit Capability Factor (UCF) | [18 empty] | : | 65.58 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.97 %
Load Factor (LF) | [18 empty] | : | 63.72 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.37 %
Operating Factor (OF) | [18 empty] | : | 65.53 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3028 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 663.15 | 626.46 |  |  |  | 598.27 |  | 672.27 | [8 empty] | 616.44 |  |  | 210.14 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 430.19 |  |  | 678.51 | [9 empty] | 597.79 |  |  | 5093.20
EAF [%] |  |  |  |  | 97.72 | 99.89 |  |  |  | 90.81 |  | 99.91 | [8 empty] | 91.06 |  |  | 32.08 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 62.62 |  |  | 99.92 | [9 empty] | 86.24 |  |  | 63.21
UCF [%] |  |  |  |  | 100.00 | 99.89 |  |  |  | 95.65 |  | 100.00 | [8 empty] | 100.00 |  |  | 39.79 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 3.34 |  |  | 62.62 |  |  | 99.92 | [9 empty] | 87.36 |  |  | 65.58
LF [%] |  |  |  |  | 97.95 | 98.91 |  |  |  | 88.48 |  | 102.60 | [8 empty] | 91.05 |  |  | 32.07 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 63.45 |  |  | 103.56 | [9 empty] | 88.30 |  |  | 63.72
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 91.66 |  | 100.00 | [8 empty] | 100.00 |  |  | 40.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 68.32 |  |  | 100.00 | [9 empty] | 87.90 |  |  | 65.53
FLR [%] |  |  |  |  | 0.00 | 0.09 |  |  |  | 4.35 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 4.09 |  |  | 0.00 | [9 empty] | 12.64 |  |  | 2.49
UCL [%] |  |  |  |  | 0.00 | 0.09 |  |  |  | 4.35 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 15.86 |  |  |  | 96.66 |  |  | 32.27 |  |  | 0.00 | [9 empty] | 12.64 |  |  | 13.45
PUF [%] |  |  |  |  | 0.00 | 0.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 60.21 | [6 empty] | 100.00 |  | 84.14 |  |  |  | 0.00 |  |  | 5.12 |  |  | 0.08 | [9 empty] | 0.00 |  |  | 20.97
XUF [%] |  |  |  |  | 2.28 | 0.00 |  |  |  | 4.83 |  | 0.09 | [8 empty] | 8.94 |  |  | 7.70 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 3.33 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 1.12 |  |  | 2.37
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 227027.5 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.72 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.66 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.34 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.62 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.03 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.36 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.96 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.43 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 1912.00 |  |  | 2739 |  |  |  | 910 | [10 empty] | 87.37 |  |  |  | 87.37 | [5 empty] | 87.37 |  |  | 86.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.63 |  |  |  |  | 0.00
1984 |  |  |  | 5944.00 |  |  | 7055 |  |  |  | 910 | [10 empty] | 80.35 |  |  |  | 80.35 | [5 empty] | 74.36 |  |  | 80.32 |  |  |  | 4.20 |  | 3.53 | [8 empty] | 16.13 |  |  |  |  | 0.00
1985 |  |  |  | 6568.90 |  |  | 7729 |  |  |  | 910 | [10 empty] | 86.57 |  |  |  | 86.96 | [5 empty] | 82.40 |  |  | 88.23 |  |  |  | 2.89 |  | 2.59 | [8 empty] | 10.45 |  |  |  |  | 0.40
1986 |  |  |  | 6504.90 |  |  | 7759 |  |  |  | 910 | [10 empty] | 88.15 |  |  |  | 88.26 | [5 empty] | 81.60 |  |  | 88.57 |  |  |  | 1.39 |  | 1.25 | [8 empty] | 10.50 |  |  |  |  | 0.11
1987 |  |  |  | 4304.70 |  |  | 5473 |  |  |  | 910 | [10 empty] | 93.47 |  |  |  | 93.91 | [5 empty] | 54.00 |  |  | 62.48 |  |  |  | 0.41 |  | 0.39 | [8 empty] | 5.70 |  |  |  |  | 0.44
1988 |  |  |  | 5287.00 |  |  | 6708 |  |  |  | 910 | [10 empty] | 81.56 |  |  |  | 82.76 | [5 empty] | 66.14 |  |  | 76.37 |  |  |  | 5.58 |  | 4.89 | [8 empty] | 12.35 |  |  |  |  | 1.20
1989 |  |  |  | 6086.42 |  |  | 7292 |  |  |  | 910 | [10 empty] | 78.54 |  |  |  | 82.65 | [5 empty] | 76.35 |  |  | 83.24 |  |  |  | 5.65 |  | 4.94 | [8 empty] | 12.40 |  |  |  |  | 4.11
1990 |  |  |  | 4871.16 |  |  | 5673 |  |  |  | 910 | [10 empty] | 62.81 |  |  |  | 64.32 | [5 empty] | 61.11 |  |  | 64.76 |  |  |  | 17.56 |  | 13.70 | [8 empty] | 21.98 |  |  |  |  | 1.51
1991 |  |  |  | 6372.29 |  |  | 7448 |  |  |  | 910 | [10 empty] | 83.97 |  |  |  | 84.62 | [5 empty] | 79.94 |  |  | 85.02 |  |  |  | 3.34 |  | 2.93 | [8 empty] | 12.45 |  |  |  |  | 0.65
1992 |  |  |  | 5967.94 |  |  | 7220 |  |  |  | 910 | [10 empty] | 81.80 |  |  |  | 83.02 | [5 empty] | 74.66 |  |  | 82.19 |  |  |  | 5.19 |  | 4.54 | [8 empty] | 12.44 |  |  |  |  | 1.22
1993 |  |  |  | 6285.26 |  |  | 7728 |  |  |  | 910 | [10 empty] | 79.77 |  |  |  | 87.71 | [5 empty] | 78.85 |  |  | 88.22 |  |  |  | 1.40 |  | 1.25 | [8 empty] | 11.04 |  |  |  |  | 7.94
1994 |  |  |  | 4212.82 |  |  | 4979 |  |  |  | 910 | [10 empty] | 57.74 |  |  |  | 57.77 | [5 empty] | 52.85 |  |  | 56.84 |  |  |  | 20.93 |  | 15.29 | [8 empty] | 26.93 |  |  |  |  | 0.03
1995 |  |  |  | 6739.57 |  |  | 7525 |  |  |  | 910 | [10 empty] | 85.38 |  |  |  | 85.89 | [5 empty] | 84.54 |  |  | 85.90 |  |  |  | 0.25 |  | 0.21 | [8 empty] | 13.89 |  |  |  |  | 0.51
1996 |  |  |  | 6924.05 |  |  | 7744 |  |  |  | 910 | [10 empty] | 86.76 |  |  |  | 87.15 | [5 empty] | 86.62 |  |  | 88.16 |  |  |  | 2.56 |  | 2.29 | [8 empty] | 10.57 |  |  |  |  | 0.39
1997 |  |  |  | 6614.05 |  |  | 7659 |  |  |  | 910 | [10 empty] | 86.41 |  |  |  | 86.41 | [5 empty] | 82.97 |  |  | 87.43 |  |  |  | 0.38 |  | 0.33 | [8 empty] | 13.26 |  |  |  |  | 0.00
1998 |  |  |  | 6970.16 |  |  | 7954 |  |  |  | 910 | [10 empty] | 87.77 |  |  |  | 90.07 | [5 empty] | 87.44 |  |  | 90.80 |  |  |  | 1.63 |  | 1.50 | [8 empty] | 8.44 |  |  |  |  | 2.30
1999 |  |  |  | 5123.02 |  |  | 5861 |  |  |  | 910 | [10 empty] | 64.20 |  |  |  | 66.83 | [5 empty] | 64.27 |  |  | 66.91 |  |  |  | 24.93 |  | 22.19 | [8 empty] | 10.98 |  |  |  |  | 2.63
2000 |  |  |  | 6183.61 |  |  | 7143 |  |  |  | 910 | [10 empty] | 78.19 |  |  |  | 80.27 | [5 empty] | 77.36 |  |  | 81.32 |  |  |  | 11.24 |  | 10.17 | [8 empty] | 9.56 |  |  |  |  | 2.08
2001 |  |  |  | 6707.06 |  |  | 7540 |  |  |  | 910 | [10 empty] | 84.22 |  |  |  | 85.36 | [5 empty] | 84.14 |  |  | 86.07 |  |  |  | 3.65 |  | 3.23 | [8 empty] | 11.40 |  |  |  |  | 1.15
2002 |  |  |  | 6882.02 |  |  | 7682 |  |  |  | 910 | [10 empty] | 86.44 |  |  |  | 87.52 | [5 empty] | 86.33 |  |  | 87.69 |  |  |  | 3.06 |  | 2.77 | [8 empty] | 9.71 |  |  |  |  | 1.08
2003 |  |  |  | 5844.86 |  |  | 6725 |  |  |  | 910 | [10 empty] | 73.57 |  |  |  | 86.51 | [5 empty] | 73.32 |  |  | 76.77 |  |  |  | 2.41 |  | 2.14 | [8 empty] | 11.36 |  |  |  |  | 12.93
2004 |  |  |  | 5822.81 |  |  | 6699 |  |  |  | 910 | [10 empty] | 72.46 |  |  |  | 75.20 | [5 empty] | 72.84 |  |  | 76.26 |  |  |  | 1.50 |  | 1.15 | [8 empty] | 23.65 |  |  |  |  | 2.74
2005 |  |  |  | 5868.13 |  |  | 6875 |  |  |  | 910 | [10 empty] | 76.42 |  |  |  | 80.27 | [5 empty] | 73.61 |  |  | 78.48 |  |  |  | 1.83 |  | 11.21 | [8 empty] | 8.52 |  |  |  |  | 3.85
2006 |  |  |  | 6515.66 |  |  | 7340 |  |  |  | 910 | [10 empty] | 81.51 |  |  |  | 82.76 | [5 empty] | 81.75 |  |  | 83.80 |  |  |  | 0.38 |  | 3.30 | [8 empty] | 13.95 |  |  |  |  | 1.25
2007 |  |  |  | 7441.68 |  |  | 8035 |  |  |  | 910 | [10 empty] | 90.86 |  |  |  | 90.92 | [5 empty] | 93.35 |  |  | 91.72 |  |  |  | 1.11 |  | 1.02 | [8 empty] | 8.06 |  |  |  |  | 0.06
2008 |  |  |  | 7138.33 |  |  | 7676 |  |  |  | 910 | [10 empty] | 86.85 |  |  |  | 87.02 | [5 empty] | 89.30 |  |  | 87.39 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 12.94 |  |  |  |  | 0.17
2009 |  |  |  | 6134.50 |  |  | 6949 |  |  |  | 910 | [10 empty] | 75.79 |  |  |  | 87.09 | [5 empty] | 76.95 |  |  | 79.33 |  |  |  | 1.16 |  | 5.43 | [8 empty] | 7.48 |  |  |  |  | 11.31
2010 |  |  |  | 6679.72 |  |  | 7390 |  |  |  | 910 | [10 empty] | 82.23 |  |  |  | 83.14 | [5 empty] | 83.79 |  |  | 84.36 |  |  |  | 2.65 |  | 4.05 | [8 empty] | 12.82 |  |  |  |  | 0.91
2011 |  |  |  | 6925.35 |  |  | 7769 |  |  |  | 910 | [10 empty] | 85.73 |  |  |  | 88.23 | [5 empty] | 86.88 |  |  | 88.69 |  |  |  | 0.20 |  | 2.48 | [8 empty] | 9.29 |  |  |  |  | 2.51
2012 |  |  |  | 6747.82 |  |  | 7436 |  |  |  | 910 | [10 empty] | 83.03 |  |  |  | 83.86 | [5 empty] | 84.42 |  |  | 84.65 |  |  |  | 1.77 |  | 2.46 | [8 empty] | 13.68 |  |  |  |  | 0.83
2013 |  |  |  | 6944.29 |  |  | 7535 |  |  |  | 910 | [10 empty] | 85.41 |  |  |  | 86.05 | [5 empty] | 87.11 |  |  | 86.02 |  |  |  | 0.03 |  | 6.65 | [8 empty] | 7.30 |  |  |  |  | 0.64
2014 |  |  |  | 4270.69 |  |  | 4677 |  |  |  | 910 | [10 empty] | 55.53 |  |  |  | 55.92 | [5 empty] | 53.57 |  |  | 53.39 |  |  |  | 0.31 |  | 0.17 | [8 empty] | 43.91 |  |  |  |  | 0.38
2015 |  |  |  | 2219.74 |  |  | 2748 |  |  |  | 910 | [10 empty] | 27.06 |  |  |  | 27.11 | [5 empty] | 27.85 |  |  | 31.37 |  |  |  | 7.87 |  | 2.32 | [8 empty] | 70.58 |  |  |  |  | 0.04
2016 |  |  |  | 6569.71 |  |  | 7181 |  |  |  | 910 | [10 empty] | 79.82 |  |  |  | 80.04 | [5 empty] | 82.19 |  |  | 81.75 |  |  |  | 1.18 |  | 3.63 | [8 empty] | 16.32 |  |  |  |  | 0.23
2017 |  |  |  | 6902.06 |  |  | 7507 |  |  |  | 910 | [10 empty] | 85.20 |  |  |  | 89.60 | [5 empty] | 86.58 |  |  | 85.70 |  |  |  | 0.15 |  | 0.70 | [8 empty] | 9.70 |  |  |  |  | 4.40
2018 |  |  |  | 6427.78 |  |  | 7110 |  |  |  | 910 | [10 empty] | 80.36 |  |  |  | 80.69 | [5 empty] | 80.63 |  |  | 81.16 |  |  |  | 0.60 |  | 2.34 | [8 empty] | 16.97 |  |  |  |  | 0.33
2019 |  |  |  | 7147.00 |  |  | 7935 |  |  |  | 910 | [10 empty] | 89.85 |  |  |  | 90.14 | [5 empty] | 89.66 |  |  | 90.58 |  |  |  | 1.06 |  | 0.97 | [8 empty] | 8.89 |  |  |  |  | 0.29
2020 |  |  |  | 5093.20 |  |  | 5756 |  |  |  | 910 | [10 empty] | 63.21 |  |  |  | 65.58 | [5 empty] | 63.72 |  |  | 65.53 |  |  |  | 2.49 |  | 13.45 | [8 empty] | 20.97 |  |  |  |  | 2.37
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 248
B. |  | Refuelling without maintenance | [35 empty] | 96
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1104 |  |  |  | 5
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 19 |  |  |  | 0
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 21
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 7
L. |  | Human factor related | [39 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 30
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 1 | [11 empty] | 19
Z. |  | Other | [39 empty] | 45 | [11 empty] | 10
Subtotal | [37 empty] | 1223 |  |  |  | 322 | [11 empty] | 66
Total | [22 empty] | 0 | [14 empty] | 1611
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 11
12. |  |  | Reactor I&C Systems | [34 empty] | 19
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 26
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 60
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 12
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 57
41. |  |  | Main Generator Systems | [34 empty] | 32
42. |  |  | Electrical Power Supply Systems | [34 empty] | 14
Total | [37 empty] | 257

## BLAYAIS-4
2020 Operating Experience
FR-35 | [8 empty] | BLAYAIS-4 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-04-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-05-16
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-10-01
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.44 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6573.47 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.29 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.4 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.06 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.86 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.08 %
Load Factor (LF) | [18 empty] | : | 82.24 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.46 %
Operating Factor (OF) | [18 empty] | : | 85.05 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1313 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 540.88 | 613.56 |  |  |  | 668.66 |  | 637.18 | [8 empty] | 670.08 |  |  | 647.93 | [6 empty] | 666.39 |  | 660.09 |  |  |  | 644.96 |  |  | 593.30 |  |  | 0.00 | [9 empty] | 230.46 |  |  | 6573.47
EAF [%] |  |  |  |  | 78.99 | 97.60 |  |  |  | 99.95 |  | 97.81 | [8 empty] | 99.67 |  |  | 99.15 | [6 empty] | 98.50 |  | 97.43 |  |  |  | 98.41 |  |  | 87.52 |  |  | 0.00 | [9 empty] | 33.70 |  |  | 82.40
UCF [%] |  |  |  |  | 78.99 | 99.56 |  |  |  | 99.99 |  | 97.81 | [8 empty] | 99.69 |  |  | 99.95 | [6 empty] | 99.94 |  | 99.84 |  |  |  | 99.98 |  |  | 96.65 |  |  | 0.00 | [9 empty] | 33.70 |  |  | 83.86
LF [%] |  |  |  |  | 79.89 | 96.87 |  |  |  | 98.89 |  | 97.25 | [8 empty] | 98.97 |  |  | 98.89 | [6 empty] | 98.43 |  | 97.50 |  |  |  | 98.44 |  |  | 87.51 |  |  | 0.00 | [9 empty] | 34.04 |  |  | 82.24
OF [%] |  |  |  |  | 83.74 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 96.78 |  |  | 0.00 | [9 empty] | 39.78 |  |  | 85.05
FLR [%] |  |  |  |  | 0.37 | 0.39 |  |  |  | 0.01 |  | 2.15 | [8 empty] | 0.05 |  |  | 0.05 | [6 empty] | 0.01 |  | 0.04 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.29
UCL [%] |  |  |  |  | 16.51 | 0.39 |  |  |  | 0.01 |  | 2.15 | [8 empty] | 0.05 |  |  | 0.05 | [6 empty] | 0.01 |  | 0.04 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 40.59 |  |  | 5.06
PUF [%] |  |  |  |  | 4.51 | 0.05 |  |  |  | 0.00 |  | 0.04 | [8 empty] | 0.26 |  |  | 0.00 | [6 empty] | 0.05 |  | 0.12 |  |  |  | 0.00 |  |  | 3.35 |  |  | 100.00 | [9 empty] | 25.71 |  |  | 11.08
XUF [%] |  |  |  |  | 0.00 | 1.96 |  |  |  | 0.05 |  | 0.00 | [8 empty] | 0.03 |  |  | 0.80 | [6 empty] | 1.44 |  | 2.41 |  |  |  | 1.57 |  |  | 9.13 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.46
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 224721.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.51 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.78 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.61 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.22 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.17 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.44 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.59 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 3356.00 |  |  | 4418 |  |  |  | 910 | [10 empty] | 93.49 |  |  |  | 93.49 | [5 empty] | 94.46 |  |  | 94.75 |  |  |  | 6.51 |  | 6.51 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 6012.00 |  |  | 6780 |  |  |  | 910 | [10 empty] | 76.00 |  |  |  | 76.00 | [5 empty] | 75.21 |  |  | 77.19 |  |  |  | 3.36 |  | 2.64 | [8 empty] | 21.36 |  |  |  |  | 0.00
1985 |  |  |  | 5972.60 |  |  | 7024 |  |  |  | 910 | [10 empty] | 78.72 |  |  |  | 78.77 | [5 empty] | 74.92 |  |  | 80.18 |  |  |  | 14.40 |  | 13.25 | [8 empty] | 7.98 |  |  |  |  | 0.06
1986 |  |  |  | 6278.10 |  |  | 7412 |  |  |  | 910 | [10 empty] | 81.87 |  |  |  | 82.50 | [5 empty] | 78.76 |  |  | 84.61 |  |  |  | 5.24 |  | 4.56 | [8 empty] | 12.94 |  |  |  |  | 0.62
1987 |  |  |  | 6104.60 |  |  | 7437 |  |  |  | 910 | [10 empty] | 83.87 |  |  |  | 85.61 | [5 empty] | 76.58 |  |  | 84.90 |  |  |  | 4.28 |  | 3.83 | [8 empty] | 10.56 |  |  |  |  | 1.74
1988 |  |  |  | 4337.00 |  |  | 5662 |  |  |  | 910 | [10 empty] | 70.16 |  |  |  | 71.53 | [5 empty] | 54.26 |  |  | 64.46 |  |  |  | 10.95 |  | 8.79 | [8 empty] | 19.68 |  |  |  |  | 1.36
1989 |  |  |  | 5816.26 |  |  | 7250 |  |  |  | 910 | [10 empty] | 87.48 |  |  |  | 89.41 | [5 empty] | 72.96 |  |  | 82.76 |  |  |  | 10.17 |  | 10.12 | [8 empty] | 0.47 |  |  |  |  | 1.93
1990 |  |  |  | 5912.31 |  |  | 7347 |  |  |  | 910 | [10 empty] | 78.18 |  |  |  | 83.42 | [5 empty] | 74.17 |  |  | 83.87 |  |  |  | 4.46 |  | 3.89 | [8 empty] | 12.69 |  |  |  |  | 5.24
1991 |  |  |  | 5467.70 |  |  | 6496 |  |  |  | 910 | [10 empty] | 73.14 |  |  |  | 73.50 | [5 empty] | 68.59 |  |  | 74.16 |  |  |  | 12.22 |  | 10.23 | [8 empty] | 16.27 |  |  |  |  | 0.36
1992 |  |  |  | 6120.58 |  |  | 7430 |  |  |  | 910 | [10 empty] | 83.48 |  |  |  | 84.10 | [5 empty] | 76.57 |  |  | 84.59 |  |  |  | 0.53 |  | 0.44 | [8 empty] | 15.45 |  |  |  |  | 0.62
1993 |  |  |  | 5096.35 |  |  | 6854 |  |  |  | 910 | [10 empty] | 72.90 |  |  |  | 85.31 | [5 empty] | 63.93 |  |  | 78.24 |  |  |  | 2.81 |  | 2.47 | [8 empty] | 12.22 |  |  |  |  | 12.41
1994 |  |  |  | 5897.06 |  |  | 7308 |  |  |  | 910 | [10 empty] | 81.85 |  |  |  | 82.61 | [5 empty] | 73.98 |  |  | 83.42 |  |  |  | 4.78 |  | 4.14 | [8 empty] | 13.25 |  |  |  |  | 0.76
1995 |  |  |  | 5342.37 |  |  | 6198 |  |  |  | 910 | [10 empty] | 71.47 |  |  |  | 75.19 | [5 empty] | 67.02 |  |  | 70.75 |  |  |  | 1.19 |  | 0.90 | [8 empty] | 23.91 |  |  |  |  | 3.72
1996 |  |  |  | 6719.61 |  |  | 7761 |  |  |  | 910 | [10 empty] | 86.92 |  |  |  | 88.17 | [5 empty] | 84.06 |  |  | 88.35 |  |  |  | 1.73 |  | 1.55 | [8 empty] | 10.27 |  |  |  |  | 1.26
1997 |  |  |  | 6497.20 |  |  | 7705 |  |  |  | 910 | [10 empty] | 86.56 |  |  |  | 89.14 | [5 empty] | 81.50 |  |  | 87.96 |  |  |  | 0.83 |  | 0.75 | [8 empty] | 10.12 |  |  |  |  | 2.58
1998 |  |  |  | 6692.57 |  |  | 7930 |  |  |  | 910 | [10 empty] | 87.93 |  |  |  | 90.26 | [5 empty] | 83.96 |  |  | 90.53 |  |  |  | 1.47 |  | 1.35 | [8 empty] | 8.39 |  |  |  |  | 2.33
1999 |  |  |  | 6161.15 |  |  | 7369 |  |  |  | 910 | [10 empty] | 80.20 |  |  |  | 83.33 | [5 empty] | 77.29 |  |  | 84.12 |  |  |  | 4.52 |  | 3.94 | [8 empty] | 12.73 |  |  |  |  | 3.13
2000 |  |  |  | 5467.51 |  |  | 6559 |  |  |  | 910 | [10 empty] | 72.53 |  |  |  | 75.05 | [5 empty] | 68.40 |  |  | 74.67 |  |  |  | 15.60 |  | 13.87 | [8 empty] | 11.08 |  |  |  |  | 2.53
2001 |  |  |  | 6370.03 |  |  | 7297 |  |  |  | 910 | [10 empty] | 82.09 |  |  |  | 82.44 | [5 empty] | 79.91 |  |  | 83.30 |  |  |  | 5.22 |  | 4.54 | [8 empty] | 13.01 |  |  |  |  | 0.35
2002 |  |  |  | 6462.24 |  |  | 7623 |  |  |  | 910 | [10 empty] | 85.09 |  |  |  | 86.19 | [5 empty] | 81.07 |  |  | 87.02 |  |  |  | 3.08 |  | 2.74 | [8 empty] | 11.07 |  |  |  |  | 1.10
2003 |  |  |  | 5311.06 |  |  | 6292 |  |  |  | 910 | [10 empty] | 68.45 |  |  |  | 72.86 | [5 empty] | 66.62 |  |  | 71.83 |  |  |  | 17.64 |  | 15.61 | [8 empty] | 11.53 |  |  |  |  | 4.41
2004 |  |  |  | 6560.31 |  |  | 7749 |  |  |  | 910 | [10 empty] | 84.57 |  |  |  | 88.32 | [5 empty] | 82.07 |  |  | 88.22 |  |  |  | 3.30 |  | 3.01 | [8 empty] | 8.66 |  |  |  |  | 3.75
2005 |  |  |  | 5454.68 |  |  | 6357 |  |  |  | 910 | [10 empty] | 69.58 |  |  |  | 71.55 | [5 empty] | 68.43 |  |  | 72.57 |  |  |  | 3.26 |  | 4.42 | [8 empty] | 24.03 |  |  |  |  | 1.96
2006 |  |  |  | 6758.43 |  |  | 7827 |  |  |  | 910 | [10 empty] | 86.48 |  |  |  | 88.49 | [5 empty] | 84.78 |  |  | 89.35 |  |  |  | 2.00 |  | 1.96 | [8 empty] | 9.55 |  |  |  |  | 2.01
2007 |  |  |  | 6607.83 |  |  | 7484 |  |  |  | 910 | [10 empty] | 84.23 |  |  |  | 84.69 | [5 empty] | 82.89 |  |  | 85.43 |  |  |  | 3.51 |  | 4.38 | [8 empty] | 10.94 |  |  |  |  | 0.46
2008 |  |  |  | 6755.66 |  |  | 7760 |  |  |  | 910 | [10 empty] | 86.97 |  |  |  | 87.44 | [5 empty] | 84.52 |  |  | 88.34 |  |  |  | 1.07 |  | 4.83 | [8 empty] | 7.73 |  |  |  |  | 0.46
2009 |  |  |  | 4574.28 |  |  | 5295 |  |  |  | 910 | [10 empty] | 58.35 |  |  |  | 70.81 | [5 empty] | 57.38 |  |  | 60.45 |  |  |  | 1.33 |  | 16.86 | [8 empty] | 12.33 |  |  |  |  | 12.46
2010 |  |  |  | 6723.73 |  |  | 7718 |  |  |  | 910 | [10 empty] | 85.49 |  |  |  | 86.58 | [5 empty] | 84.35 |  |  | 88.11 |  |  |  | 3.34 |  | 5.11 | [8 empty] | 8.31 |  |  |  |  | 1.09
2011 |  |  |  | 6138.08 |  |  | 7079 |  |  |  | 910 | [10 empty] | 79.11 |  |  |  | 79.42 | [5 empty] | 77.00 |  |  | 80.81 |  |  |  | 2.44 |  | 6.58 | [8 empty] | 14.00 |  |  |  |  | 0.30
2012 |  |  |  | 6615.11 |  |  | 7653 |  |  |  | 910 | [10 empty] | 83.71 |  |  |  | 86.20 | [5 empty] | 82.76 |  |  | 87.12 |  |  |  | 0.70 |  | 3.69 | [8 empty] | 10.11 |  |  |  |  | 2.49
2013 |  |  |  | 5146.77 |  |  | 5924 |  |  |  | 910 | [10 empty] | 64.78 |  |  |  | 66.27 | [5 empty] | 64.56 |  |  | 67.63 |  |  |  | 2.73 |  | 7.86 | [8 empty] | 25.87 |  |  |  |  | 1.49
2014 |  |  |  | 6463.78 |  |  | 7566 |  |  |  | 910 | [10 empty] | 84.41 |  |  |  | 84.81 | [5 empty] | 81.09 |  |  | 86.37 |  |  |  | 5.02 |  | 4.48 | [8 empty] | 10.70 |  |  |  |  | 0.40
2015 |  |  |  | 4522.44 |  |  | 5124 |  |  |  | 910 | [10 empty] | 57.32 |  |  |  | 57.84 | [5 empty] | 56.73 |  |  | 58.49 |  |  |  | 5.33 |  | 11.75 | [8 empty] | 30.42 |  |  |  |  | 0.52
2016 |  |  |  | 6772.22 |  |  | 7859 |  |  |  | 910 | [10 empty] | 86.75 |  |  |  | 87.42 | [5 empty] | 84.72 |  |  | 89.47 |  |  |  | 1.11 |  | 4.22 | [8 empty] | 8.36 |  |  |  |  | 0.67
2017 |  |  |  | 6184.82 |  |  | 7044 |  |  |  | 910 | [10 empty] | 78.98 |  |  |  | 79.62 | [5 empty] | 77.59 |  |  | 80.41 |  |  |  | 0.67 |  | 3.72 | [8 empty] | 16.65 |  |  |  |  | 0.64
2018 |  |  |  | 6690.11 |  |  | 7744 |  |  |  | 910 | [10 empty] | 86.13 |  |  |  | 88.42 | [5 empty] | 83.92 |  |  | 88.40 |  |  |  | 1.33 |  | 2.38 | [8 empty] | 9.20 |  |  |  |  | 2.28
2019 |  |  |  | 4935.56 |  |  | 5685 |  |  |  | 910 | [10 empty] | 63.09 |  |  |  | 74.97 | [5 empty] | 61.91 |  |  | 64.90 |  |  |  | 1.58 |  | 7.26 | [8 empty] | 17.77 |  |  |  |  | 11.88
2020 |  |  |  | 6573.47 |  |  | 7471 |  |  |  | 910 | [10 empty] | 82.40 |  |  |  | 83.86 | [5 empty] | 82.24 |  |  | 85.05 |  |  |  | 0.29 |  | 5.06 | [8 empty] | 11.08 |  |  |  |  | 1.46
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 339
B. |  | Refuelling without maintenance | [35 empty] | 121
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 957 |  |  |  | 24
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 6 |  |  |  | 7
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 7
L. |  | Human factor related | [39 empty] | 13
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 21
O. |  | Load dispatching, prioritization | [51 empty] | 3
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 49
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 2
Z. |  | Other | [39 empty] | 26 | [11 empty] | 5
Subtotal | [37 empty] | 1086 |  |  |  | 417 | [11 empty] | 80
Total | [22 empty] | 0 | [14 empty] | 1583
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [34 empty] | 44
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 12
14. |  |  | Safety Systems | [34 empty] | 34
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 34
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 18
31. |  |  | Turbine and auxiliaries | [34 empty] | 42
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
33. |  |  | Circulating Water System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 73
41. |  |  | Main Generator Systems | [34 empty] | 43
42. |  |  | Electrical Power Supply Systems | [34 empty] | 19
Total | [37 empty] | 345

## BUGEY-2
2020 Operating Experience
FR-13 | [8 empty] | BUGEY-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | FRAM (FRAMATOME)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP0 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-11-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-05-10
Gross electrical power | [12 empty] | : |  |  | 945 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-03-01
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 351.5 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.13 %
Energy Availability Factor (EAF) | [18 empty] | : | 4.4 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 38.41 %
Unit Capability Factor (UCF) | [18 empty] | : | 9.96 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 51.63 %
Load Factor (LF) | [18 empty] | : | 4.4 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 5.55 %
Operating Factor (OF) | [18 empty] | : | 4.69 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8372 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 351.50 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 351.50
EAF [%] |  |  |  |  | 51.96 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.40
UCF [%] |  |  |  |  | 53.77 | 0.00 |  |  |  | 0.00 |  | 2.08 | [8 empty] | 5.32 |  |  | 0.00 | [6 empty] | 16.12 |  | 40.32 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.96
LF [%] |  |  |  |  | 51.92 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.40
OF [%] |  |  |  |  | 55.38 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.69
FLR [%] |  |  |  |  | 0.28 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.13
UCL [%] |  |  |  |  | 0.15 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 59.68 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 38.41
PUF [%] |  |  |  |  | 46.08 | 100.00 |  |  |  | 100.00 |  | 97.92 | [8 empty] | 94.68 |  |  | 100.00 | [6 empty] | 83.88 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 51.63
XUF [%] |  |  |  |  | 1.81 | 0.00 |  |  |  | 0.00 |  | 2.08 | [8 empty] | 5.30 |  |  | 0.00 | [6 empty] | 16.12 |  | 40.32 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.55
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 229099.48 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 8.4 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.94 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.18 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.18 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.64 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 68.01 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.24 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.65 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 4379.00 |  |  | 5588 |  |  |  | 925 | [10 empty] | 53.15 |  |  |  | 53.15 | [5 empty] | 52.04 |  |  | 60.48 |  |  |  | 3.85 |  | 2.13 | [8 empty] | 44.72 |  |  |  |  | 0.00
1980 |  |  |  | 4460.00 |  |  | 5271 |  |  |  | 920 | [10 empty] | 55.71 |  |  |  | 55.71 | [5 empty] | 55.19 |  |  | 60.01 |  |  |  | 21.66 |  | 15.40 | [8 empty] | 28.89 |  |  |  |  | 0.00
1981 |  |  |  | 5209.60 |  |  | 6017 |  |  |  | 920 | [10 empty] | 65.16 |  |  |  | 65.16 | [5 empty] | 64.64 |  |  | 68.69 |  |  |  | 13.23 |  | 9.93 | [8 empty] | 24.90 |  |  |  |  | 0.00
1982 |  |  |  | 3341.70 |  |  | 3863 |  |  |  | 920 | [10 empty] | 41.65 |  |  |  | 41.65 | [5 empty] | 41.46 |  |  | 44.10 |  |  |  | 42.64 |  | 30.96 | [8 empty] | 27.40 |  |  |  |  | 0.00
1983 |  |  |  | 6725.00 |  |  | 7689 |  |  |  | 920 | [10 empty] | 85.30 |  |  |  | 85.30 | [5 empty] | 83.45 |  |  | 87.77 |  |  |  | 6.98 |  | 6.40 | [8 empty] | 8.30 |  |  |  |  | 0.00
1984 |  |  |  | 5748.00 |  |  | 6580 |  |  |  | 920 | [10 empty] | 87.95 |  |  |  | 87.95 | [5 empty] | 71.13 |  |  | 74.91 |  |  |  | 4.49 |  | 4.13 | [8 empty] | 7.92 |  |  |  |  | 0.00
1985 |  |  |  | 5948.80 |  |  | 7118 |  |  |  | 920 | [10 empty] | 76.00 |  |  |  | 79.74 | [5 empty] | 73.81 |  |  | 81.26 |  |  |  | 6.30 |  | 5.36 | [8 empty] | 14.90 |  |  |  |  | 3.74
1986 |  |  |  | 5945.60 |  |  | 7515 |  |  |  | 920 | [10 empty] | 84.51 |  |  |  | 86.37 | [5 empty] | 73.77 |  |  | 85.79 |  |  |  | 3.30 |  | 2.94 | [8 empty] | 10.68 |  |  |  |  | 1.86
1987 |  |  |  | 3581.10 |  |  | 4729 |  |  |  | 920 | [10 empty] | 51.62 |  |  |  | 53.37 | [5 empty] | 44.43 |  |  | 53.98 |  |  |  | 37.63 |  | 32.20 | [8 empty] | 14.43 |  |  |  |  | 1.75
1988 |  |  |  | 4495.00 |  |  | 5718 |  |  |  | 920 | [10 empty] | 63.15 |  |  |  | 67.02 | [5 empty] | 55.62 |  |  | 65.10 |  |  |  | 22.17 |  | 19.09 | [8 empty] | 13.88 |  |  |  |  | 3.87
1989 |  |  |  | 4700.83 |  |  | 5721 |  |  |  | 920 | [10 empty] | 61.06 |  |  |  | 64.74 | [5 empty] | 58.33 |  |  | 65.31 |  |  |  | 20.60 |  | 16.79 | [8 empty] | 18.47 |  |  |  |  | 3.68
1990 |  |  |  | 4878.71 |  |  | 6213 |  |  |  | 920 | [10 empty] | 69.32 |  |  |  | 69.66 | [5 empty] | 60.54 |  |  | 70.92 |  |  |  | 11.42 |  | 8.98 | [8 empty] | 21.36 |  |  |  |  | 0.34
1991 |  |  |  | 4927.21 |  |  | 6001 |  |  |  | 920 | [10 empty] | 64.44 |  |  |  | 66.70 | [5 empty] | 61.14 |  |  | 68.50 |  |  |  | 2.73 |  | 1.87 | [8 empty] | 31.42 |  |  |  |  | 2.26
1992 |  |  |  | 3918.31 |  |  | 4781 |  |  |  | 910 | [10 empty] | 50.22 |  |  |  | 53.86 | [5 empty] | 49.02 |  |  | 54.43 |  |  |  | 19.55 |  | 13.09 | [8 empty] | 33.06 |  |  |  |  | 3.64
1993 |  |  |  | 4509.91 |  |  | 5718 |  |  |  | 910 | [10 empty] | 94.18 |  |  |  | 99.21 | [5 empty] | 56.57 |  |  | 65.27 |  |  |  | 0.79 |  | 0.79 | [8 empty] | 0.00 |  |  |  |  | 5.03
1994 |  |  |  | 5782.19 |  |  | 6811 |  |  |  | 910 | [10 empty] | 76.55 |  |  |  | 77.70 | [5 empty] | 72.53 |  |  | 77.75 |  |  |  | 5.88 |  | 4.86 | [8 empty] | 17.44 |  |  |  |  | 1.15
1995 |  |  |  | 6045.65 |  |  | 7051 |  |  |  | 910 | [10 empty] | 78.10 |  |  |  | 79.65 | [5 empty] | 75.84 |  |  | 80.49 |  |  |  | 4.74 |  | 3.96 | [8 empty] | 16.39 |  |  |  |  | 1.55
1996 |  |  |  | 5533.91 |  |  | 6863 |  |  |  | 910 | [10 empty] | 75.43 |  |  |  | 78.74 | [5 empty] | 69.23 |  |  | 78.13 |  |  |  | 8.62 |  | 7.42 | [8 empty] | 13.84 |  |  |  |  | 3.30
1997 |  |  |  | 5477.66 |  |  | 6815 |  |  |  | 910 | [10 empty] | 81.00 |  |  |  | 84.40 | [5 empty] | 68.71 |  |  | 77.80 |  |  |  | 4.70 |  | 4.16 | [8 empty] | 11.44 |  |  |  |  | 3.40
1998 |  |  |  | 5379.41 |  |  | 6605 |  |  |  | 910 | [10 empty] | 72.90 |  |  |  | 77.60 | [5 empty] | 67.48 |  |  | 75.40 |  |  |  | 7.39 |  | 6.19 | [8 empty] | 16.21 |  |  |  |  | 4.70
1999 |  |  |  | 5960.27 |  |  | 7050 |  |  |  | 910 | [10 empty] | 77.52 |  |  |  | 78.94 | [5 empty] | 74.77 |  |  | 80.48 |  |  |  | 8.83 |  | 7.64 | [8 empty] | 13.42 |  |  |  |  | 1.42
2000 |  |  |  | 5183.54 |  |  | 6025 |  |  |  | 910 | [10 empty] | 66.29 |  |  |  | 68.50 | [5 empty] | 64.85 |  |  | 68.59 |  |  |  | 0.55 |  | 0.38 | [8 empty] | 31.13 |  |  |  |  | 2.20
2001 |  |  |  | 5685.92 |  |  | 6493 |  |  |  | 910 | [10 empty] | 72.23 |  |  |  | 72.27 | [5 empty] | 71.33 |  |  | 74.12 |  |  |  | 26.61 |  | 26.21 | [8 empty] | 1.53 |  |  |  |  | 0.03
2002 |  |  |  | 5542.28 |  |  | 6212 |  |  |  | 910 | [10 empty] | 69.90 |  |  |  | 70.17 | [5 empty] | 69.53 |  |  | 70.91 |  |  |  | 20.40 |  | 17.98 | [8 empty] | 11.85 |  |  |  |  | 0.26
2003 |  |  |  | 5521.65 |  |  | 6579 |  |  |  | 910 | [10 empty] | 71.00 |  |  |  | 74.83 | [5 empty] | 69.27 |  |  | 75.10 |  |  |  | 4.82 |  | 3.79 | [8 empty] | 21.38 |  |  |  |  | 3.83
2004 |  |  |  | 7593.43 |  |  | 8571 |  |  |  | 910 | [10 empty] | 95.97 |  |  |  | 97.12 | [5 empty] | 95.00 |  |  | 97.58 |  |  |  | 2.17 |  | 2.16 | [8 empty] | 0.72 |  |  |  |  | 1.14
2005 |  |  |  | 6373.89 |  |  | 7607 |  |  |  | 910 | [10 empty] | 81.71 |  |  |  | 86.74 | [5 empty] | 79.96 |  |  | 86.84 |  |  |  | 2.19 |  | 3.88 | [8 empty] | 9.38 |  |  |  |  | 5.03
2006 |  |  |  | 6125.65 |  |  | 7158 |  |  |  | 910 | [10 empty] | 79.17 |  |  |  | 80.93 | [5 empty] | 76.85 |  |  | 81.72 |  |  |  | 1.63 |  | 5.28 | [8 empty] | 13.79 |  |  |  |  | 1.76
2007 |  |  |  | 6925.13 |  |  | 7880 |  |  |  | 910 | [10 empty] | 87.64 |  |  |  | 88.72 | [5 empty] | 86.86 |  |  | 89.94 |  |  |  | 1.48 |  | 1.63 | [8 empty] | 9.65 |  |  |  |  | 1.07
2008 |  |  |  | 6130.76 |  |  | 7517 |  |  |  | 910 | [10 empty] | 77.74 |  |  |  | 78.90 | [5 empty] | 76.70 |  |  | 85.58 |  |  |  | 8.03 |  | 6.89 | [8 empty] | 14.21 |  |  |  |  | 1.16
2009 |  |  |  | 7285.26 |  |  | 8731 |  |  |  | 910 | [10 empty] | 96.09 |  |  |  | 98.97 | [5 empty] | 91.39 |  |  | 99.67 |  |  |  | 0.98 |  | 0.98 | [8 empty] | 0.05 |  |  |  |  | 2.88
2010 |  |  |  | 2218.07 |  |  | 2732 |  |  |  | 910 | [10 empty] | 27.93 |  |  |  | 31.94 | [5 empty] | 27.82 |  |  | 31.19 |  |  |  | 1.30 |  | 12.29 | [8 empty] | 55.77 |  |  |  |  | 4.01
2011 |  |  |  | 6127.50 |  |  | 7260 |  |  |  | 910 | [10 empty] | 79.65 |  |  |  | 82.06 | [5 empty] | 76.87 |  |  | 82.88 |  |  |  | 2.28 |  | 8.69 | [8 empty] | 9.26 |  |  |  |  | 2.41
2012 |  |  |  | 7658.29 |  |  | 8712 |  |  |  | 910 | [10 empty] | 98.37 |  |  |  | 99.27 | [5 empty] | 95.81 |  |  | 99.18 |  |  |  | 0.72 |  | 0.72 | [8 empty] | 0.01 |  |  |  |  | 0.90
2013 |  |  |  | 4679.30 |  |  | 5482 |  |  |  | 910 | [10 empty] | 60.35 |  |  |  | 61.21 | [5 empty] | 58.70 |  |  | 62.58 |  |  |  | 1.56 |  | 22.31 | [8 empty] | 16.49 |  |  |  |  | 0.85
2014 |  |  |  | 6386.08 |  |  | 7390 |  |  |  | 910 | [10 empty] | 82.10 |  |  |  | 83.54 | [5 empty] | 80.11 |  |  | 84.36 |  |  |  | 1.95 |  | 1.67 | [8 empty] | 14.79 |  |  |  |  | 1.44
2015 |  |  |  | 7307.72 |  |  | 8526 |  |  |  | 910 | [10 empty] | 95.01 |  |  |  | 98.48 | [5 empty] | 91.67 |  |  | 97.33 |  |  |  | 1.50 |  | 1.50 | [8 empty] | 0.02 |  |  |  |  | 3.47
2016 |  |  |  | 4345.61 |  |  | 5400 |  |  |  | 910 | [10 empty] | 54.40 |  |  |  | 60.80 | [5 empty] | 54.36 |  |  | 61.48 |  |  |  | 3.78 |  | 17.55 | [8 empty] | 21.65 |  |  |  |  | 6.39
2017 |  |  |  | 6690.06 |  |  | 7569 |  |  |  | 910 | [10 empty] | 84.40 |  |  |  | 87.66 | [5 empty] | 83.92 |  |  | 86.40 |  |  |  | 2.60 |  | 2.34 | [8 empty] | 10.00 |  |  |  |  | 3.25
2018 |  |  |  | 6115.35 |  |  | 6916 |  |  |  | 910 | [10 empty] | 76.59 |  |  |  | 79.71 | [5 empty] | 76.71 |  |  | 78.95 |  |  |  | 0.09 |  | 0.19 | [8 empty] | 20.10 |  |  |  |  | 3.12
2019 |  |  |  | 7443.41 |  |  | 8383 |  |  |  | 910 | [10 empty] | 93.64 |  |  |  | 95.04 | [5 empty] | 93.37 |  |  | 95.70 |  |  |  | 4.95 |  | 4.95 | [8 empty] | 0.01 |  |  |  |  | 1.39
2020 |  |  |  | 351.50 |  |  | 412 |  |  |  | 910 | [10 empty] | 4.40 |  |  |  | 9.96 | [5 empty] | 4.40 |  |  | 4.69 |  |  |  | 0.13 |  | 38.41 | [8 empty] | 51.63 |  |  |  |  | 5.55
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1979 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 515
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1177 |  |  |  | 32
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 90
E. |  | Testing of plant systems or components | [35 empty] | 9 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 32
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 11
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 5
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 31
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 1
Z. |  | Other | [35 empty] | 2 |  |  |  | 72
Subtotal | [37 empty] | 1278 |  |  |  | 662 | [11 empty] | 38
Total | [22 empty] | 0 | [14 empty] | 1978
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1979 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 176
12. |  |  | Reactor I&C Systems | [34 empty] | 20
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 50
15. |  |  | Reactor Cooling Systems | [34 empty] | 26
16. |  |  | Steam generation systems | [34 empty] | 26
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 36
32. |  |  | Feedwater and Main Steam System | [34 empty] | 23
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 92
35. |  |  | All other I&C Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 53
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [37 empty] | 526

## BUGEY-3
2020 Operating Experience
FR-14 | [8 empty] | BUGEY-3 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | FRAM (FRAMATOME)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP0 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-09-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-09-21
Gross electrical power | [12 empty] | : |  |  | 945 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-03-01
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2537.87 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 28.8 %
Energy Availability Factor (EAF) | [18 empty] | : | 33.18 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 46.21 %
Unit Capability Factor (UCF) | [18 empty] | : | 33.18 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.61 %
Load Factor (LF) | [18 empty] | : | 31.75 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 33.72 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 5822 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 581.07 | 532.88 |  |  |  | 670.44 |  | 631.05 | [8 empty] | 122.44 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2537.87
EAF [%] |  |  |  |  | 85.51 | 99.30 |  |  |  | 99.45 |  | 99.12 | [8 empty] | 18.10 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 33.18
UCF [%] |  |  |  |  | 85.51 | 99.30 |  |  |  | 99.45 |  | 99.12 | [8 empty] | 18.10 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 33.18
LF [%] |  |  |  |  | 85.82 | 84.13 |  |  |  | 99.16 |  | 96.31 | [8 empty] | 18.08 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 31.75
OF [%] |  |  |  |  | 86.42 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 21.51 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 33.72
FLR [%] |  |  |  |  | 13.42 | 0.69 |  |  |  | 0.51 |  | 0.87 | [8 empty] | 81.90 |  |  | 100.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 28.80
UCL [%] |  |  |  |  | 13.26 | 0.69 |  |  |  | 0.51 |  | 0.87 | [8 empty] | 81.90 |  |  | 63.33 | [6 empty] | 54.84 |  | 100.00 |  |  |  | 90.00 |  |  | 0.00 |  |  | 46.67 | [9 empty] | 100.00 |  |  | 46.21
PUF [%] |  |  |  |  | 1.23 | 0.01 |  |  |  | 0.04 |  | 0.01 | [8 empty] | 0.00 |  |  | 36.67 | [6 empty] | 45.16 |  | 0.00 |  |  |  | 10.00 |  |  | 100.00 |  |  | 53.33 | [9 empty] | 0.00 |  |  | 20.61
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 222466.34 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.79 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 70.65 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.98 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 73.18 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.84 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 66.24 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.53 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 71.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 3504.00 |  |  | 4389 |  |  |  | 925 | [10 empty] | 39.87 |  |  |  | 39.87 | [5 empty] | 40.39 |  |  | 45.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 60.13 |  |  |  |  | 0.00
1980 |  |  |  | 5960.00 |  |  | 6951 |  |  |  | 920 | [10 empty] | 74.66 |  |  |  | 74.66 | [5 empty] | 73.75 |  |  | 79.13 |  |  |  | 12.90 |  | 11.05 | [8 empty] | 14.28 |  |  |  |  | 0.00
1981 |  |  |  | 4849.60 |  |  | 5646 |  |  |  | 920 | [10 empty] | 61.04 |  |  |  | 61.04 | [5 empty] | 60.17 |  |  | 64.45 |  |  |  | 7.91 |  | 5.24 | [8 empty] | 33.71 |  |  |  |  | 0.00
1982 |  |  |  | 6002.20 |  |  | 7661 |  |  |  | 920 | [10 empty] | 78.90 |  |  |  | 78.90 | [5 empty] | 74.48 |  |  | 87.45 |  |  |  | 7.28 |  | 6.20 | [8 empty] | 14.90 |  |  |  |  | 0.00
1983 |  |  |  | 5525.00 |  |  | 6556 |  |  |  | 920 | [10 empty] | 74.04 |  |  |  | 74.04 | [5 empty] | 68.56 |  |  | 74.84 |  |  |  | 10.03 |  | 8.25 | [8 empty] | 17.71 |  |  |  |  | 0.00
1984 |  |  |  | 5793.00 |  |  | 6905 |  |  |  | 920 | [10 empty] | 77.95 |  |  |  | 77.95 | [5 empty] | 71.68 |  |  | 78.61 |  |  |  | 10.85 |  | 9.49 | [8 empty] | 12.56 |  |  |  |  | 0.00
1985 |  |  |  | 4571.10 |  |  | 5235 |  |  |  | 920 | [10 empty] | 57.17 |  |  |  | 58.70 | [5 empty] | 56.72 |  |  | 59.76 |  |  |  | 31.91 |  | 27.51 | [8 empty] | 13.80 |  |  |  |  | 1.53
1986 |  |  |  | 6558.10 |  |  | 7634 |  |  |  | 920 | [10 empty] | 87.13 |  |  |  | 87.65 | [5 empty] | 81.37 |  |  | 87.15 |  |  |  | 1.89 |  | 1.69 | [8 empty] | 10.66 |  |  |  |  | 0.52
1987 |  |  |  | 5482.50 |  |  | 6637 |  |  |  | 920 | [10 empty] | 76.39 |  |  |  | 78.36 | [5 empty] | 68.03 |  |  | 75.76 |  |  |  | 10.45 |  | 9.14 | [8 empty] | 12.50 |  |  |  |  | 1.97
1988 |  |  |  | 3812.00 |  |  | 4935 |  |  |  | 920 | [10 empty] | 62.42 |  |  |  | 64.68 | [5 empty] | 47.17 |  |  | 56.18 |  |  |  | 23.14 |  | 19.48 | [8 empty] | 15.84 |  |  |  |  | 2.26
1989 |  |  |  | 4914.26 |  |  | 6467 |  |  |  | 920 | [10 empty] | 87.37 |  |  |  | 88.72 | [5 empty] | 60.98 |  |  | 73.82 |  |  |  | 10.86 |  | 10.81 | [8 empty] | 0.47 |  |  |  |  | 1.35
1990 |  |  |  | 4538.61 |  |  | 5474 |  |  |  | 920 | [10 empty] | 62.95 |  |  |  | 68.02 | [5 empty] | 56.32 |  |  | 62.49 |  |  |  | 14.73 |  | 11.75 | [8 empty] | 20.24 |  |  |  |  | 5.07
1991 |  |  |  | 3442.82 |  |  | 4168 |  |  |  | 920 | [10 empty] | 51.68 |  |  |  | 55.68 | [5 empty] | 42.72 |  |  | 47.58 |  |  |  | 9.48 |  | 5.83 | [8 empty] | 38.49 |  |  |  |  | 4.00
1992 |  |  |  | 2489.99 |  |  | 2879 |  |  |  | 910 | [10 empty] | 32.19 |  |  |  | 32.50 | [5 empty] | 31.15 |  |  | 32.78 |  |  |  | 67.39 |  | 67.17 | [8 empty] | 0.33 |  |  |  |  | 0.31
1993 |  |  |  | 5954.45 |  |  | 7117 |  |  |  | 910 | [10 empty] | 76.13 |  |  |  | 80.20 | [5 empty] | 74.70 |  |  | 81.24 |  |  |  | 3.88 |  | 3.24 | [8 empty] | 16.56 |  |  |  |  | 4.07
1994 |  |  |  | 4717.68 |  |  | 5872 |  |  |  | 910 | [10 empty] | 65.25 |  |  |  | 69.97 | [5 empty] | 59.18 |  |  | 67.03 |  |  |  | 16.89 |  | 14.22 | [8 empty] | 15.80 |  |  |  |  | 4.72
1995 |  |  |  | 5535.71 |  |  | 6564 |  |  |  | 910 | [10 empty] | 95.21 |  |  |  | 95.93 | [5 empty] | 69.44 |  |  | 74.93 |  |  |  | 3.60 |  | 3.59 | [8 empty] | 0.48 |  |  |  |  | 0.72
1996 |  |  |  | 5652.94 |  |  | 7012 |  |  |  | 910 | [10 empty] | 76.38 |  |  |  | 78.72 | [5 empty] | 70.72 |  |  | 79.83 |  |  |  | 10.63 |  | 9.37 | [8 empty] | 11.91 |  |  |  |  | 2.34
1997 |  |  |  | 5596.64 |  |  | 6561 |  |  |  | 910 | [10 empty] | 74.89 |  |  |  | 74.98 | [5 empty] | 70.21 |  |  | 74.90 |  |  |  | 10.44 |  | 8.74 | [8 empty] | 16.28 |  |  |  |  | 0.08
1998 |  |  |  | 6680.36 |  |  | 7875 |  |  |  | 910 | [10 empty] | 89.04 |  |  |  | 89.13 | [5 empty] | 83.80 |  |  | 89.90 |  |  |  | 1.44 |  | 1.30 | [8 empty] | 9.56 |  |  |  |  | 0.09
1999 |  |  |  | 5786.61 |  |  | 7001 |  |  |  | 910 | [10 empty] | 77.26 |  |  |  | 77.60 | [5 empty] | 72.59 |  |  | 79.92 |  |  |  | 10.96 |  | 9.56 | [8 empty] | 12.85 |  |  |  |  | 0.33
2000 |  |  |  | 5745.14 |  |  | 6765 |  |  |  | 910 | [10 empty] | 74.71 |  |  |  | 75.70 | [5 empty] | 71.87 |  |  | 77.02 |  |  |  | 13.70 |  | 12.02 | [8 empty] | 12.28 |  |  |  |  | 0.99
2001 |  |  |  | 6230.61 |  |  | 7129 |  |  |  | 910 | [10 empty] | 81.20 |  |  |  | 81.80 | [5 empty] | 78.16 |  |  | 81.38 |  |  |  | 4.21 |  | 3.60 | [8 empty] | 14.60 |  |  |  |  | 0.60
2002 |  |  |  | 4634.68 |  |  | 5654 |  |  |  | 910 | [10 empty] | 63.88 |  |  |  | 66.43 | [5 empty] | 58.14 |  |  | 64.54 |  |  |  | 4.18 |  | 2.90 | [8 empty] | 30.68 |  |  |  |  | 2.54
2003 |  |  |  | 6646.07 |  |  | 7924 |  |  |  | 910 | [10 empty] | 85.15 |  |  |  | 97.22 | [5 empty] | 83.37 |  |  | 90.46 |  |  |  | 1.42 |  | 1.40 | [8 empty] | 1.38 |  |  |  |  | 12.06
2004 |  |  |  | 6447.31 |  |  | 7461 |  |  |  | 910 | [10 empty] | 87.85 |  |  |  | 88.23 | [5 empty] | 80.66 |  |  | 84.94 |  |  |  | 2.89 |  | 2.62 | [8 empty] | 9.15 |  |  |  |  | 0.37
2005 |  |  |  | 5805.39 |  |  | 7017 |  |  |  | 910 | [10 empty] | 76.85 |  |  |  | 82.31 | [5 empty] | 72.83 |  |  | 80.10 |  |  |  | 4.37 |  | 4.48 | [8 empty] | 13.20 |  |  |  |  | 5.46
2006 |  |  |  | 6563.54 |  |  | 7624 |  |  |  | 910 | [10 empty] | 83.89 |  |  |  | 89.14 | [5 empty] | 82.34 |  |  | 87.03 |  |  |  | 2.00 |  | 2.09 | [8 empty] | 8.77 |  |  |  |  | 5.25
2007 |  |  |  | 7277.78 |  |  | 8258 |  |  |  | 910 | [10 empty] | 91.39 |  |  |  | 93.44 | [5 empty] | 91.30 |  |  | 94.27 |  |  |  | 3.85 |  | 3.74 | [8 empty] | 2.82 |  |  |  |  | 2.05
2008 |  |  |  | 5807.10 |  |  | 7352 |  |  |  | 910 | [10 empty] | 72.94 |  |  |  | 73.49 | [5 empty] | 72.65 |  |  | 83.70 |  |  |  | 14.37 |  | 13.33 | [8 empty] | 13.18 |  |  |  |  | 0.54
2009 |  |  |  | 1984.81 |  |  | 2676 |  |  |  | 910 | [10 empty] | 24.97 |  |  |  | 31.00 | [5 empty] | 24.90 |  |  | 30.55 |  |  |  | 16.68 |  | 60.24 | [8 empty] | 8.76 |  |  |  |  | 6.04
2010 |  |  |  | 0.00 |  |  | 0 |  |  |  | 910 | [10 empty] | 0.00 |  |  |  | 12.88 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 58.34 | [8 empty] | 28.78 |  |  |  |  | 12.88
2011 |  |  |  | 7184.55 |  |  | 8370 |  |  |  | 910 | [10 empty] | 92.08 |  |  |  | 96.70 | [5 empty] | 90.13 |  |  | 95.55 |  |  |  | 1.77 |  | 1.75 | [8 empty] | 1.55 |  |  |  |  | 4.62
2012 |  |  |  | 5696.79 |  |  | 6487 |  |  |  | 910 | [10 empty] | 71.64 |  |  |  | 73.68 | [5 empty] | 71.27 |  |  | 73.85 |  |  |  | 5.07 |  | 11.11 | [8 empty] | 15.21 |  |  |  |  | 2.04
2013 |  |  |  | 4321.81 |  |  | 4929 |  |  |  | 910 | [10 empty] | 55.12 |  |  |  | 55.40 | [5 empty] | 54.22 |  |  | 56.27 |  |  |  | 2.07 |  | 11.31 | [8 empty] | 33.30 |  |  |  |  | 0.27
2014 |  |  |  | 7412.21 |  |  | 8563 |  |  |  | 910 | [10 empty] | 97.69 |  |  |  | 98.52 | [5 empty] | 92.98 |  |  | 97.75 |  |  |  | 1.43 |  | 1.43 | [8 empty] | 0.06 |  |  |  |  | 0.83
2015 |  |  |  | 6656.93 |  |  | 7664 |  |  |  | 910 | [10 empty] | 84.60 |  |  |  | 86.70 | [5 empty] | 83.51 |  |  | 87.49 |  |  |  | 3.30 |  | 3.21 | [8 empty] | 10.09 |  |  |  |  | 2.10
2016 |  |  |  | 5556.90 |  |  | 6516 |  |  |  | 910 | [10 empty] | 70.15 |  |  |  | 71.51 | [5 empty] | 69.52 |  |  | 74.18 |  |  |  | 6.77 |  | 8.61 | [8 empty] | 19.88 |  |  |  |  | 1.36
2017 |  |  |  | 6840.57 |  |  | 7744 |  |  |  | 910 | [10 empty] | 86.28 |  |  |  | 89.66 | [5 empty] | 85.81 |  |  | 88.40 |  |  |  | 0.80 |  | 0.72 | [8 empty] | 9.62 |  |  |  |  | 3.38
2018 |  |  |  | 6993.15 |  |  | 8196 |  |  |  | 910 | [10 empty] | 89.68 |  |  |  | 99.94 | [5 empty] | 87.73 |  |  | 93.56 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 0.01 |  |  |  |  | 10.26
2019 |  |  |  | 4893.90 |  |  | 5806 |  |  |  | 910 | [10 empty] | 61.73 |  |  |  | 64.80 | [5 empty] | 61.39 |  |  | 66.28 |  |  |  | 10.14 |  | 8.55 | [8 empty] | 26.64 |  |  |  |  | 3.07
2020 |  |  |  | 2537.87 |  |  | 2962 |  |  |  | 910 | [10 empty] | 33.18 |  |  |  | 33.18 | [5 empty] | 31.75 |  |  | 33.72 |  |  |  | 28.80 |  | 46.21 | [8 empty] | 20.61 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1979 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 705
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1055 |  |  |  | 31
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 55
E. |  | Testing of plant systems or components | [35 empty] | 35 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 11
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 29
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 19 | [11 empty] | 99
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 1
Z. |  | Other | [39 empty] | 12
Subtotal | [37 empty] | 1147 |  |  |  | 781 | [11 empty] | 141
Total | [22 empty] | 0 | [14 empty] | 2069
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1979 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 158
12. |  |  | Reactor I&C Systems | [34 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 13
14. |  |  | Safety Systems | [34 empty] | 16
15. |  |  | Reactor Cooling Systems | [34 empty] | 32
16. |  |  | Steam generation systems | [34 empty] | 257
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 44
32. |  |  | Feedwater and Main Steam System | [34 empty] | 20
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 53
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 85
42. |  |  | Electrical Power Supply Systems | [34 empty] | 13
Total | [37 empty] | 704

## BUGEY-4
2020 Operating Experience
FR-15 | [8 empty] | BUGEY-4 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | FRAM (FRAMATOME)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP0 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-06-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1979-03-08
Gross electrical power | [12 empty] | : |  |  | 917 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-07-01
Reference unit power (net) | [12 empty] | : |  |  | 880 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6391.78 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.3 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.8 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.94 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.1 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.96 %
Load Factor (LF) | [18 empty] | : | 82.69 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.3 %
Operating Factor (OF) | [18 empty] | : | 86.45 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1190 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 675.04 | 605.30 |  |  |  | 615.89 |  | 543.76 | [8 empty] | 604.98 |  |  | 628.79 | [6 empty] | 604.00 |  | 642.51 |  |  |  | 619.59 |  |  | 496.70 |  |  | 355.22 | [9 empty] | 0.00 |  |  | 6391.78
EAF [%] |  |  |  |  | 100.00 | 99.58 |  |  |  | 100.00 |  | 99.78 | [8 empty] | 99.89 |  |  | 99.49 | [6 empty] | 92.32 |  | 98.20 |  |  |  | 97.91 |  |  | 75.80 |  |  | 56.12 | [9 empty] | 0.00 |  |  | 84.80
UCF [%] |  |  |  |  | 100.00 | 99.77 |  |  |  | 100.00 |  | 99.78 | [8 empty] | 99.99 |  |  | 99.91 | [6 empty] | 93.58 |  | 99.70 |  |  |  | 99.88 |  |  | 77.18 |  |  | 64.99 | [9 empty] | 0.00 |  |  | 86.10
LF [%] |  |  |  |  | 103.10 | 98.83 |  |  |  | 94.20 |  | 85.82 | [8 empty] | 92.40 |  |  | 99.24 | [6 empty] | 92.25 |  | 98.13 |  |  |  | 97.79 |  |  | 75.76 |  |  | 56.06 | [9 empty] | 0.00 |  |  | 82.69
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 94.09 |  | 100.00 |  |  |  | 100.00 |  |  | 77.85 |  |  | 67.08 | [9 empty] | 0.00 |  |  | 86.45
FLR [%] |  |  |  |  | 0.00 | 0.20 |  |  |  | 0.00 |  | 0.22 | [8 empty] | 0.00 |  |  | 0.08 | [6 empty] | 6.41 |  | 0.29 |  |  |  | 0.11 |  |  | 22.81 |  |  | 6.79 | [9 empty] | 0.00 |  |  | 3.30
UCL [%] |  |  |  |  | 0.00 | 0.20 |  |  |  | 0.00 |  | 0.22 | [8 empty] | 0.00 |  |  | 0.08 | [6 empty] | 6.40 |  | 0.29 |  |  |  | 0.11 |  |  | 22.81 |  |  | 4.74 | [9 empty] | 0.00 |  |  | 2.94
PUF [%] |  |  |  |  | 0.00 | 0.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.01 | [6 empty] | 0.02 |  | 0.01 |  |  |  | 0.01 |  |  | 0.01 |  |  | 30.27 | [9 empty] | 100.00 |  |  | 10.96
XUF [%] |  |  |  |  | 0.00 | 0.18 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.10 |  |  | 0.42 | [6 empty] | 1.26 |  | 1.51 |  |  |  | 1.97 |  |  | 1.38 |  |  | 8.86 | [9 empty] | 0.00 |  |  | 1.30
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 228177.72 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 8.01 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.89 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.13 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.93 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.94 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.55 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.33 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 3528.00 |  |  | 5030 |  |  |  | 900 | [10 empty] | 64.64 |  |  |  | 64.64 | [5 empty] | 58.45 |  |  | 64.63 |  |  |  | 7.03 |  | 4.89 | [8 empty] | 30.47 |  |  |  |  | 0.00
1980 |  |  |  | 5063.00 |  |  | 5983 |  |  |  | 900 | [10 empty] | 65.84 |  |  |  | 65.84 | [5 empty] | 64.04 |  |  | 68.11 |  |  |  | 7.76 |  | 5.54 | [8 empty] | 28.63 |  |  |  |  | 0.00
1981 |  |  |  | 5671.90 |  |  | 6834 |  |  |  | 900 | [10 empty] | 75.58 |  |  |  | 75.58 | [5 empty] | 71.94 |  |  | 78.01 |  |  |  | 7.43 |  | 6.07 | [8 empty] | 18.35 |  |  |  |  | 0.00
1982 |  |  |  | 5474.90 |  |  | 6276 |  |  |  | 900 | [10 empty] | 69.75 |  |  |  | 69.75 | [5 empty] | 69.44 |  |  | 71.64 |  |  |  | 18.88 |  | 16.23 | [8 empty] | 14.02 |  |  |  |  | 0.00
1983 |  |  |  | 6329.00 |  |  | 7389 |  |  |  | 900 | [10 empty] | 83.23 |  |  |  | 83.28 | [5 empty] | 80.28 |  |  | 84.35 |  |  |  | 2.40 |  | 2.05 | [8 empty] | 14.67 |  |  |  |  | 0.05
1984 |  |  |  | 5882.00 |  |  | 6896 |  |  |  | 900 | [10 empty] | 75.84 |  |  |  | 75.84 | [5 empty] | 74.40 |  |  | 78.51 |  |  |  | 8.57 |  | 7.11 | [8 empty] | 17.05 |  |  |  |  | 0.00
1985 |  |  |  | 6224.40 |  |  | 7696 |  |  |  | 900 | [10 empty] | 86.67 |  |  |  | 87.22 | [5 empty] | 78.95 |  |  | 87.85 |  |  |  | 2.08 |  | 1.85 | [8 empty] | 10.93 |  |  |  |  | 0.55
1986 |  |  |  | 5312.70 |  |  | 6622 |  |  |  | 900 | [10 empty] | 76.12 |  |  |  | 78.72 | [5 empty] | 67.39 |  |  | 75.59 |  |  |  | 6.46 |  | 5.44 | [8 empty] | 15.84 |  |  |  |  | 2.60
1987 |  |  |  | 4670.90 |  |  | 6180 |  |  |  | 900 | [10 empty] | 78.16 |  |  |  | 79.80 | [5 empty] | 59.25 |  |  | 70.55 |  |  |  | 6.45 |  | 5.50 | [8 empty] | 14.70 |  |  |  |  | 1.63
1988 |  |  |  | 3323.00 |  |  | 4524 |  |  |  | 900 | [10 empty] | 51.52 |  |  |  | 67.31 | [5 empty] | 42.03 |  |  | 51.50 |  |  |  | 23.06 |  | 20.18 | [8 empty] | 12.51 |  |  |  |  | 15.80
1989 |  |  |  | 5541.34 |  |  | 6846 |  |  |  | 900 | [10 empty] | 76.16 |  |  |  | 76.69 | [5 empty] | 70.29 |  |  | 78.15 |  |  |  | 9.60 |  | 8.14 | [8 empty] | 15.17 |  |  |  |  | 0.53
1990 |  |  |  | 3186.65 |  |  | 4312 |  |  |  | 880 | [10 empty] | 53.52 |  |  |  | 56.66 | [5 empty] | 41.34 |  |  | 49.22 |  |  |  | 4.28 |  | 2.53 | [8 empty] | 40.81 |  |  |  |  | 3.13
1991 |  |  |  | 4984.85 |  |  | 6317 |  |  |  | 880 | [10 empty] | 69.33 |  |  |  | 71.78 | [5 empty] | 64.66 |  |  | 72.11 |  |  |  | 12.15 |  | 9.93 | [8 empty] | 18.29 |  |  |  |  | 2.45
1992 |  |  |  | 1649.11 |  |  | 2012 |  |  |  | 880 | [10 empty] | 22.25 |  |  |  | 22.25 | [5 empty] | 21.33 |  |  | 22.91 |  |  |  | 77.11 |  | 74.94 | [8 empty] | 2.82 |  |  |  |  | 0.00
1993 |  |  |  | 5748.62 |  |  | 7506 |  |  |  | 880 | [10 empty] | 74.24 |  |  |  | 82.16 | [5 empty] | 74.57 |  |  | 85.68 |  |  |  | 5.37 |  | 4.66 | [8 empty] | 13.18 |  |  |  |  | 7.92
1994 |  |  |  | 5209.34 |  |  | 6619 |  |  |  | 880 | [10 empty] | 82.16 |  |  |  | 83.47 | [5 empty] | 67.58 |  |  | 75.56 |  |  |  | 3.58 |  | 3.10 | [8 empty] | 13.43 |  |  |  |  | 1.31
1995 |  |  |  | 3989.94 |  |  | 4843 |  |  |  | 880 | [10 empty] | 59.14 |  |  |  | 64.32 | [5 empty] | 51.76 |  |  | 55.29 |  |  |  | 16.92 |  | 13.10 | [8 empty] | 22.57 |  |  |  |  | 5.19
1996 |  |  |  | 4188.12 |  |  | 5333 |  |  |  | 880 | [10 empty] | 62.37 |  |  |  | 62.57 | [5 empty] | 54.18 |  |  | 60.71 |  |  |  | 34.28 |  | 32.64 | [8 empty] | 4.79 |  |  |  |  | 0.20
1997 |  |  |  | 5652.46 |  |  | 7420 |  |  |  | 880 | [10 empty] | 80.75 |  |  |  | 83.58 | [5 empty] | 73.32 |  |  | 84.70 |  |  |  | 2.58 |  | 2.21 | [8 empty] | 14.21 |  |  |  |  | 2.83
1998 |  |  |  | 6304.00 |  |  | 7791 |  |  |  | 880 | [10 empty] | 86.32 |  |  |  | 88.31 | [5 empty] | 81.78 |  |  | 88.94 |  |  |  | 2.09 |  | 1.88 | [8 empty] | 9.81 |  |  |  |  | 1.99
1999 |  |  |  | 5591.31 |  |  | 7231 |  |  |  | 880 | [10 empty] | 77.46 |  |  |  | 81.55 | [5 empty] | 72.53 |  |  | 82.55 |  |  |  | 0.39 |  | 0.32 | [8 empty] | 18.13 |  |  |  |  | 4.09
2000 |  |  |  | 5987.96 |  |  | 7544 |  |  |  | 880 | [10 empty] | 82.58 |  |  |  | 85.08 | [5 empty] | 77.46 |  |  | 85.88 |  |  |  | 3.07 |  | 2.70 | [8 empty] | 12.22 |  |  |  |  | 2.50
2001 |  |  |  | 4746.00 |  |  | 5921 |  |  |  | 880 | [10 empty] | 63.43 |  |  |  | 65.82 | [5 empty] | 61.57 |  |  | 67.59 |  |  |  | 2.47 |  | 1.66 | [8 empty] | 32.52 |  |  |  |  | 2.39
2002 |  |  |  | 5590.81 |  |  | 7130 |  |  |  | 880 | [10 empty] | 83.36 |  |  |  | 83.51 | [5 empty] | 72.53 |  |  | 81.39 |  |  |  | 0.90 |  | 0.76 | [8 empty] | 15.73 |  |  |  |  | 0.15
2003 |  |  |  | 6645.34 |  |  | 8192 |  |  |  | 880 | [10 empty] | 94.23 |  |  |  | 95.56 | [5 empty] | 86.20 |  |  | 93.52 |  |  |  | 4.43 |  | 4.43 | [8 empty] | 0.01 |  |  |  |  | 1.33
2004 |  |  |  | 6098.32 |  |  | 7367 |  |  |  | 880 | [10 empty] | 81.31 |  |  |  | 82.97 | [5 empty] | 78.89 |  |  | 83.87 |  |  |  | 2.42 |  | 2.05 | [8 empty] | 14.98 |  |  |  |  | 1.66
2005 |  |  |  | 6073.19 |  |  | 7672 |  |  |  | 880 | [10 empty] | 80.34 |  |  |  | 83.97 | [5 empty] | 78.78 |  |  | 87.58 |  |  |  | 7.39 |  | 6.70 | [8 empty] | 9.33 |  |  |  |  | 3.63
2006 |  |  |  | 6846.66 |  |  | 8341 |  |  |  | 880 | [10 empty] | 93.15 |  |  |  | 94.65 | [5 empty] | 88.82 |  |  | 95.22 |  |  |  | 2.50 |  | 2.42 | [8 empty] | 2.93 |  |  |  |  | 1.50
2007 |  |  |  | 3586.19 |  |  | 4217 |  |  |  | 880 | [10 empty] | 46.76 |  |  |  | 47.20 | [5 empty] | 46.52 |  |  | 48.14 |  |  |  | 1.14 |  | 15.77 | [8 empty] | 37.03 |  |  |  |  | 0.44
2008 |  |  |  | 6790.40 |  |  | 7891 |  |  |  | 880 | [10 empty] | 87.70 |  |  |  | 88.48 | [5 empty] | 87.85 |  |  | 89.83 |  |  |  | 1.46 |  | 1.54 | [8 empty] | 9.98 |  |  |  |  | 0.78
2009 |  |  |  | 5094.25 |  |  | 6262 |  |  |  | 880 | [10 empty] | 67.46 |  |  |  | 75.16 | [5 empty] | 66.08 |  |  | 71.48 |  |  |  | 5.81 |  | 10.47 | [8 empty] | 14.36 |  |  |  |  | 7.70
2010 |  |  |  | 7374.14 |  |  | 8674 |  |  |  | 880 | [10 empty] | 98.36 |  |  |  | 98.95 | [5 empty] | 95.66 |  |  | 99.02 |  |  |  | 1.03 |  | 1.02 | [8 empty] | 0.02 |  |  |  |  | 0.59
2011 |  |  |  | 4458.28 |  |  | 5344 |  |  |  | 880 | [10 empty] | 58.75 |  |  |  | 59.29 | [5 empty] | 57.83 |  |  | 61.00 |  |  |  | 1.87 |  | 10.14 | [8 empty] | 30.56 |  |  |  |  | 0.54
2012 |  |  |  | 6365.58 |  |  | 7529 |  |  |  | 880 | [10 empty] | 83.51 |  |  |  | 87.26 | [5 empty] | 82.35 |  |  | 85.71 |  |  |  | 1.52 |  | 4.14 | [8 empty] | 8.59 |  |  |  |  | 3.75
2013 |  |  |  | 7125.79 |  |  | 8425 |  |  |  | 880 | [10 empty] | 95.40 |  |  |  | 96.19 | [5 empty] | 92.44 |  |  | 96.18 |  |  |  | 3.79 |  | 3.79 | [8 empty] | 0.02 |  |  |  |  | 0.79
2014 |  |  |  | 5022.76 |  |  | 6265 |  |  |  | 880 | [10 empty] | 68.53 |  |  |  | 70.60 | [5 empty] | 65.16 |  |  | 71.52 |  |  |  | 1.36 |  | 8.47 | [8 empty] | 20.93 |  |  |  |  | 2.06
2015 |  |  |  | 6335.29 |  |  | 7448 |  |  |  | 880 | [10 empty] | 82.93 |  |  |  | 83.43 | [5 empty] | 82.18 |  |  | 85.02 |  |  |  | 5.88 |  | 5.64 | [8 empty] | 10.94 |  |  |  |  | 0.50
2016 |  |  |  | 4915.52 |  |  | 5739 |  |  |  | 880 | [10 empty] | 64.52 |  |  |  | 65.19 | [5 empty] | 63.59 |  |  | 65.33 |  |  |  | 0.11 |  | 12.89 | [8 empty] | 21.92 |  |  |  |  | 0.67
2017 |  |  |  | 7189.64 |  |  | 8420 |  |  |  | 880 | [10 empty] | 94.74 |  |  |  | 95.20 | [5 empty] | 93.27 |  |  | 96.12 |  |  |  | 0.49 |  | 4.19 | [8 empty] | 0.61 |  |  |  |  | 0.46
2018 |  |  |  | 5628.66 |  |  | 6625 |  |  |  | 880 | [10 empty] | 73.06 |  |  |  | 74.24 | [5 empty] | 73.02 |  |  | 75.63 |  |  |  | 5.71 |  | 5.27 | [8 empty] | 20.48 |  |  |  |  | 1.19
2019 |  |  |  | 6584.52 |  |  | 7618 |  |  |  | 880 | [10 empty] | 84.80 |  |  |  | 85.47 | [5 empty] | 85.42 |  |  | 86.96 |  |  |  | 3.25 |  | 4.26 | [8 empty] | 10.27 |  |  |  |  | 0.67
2020 |  |  |  | 6391.78 |  |  | 7594 |  |  |  | 880 | [10 empty] | 84.80 |  |  |  | 86.10 | [5 empty] | 82.69 |  |  | 86.45 |  |  |  | 3.30 |  | 2.94 | [8 empty] | 10.96 |  |  |  |  | 1.30
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1979 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 546
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1116 |  |  |  | 16
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 76
E. |  | Testing of plant systems or components | [35 empty] | 10 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 27
L. |  | Human factor related | [39 empty] | 10
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 42
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 6
Z. |  | Other | [39 empty] | 15
Subtotal | [37 empty] | 1202 |  |  |  | 614 | [11 empty] | 48
Total | [22 empty] | 0 | [14 empty] | 1864
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1979 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 198
12. |  |  | Reactor I&C Systems | [34 empty] | 23
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 19
15. |  |  | Reactor Cooling Systems | [34 empty] | 18
16. |  |  | Steam generation systems | [34 empty] | 70
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 44
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 42
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 29
42. |  |  | Electrical Power Supply Systems | [34 empty] | 99
Total | [37 empty] | 567

## BUGEY-5
2020 Operating Experience
FR-16 | [8 empty] | BUGEY-5 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | FRAM (FRAMATOME)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP0 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-07-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1979-07-31
Gross electrical power | [12 empty] | : |  |  | 917 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-01-03
Reference unit power (net) | [12 empty] | : |  |  | 880 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5887.45 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.68 %
Energy Availability Factor (EAF) | [18 empty] | : | 76.2 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.88 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.59 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.53 %
Load Factor (LF) | [18 empty] | : | 76.16 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 7.39 %
Operating Factor (OF) | [18 empty] | : | 78.56 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1883 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 524.86 | 397.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 566.11 |  |  | 630.80 | [6 empty] | 647.28 |  | 559.57 |  |  |  | 623.41 |  |  | 651.32 |  |  | 629.55 | [9 empty] | 657.36 |  |  | 5887.45
EAF [%] |  |  |  |  | 80.02 | 64.91 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 86.76 |  |  | 99.53 | [6 empty] | 98.86 |  | 85.49 |  |  |  | 98.23 |  |  | 99.74 |  |  | 99.77 | [9 empty] | 99.97 |  |  | 76.20
UCF [%] |  |  |  |  | 100.00 | 80.24 |  |  |  | 0.01 |  | 50.01 | [8 empty] | 87.06 |  |  | 99.96 | [6 empty] | 99.99 |  | 86.66 |  |  |  | 99.79 |  |  | 99.74 |  |  | 99.80 | [9 empty] | 99.97 |  |  | 83.59
LF [%] |  |  |  |  | 80.17 | 64.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 86.47 |  |  | 99.56 | [6 empty] | 98.86 |  | 85.47 |  |  |  | 98.39 |  |  | 99.35 |  |  | 99.36 | [9 empty] | 100.40 |  |  | 76.16
OF [%] |  |  |  |  | 81.59 | 78.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 94.76 |  |  | 100.00 | [6 empty] | 100.00 |  | 87.10 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.56
FLR [%] |  |  |  |  | 0.00 | 2.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.93 |  |  | 0.02 | [6 empty] | 0.00 |  | 13.34 |  |  |  | 0.19 |  |  | 0.26 |  |  | 0.18 | [9 empty] | 0.03 |  |  | 1.68
UCL [%] |  |  |  |  | 0.00 | 2.24 |  |  |  | 0.00 |  | 36.66 | [8 empty] | 6.03 |  |  | 0.02 | [6 empty] | 0.00 |  | 13.34 |  |  |  | 0.19 |  |  | 0.26 |  |  | 0.18 | [9 empty] | 0.03 |  |  | 4.88
PUF [%] |  |  |  |  | 0.00 | 17.52 |  |  |  | 99.99 |  | 13.34 | [8 empty] | 6.91 |  |  | 0.02 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 11.53
XUF [%] |  |  |  |  | 19.98 | 15.32 |  |  |  | 0.00 |  | 50.00 | [8 empty] | 0.29 |  |  | 0.43 | [6 empty] | 1.13 |  | 1.17 |  |  |  | 1.56 |  |  | 0.00 |  |  | 0.04 | [9 empty] | 0.00 |  |  | 7.39
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 218279.85 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.39 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.87 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 10.16 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.21 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.63 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 68.31 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.34 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.49 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 6589.00 |  |  | 8050 |  |  |  | 900 | [10 empty] | 84.50 |  |  |  | 84.50 | [5 empty] | 83.35 |  |  | 91.64 |  |  |  | 5.14 |  | 4.58 | [8 empty] | 10.92 |  |  |  |  | 0.00
1981 |  |  |  | 4869.30 |  |  | 6061 |  |  |  | 900 | [10 empty] | 62.75 |  |  |  | 62.75 | [5 empty] | 61.76 |  |  | 69.19 |  |  |  | 15.79 |  | 11.77 | [8 empty] | 25.49 |  |  |  |  | 0.00
1982 |  |  |  | 5738.50 |  |  | 6956 |  |  |  | 900 | [10 empty] | 76.38 |  |  |  | 76.38 | [5 empty] | 72.79 |  |  | 79.41 |  |  |  | 7.50 |  | 6.20 | [8 empty] | 17.43 |  |  |  |  | 0.00
1983 |  |  |  | 5578.00 |  |  | 6649 |  |  |  | 900 | [10 empty] | 73.90 |  |  |  | 73.90 | [5 empty] | 70.75 |  |  | 75.90 |  |  |  | 6.20 |  | 4.88 | [8 empty] | 21.21 |  |  |  |  | 0.00
1984 |  |  |  | 5778.00 |  |  | 6884 |  |  |  | 900 | [10 empty] | 74.10 |  |  |  | 74.10 | [5 empty] | 73.09 |  |  | 78.37 |  |  |  | 8.03 |  | 6.47 | [8 empty] | 19.43 |  |  |  |  | 0.00
1985 |  |  |  | 6079.70 |  |  | 7314 |  |  |  | 900 | [10 empty] | 80.50 |  |  |  | 84.57 | [5 empty] | 77.11 |  |  | 83.49 |  |  |  | 5.26 |  | 4.69 | [8 empty] | 10.74 |  |  |  |  | 4.07
1986 |  |  |  | 5465.50 |  |  | 6493 |  |  |  | 900 | [10 empty] | 75.53 |  |  |  | 75.70 | [5 empty] | 69.32 |  |  | 74.12 |  |  |  | 9.49 |  | 7.94 | [8 empty] | 16.36 |  |  |  |  | 0.17
1987 |  |  |  | 5015.90 |  |  | 6044 |  |  |  | 900 | [10 empty] | 66.65 |  |  |  | 67.77 | [5 empty] | 63.62 |  |  | 69.00 |  |  |  | 19.07 |  | 15.97 | [8 empty] | 16.26 |  |  |  |  | 1.12
1988 |  |  |  | 5466.00 |  |  | 6465 |  |  |  | 900 | [10 empty] | 84.64 |  |  |  | 89.74 | [5 empty] | 69.14 |  |  | 73.60 |  |  |  | 10.26 |  | 10.26 | [8 empty] | 0.00 |  |  |  |  | 5.10
1989 |  |  |  | 4757.98 |  |  | 6185 |  |  |  | 900 | [10 empty] | 64.71 |  |  |  | 68.78 | [5 empty] | 60.35 |  |  | 70.61 |  |  |  | 17.71 |  | 14.80 | [8 empty] | 16.42 |  |  |  |  | 4.06
1990 |  |  |  | 5585.97 |  |  | 7156 |  |  |  | 880 | [10 empty] | 74.85 |  |  |  | 80.74 | [5 empty] | 72.46 |  |  | 81.69 |  |  |  | 3.54 |  | 2.97 | [8 empty] | 16.29 |  |  |  |  | 5.88
1991 |  |  |  | 3358.36 |  |  | 4258 |  |  |  | 880 | [10 empty] | 43.96 |  |  |  | 47.88 | [5 empty] | 43.57 |  |  | 48.61 |  |  |  | 18.91 |  | 11.16 | [8 empty] | 40.95 |  |  |  |  | 3.92
1992 |  |  |  | 4034.99 |  |  | 5003 |  |  |  | 880 | [10 empty] | 52.52 |  |  |  | 56.39 | [5 empty] | 52.20 |  |  | 56.96 |  |  |  | 15.49 |  | 10.33 | [8 empty] | 33.28 |  |  |  |  | 3.87
1993 |  |  |  | 4416.61 |  |  | 5329 |  |  |  | 880 | [10 empty] | 57.37 |  |  |  | 60.55 | [5 empty] | 57.29 |  |  | 60.83 |  |  |  | 4.76 |  | 3.03 | [8 empty] | 36.42 |  |  |  |  | 3.18
1994 |  |  |  | 4487.33 |  |  | 6311 |  |  |  | 880 | [10 empty] | 85.68 |  |  |  | 85.91 | [5 empty] | 58.21 |  |  | 72.04 |  |  |  | 1.40 |  | 1.22 | [8 empty] | 12.87 |  |  |  |  | 0.22
1995 |  |  |  | 5582.80 |  |  | 7060 |  |  |  | 880 | [10 empty] | 77.97 |  |  |  | 79.88 | [5 empty] | 72.42 |  |  | 80.59 |  |  |  | 8.08 |  | 7.02 | [8 empty] | 13.11 |  |  |  |  | 1.91
1996 |  |  |  | 5361.36 |  |  | 6844 |  |  |  | 880 | [10 empty] | 77.53 |  |  |  | 79.00 | [5 empty] | 69.36 |  |  | 77.91 |  |  |  | 4.57 |  | 3.78 | [8 empty] | 17.22 |  |  |  |  | 1.47
1997 |  |  |  | 5592.90 |  |  | 7302 |  |  |  | 880 | [10 empty] | 84.27 |  |  |  | 87.99 | [5 empty] | 72.55 |  |  | 83.36 |  |  |  | 1.27 |  | 1.13 | [8 empty] | 10.89 |  |  |  |  | 3.72
1998 |  |  |  | 5320.37 |  |  | 6844 |  |  |  | 880 | [10 empty] | 80.46 |  |  |  | 83.94 | [5 empty] | 69.02 |  |  | 78.13 |  |  |  | 4.52 |  | 3.97 | [8 empty] | 12.08 |  |  |  |  | 3.48
1999 |  |  |  | 6108.75 |  |  | 7679 |  |  |  | 880 | [10 empty] | 82.66 |  |  |  | 86.75 | [5 empty] | 79.24 |  |  | 87.66 |  |  |  | 1.02 |  | 0.89 | [8 empty] | 12.35 |  |  |  |  | 4.09
2000 |  |  |  | 5403.24 |  |  | 6889 |  |  |  | 880 | [10 empty] | 74.63 |  |  |  | 77.30 | [5 empty] | 69.90 |  |  | 78.43 |  |  |  | 11.53 |  | 10.08 | [8 empty] | 12.63 |  |  |  |  | 2.67
2001 |  |  |  | 4358.59 |  |  | 5604 |  |  |  | 880 | [10 empty] | 72.09 |  |  |  | 77.89 | [5 empty] | 56.54 |  |  | 63.97 |  |  |  | 0.26 |  | 0.20 | [8 empty] | 21.91 |  |  |  |  | 5.80
2002 |  |  |  | 6146.94 |  |  | 7925 |  |  |  | 880 | [10 empty] | 90.98 |  |  |  | 90.98 | [5 empty] | 79.74 |  |  | 90.47 |  |  |  | 3.60 |  | 3.40 | [8 empty] | 5.62 |  |  |  |  | 0.00
2003 |  |  |  | 5711.09 |  |  | 7220 |  |  |  | 880 | [10 empty] | 80.03 |  |  |  | 83.52 | [5 empty] | 74.09 |  |  | 82.42 |  |  |  | 6.30 |  | 5.62 | [8 empty] | 10.86 |  |  |  |  | 3.49
2004 |  |  |  | 5256.10 |  |  | 6438 |  |  |  | 880 | [10 empty] | 71.42 |  |  |  | 72.70 | [5 empty] | 68.00 |  |  | 73.29 |  |  |  | 14.46 |  | 12.29 | [8 empty] | 15.01 |  |  |  |  | 1.28
2005 |  |  |  | 7022.84 |  |  | 8573 |  |  |  | 880 | [10 empty] | 97.55 |  |  |  | 98.85 | [5 empty] | 91.09 |  |  | 97.85 |  |  |  | 1.13 |  | 1.13 | [8 empty] | 0.02 |  |  |  |  | 1.30
2006 |  |  |  | 6118.12 |  |  | 7765 |  |  |  | 880 | [10 empty] | 86.64 |  |  |  | 88.48 | [5 empty] | 79.37 |  |  | 88.64 |  |  |  | 3.43 |  | 3.33 | [8 empty] | 8.20 |  |  |  |  | 1.84
2007 |  |  |  | 5752.87 |  |  | 7051 |  |  |  | 880 | [10 empty] | 75.07 |  |  |  | 77.36 | [5 empty] | 74.63 |  |  | 80.49 |  |  |  | 4.33 |  | 7.74 | [8 empty] | 14.90 |  |  |  |  | 2.29
2008 |  |  |  | 6302.49 |  |  | 7822 |  |  |  | 880 | [10 empty] | 84.34 |  |  |  | 86.98 | [5 empty] | 81.53 |  |  | 89.05 |  |  |  | 4.17 |  | 4.08 | [8 empty] | 8.94 |  |  |  |  | 2.64
2009 |  |  |  | 6556.83 |  |  | 7935 |  |  |  | 880 | [10 empty] | 86.60 |  |  |  | 89.78 | [5 empty] | 85.06 |  |  | 90.58 |  |  |  | 1.13 |  | 1.02 | [8 empty] | 9.20 |  |  |  |  | 3.18
2010 |  |  |  | 5927.46 |  |  | 7457 |  |  |  | 880 | [10 empty] | 80.13 |  |  |  | 89.11 | [5 empty] | 76.89 |  |  | 85.13 |  |  |  | 2.82 |  | 4.35 | [8 empty] | 6.54 |  |  |  |  | 8.98
2011 |  |  |  | 3271.68 |  |  | 4079 |  |  |  | 880 | [10 empty] | 43.46 |  |  |  | 45.86 | [5 empty] | 42.44 |  |  | 46.56 |  |  |  | 2.41 |  | 22.04 | [8 empty] | 32.10 |  |  |  |  | 2.39
2012 |  |  |  | 7133.76 |  |  | 8569 |  |  |  | 880 | [10 empty] | 98.27 |  |  |  | 98.68 | [5 empty] | 92.29 |  |  | 97.55 |  |  |  | 1.31 |  | 1.31 | [8 empty] | 0.01 |  |  |  |  | 0.41
2013 |  |  |  | 5083.50 |  |  | 5997 |  |  |  | 880 | [10 empty] | 66.73 |  |  |  | 67.79 | [5 empty] | 65.94 |  |  | 68.46 |  |  |  | 18.44 |  | 22.38 | [8 empty] | 9.83 |  |  |  |  | 1.05
2014 |  |  |  | 5508.01 |  |  | 6492 |  |  |  | 880 | [10 empty] | 72.44 |  |  |  | 73.04 | [5 empty] | 71.45 |  |  | 74.11 |  |  |  | 3.11 |  | 2.74 | [8 empty] | 24.22 |  |  |  |  | 0.60
2015 |  |  |  | 4924.48 |  |  | 5693 |  |  |  | 880 | [10 empty] | 63.94 |  |  |  | 65.20 | [5 empty] | 63.88 |  |  | 64.99 |  |  |  | 1.07 |  | 14.91 | [8 empty] | 19.89 |  |  |  |  | 1.26
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 880 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 3282.27 |  |  | 3887 |  |  |  | 880 | [10 empty] | 42.74 |  |  |  | 43.19 | [5 empty] | 42.58 |  |  | 44.37 |  |  |  | 0.44 |  | 48.14 | [8 empty] | 8.67 |  |  |  |  | 0.45
2018 |  |  |  | 5098.42 |  |  | 5902 |  |  |  | 880 | [10 empty] | 65.87 |  |  |  | 66.62 | [5 empty] | 66.14 |  |  | 67.37 |  |  |  | 9.11 |  | 13.37 | [8 empty] | 20.02 |  |  |  |  | 0.75
2019 |  |  |  | 7323.23 |  |  | 8655 |  |  |  | 880 | [10 empty] | 97.31 |  |  |  | 99.34 | [5 empty] | 95.00 |  |  | 98.80 |  |  |  | 0.63 |  | 0.63 | [8 empty] | 0.04 |  |  |  |  | 2.03
2020 |  |  |  | 5887.45 |  |  | 6901 |  |  |  | 880 | [10 empty] | 76.20 |  |  |  | 83.59 | [5 empty] | 76.16 |  |  | 78.56 |  |  |  | 1.68 |  | 4.88 | [8 empty] | 11.53 |  |  |  |  | 7.39
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1980 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 390
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1169 |  |  |  | 9
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 22
E. |  | Testing of plant systems or components | [35 empty] | 8 |  |  |  | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 339
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 14 | [11 empty] | 0
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 6
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 8 | [11 empty] | 18
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 6
Z. |  | Other | [39 empty] | 41 | [11 empty] | 10
Subtotal | [37 empty] | 1199 |  |  |  | 803 | [11 empty] | 53
Total | [22 empty] | 0 | [14 empty] | 2055
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1980 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 18
12. |  |  | Reactor I&C Systems | [34 empty] | 46
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 21
16. |  |  | Steam generation systems | [34 empty] | 443
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 78
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 45
41. |  |  | Main Generator Systems | [34 empty] | 47
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [37 empty] | 735

## CATTENOM-1
2020 Operating Experience
FR-50 | [8 empty] | CATTENOM-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-10-29
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-11-13
Gross electrical power | [12 empty] | : |  |  | 1362 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-04-01
Reference unit power (net) | [12 empty] | : |  |  | 1300 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8894.78 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 6.33 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.48 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 6.33 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.64 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.03 %
Load Factor (LF) | [18 empty] | : | 77.89 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 8.16 %
Operating Factor (OF) | [18 empty] | : | 89.05 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 962 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 934.28 | 693.72 |  |  |  | 70.63 |  | 428.85 | [8 empty] | 711.04 |  |  | 799.64 | [6 empty] | 833.41 |  | 884.85 |  |  |  | 864.30 |  |  | 864.47 |  |  | 888.09 | [9 empty] | 921.50 |  |  | 8894.78
EAF [%] |  |  |  |  | 96.66 | 96.40 |  |  |  | 15.40 |  | 57.72 | [8 empty] | 82.25 |  |  | 95.70 | [6 empty] | 97.51 |  | 96.62 |  |  |  | 97.18 |  |  | 98.45 |  |  | 97.35 | [9 empty] | 95.32 |  |  | 85.48
UCF [%] |  |  |  |  | 97.02 | 96.74 |  |  |  | 59.05 |  | 81.39 | [8 empty] | 99.07 |  |  | 98.88 | [6 empty] | 99.34 |  | 99.23 |  |  |  | 98.87 |  |  | 99.24 |  |  | 98.77 | [9 empty] | 96.32 |  |  | 93.64
LF [%] |  |  |  |  | 96.60 | 76.67 |  |  |  | 7.31 |  | 45.82 | [8 empty] | 73.52 |  |  | 85.43 | [6 empty] | 86.17 |  | 91.49 |  |  |  | 92.34 |  |  | 89.26 |  |  | 94.88 | [9 empty] | 95.27 |  |  | 77.89
OF [%] |  |  |  |  | 99.73 | 100.00 |  |  |  | 15.48 |  | 71.25 | [8 empty] | 86.83 |  |  | 100.00 | [6 empty] | 96.51 |  | 100.00 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.05
FLR [%] |  |  |  |  | 2.96 | 3.26 |  |  |  | 40.95 |  | 18.61 | [8 empty] | 0.93 |  |  | 1.09 | [6 empty] | 0.60 |  | 0.77 |  |  |  | 0.97 |  |  | 0.76 |  |  | 1.20 | [9 empty] | 3.63 |  |  | 6.33
UCL [%] |  |  |  |  | 2.96 | 3.26 |  |  |  | 40.95 |  | 18.61 | [8 empty] | 0.93 |  |  | 1.09 | [6 empty] | 0.60 |  | 0.77 |  |  |  | 0.97 |  |  | 0.76 |  |  | 1.20 | [9 empty] | 3.63 |  |  | 6.33
PUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.03 | [6 empty] | 0.05 |  | 0.00 |  |  |  | 0.16 |  |  | 0.00 |  |  | 0.03 | [9 empty] | 0.05 |  |  | 0.03
XUF [%] |  |  |  |  | 0.36 | 0.34 |  |  |  | 43.65 |  | 23.66 | [8 empty] | 16.83 |  |  | 3.19 | [6 empty] | 1.83 |  | 2.61 |  |  |  | 1.69 |  |  | 0.79 |  |  | 1.43 | [9 empty] | 1.00 |  |  | 8.16
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 269615.3 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 11.99 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.32 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.88 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.09 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.03 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 69.7 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.78 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.41 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 7429.80 |  |  | 6393 |  |  |  | 1265 | [10 empty] | 68.80 |  |  |  | 69.47 | [5 empty] | 65.53 |  |  | 68.38 |  |  |  | 30.53 |  | 30.53 | [8 empty] | 0.00 |  |  |  |  | 0.67
1988 |  |  |  | 5283.00 |  |  | 4369 |  |  |  | 1300 | [10 empty] | 47.40 |  |  |  | 47.80 | [5 empty] | 46.26 |  |  | 49.74 |  |  |  | 32.01 |  | 22.51 | [8 empty] | 29.70 |  |  |  |  | 0.39
1989 |  |  |  | 6802.43 |  |  | 5548 |  |  |  | 1300 | [10 empty] | 60.28 |  |  |  | 60.28 | [5 empty] | 59.73 |  |  | 63.33 |  |  |  | 24.40 |  | 19.46 | [8 empty] | 20.26 |  |  |  |  | 0.00
1990 |  |  |  | 7781.88 |  |  | 6710 |  |  |  | 1300 | [10 empty] | 75.29 |  |  |  | 75.71 | [5 empty] | 68.33 |  |  | 76.60 |  |  |  | 11.10 |  | 9.46 | [8 empty] | 14.84 |  |  |  |  | 0.42
1991 |  |  |  | 1509.28 |  |  | 1336 |  |  |  | 1300 | [10 empty] | 13.48 |  |  |  | 13.48 | [5 empty] | 13.25 |  |  | 15.25 |  |  |  | 84.22 |  | 71.92 | [8 empty] | 14.61 |  |  |  |  | 0.00
1992 |  |  |  | 7933.30 |  |  | 6595 |  |  |  | 1300 | [10 empty] | 71.02 |  |  |  | 71.46 | [5 empty] | 69.47 |  |  | 75.08 |  |  |  | 12.28 |  | 10.00 | [8 empty] | 18.54 |  |  |  |  | 0.44
1993 |  |  |  | 6956.55 |  |  | 5608 |  |  |  | 1300 | [10 empty] | 61.46 |  |  |  | 63.47 | [5 empty] | 61.09 |  |  | 64.02 |  |  |  | 25.00 |  | 21.15 | [8 empty] | 15.37 |  |  |  |  | 2.01
1994 |  |  |  | 6775.45 |  |  | 6006 |  |  |  | 1300 | [10 empty] | 64.04 |  |  |  | 64.06 | [5 empty] | 59.50 |  |  | 68.56 |  |  |  | 35.14 |  | 34.71 | [8 empty] | 1.22 |  |  |  |  | 0.02
1995 |  |  |  | 6634.25 |  |  | 6346 |  |  |  | 1300 | [10 empty] | 59.54 |  |  |  | 59.84 | [5 empty] | 58.26 |  |  | 72.44 |  |  |  | 27.42 |  | 22.60 | [8 empty] | 17.55 |  |  |  |  | 0.30
1996 |  |  |  | 9539.24 |  |  | 7783 |  |  |  | 1300 | [10 empty] | 87.29 |  |  |  | 87.48 | [5 empty] | 83.54 |  |  | 88.60 |  |  |  | 0.58 |  | 0.51 | [8 empty] | 12.01 |  |  |  |  | 0.19
1997 |  |  |  | 8688.94 |  |  | 7374 |  |  |  | 1300 | [10 empty] | 81.38 |  |  |  | 84.07 | [5 empty] | 76.30 |  |  | 84.18 |  |  |  | 0.75 |  | 0.64 | [8 empty] | 15.29 |  |  |  |  | 2.69
1998 |  |  |  | 9365.85 |  |  | 7644 |  |  |  | 1300 | [10 empty] | 85.65 |  |  |  | 85.89 | [5 empty] | 82.24 |  |  | 87.26 |  |  |  | 5.54 |  | 5.04 | [8 empty] | 9.07 |  |  |  |  | 0.23
1999 |  |  |  | 8273.01 |  |  | 7028 |  |  |  | 1300 | [10 empty] | 76.29 |  |  |  | 79.76 | [5 empty] | 72.65 |  |  | 80.23 |  |  |  | 1.45 |  | 1.17 | [8 empty] | 19.07 |  |  |  |  | 3.46
2000 |  |  |  | 8053.79 |  |  | 6873 |  |  |  | 1300 | [10 empty] | 78.09 |  |  |  | 81.03 | [5 empty] | 70.53 |  |  | 78.24 |  |  |  | 0.87 |  | 0.71 | [8 empty] | 18.26 |  |  |  |  | 2.94
2001 |  |  |  | 9220.15 |  |  | 8094 |  |  |  | 1300 | [10 empty] | 96.42 |  |  |  | 96.44 | [5 empty] | 80.96 |  |  | 92.40 |  |  |  | 1.60 |  | 1.57 | [8 empty] | 1.99 |  |  |  |  | 0.02
2002 |  |  |  | 8270.16 |  |  | 7011 |  |  |  | 1300 | [10 empty] | 79.18 |  |  |  | 79.38 | [5 empty] | 72.62 |  |  | 80.03 |  |  |  | 8.52 |  | 7.39 | [8 empty] | 13.23 |  |  |  |  | 0.19
2003 |  |  |  | 8530.97 |  |  | 7150 |  |  |  | 1300 | [10 empty] | 78.44 |  |  |  | 80.35 | [5 empty] | 74.91 |  |  | 81.62 |  |  |  | 0.89 |  | 0.72 | [8 empty] | 18.92 |  |  |  |  | 1.91
2004 |  |  |  | 9764.16 |  |  | 8583 |  |  |  | 1300 | [10 empty] | 96.38 |  |  |  | 96.94 | [5 empty] | 85.51 |  |  | 97.71 |  |  |  | 1.94 |  | 1.91 | [8 empty] | 1.15 |  |  |  |  | 0.56
2005 |  |  |  | 9323.78 |  |  | 7919 |  |  |  | 1300 | [10 empty] | 83.23 |  |  |  | 89.12 | [5 empty] | 81.86 |  |  | 90.39 |  |  |  | 0.25 |  | 1.05 | [8 empty] | 9.83 |  |  |  |  | 5.89
2006 |  |  |  | 7448.99 |  |  | 6480 |  |  |  | 1300 | [10 empty] | 68.59 |  |  |  | 71.55 | [5 empty] | 65.41 |  |  | 73.97 |  |  |  | 2.32 |  | 2.45 | [8 empty] | 26.00 |  |  |  |  | 2.96
2007 |  |  |  | 9696.23 |  |  | 8426 |  |  |  | 1300 | [10 empty] | 92.42 |  |  |  | 93.96 | [5 empty] | 85.14 |  |  | 96.19 |  |  |  | 5.90 |  | 5.89 | [8 empty] | 0.15 |  |  |  |  | 1.54
2008 |  |  |  | 9022.88 |  |  | 7881 |  |  |  | 1300 | [10 empty] | 79.19 |  |  |  | 82.22 | [5 empty] | 79.02 |  |  | 89.72 |  |  |  | 7.91 |  | 8.73 | [8 empty] | 9.05 |  |  |  |  | 3.03
2009 |  |  |  | 7612.66 |  |  | 6261 |  |  |  | 1300 | [10 empty] | 68.35 |  |  |  | 73.14 | [5 empty] | 66.85 |  |  | 71.47 |  |  |  | 2.20 |  | 8.29 | [8 empty] | 18.56 |  |  |  |  | 4.79
2010 |  |  |  | 9864.05 |  |  | 7948 |  |  |  | 1300 | [10 empty] | 87.65 |  |  |  | 89.44 | [5 empty] | 86.62 |  |  | 90.73 |  |  |  | 1.81 |  | 3.20 | [8 empty] | 7.36 |  |  |  |  | 1.79
2011 |  |  |  | 10033.88 |  |  | 8538 |  |  |  | 1300 | [10 empty] | 96.69 |  |  |  | 98.22 | [5 empty] | 88.11 |  |  | 97.47 |  |  |  | 1.63 |  | 1.63 | [8 empty] | 0.15 |  |  |  |  | 1.54
2012 |  |  |  | 6818.80 |  |  | 5738 |  |  |  | 1300 | [10 empty] | 60.27 |  |  |  | 63.12 | [5 empty] | 59.71 |  |  | 65.32 |  |  |  | 4.83 |  | 19.50 | [8 empty] | 17.38 |  |  |  |  | 2.85
2013 |  |  |  | 6624.72 |  |  | 5440 |  |  |  | 1300 | [10 empty] | 59.23 |  |  |  | 59.70 | [5 empty] | 58.17 |  |  | 62.10 |  |  |  | 33.56 |  | 30.33 | [8 empty] | 9.97 |  |  |  |  | 0.47
2014 |  |  |  | 10106.20 |  |  | 8421 |  |  |  | 1300 | [10 empty] | 96.54 |  |  |  | 97.98 | [5 empty] | 88.74 |  |  | 96.13 |  |  |  | 1.97 |  | 1.97 | [8 empty] | 0.05 |  |  |  |  | 1.44
2015 |  |  |  | 7013.40 |  |  | 5683 |  |  |  | 1300 | [10 empty] | 61.96 |  |  |  | 64.19 | [5 empty] | 61.59 |  |  | 64.87 |  |  |  | 2.94 |  | 12.59 | [8 empty] | 23.22 |  |  |  |  | 2.23
2016 |  |  |  | 6428.77 |  |  | 5371 |  |  |  | 1300 | [10 empty] | 56.57 |  |  |  | 56.93 | [5 empty] | 56.30 |  |  | 61.15 |  |  |  | 1.84 |  | 5.10 | [8 empty] | 37.97 |  |  |  |  | 0.36
2017 |  |  |  | 9134.86 |  |  | 7393 |  |  |  | 1300 | [10 empty] | 82.49 |  |  |  | 83.34 | [5 empty] | 80.21 |  |  | 84.39 |  |  |  | 16.58 |  | 16.56 | [8 empty] | 0.10 |  |  |  |  | 0.85
2018 |  |  |  | 8198.29 |  |  | 6694 |  |  |  | 1300 | [10 empty] | 72.02 |  |  |  | 77.35 | [5 empty] | 71.99 |  |  | 76.42 |  |  |  | 9.64 |  | 11.24 | [8 empty] | 11.41 |  |  |  |  | 5.33
2019 |  |  |  | 6861.87 |  |  | 5497 |  |  |  | 1300 | [10 empty] | 60.39 |  |  |  | 60.74 | [5 empty] | 60.26 |  |  | 62.75 |  |  |  | 3.11 |  | 11.99 | [8 empty] | 27.26 |  |  |  |  | 0.35
2020 |  |  |  | 8894.78 |  |  | 7822 |  |  |  | 1300 | [10 empty] | 85.48 |  |  |  | 93.64 | [5 empty] | 77.89 |  |  | 89.05 |  |  |  | 6.33 |  | 6.33 | [8 empty] | 0.03 |  |  |  |  | 8.16
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 819
B. |  | Refuelling without maintenance | [35 empty] | 85
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 929 |  |  |  | 10
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 36 |  |  |  | 6
E. |  | Testing of plant systems or components | [35 empty] | 45
H. |  | Nuclear regulatory requirements | [39 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 10
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 0 | [11 empty] | 25
Z. |  | Other | [39 empty] | 46
Subtotal | [37 empty] | 1095 |  |  |  | 897 | [11 empty] | 31
Total | [22 empty] | 0 | [14 empty] | 2023
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 24
12. |  |  | Reactor I&C Systems | [34 empty] | 57
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 33
14. |  |  | Safety Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 60
16. |  |  | Steam generation systems | [34 empty] | 30
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 7
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 59
32. |  |  | Feedwater and Main Steam System | [34 empty] | 60
33. |  |  | Circulating Water System | [34 empty] | 18
34. |  |  | Miscellaneous Systems | [34 empty] | 92
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 253
42. |  |  | Electrical Power Supply Systems | [34 empty] | 99
Total | [37 empty] | 808

## CATTENOM-2
2020 Operating Experience
FR-53 | [8 empty] | CATTENOM-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-07-28
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-09-17
Gross electrical power | [12 empty] | : |  |  | 1362 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-02-01
Reference unit power (net) | [12 empty] | : |  |  | 1300 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5634.04 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.48 %
Energy Availability Factor (EAF) | [18 empty] | : | 49.54 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 18.56 %
Unit Capability Factor (UCF) | [18 empty] | : | 57.06 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 24.38 %
Load Factor (LF) | [18 empty] | : | 49.34 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 7.51 %
Operating Factor (OF) | [18 empty] | : | 53.49 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4085 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 942.32 | 838.38 |  |  |  | 808.90 |  | 47.07 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 233.72 |  |  | 934.59 |  |  | 911.13 | [9 empty] | 917.93 |  |  | 5634.04
EAF [%] |  |  |  |  | 97.53 | 92.66 |  |  |  | 83.75 |  | 5.03 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 24.99 |  |  | 96.81 |  |  | 97.83 | [9 empty] | 96.38 |  |  | 49.54
UCF [%] |  |  |  |  | 99.03 | 99.73 |  |  |  | 100.00 |  | 7.13 | [8 empty] | 0.00 |  |  | 10.00 | [6 empty] | 51.89 |  | 0.00 |  |  |  | 24.99 |  |  | 97.04 |  |  | 97.95 | [9 empty] | 96.82 |  |  | 57.06
LF [%] |  |  |  |  | 97.43 | 92.66 |  |  |  | 83.75 |  | 5.03 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 24.97 |  |  | 96.50 |  |  | 97.34 | [9 empty] | 94.91 |  |  | 49.34
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 7.22 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 35.56 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 53.49
FLR [%] |  |  |  |  | 0.97 | 0.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 5.56 |  |  | 2.46 |  |  | 1.95 | [9 empty] | 3.16 |  |  | 1.48
UCL [%] |  |  |  |  | 0.97 | 0.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 48.11 |  | 100.00 |  |  |  | 64.38 |  |  | 2.45 |  |  | 1.94 | [9 empty] | 3.16 |  |  | 18.56
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 92.87 | [8 empty] | 100.00 |  |  | 90.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 10.64 |  |  | 0.51 |  |  | 0.10 | [9 empty] | 0.02 |  |  | 24.38
XUF [%] |  |  |  |  | 1.50 | 7.07 |  |  |  | 16.25 |  | 2.10 | [8 empty] | 0.00 |  |  | 9.99 | [6 empty] | 51.88 |  | 0.00 |  |  |  | 0.00 |  |  | 0.23 |  |  | 0.13 | [9 empty] | 0.44 |  |  | 7.51
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 272578.94 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.8 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.96 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.52 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.33 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.19 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.37 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.93 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 8138.00 |  |  | 7156 |  |  |  | 1300 | [10 empty] | 90.80 |  |  |  | 91.04 | [5 empty] | 71.35 |  |  | 81.94 |  |  |  | 5.24 |  | 5.03 | [8 empty] | 3.93 |  |  |  |  | 0.24
1989 |  |  |  | 1765.48 |  |  | 1452 |  |  |  | 1300 | [10 empty] | 15.48 |  |  |  | 16.51 | [5 empty] | 15.50 |  |  | 16.58 |  |  |  | 77.27 |  | 56.12 | [8 empty] | 27.37 |  |  |  |  | 1.03
1990 |  |  |  | 8137.59 |  |  | 6670 |  |  |  | 1300 | [10 empty] | 82.70 |  |  |  | 82.98 | [5 empty] | 71.46 |  |  | 76.14 |  |  |  | 6.39 |  | 5.66 | [8 empty] | 11.36 |  |  |  |  | 0.27
1991 |  |  |  | 7543.13 |  |  | 6472 |  |  |  | 1300 | [10 empty] | 68.21 |  |  |  | 71.75 | [5 empty] | 66.24 |  |  | 73.88 |  |  |  | 11.68 |  | 9.49 | [8 empty] | 18.77 |  |  |  |  | 3.54
1992 |  |  |  | 8134.30 |  |  | 6752 |  |  |  | 1300 | [10 empty] | 72.38 |  |  |  | 75.63 | [5 empty] | 71.23 |  |  | 76.87 |  |  |  | 7.25 |  | 5.91 | [8 empty] | 18.46 |  |  |  |  | 3.26
1993 |  |  |  | 8626.96 |  |  | 6990 |  |  |  | 1300 | [10 empty] | 76.22 |  |  |  | 78.82 | [5 empty] | 75.75 |  |  | 79.79 |  |  |  | 6.36 |  | 5.36 | [8 empty] | 15.83 |  |  |  |  | 2.60
1994 |  |  |  | 8526.27 |  |  | 7158 |  |  |  | 1300 | [10 empty] | 77.69 |  |  |  | 80.49 | [5 empty] | 74.87 |  |  | 81.71 |  |  |  | 3.61 |  | 3.01 | [8 empty] | 16.50 |  |  |  |  | 2.80
1995 |  |  |  | 8603.72 |  |  | 7138 |  |  |  | 1300 | [10 empty] | 78.31 |  |  |  | 79.93 | [5 empty] | 75.55 |  |  | 81.48 |  |  |  | 7.42 |  | 6.40 | [8 empty] | 13.67 |  |  |  |  | 1.62
1996 |  |  |  | 9018.10 |  |  | 7804 |  |  |  | 1300 | [10 empty] | 98.09 |  |  |  | 99.57 | [5 empty] | 78.97 |  |  | 88.84 |  |  |  | 0.38 |  | 0.38 | [8 empty] | 0.04 |  |  |  |  | 1.49
1997 |  |  |  | 8487.38 |  |  | 7503 |  |  |  | 1300 | [10 empty] | 82.21 |  |  |  | 84.39 | [5 empty] | 74.53 |  |  | 85.65 |  |  |  | 4.23 |  | 3.73 | [8 empty] | 11.88 |  |  |  |  | 2.19
1998 |  |  |  | 7259.47 |  |  | 6144 |  |  |  | 1300 | [10 empty] | 67.96 |  |  |  | 68.96 | [5 empty] | 63.75 |  |  | 70.14 |  |  |  | 7.64 |  | 5.71 | [8 empty] | 25.34 |  |  |  |  | 1.00
1999 |  |  |  | 9367.49 |  |  | 7781 |  |  |  | 1300 | [10 empty] | 87.28 |  |  |  | 90.19 | [5 empty] | 82.26 |  |  | 88.82 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 9.61 |  |  |  |  | 2.91
2000 |  |  |  | 9164.30 |  |  | 7868 |  |  |  | 1300 | [10 empty] | 88.57 |  |  |  | 88.61 | [5 empty] | 80.25 |  |  | 89.57 |  |  |  | 7.45 |  | 7.14 | [8 empty] | 4.25 |  |  |  |  | 0.05
2001 |  |  |  | 8649.04 |  |  | 7033 |  |  |  | 1300 | [10 empty] | 77.53 |  |  |  | 79.41 | [5 empty] | 75.95 |  |  | 80.29 |  |  |  | 2.80 |  | 2.28 | [8 empty] | 18.30 |  |  |  |  | 1.88
2002 |  |  |  | 8288.00 |  |  | 6918 |  |  |  | 1300 | [10 empty] | 76.87 |  |  |  | 76.92 | [5 empty] | 72.78 |  |  | 78.97 |  |  |  | 8.18 |  | 6.85 | [8 empty] | 16.23 |  |  |  |  | 0.05
2003 |  |  |  | 10197.46 |  |  | 8217 |  |  |  | 1300 | [10 empty] | 93.45 |  |  |  | 99.30 | [5 empty] | 89.55 |  |  | 93.80 |  |  |  | 0.63 |  | 0.63 | [8 empty] | 0.07 |  |  |  |  | 5.84
2004 |  |  |  | 7368.16 |  |  | 6183 |  |  |  | 1300 | [10 empty] | 66.80 |  |  |  | 68.70 | [5 empty] | 64.52 |  |  | 70.39 |  |  |  | 18.24 |  | 15.33 | [8 empty] | 15.97 |  |  |  |  | 1.90
2005 |  |  |  | 9247.81 |  |  | 7845 |  |  |  | 1300 | [10 empty] | 84.65 |  |  |  | 87.87 | [5 empty] | 81.21 |  |  | 89.55 |  |  |  | 1.12 |  | 2.04 | [8 empty] | 10.09 |  |  |  |  | 3.22
2006 |  |  |  | 9870.28 |  |  | 8626 |  |  |  | 1300 | [10 empty] | 96.14 |  |  |  | 97.96 | [5 empty] | 86.67 |  |  | 98.47 |  |  |  | 1.97 |  | 1.97 | [8 empty] | 0.07 |  |  |  |  | 1.82
2007 |  |  |  | 9526.50 |  |  | 7758 |  |  |  | 1300 | [10 empty] | 85.72 |  |  |  | 87.82 | [5 empty] | 83.65 |  |  | 88.56 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 12.11 |  |  |  |  | 2.10
2008 |  |  |  | 7707.77 |  |  | 6356 |  |  |  | 1300 | [10 empty] | 69.45 |  |  |  | 71.67 | [5 empty] | 67.50 |  |  | 72.36 |  |  |  | 0.45 |  | 3.47 | [8 empty] | 24.86 |  |  |  |  | 2.22
2009 |  |  |  | 9460.92 |  |  | 7845 |  |  |  | 1300 | [10 empty] | 85.12 |  |  |  | 88.12 | [5 empty] | 83.08 |  |  | 89.55 |  |  |  | 1.47 |  | 2.88 | [8 empty] | 9.00 |  |  |  |  | 3.00
2010 |  |  |  | 8866.22 |  |  | 8001 |  |  |  | 1300 | [10 empty] | 89.41 |  |  |  | 94.65 | [5 empty] | 77.86 |  |  | 91.34 |  |  |  | 5.32 |  | 5.32 | [8 empty] | 0.03 |  |  |  |  | 5.24
2011 |  |  |  | 7188.84 |  |  | 5995 |  |  |  | 1300 | [10 empty] | 64.26 |  |  |  | 66.64 | [5 empty] | 63.13 |  |  | 68.44 |  |  |  | 2.91 |  | 12.06 | [8 empty] | 21.30 |  |  |  |  | 2.38
2012 |  |  |  | 7149.60 |  |  | 5981 |  |  |  | 1300 | [10 empty] | 65.49 |  |  |  | 69.16 | [5 empty] | 62.61 |  |  | 68.09 |  |  |  | 10.21 |  | 23.70 | [8 empty] | 7.14 |  |  |  |  | 3.67
2013 |  |  |  | 9766.15 |  |  | 7830 |  |  |  | 1300 | [10 empty] | 86.59 |  |  |  | 87.79 | [5 empty] | 85.76 |  |  | 89.38 |  |  |  | 2.78 |  | 9.93 | [8 empty] | 2.28 |  |  |  |  | 1.20
2014 |  |  |  | 7475.58 |  |  | 6535 |  |  |  | 1300 | [10 empty] | 72.92 |  |  |  | 73.61 | [5 empty] | 65.64 |  |  | 74.60 |  |  |  | 6.20 |  | 4.86 | [8 empty] | 21.52 |  |  |  |  | 0.69
2015 |  |  |  | 9474.83 |  |  | 7870 |  |  |  | 1300 | [10 empty] | 86.81 |  |  |  | 89.49 | [5 empty] | 83.20 |  |  | 89.84 |  |  |  | 1.18 |  | 1.07 | [8 empty] | 9.44 |  |  |  |  | 2.68
2016 |  |  |  | 10129.04 |  |  | 8664 |  |  |  | 1300 | [10 empty] | 94.52 |  |  |  | 97.10 | [5 empty] | 88.70 |  |  | 98.63 |  |  |  | 2.87 |  | 2.86 | [8 empty] | 0.04 |  |  |  |  | 2.58
2017 |  |  |  | 7853.19 |  |  | 6649 |  |  |  | 1300 | [10 empty] | 72.48 |  |  |  | 75.10 | [5 empty] | 68.96 |  |  | 75.90 |  |  |  | 1.23 |  | 0.93 | [8 empty] | 23.96 |  |  |  |  | 2.62
2018 |  |  |  | 5487.63 |  |  | 4386 |  |  |  | 1300 | [10 empty] | 48.54 |  |  |  | 49.10 | [5 empty] | 48.19 |  |  | 50.07 |  |  |  | 18.90 |  | 11.44 | [8 empty] | 39.45 |  |  |  |  | 0.56
2019 |  |  |  | 9366.77 |  |  | 8046 |  |  |  | 1300 | [10 empty] | 88.69 |  |  |  | 92.57 | [5 empty] | 82.25 |  |  | 91.85 |  |  |  | 7.39 |  | 7.39 | [8 empty] | 0.04 |  |  |  |  | 3.88
2020 |  |  |  | 5634.04 |  |  | 4699 |  |  |  | 1300 | [10 empty] | 49.54 |  |  |  | 57.06 | [5 empty] | 49.34 |  |  | 53.49 |  |  |  | 1.48 |  | 18.56 | [8 empty] | 24.38 |  |  |  |  | 7.51
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 466
B. |  | Refuelling without maintenance | [35 empty] | 65
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 929 |  |  |  | 5
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 41 |  |  |  | 14
E. |  | Testing of plant systems or components | [35 empty] | 37 |  |  |  | 0 | [11 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 23
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 14
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 20
Z. |  | Other | [39 empty] | 26 | [11 empty] | 20
Subtotal | [37 empty] | 1072 |  |  |  | 534 | [11 empty] | 58
Total | [22 empty] | 0 | [14 empty] | 1664
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 8
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 53
15. |  |  | Reactor Cooling Systems | [34 empty] | 124
16. |  |  | Steam generation systems | [34 empty] | 59
31. |  |  | Turbine and auxiliaries | [34 empty] | 13
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 104
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 54
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [37 empty] | 463

## CATTENOM-3
2020 Operating Experience
FR-60 | [8 empty] | CATTENOM-3 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-06-15
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-07-06
Gross electrical power | [12 empty] | : |  |  | 1362 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1991-02-01
Reference unit power (net) | [12 empty] | : |  |  | 1300 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9190.97 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 7.95 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.57 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.76 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.88 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.35 %
Load Factor (LF) | [18 empty] | : | 80.49 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.31 %
Operating Factor (OF) | [18 empty] | : | 87.8 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1072 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 911.55 | 718.33 |  |  |  | 141.62 |  | 597.13 | [8 empty] | 735.35 |  |  | 837.28 | [6 empty] | 896.00 |  | 823.92 |  |  |  | 836.33 |  |  | 921.30 |  |  | 899.18 | [9 empty] | 872.97 |  |  | 9190.97
EAF [%] |  |  |  |  | 98.10 | 93.38 |  |  |  | 29.54 |  | 72.19 | [8 empty] | 86.67 |  |  | 92.11 | [6 empty] | 97.84 |  | 86.61 |  |  |  | 92.78 |  |  | 98.67 |  |  | 99.32 | [9 empty] | 92.34 |  |  | 86.57
UCF [%] |  |  |  |  | 99.96 | 98.63 |  |  |  | 36.02 |  | 83.11 | [8 empty] | 87.35 |  |  | 98.59 | [6 empty] | 99.68 |  | 89.68 |  |  |  | 94.59 |  |  | 99.72 |  |  | 99.71 | [9 empty] | 92.58 |  |  | 89.88
LF [%] |  |  |  |  | 94.25 | 79.39 |  |  |  | 14.66 |  | 63.80 | [8 empty] | 76.03 |  |  | 89.45 | [6 empty] | 92.64 |  | 85.19 |  |  |  | 89.35 |  |  | 95.13 |  |  | 96.07 | [9 empty] | 90.26 |  |  | 80.49
OF [%] |  |  |  |  | 100.00 | 99.43 |  |  |  | 16.82 |  | 74.17 | [8 empty] | 89.38 |  |  | 96.11 | [6 empty] | 100.00 |  | 90.32 |  |  |  | 95.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 93.55 |  |  | 87.80
FLR [%] |  |  |  |  | 0.00 | 0.02 |  |  |  | 63.98 |  | 1.57 | [8 empty] | 2.08 |  |  | 1.30 | [6 empty] | 0.20 |  | 10.20 |  |  |  | 5.35 |  |  | 0.19 |  |  | 0.26 | [9 empty] | 7.35 |  |  | 7.95
UCL [%] |  |  |  |  | 0.00 | 0.02 |  |  |  | 63.98 |  | 1.33 | [8 empty] | 1.85 |  |  | 1.30 | [6 empty] | 0.20 |  | 10.19 |  |  |  | 5.35 |  |  | 0.19 |  |  | 0.26 | [9 empty] | 7.34 |  |  | 7.76
PUF [%] |  |  |  |  | 0.03 | 1.35 |  |  |  | 0.00 |  | 15.56 | [8 empty] | 10.80 |  |  | 0.11 | [6 empty] | 0.12 |  | 0.13 |  |  |  | 0.06 |  |  | 0.09 |  |  | 0.03 | [9 empty] | 0.08 |  |  | 2.35
XUF [%] |  |  |  |  | 1.87 | 5.25 |  |  |  | 6.47 |  | 10.93 | [8 empty] | 0.67 |  |  | 6.48 | [6 empty] | 1.84 |  | 3.07 |  |  |  | 1.81 |  |  | 1.04 |  |  | 0.39 | [9 empty] | 0.23 |  |  | 3.31
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 257389.34 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.6 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.21 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.75 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.87 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.9 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.17 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.21 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1991 |  |  |  | 9683.15 |  |  | 7897 |  |  |  | 1300 | [10 empty] | 88.20 |  |  |  | 89.61 | [5 empty] | 85.70 |  |  | 90.51 |  |  |  | 10.29 |  | 10.27 | [8 empty] | 0.12 |  |  |  |  | 1.41
1992 |  |  |  | 7145.04 |  |  | 5903 |  |  |  | 1300 | [10 empty] | 65.61 |  |  |  | 67.00 | [5 empty] | 62.57 |  |  | 67.20 |  |  |  | 3.95 |  | 2.76 | [8 empty] | 30.24 |  |  |  |  | 1.40
1993 |  |  |  | 8035.13 |  |  | 6858 |  |  |  | 1300 | [10 empty] | 75.86 |  |  |  | 81.16 | [5 empty] | 70.56 |  |  | 78.29 |  |  |  | 1.87 |  | 1.55 | [8 empty] | 17.30 |  |  |  |  | 5.29
1994 |  |  |  | 8613.33 |  |  | 7464 |  |  |  | 1300 | [10 empty] | 84.36 |  |  |  | 85.71 | [5 empty] | 75.64 |  |  | 85.21 |  |  |  | 1.30 |  | 1.13 | [8 empty] | 13.16 |  |  |  |  | 1.35
1995 |  |  |  | 8344.31 |  |  | 7269 |  |  |  | 1300 | [10 empty] | 78.93 |  |  |  | 82.24 | [5 empty] | 73.27 |  |  | 82.98 |  |  |  | 5.14 |  | 4.46 | [8 empty] | 13.30 |  |  |  |  | 3.31
1996 |  |  |  | 8264.73 |  |  | 7184 |  |  |  | 1300 | [10 empty] | 77.27 |  |  |  | 80.56 | [5 empty] | 72.38 |  |  | 81.79 |  |  |  | 3.75 |  | 3.14 | [8 empty] | 16.29 |  |  |  |  | 3.29
1997 |  |  |  | 9504.06 |  |  | 8097 |  |  |  | 1300 | [10 empty] | 93.25 |  |  |  | 94.46 | [5 empty] | 83.46 |  |  | 92.43 |  |  |  | 1.79 |  | 1.72 | [8 empty] | 3.82 |  |  |  |  | 1.22
1998 |  |  |  | 8054.93 |  |  | 7175 |  |  |  | 1300 | [10 empty] | 80.15 |  |  |  | 83.51 | [5 empty] | 70.73 |  |  | 81.91 |  |  |  | 2.52 |  | 2.16 | [8 empty] | 14.33 |  |  |  |  | 3.36
1999 |  |  |  | 8237.00 |  |  | 7169 |  |  |  | 1300 | [10 empty] | 79.73 |  |  |  | 83.51 | [5 empty] | 72.33 |  |  | 81.84 |  |  |  | 1.57 |  | 1.34 | [8 empty] | 15.15 |  |  |  |  | 3.78
2000 |  |  |  | 8933.53 |  |  | 7984 |  |  |  | 1300 | [10 empty] | 98.71 |  |  |  | 99.15 | [5 empty] | 78.23 |  |  | 90.89 |  |  |  | 0.57 |  | 0.57 | [8 empty] | 0.29 |  |  |  |  | 0.43
2001 |  |  |  | 3171.47 |  |  | 2739 |  |  |  | 1300 | [10 empty] | 29.74 |  |  |  | 29.81 | [5 empty] | 27.85 |  |  | 31.27 |  |  |  | 58.95 |  | 42.80 | [8 empty] | 27.39 |  |  |  |  | 0.07
2002 |  |  |  | 9402.46 |  |  | 7443 |  |  |  | 1300 | [10 empty] | 82.50 |  |  |  | 83.63 | [5 empty] | 82.56 |  |  | 84.97 |  |  |  | 3.03 |  | 2.62 | [8 empty] | 13.75 |  |  |  |  | 1.13
2003 |  |  |  | 11254.01 |  |  | 8715 |  |  |  | 1300 | [10 empty] | 98.37 |  |  |  | 99.34 | [5 empty] | 98.82 |  |  | 99.49 |  |  |  | 0.18 |  | 0.18 | [8 empty] | 0.47 |  |  |  |  | 0.97
2004 |  |  |  | 9162.73 |  |  | 7274 |  |  |  | 1300 | [10 empty] | 80.35 |  |  |  | 81.37 | [5 empty] | 80.24 |  |  | 82.81 |  |  |  | 3.34 |  | 2.81 | [8 empty] | 15.82 |  |  |  |  | 1.02
2005 |  |  |  | 9757.05 |  |  | 7944 |  |  |  | 1300 | [10 empty] | 86.70 |  |  |  | 89.23 | [5 empty] | 85.67 |  |  | 90.67 |  |  |  | 0.52 |  | 0.47 | [8 empty] | 10.30 |  |  |  |  | 2.53
2006 |  |  |  | 8045.34 |  |  | 7088 |  |  |  | 1300 | [10 empty] | 76.49 |  |  |  | 79.94 | [5 empty] | 70.65 |  |  | 80.91 |  |  |  | 1.63 |  | 5.67 | [8 empty] | 14.39 |  |  |  |  | 3.45
2007 |  |  |  | 9500.56 |  |  | 8559 |  |  |  | 1300 | [10 empty] | 98.46 |  |  |  | 99.27 | [5 empty] | 83.43 |  |  | 97.71 |  |  |  | 0.65 |  | 0.65 | [8 empty] | 0.07 |  |  |  |  | 0.81
2008 |  |  |  | 8712.70 |  |  | 7145 |  |  |  | 1300 | [10 empty] | 78.40 |  |  |  | 80.48 | [5 empty] | 76.30 |  |  | 81.34 |  |  |  | 1.04 |  | 11.62 | [8 empty] | 7.90 |  |  |  |  | 2.08
2009 |  |  |  | 6649.76 |  |  | 5277 |  |  |  | 1300 | [10 empty] | 58.66 |  |  |  | 60.45 | [5 empty] | 58.39 |  |  | 60.24 |  |  |  | 20.99 |  | 21.49 | [8 empty] | 18.06 |  |  |  |  | 1.79
2010 |  |  |  | 8756.81 |  |  | 6966 |  |  |  | 1300 | [10 empty] | 81.71 |  |  |  | 82.99 | [5 empty] | 76.90 |  |  | 79.52 |  |  |  | 17.00 |  | 16.99 | [8 empty] | 0.01 |  |  |  |  | 1.28
2011 |  |  |  | 7918.57 |  |  | 6306 |  |  |  | 1300 | [10 empty] | 69.59 |  |  |  | 70.83 | [5 empty] | 69.53 |  |  | 71.99 |  |  |  | 2.78 |  | 3.73 | [8 empty] | 25.44 |  |  |  |  | 1.24
2012 |  |  |  | 8337.71 |  |  | 6760 |  |  |  | 1300 | [10 empty] | 74.49 |  |  |  | 75.86 | [5 empty] | 73.01 |  |  | 76.96 |  |  |  | 1.63 |  | 16.80 | [8 empty] | 7.34 |  |  |  |  | 1.36
2013 |  |  |  | 7844.56 |  |  | 6552 |  |  |  | 1300 | [10 empty] | 72.57 |  |  |  | 74.29 | [5 empty] | 68.88 |  |  | 74.79 |  |  |  | 1.69 |  | 11.91 | [8 empty] | 13.80 |  |  |  |  | 1.72
2014 |  |  |  | 9671.58 |  |  | 8049 |  |  |  | 1300 | [10 empty] | 92.06 |  |  |  | 92.80 | [5 empty] | 84.93 |  |  | 91.88 |  |  |  | 3.56 |  | 6.74 | [8 empty] | 0.46 |  |  |  |  | 0.74
2015 |  |  |  | 9456.96 |  |  | 7813 |  |  |  | 1300 | [10 empty] | 84.04 |  |  |  | 85.30 | [5 empty] | 83.04 |  |  | 89.19 |  |  |  | 4.80 |  | 4.30 | [8 empty] | 10.41 |  |  |  |  | 1.26
2016 |  |  |  | 8053.88 |  |  | 6821 |  |  |  | 1300 | [10 empty] | 71.20 |  |  |  | 74.31 | [5 empty] | 70.53 |  |  | 77.65 |  |  |  | 1.43 |  | 1.08 | [8 empty] | 24.62 |  |  |  |  | 3.11
2017 |  |  |  | 10396.60 |  |  | 8390 |  |  |  | 1300 | [10 empty] | 92.19 |  |  |  | 97.96 | [5 empty] | 91.29 |  |  | 95.78 |  |  |  | 1.97 |  | 1.97 | [8 empty] | 0.07 |  |  |  |  | 5.78
2018 |  |  |  | 8531.74 |  |  | 7038 |  |  |  | 1300 | [10 empty] | 75.07 |  |  |  | 79.59 | [5 empty] | 74.92 |  |  | 80.34 |  |  |  | 9.36 |  | 9.07 | [8 empty] | 11.34 |  |  |  |  | 4.52
2019 |  |  |  | 7460.81 |  |  | 6029 |  |  |  | 1300 | [10 empty] | 65.97 |  |  |  | 67.85 | [5 empty] | 65.51 |  |  | 68.82 |  |  |  | 0.31 |  | 5.06 | [8 empty] | 27.09 |  |  |  |  | 1.88
2020 |  |  |  | 9190.97 |  |  | 7712 |  |  |  | 1300 | [10 empty] | 86.57 |  |  |  | 89.88 | [5 empty] | 80.49 |  |  | 87.80 |  |  |  | 7.95 |  | 7.76 | [8 empty] | 2.35 |  |  |  |  | 3.31
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1991 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 416
B. |  | Refuelling without maintenance | [35 empty] | 51
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 905 |  |  |  | 13
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 48
E. |  | Testing of plant systems or components | [35 empty] | 11
H. |  | Nuclear regulatory requirements | [39 empty] | 77
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 13
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 15
L. |  | Human factor related | [39 empty] | 6
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 1 | [11 empty] | 12
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 8
Z. |  | Other | [39 empty] | 26
Subtotal | [37 empty] | 1015 |  |  |  | 539 | [11 empty] | 48
Total | [22 empty] | 0 | [14 empty] | 1602
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1991 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 76
12. |  |  | Reactor I&C Systems | [34 empty] | 29
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 37
14. |  |  | Safety Systems | [34 empty] | 27
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 26
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [34 empty] | 22
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
34. |  |  | Miscellaneous Systems | [34 empty] | 76
41. |  |  | Main Generator Systems | [34 empty] | 80
42. |  |  | Electrical Power Supply Systems | [34 empty] | 10
Total | [37 empty] | 410

## CATTENOM-4
2020 Operating Experience
FR-65 | [8 empty] | CATTENOM-4 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1983-09-28
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1991-05-27
Gross electrical power | [12 empty] | : |  |  | 1362 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1992-01-01
Reference unit power (net) | [12 empty] | : |  |  | 1300 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 29 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7676.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 11.22 %
Energy Availability Factor (EAF) | [18 empty] | : | 70.71 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 11.7 %
Unit Capability Factor (UCF) | [18 empty] | : | 75.67 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.63 %
Load Factor (LF) | [18 empty] | : | 67.23 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 4.96 %
Operating Factor (OF) | [18 empty] | : | 76.2 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2091 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 757.81 | 405.43 |  |  |  | 838.32 |  | 854.53 | [8 empty] | 523.91 |  |  | 861.01 | [6 empty] | 858.27 |  | 832.08 |  |  |  | 73.26 |  |  | 114.72 |  |  | 849.86 | [9 empty] | 707.48 |  |  | 7676.68
EAF [%] |  |  |  |  | 91.90 | 56.29 |  |  |  | 99.79 |  | 93.72 | [8 empty] | 59.62 |  |  | 92.30 | [6 empty] | 88.78 |  | 86.03 |  |  |  | 7.83 |  |  | 11.85 |  |  | 86.39 | [9 empty] | 73.12 |  |  | 70.71
UCF [%] |  |  |  |  | 99.88 | 83.76 |  |  |  | 99.83 |  | 94.42 | [8 empty] | 60.18 |  |  | 96.92 | [6 empty] | 90.90 |  | 94.33 |  |  |  | 9.66 |  |  | 11.85 |  |  | 93.54 | [9 empty] | 73.21 |  |  | 75.67
LF [%] |  |  |  |  | 78.35 | 44.81 |  |  |  | 86.79 |  | 91.30 | [8 empty] | 54.17 |  |  | 91.99 | [6 empty] | 88.74 |  | 86.03 |  |  |  | 7.83 |  |  | 11.84 |  |  | 90.80 | [9 empty] | 73.15 |  |  | 67.23
OF [%] |  |  |  |  | 100.00 | 54.60 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 66.26 |  |  | 94.72 | [6 empty] | 94.49 |  | 100.00 |  |  |  | 13.19 |  |  | 20.00 |  |  | 94.44 | [9 empty] | 75.27 |  |  | 76.20
FLR [%] |  |  |  |  | 0.11 | 16.21 |  |  |  | 0.13 |  | 5.54 | [8 empty] | 39.76 |  |  | 3.04 | [6 empty] | 8.79 |  | 5.64 |  |  |  | 24.95 |  |  | 0.00 |  |  | 5.42 | [9 empty] | 26.75 |  |  | 11.22
UCL [%] |  |  |  |  | 0.11 | 16.20 |  |  |  | 0.13 |  | 5.54 | [8 empty] | 39.72 |  |  | 3.04 | [6 empty] | 8.76 |  | 5.64 |  |  |  | 3.21 |  |  | 25.24 |  |  | 5.36 | [9 empty] | 26.73 |  |  | 11.70
PUF [%] |  |  |  |  | 0.01 | 0.04 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.10 |  |  | 0.04 | [6 empty] | 0.34 |  | 0.03 |  |  |  | 87.13 |  |  | 62.90 |  |  | 1.09 | [9 empty] | 0.06 |  |  | 12.63
XUF [%] |  |  |  |  | 7.98 | 27.47 |  |  |  | 0.03 |  | 0.69 | [8 empty] | 0.56 |  |  | 4.62 | [6 empty] | 2.12 |  | 8.30 |  |  |  | 1.82 |  |  | 0.00 |  |  | 7.16 | [9 empty] | 0.08 |  |  | 4.96
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 254334.28 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.47 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.31 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.28 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.81 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.91 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.33 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.5 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.37 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1992 |  |  |  | 9355.95 |  |  | 7649 |  |  |  | 1300 | [10 empty] | 85.83 |  |  |  | 88.01 | [5 empty] | 81.93 |  |  | 87.08 |  |  |  | 0.88 |  | 0.78 | [8 empty] | 11.21 |  |  |  |  | 2.18
1993 |  |  |  | 7736.44 |  |  | 6251 |  |  |  | 1300 | [10 empty] | 77.98 |  |  |  | 79.09 | [5 empty] | 67.94 |  |  | 71.36 |  |  |  | 6.27 |  | 5.29 | [8 empty] | 15.62 |  |  |  |  | 1.11
1994 |  |  |  | 7828.78 |  |  | 6866 |  |  |  | 1300 | [10 empty] | 80.42 |  |  |  | 81.90 | [5 empty] | 68.75 |  |  | 78.38 |  |  |  | 2.35 |  | 1.97 | [8 empty] | 16.13 |  |  |  |  | 1.48
1995 |  |  |  | 8942.43 |  |  | 7563 |  |  |  | 1300 | [10 empty] | 82.80 |  |  |  | 85.53 | [5 empty] | 78.53 |  |  | 86.34 |  |  |  | 3.24 |  | 2.87 | [8 empty] | 11.60 |  |  |  |  | 2.73
1996 |  |  |  | 8897.57 |  |  | 7399 |  |  |  | 1300 | [10 empty] | 81.35 |  |  |  | 82.59 | [5 empty] | 77.92 |  |  | 84.23 |  |  |  | 5.41 |  | 4.73 | [8 empty] | 12.69 |  |  |  |  | 1.24
1997 |  |  |  | 8690.54 |  |  | 7382 |  |  |  | 1300 | [10 empty] | 79.28 |  |  |  | 82.61 | [5 empty] | 76.31 |  |  | 84.27 |  |  |  | 1.84 |  | 1.55 | [8 empty] | 15.84 |  |  |  |  | 3.33
1998 |  |  |  | 10000.14 |  |  | 8476 |  |  |  | 1300 | [10 empty] | 94.49 |  |  |  | 96.06 | [5 empty] | 87.81 |  |  | 96.76 |  |  |  | 2.40 |  | 2.37 | [8 empty] | 1.58 |  |  |  |  | 1.56
1999 |  |  |  | 8131.93 |  |  | 7164 |  |  |  | 1300 | [10 empty] | 80.77 |  |  |  | 82.85 | [5 empty] | 71.41 |  |  | 81.78 |  |  |  | 5.31 |  | 4.65 | [8 empty] | 12.50 |  |  |  |  | 2.08
2000 |  |  |  | 9139.01 |  |  | 7692 |  |  |  | 1300 | [10 empty] | 85.08 |  |  |  | 86.59 | [5 empty] | 80.03 |  |  | 87.57 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 13.25 |  |  |  |  | 1.51
2001 |  |  |  | 8593.18 |  |  | 7375 |  |  |  | 1300 | [10 empty] | 84.84 |  |  |  | 86.55 | [5 empty] | 75.46 |  |  | 84.19 |  |  |  | 0.30 |  | 0.26 | [8 empty] | 13.19 |  |  |  |  | 1.71
2002 |  |  |  | 10598.80 |  |  | 8467 |  |  |  | 1300 | [10 empty] | 95.10 |  |  |  | 95.29 | [5 empty] | 93.07 |  |  | 96.66 |  |  |  | 0.33 |  | 0.31 | [8 empty] | 4.40 |  |  |  |  | 0.19
2003 |  |  |  | 7708.34 |  |  | 6406 |  |  |  | 1300 | [10 empty] | 69.75 |  |  |  | 72.09 | [5 empty] | 67.69 |  |  | 73.13 |  |  |  | 1.34 |  | 0.98 | [8 empty] | 26.93 |  |  |  |  | 2.34
2004 |  |  |  | 9311.78 |  |  | 7560 |  |  |  | 1300 | [10 empty] | 84.51 |  |  |  | 85.02 | [5 empty] | 81.54 |  |  | 86.07 |  |  |  | 1.40 |  | 1.21 | [8 empty] | 13.77 |  |  |  |  | 0.51
2005 |  |  |  | 9913.85 |  |  | 8520 |  |  |  | 1300 | [10 empty] | 97.83 |  |  |  | 98.32 | [5 empty] | 87.06 |  |  | 97.26 |  |  |  | 1.66 |  | 1.66 | [8 empty] | 0.02 |  |  |  |  | 0.49
2006 |  |  |  | 8719.60 |  |  | 7440 |  |  |  | 1300 | [10 empty] | 80.57 |  |  |  | 83.51 | [5 empty] | 76.57 |  |  | 84.93 |  |  |  | 0.60 |  | 7.05 | [8 empty] | 9.44 |  |  |  |  | 2.95
2007 |  |  |  | 8562.21 |  |  | 6999 |  |  |  | 1300 | [10 empty] | 77.13 |  |  |  | 78.42 | [5 empty] | 75.19 |  |  | 79.90 |  |  |  | 1.59 |  | 7.80 | [8 empty] | 13.78 |  |  |  |  | 1.29
2008 |  |  |  | 9538.78 |  |  | 7975 |  |  |  | 1300 | [10 empty] | 87.89 |  |  |  | 89.83 | [5 empty] | 83.53 |  |  | 90.79 |  |  |  | 0.71 |  | 1.70 | [8 empty] | 8.48 |  |  |  |  | 1.93
2009 |  |  |  | 10010.11 |  |  | 8733 |  |  |  | 1300 | [10 empty] | 97.73 |  |  |  | 99.13 | [5 empty] | 87.90 |  |  | 99.69 |  |  |  | 0.85 |  | 0.85 | [8 empty] | 0.02 |  |  |  |  | 1.39
2010 |  |  |  | 7502.23 |  |  | 6677 |  |  |  | 1300 | [10 empty] | 70.36 |  |  |  | 73.24 | [5 empty] | 65.88 |  |  | 76.22 |  |  |  | 2.52 |  | 7.05 | [8 empty] | 19.71 |  |  |  |  | 2.87
2011 |  |  |  | 9152.84 |  |  | 7786 |  |  |  | 1300 | [10 empty] | 85.24 |  |  |  | 88.38 | [5 empty] | 80.37 |  |  | 88.88 |  |  |  | 0.70 |  | 4.37 | [8 empty] | 7.25 |  |  |  |  | 3.15
2012 |  |  |  | 8090.85 |  |  | 6692 |  |  |  | 1300 | [10 empty] | 75.41 |  |  |  | 76.00 | [5 empty] | 70.85 |  |  | 76.18 |  |  |  | 23.98 |  | 23.98 | [8 empty] | 0.02 |  |  |  |  | 0.59
2013 |  |  |  | 6000.78 |  |  | 4913 |  |  |  | 1300 | [10 empty] | 53.96 |  |  |  | 54.34 | [5 empty] | 52.69 |  |  | 56.08 |  |  |  | 8.92 |  | 15.38 | [8 empty] | 30.29 |  |  |  |  | 0.38
2014 |  |  |  | 8851.37 |  |  | 7240 |  |  |  | 1300 | [10 empty] | 81.05 |  |  |  | 81.55 | [5 empty] | 77.73 |  |  | 82.65 |  |  |  | 0.46 |  | 0.82 | [8 empty] | 17.63 |  |  |  |  | 0.50
2015 |  |  |  | 10400.59 |  |  | 8451 |  |  |  | 1300 | [10 empty] | 94.92 |  |  |  | 95.61 | [5 empty] | 91.33 |  |  | 96.47 |  |  |  | 4.36 |  | 4.36 | [8 empty] | 0.03 |  |  |  |  | 0.69
2016 |  |  |  | 7204.81 |  |  | 6164 |  |  |  | 1300 | [10 empty] | 65.79 |  |  |  | 77.06 | [5 empty] | 63.09 |  |  | 70.17 |  |  |  | 2.82 |  | 2.24 | [8 empty] | 20.70 |  |  |  |  | 11.27
2017 |  |  |  | 9354.28 |  |  | 7629 |  |  |  | 1300 | [10 empty] | 84.84 |  |  |  | 86.39 | [5 empty] | 82.14 |  |  | 87.09 |  |  |  | 0.16 |  | 0.14 | [8 empty] | 13.47 |  |  |  |  | 1.55
2018 |  |  |  | 8932.66 |  |  | 7525 |  |  |  | 1300 | [10 empty] | 82.90 |  |  |  | 95.41 | [5 empty] | 78.44 |  |  | 85.90 |  |  |  | 4.52 |  | 4.52 | [8 empty] | 0.06 |  |  |  |  | 12.51
2019 |  |  |  | 7428.66 |  |  | 6266 |  |  |  | 1300 | [10 empty] | 69.53 |  |  |  | 73.44 | [5 empty] | 65.23 |  |  | 71.53 |  |  |  | 3.00 |  | 3.43 | [8 empty] | 23.13 |  |  |  |  | 3.91
2020 |  |  |  | 7676.68 |  |  | 6693 |  |  |  | 1300 | [10 empty] | 70.71 |  |  |  | 75.67 | [5 empty] | 67.23 |  |  | 76.20 |  |  |  | 11.22 |  | 11.70 | [8 empty] | 12.63 |  |  |  |  | 4.96
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1992 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 276 | [11 empty] | 1
B. |  | Refuelling without maintenance | [35 empty] | 85
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 836 |  |  |  | 23
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 44
E. |  | Testing of plant systems or components | [35 empty] | 44
I. |  | Grid capacity limitation | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 23
L. |  | Human factor related | [39 empty] | 15 | [11 empty] | 9
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 2 | [11 empty] | 37
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 36
Z. |  | Other | [39 empty] | 7
Subtotal | [37 empty] | 1009 |  |  |  | 323 | [11 empty] | 107
Total | [22 empty] | 0 | [14 empty] | 1439
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1992 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 10
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 26
15. |  |  | Reactor Cooling Systems | [34 empty] | 10
16. |  |  | Steam generation systems | [34 empty] | 37
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 35
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 32
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 95
42. |  |  | Electrical Power Supply Systems | [34 empty] | 16
Total | [37 empty] | 303

## CHINON B-1
2020 Operating Experience
FR-40 | [8 empty] | CHINON B-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP2 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-03-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-11-30
Gross electrical power | [12 empty] | : |  |  | 954 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-02-01
Reference unit power (net) | [12 empty] | : |  |  | 905 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 38 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5253.27 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.39 %
Energy Availability Factor (EAF) | [18 empty] | : | 68.67 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 73.73 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.25 %
Load Factor (LF) | [18 empty] | : | 66.08 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 5.06 %
Operating Factor (OF) | [18 empty] | : | 72.04 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2456 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 632.77 | 588.23 |  |  |  | 629.49 |  | 346.73 | [8 empty] | 606.40 |  |  | 631.17 | [6 empty] | 589.82 |  | 146.01 |  |  |  | 0.00 |  |  | 0.00 |  |  | 495.23 | [9 empty] | 587.42 |  |  | 5253.27
EAF [%] |  |  |  |  | 93.98 | 93.45 |  |  |  | 94.83 |  | 71.10 | [8 empty] | 91.49 |  |  | 96.99 | [6 empty] | 87.61 |  | 22.51 |  |  |  | 0.03 |  |  | 0.03 |  |  | 79.37 | [9 empty] | 93.55 |  |  | 68.67
UCF [%] |  |  |  |  | 95.46 | 99.46 |  |  |  | 98.94 |  | 89.71 | [8 empty] | 99.29 |  |  | 99.47 | [6 empty] | 99.80 |  | 30.04 |  |  |  | 0.03 |  |  | 0.03 |  |  | 79.60 | [9 empty] | 93.86 |  |  | 73.73
LF [%] |  |  |  |  | 93.98 | 93.39 |  |  |  | 93.62 |  | 53.21 | [8 empty] | 90.06 |  |  | 96.86 | [6 empty] | 87.60 |  | 21.69 |  |  |  | 0.00 |  |  | 0.00 |  |  | 76.00 | [9 empty] | 87.24 |  |  | 66.08
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 96.64 |  | 61.39 | [8 empty] | 93.41 |  |  | 100.00 | [6 empty] | 100.00 |  | 29.84 |  |  |  | 0.00 |  |  | 0.00 |  |  | 89.17 | [9 empty] | 94.76 |  |  | 72.04
FLR [%] |  |  |  |  | 4.48 | 0.49 |  |  |  | 0.63 |  | 10.20 | [8 empty] | 0.61 |  |  | 0.28 | [6 empty] | 0.00 |  | 33.26 |  |  |  | 0.00 |  |  | 0.00 |  |  | 3.30 | [9 empty] | 6.11 |  |  | 4.39
UCL [%] |  |  |  |  | 4.48 | 0.49 |  |  |  | 0.62 |  | 10.19 | [8 empty] | 0.61 |  |  | 0.28 | [6 empty] | 0.00 |  | 14.97 |  |  |  | 0.00 |  |  | 9.53 |  |  | 12.82 | [9 empty] | 6.10 |  |  | 5.02
PUF [%] |  |  |  |  | 0.06 | 0.05 |  |  |  | 0.44 |  | 0.10 | [8 empty] | 0.09 |  |  | 0.25 | [6 empty] | 0.20 |  | 54.98 |  |  |  | 99.97 |  |  | 90.44 |  |  | 7.58 | [9 empty] | 0.03 |  |  | 21.25
XUF [%] |  |  |  |  | 1.48 | 6.01 |  |  |  | 4.11 |  | 18.61 | [8 empty] | 7.81 |  |  | 2.49 | [6 empty] | 12.19 |  | 7.54 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.23 | [9 empty] | 0.31 |  |  | 5.06
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 216971.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.29 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.44 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.27 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.27 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.45 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.12 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.83 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.27 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 4568.00 |  |  | 5570 |  |  |  | 870 | [10 empty] | 57.57 |  |  |  | 57.57 | [5 empty] | 56.11 |  |  | 60.14 |  |  |  | 16.20 |  | 11.13 | [8 empty] | 31.30 |  |  |  |  | 0.00
1985 |  |  |  | 5978.20 |  |  | 7402 |  |  |  | 870 | [10 empty] | 82.12 |  |  |  | 84.46 | [5 empty] | 78.44 |  |  | 84.50 |  |  |  | 2.46 |  | 2.13 | [8 empty] | 13.41 |  |  |  |  | 2.34
1986 |  |  |  | 6322.20 |  |  | 7609 |  |  |  | 870 | [10 empty] | 86.06 |  |  |  | 86.08 | [5 empty] | 82.96 |  |  | 86.86 |  |  |  | 3.52 |  | 3.14 | [8 empty] | 10.77 |  |  |  |  | 0.02
1987 |  |  |  | 4914.10 |  |  | 6438 |  |  |  | 870 | [10 empty] | 72.92 |  |  |  | 73.65 | [5 empty] | 64.48 |  |  | 73.49 |  |  |  | 16.21 |  | 14.25 | [8 empty] | 12.10 |  |  |  |  | 0.73
1988 |  |  |  | 5271.00 |  |  | 7195 |  |  |  | 870 | [10 empty] | 96.18 |  |  |  | 97.40 | [5 empty] | 68.97 |  |  | 81.91 |  |  |  | 2.50 |  | 2.50 | [8 empty] | 0.10 |  |  |  |  | 1.22
1989 |  |  |  | 4734.28 |  |  | 5724 |  |  |  | 870 | [10 empty] | 63.62 |  |  |  | 64.41 | [5 empty] | 62.12 |  |  | 65.34 |  |  |  | 19.35 |  | 15.45 | [8 empty] | 20.14 |  |  |  |  | 0.78
1990 |  |  |  | 5912.97 |  |  | 7043 |  |  |  | 870 | [10 empty] | 79.14 |  |  |  | 79.34 | [5 empty] | 77.59 |  |  | 80.40 |  |  |  | 9.15 |  | 7.99 | [8 empty] | 12.67 |  |  |  |  | 0.20
1991 |  |  |  | 5339.25 |  |  | 6033 |  |  |  | 905 | [10 empty] | 67.66 |  |  |  | 67.96 | [5 empty] | 67.35 |  |  | 68.87 |  |  |  | 20.43 |  | 17.45 | [8 empty] | 14.60 |  |  |  |  | 0.30
1992 |  |  |  | 5972.02 |  |  | 7133 |  |  |  | 905 | [10 empty] | 80.59 |  |  |  | 80.94 | [5 empty] | 75.12 |  |  | 81.20 |  |  |  | 3.98 |  | 3.35 | [8 empty] | 15.70 |  |  |  |  | 0.36
1993 |  |  |  | 5651.68 |  |  | 6914 |  |  |  | 905 | [10 empty] | 73.26 |  |  |  | 77.71 | [5 empty] | 71.29 |  |  | 78.93 |  |  |  | 10.64 |  | 9.25 | [8 empty] | 13.05 |  |  |  |  | 4.45
1994 |  |  |  | 5366.30 |  |  | 6347 |  |  |  | 905 | [10 empty] | 71.36 |  |  |  | 71.91 | [5 empty] | 67.69 |  |  | 72.45 |  |  |  | 4.52 |  | 3.41 | [8 empty] | 24.68 |  |  |  |  | 0.55
1995 |  |  |  | 6333.93 |  |  | 7573 |  |  |  | 905 | [10 empty] | 84.39 |  |  |  | 85.60 | [5 empty] | 79.90 |  |  | 86.45 |  |  |  | 4.43 |  | 3.97 | [8 empty] | 10.44 |  |  |  |  | 1.21
1996 |  |  |  | 6295.23 |  |  | 7476 |  |  |  | 905 | [10 empty] | 83.36 |  |  |  | 83.58 | [5 empty] | 79.19 |  |  | 85.11 |  |  |  | 5.07 |  | 4.46 | [8 empty] | 11.96 |  |  |  |  | 0.22
1997 |  |  |  | 6093.31 |  |  | 7268 |  |  |  | 905 | [10 empty] | 81.84 |  |  |  | 81.94 | [5 empty] | 76.86 |  |  | 82.97 |  |  |  | 1.47 |  | 1.22 | [8 empty] | 16.84 |  |  |  |  | 0.10
1998 |  |  |  | 6631.27 |  |  | 7759 |  |  |  | 905 | [10 empty] | 85.68 |  |  |  | 87.12 | [5 empty] | 83.65 |  |  | 88.57 |  |  |  | 1.47 |  | 1.30 | [8 empty] | 11.59 |  |  |  |  | 1.44
1999 |  |  |  | 6214.03 |  |  | 7483 |  |  |  | 905 | [10 empty] | 82.06 |  |  |  | 84.31 | [5 empty] | 78.38 |  |  | 85.42 |  |  |  | 5.73 |  | 5.12 | [8 empty] | 10.57 |  |  |  |  | 2.25
2000 |  |  |  | 6166.79 |  |  | 7416 |  |  |  | 905 | [10 empty] | 82.68 |  |  |  | 83.64 | [5 empty] | 77.57 |  |  | 84.43 |  |  |  | 5.27 |  | 4.65 | [8 empty] | 11.71 |  |  |  |  | 0.96
2001 |  |  |  | 5769.00 |  |  | 7260 |  |  |  | 905 | [10 empty] | 81.16 |  |  |  | 82.61 | [5 empty] | 72.77 |  |  | 82.88 |  |  |  | 1.95 |  | 1.65 | [8 empty] | 15.75 |  |  |  |  | 1.45
2002 |  |  |  | 6229.34 |  |  | 7671 |  |  |  | 905 | [10 empty] | 85.55 |  |  |  | 88.86 | [5 empty] | 78.58 |  |  | 87.57 |  |  |  | 2.02 |  | 1.83 | [8 empty] | 9.30 |  |  |  |  | 3.31
2003 |  |  |  | 5181.70 |  |  | 6357 |  |  |  | 905 | [10 empty] | 68.36 |  |  |  | 71.01 | [5 empty] | 65.36 |  |  | 72.57 |  |  |  | 4.62 |  | 3.44 | [8 empty] | 25.55 |  |  |  |  | 2.65
2004 |  |  |  | 6252.57 |  |  | 7536 |  |  |  | 905 | [10 empty] | 83.66 |  |  |  | 83.66 | [5 empty] | 78.65 |  |  | 85.79 |  |  |  | 6.40 |  | 5.72 | [8 empty] | 10.63 |  |  |  |  | 0.00
2005 |  |  |  | 6465.82 |  |  | 7611 |  |  |  | 905 | [10 empty] | 83.93 |  |  |  | 84.49 | [5 empty] | 81.55 |  |  | 86.87 |  |  |  | 2.05 |  | 4.40 | [8 empty] | 11.11 |  |  |  |  | 0.56
2006 |  |  |  | 6637.84 |  |  | 7873 |  |  |  | 905 | [10 empty] | 86.67 |  |  |  | 87.25 | [5 empty] | 83.73 |  |  | 89.87 |  |  |  | 2.14 |  | 1.91 | [8 empty] | 10.84 |  |  |  |  | 0.59
2007 |  |  |  | 4538.82 |  |  | 5559 |  |  |  | 905 | [10 empty] | 57.66 |  |  |  | 61.04 | [5 empty] | 57.25 |  |  | 63.46 |  |  |  | 15.66 |  | 12.83 | [8 empty] | 26.13 |  |  |  |  | 3.38
2008 |  |  |  | 6893.10 |  |  | 7862 |  |  |  | 905 | [10 empty] | 86.87 |  |  |  | 88.07 | [5 empty] | 86.71 |  |  | 89.50 |  |  |  | 1.53 |  | 2.65 | [8 empty] | 9.28 |  |  |  |  | 1.20
2009 |  |  |  | 4345.75 |  |  | 5003 |  |  |  | 905 | [10 empty] | 55.12 |  |  |  | 78.46 | [5 empty] | 54.82 |  |  | 57.11 |  |  |  | 1.51 |  | 8.58 | [8 empty] | 12.95 |  |  |  |  | 23.34
2010 |  |  |  | 4165.79 |  |  | 4893 |  |  |  | 905 | [10 empty] | 52.82 |  |  |  | 53.23 | [5 empty] | 52.55 |  |  | 55.86 |  |  |  | 35.70 |  | 31.96 | [8 empty] | 14.81 |  |  |  |  | 0.42
2011 |  |  |  | 5808.26 |  |  | 6601 |  |  |  | 905 | [10 empty] | 73.65 |  |  |  | 73.66 | [5 empty] | 73.26 |  |  | 75.35 |  |  |  | 2.27 |  | 12.09 | [8 empty] | 14.26 |  |  |  |  | 0.01
2012 |  |  |  | 6881.62 |  |  | 7766 |  |  |  | 905 | [10 empty] | 87.31 |  |  |  | 87.31 | [5 empty] | 86.57 |  |  | 88.41 |  |  |  | 1.89 |  | 5.39 | [8 empty] | 7.30 |  |  |  |  | 0.00
2013 |  |  |  | 4078.88 |  |  | 4634 |  |  |  | 905 | [10 empty] | 51.55 |  |  |  | 52.27 | [5 empty] | 51.45 |  |  | 52.90 |  |  |  | 6.40 |  | 22.45 | [8 empty] | 25.29 |  |  |  |  | 0.71
2014 |  |  |  | 6524.18 |  |  | 7473 |  |  |  | 905 | [10 empty] | 83.17 |  |  |  | 83.90 | [5 empty] | 82.29 |  |  | 85.31 |  |  |  | 3.68 |  | 7.30 | [8 empty] | 8.80 |  |  |  |  | 0.73
2015 |  |  |  | 5847.76 |  |  | 6812 |  |  |  | 905 | [10 empty] | 75.28 |  |  |  | 76.17 | [5 empty] | 73.76 |  |  | 77.76 |  |  |  | 5.56 |  | 6.73 | [8 empty] | 17.10 |  |  |  |  | 0.89
2016 |  |  |  | 6754.06 |  |  | 7846 |  |  |  | 905 | [10 empty] | 86.81 |  |  |  | 89.53 | [5 empty] | 84.96 |  |  | 89.32 |  |  |  | 0.44 |  | 1.74 | [8 empty] | 8.73 |  |  |  |  | 2.72
2017 |  |  |  | 5139.16 |  |  | 5867 |  |  |  | 905 | [10 empty] | 65.25 |  |  |  | 66.72 | [5 empty] | 64.82 |  |  | 66.97 |  |  |  | 5.36 |  | 16.47 | [8 empty] | 16.81 |  |  |  |  | 1.48
2018 |  |  |  | 6888.18 |  |  | 7949 |  |  |  | 905 | [10 empty] | 88.47 |  |  |  | 89.27 | [5 empty] | 86.89 |  |  | 90.74 |  |  |  | 0.76 |  | 1.17 | [8 empty] | 9.56 |  |  |  |  | 0.79
2019 |  |  |  | 5820.16 |  |  | 6750 |  |  |  | 905 | [10 empty] | 74.38 |  |  |  | 75.25 | [5 empty] | 73.41 |  |  | 77.05 |  |  |  | 2.81 |  | 5.65 | [8 empty] | 19.11 |  |  |  |  | 0.87
2020 |  |  |  | 5253.27 |  |  | 6328 |  |  |  | 905 | [10 empty] | 68.67 |  |  |  | 73.73 | [5 empty] | 66.08 |  |  | 72.04 |  |  |  | 4.39 |  | 5.02 | [8 empty] | 21.25 |  |  |  |  | 5.06
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 498
B. |  | Refuelling without maintenance | [35 empty] | 117
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1029 |  |  |  | 47
E. |  | Testing of plant systems or components | [35 empty] | 6 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 3
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 12
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 27 | [11 empty] | 70
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 7
Z. |  | Other | [39 empty] | 21
Subtotal | [37 empty] | 1152 |  |  |  | 616 | [11 empty] | 77
Total | [22 empty] | 0 | [14 empty] | 1845
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 9
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 27
14. |  |  | Safety Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 27
16. |  |  | Steam generation systems | [34 empty] | 14
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 13
31. |  |  | Turbine and auxiliaries | [34 empty] | 125
32. |  |  | Feedwater and Main Steam System | [34 empty] | 18
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 96
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 108
42. |  |  | Electrical Power Supply Systems | [34 empty] | 30
Total | [37 empty] | 489

## CHINON B-2
2020 Operating Experience
FR-41 | [8 empty] | CHINON B-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP2 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-03-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-11-29
Gross electrical power | [12 empty] | : |  |  | 954 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-08-01
Reference unit power (net) | [12 empty] | : |  |  | 905 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 38 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6431.85 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 11.16 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.51 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 11.15 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.7 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.15 %
Load Factor (LF) | [18 empty] | : | 80.91 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 5.19 %
Operating Factor (OF) | [18 empty] | : | 84.84 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1332 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 97.28 | 437.52 |  |  |  | 672.69 |  | 646.57 | [8 empty] | 498.47 |  |  | 442.63 | [6 empty] | 486.49 |  | 629.47 |  |  |  | 601.49 |  |  | 614.00 |  |  | 635.49 | [9 empty] | 669.74 |  |  | 6431.85
EAF [%] |  |  |  |  | 14.49 | 69.66 |  |  |  | 99.69 |  | 99.21 | [8 empty] | 80.04 |  |  | 73.28 | [6 empty] | 74.40 |  | 98.56 |  |  |  | 98.68 |  |  | 95.52 |  |  | 99.51 | [9 empty] | 99.37 |  |  | 83.51
UCF [%] |  |  |  |  | 14.49 | 81.35 |  |  |  | 99.75 |  | 99.79 | [8 empty] | 99.72 |  |  | 99.70 | [6 empty] | 76.32 |  | 99.57 |  |  |  | 99.09 |  |  | 95.88 |  |  | 99.77 | [9 empty] | 99.92 |  |  | 88.70
LF [%] |  |  |  |  | 14.45 | 69.46 |  |  |  | 100.04 |  | 99.23 | [8 empty] | 74.03 |  |  | 67.93 | [6 empty] | 72.25 |  | 93.49 |  |  |  | 92.31 |  |  | 91.07 |  |  | 97.53 | [9 empty] | 99.47 |  |  | 80.91
OF [%] |  |  |  |  | 16.80 | 70.40 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 80.11 |  |  | 74.86 | [6 empty] | 81.99 |  | 100.00 |  |  |  | 100.00 |  |  | 94.09 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.84
FLR [%] |  |  |  |  | 85.50 | 18.54 |  |  |  | 0.06 |  | 0.07 | [8 empty] | 0.21 |  |  | 0.14 | [6 empty] | 23.60 |  | 0.11 |  |  |  | 0.80 |  |  | 3.89 |  |  | 0.07 | [9 empty] | 0.00 |  |  | 11.16
UCL [%] |  |  |  |  | 85.40 | 18.52 |  |  |  | 0.06 |  | 0.07 | [8 empty] | 0.21 |  |  | 0.14 | [6 empty] | 23.58 |  | 0.11 |  |  |  | 0.80 |  |  | 3.89 |  |  | 0.07 | [9 empty] | 0.00 |  |  | 11.15
PUF [%] |  |  |  |  | 0.12 | 0.13 |  |  |  | 0.19 |  | 0.14 | [8 empty] | 0.07 |  |  | 0.15 | [6 empty] | 0.10 |  | 0.32 |  |  |  | 0.11 |  |  | 0.24 |  |  | 0.16 | [9 empty] | 0.08 |  |  | 0.15
XUF [%] |  |  |  |  | 0.00 | 11.69 |  |  |  | 0.06 |  | 0.58 | [8 empty] | 19.67 |  |  | 26.42 | [6 empty] | 1.92 |  | 1.01 |  |  |  | 0.41 |  |  | 0.35 |  |  | 0.26 | [9 empty] | 0.55 |  |  | 5.19
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 211059.72 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.64 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.72 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.18 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.67 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.8 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.95 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.93 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 5394.00 |  |  | 7226 |  |  |  | 870 | [10 empty] | 91.69 |  |  |  | 91.69 | [5 empty] | 75.83 |  |  | 81.27 |  |  |  | 8.31 |  | 8.31 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 5037.40 |  |  | 6201 |  |  |  | 870 | [10 empty] | 67.88 |  |  |  | 69.30 | [5 empty] | 66.10 |  |  | 70.79 |  |  |  | 4.44 |  | 3.22 | [8 empty] | 27.48 |  |  |  |  | 1.42
1986 |  |  |  | 6215.10 |  |  | 7639 |  |  |  | 870 | [10 empty] | 86.02 |  |  |  | 86.42 | [5 empty] | 81.55 |  |  | 87.20 |  |  |  | 3.85 |  | 3.46 | [8 empty] | 10.11 |  |  |  |  | 0.40
1987 |  |  |  | 5618.80 |  |  | 7171 |  |  |  | 870 | [10 empty] | 80.73 |  |  |  | 81.14 | [5 empty] | 73.73 |  |  | 81.86 |  |  |  | 9.38 |  | 8.40 | [8 empty] | 10.46 |  |  |  |  | 0.41
1988 |  |  |  | 4425.00 |  |  | 5731 |  |  |  | 870 | [10 empty] | 67.26 |  |  |  | 68.40 | [5 empty] | 57.90 |  |  | 65.24 |  |  |  | 23.79 |  | 21.36 | [8 empty] | 10.25 |  |  |  |  | 1.14
1989 |  |  |  | 6043.40 |  |  | 7873 |  |  |  | 870 | [10 empty] | 91.22 |  |  |  | 94.36 | [5 empty] | 79.30 |  |  | 89.87 |  |  |  | 1.27 |  | 1.21 | [8 empty] | 4.43 |  |  |  |  | 3.15
1990 |  |  |  | 5216.99 |  |  | 6714 |  |  |  | 870 | [10 empty] | 84.12 |  |  |  | 84.42 | [5 empty] | 68.45 |  |  | 76.64 |  |  |  | 7.80 |  | 7.14 | [8 empty] | 8.44 |  |  |  |  | 0.30
1991 |  |  |  | 3142.20 |  |  | 3921 |  |  |  | 870 | [10 empty] | 53.19 |  |  |  | 55.79 | [5 empty] | 41.23 |  |  | 44.76 |  |  |  | 29.04 |  | 22.83 | [8 empty] | 21.38 |  |  |  |  | 2.59
1992 |  |  |  | 6295.44 |  |  | 7321 |  |  |  | 870 | [10 empty] | 80.76 |  |  |  | 81.98 | [5 empty] | 82.38 |  |  | 83.34 |  |  |  | 2.05 |  | 1.72 | [8 empty] | 16.30 |  |  |  |  | 1.23
1993 |  |  |  | 5491.59 |  |  | 6867 |  |  |  | 870 | [10 empty] | 76.25 |  |  |  | 81.41 | [5 empty] | 72.06 |  |  | 78.39 |  |  |  | 6.53 |  | 5.68 | [8 empty] | 12.90 |  |  |  |  | 5.17
1994 |  |  |  | 6174.63 |  |  | 7407 |  |  |  | 905 | [10 empty] | 83.94 |  |  |  | 84.73 | [5 empty] | 77.89 |  |  | 84.55 |  |  |  | 4.32 |  | 3.82 | [8 empty] | 11.45 |  |  |  |  | 0.79
1995 |  |  |  | 6356.32 |  |  | 7741 |  |  |  | 905 | [10 empty] | 85.98 |  |  |  | 86.08 | [5 empty] | 80.18 |  |  | 88.37 |  |  |  | 3.28 |  | 2.92 | [8 empty] | 11.01 |  |  |  |  | 0.09
1996 |  |  |  | 5287.61 |  |  | 6206 |  |  |  | 905 | [10 empty] | 69.38 |  |  |  | 69.62 | [5 empty] | 66.51 |  |  | 70.65 |  |  |  | 7.32 |  | 5.49 | [8 empty] | 24.89 |  |  |  |  | 0.24
1997 |  |  |  | 6637.94 |  |  | 7622 |  |  |  | 905 | [10 empty] | 85.20 |  |  |  | 86.50 | [5 empty] | 83.73 |  |  | 87.01 |  |  |  | 1.86 |  | 1.64 | [8 empty] | 11.86 |  |  |  |  | 1.30
1998 |  |  |  | 6186.39 |  |  | 7136 |  |  |  | 905 | [10 empty] | 79.85 |  |  |  | 80.36 | [5 empty] | 78.03 |  |  | 81.46 |  |  |  | 7.20 |  | 6.24 | [8 empty] | 13.40 |  |  |  |  | 0.51
1999 |  |  |  | 5900.93 |  |  | 7075 |  |  |  | 905 | [10 empty] | 78.96 |  |  |  | 79.10 | [5 empty] | 74.43 |  |  | 80.76 |  |  |  | 10.24 |  | 9.03 | [8 empty] | 11.87 |  |  |  |  | 0.15
2000 |  |  |  | 6177.00 |  |  | 7260 |  |  |  | 905 | [10 empty] | 80.81 |  |  |  | 81.16 | [5 empty] | 77.70 |  |  | 82.65 |  |  |  | 5.21 |  | 4.46 | [8 empty] | 14.37 |  |  |  |  | 0.35
2001 |  |  |  | 6646.20 |  |  | 7846 |  |  |  | 905 | [10 empty] | 87.52 |  |  |  | 88.49 | [5 empty] | 83.83 |  |  | 89.57 |  |  |  | 2.09 |  | 1.89 | [8 empty] | 9.63 |  |  |  |  | 0.97
2002 |  |  |  | 6155.60 |  |  | 7404 |  |  |  | 905 | [10 empty] | 85.35 |  |  |  | 86.22 | [5 empty] | 77.65 |  |  | 84.52 |  |  |  | 0.87 |  | 0.76 | [8 empty] | 13.02 |  |  |  |  | 0.86
2003 |  |  |  | 5746.23 |  |  | 7163 |  |  |  | 905 | [10 empty] | 78.72 |  |  |  | 81.28 | [5 empty] | 72.48 |  |  | 81.77 |  |  |  | 9.09 |  | 8.13 | [8 empty] | 10.59 |  |  |  |  | 2.56
2004 |  |  |  | 6133.37 |  |  | 7252 |  |  |  | 905 | [10 empty] | 80.62 |  |  |  | 80.94 | [5 empty] | 77.15 |  |  | 82.56 |  |  |  | 6.56 |  | 5.68 | [8 empty] | 13.38 |  |  |  |  | 0.31
2005 |  |  |  | 6659.58 |  |  | 7882 |  |  |  | 905 | [10 empty] | 86.50 |  |  |  | 88.00 | [5 empty] | 84.00 |  |  | 89.98 |  |  |  | 1.73 |  | 3.38 | [8 empty] | 8.62 |  |  |  |  | 1.50
2006 |  |  |  | 4548.84 |  |  | 5503 |  |  |  | 905 | [10 empty] | 60.11 |  |  |  | 61.45 | [5 empty] | 57.38 |  |  | 62.82 |  |  |  | 12.98 |  | 15.37 | [8 empty] | 23.19 |  |  |  |  | 1.34
2007 |  |  |  | 5965.94 |  |  | 7023 |  |  |  | 905 | [10 empty] | 76.58 |  |  |  | 77.85 | [5 empty] | 75.25 |  |  | 80.17 |  |  |  | 4.21 |  | 8.74 | [8 empty] | 13.41 |  |  |  |  | 1.27
2008 |  |  |  | 5038.27 |  |  | 5852 |  |  |  | 905 | [10 empty] | 64.24 |  |  |  | 64.95 | [5 empty] | 63.38 |  |  | 66.62 |  |  |  | 2.43 |  | 19.75 | [8 empty] | 15.30 |  |  |  |  | 0.71
2009 |  |  |  | 6111.50 |  |  | 7485 |  |  |  | 905 | [10 empty] | 77.93 |  |  |  | 83.83 | [5 empty] | 77.09 |  |  | 85.45 |  |  |  | 3.97 |  | 8.11 | [8 empty] | 8.05 |  |  |  |  | 5.90
2010 |  |  |  | 5735.14 |  |  | 6561 |  |  |  | 905 | [10 empty] | 72.95 |  |  |  | 73.96 | [5 empty] | 72.34 |  |  | 74.90 |  |  |  | 3.67 |  | 11.20 | [8 empty] | 14.85 |  |  |  |  | 1.01
2011 |  |  |  | 6863.39 |  |  | 7733 |  |  |  | 905 | [10 empty] | 87.23 |  |  |  | 87.30 | [5 empty] | 86.57 |  |  | 88.28 |  |  |  | 1.00 |  | 3.94 | [8 empty] | 8.77 |  |  |  |  | 0.07
2012 |  |  |  | 6880.86 |  |  | 7965 |  |  |  | 905 | [10 empty] | 87.34 |  |  |  | 90.04 | [5 empty] | 86.56 |  |  | 90.68 |  |  |  | 2.01 |  | 1.85 | [8 empty] | 8.11 |  |  |  |  | 2.69
2013 |  |  |  | 4538.32 |  |  | 5483 |  |  |  | 905 | [10 empty] | 63.15 |  |  |  | 64.52 | [5 empty] | 57.25 |  |  | 62.59 |  |  |  | 2.30 |  | 15.85 | [8 empty] | 19.63 |  |  |  |  | 1.37
2014 |  |  |  | 5721.41 |  |  | 6565 |  |  |  | 905 | [10 empty] | 73.83 |  |  |  | 75.14 | [5 empty] | 72.17 |  |  | 74.94 |  |  |  | 3.86 |  | 8.28 | [8 empty] | 16.58 |  |  |  |  | 1.31
2015 |  |  |  | 5495.29 |  |  | 6235 |  |  |  | 905 | [10 empty] | 69.57 |  |  |  | 70.62 | [5 empty] | 69.32 |  |  | 71.18 |  |  |  | 22.10 |  | 20.79 | [8 empty] | 8.59 |  |  |  |  | 1.06
2016 |  |  |  | 3614.86 |  |  | 4251 |  |  |  | 905 | [10 empty] | 45.53 |  |  |  | 65.98 | [5 empty] | 45.47 |  |  | 48.39 |  |  |  | 0.50 |  | 3.78 | [8 empty] | 30.24 |  |  |  |  | 20.45
2017 |  |  |  | 6249.36 |  |  | 7345 |  |  |  | 905 | [10 empty] | 81.21 |  |  |  | 82.73 | [5 empty] | 78.83 |  |  | 83.85 |  |  |  | 3.64 |  | 8.43 | [8 empty] | 8.84 |  |  |  |  | 1.52
2018 |  |  |  | 5352.55 |  |  | 6303 |  |  |  | 905 | [10 empty] | 69.60 |  |  |  | 70.32 | [5 empty] | 67.52 |  |  | 71.95 |  |  |  | 0.69 |  | 12.09 | [8 empty] | 17.59 |  |  |  |  | 0.73
2019 |  |  |  | 5716.24 |  |  | 6607 |  |  |  | 905 | [10 empty] | 72.70 |  |  |  | 73.62 | [5 empty] | 72.10 |  |  | 75.42 |  |  |  | 13.61 |  | 16.80 | [8 empty] | 9.59 |  |  |  |  | 0.91
2020 |  |  |  | 6431.85 |  |  | 7452 |  |  |  | 905 | [10 empty] | 83.51 |  |  |  | 88.70 | [5 empty] | 80.91 |  |  | 84.84 |  |  |  | 11.16 |  | 11.15 | [8 empty] | 0.15 |  |  |  |  | 5.19
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 552
B. |  | Refuelling without maintenance | [35 empty] | 146
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 939 |  |  |  | 7
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 2
E. |  | Testing of plant systems or components | [35 empty] | 12 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 14
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 36
L. |  | Human factor related | [39 empty] | 16
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 4 | [11 empty] | 61
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 9 | [11 empty] | 1
Z. |  | Other | [39 empty] | 18
Subtotal | [37 empty] | 1099 |  |  |  | 621 | [11 empty] | 99
Total | [22 empty] | 0 | [14 empty] | 1819
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 18
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 32
14. |  |  | Safety Systems | [34 empty] | 30
15. |  |  | Reactor Cooling Systems | [34 empty] | 43
16. |  |  | Steam generation systems | [34 empty] | 95
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 20
31. |  |  | Turbine and auxiliaries | [34 empty] | 57
32. |  |  | Feedwater and Main Steam System | [34 empty] | 24
33. |  |  | Circulating Water System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 112
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 93
42. |  |  | Electrical Power Supply Systems | [34 empty] | 43
Total | [37 empty] | 592

## CHINON B-3
2020 Operating Experience
FR-56 | [8 empty] | CHINON B-3 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP2 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-10-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-10-20
Gross electrical power | [12 empty] | : |  |  | 954 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-03-04
Reference unit power (net) | [12 empty] | : |  |  | 905 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 38 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4848.5 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.24 %
Energy Availability Factor (EAF) | [18 empty] | : | 67.51 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 28.45 %
Unit Capability Factor (UCF) | [18 empty] | : | 70.38 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 1.17 %
Load Factor (LF) | [18 empty] | : | 60.99 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.86 %
Operating Factor (OF) | [18 empty] | : | 68.84 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2737 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 315.11 | [8 empty] | 624.56 |  |  | 397.52 | [6 empty] | 561.83 |  | 516.83 |  |  |  | 573.45 |  |  | 662.44 |  |  | 577.56 | [9 empty] | 619.20 |  |  | 4848.50
EAF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.04 |  | 53.02 | [8 empty] | 98.37 |  |  | 77.99 | [6 empty] | 91.71 |  | 96.33 |  |  |  | 93.71 |  |  | 99.17 |  |  | 97.69 | [9 empty] | 99.33 |  |  | 67.51
UCF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.04 |  | 53.13 | [8 empty] | 99.21 |  |  | 99.79 | [6 empty] | 99.28 |  | 96.90 |  |  |  | 94.39 |  |  | 99.78 |  |  | 99.64 | [9 empty] | 99.80 |  |  | 70.38
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 48.36 | [8 empty] | 92.76 |  |  | 61.01 | [6 empty] | 83.44 |  | 76.76 |  |  |  | 88.01 |  |  | 98.25 |  |  | 88.64 | [9 empty] | 91.96 |  |  | 60.99
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 65.28 | [8 empty] | 100.00 |  |  | 83.33 | [6 empty] | 93.41 |  | 85.89 |  |  |  | 95.97 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 68.84
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 34.99 | [8 empty] | 0.51 |  |  | 0.13 | [6 empty] | 0.09 |  | 2.98 |  |  |  | 5.22 |  |  | 0.13 |  |  | 0.09 | [9 empty] | 0.13 |  |  | 4.24
UCL [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 99.96 |  | 34.60 | [8 empty] | 0.51 |  |  | 0.13 | [6 empty] | 0.09 |  | 2.97 |  |  |  | 5.20 |  |  | 0.13 |  |  | 0.09 | [9 empty] | 0.13 |  |  | 28.45
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 12.28 | [8 empty] | 0.28 |  |  | 0.08 | [6 empty] | 0.63 |  | 0.13 |  |  |  | 0.40 |  |  | 0.09 |  |  | 0.27 | [9 empty] | 0.07 |  |  | 1.17
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.11 | [8 empty] | 0.85 |  |  | 21.80 | [6 empty] | 7.58 |  | 0.56 |  |  |  | 0.68 |  |  | 0.61 |  |  | 1.95 | [9 empty] | 0.47 |  |  | 2.86
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 198992.66 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.44 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.95 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.64 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.06 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.73 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.7 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 4120.60 |  |  | 5311 |  |  |  | 870 | [10 empty] | 67.61 |  |  |  | 67.61 | [5 empty] | 52.00 |  |  | 59.68 |  |  |  | 24.66 |  | 22.13 | [8 empty] | 10.26 |  |  |  |  | 0.00
1988 |  |  |  | 4413.00 |  |  | 5354 |  |  |  | 905 | [10 empty] | 58.90 |  |  |  | 61.48 | [5 empty] | 55.51 |  |  | 60.95 |  |  |  | 21.77 |  | 17.11 | [8 empty] | 21.41 |  |  |  |  | 2.58
1989 |  |  |  | 5028.58 |  |  | 6125 |  |  |  | 905 | [10 empty] | 77.81 |  |  |  | 81.19 | [5 empty] | 63.43 |  |  | 69.92 |  |  |  | 6.64 |  | 5.77 | [8 empty] | 13.04 |  |  |  |  | 3.38
1990 |  |  |  | 5417.63 |  |  | 6274 |  |  |  | 905 | [10 empty] | 69.12 |  |  |  | 69.18 | [5 empty] | 68.34 |  |  | 71.62 |  |  |  | 16.51 |  | 13.68 | [8 empty] | 17.15 |  |  |  |  | 0.06
1991 |  |  |  | 7026.39 |  |  | 8204 |  |  |  | 905 | [10 empty] | 90.66 |  |  |  | 92.91 | [5 empty] | 88.63 |  |  | 93.65 |  |  |  | 4.00 |  | 3.87 | [8 empty] | 3.22 |  |  |  |  | 2.25
1992 |  |  |  | 6091.45 |  |  | 7468 |  |  |  | 905 | [10 empty] | 85.62 |  |  |  | 87.48 | [5 empty] | 76.63 |  |  | 85.02 |  |  |  | 2.98 |  | 2.69 | [8 empty] | 9.83 |  |  |  |  | 1.86
1993 |  |  |  | 5600.75 |  |  | 6827 |  |  |  | 905 | [10 empty] | 72.61 |  |  |  | 78.35 | [5 empty] | 70.65 |  |  | 77.93 |  |  |  | 3.69 |  | 3.00 | [8 empty] | 18.65 |  |  |  |  | 5.74
1994 |  |  |  | 5064.02 |  |  | 6325 |  |  |  | 905 | [10 empty] | 75.45 |  |  |  | 76.21 | [5 empty] | 63.88 |  |  | 72.20 |  |  |  | 15.56 |  | 14.04 | [8 empty] | 9.75 |  |  |  |  | 0.76
1995 |  |  |  | 6005.65 |  |  | 7177 |  |  |  | 905 | [10 empty] | 82.54 |  |  |  | 83.34 | [5 empty] | 75.75 |  |  | 81.93 |  |  |  | 7.56 |  | 6.82 | [8 empty] | 9.84 |  |  |  |  | 0.81
1996 |  |  |  | 6277.96 |  |  | 7761 |  |  |  | 905 | [10 empty] | 86.86 |  |  |  | 87.18 | [5 empty] | 78.97 |  |  | 88.35 |  |  |  | 1.56 |  | 1.38 | [8 empty] | 11.44 |  |  |  |  | 0.31
1997 |  |  |  | 5816.77 |  |  | 7249 |  |  |  | 905 | [10 empty] | 85.07 |  |  |  | 85.10 | [5 empty] | 73.37 |  |  | 82.75 |  |  |  | 0.96 |  | 0.82 | [8 empty] | 14.08 |  |  |  |  | 0.03
1998 |  |  |  | 6345.64 |  |  | 7472 |  |  |  | 905 | [10 empty] | 81.32 |  |  |  | 84.10 | [5 empty] | 80.04 |  |  | 85.30 |  |  |  | 0.65 |  | 0.55 | [8 empty] | 15.35 |  |  |  |  | 2.77
1999 |  |  |  | 5601.97 |  |  | 6656 |  |  |  | 905 | [10 empty] | 72.19 |  |  |  | 74.80 | [5 empty] | 70.66 |  |  | 75.98 |  |  |  | 4.22 |  | 3.30 | [8 empty] | 21.90 |  |  |  |  | 2.62
2000 |  |  |  | 6330.11 |  |  | 7386 |  |  |  | 905 | [10 empty] | 82.52 |  |  |  | 83.12 | [5 empty] | 79.63 |  |  | 84.08 |  |  |  | 3.89 |  | 3.36 | [8 empty] | 13.52 |  |  |  |  | 0.60
2001 |  |  |  | 6318.00 |  |  | 7665 |  |  |  | 905 | [10 empty] | 84.76 |  |  |  | 87.05 | [5 empty] | 79.69 |  |  | 87.50 |  |  |  | 1.29 |  | 1.14 | [8 empty] | 11.82 |  |  |  |  | 2.29
2002 |  |  |  | 6720.45 |  |  | 7971 |  |  |  | 905 | [10 empty] | 87.57 |  |  |  | 90.03 | [5 empty] | 84.77 |  |  | 90.99 |  |  |  | 0.43 |  | 0.39 | [8 empty] | 9.58 |  |  |  |  | 2.46
2003 |  |  |  | 5807.75 |  |  | 6954 |  |  |  | 905 | [10 empty] | 77.57 |  |  |  | 77.72 | [5 empty] | 73.26 |  |  | 79.38 |  |  |  | 11.07 |  | 9.68 | [8 empty] | 12.60 |  |  |  |  | 0.15
2004 |  |  |  | 5784.36 |  |  | 7444 |  |  |  | 905 | [10 empty] | 82.34 |  |  |  | 82.47 | [5 empty] | 72.76 |  |  | 84.74 |  |  |  | 7.64 |  | 6.82 | [8 empty] | 10.70 |  |  |  |  | 0.14
2005 |  |  |  | 5595.37 |  |  | 7287 |  |  |  | 905 | [10 empty] | 76.52 |  |  |  | 79.10 | [5 empty] | 70.58 |  |  | 83.18 |  |  |  | 7.97 |  | 6.85 | [8 empty] | 14.05 |  |  |  |  | 2.58
2006 |  |  |  | 6369.75 |  |  | 7930 |  |  |  | 905 | [10 empty] | 86.29 |  |  |  | 89.00 | [5 empty] | 80.35 |  |  | 90.53 |  |  |  | 1.62 |  | 2.28 | [8 empty] | 8.72 |  |  |  |  | 2.71
2007 |  |  |  | 6061.29 |  |  | 7310 |  |  |  | 905 | [10 empty] | 77.89 |  |  |  | 80.19 | [5 empty] | 76.46 |  |  | 83.45 |  |  |  | 4.04 |  | 7.56 | [8 empty] | 12.25 |  |  |  |  | 2.30
2008 |  |  |  | 6498.11 |  |  | 7760 |  |  |  | 905 | [10 empty] | 82.30 |  |  |  | 83.51 | [5 empty] | 81.74 |  |  | 88.34 |  |  |  | 5.36 |  | 8.73 | [8 empty] | 7.76 |  |  |  |  | 1.21
2009 |  |  |  | 3433.46 |  |  | 4114 |  |  |  | 905 | [10 empty] | 43.40 |  |  |  | 52.08 | [5 empty] | 43.31 |  |  | 46.96 |  |  |  | 7.88 |  | 17.47 | [8 empty] | 30.45 |  |  |  |  | 8.68
2010 |  |  |  | 6488.82 |  |  | 7485 |  |  |  | 905 | [10 empty] | 82.45 |  |  |  | 82.48 | [5 empty] | 81.85 |  |  | 85.45 |  |  |  | 4.78 |  | 8.66 | [8 empty] | 8.87 |  |  |  |  | 0.03
2011 |  |  |  | 6043.83 |  |  | 6906 |  |  |  | 905 | [10 empty] | 77.58 |  |  |  | 77.78 | [5 empty] | 76.24 |  |  | 78.84 |  |  |  | 2.04 |  | 9.83 | [8 empty] | 12.40 |  |  |  |  | 0.20
2012 |  |  |  | 6770.53 |  |  | 7662 |  |  |  | 905 | [10 empty] | 85.87 |  |  |  | 88.39 | [5 empty] | 85.17 |  |  | 87.23 |  |  |  | 1.65 |  | 3.15 | [8 empty] | 8.46 |  |  |  |  | 2.52
2013 |  |  |  | 5930.23 |  |  | 6823 |  |  |  | 905 | [10 empty] | 75.27 |  |  |  | 76.20 | [5 empty] | 74.80 |  |  | 77.89 |  |  |  | 3.07 |  | 9.76 | [8 empty] | 14.04 |  |  |  |  | 0.93
2014 |  |  |  | 6733.16 |  |  | 7711 |  |  |  | 905 | [10 empty] | 86.59 |  |  |  | 87.34 | [5 empty] | 84.93 |  |  | 88.03 |  |  |  | 2.77 |  | 3.91 | [8 empty] | 8.75 |  |  |  |  | 0.75
2015 |  |  |  | 5735.52 |  |  | 6515 |  |  |  | 905 | [10 empty] | 72.75 |  |  |  | 73.26 | [5 empty] | 72.35 |  |  | 74.37 |  |  |  | 0.72 |  | 10.27 | [8 empty] | 16.47 |  |  |  |  | 0.51
2016 |  |  |  | 6806.55 |  |  | 7949 |  |  |  | 905 | [10 empty] | 87.43 |  |  |  | 88.25 | [5 empty] | 85.62 |  |  | 90.49 |  |  |  | 1.28 |  | 3.19 | [8 empty] | 8.56 |  |  |  |  | 0.82
2017 |  |  |  | 6070.41 |  |  | 7079 |  |  |  | 905 | [10 empty] | 78.88 |  |  |  | 79.62 | [5 empty] | 76.57 |  |  | 80.81 |  |  |  | 0.51 |  | 3.70 | [8 empty] | 16.68 |  |  |  |  | 0.74
2018 |  |  |  | 6593.67 |  |  | 7668 |  |  |  | 905 | [10 empty] | 84.70 |  |  |  | 85.60 | [5 empty] | 83.17 |  |  | 87.53 |  |  |  | 3.35 |  | 5.09 | [8 empty] | 9.31 |  |  |  |  | 0.90
2019 |  |  |  | 4795.66 |  |  | 5526 |  |  |  | 905 | [10 empty] | 62.11 |  |  |  | 63.02 | [5 empty] | 60.49 |  |  | 63.08 |  |  |  | 2.45 |  | 5.42 | [8 empty] | 31.56 |  |  |  |  | 0.91
2020 |  |  |  | 4848.50 |  |  | 6047 |  |  |  | 905 | [10 empty] | 67.51 |  |  |  | 70.38 | [5 empty] | 60.99 |  |  | 68.84 |  |  |  | 4.24 |  | 28.45 | [8 empty] | 1.17 |  |  |  |  | 2.86
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 360
B. |  | Refuelling without maintenance | [35 empty] | 126
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 928 |  |  |  | 23
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 27
E. |  | Testing of plant systems or components | [35 empty] | 24 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 13
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 14
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 2 | [11 empty] | 30
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 8
Z. |  | Other | [39 empty] | 43
Subtotal | [37 empty] | 1105 |  |  |  | 464 | [11 empty] | 30
Total | [22 empty] | 0 | [14 empty] | 1599
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 25
12. |  |  | Reactor I&C Systems | [34 empty] | 10
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 35
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 24
16. |  |  | Steam generation systems | [34 empty] | 20
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 21
31. |  |  | Turbine and auxiliaries | [34 empty] | 64
32. |  |  | Feedwater and Main Steam System | [34 empty] | 29
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 87
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 30
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [37 empty] | 362

## CHINON B-4
2020 Operating Experience
FR-57 | [8 empty] | CHINON B-4 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP2 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-02-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-11-14
Gross electrical power | [12 empty] | : |  |  | 954 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-04-01
Reference unit power (net) | [12 empty] | : |  |  | 905 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 38 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3089.77 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.21 %
Energy Availability Factor (EAF) | [18 empty] | : | 39.76 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 18.66 %
Unit Capability Factor (UCF) | [18 empty] | : | 41.33 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 40.01 %
Load Factor (LF) | [18 empty] | : | 38.87 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.57 %
Operating Factor (OF) | [18 empty] | : | 40.79 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 5201 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 644.53 | 593.24 |  |  |  | 660.28 |  | 611.90 | [8 empty] | 579.81 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3089.77
EAF [%] |  |  |  |  | 96.01 | 95.52 |  |  |  | 98.80 |  | 98.90 | [8 empty] | 89.59 |  |  | 0.03 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.01 |  |  | 0.04 | [9 empty] | 0.04 |  |  | 39.76
UCF [%] |  |  |  |  | 99.83 | 99.79 |  |  |  | 99.31 |  | 99.46 | [8 empty] | 93.43 |  |  | 0.03 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 5.78 |  |  | 0.04 | [9 empty] | 0.04 |  |  | 41.33
LF [%] |  |  |  |  | 95.72 | 94.18 |  |  |  | 98.20 |  | 93.91 | [8 empty] | 86.11 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 38.87
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 91.40 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 40.79
FLR [%] |  |  |  |  | 0.10 | 0.11 |  |  |  | 0.34 |  | 0.47 | [8 empty] | 0.03 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.21
UCL [%] |  |  |  |  | 0.10 | 0.11 |  |  |  | 0.34 |  | 0.47 | [8 empty] | 0.03 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 42.68 |  |  | 99.96 | [9 empty] | 79.82 |  |  | 18.66
PUF [%] |  |  |  |  | 0.07 | 0.10 |  |  |  | 0.35 |  | 0.07 | [8 empty] | 6.54 |  |  | 99.97 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 51.54 |  |  | 0.00 | [9 empty] | 20.13 |  |  | 40.01
XUF [%] |  |  |  |  | 3.82 | 4.27 |  |  |  | 0.52 |  | 0.57 | [8 empty] | 3.83 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 5.77 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.57
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 194246.41 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.67 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.22 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.5 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.93 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.21 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 4410.00 |  |  | 5897 |  |  |  | 905 | [10 empty] | 86.17 |  |  |  | 89.04 | [5 empty] | 56.36 |  |  | 67.79 |  |  |  | 10.96 |  | 10.96 | [8 empty] | 0.00 |  |  |  |  | 2.86
1989 |  |  |  | 4688.12 |  |  | 5664 |  |  |  | 905 | [10 empty] | 60.39 |  |  |  | 63.58 | [5 empty] | 59.14 |  |  | 64.66 |  |  |  | 13.81 |  | 10.18 | [8 empty] | 26.24 |  |  |  |  | 3.19
1990 |  |  |  | 6098.01 |  |  | 7003 |  |  |  | 905 | [10 empty] | 77.01 |  |  |  | 77.22 | [5 empty] | 76.92 |  |  | 79.94 |  |  |  | 11.20 |  | 9.74 | [8 empty] | 13.04 |  |  |  |  | 0.21
1991 |  |  |  | 6339.97 |  |  | 7204 |  |  |  | 905 | [10 empty] | 79.24 |  |  |  | 79.96 | [5 empty] | 79.97 |  |  | 82.24 |  |  |  | 7.12 |  | 6.13 | [8 empty] | 13.91 |  |  |  |  | 0.71
1992 |  |  |  | 6387.95 |  |  | 7544 |  |  |  | 905 | [10 empty] | 82.80 |  |  |  | 85.03 | [5 empty] | 80.36 |  |  | 85.88 |  |  |  | 0.66 |  | 0.56 | [8 empty] | 14.40 |  |  |  |  | 2.23
1993 |  |  |  | 6016.91 |  |  | 7359 |  |  |  | 905 | [10 empty] | 80.12 |  |  |  | 85.77 | [5 empty] | 75.90 |  |  | 84.01 |  |  |  | 3.60 |  | 3.20 | [8 empty] | 11.03 |  |  |  |  | 5.65
1994 |  |  |  | 5935.09 |  |  | 7196 |  |  |  | 905 | [10 empty] | 81.25 |  |  |  | 82.44 | [5 empty] | 74.86 |  |  | 82.15 |  |  |  | 2.73 |  | 2.31 | [8 empty] | 15.25 |  |  |  |  | 1.19
1995 |  |  |  | 6566.02 |  |  | 7805 |  |  |  | 905 | [10 empty] | 87.88 |  |  |  | 88.17 | [5 empty] | 82.82 |  |  | 89.10 |  |  |  | 1.73 |  | 1.55 | [8 empty] | 10.28 |  |  |  |  | 0.29
1996 |  |  |  | 6574.24 |  |  | 7764 |  |  |  | 905 | [10 empty] | 87.03 |  |  |  | 87.64 | [5 empty] | 82.70 |  |  | 88.39 |  |  |  | 1.90 |  | 1.70 | [8 empty] | 10.66 |  |  |  |  | 0.61
1997 |  |  |  | 6345.37 |  |  | 7795 |  |  |  | 905 | [10 empty] | 85.64 |  |  |  | 88.73 | [5 empty] | 80.04 |  |  | 88.98 |  |  |  | 1.09 |  | 0.98 | [8 empty] | 10.29 |  |  |  |  | 3.09
1998 |  |  |  | 5940.13 |  |  | 7326 |  |  |  | 905 | [10 empty] | 80.18 |  |  |  | 83.14 | [5 empty] | 74.93 |  |  | 83.63 |  |  |  | 2.98 |  | 2.56 | [8 empty] | 14.31 |  |  |  |  | 2.96
1999 |  |  |  | 5596.27 |  |  | 7059 |  |  |  | 905 | [10 empty] | 88.17 |  |  |  | 89.89 | [5 empty] | 70.59 |  |  | 80.58 |  |  |  | 9.99 |  | 9.98 | [8 empty] | 0.13 |  |  |  |  | 1.72
2000 |  |  |  | 5110.70 |  |  | 6445 |  |  |  | 905 | [10 empty] | 72.91 |  |  |  | 74.09 | [5 empty] | 64.29 |  |  | 73.37 |  |  |  | 5.72 |  | 4.49 | [8 empty] | 21.42 |  |  |  |  | 1.18
2001 |  |  |  | 5764.99 |  |  | 7078 |  |  |  | 905 | [10 empty] | 79.91 |  |  |  | 81.33 | [5 empty] | 72.72 |  |  | 80.80 |  |  |  | 10.39 |  | 9.43 | [8 empty] | 9.24 |  |  |  |  | 1.42
2002 |  |  |  | 6321.31 |  |  | 7584 |  |  |  | 905 | [10 empty] | 84.03 |  |  |  | 85.53 | [5 empty] | 79.74 |  |  | 86.58 |  |  |  | 2.58 |  | 2.27 | [8 empty] | 12.20 |  |  |  |  | 1.50
2003 |  |  |  | 6431.76 |  |  | 7811 |  |  |  | 905 | [10 empty] | 86.62 |  |  |  | 87.71 | [5 empty] | 81.13 |  |  | 89.17 |  |  |  | 3.61 |  | 3.29 | [8 empty] | 9.00 |  |  |  |  | 1.10
2004 |  |  |  | 5513.22 |  |  | 6883 |  |  |  | 905 | [10 empty] | 74.88 |  |  |  | 75.12 | [5 empty] | 69.35 |  |  | 78.36 |  |  |  | 13.19 |  | 11.41 | [8 empty] | 13.47 |  |  |  |  | 0.24
2005 |  |  |  | 5356.45 |  |  | 7030 |  |  |  | 905 | [10 empty] | 69.72 |  |  |  | 71.15 | [5 empty] | 67.57 |  |  | 80.25 |  |  |  | 19.49 |  | 17.23 | [8 empty] | 11.63 |  |  |  |  | 1.43
2006 |  |  |  | 6368.95 |  |  | 7558 |  |  |  | 905 | [10 empty] | 83.27 |  |  |  | 84.36 | [5 empty] | 80.34 |  |  | 86.28 |  |  |  | 0.89 |  | 1.15 | [8 empty] | 14.48 |  |  |  |  | 1.09
2007 |  |  |  | 6485.73 |  |  | 7691 |  |  |  | 905 | [10 empty] | 84.82 |  |  |  | 86.11 | [5 empty] | 81.81 |  |  | 87.80 |  |  |  | 2.22 |  | 6.15 | [8 empty] | 7.74 |  |  |  |  | 1.29
2008 |  |  |  | 5863.53 |  |  | 6881 |  |  |  | 905 | [10 empty] | 75.65 |  |  |  | 77.15 | [5 empty] | 73.76 |  |  | 78.34 |  |  |  | 0.74 |  | 3.33 | [8 empty] | 19.52 |  |  |  |  | 1.50
2009 |  |  |  | 5250.85 |  |  | 6232 |  |  |  | 905 | [10 empty] | 67.43 |  |  |  | 85.76 | [5 empty] | 66.23 |  |  | 71.14 |  |  |  | 4.16 |  | 6.30 | [8 empty] | 7.94 |  |  |  |  | 18.33
2010 |  |  |  | 4302.57 |  |  | 4902 |  |  |  | 905 | [10 empty] | 54.34 |  |  |  | 54.98 | [5 empty] | 54.27 |  |  | 55.96 |  |  |  | 1.78 |  | 21.24 | [8 empty] | 23.78 |  |  |  |  | 0.64
2011 |  |  |  | 6790.85 |  |  | 7868 |  |  |  | 905 | [10 empty] | 86.40 |  |  |  | 86.81 | [5 empty] | 85.66 |  |  | 89.82 |  |  |  | 3.56 |  | 5.85 | [8 empty] | 7.34 |  |  |  |  | 0.42
2012 |  |  |  | 6125.00 |  |  | 6958 |  |  |  | 905 | [10 empty] | 77.51 |  |  |  | 77.81 | [5 empty] | 77.05 |  |  | 79.21 |  |  |  | 1.15 |  | 7.80 | [8 empty] | 14.38 |  |  |  |  | 0.31
2013 |  |  |  | 6660.90 |  |  | 7573 |  |  |  | 905 | [10 empty] | 84.94 |  |  |  | 85.68 | [5 empty] | 84.02 |  |  | 86.45 |  |  |  | 1.50 |  | 4.93 | [8 empty] | 9.39 |  |  |  |  | 0.74
2014 |  |  |  | 6071.89 |  |  | 7092 |  |  |  | 905 | [10 empty] | 78.89 |  |  |  | 80.42 | [5 empty] | 76.59 |  |  | 80.96 |  |  |  | 0.30 |  | 0.24 | [8 empty] | 19.34 |  |  |  |  | 1.53
2015 |  |  |  | 6944.68 |  |  | 7944 |  |  |  | 905 | [10 empty] | 88.88 |  |  |  | 89.44 | [5 empty] | 87.60 |  |  | 90.68 |  |  |  | 2.37 |  | 2.18 | [8 empty] | 8.38 |  |  |  |  | 0.56
2016 |  |  |  | 6037.90 |  |  | 7119 |  |  |  | 905 | [10 empty] | 76.24 |  |  |  | 77.46 | [5 empty] | 75.95 |  |  | 81.05 |  |  |  | 0.45 |  | 5.88 | [8 empty] | 16.66 |  |  |  |  | 1.22
2017 |  |  |  | 6630.00 |  |  | 7624 |  |  |  | 905 | [10 empty] | 85.17 |  |  |  | 85.78 | [5 empty] | 83.63 |  |  | 87.03 |  |  |  | 4.57 |  | 4.90 | [8 empty] | 9.31 |  |  |  |  | 0.61
2018 |  |  |  | 5530.08 |  |  | 6388 |  |  |  | 905 | [10 empty] | 71.13 |  |  |  | 72.10 | [5 empty] | 69.76 |  |  | 72.92 |  |  |  | 2.86 |  | 10.34 | [8 empty] | 17.56 |  |  |  |  | 0.97
2019 |  |  |  | 6839.72 |  |  | 7843 |  |  |  | 905 | [10 empty] | 86.97 |  |  |  | 88.70 | [5 empty] | 86.28 |  |  | 89.53 |  |  |  | 0.94 |  | 1.64 | [8 empty] | 9.67 |  |  |  |  | 1.72
2020 |  |  |  | 3089.77 |  |  | 3583 |  |  |  | 905 | [10 empty] | 39.76 |  |  |  | 41.33 | [5 empty] | 38.87 |  |  | 40.79 |  |  |  | 0.21 |  | 18.66 | [8 empty] | 40.01 |  |  |  |  | 1.57
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 338
B. |  | Refuelling without maintenance | [35 empty] | 132
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 872 |  |  |  | 12
E. |  | Testing of plant systems or components | [35 empty] | 20
H. |  | Nuclear regulatory requirements | [39 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 4
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 6 | [11 empty] | 50
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 8 | [11 empty] | 1
Z. |  | Other | [39 empty] | 36 | [11 empty] | 15
Subtotal | [37 empty] | 1024 |  |  |  | 405 | [11 empty] | 70
Total | [22 empty] | 0 | [14 empty] | 1499
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 48
12. |  |  | Reactor I&C Systems | [34 empty] | 16
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 28
14. |  |  | Safety Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 40
16. |  |  | Steam generation systems | [34 empty] | 10
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 15
31. |  |  | Turbine and auxiliaries | [34 empty] | 40
32. |  |  | Feedwater and Main Steam System | [34 empty] | 12
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 60
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 28
42. |  |  | Electrical Power Supply Systems | [34 empty] | 24
Total | [37 empty] | 336

## CHOOZ B-1
2020 Operating Experience
FR-62 | [8 empty] | CHOOZ B-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | FRAM (FRAMATOME)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / N4 REP 1450 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-01-01
Thermal power | [12 empty] | : |  |  | 4270 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1996-08-30
Gross electrical power | [12 empty] | : |  |  | 1560 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2000-05-15
Reference unit power (net) | [12 empty] | : |  |  | 1500 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 24 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.3
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 39000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.47 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.1
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 205 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.92 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 25 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4440.81 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 9.13 %
Energy Availability Factor (EAF) | [18 empty] | : | 33.73 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 8.19 %
Unit Capability Factor (UCF) | [18 empty] | : | 51.27 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 40.54 %
Load Factor (LF) | [18 empty] | : | 33.7 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 17.54 %
Operating Factor (OF) | [18 empty] | : | 36.48 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 5580 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1029.55 | 618.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 116.55 |  |  |  | 88.21 |  |  | 1079.14 |  |  | 1054.11 | [9 empty] | 454.55 |  |  | 4440.81
EAF [%] |  |  |  |  | 92.27 | 59.30 |  |  |  | 0.07 |  | 0.04 | [8 empty] | 0.05 |  |  | 0.07 | [6 empty] | 0.04 |  | 10.48 |  |  |  | 8.25 |  |  | 96.56 |  |  | 97.57 | [9 empty] | 40.64 |  |  | 33.73
UCF [%] |  |  |  |  | 99.93 | 71.67 |  |  |  | 0.07 |  | 0.04 | [8 empty] | 0.05 |  |  | 0.07 | [6 empty] | 48.42 |  | 58.06 |  |  |  | 99.63 |  |  | 99.12 |  |  | 98.54 | [9 empty] | 40.66 |  |  | 51.27
LF [%] |  |  |  |  | 92.25 | 59.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 10.44 |  |  |  | 8.17 |  |  | 96.57 |  |  | 97.60 | [9 empty] | 40.73 |  |  | 33.70
OF [%] |  |  |  |  | 100.00 | 72.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 16.67 |  |  |  | 9.17 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 40.86 |  |  | 36.48
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.19 |  |  | 1.35 | [9 empty] | 59.33 |  |  | 9.13
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 35.85 |  |  |  | 0.00 |  |  | 0.19 |  |  | 1.35 | [9 empty] | 59.33 |  |  | 8.19
PUF [%] |  |  |  |  | 0.07 | 28.33 |  |  |  | 99.93 |  | 99.96 | [8 empty] | 99.95 |  |  | 99.93 | [6 empty] | 51.58 |  | 6.09 |  |  |  | 0.37 |  |  | 0.69 |  |  | 0.12 | [9 empty] | 0.00 |  |  | 40.54
XUF [%] |  |  |  |  | 7.66 | 12.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 48.38 |  | 47.58 |  |  |  | 91.38 |  |  | 2.56 |  |  | 0.96 | [9 empty] | 0.02 |  |  | 17.54
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 216776.86 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.09 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.02 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.73 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.12 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.69 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.1 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.48 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2000 |  |  |  | 8429.16 |  |  | 5877 |  |  |  | 1455 | [10 empty] | 96.94 |  |  |  | 96.94 | [5 empty] | 98.43 |  |  | 97.13 |  |  |  | 1.64 |  | 1.62 | [8 empty] | 1.43 |  |  |  |  | 0.00
2001 |  |  |  | 9524.35 |  |  | 6800 |  |  |  | 1455 | [10 empty] | 75.00 |  |  |  | 78.03 | [5 empty] | 74.73 |  |  | 77.63 |  |  |  | 6.98 |  | 5.85 | [8 empty] | 16.11 |  |  |  |  | 3.03
2002 |  |  |  | 9515.08 |  |  | 6807 |  |  |  | 1455 | [10 empty] | 80.96 |  |  |  | 82.39 | [5 empty] | 74.65 |  |  | 77.71 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 17.54 |  |  |  |  | 1.43
2003 |  |  |  | 10021.89 |  |  | 7219 |  |  |  | 1500 | [10 empty] | 85.61 |  |  |  | 89.41 | [5 empty] | 76.27 |  |  | 82.41 |  |  |  | 0.76 |  | 0.68 | [8 empty] | 9.91 |  |  |  |  | 3.79
2004 |  |  |  | 10671.09 |  |  | 7657 |  |  |  | 1500 | [10 empty] | 83.59 |  |  |  | 86.67 | [5 empty] | 80.99 |  |  | 87.17 |  |  |  | 4.38 |  | 3.97 | [8 empty] | 9.36 |  |  |  |  | 3.08
2005 |  |  |  | 9047.67 |  |  | 6285 |  |  |  | 1500 | [10 empty] | 69.59 |  |  |  | 70.47 | [5 empty] | 68.85 |  |  | 71.74 |  |  |  | 14.26 |  | 13.36 | [8 empty] | 16.17 |  |  |  |  | 0.88
2006 |  |  |  | 9845.73 |  |  | 6885 |  |  |  | 1500 | [10 empty] | 75.64 |  |  |  | 77.56 | [5 empty] | 74.93 |  |  | 78.60 |  |  |  | 2.14 |  | 3.95 | [8 empty] | 18.49 |  |  |  |  | 1.92
2007 |  |  |  | 10402.28 |  |  | 7154 |  |  |  | 1500 | [10 empty] | 79.60 |  |  |  | 80.70 | [5 empty] | 79.16 |  |  | 81.67 |  |  |  | 0.33 |  | 10.12 | [8 empty] | 9.18 |  |  |  |  | 1.10
2008 |  |  |  | 12376.75 |  |  | 8572 |  |  |  | 1500 | [10 empty] | 95.03 |  |  |  | 97.01 | [5 empty] | 93.93 |  |  | 97.59 |  |  |  | 2.98 |  | 2.98 | [8 empty] | 0.01 |  |  |  |  | 1.98
2009 |  |  |  | 8649.52 |  |  | 6307 |  |  |  | 1500 | [10 empty] | 67.49 |  |  |  | 68.96 | [5 empty] | 65.83 |  |  | 72.00 |  |  |  | 5.83 |  | 18.93 | [8 empty] | 12.11 |  |  |  |  | 1.47
2010 |  |  |  | 8663.04 |  |  | 5962 |  |  |  | 1500 | [10 empty] | 65.89 |  |  |  | 65.98 | [5 empty] | 65.93 |  |  | 68.06 |  |  |  | 3.16 |  | 3.94 | [8 empty] | 30.09 |  |  |  |  | 0.09
2011 |  |  |  | 10285.74 |  |  | 7044 |  |  |  | 1500 | [10 empty] | 79.66 |  |  |  | 81.08 | [5 empty] | 78.28 |  |  | 80.41 |  |  |  | 0.75 |  | 2.02 | [8 empty] | 16.90 |  |  |  |  | 1.43
2012 |  |  |  | 12512.93 |  |  | 8496 |  |  |  | 1500 | [10 empty] | 96.49 |  |  |  | 97.16 | [5 empty] | 94.97 |  |  | 96.72 |  |  |  | 2.82 |  | 2.82 | [8 empty] | 0.02 |  |  |  |  | 0.67
2013 |  |  |  | 10034.78 |  |  | 6905 |  |  |  | 1500 | [10 empty] | 78.25 |  |  |  | 78.86 | [5 empty] | 76.37 |  |  | 78.82 |  |  |  | 0.91 |  | 2.49 | [8 empty] | 18.65 |  |  |  |  | 0.62
2014 |  |  |  | 8950.47 |  |  | 6279 |  |  |  | 1500 | [10 empty] | 71.66 |  |  |  | 72.24 | [5 empty] | 68.12 |  |  | 71.68 |  |  |  | 0.49 |  | 0.35 | [8 empty] | 27.40 |  |  |  |  | 0.58
2015 |  |  |  | 11334.11 |  |  | 7835 |  |  |  | 1500 | [10 empty] | 88.55 |  |  |  | 89.52 | [5 empty] | 86.26 |  |  | 89.44 |  |  |  | 0.13 |  | 0.94 | [8 empty] | 9.55 |  |  |  |  | 0.97
2016 |  |  |  | 11392.17 |  |  | 8671 |  |  |  | 1500 | [10 empty] | 94.26 |  |  |  | 99.16 | [5 empty] | 86.46 |  |  | 98.71 |  |  |  | 0.26 |  | 0.25 | [8 empty] | 0.58 |  |  |  |  | 4.90
2017 |  |  |  | 8172.98 |  |  | 5760 |  |  |  | 1500 | [10 empty] | 63.27 |  |  |  | 66.99 | [5 empty] | 62.20 |  |  | 65.75 |  |  |  | 9.41 |  | 14.03 | [8 empty] | 18.97 |  |  |  |  | 3.72
2018 |  |  |  | 9526.45 |  |  | 6522 |  |  |  | 1500 | [10 empty] | 73.38 |  |  |  | 79.46 | [5 empty] | 72.50 |  |  | 74.45 |  |  |  | 0.81 |  | 0.65 | [8 empty] | 19.89 |  |  |  |  | 6.08
2019 |  |  |  | 11128.09 |  |  | 7952 |  |  |  | 1500 | [10 empty] | 90.33 |  |  |  | 98.97 | [5 empty] | 84.69 |  |  | 90.78 |  |  |  | 1.01 |  | 1.01 | [8 empty] | 0.02 |  |  |  |  | 8.64
2020 |  |  |  | 4440.81 |  |  | 3204 |  |  |  | 1500 | [10 empty] | 33.73 |  |  |  | 51.27 | [5 empty] | 33.70 |  |  | 36.48 |  |  |  | 9.13 |  | 8.19 | [8 empty] | 40.54 |  |  |  |  | 17.54
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2000 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 637
B. |  | Refuelling without maintenance | [35 empty] | 261
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 693
E. |  | Testing of plant systems or components | [35 empty] | 91
H. |  | Nuclear regulatory requirements | [39 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 10
L. |  | Human factor related | [39 empty] | 53
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 34
O. |  | Load dispatching, prioritization | [51 empty] | 12
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 24
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 50
Z. |  | Other | [39 empty] | 86
Subtotal | [37 empty] | 1045 |  |  |  | 777 | [11 empty] | 130
Total | [22 empty] | 0 | [14 empty] | 1952
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2000 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 40
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 37
16. |  |  | Steam generation systems | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 309
32. |  |  | Feedwater and Main Steam System | [34 empty] | 18
34. |  |  | Miscellaneous Systems | [34 empty] | 60
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 62
Total | [37 empty] | 551

## CHOOZ B-2
2020 Operating Experience
FR-70 | [8 empty] | CHOOZ B-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | FRAM (FRAMATOME)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / N4 REP 1450 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-12-31
Thermal power | [12 empty] | : |  |  | 4270 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1997-04-10
Gross electrical power | [12 empty] | : |  |  | 1560 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2000-09-29
Reference unit power (net) | [12 empty] | : |  |  | 1500 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 23 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.3
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 39000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.47 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.1
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 205 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.92 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 25 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8328.39 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.31 %
Energy Availability Factor (EAF) | [18 empty] | : | 70.01 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.31 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.67 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.02 %
Load Factor (LF) | [18 empty] | : | 63.21 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 29.66 %
Operating Factor (OF) | [18 empty] | : | 69.49 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2680 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1080.02 | 843.06 |  |  |  | 972.84 |  | 462.63 | [8 empty] | 0.00 |  |  | 330.68 | [6 empty] | 954.68 |  | 647.68 |  |  |  | 0.00 |  |  | 923.56 |  |  | 1013.25 | [9 empty] | 1099.96 |  |  | 8328.39
EAF [%] |  |  |  |  | 99.87 | 95.84 |  |  |  | 99.93 |  | 60.17 | [8 empty] | 0.06 |  |  | 37.62 | [6 empty] | 99.38 |  | 60.31 |  |  |  | 0.06 |  |  | 87.04 |  |  | 99.75 | [9 empty] | 99.14 |  |  | 70.01
UCF [%] |  |  |  |  | 99.99 | 96.08 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 99.97 |  | 100.00 |  |  |  | 100.00 |  |  | 99.90 |  |  | 99.89 | [9 empty] | 99.98 |  |  | 99.67
LF [%] |  |  |  |  | 96.78 | 80.75 |  |  |  | 87.29 |  | 42.84 | [8 empty] | 0.00 |  |  | 30.62 | [6 empty] | 85.54 |  | 58.04 |  |  |  | 0.00 |  |  | 82.65 |  |  | 93.82 | [9 empty] | 98.56 |  |  | 63.21
OF [%] |  |  |  |  | 100.00 | 96.41 |  |  |  | 100.00 |  | 47.50 | [8 empty] | 0.00 |  |  | 34.44 | [6 empty] | 100.00 |  | 64.65 |  |  |  | 0.00 |  |  | 89.53 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 69.49
FLR [%] |  |  |  |  | 0.00 | 3.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.31
UCL [%] |  |  |  |  | 0.00 | 3.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.31
PUF [%] |  |  |  |  | 0.01 | 0.01 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.03 |  | 0.00 |  |  |  | 0.00 |  |  | 0.10 |  |  | 0.11 | [9 empty] | 0.02 |  |  | 0.02
XUF [%] |  |  |  |  | 0.12 | 0.24 |  |  |  | 0.06 |  | 39.83 | [8 empty] | 99.94 |  |  | 62.37 | [6 empty] | 0.60 |  | 39.69 |  |  |  | 99.94 |  |  | 12.86 |  |  | 0.14 | [9 empty] | 0.84 |  |  | 29.66
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 213805.76 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.78 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.91 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.68 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.48 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.84 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.19 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 5.57 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.48 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2000 |  |  |  | 7213.35 |  |  | 5347 |  |  |  | 1455 | [10 empty] | 90.19 |  |  |  | 90.26 | [5 empty] | 92.15 |  |  | 94.70 |  |  |  | 9.74 |  | 9.74 | [8 empty] | 0.00 |  |  |  |  | 0.06
2001 |  |  |  | 10159.53 |  |  | 7221 |  |  |  | 1455 | [10 empty] | 80.36 |  |  |  | 83.42 | [5 empty] | 79.71 |  |  | 82.43 |  |  |  | 0.36 |  | 0.30 | [8 empty] | 16.28 |  |  |  |  | 3.06
2002 |  |  |  | 9814.83 |  |  | 7240 |  |  |  | 1455 | [10 empty] | 81.50 |  |  |  | 83.02 | [5 empty] | 77.00 |  |  | 82.65 |  |  |  | 0.48 |  | 0.40 | [8 empty] | 16.58 |  |  |  |  | 1.52
2003 |  |  |  | 10472.75 |  |  | 7457 |  |  |  | 1500 | [10 empty] | 83.30 |  |  |  | 87.64 | [5 empty] | 79.70 |  |  | 85.13 |  |  |  | 2.38 |  | 2.13 | [8 empty] | 10.23 |  |  |  |  | 4.34
2004 |  |  |  | 10063.94 |  |  | 7061 |  |  |  | 1500 | [10 empty] | 80.12 |  |  |  | 88.00 | [5 empty] | 76.38 |  |  | 80.38 |  |  |  | 3.42 |  | 3.12 | [8 empty] | 8.88 |  |  |  |  | 7.88
2005 |  |  |  | 10321.55 |  |  | 7343 |  |  |  | 1500 | [10 empty] | 81.65 |  |  |  | 84.06 | [5 empty] | 78.55 |  |  | 83.82 |  |  |  | 1.24 |  | 3.23 | [8 empty] | 12.71 |  |  |  |  | 2.41
2006 |  |  |  | 9460.52 |  |  | 6845 |  |  |  | 1500 | [10 empty] | 79.64 |  |  |  | 81.55 | [5 empty] | 72.00 |  |  | 78.14 |  |  |  | 1.94 |  | 2.91 | [8 empty] | 15.53 |  |  |  |  | 1.91
2007 |  |  |  | 11016.49 |  |  | 7725 |  |  |  | 1500 | [10 empty] | 85.23 |  |  |  | 86.78 | [5 empty] | 83.84 |  |  | 88.18 |  |  |  | 3.20 |  | 4.71 | [8 empty] | 8.50 |  |  |  |  | 1.55
2008 |  |  |  | 11038.88 |  |  | 7639 |  |  |  | 1500 | [10 empty] | 84.56 |  |  |  | 86.12 | [5 empty] | 83.78 |  |  | 86.96 |  |  |  | 1.19 |  | 1.44 | [8 empty] | 12.43 |  |  |  |  | 1.56
2009 |  |  |  | 7821.91 |  |  | 5593 |  |  |  | 1500 | [10 empty] | 62.48 |  |  |  | 66.03 | [5 empty] | 59.53 |  |  | 63.85 |  |  |  | 0.32 |  | 7.57 | [8 empty] | 26.40 |  |  |  |  | 3.55
2010 |  |  |  | 10739.75 |  |  | 7529 |  |  |  | 1500 | [10 empty] | 83.38 |  |  |  | 86.09 | [5 empty] | 81.73 |  |  | 85.95 |  |  |  | 2.02 |  | 4.45 | [8 empty] | 9.47 |  |  |  |  | 2.71
2011 |  |  |  | 11507.74 |  |  | 8076 |  |  |  | 1500 | [10 empty] | 91.22 |  |  |  | 95.24 | [5 empty] | 87.58 |  |  | 92.19 |  |  |  | 4.75 |  | 4.75 | [8 empty] | 0.01 |  |  |  |  | 4.03
2012 |  |  |  | 5773.74 |  |  | 4092 |  |  |  | 1500 | [10 empty] | 44.03 |  |  |  | 73.66 | [5 empty] | 43.82 |  |  | 46.58 |  |  |  | 0.02 |  | 6.71 | [8 empty] | 19.62 |  |  |  |  | 29.63
2013 |  |  |  | 10676.71 |  |  | 7351 |  |  |  | 1500 | [10 empty] | 82.43 |  |  |  | 84.44 | [5 empty] | 81.25 |  |  | 83.92 |  |  |  | 0.26 |  | 4.75 | [8 empty] | 10.81 |  |  |  |  | 2.02
2014 |  |  |  | 12405.66 |  |  | 8686 |  |  |  | 1500 | [10 empty] | 98.02 |  |  |  | 99.71 | [5 empty] | 94.41 |  |  | 99.16 |  |  |  | 0.27 |  | 0.27 | [8 empty] | 0.02 |  |  |  |  | 1.69
2015 |  |  |  | 9504.22 |  |  | 6673 |  |  |  | 1500 | [10 empty] | 74.11 |  |  |  | 75.67 | [5 empty] | 72.33 |  |  | 76.18 |  |  |  | 0.82 |  | 0.63 | [8 empty] | 23.71 |  |  |  |  | 1.56
2016 |  |  |  | 11021.73 |  |  | 7791 |  |  |  | 1500 | [10 empty] | 85.63 |  |  |  | 87.54 | [5 empty] | 83.65 |  |  | 88.70 |  |  |  | 1.48 |  | 1.32 | [8 empty] | 11.14 |  |  |  |  | 1.91
2017 |  |  |  | 7691.34 |  |  | 5351 |  |  |  | 1500 | [10 empty] | 59.82 |  |  |  | 64.05 | [5 empty] | 58.53 |  |  | 61.08 |  |  |  | 2.81 |  | 16.49 | [8 empty] | 19.46 |  |  |  |  | 4.23
2018 |  |  |  | 12031.86 |  |  | 8388 |  |  |  | 1500 | [10 empty] | 94.16 |  |  |  | 95.17 | [5 empty] | 91.57 |  |  | 95.75 |  |  |  | 4.23 |  | 4.21 | [8 empty] | 0.62 |  |  |  |  | 1.02
2019 |  |  |  | 6757.53 |  |  | 4846 |  |  |  | 1500 | [10 empty] | 53.76 |  |  |  | 60.05 | [5 empty] | 51.43 |  |  | 55.32 |  |  |  | 0.17 |  | 2.23 | [8 empty] | 37.72 |  |  |  |  | 6.29
2020 |  |  |  | 8328.39 |  |  | 6104 |  |  |  | 1500 | [10 empty] | 70.01 |  |  |  | 99.67 | [5 empty] | 63.21 |  |  | 69.49 |  |  |  | 0.31 |  | 0.31 | [8 empty] | 0.02 |  |  |  |  | 29.66
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2000 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 709
B. |  | Refuelling without maintenance | [35 empty] | 157
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 847
E. |  | Testing of plant systems or components | [35 empty] | 79 |  |  |  | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 45
L. |  | Human factor related | [39 empty] | 17
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 24
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 12 | [11 empty] | 153
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 6
Z. |  | Other | [39 empty] | 49
Subtotal | [37 empty] | 1083 |  |  |  | 787 | [11 empty] | 229
Total | [22 empty] | 0 | [14 empty] | 2099
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2000 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 51
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 29
14. |  |  | Safety Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 16
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [34 empty] | 305
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
33. |  |  | Circulating Water System | [34 empty] | 25
34. |  |  | Miscellaneous Systems | [34 empty] | 119
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 12
42. |  |  | Electrical Power Supply Systems | [34 empty] | 16
Total | [37 empty] | 616

## CIVAUX-1
2020 Operating Experience
FR-72 | [8 empty] | CIVAUX-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / N4 REP 1450 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1988-10-15
Thermal power | [12 empty] | : |  |  | 4270 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1997-12-24
Gross electrical power | [12 empty] | : |  |  | 1561 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-01-29
Reference unit power (net) | [12 empty] | : |  |  | 1495 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 23 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.3
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 35000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.47 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.1
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 205 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5723.66 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.99 %
Energy Availability Factor (EAF) | [18 empty] | : | 43.72 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 13.2 %
Unit Capability Factor (UCF) | [18 empty] | : | 58.55 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 28.25 %
Load Factor (LF) | [18 empty] | : | 43.59 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 14.83 %
Operating Factor (OF) | [18 empty] | : | 45.81 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4760 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 804.97 | 864.54 |  |  |  | 396.97 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 419.72 |  |  | 1100.69 |  |  | 1072.86 | [9 empty] | 1063.90 |  |  | 5723.66
EAF [%] |  |  |  |  | 72.52 | 83.08 |  |  |  | 35.74 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 39.13 |  |  | 99.48 |  |  | 99.77 | [9 empty] | 96.22 |  |  | 43.72
UCF [%] |  |  |  |  | 90.07 | 89.64 |  |  |  | 41.39 |  | 0.00 | [8 empty] | 0.00 |  |  | 46.67 | [6 empty] | 100.00 |  | 0.00 |  |  |  | 39.21 |  |  | 99.83 |  |  | 99.95 | [9 empty] | 96.23 |  |  | 58.55
LF [%] |  |  |  |  | 72.37 | 83.09 |  |  |  | 35.74 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 38.99 |  |  | 98.83 |  |  | 99.67 | [9 empty] | 95.65 |  |  | 43.59
OF [%] |  |  |  |  | 73.52 | 91.09 |  |  |  | 42.13 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 46.39 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 98.39 |  |  | 45.81
FLR [%] |  |  |  |  | 0.04 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 7.58 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 3.76 |  |  | 0.99
UCL [%] |  |  |  |  | 0.04 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 100.00 |  |  |  | 53.79 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 3.76 |  |  | 13.20
PUF [%] |  |  |  |  | 9.89 | 10.36 |  |  |  | 58.61 |  | 100.00 | [8 empty] | 100.00 |  |  | 53.33 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 7.00 |  |  | 0.16 |  |  | 0.05 | [9 empty] | 0.01 |  |  | 28.25
XUF [%] |  |  |  |  | 17.55 | 6.55 |  |  |  | 5.65 |  | 0.00 | [8 empty] | 0.00 |  |  | 46.66 | [6 empty] | 100.00 |  | 0.00 |  |  |  | 0.08 |  |  | 0.34 |  |  | 0.18 | [9 empty] | 0.01 |  |  | 14.83
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 198830.86 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.88 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.91 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.89 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.82 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.3 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.11 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.9 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.27 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 9544.10 |  |  | 7331 |  |  |  | 1495 | [10 empty] | 82.62 |  |  |  | 83.86 | [5 empty] | 74.72 |  |  | 84.81 |  |  |  | 2.71 |  | 2.34 | [8 empty] | 13.81 |  |  |  |  | 1.24
2003 |  |  |  | 10932.08 |  |  | 7438 |  |  |  | 1495 | [10 empty] | 83.06 |  |  |  | 84.14 | [5 empty] | 83.48 |  |  | 84.91 |  |  |  | 2.86 |  | 2.48 | [8 empty] | 13.38 |  |  |  |  | 1.08
2004 |  |  |  | 11276.48 |  |  | 7816 |  |  |  | 1495 | [10 empty] | 86.91 |  |  |  | 87.98 | [5 empty] | 85.87 |  |  | 88.98 |  |  |  | 3.22 |  | 2.92 | [8 empty] | 9.09 |  |  |  |  | 1.08
2005 |  |  |  | 9672.34 |  |  | 6855 |  |  |  | 1495 | [10 empty] | 73.78 |  |  |  | 76.26 | [5 empty] | 73.85 |  |  | 78.24 |  |  |  | 4.10 |  | 8.59 | [8 empty] | 15.15 |  |  |  |  | 2.48
2006 |  |  |  | 10318.21 |  |  | 7189 |  |  |  | 1495 | [10 empty] | 79.29 |  |  |  | 80.93 | [5 empty] | 78.79 |  |  | 82.07 |  |  |  | 8.64 |  | 11.25 | [8 empty] | 7.82 |  |  |  |  | 1.64
2007 |  |  |  | 9031.53 |  |  | 6242 |  |  |  | 1495 | [10 empty] | 69.39 |  |  |  | 69.64 | [5 empty] | 68.96 |  |  | 71.25 |  |  |  | 15.77 |  | 15.12 | [8 empty] | 15.24 |  |  |  |  | 0.25
2008 |  |  |  | 9872.98 |  |  | 6967 |  |  |  | 1495 | [10 empty] | 76.04 |  |  |  | 77.04 | [5 empty] | 75.18 |  |  | 79.31 |  |  |  | 13.43 |  | 14.99 | [8 empty] | 7.97 |  |  |  |  | 1.00
2009 |  |  |  | 9494.39 |  |  | 6852 |  |  |  | 1495 | [10 empty] | 73.43 |  |  |  | 76.52 | [5 empty] | 72.50 |  |  | 78.22 |  |  |  | 9.45 |  | 10.84 | [8 empty] | 12.64 |  |  |  |  | 3.09
2010 |  |  |  | 10590.11 |  |  | 7582 |  |  |  | 1495 | [10 empty] | 81.45 |  |  |  | 81.98 | [5 empty] | 80.86 |  |  | 86.55 |  |  |  | 5.84 |  | 5.37 | [8 empty] | 12.65 |  |  |  |  | 0.53
2011 |  |  |  | 8663.88 |  |  | 6006 |  |  |  | 1495 | [10 empty] | 67.23 |  |  |  | 67.89 | [5 empty] | 66.16 |  |  | 68.56 |  |  |  | 0.92 |  | 3.52 | [8 empty] | 28.59 |  |  |  |  | 0.66
2012 |  |  |  | 11583.20 |  |  | 8487 |  |  |  | 1495 | [10 empty] | 96.38 |  |  |  | 97.14 | [5 empty] | 88.21 |  |  | 96.62 |  |  |  | 2.44 |  | 2.43 | [8 empty] | 0.43 |  |  |  |  | 0.76
2013 |  |  |  | 7637.26 |  |  | 5425 |  |  |  | 1495 | [10 empty] | 58.90 |  |  |  | 68.87 | [5 empty] | 58.32 |  |  | 61.93 |  |  |  | 2.52 |  | 4.85 | [8 empty] | 26.28 |  |  |  |  | 9.97
2014 |  |  |  | 8649.46 |  |  | 5902 |  |  |  | 1495 | [10 empty] | 66.26 |  |  |  | 67.50 | [5 empty] | 66.05 |  |  | 67.37 |  |  |  | 0.73 |  | 3.95 | [8 empty] | 28.54 |  |  |  |  | 1.24
2015 |  |  |  | 11646.17 |  |  | 8359 |  |  |  | 1495 | [10 empty] | 94.69 |  |  |  | 96.56 | [5 empty] | 88.93 |  |  | 95.42 |  |  |  | 2.25 |  | 2.22 | [8 empty] | 1.22 |  |  |  |  | 1.87
2016 |  |  |  | 9873.52 |  |  | 7010 |  |  |  | 1495 | [10 empty] | 75.66 |  |  |  | 78.10 | [5 empty] | 75.19 |  |  | 79.80 |  |  |  | 3.46 |  | 2.80 | [8 empty] | 19.10 |  |  |  |  | 2.44
2017 |  |  |  | 7559.81 |  |  | 5263 |  |  |  | 1495 | [10 empty] | 57.73 |  |  |  | 65.44 | [5 empty] | 57.73 |  |  | 60.08 |  |  |  | 3.94 |  | 14.64 | [8 empty] | 19.92 |  |  |  |  | 7.70
2018 |  |  |  | 10636.19 |  |  | 7321 |  |  |  | 1495 | [10 empty] | 82.29 |  |  |  | 83.48 | [5 empty] | 81.22 |  |  | 83.57 |  |  |  | 4.42 |  | 6.45 | [8 empty] | 10.07 |  |  |  |  | 1.19
2019 |  |  |  | 11608.53 |  |  | 8247 |  |  |  | 1495 | [10 empty] | 94.08 |  |  |  | 96.03 | [5 empty] | 88.64 |  |  | 94.14 |  |  |  | 2.55 |  | 2.51 | [8 empty] | 1.46 |  |  |  |  | 1.94
2020 |  |  |  | 5723.66 |  |  | 4024 |  |  |  | 1495 | [10 empty] | 43.72 |  |  |  | 58.55 | [5 empty] | 43.59 |  |  | 45.81 |  |  |  | 0.99 |  | 13.20 | [8 empty] | 28.25 |  |  |  |  | 14.83
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2002 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 360
B. |  | Refuelling without maintenance | [35 empty] | 491
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 520
E. |  | Testing of plant systems or components | [35 empty] | 37
H. |  | Nuclear regulatory requirements | [39 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 30
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 9
O. |  | Load dispatching, prioritization | [51 empty] | 7
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 94
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 11
Z. |  | Other | [39 empty] | 52
Subtotal | [37 empty] | 1048 |  |  |  | 445 | [11 empty] | 123
Total | [22 empty] | 0 | [14 empty] | 1616
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2002 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 24
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 34
15. |  |  | Reactor Cooling Systems | [34 empty] | 17
16. |  |  | Steam generation systems | [34 empty] | 37
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 12
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 97
35. |  |  | All other I&C Systems | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 18
42. |  |  | Electrical Power Supply Systems | [34 empty] | 108
Total | [37 empty] | 416

## CIVAUX-2
2020 Operating Experience
FR-73 | [8 empty] | CIVAUX-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / N4 REP 1450 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1991-04-01
Thermal power | [12 empty] | : |  |  | 4270 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1999-12-24
Gross electrical power | [12 empty] | : |  |  | 1561 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-04-23
Reference unit power (net) | [12 empty] | : |  |  | 1495 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 21 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.3
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 35000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.47 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.1
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 205 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9482.62 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.96 %
Energy Availability Factor (EAF) | [18 empty] | : | 72.26 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.96 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.99 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.05 %
Load Factor (LF) | [18 empty] | : | 72.21 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 25.73 %
Operating Factor (OF) | [18 empty] | : | 93.16 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 601 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 876.96 | 1051.82 |  |  |  | 1126.86 |  | 1077.44 | [8 empty] | 359.99 |  |  | 423.51 | [6 empty] | 737.99 |  | 325.72 |  |  |  | 524.05 |  |  | 853.01 |  |  | 1018.10 | [9 empty] | 1107.19 |  |  | 9482.62
EAF [%] |  |  |  |  | 77.98 | 99.96 |  |  |  | 99.97 |  | 99.96 | [8 empty] | 32.86 |  |  | 39.42 | [6 empty] | 66.52 |  | 29.28 |  |  |  | 48.72 |  |  | 77.21 |  |  | 97.07 | [9 empty] | 99.89 |  |  | 72.26
UCF [%] |  |  |  |  | 79.43 | 99.96 |  |  |  | 99.97 |  | 99.96 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.97 |  | 99.92 |  |  |  | 99.99 |  |  | 99.87 |  |  | 97.17 | [9 empty] | 99.98 |  |  | 97.99
LF [%] |  |  |  |  | 78.84 | 101.09 |  |  |  | 101.45 |  | 100.10 | [8 empty] | 32.36 |  |  | 39.34 | [6 empty] | 66.35 |  | 29.28 |  |  |  | 48.69 |  |  | 76.59 |  |  | 94.58 | [9 empty] | 99.54 |  |  | 72.21
OF [%] |  |  |  |  | 94.35 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 83.47 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 63.47 |  |  | 77.85 |  |  | 98.89 | [9 empty] | 100.00 |  |  | 93.16
FLR [%] |  |  |  |  | 20.56 | 0.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.03 |  |  | 2.58 | [9 empty] | 0.00 |  |  | 1.96
UCL [%] |  |  |  |  | 20.56 | 0.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.03 |  |  | 2.57 | [9 empty] | 0.00 |  |  | 1.96
PUF [%] |  |  |  |  | 0.01 | 0.01 |  |  |  | 0.03 |  | 0.04 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.08 |  |  |  | 0.01 |  |  | 0.10 |  |  | 0.26 | [9 empty] | 0.02 |  |  | 0.05
XUF [%] |  |  |  |  | 1.44 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 67.13 |  |  | 60.58 | [6 empty] | 33.45 |  | 70.64 |  |  |  | 51.26 |  |  | 22.66 |  |  | 0.10 | [9 empty] | 0.09 |  |  | 25.73
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 200945.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.48 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.4 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.37 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.59 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.43 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 4.97 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.89 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 7491.29 |  |  | 6080 |  |  |  | 1495 | [10 empty] | 91.94 |  |  |  | 94.81 | [5 empty] | 70.33 |  |  | 85.80 |  |  |  | 0.68 |  | 0.65 | [8 empty] | 4.55 |  |  |  |  | 2.86
2003 |  |  |  | 9084.75 |  |  | 6542 |  |  |  | 1495 | [10 empty] | 70.38 |  |  |  | 70.48 | [5 empty] | 69.37 |  |  | 74.68 |  |  |  | 10.67 |  | 8.42 | [8 empty] | 21.10 |  |  |  |  | 0.10
2004 |  |  |  | 11698.64 |  |  | 8042 |  |  |  | 1495 | [10 empty] | 89.64 |  |  |  | 90.04 | [5 empty] | 89.08 |  |  | 91.55 |  |  |  | 0.90 |  | 0.82 | [8 empty] | 9.14 |  |  |  |  | 0.40
2005 |  |  |  | 9621.39 |  |  | 6748 |  |  |  | 1495 | [10 empty] | 73.47 |  |  |  | 75.92 | [5 empty] | 73.47 |  |  | 77.03 |  |  |  | 2.45 |  | 9.90 | [8 empty] | 14.18 |  |  |  |  | 2.44
2006 |  |  |  | 11140.10 |  |  | 7811 |  |  |  | 1495 | [10 empty] | 89.78 |  |  |  | 91.57 | [5 empty] | 85.06 |  |  | 89.17 |  |  |  | 0.33 |  | 0.55 | [8 empty] | 7.89 |  |  |  |  | 1.78
2007 |  |  |  | 9973.85 |  |  | 7141 |  |  |  | 1495 | [10 empty] | 80.24 |  |  |  | 82.26 | [5 empty] | 76.15 |  |  | 81.51 |  |  |  | 1.58 |  | 2.36 | [8 empty] | 15.38 |  |  |  |  | 2.01
2008 |  |  |  | 11321.50 |  |  | 8085 |  |  |  | 1495 | [10 empty] | 89.02 |  |  |  | 91.06 | [5 empty] | 86.21 |  |  | 92.04 |  |  |  | 0.61 |  | 1.00 | [8 empty] | 7.94 |  |  |  |  | 2.04
2009 |  |  |  | 10293.33 |  |  | 7219 |  |  |  | 1495 | [10 empty] | 80.14 |  |  |  | 82.76 | [5 empty] | 78.60 |  |  | 82.41 |  |  |  | 0.14 |  | 4.84 | [8 empty] | 12.40 |  |  |  |  | 2.62
2010 |  |  |  | 11094.03 |  |  | 7743 |  |  |  | 1495 | [10 empty] | 86.06 |  |  |  | 88.55 | [5 empty] | 84.71 |  |  | 88.39 |  |  |  | 0.92 |  | 2.71 | [8 empty] | 8.74 |  |  |  |  | 2.48
2011 |  |  |  | 10640.60 |  |  | 7717 |  |  |  | 1495 | [10 empty] | 86.58 |  |  |  | 91.40 | [5 empty] | 81.25 |  |  | 88.09 |  |  |  | 8.58 |  | 8.58 | [8 empty] | 0.03 |  |  |  |  | 4.81
2012 |  |  |  | 4561.72 |  |  | 3228 |  |  |  | 1495 | [10 empty] | 35.27 |  |  |  | 69.60 | [5 empty] | 34.74 |  |  | 36.75 |  |  |  | 0.92 |  | 1.93 | [8 empty] | 28.48 |  |  |  |  | 34.32
2013 |  |  |  | 10581.57 |  |  | 7344 |  |  |  | 1495 | [10 empty] | 82.73 |  |  |  | 83.76 | [5 empty] | 80.80 |  |  | 83.84 |  |  |  | 2.15 |  | 2.95 | [8 empty] | 13.29 |  |  |  |  | 1.04
2014 |  |  |  | 10918.20 |  |  | 8091 |  |  |  | 1495 | [10 empty] | 95.40 |  |  |  | 95.63 | [5 empty] | 83.37 |  |  | 92.36 |  |  |  | 1.85 |  | 3.95 | [8 empty] | 0.42 |  |  |  |  | 0.23
2015 |  |  |  | 8920.04 |  |  | 6332 |  |  |  | 1495 | [10 empty] | 69.44 |  |  |  | 73.89 | [5 empty] | 68.11 |  |  | 72.28 |  |  |  | 1.14 |  | 0.85 | [8 empty] | 25.26 |  |  |  |  | 4.45
2016 |  |  |  | 8169.29 |  |  | 5944 |  |  |  | 1495 | [10 empty] | 63.97 |  |  |  | 67.12 | [5 empty] | 62.21 |  |  | 67.67 |  |  |  | 2.01 |  | 16.19 | [8 empty] | 16.68 |  |  |  |  | 3.15
2017 |  |  |  | 11390.13 |  |  | 7884 |  |  |  | 1495 | [10 empty] | 87.55 |  |  |  | 88.06 | [5 empty] | 86.97 |  |  | 90.00 |  |  |  | 3.66 |  | 10.93 | [8 empty] | 1.01 |  |  |  |  | 0.51
2018 |  |  |  | 8867.46 |  |  | 6063 |  |  |  | 1495 | [10 empty] | 67.90 |  |  |  | 70.32 | [5 empty] | 67.71 |  |  | 69.21 |  |  |  | 1.69 |  | 8.46 | [8 empty] | 21.23 |  |  |  |  | 2.41
2019 |  |  |  | 10630.33 |  |  | 7243 |  |  |  | 1495 | [10 empty] | 82.37 |  |  |  | 82.53 | [5 empty] | 81.17 |  |  | 82.68 |  |  |  | 3.91 |  | 7.30 | [8 empty] | 10.17 |  |  |  |  | 0.17
2020 |  |  |  | 9482.62 |  |  | 8183 |  |  |  | 1495 | [10 empty] | 72.26 |  |  |  | 97.99 | [5 empty] | 72.21 |  |  | 93.16 |  |  |  | 1.96 |  | 1.96 | [8 empty] | 0.05 |  |  |  |  | 25.73
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2002 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 246
B. |  | Refuelling without maintenance | [35 empty] | 285
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 663
E. |  | Testing of plant systems or components | [35 empty] | 22
H. |  | Nuclear regulatory requirements | [39 empty] | 107
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 27
L. |  | Human factor related | [39 empty] | 12
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
O. |  | Load dispatching, prioritization | [51 empty] | 6
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 179
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 31
Z. |  | Other | [39 empty] | 14
Subtotal | [37 empty] | 970 |  |  |  | 379 | [11 empty] | 244
Total | [22 empty] | 0 | [14 empty] | 1593
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2002 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 19
12. |  |  | Reactor I&C Systems | [34 empty] | 16
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 18
14. |  |  | Safety Systems | [34 empty] | 25
15. |  |  | Reactor Cooling Systems | [34 empty] | 16
16. |  |  | Steam generation systems | [34 empty] | 105
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 18
31. |  |  | Turbine and auxiliaries | [34 empty] | 26
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 50
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 42
Total | [37 empty] | 347

## CRUAS-1
2020 Operating Experience
FR-42 | [8 empty] | CRUAS-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP2 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-08-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-04-29
Gross electrical power | [12 empty] | : |  |  | 956 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-04-02
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6241.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.38 %
Energy Availability Factor (EAF) | [18 empty] | : | 79.62 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.18 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.81 %
Load Factor (LF) | [18 empty] | : | 77.65 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 12.56 %
Operating Factor (OF) | [18 empty] | : | 81.5 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1625 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 65.16 | 633.94 |  |  |  | 672.89 |  | 505.02 | [8 empty] | 336.73 |  |  | 592.66 | [6 empty] | 495.83 |  | 431.12 |  |  |  | 554.57 |  |  | 612.79 |  |  | 660.06 | [9 empty] | 680.51 |  |  | 6241.26
EAF [%] |  |  |  |  | 9.59 | 99.05 |  |  |  | 99.75 |  | 77.65 | [8 empty] | 50.11 |  |  | 98.59 | [6 empty] | 76.33 |  | 68.50 |  |  |  | 87.37 |  |  | 92.11 |  |  | 99.83 | [9 empty] | 99.24 |  |  | 79.62
UCF [%] |  |  |  |  | 14.02 | 99.06 |  |  |  | 99.75 |  | 99.77 | [8 empty] | 99.79 |  |  | 99.48 | [6 empty] | 99.74 |  | 99.66 |  |  |  | 96.85 |  |  | 99.60 |  |  | 99.85 | [9 empty] | 99.93 |  |  | 92.18
LF [%] |  |  |  |  | 9.57 | 99.54 |  |  |  | 98.98 |  | 76.66 | [8 empty] | 49.46 |  |  | 89.96 | [6 empty] | 72.83 |  | 63.33 |  |  |  | 84.18 |  |  | 89.89 |  |  | 100.19 | [9 empty] | 99.96 |  |  | 77.65
OF [%] |  |  |  |  | 16.94 | 100.00 |  |  |  | 100.00 |  | 78.33 | [8 empty] | 51.61 |  |  | 100.00 | [6 empty] | 78.49 |  | 70.30 |  |  |  | 91.94 |  |  | 93.02 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.50
FLR [%] |  |  |  |  | 0.00 | 0.35 |  |  |  | 0.08 |  | 0.18 | [8 empty] | 0.16 |  |  | 0.20 | [6 empty] | 0.20 |  | 0.21 |  |  |  | 2.76 |  |  | 0.18 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.38
UCL [%] |  |  |  |  | 78.56 | 0.35 |  |  |  | 0.08 |  | 0.18 | [8 empty] | 0.16 |  |  | 0.20 | [6 empty] | 0.20 |  | 0.21 |  |  |  | 2.75 |  |  | 0.18 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.01
PUF [%] |  |  |  |  | 7.42 | 0.59 |  |  |  | 0.17 |  | 0.06 | [8 empty] | 0.05 |  |  | 0.32 | [6 empty] | 0.06 |  | 0.13 |  |  |  | 0.41 |  |  | 0.22 |  |  | 0.14 | [9 empty] | 0.07 |  |  | 0.81
XUF [%] |  |  |  |  | 4.43 | 0.01 |  |  |  | 0.00 |  | 22.12 | [8 empty] | 49.68 |  |  | 0.89 | [6 empty] | 23.41 |  | 31.16 |  |  |  | 9.48 |  |  | 7.49 |  |  | 0.02 | [9 empty] | 0.69 |  |  | 12.56
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 208968.56 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.02 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.79 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.28 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.32 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.5 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.96 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 5482.00 |  |  | 7165 |  |  |  | 880 | [10 empty] | 82.63 |  |  |  | 82.63 | [5 empty] | 82.63 |  |  | 92.86 |  |  |  | 17.37 |  | 17.37 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 5185.20 |  |  | 6615 |  |  |  | 880 | [10 empty] | 71.95 |  |  |  | 77.18 | [5 empty] | 67.26 |  |  | 75.51 |  |  |  | 3.24 |  | 2.58 | [8 empty] | 20.24 |  |  |  |  | 5.23
1986 |  |  |  | 5888.00 |  |  | 7377 |  |  |  | 880 | [10 empty] | 86.03 |  |  |  | 87.59 | [5 empty] | 76.38 |  |  | 84.21 |  |  |  | 6.55 |  | 6.13 | [8 empty] | 6.27 |  |  |  |  | 1.56
1987 |  |  |  | 5359.50 |  |  | 6860 |  |  |  | 880 | [10 empty] | 81.83 |  |  |  | 83.73 | [5 empty] | 69.52 |  |  | 78.31 |  |  |  | 1.62 |  | 1.38 | [8 empty] | 14.89 |  |  |  |  | 1.90
1988 |  |  |  | 4025.00 |  |  | 5562 |  |  |  | 880 | [10 empty] | 96.69 |  |  |  | 98.05 | [5 empty] | 52.07 |  |  | 63.32 |  |  |  | 1.95 |  | 1.95 | [8 empty] | 0.00 |  |  |  |  | 1.36
1989 |  |  |  | 5648.89 |  |  | 7239 |  |  |  | 880 | [10 empty] | 83.65 |  |  |  | 86.05 | [5 empty] | 73.28 |  |  | 82.64 |  |  |  | 3.68 |  | 3.29 | [8 empty] | 10.66 |  |  |  |  | 2.41
1990 |  |  |  | 4983.52 |  |  | 6809 |  |  |  | 880 | [10 empty] | 82.63 |  |  |  | 84.77 | [5 empty] | 64.65 |  |  | 77.73 |  |  |  | 1.48 |  | 1.27 | [8 empty] | 13.95 |  |  |  |  | 2.14
1991 |  |  |  | 4477.80 |  |  | 5762 |  |  |  | 880 | [10 empty] | 65.27 |  |  |  | 68.16 | [5 empty] | 58.09 |  |  | 65.78 |  |  |  | 9.81 |  | 7.41 | [8 empty] | 24.43 |  |  |  |  | 2.88
1992 |  |  |  | 5739.40 |  |  | 7183 |  |  |  | 880 | [10 empty] | 77.77 |  |  |  | 81.04 | [5 empty] | 74.25 |  |  | 81.77 |  |  |  | 7.42 |  | 6.50 | [8 empty] | 12.46 |  |  |  |  | 3.27
1993 |  |  |  | 6156.63 |  |  | 7353 |  |  |  | 880 | [10 empty] | 84.56 |  |  |  | 87.16 | [5 empty] | 79.86 |  |  | 83.94 |  |  |  | 2.42 |  | 2.16 | [8 empty] | 10.68 |  |  |  |  | 2.59
1994 |  |  |  | 6181.24 |  |  | 7498 |  |  |  | 915 | [10 empty] | 84.25 |  |  |  | 84.46 | [5 empty] | 77.12 |  |  | 85.59 |  |  |  | 5.48 |  | 4.90 | [8 empty] | 10.64 |  |  |  |  | 0.21
1995 |  |  |  | 4630.41 |  |  | 5624 |  |  |  | 915 | [10 empty] | 62.47 |  |  |  | 63.33 | [5 empty] | 57.77 |  |  | 64.20 |  |  |  | 12.73 |  | 9.24 | [8 empty] | 27.43 |  |  |  |  | 0.86
1996 |  |  |  | 6258.55 |  |  | 7478 |  |  |  | 915 | [10 empty] | 82.96 |  |  |  | 83.87 | [5 empty] | 77.87 |  |  | 85.13 |  |  |  | 5.97 |  | 5.32 | [8 empty] | 10.81 |  |  |  |  | 0.91
1997 |  |  |  | 5271.22 |  |  | 6784 |  |  |  | 915 | [10 empty] | 74.09 |  |  |  | 77.89 | [5 empty] | 65.76 |  |  | 77.44 |  |  |  | 9.97 |  | 8.62 | [8 empty] | 13.49 |  |  |  |  | 3.80
1998 |  |  |  | 6387.28 |  |  | 7864 |  |  |  | 915 | [10 empty] | 89.54 |  |  |  | 90.75 | [5 empty] | 79.69 |  |  | 89.77 |  |  |  | 3.61 |  | 3.40 | [8 empty] | 5.85 |  |  |  |  | 1.21
1999 |  |  |  | 5890.67 |  |  | 7367 |  |  |  | 915 | [10 empty] | 83.80 |  |  |  | 85.49 | [5 empty] | 73.49 |  |  | 84.10 |  |  |  | 3.81 |  | 3.39 | [8 empty] | 11.12 |  |  |  |  | 1.69
2000 |  |  |  | 6320.52 |  |  | 7742 |  |  |  | 915 | [10 empty] | 85.96 |  |  |  | 87.61 | [5 empty] | 78.64 |  |  | 88.14 |  |  |  | 0.74 |  | 0.65 | [8 empty] | 11.73 |  |  |  |  | 1.65
2001 |  |  |  | 5918.31 |  |  | 7264 |  |  |  | 915 | [10 empty] | 81.07 |  |  |  | 81.69 | [5 empty] | 73.84 |  |  | 82.92 |  |  |  | 6.09 |  | 5.30 | [8 empty] | 13.02 |  |  |  |  | 0.61
2002 |  |  |  | 6069.76 |  |  | 7349 |  |  |  | 915 | [10 empty] | 80.46 |  |  |  | 80.61 | [5 empty] | 75.73 |  |  | 83.89 |  |  |  | 11.38 |  | 10.35 | [8 empty] | 9.04 |  |  |  |  | 0.16
2003 |  |  |  | 6120.53 |  |  | 7403 |  |  |  | 915 | [10 empty] | 81.14 |  |  |  | 82.53 | [5 empty] | 76.36 |  |  | 84.51 |  |  |  | 5.31 |  | 4.62 | [8 empty] | 12.84 |  |  |  |  | 1.39
2004 |  |  |  | 5866.08 |  |  | 6907 |  |  |  | 915 | [10 empty] | 76.11 |  |  |  | 76.96 | [5 empty] | 72.99 |  |  | 78.63 |  |  |  | 11.69 |  | 10.19 | [8 empty] | 12.85 |  |  |  |  | 0.84
2005 |  |  |  | 5345.43 |  |  | 6311 |  |  |  | 915 | [10 empty] | 70.60 |  |  |  | 71.08 | [5 empty] | 66.69 |  |  | 72.04 |  |  |  | 5.29 |  | 4.57 | [8 empty] | 24.35 |  |  |  |  | 0.48
2006 |  |  |  | 6491.00 |  |  | 7716 |  |  |  | 915 | [10 empty] | 83.73 |  |  |  | 84.76 | [5 empty] | 80.98 |  |  | 88.08 |  |  |  | 3.88 |  | 6.16 | [8 empty] | 9.08 |  |  |  |  | 1.02
2007 |  |  |  | 4468.50 |  |  | 5506 |  |  |  | 915 | [10 empty] | 55.86 |  |  |  | 58.41 | [5 empty] | 55.75 |  |  | 62.85 |  |  |  | 4.55 |  | 18.60 | [8 empty] | 22.99 |  |  |  |  | 2.55
2008 |  |  |  | 6281.45 |  |  | 7285 |  |  |  | 915 | [10 empty] | 79.29 |  |  |  | 80.79 | [5 empty] | 78.15 |  |  | 82.93 |  |  |  | 5.37 |  | 10.11 | [8 empty] | 9.10 |  |  |  |  | 1.51
2009 |  |  |  | 5066.64 |  |  | 6016 |  |  |  | 915 | [10 empty] | 63.43 |  |  |  | 78.80 | [5 empty] | 63.21 |  |  | 68.68 |  |  |  | 2.27 |  | 7.62 | [8 empty] | 13.58 |  |  |  |  | 15.37
2010 |  |  |  | 6529.54 |  |  | 7413 |  |  |  | 915 | [10 empty] | 82.19 |  |  |  | 83.20 | [5 empty] | 81.46 |  |  | 84.62 |  |  |  | 3.46 |  | 9.49 | [8 empty] | 7.31 |  |  |  |  | 1.01
2011 |  |  |  | 5791.82 |  |  | 6573 |  |  |  | 915 | [10 empty] | 72.78 |  |  |  | 73.05 | [5 empty] | 72.26 |  |  | 75.03 |  |  |  | 2.56 |  | 11.63 | [8 empty] | 15.32 |  |  |  |  | 0.27
2012 |  |  |  | 5896.70 |  |  | 6640 |  |  |  | 915 | [10 empty] | 73.48 |  |  |  | 80.89 | [5 empty] | 73.37 |  |  | 75.59 |  |  |  | 2.26 |  | 7.59 | [8 empty] | 11.51 |  |  |  |  | 7.41
2013 |  |  |  | 6325.06 |  |  | 7087 |  |  |  | 915 | [10 empty] | 79.90 |  |  |  | 82.28 | [5 empty] | 78.91 |  |  | 80.90 |  |  |  | 1.09 |  | 4.75 | [8 empty] | 12.98 |  |  |  |  | 2.38
2014 |  |  |  | 6767.39 |  |  | 7720 |  |  |  | 915 | [10 empty] | 86.34 |  |  |  | 87.34 | [5 empty] | 84.43 |  |  | 88.13 |  |  |  | 1.31 |  | 2.70 | [8 empty] | 9.97 |  |  |  |  | 1.00
2015 |  |  |  | 3668.25 |  |  | 4245 |  |  |  | 915 | [10 empty] | 45.93 |  |  |  | 46.48 | [5 empty] | 45.77 |  |  | 48.46 |  |  |  | 6.71 |  | 22.54 | [8 empty] | 30.98 |  |  |  |  | 0.55
2016 |  |  |  | 6374.97 |  |  | 7417 |  |  |  | 915 | [10 empty] | 80.00 |  |  |  | 80.61 | [5 empty] | 79.32 |  |  | 84.44 |  |  |  | 6.32 |  | 10.34 | [8 empty] | 9.05 |  |  |  |  | 0.61
2017 |  |  |  | 3987.13 |  |  | 4655 |  |  |  | 915 | [10 empty] | 49.92 |  |  |  | 50.59 | [5 empty] | 49.74 |  |  | 53.14 |  |  |  | 2.97 |  | 18.52 | [8 empty] | 30.89 |  |  |  |  | 0.67
2018 |  |  |  | 6471.31 |  |  | 7364 |  |  |  | 915 | [10 empty] | 80.93 |  |  |  | 81.32 | [5 empty] | 80.74 |  |  | 84.06 |  |  |  | 5.60 |  | 8.65 | [8 empty] | 10.03 |  |  |  |  | 0.40
2019 |  |  |  | 5215.27 |  |  | 5891 |  |  |  | 915 | [10 empty] | 65.17 |  |  |  | 72.69 | [5 empty] | 65.07 |  |  | 67.25 |  |  |  | 2.12 |  | 4.69 | [8 empty] | 22.62 |  |  |  |  | 7.52
2020 |  |  |  | 6241.26 |  |  | 7159 |  |  |  | 915 | [10 empty] | 79.62 |  |  |  | 92.18 | [5 empty] | 77.65 |  |  | 81.50 |  |  |  | 0.38 |  | 7.01 | [8 empty] | 0.81 |  |  |  |  | 12.56
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 488
B. |  | Refuelling without maintenance | [35 empty] | 139
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 930 |  |  |  | 14
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 18
E. |  | Testing of plant systems or components | [35 empty] | 14
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 8
L. |  | Human factor related | [39 empty] | 60
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 12
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 14 | [11 empty] | 64
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 1
Z. |  | Other | [35 empty] | 2 |  |  |  | 38
Subtotal | [37 empty] | 1103 |  |  |  | 618 | [11 empty] | 86
Total | [22 empty] | 0 | [14 empty] | 1807
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 15
12. |  |  | Reactor I&C Systems | [34 empty] | 16
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 39
14. |  |  | Safety Systems | [34 empty] | 39
15. |  |  | Reactor Cooling Systems | [34 empty] | 15
16. |  |  | Steam generation systems | [34 empty] | 7
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 34
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 106
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 169
42. |  |  | Electrical Power Supply Systems | [34 empty] | 24
Total | [37 empty] | 478

## CRUAS-2
2020 Operating Experience
FR-43 | [8 empty] | CRUAS-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP2 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-11-15
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-09-06
Gross electrical power | [12 empty] | : |  |  | 956 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-04-01
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5761.69 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.96 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.5 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.35 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.9 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.75 %
Load Factor (LF) | [18 empty] | : | 71.69 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 11.4 %
Operating Factor (OF) | [18 empty] | : | 78.81 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1861 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 659.16 | 625.38 |  |  |  | 663.36 |  | 603.15 | [8 empty] | 388.20 |  |  | 0.00 | [6 empty] | 440.11 |  | 221.65 |  |  |  | 491.33 |  |  | 573.44 |  |  | 524.83 | [9 empty] | 571.08 |  |  | 5761.69
EAF [%] |  |  |  |  | 98.00 | 98.46 |  |  |  | 98.05 |  | 91.54 | [8 empty] | 57.02 |  |  | 0.00 | [6 empty] | 69.30 |  | 38.10 |  |  |  | 78.04 |  |  | 94.50 |  |  | 84.33 | [9 empty] | 86.84 |  |  | 74.50
UCF [%] |  |  |  |  | 99.24 | 98.46 |  |  |  | 98.10 |  | 99.68 | [8 empty] | 70.50 |  |  | 0.00 | [6 empty] | 70.39 |  | 99.75 |  |  |  | 98.72 |  |  | 97.91 |  |  | 98.47 | [9 empty] | 98.95 |  |  | 85.90
LF [%] |  |  |  |  | 96.83 | 98.20 |  |  |  | 97.58 |  | 91.55 | [8 empty] | 57.02 |  |  | 0.00 | [6 empty] | 64.65 |  | 32.56 |  |  |  | 74.58 |  |  | 84.12 |  |  | 79.66 | [9 empty] | 83.89 |  |  | 71.69
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 70.97 |  |  | 0.00 | [6 empty] | 76.75 |  | 38.98 |  |  |  | 81.67 |  |  | 96.78 |  |  | 90.69 | [9 empty] | 89.92 |  |  | 78.81
FLR [%] |  |  |  |  | 0.67 | 1.41 |  |  |  | 1.63 |  | 0.09 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.13 |  | 0.22 |  |  |  | 1.12 |  |  | 1.92 |  |  | 1.25 | [9 empty] | 0.94 |  |  | 0.96
UCL [%] |  |  |  |  | 0.67 | 1.41 |  |  |  | 1.63 |  | 0.09 | [8 empty] | 0.00 |  |  | 6.66 | [6 empty] | 24.03 |  | 0.22 |  |  |  | 1.12 |  |  | 1.91 |  |  | 1.25 | [9 empty] | 0.94 |  |  | 3.35
PUF [%] |  |  |  |  | 0.09 | 0.14 |  |  |  | 0.27 |  | 0.24 | [8 empty] | 29.50 |  |  | 93.35 | [6 empty] | 5.58 |  | 0.03 |  |  |  | 0.16 |  |  | 0.18 |  |  | 0.29 | [9 empty] | 0.11 |  |  | 10.75
XUF [%] |  |  |  |  | 1.23 | 0.00 |  |  |  | 0.04 |  | 8.13 | [8 empty] | 13.47 |  |  | 0.00 | [6 empty] | 1.09 |  | 61.65 |  |  |  | 20.68 |  |  | 3.41 |  |  | 14.14 | [9 empty] | 12.11 |  |  | 11.40
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 210022.9 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.33 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.66 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.35 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.98 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.97 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.06 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 6103.20 |  |  | 8330 |  |  |  | 880 | [10 empty] | 96.00 |  |  |  | 98.29 | [5 empty] | 83.40 |  |  | 97.33 |  |  |  | 1.71 |  | 1.71 | [8 empty] | 0.00 |  |  |  |  | 2.29
1986 |  |  |  | 4955.00 |  |  | 6258 |  |  |  | 880 | [10 empty] | 70.06 |  |  |  | 70.42 | [5 empty] | 64.28 |  |  | 71.44 |  |  |  | 22.40 |  | 20.33 | [8 empty] | 9.25 |  |  |  |  | 0.36
1987 |  |  |  | 5559.90 |  |  | 6761 |  |  |  | 900 | [10 empty] | 79.13 |  |  |  | 79.79 | [5 empty] | 70.52 |  |  | 77.18 |  |  |  | 1.84 |  | 1.50 | [8 empty] | 18.72 |  |  |  |  | 0.65
1988 |  |  |  | 5698.00 |  |  | 7176 |  |  |  | 915 | [10 empty] | 80.60 |  |  |  | 84.97 | [5 empty] | 70.89 |  |  | 81.69 |  |  |  | 4.03 |  | 3.57 | [8 empty] | 11.46 |  |  |  |  | 4.37
1989 |  |  |  | 6298.51 |  |  | 7697 |  |  |  | 915 | [10 empty] | 83.27 |  |  |  | 86.17 | [5 empty] | 78.58 |  |  | 87.87 |  |  |  | 3.45 |  | 3.08 | [8 empty] | 10.74 |  |  |  |  | 2.91
1990 |  |  |  | 6001.78 |  |  | 7114 |  |  |  | 915 | [10 empty] | 77.72 |  |  |  | 79.83 | [5 empty] | 74.88 |  |  | 81.21 |  |  |  | 9.42 |  | 8.30 | [8 empty] | 11.87 |  |  |  |  | 2.11
1991 |  |  |  | 4099.88 |  |  | 4838 |  |  |  | 915 | [10 empty] | 53.75 |  |  |  | 55.32 | [5 empty] | 51.15 |  |  | 55.23 |  |  |  | 27.56 |  | 21.05 | [8 empty] | 23.63 |  |  |  |  | 1.58
1992 |  |  |  | 5946.87 |  |  | 6910 |  |  |  | 915 | [10 empty] | 76.96 |  |  |  | 76.99 | [5 empty] | 73.99 |  |  | 78.67 |  |  |  | 11.95 |  | 10.44 | [8 empty] | 12.57 |  |  |  |  | 0.03
1993 |  |  |  | 5441.04 |  |  | 6463 |  |  |  | 915 | [10 empty] | 73.54 |  |  |  | 78.13 | [5 empty] | 67.88 |  |  | 73.78 |  |  |  | 12.01 |  | 10.66 | [8 empty] | 11.20 |  |  |  |  | 4.59
1994 |  |  |  | 5566.06 |  |  | 6765 |  |  |  | 915 | [10 empty] | 94.12 |  |  |  | 96.79 | [5 empty] | 69.44 |  |  | 77.23 |  |  |  | 3.16 |  | 3.16 | [8 empty] | 0.05 |  |  |  |  | 2.66
1995 |  |  |  | 5366.77 |  |  | 6581 |  |  |  | 915 | [10 empty] | 72.41 |  |  |  | 76.26 | [5 empty] | 66.96 |  |  | 75.13 |  |  |  | 11.85 |  | 10.25 | [8 empty] | 13.48 |  |  |  |  | 3.85
1996 |  |  |  | 6521.86 |  |  | 7870 |  |  |  | 915 | [10 empty] | 87.09 |  |  |  | 88.83 | [5 empty] | 81.14 |  |  | 89.59 |  |  |  | 1.32 |  | 1.19 | [8 empty] | 9.98 |  |  |  |  | 1.75
1997 |  |  |  | 5176.08 |  |  | 6596 |  |  |  | 915 | [10 empty] | 76.47 |  |  |  | 80.91 | [5 empty] | 64.58 |  |  | 75.30 |  |  |  | 0.87 |  | 0.71 | [8 empty] | 18.38 |  |  |  |  | 4.44
1998 |  |  |  | 6003.57 |  |  | 7396 |  |  |  | 915 | [10 empty] | 79.02 |  |  |  | 82.81 | [5 empty] | 74.90 |  |  | 84.43 |  |  |  | 3.10 |  | 2.65 | [8 empty] | 14.54 |  |  |  |  | 3.79
1999 |  |  |  | 6393.81 |  |  | 7787 |  |  |  | 915 | [10 empty] | 85.31 |  |  |  | 88.14 | [5 empty] | 79.77 |  |  | 88.89 |  |  |  | 0.23 |  | 0.20 | [8 empty] | 11.65 |  |  |  |  | 2.84
2000 |  |  |  | 6420.91 |  |  | 7755 |  |  |  | 915 | [10 empty] | 85.55 |  |  |  | 86.99 | [5 empty] | 79.89 |  |  | 88.29 |  |  |  | 0.81 |  | 0.71 | [8 empty] | 12.31 |  |  |  |  | 1.43
2001 |  |  |  | 5914.40 |  |  | 7053 |  |  |  | 915 | [10 empty] | 76.50 |  |  |  | 79.70 | [5 empty] | 73.79 |  |  | 80.51 |  |  |  | 8.14 |  | 7.06 | [8 empty] | 13.23 |  |  |  |  | 3.20
2002 |  |  |  | 6547.44 |  |  | 7776 |  |  |  | 915 | [10 empty] | 85.99 |  |  |  | 86.53 | [5 empty] | 81.69 |  |  | 88.77 |  |  |  | 3.83 |  | 3.45 | [8 empty] | 10.03 |  |  |  |  | 0.54
2003 |  |  |  | 5727.93 |  |  | 6927 |  |  |  | 915 | [10 empty] | 75.57 |  |  |  | 75.77 | [5 empty] | 71.46 |  |  | 79.08 |  |  |  | 12.21 |  | 10.54 | [8 empty] | 13.69 |  |  |  |  | 0.20
2004 |  |  |  | 6612.96 |  |  | 7661 |  |  |  | 915 | [10 empty] | 84.92 |  |  |  | 85.96 | [5 empty] | 82.28 |  |  | 87.22 |  |  |  | 0.57 |  | 0.49 | [8 empty] | 13.55 |  |  |  |  | 1.04
2005 |  |  |  | 6504.12 |  |  | 7684 |  |  |  | 915 | [10 empty] | 83.04 |  |  |  | 85.81 | [5 empty] | 81.14 |  |  | 87.71 |  |  |  | 1.42 |  | 1.88 | [8 empty] | 12.31 |  |  |  |  | 2.77
2006 |  |  |  | 6509.49 |  |  | 7736 |  |  |  | 915 | [10 empty] | 84.34 |  |  |  | 85.58 | [5 empty] | 81.21 |  |  | 88.31 |  |  |  | 3.94 |  | 5.89 | [8 empty] | 8.52 |  |  |  |  | 1.24
2007 |  |  |  | 4617.90 |  |  | 5602 |  |  |  | 915 | [10 empty] | 58.03 |  |  |  | 61.62 | [5 empty] | 57.61 |  |  | 63.95 |  |  |  | 1.94 |  | 8.91 | [8 empty] | 29.47 |  |  |  |  | 3.59
2008 |  |  |  | 5597.43 |  |  | 6633 |  |  |  | 915 | [10 empty] | 69.75 |  |  |  | 70.93 | [5 empty] | 69.64 |  |  | 75.51 |  |  |  | 6.25 |  | 15.48 | [8 empty] | 13.59 |  |  |  |  | 1.18
2009 |  |  |  | 5862.16 |  |  | 6886 |  |  |  | 915 | [10 empty] | 73.60 |  |  |  | 78.67 | [5 empty] | 73.14 |  |  | 78.61 |  |  |  | 2.91 |  | 7.61 | [8 empty] | 13.71 |  |  |  |  | 5.07
2010 |  |  |  | 5305.44 |  |  | 6036 |  |  |  | 915 | [10 empty] | 66.55 |  |  |  | 74.51 | [5 empty] | 66.19 |  |  | 68.90 |  |  |  | 11.78 |  | 18.28 | [8 empty] | 7.21 |  |  |  |  | 7.96
2011 |  |  |  | 5791.15 |  |  | 6577 |  |  |  | 915 | [10 empty] | 73.02 |  |  |  | 74.13 | [5 empty] | 72.25 |  |  | 75.08 |  |  |  | 6.56 |  | 11.55 | [8 empty] | 14.31 |  |  |  |  | 1.12
2012 |  |  |  | 6761.59 |  |  | 7665 |  |  |  | 915 | [10 empty] | 84.70 |  |  |  | 86.48 | [5 empty] | 84.13 |  |  | 87.26 |  |  |  | 0.15 |  | 6.31 | [8 empty] | 7.21 |  |  |  |  | 1.78
2013 |  |  |  | 5729.40 |  |  | 6729 |  |  |  | 915 | [10 empty] | 73.03 |  |  |  | 75.71 | [5 empty] | 71.48 |  |  | 76.82 |  |  |  | 1.26 |  | 7.02 | [8 empty] | 17.27 |  |  |  |  | 2.67
2014 |  |  |  | 6708.45 |  |  | 7931 |  |  |  | 915 | [10 empty] | 86.15 |  |  |  | 89.62 | [5 empty] | 83.69 |  |  | 90.54 |  |  |  | 1.26 |  | 1.69 | [8 empty] | 8.69 |  |  |  |  | 3.47
2015 |  |  |  | 5568.66 |  |  | 6630 |  |  |  | 915 | [10 empty] | 70.20 |  |  |  | 72.96 | [5 empty] | 69.47 |  |  | 75.68 |  |  |  | 3.80 |  | 10.54 | [8 empty] | 16.50 |  |  |  |  | 2.76
2016 |  |  |  | 6596.10 |  |  | 7743 |  |  |  | 915 | [10 empty] | 83.08 |  |  |  | 83.78 | [5 empty] | 82.07 |  |  | 88.15 |  |  |  | 4.55 |  | 7.17 | [8 empty] | 9.05 |  |  |  |  | 0.71
2017 |  |  |  | 6505.00 |  |  | 7739 |  |  |  | 915 | [10 empty] | 84.01 |  |  |  | 90.78 | [5 empty] | 81.16 |  |  | 88.34 |  |  |  | 0.97 |  | 0.89 | [8 empty] | 8.34 |  |  |  |  | 6.77
2018 |  |  |  | 4984.84 |  |  | 5958 |  |  |  | 915 | [10 empty] | 64.41 |  |  |  | 66.36 | [5 empty] | 62.19 |  |  | 68.01 |  |  |  | 2.10 |  | 8.57 | [8 empty] | 25.07 |  |  |  |  | 1.94
2019 |  |  |  | 4872.15 |  |  | 6038 |  |  |  | 915 | [10 empty] | 65.06 |  |  |  | 75.74 | [5 empty] | 60.78 |  |  | 68.93 |  |  |  | 1.70 |  | 2.75 | [8 empty] | 21.51 |  |  |  |  | 10.68
2020 |  |  |  | 5761.69 |  |  | 6923 |  |  |  | 915 | [10 empty] | 74.50 |  |  |  | 85.90 | [5 empty] | 71.69 |  |  | 78.81 |  |  |  | 0.96 |  | 3.35 | [8 empty] | 10.75 |  |  |  |  | 11.40
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 356
B. |  | Refuelling without maintenance | [35 empty] | 92
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 922 |  |  |  | 6
E. |  | Testing of plant systems or components | [35 empty] | 7 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 5
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 45
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 32
O. |  | Load dispatching, prioritization | [51 empty] | 2
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 8 | [11 empty] | 32
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 3 | [11 empty] | 9
Z. |  | Other | [39 empty] | 42
Subtotal | [37 empty] | 1021 |  |  |  | 465 | [11 empty] | 75
Total | [22 empty] | 0 | [14 empty] | 1561
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 27
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 22
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 87
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 45
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 104
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [37 empty] | 356

## CRUAS-3
2020 Operating Experience
FR-44 | [8 empty] | CRUAS-3 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP2 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-04-15
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-05-14
Gross electrical power | [12 empty] | : |  |  | 956 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-09-10
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4171.74 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.83 %
Energy Availability Factor (EAF) | [18 empty] | : | 52.12 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 17 %
Unit Capability Factor (UCF) | [18 empty] | : | 57.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.02 %
Load Factor (LF) | [18 empty] | : | 51.9 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 5.87 %
Operating Factor (OF) | [18 empty] | : | 55.98 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3867 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 627.74 | 390.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 33.62 |  | 489.62 |  |  |  | 645.94 |  |  | 681.31 |  |  | 638.22 | [9 empty] | 664.65 |  |  | 4171.74
EAF [%] |  |  |  |  | 92.21 | 61.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 4.94 |  | 71.93 |  |  |  | 98.02 |  |  | 99.69 |  |  | 97.57 | [9 empty] | 99.79 |  |  | 52.12
UCF [%] |  |  |  |  | 99.85 | 75.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 38.71 |  |  | 6.02 | [6 empty] | 4.94 |  | 72.45 |  |  |  | 98.86 |  |  | 99.78 |  |  | 99.60 | [9 empty] | 99.92 |  |  | 57.98
LF [%] |  |  |  |  | 92.21 | 61.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 4.94 |  | 71.92 |  |  |  | 98.05 |  |  | 99.95 |  |  | 96.88 | [9 empty] | 97.63 |  |  | 51.90
OF [%] |  |  |  |  | 100.00 | 76.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 15.19 |  | 80.78 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 55.98
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 14.28 |  | 4.88 |  |  |  | 1.04 |  |  | 0.10 |  |  | 0.08 | [9 empty] | 0.01 |  |  | 0.83
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 93.98 | [6 empty] | 85.66 |  | 22.89 |  |  |  | 1.04 |  |  | 0.10 |  |  | 0.08 | [9 empty] | 0.01 |  |  | 17.00
PUF [%] |  |  |  |  | 0.15 | 24.18 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 61.29 |  |  | 0.00 | [6 empty] | 9.40 |  | 4.66 |  |  |  | 0.10 |  |  | 0.13 |  |  | 0.32 | [9 empty] | 0.06 |  |  | 25.02
XUF [%] |  |  |  |  | 7.64 | 14.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 38.71 |  |  | 6.01 | [6 empty] | 0.00 |  | 0.52 |  |  |  | 0.84 |  |  | 0.08 |  |  | 2.04 | [9 empty] | 0.14 |  |  | 5.87
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 207969.03 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.49 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.97 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.84 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.47 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.69 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.5 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.32 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 3272.00 |  |  | 4380 |  |  |  | 880 | [10 empty] | 91.93 |  |  |  | 91.93 | [5 empty] | 89.66 |  |  | 92.73 |  |  |  | 8.07 |  | 8.07 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 5247.40 |  |  | 6557 |  |  |  | 880 | [10 empty] | 72.54 |  |  |  | 74.60 | [5 empty] | 68.07 |  |  | 74.85 |  |  |  | 8.27 |  | 6.72 | [8 empty] | 18.68 |  |  |  |  | 2.06
1986 |  |  |  | 5967.08 |  |  | 7456 |  |  |  | 880 | [10 empty] | 89.23 |  |  |  | 89.52 | [5 empty] | 77.41 |  |  | 85.11 |  |  |  | 1.96 |  | 1.79 | [8 empty] | 8.70 |  |  |  |  | 0.28
1987 |  |  |  | 4721.40 |  |  | 6013 |  |  |  | 880 | [10 empty] | 75.08 |  |  |  | 75.71 | [5 empty] | 61.25 |  |  | 68.64 |  |  |  | 11.51 |  | 9.84 | [8 empty] | 14.45 |  |  |  |  | 0.63
1988 |  |  |  | 4773.00 |  |  | 6679 |  |  |  | 880 | [10 empty] | 98.63 |  |  |  | 99.87 | [5 empty] | 61.75 |  |  | 76.04 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 0.00 |  |  |  |  | 1.24
1989 |  |  |  | 5577.93 |  |  | 6571 |  |  |  | 880 | [10 empty] | 72.81 |  |  |  | 74.19 | [5 empty] | 72.36 |  |  | 75.01 |  |  |  | 8.98 |  | 7.32 | [8 empty] | 18.49 |  |  |  |  | 1.38
1990 |  |  |  | 6129.16 |  |  | 7499 |  |  |  | 915 | [10 empty] | 85.18 |  |  |  | 87.48 | [5 empty] | 76.47 |  |  | 85.61 |  |  |  | 1.04 |  | 0.92 | [8 empty] | 11.60 |  |  |  |  | 2.30
1991 |  |  |  | 6003.22 |  |  | 7374 |  |  |  | 915 | [10 empty] | 84.75 |  |  |  | 85.16 | [5 empty] | 74.90 |  |  | 84.18 |  |  |  | 2.27 |  | 1.97 | [8 empty] | 12.87 |  |  |  |  | 0.41
1992 |  |  |  | 5174.61 |  |  | 6323 |  |  |  | 915 | [10 empty] | 70.99 |  |  |  | 73.16 | [5 empty] | 64.38 |  |  | 71.98 |  |  |  | 9.76 |  | 7.91 | [8 empty] | 18.93 |  |  |  |  | 2.17
1993 |  |  |  | 5715.35 |  |  | 7232 |  |  |  | 915 | [10 empty] | 73.91 |  |  |  | 85.66 | [5 empty] | 71.30 |  |  | 82.56 |  |  |  | 2.81 |  | 2.47 | [8 empty] | 11.87 |  |  |  |  | 11.75
1994 |  |  |  | 5013.99 |  |  | 6428 |  |  |  | 915 | [10 empty] | 78.11 |  |  |  | 78.86 | [5 empty] | 62.55 |  |  | 73.38 |  |  |  | 0.72 |  | 0.57 | [8 empty] | 20.57 |  |  |  |  | 0.75
1995 |  |  |  | 6032.66 |  |  | 7525 |  |  |  | 915 | [10 empty] | 84.28 |  |  |  | 89.56 | [5 empty] | 75.26 |  |  | 85.90 |  |  |  | 0.94 |  | 0.85 | [8 empty] | 9.59 |  |  |  |  | 5.29
1996 |  |  |  | 5882.20 |  |  | 7724 |  |  |  | 915 | [10 empty] | 91.89 |  |  |  | 99.67 | [5 empty] | 73.19 |  |  | 87.93 |  |  |  | 0.22 |  | 0.22 | [8 empty] | 0.11 |  |  |  |  | 7.78
1997 |  |  |  | 5347.79 |  |  | 6961 |  |  |  | 915 | [10 empty] | 80.20 |  |  |  | 86.11 | [5 empty] | 66.72 |  |  | 79.46 |  |  |  | 0.27 |  | 0.24 | [8 empty] | 13.66 |  |  |  |  | 5.91
1998 |  |  |  | 6281.40 |  |  | 7758 |  |  |  | 915 | [10 empty] | 78.69 |  |  |  | 81.74 | [5 empty] | 78.37 |  |  | 88.56 |  |  |  | 7.63 |  | 6.75 | [8 empty] | 11.51 |  |  |  |  | 3.05
1999 |  |  |  | 6316.70 |  |  | 7654 |  |  |  | 915 | [10 empty] | 87.83 |  |  |  | 89.77 | [5 empty] | 78.81 |  |  | 87.37 |  |  |  | 2.25 |  | 2.07 | [8 empty] | 8.17 |  |  |  |  | 1.93
2000 |  |  |  | 5493.99 |  |  | 6914 |  |  |  | 915 | [10 empty] | 78.98 |  |  |  | 81.39 | [5 empty] | 68.36 |  |  | 78.71 |  |  |  | 6.81 |  | 5.94 | [8 empty] | 12.67 |  |  |  |  | 2.40
2001 |  |  |  | 5867.85 |  |  | 7254 |  |  |  | 915 | [10 empty] | 79.61 |  |  |  | 82.12 | [5 empty] | 73.21 |  |  | 82.81 |  |  |  | 8.89 |  | 8.02 | [8 empty] | 9.86 |  |  |  |  | 2.51
2002 |  |  |  | 6052.00 |  |  | 7307 |  |  |  | 915 | [10 empty] | 80.94 |  |  |  | 82.10 | [5 empty] | 75.50 |  |  | 83.41 |  |  |  | 6.56 |  | 5.77 | [8 empty] | 12.14 |  |  |  |  | 1.16
2003 |  |  |  | 5779.36 |  |  | 7146 |  |  |  | 915 | [10 empty] | 76.75 |  |  |  | 79.21 | [5 empty] | 72.10 |  |  | 81.58 |  |  |  | 7.77 |  | 6.67 | [8 empty] | 14.13 |  |  |  |  | 2.45
2004 |  |  |  | 5081.25 |  |  | 6074 |  |  |  | 915 | [10 empty] | 64.07 |  |  |  | 65.92 | [5 empty] | 63.22 |  |  | 69.15 |  |  |  | 12.26 |  | 9.21 | [8 empty] | 24.87 |  |  |  |  | 1.85
2005 |  |  |  | 6941.58 |  |  | 7863 |  |  |  | 915 | [10 empty] | 87.79 |  |  |  | 88.28 | [5 empty] | 86.59 |  |  | 89.75 |  |  |  | 2.66 |  | 3.72 | [8 empty] | 8.00 |  |  |  |  | 0.49
2006 |  |  |  | 6487.52 |  |  | 7520 |  |  |  | 915 | [10 empty] | 83.06 |  |  |  | 83.49 | [5 empty] | 80.94 |  |  | 85.84 |  |  |  | 2.45 |  | 4.95 | [8 empty] | 11.56 |  |  |  |  | 0.43
2007 |  |  |  | 5435.78 |  |  | 6456 |  |  |  | 915 | [10 empty] | 68.07 |  |  |  | 71.39 | [5 empty] | 67.82 |  |  | 73.70 |  |  |  | 5.03 |  | 14.99 | [8 empty] | 13.62 |  |  |  |  | 3.32
2008 |  |  |  | 4858.57 |  |  | 5750 |  |  |  | 915 | [10 empty] | 60.85 |  |  |  | 61.00 | [5 empty] | 60.45 |  |  | 65.46 |  |  |  | 6.02 |  | 20.85 | [8 empty] | 18.16 |  |  |  |  | 0.14
2009 |  |  |  | 6365.97 |  |  | 7392 |  |  |  | 915 | [10 empty] | 79.89 |  |  |  | 84.35 | [5 empty] | 79.42 |  |  | 84.38 |  |  |  | 5.10 |  | 7.58 | [8 empty] | 8.07 |  |  |  |  | 4.45
2010 |  |  |  | 6277.78 |  |  | 7004 |  |  |  | 915 | [10 empty] | 78.27 |  |  |  | 79.59 | [5 empty] | 78.32 |  |  | 79.95 |  |  |  | 3.10 |  | 7.69 | [8 empty] | 12.72 |  |  |  |  | 1.32
2011 |  |  |  | 6741.60 |  |  | 7580 |  |  |  | 915 | [10 empty] | 85.02 |  |  |  | 85.72 | [5 empty] | 84.11 |  |  | 86.53 |  |  |  | 5.39 |  | 7.15 | [8 empty] | 7.14 |  |  |  |  | 0.70
2012 |  |  |  | 5106.74 |  |  | 5899 |  |  |  | 915 | [10 empty] | 64.48 |  |  |  | 83.03 | [5 empty] | 63.54 |  |  | 67.16 |  |  |  | 2.31 |  | 2.90 | [8 empty] | 14.07 |  |  |  |  | 18.55
2013 |  |  |  | 6866.75 |  |  | 7750 |  |  |  | 915 | [10 empty] | 88.16 |  |  |  | 89.86 | [5 empty] | 85.67 |  |  | 88.47 |  |  |  | 0.32 |  | 1.26 | [8 empty] | 8.88 |  |  |  |  | 1.70
2014 |  |  |  | 4529.71 |  |  | 5148 |  |  |  | 915 | [10 empty] | 57.11 |  |  |  | 58.35 | [5 empty] | 56.51 |  |  | 58.77 |  |  |  | 1.09 |  | 12.03 | [8 empty] | 29.62 |  |  |  |  | 1.24
2015 |  |  |  | 6297.99 |  |  | 7085 |  |  |  | 915 | [10 empty] | 78.71 |  |  |  | 79.01 | [5 empty] | 78.57 |  |  | 80.88 |  |  |  | 11.58 |  | 12.23 | [8 empty] | 8.76 |  |  |  |  | 0.30
2016 |  |  |  | 4910.49 |  |  | 6144 |  |  |  | 915 | [10 empty] | 61.26 |  |  |  | 61.76 | [5 empty] | 61.10 |  |  | 69.95 |  |  |  | 6.85 |  | 22.17 | [8 empty] | 16.07 |  |  |  |  | 0.50
2017 |  |  |  | 6067.31 |  |  | 6910 |  |  |  | 915 | [10 empty] | 75.99 |  |  |  | 77.24 | [5 empty] | 75.70 |  |  | 78.88 |  |  |  | 3.27 |  | 14.04 | [8 empty] | 8.71 |  |  |  |  | 1.25
2018 |  |  |  | 5672.76 |  |  | 6425 |  |  |  | 915 | [10 empty] | 70.87 |  |  |  | 71.89 | [5 empty] | 70.77 |  |  | 73.34 |  |  |  | 5.03 |  | 10.67 | [8 empty] | 17.44 |  |  |  |  | 1.02
2019 |  |  |  | 5632.07 |  |  | 6451 |  |  |  | 915 | [10 empty] | 70.96 |  |  |  | 99.01 | [5 empty] | 70.27 |  |  | 73.64 |  |  |  | 0.87 |  | 0.87 | [8 empty] | 0.12 |  |  |  |  | 28.05
2020 |  |  |  | 4171.74 |  |  | 4917 |  |  |  | 915 | [10 empty] | 52.12 |  |  |  | 57.98 | [5 empty] | 51.90 |  |  | 55.98 |  |  |  | 0.83 |  | 17.00 | [8 empty] | 25.02 |  |  |  |  | 5.87
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 311
B. |  | Refuelling without maintenance | [35 empty] | 107
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 873 |  |  |  | 23
D. |  | Inspection, maintenance or repair without refuelling | [39 empty] | 4
E. |  | Testing of plant systems or components | [35 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 71
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 23
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 51
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 43
Z. |  | Other | [39 empty] | 53 | [11 empty] | 13
Subtotal | [37 empty] | 986 |  |  |  | 462 | [11 empty] | 135
Total | [22 empty] | 0 | [14 empty] | 1583
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 24
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 15
14. |  |  | Safety Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 60
16. |  |  | Steam generation systems | [34 empty] | 21
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 49
32. |  |  | Feedwater and Main Steam System | [34 empty] | 12
34. |  |  | Miscellaneous Systems | [34 empty] | 77
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 16
42. |  |  | Electrical Power Supply Systems | [34 empty] | 30
Total | [37 empty] | 331

## CRUAS-4
2020 Operating Experience
FR-45 | [8 empty] | CRUAS-4 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP2 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-10-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-10-27
Gross electrical power | [12 empty] | : |  |  | 956 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-02-11
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5265.57 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 65.86 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.79 %
Unit Capability Factor (UCF) | [18 empty] | : | 71.21 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.99 %
Load Factor (LF) | [18 empty] | : | 65.51 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 5.35 %
Operating Factor (OF) | [18 empty] | : | 71.29 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2522 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 659.52 | 569.17 |  |  |  | 673.37 |  | 650.80 | [8 empty] | 665.07 |  |  | 629.73 | [6 empty] | 564.19 |  | 220.12 |  |  |  | 0.00 |  |  | 0.00 |  |  | 52.75 | [9 empty] | 580.85 |  |  | 5265.57
EAF [%] |  |  |  |  | 97.23 | 91.91 |  |  |  | 99.32 |  | 99.63 | [8 empty] | 98.25 |  |  | 95.60 | [6 empty] | 82.86 |  | 32.35 |  |  |  | 0.00 |  |  | 0.00 |  |  | 8.01 | [9 empty] | 85.09 |  |  | 65.86
UCF [%] |  |  |  |  | 99.93 | 99.44 |  |  |  | 99.32 |  | 99.88 | [8 empty] | 98.90 |  |  | 99.63 | [6 empty] | 99.84 |  | 50.17 |  |  |  | 0.00 |  |  | 0.00 |  |  | 8.01 | [9 empty] | 98.91 |  |  | 71.21
LF [%] |  |  |  |  | 96.88 | 89.37 |  |  |  | 99.05 |  | 98.79 | [8 empty] | 97.70 |  |  | 95.59 | [6 empty] | 82.88 |  | 32.33 |  |  |  | 0.00 |  |  | 0.00 |  |  | 8.01 | [9 empty] | 85.32 |  |  | 65.51
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 45.03 |  |  |  | 0.00 |  |  | 0.00 |  |  | 23.89 | [9 empty] | 86.56 |  |  | 71.29
FLR [%] |  |  |  |  | 0.04 | 0.47 |  |  |  | 0.02 |  | 0.06 | [8 empty] | 0.91 |  |  | 0.27 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 47.03 | [9 empty] | 0.11 |  |  | 1.03
UCL [%] |  |  |  |  | 0.04 | 0.47 |  |  |  | 0.02 |  | 0.06 | [8 empty] | 0.91 |  |  | 0.27 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 9.66 |  |  | 83.17 | [9 empty] | 0.11 |  |  | 7.79
PUF [%] |  |  |  |  | 0.03 | 0.09 |  |  |  | 0.67 |  | 0.06 | [8 empty] | 0.18 |  |  | 0.10 | [6 empty] | 0.16 |  | 49.83 |  |  |  | 100.00 |  |  | 90.34 |  |  | 8.82 | [9 empty] | 0.98 |  |  | 20.99
XUF [%] |  |  |  |  | 2.70 | 7.52 |  |  |  | 0.00 |  | 0.25 | [8 empty] | 0.65 |  |  | 4.03 | [6 empty] | 16.98 |  | 17.83 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 13.82 |  |  | 5.35
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 204873.12 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.72 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.77 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.19 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.03 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.39 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.48 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 5773.60 |  |  | 7434 |  |  |  | 880 | [10 empty] | 85.67 |  |  |  | 87.12 | [5 empty] | 73.53 |  |  | 84.32 |  |  |  | 12.88 |  | 12.88 | [8 empty] | 0.00 |  |  |  |  | 1.45
1986 |  |  |  | 5452.60 |  |  | 6816 |  |  |  | 880 | [10 empty] | 76.67 |  |  |  | 80.33 | [5 empty] | 70.73 |  |  | 77.81 |  |  |  | 0.60 |  | 0.48 | [8 empty] | 19.18 |  |  |  |  | 3.66
1987 |  |  |  | 5313.40 |  |  | 6888 |  |  |  | 880 | [10 empty] | 84.24 |  |  |  | 85.14 | [5 empty] | 68.93 |  |  | 78.63 |  |  |  | 4.76 |  | 4.25 | [8 empty] | 10.60 |  |  |  |  | 0.90
1988 |  |  |  | 3247.00 |  |  | 4271 |  |  |  | 880 | [10 empty] | 74.17 |  |  |  | 75.95 | [5 empty] | 42.01 |  |  | 48.62 |  |  |  | 15.53 |  | 13.96 | [8 empty] | 10.09 |  |  |  |  | 1.79
1989 |  |  |  | 4852.19 |  |  | 6025 |  |  |  | 880 | [10 empty] | 71.30 |  |  |  | 71.43 | [5 empty] | 62.94 |  |  | 68.78 |  |  |  | 17.85 |  | 15.52 | [8 empty] | 13.05 |  |  |  |  | 0.14
1990 |  |  |  | 6215.34 |  |  | 7607 |  |  |  | 880 | [10 empty] | 86.02 |  |  |  | 86.39 | [5 empty] | 80.63 |  |  | 86.84 |  |  |  | 8.69 |  | 8.23 | [8 empty] | 5.38 |  |  |  |  | 0.38
1991 |  |  |  | 6005.38 |  |  | 7259 |  |  |  | 880 | [10 empty] | 81.10 |  |  |  | 83.93 | [5 empty] | 77.90 |  |  | 82.87 |  |  |  | 8.63 |  | 7.93 | [8 empty] | 8.13 |  |  |  |  | 2.83
1992 |  |  |  | 4953.60 |  |  | 5862 |  |  |  | 880 | [10 empty] | 64.95 |  |  |  | 66.00 | [5 empty] | 64.08 |  |  | 66.73 |  |  |  | 13.05 |  | 9.90 | [8 empty] | 24.10 |  |  |  |  | 1.04
1993 |  |  |  | 5279.97 |  |  | 6653 |  |  |  | 880 | [10 empty] | 77.14 |  |  |  | 84.92 | [5 empty] | 68.49 |  |  | 75.95 |  |  |  | 2.69 |  | 2.35 | [8 empty] | 12.73 |  |  |  |  | 7.78
1994 |  |  |  | 5552.11 |  |  | 6856 |  |  |  | 915 | [10 empty] | 83.79 |  |  |  | 86.83 | [5 empty] | 69.27 |  |  | 78.26 |  |  |  | 2.94 |  | 2.63 | [8 empty] | 10.54 |  |  |  |  | 3.04
1995 |  |  |  | 6280.30 |  |  | 7375 |  |  |  | 915 | [10 empty] | 82.14 |  |  |  | 85.97 | [5 empty] | 78.35 |  |  | 84.19 |  |  |  | 4.78 |  | 4.31 | [8 empty] | 9.71 |  |  |  |  | 3.83
1996 |  |  |  | 5886.51 |  |  | 7180 |  |  |  | 915 | [10 empty] | 79.43 |  |  |  | 80.67 | [5 empty] | 73.24 |  |  | 81.74 |  |  |  | 0.71 |  | 0.58 | [8 empty] | 18.75 |  |  |  |  | 1.24
1997 |  |  |  | 5976.62 |  |  | 7334 |  |  |  | 915 | [10 empty] | 80.23 |  |  |  | 84.06 | [5 empty] | 74.56 |  |  | 83.72 |  |  |  | 1.47 |  | 1.25 | [8 empty] | 14.69 |  |  |  |  | 3.83
1998 |  |  |  | 6629.20 |  |  | 7885 |  |  |  | 915 | [10 empty] | 85.52 |  |  |  | 88.69 | [5 empty] | 82.71 |  |  | 90.01 |  |  |  | 0.97 |  | 0.87 | [8 empty] | 10.43 |  |  |  |  | 3.18
1999 |  |  |  | 5829.81 |  |  | 7159 |  |  |  | 915 | [10 empty] | 81.90 |  |  |  | 85.43 | [5 empty] | 72.73 |  |  | 81.72 |  |  |  | 1.81 |  | 1.57 | [8 empty] | 13.00 |  |  |  |  | 3.53
2000 |  |  |  | 6630.69 |  |  | 7915 |  |  |  | 915 | [10 empty] | 88.43 |  |  |  | 89.66 | [5 empty] | 82.50 |  |  | 90.11 |  |  |  | 0.72 |  | 0.65 | [8 empty] | 9.69 |  |  |  |  | 1.22
2001 |  |  |  | 5915.77 |  |  | 7172 |  |  |  | 915 | [10 empty] | 80.63 |  |  |  | 83.26 | [5 empty] | 73.81 |  |  | 81.87 |  |  |  | 2.82 |  | 2.42 | [8 empty] | 14.32 |  |  |  |  | 2.63
2002 |  |  |  | 6399.58 |  |  | 7474 |  |  |  | 915 | [10 empty] | 82.89 |  |  |  | 83.41 | [5 empty] | 79.84 |  |  | 85.32 |  |  |  | 3.93 |  | 3.41 | [8 empty] | 13.18 |  |  |  |  | 0.53
2003 |  |  |  | 6296.69 |  |  | 7371 |  |  |  | 915 | [10 empty] | 81.63 |  |  |  | 82.86 | [5 empty] | 78.56 |  |  | 84.14 |  |  |  | 5.97 |  | 5.26 | [8 empty] | 11.88 |  |  |  |  | 1.23
2004 |  |  |  | 6377.38 |  |  | 7443 |  |  |  | 915 | [10 empty] | 80.62 |  |  |  | 83.44 | [5 empty] | 79.35 |  |  | 84.73 |  |  |  | 4.36 |  | 3.80 | [8 empty] | 12.75 |  |  |  |  | 2.82
2005 |  |  |  | 6255.06 |  |  | 7360 |  |  |  | 915 | [10 empty] | 79.62 |  |  |  | 81.58 | [5 empty] | 78.04 |  |  | 84.02 |  |  |  | 10.98 |  | 10.06 | [8 empty] | 8.35 |  |  |  |  | 1.96
2006 |  |  |  | 3752.65 |  |  | 4259 |  |  |  | 915 | [10 empty] | 47.64 |  |  |  | 47.64 | [5 empty] | 46.82 |  |  | 48.62 |  |  |  | 21.85 |  | 29.21 | [8 empty] | 23.15 |  |  |  |  | 0.00
2007 |  |  |  | 4947.25 |  |  | 5839 |  |  |  | 915 | [10 empty] | 61.73 |  |  |  | 61.97 | [5 empty] | 61.72 |  |  | 66.66 |  |  |  | 5.80 |  | 5.03 | [8 empty] | 33.00 |  |  |  |  | 0.24
2008 |  |  |  | 6228.77 |  |  | 7011 |  |  |  | 915 | [10 empty] | 77.36 |  |  |  | 78.52 | [5 empty] | 77.50 |  |  | 79.82 |  |  |  | 0.47 |  | 8.84 | [8 empty] | 12.64 |  |  |  |  | 1.16
2009 |  |  |  | 6321.83 |  |  | 7347 |  |  |  | 915 | [10 empty] | 79.49 |  |  |  | 86.09 | [5 empty] | 78.87 |  |  | 83.87 |  |  |  | 1.17 |  | 4.77 | [8 empty] | 9.14 |  |  |  |  | 6.60
2010 |  |  |  | 5107.05 |  |  | 5779 |  |  |  | 915 | [10 empty] | 63.76 |  |  |  | 67.48 | [5 empty] | 63.72 |  |  | 65.97 |  |  |  | 3.99 |  | 18.93 | [8 empty] | 13.60 |  |  |  |  | 3.72
2011 |  |  |  | 7152.54 |  |  | 7938 |  |  |  | 915 | [10 empty] | 89.16 |  |  |  | 89.73 | [5 empty] | 89.23 |  |  | 90.62 |  |  |  | 0.83 |  | 3.06 | [8 empty] | 7.21 |  |  |  |  | 0.57
2012 |  |  |  | 4305.94 |  |  | 4853 |  |  |  | 915 | [10 empty] | 53.33 |  |  |  | 61.67 | [5 empty] | 53.57 |  |  | 55.25 |  |  |  | 0.78 |  | 24.41 | [8 empty] | 13.91 |  |  |  |  | 8.34
2013 |  |  |  | 6916.18 |  |  | 7727 |  |  |  | 915 | [10 empty] | 86.05 |  |  |  | 86.62 | [5 empty] | 86.29 |  |  | 88.21 |  |  |  | 0.72 |  | 5.31 | [8 empty] | 8.07 |  |  |  |  | 0.57
2014 |  |  |  | 4677.86 |  |  | 5611 |  |  |  | 915 | [10 empty] | 58.41 |  |  |  | 60.46 | [5 empty] | 58.36 |  |  | 64.05 |  |  |  | 2.88 |  | 7.31 | [8 empty] | 32.23 |  |  |  |  | 2.05
2015 |  |  |  | 6465.66 |  |  | 7267 |  |  |  | 915 | [10 empty] | 81.10 |  |  |  | 81.88 | [5 empty] | 80.67 |  |  | 82.96 |  |  |  | 8.14 |  | 8.35 | [8 empty] | 9.77 |  |  |  |  | 0.78
2016 |  |  |  | 4642.10 |  |  | 5435 |  |  |  | 915 | [10 empty] | 57.68 |  |  |  | 58.89 | [5 empty] | 57.76 |  |  | 61.87 |  |  |  | 8.02 |  | 10.04 | [8 empty] | 31.07 |  |  |  |  | 1.20
2017 |  |  |  | 6395.66 |  |  | 7187 |  |  |  | 915 | [10 empty] | 80.24 |  |  |  | 80.72 | [5 empty] | 79.79 |  |  | 82.04 |  |  |  | 1.59 |  | 8.30 | [8 empty] | 10.97 |  |  |  |  | 0.49
2018 |  |  |  | 5094.14 |  |  | 5821 |  |  |  | 915 | [10 empty] | 63.65 |  |  |  | 64.08 | [5 empty] | 63.55 |  |  | 66.45 |  |  |  | 2.29 |  | 18.62 | [8 empty] | 17.30 |  |  |  |  | 0.43
2019 |  |  |  | 5902.70 |  |  | 7017 |  |  |  | 915 | [10 empty] | 73.89 |  |  |  | 82.37 | [5 empty] | 73.64 |  |  | 80.10 |  |  |  | 8.64 |  | 8.14 | [8 empty] | 9.48 |  |  |  |  | 8.48
2020 |  |  |  | 5265.57 |  |  | 6262 |  |  |  | 915 | [10 empty] | 65.86 |  |  |  | 71.21 | [5 empty] | 65.51 |  |  | 71.29 |  |  |  | 1.03 |  | 7.79 | [8 empty] | 20.99 |  |  |  |  | 5.35
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 472
B. |  | Refuelling without maintenance | [35 empty] | 164
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 814 |  |  |  | 38
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 7
E. |  | Testing of plant systems or components | [35 empty] | 9 |  |  |  | 2
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 74
H. |  | Nuclear regulatory requirements | [39 empty] | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 18
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 26
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 67
Z. |  | Other | [39 empty] | 24
Subtotal | [37 empty] | 1068 |  |  |  | 556 | [11 empty] | 94
Total | [22 empty] | 0 | [14 empty] | 1718
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 25
14. |  |  | Safety Systems | [34 empty] | 20
15. |  |  | Reactor Cooling Systems | [34 empty] | 34
16. |  |  | Steam generation systems | [34 empty] | 92
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 76
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
34. |  |  | Miscellaneous Systems | [34 empty] | 135
41. |  |  | Main Generator Systems | [34 empty] | 27
42. |  |  | Electrical Power Supply Systems | [34 empty] | 30
Total | [37 empty] | 472

## DAMPIERRE-1
2020 Operating Experience
FR-22 | [8 empty] | DAMPIERRE-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-02-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-03-23
Gross electrical power | [12 empty] | : |  |  | 937 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-09-10
Reference unit power (net) | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3511.39 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.66 %
Energy Availability Factor (EAF) | [18 empty] | : | 45.96 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.65 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.01 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.34 %
Load Factor (LF) | [18 empty] | : | 44.92 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 50.05 %
Operating Factor (OF) | [18 empty] | : | 47.03 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4653 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 659.70 | 532.18 |  |  |  | 589.53 |  | 480.08 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 16.45 |  |  | 606.44 | [9 empty] | 627.02 |  |  | 3511.39
EAF [%] |  |  |  |  | 99.92 | 86.40 |  |  |  | 90.13 |  | 78.30 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 2.50 |  |  | 96.87 | [9 empty] | 99.88 |  |  | 45.96
UCF [%] |  |  |  |  | 99.92 | 89.04 |  |  |  | 90.19 |  | 98.57 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 76.77 |  |  | 97.74 | [9 empty] | 99.88 |  |  | 96.01
LF [%] |  |  |  |  | 99.63 | 85.91 |  |  |  | 89.15 |  | 74.92 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 2.48 |  |  | 94.64 | [9 empty] | 94.69 |  |  | 44.92
OF [%] |  |  |  |  | 100.00 | 89.66 |  |  |  | 90.85 |  | 80.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 6.44 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 47.03
FLR [%] |  |  |  |  | 0.06 | 10.94 |  |  |  | 9.77 |  | 1.42 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 20.68 |  |  | 1.54 | [9 empty] | 0.12 |  |  | 3.66
UCL [%] |  |  |  |  | 0.06 | 10.94 |  |  |  | 9.76 |  | 1.42 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 20.02 |  |  | 1.53 | [9 empty] | 0.12 |  |  | 3.65
PUF [%] |  |  |  |  | 0.01 | 0.02 |  |  |  | 0.05 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 3.21 |  |  | 0.73 | [9 empty] | 0.00 |  |  | 0.34
XUF [%] |  |  |  |  | 0.00 | 2.65 |  |  |  | 0.06 |  | 20.27 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 74.27 |  |  | 0.87 | [9 empty] | 0.00 |  |  | 50.05
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 227598.56 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.02 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.52 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.33 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.06 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.52 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.08 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 2764.00 |  |  | 3950 |  |  |  | 898 | [10 empty] | 61.91 |  |  |  | 61.91 | [5 empty] | 69.14 |  |  | 73.12 |  |  |  | 5.60 |  | 3.67 | [8 empty] | 34.41 |  |  |  |  | 0.00
1981 |  |  |  | 4322.10 |  |  | 5270 |  |  |  | 900 | [10 empty] | 55.90 |  |  |  | 55.90 | [5 empty] | 54.82 |  |  | 60.16 |  |  |  | 14.79 |  | 9.70 | [8 empty] | 34.39 |  |  |  |  | 0.00
1982 |  |  |  | 5043.90 |  |  | 5994 |  |  |  | 890 | [10 empty] | 65.56 |  |  |  | 65.56 | [5 empty] | 64.70 |  |  | 68.42 |  |  |  | 20.59 |  | 17.00 | [8 empty] | 17.43 |  |  |  |  | 0.00
1983 |  |  |  | 6263.00 |  |  | 7847 |  |  |  | 890 | [10 empty] | 85.88 |  |  |  | 85.88 | [5 empty] | 80.33 |  |  | 89.58 |  |  |  | 14.12 |  | 14.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 5391.00 |  |  | 6777 |  |  |  | 890 | [10 empty] | 73.61 |  |  |  | 73.61 | [5 empty] | 68.96 |  |  | 77.15 |  |  |  | 9.12 |  | 7.38 | [8 empty] | 19.01 |  |  |  |  | 0.00
1985 |  |  |  | 5738.50 |  |  | 7223 |  |  |  | 890 | [10 empty] | 80.64 |  |  |  | 80.91 | [5 empty] | 73.60 |  |  | 82.45 |  |  |  | 7.64 |  | 6.69 | [8 empty] | 12.40 |  |  |  |  | 0.27
1986 |  |  |  | 5157.40 |  |  | 6673 |  |  |  | 890 | [10 empty] | 75.73 |  |  |  | 75.91 | [5 empty] | 66.15 |  |  | 76.18 |  |  |  | 5.33 |  | 4.27 | [8 empty] | 19.82 |  |  |  |  | 0.18
1987 |  |  |  | 4780.20 |  |  | 6245 |  |  |  | 890 | [10 empty] | 65.93 |  |  |  | 67.88 | [5 empty] | 61.31 |  |  | 71.29 |  |  |  | 12.79 |  | 9.96 | [8 empty] | 22.16 |  |  |  |  | 1.95
1988 |  |  |  | 3920.00 |  |  | 5239 |  |  |  | 890 | [10 empty] | 59.60 |  |  |  | 61.15 | [5 empty] | 50.14 |  |  | 59.64 |  |  |  | 25.06 |  | 20.45 | [8 empty] | 18.39 |  |  |  |  | 1.55
1989 |  |  |  | 6467.63 |  |  | 8207 |  |  |  | 890 | [10 empty] | 97.86 |  |  |  | 98.65 | [5 empty] | 82.96 |  |  | 93.69 |  |  |  | 1.22 |  | 1.22 | [8 empty] | 0.13 |  |  |  |  | 0.79
1990 |  |  |  | 2187.08 |  |  | 3110 |  |  |  | 890 | [10 empty] | 33.96 |  |  |  | 36.33 | [5 empty] | 28.05 |  |  | 35.50 |  |  |  | 6.49 |  | 2.52 | [8 empty] | 61.15 |  |  |  |  | 2.37
1991 |  |  |  | 6390.92 |  |  | 7305 |  |  |  | 890 | [10 empty] | 81.80 |  |  |  | 82.25 | [5 empty] | 81.97 |  |  | 83.39 |  |  |  | 5.49 |  | 4.78 | [8 empty] | 12.97 |  |  |  |  | 0.45
1992 |  |  |  | 6305.06 |  |  | 7293 |  |  |  | 890 | [10 empty] | 80.73 |  |  |  | 81.73 | [5 empty] | 80.65 |  |  | 83.03 |  |  |  | 1.93 |  | 1.61 | [8 empty] | 16.66 |  |  |  |  | 1.00
1993 |  |  |  | 6702.80 |  |  | 7676 |  |  |  | 890 | [10 empty] | 86.38 |  |  |  | 86.64 | [5 empty] | 85.97 |  |  | 87.63 |  |  |  | 2.63 |  | 2.34 | [8 empty] | 11.02 |  |  |  |  | 0.26
1994 |  |  |  | 5299.19 |  |  | 6185 |  |  |  | 890 | [10 empty] | 68.88 |  |  |  | 69.68 | [5 empty] | 67.97 |  |  | 70.61 |  |  |  | 20.96 |  | 18.48 | [8 empty] | 11.85 |  |  |  |  | 0.80
1995 |  |  |  | 6193.95 |  |  | 7413 |  |  |  | 890 | [10 empty] | 82.91 |  |  |  | 84.36 | [5 empty] | 79.45 |  |  | 84.62 |  |  |  | 4.82 |  | 4.27 | [8 empty] | 11.37 |  |  |  |  | 1.44
1996 |  |  |  | 5895.50 |  |  | 7378 |  |  |  | 890 | [10 empty] | 82.24 |  |  |  | 83.11 | [5 empty] | 75.41 |  |  | 83.99 |  |  |  | 5.96 |  | 5.27 | [8 empty] | 11.62 |  |  |  |  | 0.88
1997 |  |  |  | 5172.13 |  |  | 6465 |  |  |  | 890 | [10 empty] | 71.92 |  |  |  | 72.27 | [5 empty] | 66.34 |  |  | 73.80 |  |  |  | 14.89 |  | 12.65 | [8 empty] | 15.08 |  |  |  |  | 0.35
1998 |  |  |  | 6042.70 |  |  | 7294 |  |  |  | 890 | [10 empty] | 80.53 |  |  |  | 81.91 | [5 empty] | 77.51 |  |  | 83.26 |  |  |  | 5.07 |  | 4.38 | [8 empty] | 13.71 |  |  |  |  | 1.39
1999 |  |  |  | 5492.41 |  |  | 6815 |  |  |  | 890 | [10 empty] | 75.31 |  |  |  | 76.85 | [5 empty] | 70.45 |  |  | 77.80 |  |  |  | 15.21 |  | 13.79 | [8 empty] | 9.36 |  |  |  |  | 1.54
2000 |  |  |  | 6153.75 |  |  | 7676 |  |  |  | 890 | [10 empty] | 85.40 |  |  |  | 87.01 | [5 empty] | 78.72 |  |  | 87.39 |  |  |  | 1.08 |  | 0.95 | [8 empty] | 12.04 |  |  |  |  | 1.61
2001 |  |  |  | 4125.07 |  |  | 5152 |  |  |  | 890 | [10 empty] | 56.67 |  |  |  | 56.75 | [5 empty] | 52.91 |  |  | 58.81 |  |  |  | 35.87 |  | 31.74 | [8 empty] | 11.50 |  |  |  |  | 0.09
2002 |  |  |  | 6249.59 |  |  | 7586 |  |  |  | 890 | [10 empty] | 86.84 |  |  |  | 87.56 | [5 empty] | 80.16 |  |  | 86.60 |  |  |  | 0.58 |  | 1.91 | [8 empty] | 10.54 |  |  |  |  | 0.72
2003 |  |  |  | 5733.30 |  |  | 6964 |  |  |  | 890 | [10 empty] | 76.79 |  |  |  | 78.32 | [5 empty] | 73.54 |  |  | 79.50 |  |  |  | 10.57 |  | 9.26 | [8 empty] | 12.42 |  |  |  |  | 1.53
2004 |  |  |  | 6091.18 |  |  | 7840 |  |  |  | 890 | [10 empty] | 89.26 |  |  |  | 89.71 | [5 empty] | 77.91 |  |  | 89.25 |  |  |  | 1.97 |  | 1.81 | [8 empty] | 8.48 |  |  |  |  | 0.45
2005 |  |  |  | 5838.83 |  |  | 7554 |  |  |  | 890 | [10 empty] | 82.84 |  |  |  | 85.19 | [5 empty] | 74.89 |  |  | 86.23 |  |  |  | 1.46 |  | 3.00 | [8 empty] | 11.81 |  |  |  |  | 2.35
2006 |  |  |  | 6615.07 |  |  | 8077 |  |  |  | 890 | [10 empty] | 88.56 |  |  |  | 91.15 | [5 empty] | 84.85 |  |  | 92.20 |  |  |  | 0.96 |  | 0.89 | [8 empty] | 7.96 |  |  |  |  | 2.59
2007 |  |  |  | 6050.04 |  |  | 7329 |  |  |  | 890 | [10 empty] | 80.66 |  |  |  | 82.56 | [5 empty] | 77.60 |  |  | 83.66 |  |  |  | 0.92 |  | 5.59 | [8 empty] | 11.84 |  |  |  |  | 1.90
2008 |  |  |  | 6545.33 |  |  | 8051 |  |  |  | 890 | [10 empty] | 89.68 |  |  |  | 90.71 | [5 empty] | 83.72 |  |  | 91.66 |  |  |  | 1.59 |  | 2.47 | [8 empty] | 6.82 |  |  |  |  | 1.03
2009 |  |  |  | 4973.23 |  |  | 6048 |  |  |  | 890 | [10 empty] | 66.69 |  |  |  | 77.56 | [5 empty] | 63.79 |  |  | 69.04 |  |  |  | 7.83 |  | 8.58 | [8 empty] | 13.86 |  |  |  |  | 10.87
2010 |  |  |  | 6357.03 |  |  | 7511 |  |  |  | 890 | [10 empty] | 83.94 |  |  |  | 84.85 | [5 empty] | 81.54 |  |  | 85.74 |  |  |  | 2.34 |  | 7.82 | [8 empty] | 7.33 |  |  |  |  | 0.91
2011 |  |  |  | 5426.06 |  |  | 6373 |  |  |  | 890 | [10 empty] | 70.74 |  |  |  | 71.18 | [5 empty] | 69.60 |  |  | 72.75 |  |  |  | 1.60 |  | 3.20 | [8 empty] | 25.62 |  |  |  |  | 0.43
2012 |  |  |  | 6464.50 |  |  | 7623 |  |  |  | 890 | [10 empty] | 84.47 |  |  |  | 86.10 | [5 empty] | 82.69 |  |  | 86.78 |  |  |  | 0.74 |  | 2.69 | [8 empty] | 11.21 |  |  |  |  | 1.63
2013 |  |  |  | 5072.13 |  |  | 5882 |  |  |  | 890 | [10 empty] | 65.93 |  |  |  | 66.35 | [5 empty] | 65.06 |  |  | 67.15 |  |  |  | 3.87 |  | 19.87 | [8 empty] | 13.78 |  |  |  |  | 0.42
2014 |  |  |  | 6775.73 |  |  | 7927 |  |  |  | 890 | [10 empty] | 87.71 |  |  |  | 89.35 | [5 empty] | 86.91 |  |  | 90.49 |  |  |  | 0.64 |  | 1.87 | [8 empty] | 8.78 |  |  |  |  | 1.64
2015 |  |  |  | 6035.49 |  |  | 7168 |  |  |  | 890 | [10 empty] | 78.68 |  |  |  | 80.56 | [5 empty] | 77.41 |  |  | 81.83 |  |  |  | 1.62 |  | 1.33 | [8 empty] | 18.11 |  |  |  |  | 1.89
2016 |  |  |  | 6803.89 |  |  | 8073 |  |  |  | 890 | [10 empty] | 89.34 |  |  |  | 90.51 | [5 empty] | 87.03 |  |  | 91.91 |  |  |  | 0.77 |  | 0.92 | [8 empty] | 8.56 |  |  |  |  | 1.18
2017 |  |  |  | 6000.03 |  |  | 7027 |  |  |  | 890 | [10 empty] | 78.72 |  |  |  | 79.99 | [5 empty] | 76.96 |  |  | 80.22 |  |  |  | 0.30 |  | 3.42 | [8 empty] | 16.59 |  |  |  |  | 1.27
2018 |  |  |  | 6520.92 |  |  | 7824 |  |  |  | 890 | [10 empty] | 86.61 |  |  |  | 88.58 | [5 empty] | 83.64 |  |  | 89.32 |  |  |  | 1.40 |  | 2.23 | [8 empty] | 9.19 |  |  |  |  | 1.97
2019 |  |  |  | 4901.76 |  |  | 5699 |  |  |  | 890 | [10 empty] | 63.90 |  |  |  | 65.93 | [5 empty] | 62.87 |  |  | 65.06 |  |  |  | 10.34 |  | 12.95 | [8 empty] | 21.11 |  |  |  |  | 2.03
2020 |  |  |  | 3511.39 |  |  | 4131 |  |  |  | 890 | [10 empty] | 45.96 |  |  |  | 96.01 | [5 empty] | 44.92 |  |  | 47.03 |  |  |  | 3.66 |  | 3.65 | [8 empty] | 0.34 |  |  |  |  | 50.05
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1980 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 316
B. |  | Refuelling without maintenance | [35 empty] | 135
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1002 |  |  |  | 26
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 47 |  |  |  | 1
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 28
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 53
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 5 | [11 empty] | 1
Z. |  | Other | [39 empty] | 132
Subtotal | [37 empty] | 1186 |  |  |  | 509 | [11 empty] | 60
Total | [22 empty] | 0 | [14 empty] | 1755
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1980 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
12. |  |  | Reactor I&C Systems | [34 empty] | 29
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 12
14. |  |  | Safety Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 32
16. |  |  | Steam generation systems | [34 empty] | 38
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 15
32. |  |  | Feedwater and Main Steam System | [34 empty] | 22
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 82
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 44
42. |  |  | Electrical Power Supply Systems | [34 empty] | 18
Total | [37 empty] | 315

## DAMPIERRE-2
2020 Operating Experience
FR-29 | [8 empty] | DAMPIERRE-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-04-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-12-10
Gross electrical power | [12 empty] | : |  |  | 937 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-02-16
Reference unit power (net) | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5081.11 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 9.29 %
Energy Availability Factor (EAF) | [18 empty] | : | 63.08 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 13.96 %
Unit Capability Factor (UCF) | [18 empty] | : | 64.56 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.48 %
Load Factor (LF) | [18 empty] | : | 64.99 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.48 %
Operating Factor (OF) | [18 empty] | : | 68.44 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2772 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 663.12 | 614.42 |  |  |  | 682.67 |  | 650.58 | [8 empty] | 592.42 |  |  | 83.42 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 253.55 |  |  | 306.74 |  |  | 537.88 | [9 empty] | 696.30 |  |  | 5081.11
EAF [%] |  |  |  |  | 96.13 | 96.32 |  |  |  | 98.56 |  | 99.45 | [8 empty] | 89.47 |  |  | 13.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 38.53 |  |  | 45.49 |  |  | 81.62 | [9 empty] | 100.00 |  |  | 63.08
UCF [%] |  |  |  |  | 98.87 | 96.64 |  |  |  | 98.56 |  | 99.82 | [8 empty] | 99.97 |  |  | 16.60 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 38.53 |  |  | 45.49 |  |  | 81.70 | [9 empty] | 100.00 |  |  | 64.56
LF [%] |  |  |  |  | 100.15 | 99.19 |  |  |  | 103.24 |  | 101.53 | [8 empty] | 89.47 |  |  | 13.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 39.57 |  |  | 46.26 |  |  | 83.94 | [9 empty] | 105.16 |  |  | 64.99
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 16.67 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 47.08 |  |  | 59.33 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 68.44
FLR [%] |  |  |  |  | 1.11 | 3.35 |  |  |  | 1.44 |  | 0.18 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 54.51 |  |  | 18.25 | [9 empty] | 0.00 |  |  | 9.29
UCL [%] |  |  |  |  | 1.11 | 3.34 |  |  |  | 1.44 |  | 0.18 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 35.48 |  |  |  | 52.94 |  |  | 54.51 |  |  | 18.24 | [9 empty] | 0.00 |  |  | 13.96
PUF [%] |  |  |  |  | 0.03 | 0.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  | 83.40 | [6 empty] | 100.00 |  | 64.52 |  |  |  | 8.54 |  |  | 0.00 |  |  | 0.06 | [9 empty] | 0.00 |  |  | 21.48
XUF [%] |  |  |  |  | 2.73 | 0.32 |  |  |  | 0.00 |  | 0.37 | [8 empty] | 10.50 |  |  | 3.58 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.09 | [9 empty] | 0.00 |  |  | 1.48
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 222441.52 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.68 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.7 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.29 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.27 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.7 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.17 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 5818.40 |  |  | 7306 |  |  |  | 900 | [10 empty] | 75.54 |  |  |  | 75.54 | [5 empty] | 73.88 |  |  | 81.74 |  |  |  | 3.68 |  | 2.89 | [8 empty] | 21.58 |  |  |  |  | 0.00
1982 |  |  |  | 4110.80 |  |  | 4848 |  |  |  | 890 | [10 empty] | 53.04 |  |  |  | 53.04 | [5 empty] | 52.73 |  |  | 55.34 |  |  |  | 19.31 |  | 12.69 | [8 empty] | 34.27 |  |  |  |  | 0.00
1983 |  |  |  | 5191.00 |  |  | 6139 |  |  |  | 890 | [10 empty] | 67.67 |  |  |  | 67.67 | [5 empty] | 66.58 |  |  | 70.08 |  |  |  | 13.96 |  | 10.98 | [8 empty] | 21.36 |  |  |  |  | 0.00
1984 |  |  |  | 5781.00 |  |  | 6884 |  |  |  | 890 | [10 empty] | 76.07 |  |  |  | 76.07 | [5 empty] | 73.95 |  |  | 78.37 |  |  |  | 8.21 |  | 6.80 | [8 empty] | 17.12 |  |  |  |  | 0.00
1985 |  |  |  | 6056.90 |  |  | 7400 |  |  |  | 890 | [10 empty] | 84.34 |  |  |  | 84.47 | [5 empty] | 77.69 |  |  | 84.47 |  |  |  | 8.91 |  | 8.26 | [8 empty] | 7.27 |  |  |  |  | 0.13
1986 |  |  |  | 5658.50 |  |  | 6983 |  |  |  | 890 | [10 empty] | 81.99 |  |  |  | 82.18 | [5 empty] | 72.58 |  |  | 79.71 |  |  |  | 2.22 |  | 1.87 | [8 empty] | 15.95 |  |  |  |  | 0.19
1987 |  |  |  | 4855.97 |  |  | 5715 |  |  |  | 890 | [10 empty] | 76.42 |  |  |  | 78.85 | [5 empty] | 62.28 |  |  | 65.24 |  |  |  | 9.38 |  | 8.16 | [8 empty] | 12.99 |  |  |  |  | 2.43
1988 |  |  |  | 4583.00 |  |  | 6153 |  |  |  | 890 | [10 empty] | 92.39 |  |  |  | 95.06 | [5 empty] | 58.62 |  |  | 70.05 |  |  |  | 4.94 |  | 4.94 | [8 empty] | 0.00 |  |  |  |  | 2.67
1989 |  |  |  | 5485.29 |  |  | 6927 |  |  |  | 890 | [10 empty] | 76.96 |  |  |  | 79.73 | [5 empty] | 70.36 |  |  | 79.08 |  |  |  | 2.27 |  | 1.85 | [8 empty] | 18.42 |  |  |  |  | 2.77
1990 |  |  |  | 4869.51 |  |  | 6292 |  |  |  | 890 | [10 empty] | 67.77 |  |  |  | 69.95 | [5 empty] | 62.46 |  |  | 71.83 |  |  |  | 10.53 |  | 8.23 | [8 empty] | 21.82 |  |  |  |  | 2.18
1991 |  |  |  | 4201.95 |  |  | 5407 |  |  |  | 890 | [10 empty] | 63.27 |  |  |  | 67.59 | [5 empty] | 53.90 |  |  | 61.72 |  |  |  | 8.16 |  | 6.00 | [8 empty] | 26.41 |  |  |  |  | 4.32
1992 |  |  |  | 5049.75 |  |  | 6429 |  |  |  | 890 | [10 empty] | 74.74 |  |  |  | 75.87 | [5 empty] | 64.59 |  |  | 73.19 |  |  |  | 11.67 |  | 10.02 | [8 empty] | 14.11 |  |  |  |  | 1.13
1993 |  |  |  | 5976.57 |  |  | 7625 |  |  |  | 890 | [10 empty] | 79.62 |  |  |  | 87.41 | [5 empty] | 76.66 |  |  | 87.04 |  |  |  | 1.28 |  | 1.13 | [8 empty] | 11.46 |  |  |  |  | 7.80
1994 |  |  |  | 4444.99 |  |  | 5328 |  |  |  | 890 | [10 empty] | 84.77 |  |  |  | 84.84 | [5 empty] | 57.01 |  |  | 60.82 |  |  |  | 3.76 |  | 3.31 | [8 empty] | 11.85 |  |  |  |  | 0.07
1995 |  |  |  | 5562.04 |  |  | 6952 |  |  |  | 890 | [10 empty] | 94.97 |  |  |  | 95.55 | [5 empty] | 71.34 |  |  | 79.36 |  |  |  | 4.38 |  | 4.38 | [8 empty] | 0.07 |  |  |  |  | 0.58
1996 |  |  |  | 5761.00 |  |  | 7437 |  |  |  | 890 | [10 empty] | 81.47 |  |  |  | 84.23 | [5 empty] | 73.69 |  |  | 84.67 |  |  |  | 3.01 |  | 2.61 | [8 empty] | 13.16 |  |  |  |  | 2.75
1997 |  |  |  | 4966.59 |  |  | 6204 |  |  |  | 890 | [10 empty] | 67.53 |  |  |  | 69.32 | [5 empty] | 63.70 |  |  | 70.82 |  |  |  | 21.57 |  | 19.06 | [8 empty] | 11.62 |  |  |  |  | 1.79
1998 |  |  |  | 5855.92 |  |  | 7192 |  |  |  | 890 | [10 empty] | 78.32 |  |  |  | 80.33 | [5 empty] | 75.11 |  |  | 82.10 |  |  |  | 5.67 |  | 4.82 | [8 empty] | 14.85 |  |  |  |  | 2.01
1999 |  |  |  | 5312.90 |  |  | 6688 |  |  |  | 890 | [10 empty] | 69.21 |  |  |  | 72.58 | [5 empty] | 68.15 |  |  | 76.35 |  |  |  | 16.72 |  | 14.57 | [8 empty] | 12.85 |  |  |  |  | 3.37
2000 |  |  |  | 5866.14 |  |  | 7121 |  |  |  | 890 | [10 empty] | 76.03 |  |  |  | 77.55 | [5 empty] | 75.04 |  |  | 81.07 |  |  |  | 10.45 |  | 9.05 | [8 empty] | 13.40 |  |  |  |  | 1.52
2001 |  |  |  | 5355.88 |  |  | 6593 |  |  |  | 890 | [10 empty] | 72.43 |  |  |  | 75.09 | [5 empty] | 68.70 |  |  | 75.26 |  |  |  | 10.96 |  | 9.25 | [8 empty] | 15.66 |  |  |  |  | 2.67
2002 |  |  |  | 4307.55 |  |  | 5196 |  |  |  | 890 | [10 empty] | 55.95 |  |  |  | 56.33 | [5 empty] | 55.25 |  |  | 59.32 |  |  |  | 22.06 |  | 15.94 | [8 empty] | 27.72 |  |  |  |  | 0.38
2003 |  |  |  | 6268.32 |  |  | 7631 |  |  |  | 890 | [10 empty] | 81.32 |  |  |  | 81.37 | [5 empty] | 80.40 |  |  | 87.11 |  |  |  | 8.14 |  | 7.21 | [8 empty] | 11.42 |  |  |  |  | 0.04
2004 |  |  |  | 5983.93 |  |  | 7286 |  |  |  | 890 | [10 empty] | 93.70 |  |  |  | 95.73 | [5 empty] | 76.54 |  |  | 82.95 |  |  |  | 2.41 |  | 2.36 | [8 empty] | 1.91 |  |  |  |  | 2.03
2005 |  |  |  | 5255.28 |  |  | 6719 |  |  |  | 890 | [10 empty] | 75.79 |  |  |  | 76.34 | [5 empty] | 67.41 |  |  | 76.70 |  |  |  | 1.27 |  | 1.64 | [8 empty] | 22.02 |  |  |  |  | 0.55
2006 |  |  |  | 5880.50 |  |  | 7371 |  |  |  | 890 | [10 empty] | 83.23 |  |  |  | 85.47 | [5 empty] | 75.43 |  |  | 84.14 |  |  |  | 1.12 |  | 3.63 | [8 empty] | 10.90 |  |  |  |  | 2.24
2007 |  |  |  | 6582.66 |  |  | 8201 |  |  |  | 890 | [10 empty] | 88.94 |  |  |  | 91.70 | [5 empty] | 84.43 |  |  | 93.62 |  |  |  | 1.32 |  | 1.23 | [8 empty] | 7.07 |  |  |  |  | 2.76
2008 |  |  |  | 6014.89 |  |  | 7462 |  |  |  | 890 | [10 empty] | 82.11 |  |  |  | 83.97 | [5 empty] | 76.94 |  |  | 84.95 |  |  |  | 2.95 |  | 4.77 | [8 empty] | 11.26 |  |  |  |  | 1.86
2009 |  |  |  | 6455.29 |  |  | 7902 |  |  |  | 890 | [10 empty] | 86.56 |  |  |  | 89.50 | [5 empty] | 82.80 |  |  | 90.21 |  |  |  | 2.14 |  | 3.72 | [8 empty] | 6.78 |  |  |  |  | 2.94
2010 |  |  |  | 5399.78 |  |  | 6491 |  |  |  | 890 | [10 empty] | 71.18 |  |  |  | 72.78 | [5 empty] | 69.26 |  |  | 74.10 |  |  |  | 3.65 |  | 14.22 | [8 empty] | 13.00 |  |  |  |  | 1.60
2011 |  |  |  | 6741.93 |  |  | 7890 |  |  |  | 890 | [10 empty] | 88.69 |  |  |  | 89.33 | [5 empty] | 86.47 |  |  | 90.07 |  |  |  | 1.08 |  | 3.34 | [8 empty] | 7.32 |  |  |  |  | 0.64
2012 |  |  |  | 5117.98 |  |  | 6091 |  |  |  | 890 | [10 empty] | 67.39 |  |  |  | 68.14 | [5 empty] | 65.47 |  |  | 69.34 |  |  |  | 0.96 |  | 3.72 | [8 empty] | 28.15 |  |  |  |  | 0.74
2013 |  |  |  | 6508.82 |  |  | 7666 |  |  |  | 890 | [10 empty] | 87.41 |  |  |  | 88.66 | [5 empty] | 83.48 |  |  | 87.51 |  |  |  | 1.66 |  | 4.38 | [8 empty] | 6.96 |  |  |  |  | 1.25
2014 |  |  |  | 5771.73 |  |  | 6913 |  |  |  | 890 | [10 empty] | 77.81 |  |  |  | 78.39 | [5 empty] | 74.03 |  |  | 78.92 |  |  |  | 0.99 |  | 5.71 | [8 empty] | 15.89 |  |  |  |  | 0.58
2015 |  |  |  | 6402.25 |  |  | 7490 |  |  |  | 890 | [10 empty] | 82.98 |  |  |  | 84.49 | [5 empty] | 82.12 |  |  | 85.50 |  |  |  | 7.87 |  | 7.21 | [8 empty] | 8.30 |  |  |  |  | 1.51
2016 |  |  |  | 4932.37 |  |  | 5619 |  |  |  | 890 | [10 empty] | 61.60 |  |  |  | 69.59 | [5 empty] | 63.09 |  |  | 63.97 |  |  |  | 0.64 |  | 8.86 | [8 empty] | 21.55 |  |  |  |  | 7.99
2017 |  |  |  | 6153.50 |  |  | 6869 |  |  |  | 890 | [10 empty] | 77.15 |  |  |  | 77.36 | [5 empty] | 78.93 |  |  | 78.41 |  |  |  | 13.03 |  | 13.67 | [8 empty] | 8.97 |  |  |  |  | 0.21
2018 |  |  |  | 5831.89 |  |  | 6585 |  |  |  | 890 | [10 empty] | 72.94 |  |  |  | 73.46 | [5 empty] | 74.80 |  |  | 75.17 |  |  |  | 5.93 |  | 9.23 | [8 empty] | 17.30 |  |  |  |  | 0.53
2019 |  |  |  | 7062.17 |  |  | 7793 |  |  |  | 890 | [10 empty] | 87.56 |  |  |  | 87.57 | [5 empty] | 90.58 |  |  | 88.96 |  |  |  | 4.20 |  | 3.84 | [8 empty] | 8.58 |  |  |  |  | 0.01
2020 |  |  |  | 5081.11 |  |  | 6012 |  |  |  | 890 | [10 empty] | 63.08 |  |  |  | 64.56 | [5 empty] | 64.99 |  |  | 68.44 |  |  |  | 9.29 |  | 13.96 | [8 empty] | 21.48 |  |  |  |  | 1.48
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 344
B. |  | Refuelling without maintenance | [35 empty] | 117
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 961 |  |  |  | 12
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 57
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 3
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 14
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 1 | [11 empty] | 21
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 9
Z. |  | Other | [39 empty] | 101 | [11 empty] | 16
Subtotal | [37 empty] | 1138 |  |  |  | 484 | [11 empty] | 42
Total | [22 empty] | 0 | [14 empty] | 1664
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 4
12. |  |  | Reactor I&C Systems | [34 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 36
16. |  |  | Steam generation systems | [34 empty] | 37
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 52
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
34. |  |  | Miscellaneous Systems | [34 empty] | 79
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 37
42. |  |  | Electrical Power Supply Systems | [34 empty] | 48
Total | [37 empty] | 359

## DAMPIERRE-3
2020 Operating Experience
FR-30 | [8 empty] | DAMPIERRE-3 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-09-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-01-30
Gross electrical power | [12 empty] | : |  |  | 937 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-05-27
Reference unit power (net) | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6930.71 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.82 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.5 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.53 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.9 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.57 %
Load Factor (LF) | [18 empty] | : | 88.65 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.4 %
Operating Factor (OF) | [18 empty] | : | 90.26 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 856 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 688.52 | 640.51 |  |  |  | 687.33 |  | 578.95 | [8 empty] | 641.87 |  |  | 631.65 | [6 empty] | 615.10 |  | 652.70 |  |  |  | 110.41 |  |  | 467.37 |  |  | 556.29 | [9 empty] | 660.01 |  |  | 6930.71
EAF [%] |  |  |  |  | 99.98 | 99.90 |  |  |  | 99.97 |  | 99.92 | [8 empty] | 99.99 |  |  | 99.68 | [6 empty] | 91.76 |  | 98.31 |  |  |  | 17.10 |  |  | 70.11 |  |  | 86.47 | [9 empty] | 97.90 |  |  | 88.50
UCF [%] |  |  |  |  | 99.98 | 99.90 |  |  |  | 99.97 |  | 99.92 | [8 empty] | 99.99 |  |  | 99.73 | [6 empty] | 92.15 |  | 98.53 |  |  |  | 17.12 |  |  | 70.11 |  |  | 88.69 | [9 empty] | 99.80 |  |  | 88.90
LF [%] |  |  |  |  | 103.98 | 103.40 |  |  |  | 103.94 |  | 90.35 | [8 empty] | 96.94 |  |  | 98.57 | [6 empty] | 92.89 |  | 98.57 |  |  |  | 17.23 |  |  | 70.49 |  |  | 86.81 | [9 empty] | 99.67 |  |  | 88.65
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 17.50 |  |  | 73.96 |  |  | 90.56 | [9 empty] | 100.00 |  |  | 90.26
FLR [%] |  |  |  |  | 0.01 | 0.09 |  |  |  | 0.00 |  | 0.07 | [8 empty] | 0.00 |  |  | 0.20 | [6 empty] | 7.84 |  | 1.38 |  |  |  | 57.20 |  |  | 0.00 |  |  | 10.27 | [9 empty] | 0.16 |  |  | 3.82
UCL [%] |  |  |  |  | 0.01 | 0.09 |  |  |  | 0.00 |  | 0.07 | [8 empty] | 0.00 |  |  | 0.20 | [6 empty] | 7.84 |  | 1.38 |  |  |  | 22.88 |  |  | 0.00 |  |  | 10.15 | [9 empty] | 0.16 |  |  | 3.53
PUF [%] |  |  |  |  | 0.01 | 0.01 |  |  |  | 0.03 |  | 0.01 | [8 empty] | 0.01 |  |  | 0.07 | [6 empty] | 0.01 |  | 0.09 |  |  |  | 60.00 |  |  | 29.89 |  |  | 1.16 | [9 empty] | 0.04 |  |  | 7.57
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.05 | [6 empty] | 0.39 |  | 0.22 |  |  |  | 0.02 |  |  | 0.00 |  |  | 2.22 | [9 empty] | 1.90 |  |  | 0.40
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 231675.3 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.49 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.02 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.89 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.83 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.28 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.61 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.81 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 5123.40 |  |  | 6452 |  |  |  | 900 | [10 empty] | 83.51 |  |  |  | 83.51 | [5 empty] | 81.70 |  |  | 86.95 |  |  |  | 3.93 |  | 3.41 | [8 empty] | 13.08 |  |  |  |  | 0.00
1982 |  |  |  | 3767.60 |  |  | 4632 |  |  |  | 890 | [10 empty] | 48.72 |  |  |  | 48.72 | [5 empty] | 48.32 |  |  | 52.88 |  |  |  | 22.04 |  | 13.77 | [8 empty] | 37.51 |  |  |  |  | 0.00
1983 |  |  |  | 5517.00 |  |  | 6638 |  |  |  | 890 | [10 empty] | 72.69 |  |  |  | 72.69 | [5 empty] | 70.76 |  |  | 75.78 |  |  |  | 12.35 |  | 10.24 | [8 empty] | 17.07 |  |  |  |  | 0.00
1984 |  |  |  | 6206.00 |  |  | 7121 |  |  |  | 890 | [10 empty] | 79.68 |  |  |  | 79.68 | [5 empty] | 79.38 |  |  | 81.07 |  |  |  | 7.35 |  | 6.32 | [8 empty] | 14.00 |  |  |  |  | 0.00
1985 |  |  |  | 6364.40 |  |  | 7523 |  |  |  | 890 | [10 empty] | 84.89 |  |  |  | 85.11 | [5 empty] | 81.63 |  |  | 85.88 |  |  |  | 2.99 |  | 2.62 | [8 empty] | 12.26 |  |  |  |  | 0.22
1986 |  |  |  | 6717.20 |  |  | 8330 |  |  |  | 890 | [10 empty] | 99.52 |  |  |  | 99.87 | [5 empty] | 86.16 |  |  | 95.09 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 0.00 |  |  |  |  | 0.35
1987 |  |  |  | 5019.50 |  |  | 6269 |  |  |  | 890 | [10 empty] | 79.33 |  |  |  | 82.43 | [5 empty] | 64.38 |  |  | 71.56 |  |  |  | 7.76 |  | 6.94 | [8 empty] | 10.63 |  |  |  |  | 3.10
1988 |  |  |  | 4964.00 |  |  | 6435 |  |  |  | 890 | [10 empty] | 68.53 |  |  |  | 72.91 | [5 empty] | 63.50 |  |  | 73.26 |  |  |  | 8.48 |  | 6.75 | [8 empty] | 20.34 |  |  |  |  | 4.37
1989 |  |  |  | 5912.85 |  |  | 7242 |  |  |  | 890 | [10 empty] | 78.38 |  |  |  | 82.16 | [5 empty] | 75.84 |  |  | 82.67 |  |  |  | 5.95 |  | 5.20 | [8 empty] | 12.65 |  |  |  |  | 3.78
1990 |  |  |  | 5996.46 |  |  | 7348 |  |  |  | 890 | [10 empty] | 79.77 |  |  |  | 82.50 | [5 empty] | 76.91 |  |  | 83.88 |  |  |  | 1.91 |  | 1.61 | [8 empty] | 15.89 |  |  |  |  | 2.73
1991 |  |  |  | 5124.05 |  |  | 6244 |  |  |  | 890 | [10 empty] | 69.56 |  |  |  | 70.04 | [5 empty] | 65.72 |  |  | 71.28 |  |  |  | 18.40 |  | 15.79 | [8 empty] | 14.17 |  |  |  |  | 0.47
1992 |  |  |  | 4875.11 |  |  | 5814 |  |  |  | 890 | [10 empty] | 65.50 |  |  |  | 65.51 | [5 empty] | 62.36 |  |  | 66.19 |  |  |  | 5.88 |  | 4.10 | [8 empty] | 30.40 |  |  |  |  | 0.00
1993 |  |  |  | 6148.83 |  |  | 7333 |  |  |  | 890 | [10 empty] | 82.76 |  |  |  | 82.76 | [5 empty] | 78.87 |  |  | 83.71 |  |  |  | 4.85 |  | 4.22 | [8 empty] | 13.02 |  |  |  |  | 0.00
1994 |  |  |  | 5537.56 |  |  | 7013 |  |  |  | 890 | [10 empty] | 82.73 |  |  |  | 86.17 | [5 empty] | 71.03 |  |  | 80.06 |  |  |  | 0.38 |  | 0.33 | [8 empty] | 13.50 |  |  |  |  | 3.43
1995 |  |  |  | 4773.50 |  |  | 6343 |  |  |  | 890 | [10 empty] | 80.20 |  |  |  | 83.44 | [5 empty] | 61.23 |  |  | 72.41 |  |  |  | 0.78 |  | 0.65 | [8 empty] | 15.91 |  |  |  |  | 3.24
1996 |  |  |  | 5575.09 |  |  | 6940 |  |  |  | 890 | [10 empty] | 77.08 |  |  |  | 77.63 | [5 empty] | 71.31 |  |  | 79.01 |  |  |  | 7.66 |  | 6.44 | [8 empty] | 15.93 |  |  |  |  | 0.55
1997 |  |  |  | 5720.89 |  |  | 7211 |  |  |  | 890 | [10 empty] | 78.29 |  |  |  | 81.02 | [5 empty] | 73.38 |  |  | 82.32 |  |  |  | 8.56 |  | 7.59 | [8 empty] | 11.39 |  |  |  |  | 2.73
1998 |  |  |  | 5905.83 |  |  | 7210 |  |  |  | 890 | [10 empty] | 81.44 |  |  |  | 82.67 | [5 empty] | 75.75 |  |  | 82.31 |  |  |  | 6.68 |  | 5.91 | [8 empty] | 11.41 |  |  |  |  | 1.24
1999 |  |  |  | 5779.45 |  |  | 7186 |  |  |  | 890 | [10 empty] | 78.23 |  |  |  | 80.89 | [5 empty] | 74.13 |  |  | 82.03 |  |  |  | 6.34 |  | 5.47 | [8 empty] | 13.64 |  |  |  |  | 2.66
2000 |  |  |  | 4308.35 |  |  | 5378 |  |  |  | 890 | [10 empty] | 57.58 |  |  |  | 59.78 | [5 empty] | 55.11 |  |  | 61.22 |  |  |  | 31.56 |  | 27.56 | [8 empty] | 12.66 |  |  |  |  | 2.20
2001 |  |  |  | 5993.02 |  |  | 7060 |  |  |  | 890 | [10 empty] | 77.38 |  |  |  | 77.75 | [5 empty] | 76.87 |  |  | 80.59 |  |  |  | 5.76 |  | 7.77 | [8 empty] | 14.48 |  |  |  |  | 0.38
2002 |  |  |  | 5929.80 |  |  | 6877 |  |  |  | 890 | [10 empty] | 76.85 |  |  |  | 77.42 | [5 empty] | 76.06 |  |  | 78.50 |  |  |  | 9.75 |  | 8.36 | [8 empty] | 14.22 |  |  |  |  | 0.57
2003 |  |  |  | 5346.90 |  |  | 6152 |  |  |  | 890 | [10 empty] | 68.91 |  |  |  | 68.98 | [5 empty] | 68.58 |  |  | 70.23 |  |  |  | 4.75 |  | 3.44 | [8 empty] | 27.59 |  |  |  |  | 0.07
2004 |  |  |  | 6867.17 |  |  | 7920 |  |  |  | 890 | [10 empty] | 87.98 |  |  |  | 89.25 | [5 empty] | 87.84 |  |  | 90.16 |  |  |  | 0.43 |  | 0.39 | [8 empty] | 10.36 |  |  |  |  | 1.27
2005 |  |  |  | 6242.37 |  |  | 7627 |  |  |  | 890 | [10 empty] | 84.13 |  |  |  | 86.49 | [5 empty] | 80.06 |  |  | 87.06 |  |  |  | 1.25 |  | 1.10 | [8 empty] | 12.41 |  |  |  |  | 2.36
2006 |  |  |  | 6228.48 |  |  | 7991 |  |  |  | 890 | [10 empty] | 89.29 |  |  |  | 92.26 | [5 empty] | 79.89 |  |  | 91.22 |  |  |  | 0.30 |  | 0.28 | [8 empty] | 7.46 |  |  |  |  | 2.98
2007 |  |  |  | 5614.09 |  |  | 6928 |  |  |  | 890 | [10 empty] | 76.03 |  |  |  | 78.72 | [5 empty] | 72.01 |  |  | 79.09 |  |  |  | 7.35 |  | 7.58 | [8 empty] | 13.69 |  |  |  |  | 2.69
2008 |  |  |  | 6725.61 |  |  | 8100 |  |  |  | 890 | [10 empty] | 89.97 |  |  |  | 91.52 | [5 empty] | 86.03 |  |  | 92.21 |  |  |  | 0.31 |  | 1.52 | [8 empty] | 6.97 |  |  |  |  | 1.55
2009 |  |  |  | 5364.97 |  |  | 6486 |  |  |  | 890 | [10 empty] | 71.00 |  |  |  | 74.75 | [5 empty] | 68.81 |  |  | 74.04 |  |  |  | 3.64 |  | 12.66 | [8 empty] | 12.59 |  |  |  |  | 3.75
2010 |  |  |  | 6642.91 |  |  | 7660 |  |  |  | 890 | [10 empty] | 86.31 |  |  |  | 87.03 | [5 empty] | 85.20 |  |  | 87.44 |  |  |  | 3.52 |  | 5.89 | [8 empty] | 7.08 |  |  |  |  | 0.72
2011 |  |  |  | 5999.40 |  |  | 7020 |  |  |  | 890 | [10 empty] | 78.44 |  |  |  | 79.35 | [5 empty] | 76.95 |  |  | 80.14 |  |  |  | 0.30 |  | 5.88 | [8 empty] | 14.77 |  |  |  |  | 0.91
2012 |  |  |  | 6513.75 |  |  | 7595 |  |  |  | 890 | [10 empty] | 84.17 |  |  |  | 85.86 | [5 empty] | 83.32 |  |  | 86.46 |  |  |  | 0.30 |  | 7.24 | [8 empty] | 6.90 |  |  |  |  | 1.68
2013 |  |  |  | 4747.59 |  |  | 5438 |  |  |  | 890 | [10 empty] | 61.14 |  |  |  | 65.81 | [5 empty] | 60.89 |  |  | 62.08 |  |  |  | 0.78 |  | 6.13 | [8 empty] | 28.06 |  |  |  |  | 4.67
2014 |  |  |  | 6746.72 |  |  | 7824 |  |  |  | 890 | [10 empty] | 87.13 |  |  |  | 87.95 | [5 empty] | 86.54 |  |  | 89.32 |  |  |  | 0.89 |  | 3.42 | [8 empty] | 8.64 |  |  |  |  | 0.82
2015 |  |  |  | 6378.71 |  |  | 7269 |  |  |  | 890 | [10 empty] | 81.62 |  |  |  | 82.37 | [5 empty] | 81.82 |  |  | 82.98 |  |  |  | 0.68 |  | 0.57 | [8 empty] | 17.06 |  |  |  |  | 0.75
2016 |  |  |  | 6045.05 |  |  | 6807 |  |  |  | 890 | [10 empty] | 75.83 |  |  |  | 89.75 | [5 empty] | 77.32 |  |  | 77.49 |  |  |  | 0.36 |  | 1.94 | [8 empty] | 8.32 |  |  |  |  | 13.91
2017 |  |  |  | 5832.29 |  |  | 6540 |  |  |  | 890 | [10 empty] | 73.65 |  |  |  | 74.76 | [5 empty] | 74.81 |  |  | 74.66 |  |  |  | 6.55 |  | 8.80 | [8 empty] | 16.44 |  |  |  |  | 1.11
2018 |  |  |  | 6252.31 |  |  | 7054 |  |  |  | 890 | [10 empty] | 79.82 |  |  |  | 79.84 | [5 empty] | 80.19 |  |  | 80.53 |  |  |  | 7.26 |  | 11.58 | [8 empty] | 8.58 |  |  |  |  | 0.02
2019 |  |  |  | 6079.01 |  |  | 6794 |  |  |  | 890 | [10 empty] | 76.33 |  |  |  | 76.40 | [5 empty] | 77.97 |  |  | 77.56 |  |  |  | 1.66 |  | 1.29 | [8 empty] | 22.31 |  |  |  |  | 0.08
2020 |  |  |  | 6930.71 |  |  | 7928 |  |  |  | 890 | [10 empty] | 88.50 |  |  |  | 88.90 | [5 empty] | 88.65 |  |  | 90.26 |  |  |  | 3.82 |  | 3.53 | [8 empty] | 7.57 |  |  |  |  | 0.40
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 309
B. |  | Refuelling without maintenance | [35 empty] | 97
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1077 |  |  |  | 7
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 21 |  |  |  | 1
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 1
I. |  | Grid capacity limitation | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 25
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 3 | [11 empty] | 47
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 5 | [11 empty] | 1
Z. |  | Other | [39 empty] | 73
Subtotal | [37 empty] | 1199 |  |  |  | 424 | [11 empty] | 50
Total | [22 empty] | 0 | [14 empty] | 1673
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 29
15. |  |  | Reactor Cooling Systems | [34 empty] | 47
16. |  |  | Steam generation systems | [34 empty] | 65
31. |  |  | Turbine and auxiliaries | [34 empty] | 35
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 76
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 24
42. |  |  | Electrical Power Supply Systems | [34 empty] | 37
Total | [37 empty] | 336

## DAMPIERRE-4
2020 Operating Experience
FR-31 | [8 empty] | DAMPIERRE-4 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-12-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-08-18
Gross electrical power | [12 empty] | : |  |  | 937 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-11-20
Reference unit power (net) | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.61
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4457.67 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.5 %
Energy Availability Factor (EAF) | [18 empty] | : | 57.37 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 9.85 %
Unit Capability Factor (UCF) | [18 empty] | : | 67.77 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 22.38 %
Load Factor (LF) | [18 empty] | : | 57.02 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 10.4 %
Operating Factor (OF) | [18 empty] | : | 60.74 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3449 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 574.17 | 257.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 529.47 |  | 635.69 |  |  |  | 613.96 |  |  | 595.25 |  |  | 588.68 | [9 empty] | 663.31 |  |  | 4457.67
EAF [%] |  |  |  |  | 86.72 | 41.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 82.21 |  | 96.44 |  |  |  | 96.09 |  |  | 90.16 |  |  | 92.88 | [9 empty] | 99.98 |  |  | 57.37
UCF [%] |  |  |  |  | 93.18 | 49.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 83.61 |  |  | 21.29 | [6 empty] | 83.41 |  | 98.21 |  |  |  | 97.54 |  |  | 90.53 |  |  | 92.89 | [9 empty] | 99.98 |  |  | 67.77
LF [%] |  |  |  |  | 86.71 | 41.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 79.96 |  | 96.00 |  |  |  | 95.81 |  |  | 89.77 |  |  | 91.87 | [9 empty] | 100.17 |  |  | 57.02
OF [%] |  |  |  |  | 100.00 | 51.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 92.47 |  | 100.00 |  |  |  | 100.00 |  |  | 90.34 |  |  | 91.81 | [9 empty] | 100.00 |  |  | 60.74
FLR [%] |  |  |  |  | 6.82 | 4.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.03 | [6 empty] | 9.03 |  | 1.67 |  |  |  | 2.42 |  |  | 9.47 |  |  | 7.07 | [9 empty] | 0.02 |  |  | 4.50
UCL [%] |  |  |  |  | 6.82 | 2.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 78.70 | [6 empty] | 10.72 |  | 1.67 |  |  |  | 2.42 |  |  | 9.47 |  |  | 7.06 | [9 empty] | 0.02 |  |  | 9.85
PUF [%] |  |  |  |  | 0.00 | 48.27 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 16.39 |  |  | 0.01 | [6 empty] | 5.87 |  | 0.12 |  |  |  | 0.04 |  |  | 0.00 |  |  | 0.04 | [9 empty] | 0.00 |  |  | 22.38
XUF [%] |  |  |  |  | 6.46 | 7.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 83.61 |  |  | 21.28 | [6 empty] | 1.20 |  | 1.77 |  |  |  | 1.45 |  |  | 0.38 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 10.40
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 218864.65 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.54 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.51 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.43 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.92 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.65 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.5 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.41 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.56 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 1569.50 |  |  | 2392 |  |  |  | 894 | [10 empty] | 77.30 |  |  |  | 77.30 | [5 empty] | 77.30 |  |  | 79.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.70 |  |  |  |  | 0.00
1982 |  |  |  | 5745.60 |  |  | 7413 |  |  |  | 890 | [10 empty] | 81.81 |  |  |  | 81.81 | [5 empty] | 73.70 |  |  | 84.62 |  |  |  | 18.19 |  | 18.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 4156.00 |  |  | 5207 |  |  |  | 890 | [10 empty] | 57.60 |  |  |  | 57.60 | [5 empty] | 53.31 |  |  | 59.44 |  |  |  | 13.86 |  | 9.27 | [8 empty] | 33.13 |  |  |  |  | 0.00
1984 |  |  |  | 6276.00 |  |  | 7765 |  |  |  | 890 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 80.28 |  |  | 88.40 |  |  |  | 4.15 |  | 3.69 | [8 empty] | 11.21 |  |  |  |  | 0.00
1985 |  |  |  | 5859.90 |  |  | 7387 |  |  |  | 890 | [10 empty] | 78.92 |  |  |  | 83.46 | [5 empty] | 75.16 |  |  | 84.33 |  |  |  | 5.42 |  | 4.78 | [8 empty] | 11.76 |  |  |  |  | 4.54
1986 |  |  |  | 6664.90 |  |  | 7862 |  |  |  | 890 | [10 empty] | 88.47 |  |  |  | 88.80 | [5 empty] | 85.49 |  |  | 89.75 |  |  |  | 1.03 |  | 0.93 | [8 empty] | 10.28 |  |  |  |  | 0.33
1987 |  |  |  | 5447.80 |  |  | 6795 |  |  |  | 890 | [10 empty] | 78.10 |  |  |  | 78.40 | [5 empty] | 69.88 |  |  | 77.57 |  |  |  | 6.17 |  | 5.15 | [8 empty] | 16.44 |  |  |  |  | 0.31
1988 |  |  |  | 5086.00 |  |  | 6645 |  |  |  | 890 | [10 empty] | 79.93 |  |  |  | 82.92 | [5 empty] | 65.06 |  |  | 75.65 |  |  |  | 4.87 |  | 4.25 | [8 empty] | 12.83 |  |  |  |  | 2.99
1989 |  |  |  | 5392.37 |  |  | 6621 |  |  |  | 890 | [10 empty] | 72.88 |  |  |  | 73.73 | [5 empty] | 69.16 |  |  | 75.58 |  |  |  | 6.75 |  | 5.33 | [8 empty] | 20.94 |  |  |  |  | 0.85
1990 |  |  |  | 5153.00 |  |  | 6792 |  |  |  | 890 | [10 empty] | 87.31 |  |  |  | 91.20 | [5 empty] | 66.09 |  |  | 77.53 |  |  |  | 2.32 |  | 2.17 | [8 empty] | 6.63 |  |  |  |  | 3.89
1991 |  |  |  | 6062.80 |  |  | 7612 |  |  |  | 890 | [10 empty] | 86.70 |  |  |  | 88.34 | [5 empty] | 77.76 |  |  | 86.89 |  |  |  | 3.50 |  | 3.21 | [8 empty] | 8.45 |  |  |  |  | 1.64
1992 |  |  |  | 5331.48 |  |  | 6832 |  |  |  | 890 | [10 empty] | 74.50 |  |  |  | 76.68 | [5 empty] | 68.20 |  |  | 77.78 |  |  |  | 10.71 |  | 9.19 | [8 empty] | 14.13 |  |  |  |  | 2.18
1993 |  |  |  | 4827.70 |  |  | 6103 |  |  |  | 890 | [10 empty] | 63.35 |  |  |  | 69.25 | [5 empty] | 61.92 |  |  | 69.67 |  |  |  | 8.17 |  | 6.16 | [8 empty] | 24.59 |  |  |  |  | 5.90
1994 |  |  |  | 5263.99 |  |  | 7103 |  |  |  | 890 | [10 empty] | 79.52 |  |  |  | 80.74 | [5 empty] | 67.52 |  |  | 81.08 |  |  |  | 9.93 |  | 8.90 | [8 empty] | 10.36 |  |  |  |  | 1.22
1995 |  |  |  | 5488.04 |  |  | 6997 |  |  |  | 890 | [10 empty] | 75.36 |  |  |  | 78.84 | [5 empty] | 70.39 |  |  | 79.87 |  |  |  | 10.89 |  | 9.63 | [8 empty] | 11.52 |  |  |  |  | 3.48
1996 |  |  |  | 6118.49 |  |  | 7596 |  |  |  | 890 | [10 empty] | 82.93 |  |  |  | 83.67 | [5 empty] | 78.26 |  |  | 86.48 |  |  |  | 4.95 |  | 4.35 | [8 empty] | 11.98 |  |  |  |  | 0.74
1997 |  |  |  | 5918.58 |  |  | 7178 |  |  |  | 890 | [10 empty] | 80.46 |  |  |  | 80.86 | [5 empty] | 75.91 |  |  | 81.94 |  |  |  | 5.26 |  | 4.48 | [8 empty] | 14.66 |  |  |  |  | 0.39
1998 |  |  |  | 4506.48 |  |  | 5435 |  |  |  | 890 | [10 empty] | 58.98 |  |  |  | 60.59 | [5 empty] | 57.80 |  |  | 62.04 |  |  |  | 26.81 |  | 22.20 | [8 empty] | 17.22 |  |  |  |  | 1.60
1999 |  |  |  | 4642.53 |  |  | 5770 |  |  |  | 890 | [10 empty] | 64.13 |  |  |  | 64.76 | [5 empty] | 59.55 |  |  | 65.87 |  |  |  | 28.25 |  | 25.50 | [8 empty] | 9.74 |  |  |  |  | 0.63
2000 |  |  |  | 5598.66 |  |  | 6752 |  |  |  | 890 | [10 empty] | 75.15 |  |  |  | 76.02 | [5 empty] | 71.61 |  |  | 76.87 |  |  |  | 11.87 |  | 10.24 | [8 empty] | 13.74 |  |  |  |  | 0.87
2001 |  |  |  | 5361.82 |  |  | 6422 |  |  |  | 890 | [10 empty] | 70.08 |  |  |  | 70.91 | [5 empty] | 68.77 |  |  | 73.31 |  |  |  | 28.41 |  | 28.14 | [8 empty] | 0.95 |  |  |  |  | 0.83
2002 |  |  |  | 6134.48 |  |  | 7576 |  |  |  | 890 | [10 empty] | 83.77 |  |  |  | 85.28 | [5 empty] | 78.68 |  |  | 86.48 |  |  |  | 2.77 |  | 2.43 | [8 empty] | 12.30 |  |  |  |  | 1.50
2003 |  |  |  | 5547.40 |  |  | 6759 |  |  |  | 890 | [10 empty] | 73.37 |  |  |  | 77.39 | [5 empty] | 71.15 |  |  | 77.16 |  |  |  | 3.55 |  | 9.60 | [8 empty] | 13.02 |  |  |  |  | 4.02
2004 |  |  |  | 4531.79 |  |  | 5551 |  |  |  | 890 | [10 empty] | 59.44 |  |  |  | 61.31 | [5 empty] | 57.97 |  |  | 63.19 |  |  |  | 16.90 |  | 12.47 | [8 empty] | 26.23 |  |  |  |  | 1.87
2005 |  |  |  | 6566.95 |  |  | 7956 |  |  |  | 890 | [10 empty] | 87.56 |  |  |  | 88.67 | [5 empty] | 84.22 |  |  | 90.81 |  |  |  | 1.62 |  | 2.61 | [8 empty] | 8.71 |  |  |  |  | 1.11
2006 |  |  |  | 5905.36 |  |  | 7428 |  |  |  | 890 | [10 empty] | 83.57 |  |  |  | 85.77 | [5 empty] | 75.74 |  |  | 84.79 |  |  |  | 1.50 |  | 1.45 | [8 empty] | 12.79 |  |  |  |  | 2.20
2007 |  |  |  | 5763.52 |  |  | 7384 |  |  |  | 890 | [10 empty] | 83.51 |  |  |  | 88.11 | [5 empty] | 73.93 |  |  | 84.29 |  |  |  | 3.21 |  | 3.30 | [8 empty] | 8.59 |  |  |  |  | 4.60
2008 |  |  |  | 5249.14 |  |  | 6317 |  |  |  | 890 | [10 empty] | 67.53 |  |  |  | 68.82 | [5 empty] | 67.14 |  |  | 71.91 |  |  |  | 4.44 |  | 5.11 | [8 empty] | 26.07 |  |  |  |  | 1.29
2009 |  |  |  | 6259.13 |  |  | 7151 |  |  |  | 890 | [10 empty] | 80.17 |  |  |  | 86.31 | [5 empty] | 80.28 |  |  | 81.63 |  |  |  | 2.04 |  | 5.80 | [8 empty] | 7.90 |  |  |  |  | 6.13
2010 |  |  |  | 6472.40 |  |  | 7344 |  |  |  | 890 | [10 empty] | 82.59 |  |  |  | 83.17 | [5 empty] | 83.02 |  |  | 83.84 |  |  |  | 0.18 |  | 3.71 | [8 empty] | 13.12 |  |  |  |  | 0.59
2011 |  |  |  | 6433.47 |  |  | 7506 |  |  |  | 890 | [10 empty] | 83.13 |  |  |  | 83.74 | [5 empty] | 82.52 |  |  | 85.68 |  |  |  | 5.60 |  | 8.16 | [8 empty] | 8.10 |  |  |  |  | 0.61
2012 |  |  |  | 5014.64 |  |  | 5644 |  |  |  | 890 | [10 empty] | 63.57 |  |  |  | 82.56 | [5 empty] | 64.14 |  |  | 64.25 |  |  |  | 0.30 |  | 4.66 | [8 empty] | 12.78 |  |  |  |  | 18.98
2013 |  |  |  | 7074.86 |  |  | 7942 |  |  |  | 890 | [10 empty] | 89.80 |  |  |  | 90.31 | [5 empty] | 90.75 |  |  | 90.66 |  |  |  | 0.65 |  | 2.17 | [8 empty] | 7.51 |  |  |  |  | 0.52
2014 |  |  |  | 3970.80 |  |  | 4507 |  |  |  | 890 | [10 empty] | 50.26 |  |  |  | 50.26 | [5 empty] | 50.93 |  |  | 51.45 |  |  |  | 0.36 |  | 8.86 | [8 empty] | 40.87 |  |  |  |  | 0.00
2015 |  |  |  | 6750.08 |  |  | 8025 |  |  |  | 890 | [10 empty] | 86.66 |  |  |  | 90.66 | [5 empty] | 86.58 |  |  | 91.61 |  |  |  | 0.38 |  | 0.81 | [8 empty] | 8.53 |  |  |  |  | 4.00
2016 |  |  |  | 6456.43 |  |  | 7442 |  |  |  | 890 | [10 empty] | 82.44 |  |  |  | 83.60 | [5 empty] | 82.59 |  |  | 84.72 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 16.24 |  |  |  |  | 1.16
2017 |  |  |  | 6599.79 |  |  | 7688 |  |  |  | 890 | [10 empty] | 84.58 |  |  |  | 85.18 | [5 empty] | 84.65 |  |  | 87.76 |  |  |  | 3.79 |  | 6.03 | [8 empty] | 8.80 |  |  |  |  | 0.60
2018 |  |  |  | 3438.52 |  |  | 4116 |  |  |  | 890 | [10 empty] | 44.32 |  |  |  | 45.36 | [5 empty] | 44.10 |  |  | 46.99 |  |  |  | 4.16 |  | 37.73 | [8 empty] | 16.91 |  |  |  |  | 1.03
2019 |  |  |  | 5979.78 |  |  | 7196 |  |  |  | 890 | [10 empty] | 79.76 |  |  |  | 80.98 | [5 empty] | 76.70 |  |  | 82.15 |  |  |  | 19.00 |  | 19.00 | [8 empty] | 0.03 |  |  |  |  | 1.21
2020 |  |  |  | 4457.67 |  |  | 5335 |  |  |  | 890 | [10 empty] | 57.37 |  |  |  | 67.77 | [5 empty] | 57.02 |  |  | 60.74 |  |  |  | 4.50 |  | 9.85 | [8 empty] | 22.38 |  |  |  |  | 10.40
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 491
B. |  | Refuelling without maintenance | [35 empty] | 102
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 983 |  |  |  | 22
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 4 |  |  |  | 1
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 13
L. |  | Human factor related | [39 empty] | 19
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 6
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 4 | [11 empty] | 66
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 7 | [11 empty] | 1
Z. |  | Other | [39 empty] | 67 | [11 empty] | 6
Subtotal | [37 empty] | 1093 |  |  |  | 613 | [11 empty] | 93
Total | [22 empty] | 0 | [14 empty] | 1799
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 39
12. |  |  | Reactor I&C Systems | [34 empty] | 4
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 40
14. |  |  | Safety Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 14
16. |  |  | Steam generation systems | [34 empty] | 140
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 32
32. |  |  | Feedwater and Main Steam System | [34 empty] | 24
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 92
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 74
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 488

## FESSENHEIM-1
2020 Operating Experience
FR-11 | [8 empty] | FESSENHEIM-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | FRAM (FRAMATOME)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP0 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-09-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-04-06
Gross electrical power | [12 empty] | : |  |  | 920 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1978-01-01
Reference unit power (net) | [12 empty] | : |  |  | 880 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 14 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.257
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 1082.25 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.29 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.7 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.26 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.7 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.03 %
Load Factor (LF) | [18 empty] | : | 96.68 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 98.27 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 22 hours
Annual Summary
[5 empty] | Oct | Nov |  |  |  | Dec |  | Mar | [8 empty] | Apr |  |  | May | [6 empty] | Jun |  | Jul |  |  |  | Sep |  |  | Aug |  |  | Jan | [9 empty] | Feb |  |  | Annual
GW(e)-h | [42 empty] | 639.78 | [9 empty] | 442.47 |  |  | 1082.25
EAF [%] | [42 empty] | 97.84 | [9 empty] | 95.10 |  |  | 96.70
UCF [%] | [42 empty] | 97.84 | [9 empty] | 95.10 |  |  | 96.70
LF [%] | [42 empty] | 97.72 | [9 empty] | 95.23 |  |  | 96.68
OF [%] | [42 empty] | 100.00 | [9 empty] | 95.83 |  |  | 98.27
FLR [%] | [42 empty] | 2.16 | [9 empty] | 0.00 |  |  | 1.29
UCL [%] | [42 empty] | 2.16 | [9 empty] | 0.00 |  |  | 1.26
PUF [%] | [42 empty] | 0.00 | [9 empty] | 4.90 |  |  | 2.03
XUF [%] | [42 empty] | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 226734.76 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 11.57 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.18 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.82 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 73.61 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.57 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 69.46 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.43 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.07 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1978 |  |  |  | 6079.20 |  |  | 7302 |  |  |  | 890 | [10 empty] | 78.17 |  |  |  | 78.17 | [5 empty] | 77.97 |  |  | 83.36 |  |  |  | 21.83 |  | 21.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
1979 |  |  |  | 4542.00 |  |  | 5338 |  |  |  | 890 | [10 empty] | 58.75 |  |  |  | 58.75 | [5 empty] | 58.26 |  |  | 60.94 |  |  |  | 3.91 |  | 2.39 | [8 empty] | 38.85 |  |  |  |  | 0.00
1980 |  |  |  | 5510.00 |  |  | 6350 |  |  |  | 890 | [10 empty] | 70.74 |  |  |  | 70.74 | [5 empty] | 70.48 |  |  | 72.29 |  |  |  | 15.86 |  | 13.34 | [8 empty] | 15.92 |  |  |  |  | 0.00
1981 |  |  |  | 5065.30 |  |  | 5844 |  |  |  | 890 | [10 empty] | 65.30 |  |  |  | 65.30 | [5 empty] | 64.97 |  |  | 66.71 |  |  |  | 17.87 |  | 14.21 | [8 empty] | 20.49 |  |  |  |  | 0.00
1982 |  |  |  | 1848.20 |  |  | 2138 |  |  |  | 880 | [10 empty] | 24.01 |  |  |  | 24.01 | [5 empty] | 23.98 |  |  | 24.41 |  |  |  | 75.17 |  | 72.68 | [8 empty] | 3.31 |  |  |  |  | 0.00
1983 |  |  |  | 5690.00 |  |  | 6701 |  |  |  | 880 | [10 empty] | 75.33 |  |  |  | 75.33 | [5 empty] | 73.81 |  |  | 76.50 |  |  |  | 2.54 |  | 1.97 | [8 empty] | 22.71 |  |  |  |  | 0.00
1984 |  |  |  | 6503.00 |  |  | 7731 |  |  |  | 880 | [10 empty] | 85.18 |  |  |  | 85.18 | [5 empty] | 84.13 |  |  | 88.01 |  |  |  | 4.53 |  | 4.04 | [8 empty] | 10.78 |  |  |  |  | 0.00
1985 |  |  |  | 6044.60 |  |  | 7105 |  |  |  | 880 | [10 empty] | 79.84 |  |  |  | 80.36 | [5 empty] | 78.41 |  |  | 81.11 |  |  |  | 4.16 |  | 3.49 | [8 empty] | 16.15 |  |  |  |  | 0.53
1986 |  |  |  | 5661.30 |  |  | 6702 |  |  |  | 880 | [10 empty] | 74.74 |  |  |  | 75.06 | [5 empty] | 73.44 |  |  | 76.51 |  |  |  | 13.65 |  | 11.87 | [8 empty] | 13.08 |  |  |  |  | 0.32
1987 |  |  |  | 5029.60 |  |  | 6147 |  |  |  | 880 | [10 empty] | 73.60 |  |  |  | 74.13 | [5 empty] | 65.24 |  |  | 70.17 |  |  |  | 25.87 |  | 25.87 | [8 empty] | 0.00 |  |  |  |  | 0.53
1988 |  |  |  | 5399.00 |  |  | 7069 |  |  |  | 880 | [10 empty] | 77.87 |  |  |  | 86.47 | [5 empty] | 69.85 |  |  | 80.48 |  |  |  | 0.89 |  | 0.78 | [8 empty] | 12.76 |  |  |  |  | 8.60
1989 |  |  |  | 3253.33 |  |  | 4108 |  |  |  | 880 | [10 empty] | 43.44 |  |  |  | 46.13 | [5 empty] | 42.20 |  |  | 46.89 |  |  |  | 26.19 |  | 16.37 | [8 empty] | 37.50 |  |  |  |  | 2.69
1990 |  |  |  | 5036.69 |  |  | 6481 |  |  |  | 880 | [10 empty] | 74.58 |  |  |  | 79.61 | [5 empty] | 65.34 |  |  | 73.98 |  |  |  | 8.38 |  | 7.28 | [8 empty] | 13.11 |  |  |  |  | 5.02
1991 |  |  |  | 4053.54 |  |  | 4900 |  |  |  | 880 | [10 empty] | 55.47 |  |  |  | 55.75 | [5 empty] | 52.58 |  |  | 55.94 |  |  |  | 23.22 |  | 16.86 | [8 empty] | 27.39 |  |  |  |  | 0.27
1992 |  |  |  | 4867.06 |  |  | 6079 |  |  |  | 880 | [10 empty] | 66.87 |  |  |  | 67.18 | [5 empty] | 62.96 |  |  | 69.21 |  |  |  | 31.61 |  | 31.05 | [8 empty] | 1.77 |  |  |  |  | 0.31
1993 |  |  |  | 5548.68 |  |  | 7161 |  |  |  | 880 | [10 empty] | 74.64 |  |  |  | 80.96 | [5 empty] | 71.98 |  |  | 81.75 |  |  |  | 2.78 |  | 2.31 | [8 empty] | 16.73 |  |  |  |  | 6.32
1994 |  |  |  | 6186.14 |  |  | 7508 |  |  |  | 880 | [10 empty] | 86.45 |  |  |  | 87.39 | [5 empty] | 80.25 |  |  | 85.71 |  |  |  | 0.96 |  | 0.84 | [8 empty] | 11.76 |  |  |  |  | 0.94
1995 |  |  |  | 5856.09 |  |  | 6990 |  |  |  | 880 | [10 empty] | 84.68 |  |  |  | 85.51 | [5 empty] | 75.97 |  |  | 79.79 |  |  |  | 0.92 |  | 0.79 | [8 empty] | 13.70 |  |  |  |  | 0.83
1996 |  |  |  | 6164.97 |  |  | 7544 |  |  |  | 880 | [10 empty] | 85.21 |  |  |  | 85.35 | [5 empty] | 79.75 |  |  | 85.88 |  |  |  | 2.19 |  | 1.91 | [8 empty] | 12.74 |  |  |  |  | 0.14
1997 |  |  |  | 5826.79 |  |  | 7209 |  |  |  | 880 | [10 empty] | 81.53 |  |  |  | 81.60 | [5 empty] | 75.59 |  |  | 82.29 |  |  |  | 4.77 |  | 4.09 | [8 empty] | 14.31 |  |  |  |  | 0.07
1998 |  |  |  | 4617.05 |  |  | 5727 |  |  |  | 880 | [10 empty] | 61.66 |  |  |  | 64.30 | [5 empty] | 59.89 |  |  | 65.38 |  |  |  | 7.87 |  | 5.50 | [8 empty] | 30.20 |  |  |  |  | 2.64
1999 |  |  |  | 5228.79 |  |  | 6283 |  |  |  | 880 | [10 empty] | 70.80 |  |  |  | 71.16 | [5 empty] | 67.83 |  |  | 71.72 |  |  |  | 6.81 |  | 5.20 | [8 empty] | 23.64 |  |  |  |  | 0.36
2000 |  |  |  | 5782.65 |  |  | 7145 |  |  |  | 880 | [10 empty] | 80.82 |  |  |  | 81.08 | [5 empty] | 74.81 |  |  | 81.34 |  |  |  | 11.07 |  | 10.10 | [8 empty] | 8.83 |  |  |  |  | 0.25
2001 |  |  |  | 5507.53 |  |  | 7095 |  |  |  | 880 | [10 empty] | 78.36 |  |  |  | 79.64 | [5 empty] | 71.44 |  |  | 80.99 |  |  |  | 8.04 |  | 6.96 | [8 empty] | 13.40 |  |  |  |  | 1.28
2002 |  |  |  | 2989.75 |  |  | 3832 |  |  |  | 880 | [10 empty] | 41.08 |  |  |  | 42.92 | [5 empty] | 38.78 |  |  | 43.74 |  |  |  | 2.12 |  | 0.93 | [8 empty] | 56.15 |  |  |  |  | 1.84
2003 |  |  |  | 6985.20 |  |  | 8518 |  |  |  | 880 | [10 empty] | 96.45 |  |  |  | 98.18 | [5 empty] | 90.61 |  |  | 97.24 |  |  |  | 1.54 |  | 1.53 | [8 empty] | 0.29 |  |  |  |  | 1.72
2004 |  |  |  | 3726.49 |  |  | 4500 |  |  |  | 880 | [10 empty] | 49.64 |  |  |  | 50.24 | [5 empty] | 48.21 |  |  | 51.23 |  |  |  | 44.83 |  | 40.82 | [8 empty] | 8.94 |  |  |  |  | 0.60
2005 |  |  |  | 5448.42 |  |  | 6673 |  |  |  | 880 | [10 empty] | 75.32 |  |  |  | 75.38 | [5 empty] | 70.68 |  |  | 76.18 |  |  |  | 2.30 |  | 8.17 | [8 empty] | 16.45 |  |  |  |  | 0.06
2006 |  |  |  | 6875.72 |  |  | 8338 |  |  |  | 880 | [10 empty] | 93.50 |  |  |  | 94.09 | [5 empty] | 89.19 |  |  | 95.18 |  |  |  | 5.90 |  | 5.90 | [8 empty] | 0.01 |  |  |  |  | 0.58
2007 |  |  |  | 4666.98 |  |  | 5715 |  |  |  | 880 | [10 empty] | 61.11 |  |  |  | 63.24 | [5 empty] | 60.54 |  |  | 65.24 |  |  |  | 11.57 |  | 27.22 | [8 empty] | 9.54 |  |  |  |  | 2.13
2008 |  |  |  | 5147.36 |  |  | 6120 |  |  |  | 880 | [10 empty] | 66.84 |  |  |  | 67.85 | [5 empty] | 66.59 |  |  | 69.67 |  |  |  | 2.69 |  | 17.25 | [8 empty] | 14.89 |  |  |  |  | 1.01
2009 |  |  |  | 5382.77 |  |  | 6365 |  |  |  | 880 | [10 empty] | 70.10 |  |  |  | 71.39 | [5 empty] | 69.83 |  |  | 72.66 |  |  |  | 9.81 |  | 7.76 | [8 empty] | 20.85 |  |  |  |  | 1.29
2010 |  |  |  | 5181.48 |  |  | 6209 |  |  |  | 880 | [10 empty] | 68.01 |  |  |  | 68.10 | [5 empty] | 67.22 |  |  | 70.88 |  |  |  | 11.12 |  | 27.10 | [8 empty] | 4.80 |  |  |  |  | 0.09
2011 |  |  |  | 5187.84 |  |  | 6197 |  |  |  | 880 | [10 empty] | 68.03 |  |  |  | 68.45 | [5 empty] | 67.30 |  |  | 70.74 |  |  |  | 4.96 |  | 18.42 | [8 empty] | 13.13 |  |  |  |  | 0.42
2012 |  |  |  | 7031.35 |  |  | 8158 |  |  |  | 880 | [10 empty] | 92.44 |  |  |  | 92.50 | [5 empty] | 90.96 |  |  | 92.87 |  |  |  | 2.48 |  | 2.35 | [8 empty] | 5.15 |  |  |  |  | 0.06
2013 |  |  |  | 4453.46 |  |  | 5419 |  |  |  | 880 | [10 empty] | 58.06 |  |  |  | 60.17 | [5 empty] | 57.77 |  |  | 61.86 |  |  |  | 15.40 |  | 20.17 | [8 empty] | 19.66 |  |  |  |  | 2.10
2014 |  |  |  | 5361.14 |  |  | 6441 |  |  |  | 880 | [10 empty] | 70.47 |  |  |  | 71.47 | [5 empty] | 69.55 |  |  | 73.53 |  |  |  | 17.19 |  | 16.67 | [8 empty] | 11.86 |  |  |  |  | 1.00
2015 |  |  |  | 7194.82 |  |  | 8433 |  |  |  | 880 | [10 empty] | 93.80 |  |  |  | 94.39 | [5 empty] | 93.33 |  |  | 96.27 |  |  |  | 4.01 |  | 3.94 | [8 empty] | 1.67 |  |  |  |  | 0.60
2016 |  |  |  | 4981.46 |  |  | 6167 |  |  |  | 880 | [10 empty] | 64.89 |  |  |  | 72.67 | [5 empty] | 64.44 |  |  | 70.21 |  |  |  | 5.03 |  | 6.19 | [8 empty] | 21.14 |  |  |  |  | 7.78
2017 |  |  |  | 5807.00 |  |  | 6803 |  |  |  | 880 | [10 empty] | 76.11 |  |  |  | 77.29 | [5 empty] | 75.33 |  |  | 77.66 |  |  |  | 3.34 |  | 7.82 | [8 empty] | 14.89 |  |  |  |  | 1.18
2018 |  |  |  | 7037.75 |  |  | 8504 |  |  |  | 880 | [10 empty] | 93.10 |  |  |  | 98.06 | [5 empty] | 91.29 |  |  | 97.08 |  |  |  | 1.91 |  | 1.91 | [8 empty] | 0.03 |  |  |  |  | 4.97
2019 |  |  |  | 6208.07 |  |  | 7325 |  |  |  | 880 | [10 empty] | 81.03 |  |  |  | 82.73 | [5 empty] | 80.53 |  |  | 83.62 |  |  |  | 2.55 |  | 2.16 | [8 empty] | 15.10 |  |  |  |  | 1.70
2020 |  |  |  | 1082.25 |  |  | 1250 |  |  |  | 880 | [10 empty] | 96.70 |  |  |  | 96.70 | [5 empty] | 96.68 |  |  | 98.27 |  |  |  | 1.29 |  | 1.26 | [8 empty] | 2.03 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1978 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 784
B. |  | Refuelling without maintenance | [35 empty] | 77
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1099 |  |  |  | 10
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 53 |  |  |  | 8
E. |  | Testing of plant systems or components | [35 empty] | 12 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 43
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 84
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 5
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 5 | [11 empty] | 16
Z. |  | Other | [39 empty] | 2 | [11 empty] | 1
Subtotal | [37 empty] | 1241 |  |  |  | 937 | [11 empty] | 25
Total | [22 empty] | 0 | [14 empty] | 2203
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1978 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 237
12. |  |  | Reactor I&C Systems | [34 empty] | 38
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 49
15. |  |  | Reactor Cooling Systems | [34 empty] | 48
16. |  |  | Steam generation systems | [34 empty] | 38
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 122
32. |  |  | Feedwater and Main Steam System | [34 empty] | 26
34. |  |  | Miscellaneous Systems | [34 empty] | 78
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 84
42. |  |  | Electrical Power Supply Systems | [34 empty] | 52
Total | [37 empty] | 789

## FESSENHEIM-2
2020 Operating Experience
FR-12 | [8 empty] | FESSENHEIM-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | FRAM (FRAMATOME)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP0 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-02-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-10-07
Gross electrical power | [12 empty] | : |  |  | 920 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1978-04-01
Reference unit power (net) | [12 empty] | : |  |  | 880 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 332
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.257
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3697.08 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.91 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.78 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.9 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.43 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.67 %
Load Factor (LF) | [18 empty] | : | 96.2 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.65 %
Operating Factor (OF) | [18 empty] | : | 97.25 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 120 hours
Annual Summary
[5 empty] | Sep | Oct |  |  |  | Nov |  | Dec | [8 empty] | Jul |  |  | Aug | [6 empty] | Jan |  | Feb |  |  |  | Mar |  |  | Apr |  |  | May | [9 empty] | Jun |  |  | Annual
GW(e)-h | [30 empty] | 644.48 |  | 611.46 |  |  |  | 653.71 |  |  | 574.45 |  |  | 645.44 | [9 empty] | 567.54 |  |  | 3697.08
EAF [%] | [30 empty] | 98.08 |  | 99.98 |  |  |  | 99.99 |  |  | 92.40 |  |  | 99.65 | [9 empty] | 90.44 |  |  | 96.78
UCF [%] | [30 empty] | 98.08 |  | 99.98 |  |  |  | 99.99 |  |  | 92.40 |  |  | 99.99 | [9 empty] | 94.06 |  |  | 97.43
LF [%] | [30 empty] | 98.44 |  | 99.83 |  |  |  | 99.98 |  |  | 90.67 |  |  | 98.58 | [9 empty] | 89.57 |  |  | 96.20
OF [%] | [30 empty] | 98.39 |  | 100.00 |  |  |  | 100.00 |  |  | 92.50 |  |  | 100.00 | [9 empty] | 92.50 |  |  | 97.25
FLR [%] | [30 empty] | 1.92 |  | 0.02 |  |  |  | 0.00 |  |  | 7.60 |  |  | 0.00 | [9 empty] | 1.99 |  |  | 1.91
UCL [%] | [30 empty] | 1.92 |  | 0.02 |  |  |  | 0.00 |  |  | 7.60 |  |  | 0.00 | [9 empty] | 1.91 |  |  | 1.90
PUF [%] | [30 empty] | 0.00 |  | 0.00 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 4.02 |  |  | 0.67
XUF [%] | [30 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.33 | [9 empty] | 3.62 |  |  | 0.65
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 220567.97 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.09 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 70.8 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 72.16 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.29 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.36 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.15 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1978 |  |  |  | 5760.40 |  |  | 7032 |  |  |  | 890 | [10 empty] | 81.80 |  |  |  | 82.75 | [5 empty] | 81.47 |  |  | 85.58 |  |  |  | 17.25 |  | 17.25 | [8 empty] | 0.00 |  |  |  |  | 0.95
1979 |  |  |  | 4521.00 |  |  | 5684 |  |  |  | 890 | [10 empty] | 58.68 |  |  |  | 58.68 | [5 empty] | 57.99 |  |  | 64.89 |  |  |  | 6.28 |  | 3.93 | [8 empty] | 37.39 |  |  |  |  | 0.00
1980 |  |  |  | 5601.00 |  |  | 6603 |  |  |  | 890 | [10 empty] | 72.21 |  |  |  | 72.21 | [5 empty] | 71.64 |  |  | 75.17 |  |  |  | 14.40 |  | 12.15 | [8 empty] | 15.64 |  |  |  |  | 0.00
1981 |  |  |  | 6055.00 |  |  | 7117 |  |  |  | 890 | [10 empty] | 79.45 |  |  |  | 79.45 | [5 empty] | 77.66 |  |  | 81.24 |  |  |  | 4.79 |  | 4.00 | [8 empty] | 16.55 |  |  |  |  | 0.00
1982 |  |  |  | 6047.90 |  |  | 8247 |  |  |  | 880 | [10 empty] | 93.12 |  |  |  | 93.12 | [5 empty] | 78.45 |  |  | 94.14 |  |  |  | 6.87 |  | 6.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 4315.00 |  |  | 5206 |  |  |  | 880 | [10 empty] | 58.18 |  |  |  | 58.18 | [5 empty] | 55.97 |  |  | 59.43 |  |  |  | 20.64 |  | 15.13 | [8 empty] | 26.69 |  |  |  |  | 0.00
1984 |  |  |  | 6459.00 |  |  | 7860 |  |  |  | 880 | [10 empty] | 88.44 |  |  |  | 88.44 | [5 empty] | 83.56 |  |  | 89.48 |  |  |  | 2.18 |  | 1.97 | [8 empty] | 9.59 |  |  |  |  | 0.00
1985 |  |  |  | 5917.20 |  |  | 7248 |  |  |  | 880 | [10 empty] | 78.64 |  |  |  | 80.02 | [5 empty] | 76.76 |  |  | 82.74 |  |  |  | 4.74 |  | 3.99 | [8 empty] | 15.99 |  |  |  |  | 1.38
1986 |  |  |  | 5522.50 |  |  | 6573 |  |  |  | 880 | [10 empty] | 73.20 |  |  |  | 73.43 | [5 empty] | 71.64 |  |  | 75.03 |  |  |  | 17.34 |  | 15.41 | [8 empty] | 11.16 |  |  |  |  | 0.23
1987 |  |  |  | 6150.10 |  |  | 7335 |  |  |  | 880 | [10 empty] | 82.64 |  |  |  | 83.64 | [5 empty] | 79.78 |  |  | 83.73 |  |  |  | 4.49 |  | 3.93 | [8 empty] | 12.43 |  |  |  |  | 1.00
1988 |  |  |  | 4830.00 |  |  | 6158 |  |  |  | 880 | [10 empty] | 69.81 |  |  |  | 72.42 | [5 empty] | 62.48 |  |  | 70.10 |  |  |  | 15.48 |  | 13.26 | [8 empty] | 14.32 |  |  |  |  | 2.61
1989 |  |  |  | 5643.37 |  |  | 6944 |  |  |  | 880 | [10 empty] | 96.16 |  |  |  | 97.01 | [5 empty] | 73.21 |  |  | 79.27 |  |  |  | 2.93 |  | 2.93 | [8 empty] | 0.07 |  |  |  |  | 0.85
1990 |  |  |  | 3552.40 |  |  | 4612 |  |  |  | 880 | [10 empty] | 49.62 |  |  |  | 52.01 | [5 empty] | 46.08 |  |  | 52.65 |  |  |  | 8.36 |  | 4.74 | [8 empty] | 43.24 |  |  |  |  | 2.39
1991 |  |  |  | 5308.43 |  |  | 6537 |  |  |  | 880 | [10 empty] | 72.78 |  |  |  | 73.30 | [5 empty] | 68.86 |  |  | 74.62 |  |  |  | 12.15 |  | 10.14 | [8 empty] | 16.56 |  |  |  |  | 0.52
1992 |  |  |  | 2202.03 |  |  | 2699 |  |  |  | 880 | [10 empty] | 29.94 |  |  |  | 29.94 | [5 empty] | 28.49 |  |  | 30.73 |  |  |  | 42.88 |  | 22.47 | [8 empty] | 47.59 |  |  |  |  | 0.00
1993 |  |  |  | 5775.09 |  |  | 7167 |  |  |  | 880 | [10 empty] | 77.57 |  |  |  | 81.03 | [5 empty] | 74.92 |  |  | 81.82 |  |  |  | 5.47 |  | 4.69 | [8 empty] | 14.28 |  |  |  |  | 3.46
1994 |  |  |  | 5294.89 |  |  | 6807 |  |  |  | 880 | [10 empty] | 98.22 |  |  |  | 98.51 | [5 empty] | 68.69 |  |  | 77.71 |  |  |  | 1.48 |  | 1.47 | [8 empty] | 0.01 |  |  |  |  | 0.29
1995 |  |  |  | 5098.25 |  |  | 6305 |  |  |  | 880 | [10 empty] | 70.48 |  |  |  | 71.52 | [5 empty] | 66.14 |  |  | 71.97 |  |  |  | 17.84 |  | 15.53 | [8 empty] | 12.95 |  |  |  |  | 1.04
1996 |  |  |  | 6192.10 |  |  | 7515 |  |  |  | 880 | [10 empty] | 84.43 |  |  |  | 84.91 | [5 empty] | 80.11 |  |  | 85.55 |  |  |  | 2.76 |  | 2.41 | [8 empty] | 12.68 |  |  |  |  | 0.48
1997 |  |  |  | 5808.56 |  |  | 6982 |  |  |  | 880 | [10 empty] | 80.01 |  |  |  | 80.56 | [5 empty] | 75.35 |  |  | 79.70 |  |  |  | 1.59 |  | 1.31 | [8 empty] | 18.13 |  |  |  |  | 0.55
1998 |  |  |  | 5597.00 |  |  | 6797 |  |  |  | 880 | [10 empty] | 73.67 |  |  |  | 75.94 | [5 empty] | 72.61 |  |  | 77.59 |  |  |  | 12.40 |  | 10.75 | [8 empty] | 13.31 |  |  |  |  | 2.27
1999 |  |  |  | 6392.59 |  |  | 7708 |  |  |  | 880 | [10 empty] | 86.40 |  |  |  | 87.09 | [5 empty] | 82.93 |  |  | 87.99 |  |  |  | 1.31 |  | 1.16 | [8 empty] | 11.75 |  |  |  |  | 0.68
2000 |  |  |  | 3730.37 |  |  | 4514 |  |  |  | 880 | [10 empty] | 51.05 |  |  |  | 51.39 | [5 empty] | 48.26 |  |  | 51.39 |  |  |  | 17.15 |  | 10.64 | [8 empty] | 37.97 |  |  |  |  | 0.34
2001 |  |  |  | 6699.95 |  |  | 7876 |  |  |  | 880 | [10 empty] | 87.27 |  |  |  | 88.59 | [5 empty] | 86.91 |  |  | 89.91 |  |  |  | 9.56 |  | 9.37 | [8 empty] | 2.04 |  |  |  |  | 1.32
2002 |  |  |  | 6562.58 |  |  | 7729 |  |  |  | 880 | [10 empty] | 85.64 |  |  |  | 87.08 | [5 empty] | 85.13 |  |  | 88.23 |  |  |  | 2.66 |  | 2.38 | [8 empty] | 10.53 |  |  |  |  | 1.45
2003 |  |  |  | 4589.49 |  |  | 5434 |  |  |  | 880 | [10 empty] | 60.67 |  |  |  | 60.67 | [5 empty] | 59.54 |  |  | 62.03 |  |  |  | 25.14 |  | 20.37 | [8 empty] | 18.95 |  |  |  |  | 0.00
2004 |  |  |  | 6913.74 |  |  | 8435 |  |  |  | 880 | [10 empty] | 93.55 |  |  |  | 94.47 | [5 empty] | 89.44 |  |  | 96.03 |  |  |  | 5.24 |  | 5.23 | [8 empty] | 0.30 |  |  |  |  | 0.92
2005 |  |  |  | 6381.24 |  |  | 7813 |  |  |  | 880 | [10 empty] | 85.07 |  |  |  | 87.62 | [5 empty] | 82.77 |  |  | 89.18 |  |  |  | 1.76 |  | 3.38 | [8 empty] | 9.00 |  |  |  |  | 2.55
2006 |  |  |  | 4803.12 |  |  | 5844 |  |  |  | 880 | [10 empty] | 64.69 |  |  |  | 64.69 | [5 empty] | 62.31 |  |  | 66.71 |  |  |  | 13.06 |  | 15.76 | [8 empty] | 19.55 |  |  |  |  | 0.00
2007 |  |  |  | 4816.72 |  |  | 5781 |  |  |  | 880 | [10 empty] | 62.91 |  |  |  | 64.51 | [5 empty] | 62.48 |  |  | 65.99 |  |  |  | 15.38 |  | 23.23 | [8 empty] | 12.26 |  |  |  |  | 1.60
2008 |  |  |  | 5131.40 |  |  | 6384 |  |  |  | 880 | [10 empty] | 66.79 |  |  |  | 68.52 | [5 empty] | 66.38 |  |  | 72.68 |  |  |  | 31.06 |  | 30.87 | [8 empty] | 0.60 |  |  |  |  | 1.73
2009 |  |  |  | 3366.58 |  |  | 4206 |  |  |  | 880 | [10 empty] | 43.92 |  |  |  | 47.10 | [5 empty] | 43.67 |  |  | 48.01 |  |  |  | 4.83 |  | 37.00 | [8 empty] | 15.90 |  |  |  |  | 3.18
2010 |  |  |  | 6573.08 |  |  | 8100 |  |  |  | 880 | [10 empty] | 87.02 |  |  |  | 89.83 | [5 empty] | 85.27 |  |  | 92.47 |  |  |  | 10.05 |  | 10.04 | [8 empty] | 0.12 |  |  |  |  | 2.81
2011 |  |  |  | 1976.89 |  |  | 2521 |  |  |  | 880 | [10 empty] | 25.68 |  |  |  | 27.75 | [5 empty] | 25.64 |  |  | 28.78 |  |  |  | 3.50 |  | 9.23 | [8 empty] | 63.02 |  |  |  |  | 2.07
2012 |  |  |  | 5427.83 |  |  | 6584 |  |  |  | 880 | [10 empty] | 73.11 |  |  |  | 79.29 | [5 empty] | 70.22 |  |  | 74.95 |  |  |  | 2.06 |  | 19.60 | [8 empty] | 1.10 |  |  |  |  | 6.18
2013 |  |  |  | 4815.26 |  |  | 5841 |  |  |  | 880 | [10 empty] | 63.34 |  |  |  | 66.22 | [5 empty] | 62.46 |  |  | 66.68 |  |  |  | 1.98 |  | 12.02 | [8 empty] | 21.76 |  |  |  |  | 2.88
2014 |  |  |  | 6874.97 |  |  | 8244 |  |  |  | 880 | [10 empty] | 91.71 |  |  |  | 93.09 | [5 empty] | 89.18 |  |  | 94.11 |  |  |  | 6.73 |  | 6.71 | [8 empty] | 0.20 |  |  |  |  | 1.38
2015 |  |  |  | 5669.65 |  |  | 6904 |  |  |  | 880 | [10 empty] | 76.73 |  |  |  | 83.88 | [5 empty] | 73.55 |  |  | 78.81 |  |  |  | 2.53 |  | 4.65 | [8 empty] | 11.47 |  |  |  |  | 7.15
2016 |  |  |  | 3428.20 |  |  | 3960 |  |  |  | 880 | [10 empty] | 44.58 |  |  |  | 44.72 | [5 empty] | 44.35 |  |  | 45.08 |  |  |  | 0.56 |  | 42.35 | [8 empty] | 12.93 |  |  |  |  | 0.14
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 880 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 4909.07 |  |  | 6006 |  |  |  | 880 | [10 empty] | 64.50 |  |  |  | 67.30 | [5 empty] | 63.68 |  |  | 68.56 |  |  |  | 6.93 |  | 26.51 | [8 empty] | 6.19 |  |  |  |  | 2.79
2019 |  |  |  | 6108.70 |  |  | 7064 |  |  |  | 880 | [10 empty] | 79.65 |  |  |  | 79.87 | [5 empty] | 79.24 |  |  | 80.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.12 |  |  |  |  | 0.22
2020 |  |  |  | 3697.08 |  |  | 4247 |  |  |  | 880 | [10 empty] | 96.78 |  |  |  | 97.43 | [5 empty] | 96.20 |  |  | 97.25 |  |  |  | 1.91 |  | 1.90 | [8 empty] | 0.67 |  |  |  |  | 0.65
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1978 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 622 | [11 empty] | 3
B. |  | Refuelling without maintenance | [35 empty] | 40
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1144 |  |  |  | 5
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 47 |  |  |  | 19
E. |  | Testing of plant systems or components | [35 empty] | 17 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 349
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 13 | [11 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 11
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 25
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 24
Z. |  | Other | [39 empty] | 13
Subtotal | [37 empty] | 1249 |  |  |  | 1022 | [11 empty] | 65
Total | [22 empty] | 0 | [14 empty] | 2336
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1978 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 47
12. |  |  | Reactor I&C Systems | [34 empty] | 31
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 49
14. |  |  | Safety Systems | [34 empty] | 26
15. |  |  | Reactor Cooling Systems | [34 empty] | 23
16. |  |  | Steam generation systems | [34 empty] | 486
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 66
32. |  |  | Feedwater and Main Steam System | [34 empty] | 53
33. |  |  | Circulating Water System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 120
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 51
42. |  |  | Electrical Power Supply Systems | [34 empty] | 9
Total | [37 empty] | 974

## FLAMANVILLE-1
2020 Operating Experience
FR-46 | [8 empty] | FLAMANVILLE-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-12-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-12-04
Gross electrical power | [12 empty] | : |  |  | 1382 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-12-01
Reference unit power (net) | [12 empty] | : |  |  | 1330 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 84.57 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 84.57 %
Unit Capability Factor (UCF) | [18 empty] | : | 15.43 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 15.43 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 52.49 |  | 100.00 | [8 empty] | 32.93 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.43
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 47.51 |  | 0.00 | [8 empty] | 67.07 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.57
UCL [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 47.51 |  | 0.00 | [8 empty] | 67.07 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.57
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 52.49 |  | 100.00 | [8 empty] | 32.93 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.43
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 264895.71 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 14.51 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 69.85 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 15.08 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 72.5 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.41 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.73 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.65 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.15 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 5273.00 |  |  | 4840 |  |  |  | 1290 | [10 empty] | 97.32 |  |  |  | 97.34 | [5 empty] | 100.64 |  |  | 97.58 |  |  |  | 2.66 |  | 2.66 | [8 empty] | 0.00 |  |  |  |  | 0.02
1987 |  |  |  | 7150.80 |  |  | 5656 |  |  |  | 1290 | [10 empty] | 62.17 |  |  |  | 63.23 | [5 empty] | 63.28 |  |  | 64.57 |  |  |  | 15.78 |  | 11.84 | [8 empty] | 24.93 |  |  |  |  | 1.06
1988 |  |  |  | 7175.00 |  |  | 5757 |  |  |  | 1330 | [10 empty] | 66.02 |  |  |  | 67.42 | [5 empty] | 61.42 |  |  | 65.54 |  |  |  | 19.17 |  | 15.99 | [8 empty] | 16.59 |  |  |  |  | 1.40
1989 |  |  |  | 8775.16 |  |  | 7146 |  |  |  | 1330 | [10 empty] | 80.59 |  |  |  | 81.02 | [5 empty] | 75.32 |  |  | 81.58 |  |  |  | 18.90 |  | 18.88 | [8 empty] | 0.10 |  |  |  |  | 0.43
1990 |  |  |  | 7089.98 |  |  | 6360 |  |  |  | 1330 | [10 empty] | 65.70 |  |  |  | 67.04 | [5 empty] | 60.85 |  |  | 72.60 |  |  |  | 18.85 |  | 15.57 | [8 empty] | 17.39 |  |  |  |  | 1.35
1991 |  |  |  | 5882.88 |  |  | 5481 |  |  |  | 1330 | [10 empty] | 59.40 |  |  |  | 68.35 | [5 empty] | 50.49 |  |  | 62.57 |  |  |  | 15.52 |  | 12.56 | [8 empty] | 19.09 |  |  |  |  | 8.96
1992 |  |  |  | 7606.83 |  |  | 5901 |  |  |  | 1330 | [10 empty] | 66.20 |  |  |  | 66.20 | [5 empty] | 65.11 |  |  | 67.18 |  |  |  | 20.37 |  | 16.93 | [8 empty] | 16.87 |  |  |  |  | 0.00
1993 |  |  |  | 9301.82 |  |  | 7936 |  |  |  | 1330 | [10 empty] | 87.17 |  |  |  | 96.79 | [5 empty] | 79.84 |  |  | 90.59 |  |  |  | 3.15 |  | 3.15 | [8 empty] | 0.06 |  |  |  |  | 9.63
1994 |  |  |  | 7145.81 |  |  | 6515 |  |  |  | 1330 | [10 empty] | 75.32 |  |  |  | 80.13 | [5 empty] | 61.33 |  |  | 74.37 |  |  |  | 5.29 |  | 4.48 | [8 empty] | 15.39 |  |  |  |  | 4.81
1995 |  |  |  | 7665.06 |  |  | 6654 |  |  |  | 1330 | [10 empty] | 73.20 |  |  |  | 77.40 | [5 empty] | 65.79 |  |  | 75.96 |  |  |  | 10.29 |  | 8.87 | [8 empty] | 13.72 |  |  |  |  | 4.20
1996 |  |  |  | 8598.28 |  |  | 7050 |  |  |  | 1330 | [10 empty] | 77.80 |  |  |  | 84.58 | [5 empty] | 73.60 |  |  | 80.26 |  |  |  | 4.04 |  | 3.56 | [8 empty] | 11.86 |  |  |  |  | 6.79
1997 |  |  |  | 6853.94 |  |  | 5529 |  |  |  | 1330 | [10 empty] | 62.33 |  |  |  | 63.92 | [5 empty] | 58.83 |  |  | 63.12 |  |  |  | 16.88 |  | 12.98 | [8 empty] | 23.09 |  |  |  |  | 1.60
1998 |  |  |  | 9469.38 |  |  | 7855 |  |  |  | 1330 | [10 empty] | 86.66 |  |  |  | 86.67 | [5 empty] | 81.28 |  |  | 89.67 |  |  |  | 11.93 |  | 11.74 | [8 empty] | 1.59 |  |  |  |  | 0.01
1999 |  |  |  | 6979.37 |  |  | 5906 |  |  |  | 1330 | [10 empty] | 64.45 |  |  |  | 66.13 | [5 empty] | 59.90 |  |  | 67.42 |  |  |  | 12.88 |  | 9.78 | [8 empty] | 24.10 |  |  |  |  | 1.68
2000 |  |  |  | 8035.27 |  |  | 6607 |  |  |  | 1330 | [10 empty] | 74.51 |  |  |  | 75.55 | [5 empty] | 68.78 |  |  | 75.22 |  |  |  | 10.11 |  | 8.50 | [8 empty] | 15.95 |  |  |  |  | 1.04
2001 |  |  |  | 10038.55 |  |  | 8126 |  |  |  | 1330 | [10 empty] | 92.54 |  |  |  | 92.57 | [5 empty] | 86.16 |  |  | 92.76 |  |  |  | 6.82 |  | 6.77 | [8 empty] | 0.66 |  |  |  |  | 0.03
2002 |  |  |  | 8141.77 |  |  | 6736 |  |  |  | 1330 | [10 empty] | 73.11 |  |  |  | 75.51 | [5 empty] | 69.88 |  |  | 76.89 |  |  |  | 11.60 |  | 9.91 | [8 empty] | 14.57 |  |  |  |  | 2.40
2003 |  |  |  | 7510.77 |  |  | 6090 |  |  |  | 1330 | [10 empty] | 67.81 |  |  |  | 68.17 | [5 empty] | 64.47 |  |  | 69.52 |  |  |  | 12.17 |  | 9.45 | [8 empty] | 22.38 |  |  |  |  | 0.36
2004 |  |  |  | 10630.05 |  |  | 8668 |  |  |  | 1330 | [10 empty] | 96.85 |  |  |  | 98.20 | [5 empty] | 90.99 |  |  | 98.68 |  |  |  | 1.67 |  | 1.66 | [8 empty] | 0.13 |  |  |  |  | 1.35
2005 |  |  |  | 9099.89 |  |  | 7627 |  |  |  | 1330 | [10 empty] | 83.28 |  |  |  | 85.64 | [5 empty] | 78.10 |  |  | 87.06 |  |  |  | 3.77 |  | 3.36 | [8 empty] | 11.00 |  |  |  |  | 2.36
2006 |  |  |  | 7790.93 |  |  | 6675 |  |  |  | 1330 | [10 empty] | 69.12 |  |  |  | 72.51 | [5 empty] | 66.87 |  |  | 76.20 |  |  |  | 9.65 |  | 14.55 | [8 empty] | 12.93 |  |  |  |  | 3.39
2007 |  |  |  | 9595.59 |  |  | 8041 |  |  |  | 1330 | [10 empty] | 88.98 |  |  |  | 90.50 | [5 empty] | 82.36 |  |  | 91.79 |  |  |  | 9.49 |  | 9.49 | [8 empty] | 0.02 |  |  |  |  | 1.52
2008 |  |  |  | 4962.39 |  |  | 4018 |  |  |  | 1330 | [10 empty] | 42.91 |  |  |  | 43.78 | [5 empty] | 42.48 |  |  | 45.74 |  |  |  | 26.40 |  | 28.80 | [8 empty] | 27.41 |  |  |  |  | 0.87
2009 |  |  |  | 6956.71 |  |  | 5593 |  |  |  | 1330 | [10 empty] | 62.70 |  |  |  | 68.20 | [5 empty] | 59.71 |  |  | 63.85 |  |  |  | 5.98 |  | 18.71 | [8 empty] | 13.09 |  |  |  |  | 5.50
2010 |  |  |  | 8519.72 |  |  | 6955 |  |  |  | 1330 | [10 empty] | 75.78 |  |  |  | 77.58 | [5 empty] | 73.13 |  |  | 79.39 |  |  |  | 14.73 |  | 21.22 | [8 empty] | 1.21 |  |  |  |  | 1.80
2011 |  |  |  | 9572.66 |  |  | 7768 |  |  |  | 1330 | [10 empty] | 87.24 |  |  |  | 87.45 | [5 empty] | 82.16 |  |  | 88.68 |  |  |  | 0.75 |  | 2.59 | [8 empty] | 9.97 |  |  |  |  | 0.21
2012 |  |  |  | 6778.12 |  |  | 5618 |  |  |  | 1330 | [10 empty] | 61.38 |  |  |  | 65.94 | [5 empty] | 58.02 |  |  | 63.96 |  |  |  | 5.74 |  | 18.02 | [8 empty] | 16.04 |  |  |  |  | 4.57
2013 |  |  |  | 10422.78 |  |  | 8682 |  |  |  | 1330 | [10 empty] | 97.47 |  |  |  | 98.81 | [5 empty] | 89.46 |  |  | 99.11 |  |  |  | 1.17 |  | 1.17 | [8 empty] | 0.02 |  |  |  |  | 1.34
2014 |  |  |  | 8767.06 |  |  | 7002 |  |  |  | 1330 | [10 empty] | 77.96 |  |  |  | 81.21 | [5 empty] | 75.25 |  |  | 79.93 |  |  |  | 6.24 |  | 7.04 | [8 empty] | 11.75 |  |  |  |  | 3.26
2015 |  |  |  | 8408.87 |  |  | 6584 |  |  |  | 1330 | [10 empty] | 72.76 |  |  |  | 72.92 | [5 empty] | 72.17 |  |  | 75.16 |  |  |  | 2.46 |  | 1.84 | [8 empty] | 25.24 |  |  |  |  | 0.16
2016 |  |  |  | 9991.47 |  |  | 8013 |  |  |  | 1330 | [10 empty] | 87.04 |  |  |  | 87.68 | [5 empty] | 85.52 |  |  | 91.22 |  |  |  | 3.22 |  | 2.92 | [8 empty] | 9.41 |  |  |  |  | 0.64
2017 |  |  |  | 6352.00 |  |  | 5245 |  |  |  | 1330 | [10 empty] | 55.17 |  |  |  | 55.42 | [5 empty] | 54.52 |  |  | 59.87 |  |  |  | 44.56 |  | 44.55 | [8 empty] | 0.04 |  |  |  |  | 0.25
2018 |  |  |  | 2316.68 |  |  | 1832 |  |  |  | 1330 | [10 empty] | 23.48 |  |  |  | 25.31 | [5 empty] | 19.88 |  |  | 20.91 |  |  |  | 10.02 |  | 30.57 | [8 empty] | 44.12 |  |  |  |  | 1.83
2019 |  |  |  | 6402.31 |  |  | 5227 |  |  |  | 1330 | [10 empty] | 55.39 |  |  |  | 55.57 | [5 empty] | 54.95 |  |  | 59.67 |  |  |  | 38.19 |  | 41.69 | [8 empty] | 2.74 |  |  |  |  | 0.18
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1330 | [10 empty] | 0.00 |  |  |  | 15.43 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 84.57 |  | 84.57 | [8 empty] | 0.00 |  |  |  |  | 15.43
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1027
B. |  | Refuelling without maintenance | [35 empty] | 101
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 922
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 23
E. |  | Testing of plant systems or components | [35 empty] | 9 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 10
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 13
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 20
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 1 | [11 empty] | 36
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 6
Z. |  | Other | [39 empty] | 17 | [11 empty] | 1
Subtotal | [37 empty] | 1055 |  |  |  | 1059 | [11 empty] | 75
Total | [22 empty] | 0 | [14 empty] | 2189
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 90
12. |  |  | Reactor I&C Systems | [34 empty] | 36
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 40
14. |  |  | Safety Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 18
16. |  |  | Steam generation systems | [34 empty] | 49
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 138
32. |  |  | Feedwater and Main Steam System | [34 empty] | 61
33. |  |  | Circulating Water System | [34 empty] | 15
34. |  |  | Miscellaneous Systems | [34 empty] | 167
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 105
42. |  |  | Electrical Power Supply Systems | [34 empty] | 265
Total | [37 empty] | 1006

## FLAMANVILLE-2
2020 Operating Experience
FR-47 | [8 empty] | FLAMANVILLE-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-05-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-07-18
Gross electrical power | [12 empty] | : |  |  | 1382 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-03-09
Reference unit power (net) | [12 empty] | : |  |  | 1330 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 404.48 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.7 %
Energy Availability Factor (EAF) | [18 empty] | : | 3.47 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 80.83 %
Unit Capability Factor (UCF) | [18 empty] | : | 17.25 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 1.91 %
Load Factor (LF) | [18 empty] | : | 3.46 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 13.79 %
Operating Factor (OF) | [18 empty] | : | 5.44 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8306 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 404.48 |  |  | 404.48
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 40.93 |  |  | 3.47
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 52.49 |  | 100.00 | [8 empty] | 13.58 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 40.93 |  |  | 17.25
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 40.88 |  |  | 3.46
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 64.25 |  |  | 5.44
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 3.39 |  |  | 0.70
UCL [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 47.51 |  | 0.00 | [8 empty] | 86.42 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 36.48 |  |  | 80.83
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 22.59 |  |  | 1.91
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 52.49 |  | 100.00 | [8 empty] | 13.57 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.79
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 270622.3 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.78 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.08 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.14 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.08 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.78 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.85 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 7140.20 |  |  | 6310 |  |  |  | 1290 | [10 empty] | 88.69 |  |  |  | 88.92 | [5 empty] | 58.89 |  |  | 69.36 |  |  |  | 11.08 |  | 11.08 | [8 empty] | 0.00 |  |  |  |  | 0.23
1988 |  |  |  | 7106.00 |  |  | 5674 |  |  |  | 1330 | [10 empty] | 65.40 |  |  |  | 67.44 | [5 empty] | 60.82 |  |  | 64.59 |  |  |  | 8.21 |  | 6.03 | [8 empty] | 26.53 |  |  |  |  | 2.04
1989 |  |  |  | 4824.50 |  |  | 3836 |  |  |  | 1330 | [10 empty] | 48.67 |  |  |  | 50.57 | [5 empty] | 41.41 |  |  | 43.79 |  |  |  | 38.47 |  | 31.61 | [8 empty] | 17.82 |  |  |  |  | 1.89
1990 |  |  |  | 7819.60 |  |  | 6392 |  |  |  | 1330 | [10 empty] | 75.74 |  |  |  | 76.63 | [5 empty] | 67.12 |  |  | 72.97 |  |  |  | 22.84 |  | 22.68 | [8 empty] | 0.69 |  |  |  |  | 0.89
1991 |  |  |  | 7965.71 |  |  | 6432 |  |  |  | 1330 | [10 empty] | 70.59 |  |  |  | 72.34 | [5 empty] | 68.37 |  |  | 73.42 |  |  |  | 10.85 |  | 8.80 | [8 empty] | 18.86 |  |  |  |  | 1.75
1992 |  |  |  | 8842.44 |  |  | 6962 |  |  |  | 1330 | [10 empty] | 77.96 |  |  |  | 78.17 | [5 empty] | 75.69 |  |  | 79.26 |  |  |  | 6.18 |  | 5.15 | [8 empty] | 16.68 |  |  |  |  | 0.21
1993 |  |  |  | 7985.20 |  |  | 6338 |  |  |  | 1330 | [10 empty] | 69.15 |  |  |  | 71.43 | [5 empty] | 68.54 |  |  | 72.35 |  |  |  | 10.51 |  | 8.39 | [8 empty] | 20.18 |  |  |  |  | 2.28
1994 |  |  |  | 8384.27 |  |  | 6711 |  |  |  | 1330 | [10 empty] | 75.34 |  |  |  | 75.40 | [5 empty] | 71.96 |  |  | 76.61 |  |  |  | 10.72 |  | 9.06 | [8 empty] | 15.54 |  |  |  |  | 0.06
1995 |  |  |  | 8962.41 |  |  | 7264 |  |  |  | 1330 | [10 empty] | 81.40 |  |  |  | 82.14 | [5 empty] | 76.93 |  |  | 82.92 |  |  |  | 5.55 |  | 4.83 | [8 empty] | 13.03 |  |  |  |  | 0.74
1996 |  |  |  | 9387.50 |  |  | 7685 |  |  |  | 1330 | [10 empty] | 86.62 |  |  |  | 87.51 | [5 empty] | 80.35 |  |  | 87.49 |  |  |  | 1.62 |  | 1.44 | [8 empty] | 11.05 |  |  |  |  | 0.89
1997 |  |  |  | 8546.04 |  |  | 7351 |  |  |  | 1330 | [10 empty] | 95.30 |  |  |  | 95.36 | [5 empty] | 73.35 |  |  | 83.92 |  |  |  | 4.22 |  | 4.20 | [8 empty] | 0.43 |  |  |  |  | 0.06
1998 |  |  |  | 5656.61 |  |  | 4880 |  |  |  | 1330 | [10 empty] | 55.37 |  |  |  | 55.40 | [5 empty] | 48.55 |  |  | 55.71 |  |  |  | 9.47 |  | 5.79 | [8 empty] | 38.81 |  |  |  |  | 0.03
1999 |  |  |  | 7248.90 |  |  | 6034 |  |  |  | 1330 | [10 empty] | 65.22 |  |  |  | 67.42 | [5 empty] | 62.22 |  |  | 68.88 |  |  |  | 12.53 |  | 9.65 | [8 empty] | 22.92 |  |  |  |  | 2.20
2000 |  |  |  | 9907.94 |  |  | 8122 |  |  |  | 1330 | [10 empty] | 93.75 |  |  |  | 94.20 | [5 empty] | 84.81 |  |  | 92.46 |  |  |  | 4.93 |  | 4.89 | [8 empty] | 0.91 |  |  |  |  | 0.45
2001 |  |  |  | 8565.10 |  |  | 6863 |  |  |  | 1330 | [10 empty] | 76.22 |  |  |  | 77.88 | [5 empty] | 73.52 |  |  | 78.34 |  |  |  | 8.51 |  | 7.24 | [8 empty] | 14.88 |  |  |  |  | 1.66
2002 |  |  |  | 8502.35 |  |  | 6839 |  |  |  | 1330 | [10 empty] | 77.94 |  |  |  | 78.05 | [5 empty] | 72.98 |  |  | 78.07 |  |  |  | 11.37 |  | 10.02 | [8 empty] | 11.93 |  |  |  |  | 0.12
2003 |  |  |  | 10065.35 |  |  | 8365 |  |  |  | 1330 | [10 empty] | 93.39 |  |  |  | 93.64 | [5 empty] | 86.39 |  |  | 95.49 |  |  |  | 5.35 |  | 5.29 | [8 empty] | 1.07 |  |  |  |  | 0.25
2004 |  |  |  | 7499.84 |  |  | 6125 |  |  |  | 1330 | [10 empty] | 66.76 |  |  |  | 68.31 | [5 empty] | 64.20 |  |  | 69.73 |  |  |  | 12.84 |  | 10.06 | [8 empty] | 21.63 |  |  |  |  | 1.55
2005 |  |  |  | 9779.11 |  |  | 7894 |  |  |  | 1330 | [10 empty] | 86.69 |  |  |  | 89.11 | [5 empty] | 83.94 |  |  | 90.11 |  |  |  | 1.25 |  | 1.37 | [8 empty] | 9.52 |  |  |  |  | 2.42
2006 |  |  |  | 10125.81 |  |  | 8438 |  |  |  | 1330 | [10 empty] | 97.55 |  |  |  | 98.01 | [5 empty] | 86.91 |  |  | 96.32 |  |  |  | 1.97 |  | 1.97 | [8 empty] | 0.01 |  |  |  |  | 0.47
2007 |  |  |  | 8063.02 |  |  | 7021 |  |  |  | 1330 | [10 empty] | 76.52 |  |  |  | 78.31 | [5 empty] | 69.21 |  |  | 80.15 |  |  |  | 2.12 |  | 4.44 | [8 empty] | 17.25 |  |  |  |  | 1.79
2008 |  |  |  | 6140.92 |  |  | 5052 |  |  |  | 1330 | [10 empty] | 54.39 |  |  |  | 57.86 | [5 empty] | 52.56 |  |  | 57.51 |  |  |  | 6.63 |  | 14.49 | [8 empty] | 27.65 |  |  |  |  | 3.47
2009 |  |  |  | 9531.78 |  |  | 8016 |  |  |  | 1330 | [10 empty] | 88.36 |  |  |  | 90.94 | [5 empty] | 81.81 |  |  | 91.51 |  |  |  | 9.04 |  | 9.03 | [8 empty] | 0.03 |  |  |  |  | 2.57
2010 |  |  |  | 7594.30 |  |  | 6329 |  |  |  | 1330 | [10 empty] | 68.79 |  |  |  | 75.21 | [5 empty] | 65.18 |  |  | 72.25 |  |  |  | 3.69 |  | 7.81 | [8 empty] | 16.97 |  |  |  |  | 6.42
2011 |  |  |  | 9342.70 |  |  | 7438 |  |  |  | 1330 | [10 empty] | 83.49 |  |  |  | 83.83 | [5 empty] | 80.19 |  |  | 84.91 |  |  |  | 3.44 |  | 7.77 | [8 empty] | 8.39 |  |  |  |  | 0.34
2012 |  |  |  | 10359.02 |  |  | 8733 |  |  |  | 1330 | [10 empty] | 99.27 |  |  |  | 99.52 | [5 empty] | 88.67 |  |  | 99.42 |  |  |  | 0.47 |  | 0.47 | [8 empty] | 0.02 |  |  |  |  | 0.25
2013 |  |  |  | 7631.58 |  |  | 6183 |  |  |  | 1330 | [10 empty] | 66.34 |  |  |  | 70.74 | [5 empty] | 65.50 |  |  | 70.58 |  |  |  | 2.11 |  | 9.95 | [8 empty] | 19.31 |  |  |  |  | 4.40
2014 |  |  |  | 9693.92 |  |  | 7610 |  |  |  | 1330 | [10 empty] | 84.82 |  |  |  | 85.27 | [5 empty] | 83.20 |  |  | 86.87 |  |  |  | 3.88 |  | 5.01 | [8 empty] | 9.72 |  |  |  |  | 0.45
2015 |  |  |  | 7869.45 |  |  | 6149 |  |  |  | 1330 | [10 empty] | 68.68 |  |  |  | 69.94 | [5 empty] | 67.54 |  |  | 70.19 |  |  |  | 3.76 |  | 4.32 | [8 empty] | 25.75 |  |  |  |  | 1.26
2016 |  |  |  | 9880.46 |  |  | 8013 |  |  |  | 1330 | [10 empty] | 87.97 |  |  |  | 88.51 | [5 empty] | 84.57 |  |  | 91.22 |  |  |  | 11.45 |  | 11.45 | [8 empty] | 0.04 |  |  |  |  | 0.54
2017 |  |  |  | 7646.67 |  |  | 6107 |  |  |  | 1330 | [10 empty] | 65.67 |  |  |  | 68.03 | [5 empty] | 65.63 |  |  | 69.71 |  |  |  | 7.65 |  | 5.63 | [8 empty] | 26.33 |  |  |  |  | 2.36
2018 |  |  |  | 10350.78 |  |  | 8415 |  |  |  | 1330 | [10 empty] | 90.14 |  |  |  | 98.71 | [5 empty] | 88.84 |  |  | 96.06 |  |  |  | 0.84 |  | 0.84 | [8 empty] | 0.45 |  |  |  |  | 8.57
2019 |  |  |  | 236.76 |  |  | 217 |  |  |  | 1330 | [10 empty] | 2.04 |  |  |  | 3.40 | [5 empty] | 2.03 |  |  | 2.48 |  |  |  | 0.00 |  | 47.00 | [8 empty] | 49.60 |  |  |  |  | 1.36
2020 |  |  |  | 404.48 |  |  | 478 |  |  |  | 1330 | [10 empty] | 3.47 |  |  |  | 17.25 | [5 empty] | 3.46 |  |  | 5.44 |  |  |  | 0.70 |  | 80.83 | [8 empty] | 1.91 |  |  |  |  | 13.79
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 690
B. |  | Refuelling without maintenance | [35 empty] | 67
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1016 |  |  |  | 23
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 68
E. |  | Testing of plant systems or components | [35 empty] | 17 |  |  |  | 1 | [11 empty] | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 14
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 7
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 7
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 11
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 1 | [11 empty] | 23
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 1 | [15 empty] | 8
Z. |  | Other | [39 empty] | 17
Subtotal | [37 empty] | 1169 |  |  |  | 753 | [11 empty] | 49
Total | [22 empty] | 0 | [14 empty] | 1971
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 9
12. |  |  | Reactor I&C Systems | [34 empty] | 27
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 39
14. |  |  | Safety Systems | [34 empty] | 15
15. |  |  | Reactor Cooling Systems | [34 empty] | 136
16. |  |  | Steam generation systems | [34 empty] | 51
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 6
31. |  |  | Turbine and auxiliaries | [34 empty] | 81
32. |  |  | Feedwater and Main Steam System | [34 empty] | 32
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 154
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 41
42. |  |  | Electrical Power Supply Systems | [34 empty] | 81
Total | [37 empty] | 682

## GOLFECH-1
2020 Operating Experience
FR-61 | [8 empty] | GOLFECH-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-11-17
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-06-07
Gross electrical power | [12 empty] | : |  |  | 1363 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1991-02-01
Reference unit power (net) | [12 empty] | : |  |  | 1310 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7133.37 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.12 %
Energy Availability Factor (EAF) | [18 empty] | : | 63.13 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.54 %
Unit Capability Factor (UCF) | [18 empty] | : | 68.53 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 23.93 %
Load Factor (LF) | [18 empty] | : | 61.99 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 5.39 %
Operating Factor (OF) | [18 empty] | : | 66.39 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2952 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 912.15 | 862.40 |  |  |  | 955.32 |  | 924.79 | [8 empty] | 947.97 |  |  | 897.05 | [6 empty] | 831.47 |  | 220.88 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 581.34 |  |  | 7133.37
EAF [%] |  |  |  |  | 99.85 | 99.85 |  |  |  | 99.48 |  | 98.40 | [8 empty] | 97.65 |  |  | 95.21 | [6 empty] | 85.37 |  | 22.66 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 59.74 |  |  | 63.13
UCF [%] |  |  |  |  | 99.92 | 99.95 |  |  |  | 99.78 |  | 99.60 | [8 empty] | 99.62 |  |  | 99.89 | [6 empty] | 99.94 |  | 45.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 17.78 | [9 empty] | 61.15 |  |  | 68.53
LF [%] |  |  |  |  | 93.59 | 94.59 |  |  |  | 98.15 |  | 98.05 | [8 empty] | 97.26 |  |  | 95.11 | [6 empty] | 85.31 |  | 22.66 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 59.65 |  |  | 61.99
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 29.30 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 67.61 |  |  | 66.39
FLR [%] |  |  |  |  | 0.05 | 0.02 |  |  |  | 0.19 |  | 0.25 | [8 empty] | 0.31 |  |  | 0.07 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.10 | [9 empty] | 0.11 |  |  | 0.12
UCL [%] |  |  |  |  | 0.05 | 0.02 |  |  |  | 0.19 |  | 0.25 | [8 empty] | 0.31 |  |  | 0.07 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 59.00 | [9 empty] | 31.09 |  |  | 7.54
PUF [%] |  |  |  |  | 0.03 | 0.03 |  |  |  | 0.03 |  | 0.15 | [8 empty] | 0.08 |  |  | 0.03 | [6 empty] | 0.06 |  | 55.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 23.22 | [9 empty] | 7.75 |  |  | 23.93
XUF [%] |  |  |  |  | 0.07 | 0.10 |  |  |  | 0.30 |  | 1.19 | [8 empty] | 1.97 |  |  | 4.69 | [6 empty] | 14.57 |  | 22.34 |  |  |  | 0.00 |  |  | 0.00 |  |  | 17.77 | [9 empty] | 1.42 |  |  | 5.39
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 263833.93 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.04 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.9 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.45 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.65 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.14 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.99 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.43 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1991 |  |  |  | 9536.95 |  |  | 8167 |  |  |  | 1310 | [10 empty] | 96.09 |  |  |  | 97.76 | [5 empty] | 84.48 |  |  | 94.91 |  |  |  | 2.21 |  | 2.21 | [8 empty] | 0.02 |  |  |  |  | 1.68
1992 |  |  |  | 7065.89 |  |  | 6128 |  |  |  | 1310 | [10 empty] | 64.35 |  |  |  | 67.86 | [5 empty] | 61.40 |  |  | 69.76 |  |  |  | 4.27 |  | 3.02 | [8 empty] | 29.11 |  |  |  |  | 3.51
1993 |  |  |  | 7925.62 |  |  | 7143 |  |  |  | 1310 | [10 empty] | 72.66 |  |  |  | 82.63 | [5 empty] | 69.06 |  |  | 81.54 |  |  |  | 1.85 |  | 1.55 | [8 empty] | 15.81 |  |  |  |  | 9.98
1994 |  |  |  | 7756.13 |  |  | 7215 |  |  |  | 1310 | [10 empty] | 77.76 |  |  |  | 81.29 | [5 empty] | 67.59 |  |  | 82.36 |  |  |  | 5.91 |  | 5.10 | [8 empty] | 13.61 |  |  |  |  | 3.53
1995 |  |  |  | 7897.84 |  |  | 7005 |  |  |  | 1310 | [10 empty] | 75.60 |  |  |  | 83.48 | [5 empty] | 68.82 |  |  | 79.97 |  |  |  | 2.12 |  | 1.81 | [8 empty] | 14.71 |  |  |  |  | 7.89
1996 |  |  |  | 8862.41 |  |  | 7598 |  |  |  | 1310 | [10 empty] | 83.25 |  |  |  | 84.83 | [5 empty] | 77.02 |  |  | 86.50 |  |  |  | 1.33 |  | 1.14 | [8 empty] | 14.02 |  |  |  |  | 1.58
1997 |  |  |  | 9151.57 |  |  | 8000 |  |  |  | 1310 | [10 empty] | 94.51 |  |  |  | 94.63 | [5 empty] | 79.75 |  |  | 91.32 |  |  |  | 5.19 |  | 5.18 | [8 empty] | 0.19 |  |  |  |  | 0.12
1998 |  |  |  | 8576.56 |  |  | 7472 |  |  |  | 1310 | [10 empty] | 81.11 |  |  |  | 84.75 | [5 empty] | 74.74 |  |  | 85.30 |  |  |  | 1.96 |  | 1.69 | [8 empty] | 13.56 |  |  |  |  | 3.64
1999 |  |  |  | 7926.35 |  |  | 6837 |  |  |  | 1310 | [10 empty] | 77.23 |  |  |  | 80.77 | [5 empty] | 69.07 |  |  | 78.05 |  |  |  | 6.76 |  | 5.86 | [8 empty] | 13.37 |  |  |  |  | 3.54
2000 |  |  |  | 8766.29 |  |  | 7901 |  |  |  | 1310 | [10 empty] | 93.90 |  |  |  | 94.09 | [5 empty] | 76.18 |  |  | 89.95 |  |  |  | 5.59 |  | 5.57 | [8 empty] | 0.34 |  |  |  |  | 0.19
2001 |  |  |  | 7511.92 |  |  | 6147 |  |  |  | 1310 | [10 empty] | 68.41 |  |  |  | 69.14 | [5 empty] | 65.46 |  |  | 70.17 |  |  |  | 4.63 |  | 3.36 | [8 empty] | 27.50 |  |  |  |  | 0.74
2002 |  |  |  | 9242.42 |  |  | 7301 |  |  |  | 1310 | [10 empty] | 81.36 |  |  |  | 82.54 | [5 empty] | 80.54 |  |  | 83.34 |  |  |  | 4.01 |  | 3.45 | [8 empty] | 14.01 |  |  |  |  | 1.19
2003 |  |  |  | 10342.73 |  |  | 8252 |  |  |  | 1310 | [10 empty] | 93.92 |  |  |  | 99.20 | [5 empty] | 90.13 |  |  | 94.20 |  |  |  | 0.76 |  | 0.76 | [8 empty] | 0.04 |  |  |  |  | 5.28
2004 |  |  |  | 9051.07 |  |  | 7721 |  |  |  | 1310 | [10 empty] | 84.75 |  |  |  | 87.60 | [5 empty] | 78.66 |  |  | 87.90 |  |  |  | 2.63 |  | 2.36 | [8 empty] | 10.04 |  |  |  |  | 2.85
2005 |  |  |  | 8653.53 |  |  | 7014 |  |  |  | 1310 | [10 empty] | 78.73 |  |  |  | 78.73 | [5 empty] | 75.40 |  |  | 80.06 |  |  |  | 1.77 |  | 1.42 | [8 empty] | 19.85 |  |  |  |  | 0.00
2006 |  |  |  | 9475.13 |  |  | 7848 |  |  |  | 1310 | [10 empty] | 85.72 |  |  |  | 88.74 | [5 empty] | 82.57 |  |  | 89.59 |  |  |  | 0.14 |  | 2.57 | [8 empty] | 8.69 |  |  |  |  | 3.02
2007 |  |  |  | 9517.60 |  |  | 8554 |  |  |  | 1310 | [10 empty] | 97.73 |  |  |  | 98.16 | [5 empty] | 82.94 |  |  | 97.65 |  |  |  | 1.82 |  | 1.82 | [8 empty] | 0.02 |  |  |  |  | 0.43
2008 |  |  |  | 8556.94 |  |  | 7104 |  |  |  | 1310 | [10 empty] | 77.81 |  |  |  | 80.02 | [5 empty] | 74.36 |  |  | 80.87 |  |  |  | 0.58 |  | 5.81 | [8 empty] | 14.17 |  |  |  |  | 2.22
2009 |  |  |  | 9662.38 |  |  | 7932 |  |  |  | 1310 | [10 empty] | 87.58 |  |  |  | 89.93 | [5 empty] | 84.20 |  |  | 90.55 |  |  |  | 1.13 |  | 1.43 | [8 empty] | 8.63 |  |  |  |  | 2.36
2010 |  |  |  | 8888.69 |  |  | 7290 |  |  |  | 1310 | [10 empty] | 81.68 |  |  |  | 83.88 | [5 empty] | 77.46 |  |  | 83.22 |  |  |  | 0.76 |  | 0.93 | [8 empty] | 15.19 |  |  |  |  | 2.19
2011 |  |  |  | 9830.09 |  |  | 8546 |  |  |  | 1310 | [10 empty] | 97.79 |  |  |  | 98.34 | [5 empty] | 85.66 |  |  | 97.56 |  |  |  | 0.25 |  | 0.41 | [8 empty] | 1.25 |  |  |  |  | 0.54
2012 |  |  |  | 7272.39 |  |  | 5889 |  |  |  | 1310 | [10 empty] | 64.64 |  |  |  | 65.74 | [5 empty] | 63.20 |  |  | 67.04 |  |  |  | 0.27 |  | 8.88 | [8 empty] | 25.38 |  |  |  |  | 1.10
2013 |  |  |  | 9694.33 |  |  | 7793 |  |  |  | 1310 | [10 empty] | 87.80 |  |  |  | 88.49 | [5 empty] | 84.48 |  |  | 88.96 |  |  |  | 1.25 |  | 3.45 | [8 empty] | 8.05 |  |  |  |  | 0.69
2014 |  |  |  | 8149.57 |  |  | 6728 |  |  |  | 1310 | [10 empty] | 76.10 |  |  |  | 78.18 | [5 empty] | 71.02 |  |  | 76.80 |  |  |  | 0.16 |  | 4.40 | [8 empty] | 17.41 |  |  |  |  | 2.08
2015 |  |  |  | 10067.40 |  |  | 8721 |  |  |  | 1310 | [10 empty] | 99.33 |  |  |  | 99.69 | [5 empty] | 87.73 |  |  | 99.55 |  |  |  | 0.24 |  | 0.24 | [8 empty] | 0.06 |  |  |  |  | 0.36
2016 |  |  |  | 9913.55 |  |  | 7917 |  |  |  | 1310 | [10 empty] | 87.08 |  |  |  | 89.93 | [5 empty] | 86.15 |  |  | 90.13 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 10.06 |  |  |  |  | 2.85
2017 |  |  |  | 8310.56 |  |  | 6654 |  |  |  | 1310 | [10 empty] | 74.48 |  |  |  | 78.36 | [5 empty] | 72.42 |  |  | 75.96 |  |  |  | 0.47 |  | 2.39 | [8 empty] | 19.25 |  |  |  |  | 3.88
2018 |  |  |  | 9174.78 |  |  | 8075 |  |  |  | 1310 | [10 empty] | 88.51 |  |  |  | 99.32 | [5 empty] | 79.95 |  |  | 92.18 |  |  |  | 0.58 |  | 0.58 | [8 empty] | 0.09 |  |  |  |  | 10.81
2019 |  |  |  | 8314.41 |  |  | 7199 |  |  |  | 1310 | [10 empty] | 81.91 |  |  |  | 88.03 | [5 empty] | 72.45 |  |  | 82.18 |  |  |  | 2.01 |  | 1.97 | [8 empty] | 10.00 |  |  |  |  | 6.12
2020 |  |  |  | 7133.37 |  |  | 5832 |  |  |  | 1310 | [10 empty] | 63.13 |  |  |  | 68.53 | [5 empty] | 61.99 |  |  | 66.39 |  |  |  | 0.12 |  | 7.54 | [8 empty] | 23.93 |  |  |  |  | 5.39
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1991 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 178
B. |  | Refuelling without maintenance | [35 empty] | 100
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 786 |  |  |  | 2
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 38
E. |  | Testing of plant systems or components | [35 empty] | 41
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 4
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 23 | [11 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 21
O. |  | Load dispatching, prioritization | [51 empty] | 3
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 0 | [11 empty] | 25
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 30
Z. |  | Other | [39 empty] | 9 | [11 empty] | 1
Subtotal | [37 empty] | 969 |  |  |  | 216 | [11 empty] | 85
Total | [22 empty] | 0 | [14 empty] | 1270
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1991 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 17
16. |  |  | Steam generation systems | [34 empty] | 12
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 60
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 28
42. |  |  | Electrical Power Supply Systems | [34 empty] | 6
Total | [37 empty] | 183

## GOLFECH-2
2020 Operating Experience
FR-68 | [8 empty] | GOLFECH-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-10-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-06-18
Gross electrical power | [12 empty] | : |  |  | 1363 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-03-04
Reference unit power (net) | [12 empty] | : |  |  | 1310 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9160.17 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 5.75 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.19 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.74 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.18 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.08 %
Load Factor (LF) | [18 empty] | : | 79.6 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.99 %
Operating Factor (OF) | [18 empty] | : | 92.71 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 640 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 900.32 | 721.88 |  |  |  | 762.03 |  | 562.51 | [8 empty] | 690.31 |  |  | 791.17 | [6 empty] | 836.94 |  | 827.39 |  |  |  | 527.63 |  |  | 888.64 |  |  | 735.73 | [9 empty] | 915.62 |  |  | 9160.17
EAF [%] |  |  |  |  | 99.36 | 98.65 |  |  |  | 99.73 |  | 81.78 | [8 empty] | 95.53 |  |  | 98.27 | [6 empty] | 97.50 |  | 93.93 |  |  |  | 60.54 |  |  | 99.34 |  |  | 81.15 | [9 empty] | 99.42 |  |  | 92.19
UCF [%] |  |  |  |  | 99.90 | 99.87 |  |  |  | 99.78 |  | 90.30 | [8 empty] | 99.73 |  |  | 99.72 | [6 empty] | 99.41 |  | 98.44 |  |  |  | 61.23 |  |  | 99.73 |  |  | 81.43 | [9 empty] | 99.57 |  |  | 94.18
LF [%] |  |  |  |  | 92.37 | 79.17 |  |  |  | 78.29 |  | 59.64 | [8 empty] | 70.83 |  |  | 83.88 | [6 empty] | 85.87 |  | 84.89 |  |  |  | 55.94 |  |  | 91.05 |  |  | 78.00 | [9 empty] | 93.94 |  |  | 79.60
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 82.22 | [8 empty] | 93.28 |  |  | 97.50 | [6 empty] | 97.85 |  | 96.91 |  |  |  | 61.67 |  |  | 99.87 |  |  | 82.22 | [9 empty] | 100.00 |  |  | 92.71
FLR [%] |  |  |  |  | 0.03 | 0.04 |  |  |  | 0.12 |  | 9.67 | [8 empty] | 0.19 |  |  | 0.18 | [6 empty] | 0.50 |  | 1.49 |  |  |  | 38.72 |  |  | 0.20 |  |  | 18.48 | [9 empty] | 0.40 |  |  | 5.75
UCL [%] |  |  |  |  | 0.03 | 0.04 |  |  |  | 0.12 |  | 9.67 | [8 empty] | 0.19 |  |  | 0.18 | [6 empty] | 0.50 |  | 1.49 |  |  |  | 38.69 |  |  | 0.20 |  |  | 18.46 | [9 empty] | 0.40 |  |  | 5.74
PUF [%] |  |  |  |  | 0.07 | 0.09 |  |  |  | 0.10 |  | 0.03 | [8 empty] | 0.08 |  |  | 0.11 | [6 empty] | 0.10 |  | 0.07 |  |  |  | 0.08 |  |  | 0.07 |  |  | 0.11 | [9 empty] | 0.03 |  |  | 0.08
XUF [%] |  |  |  |  | 0.54 | 1.22 |  |  |  | 0.05 |  | 8.52 | [8 empty] | 4.19 |  |  | 1.44 | [6 empty] | 1.90 |  | 4.52 |  |  |  | 0.69 |  |  | 0.39 |  |  | 0.28 | [9 empty] | 0.15 |  |  | 1.99
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 238250.09 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.67 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.67 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.59 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.75 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.38 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.66 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.17 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 7281.51 |  |  | 6577 |  |  |  | 1310 | [10 empty] | 99.45 |  |  |  | 99.75 | [5 empty] | 67.64 |  |  | 80.50 |  |  |  | 0.25 |  | 0.25 | [8 empty] | 0.01 |  |  |  |  | 0.30
1995 |  |  |  | 7030.15 |  |  | 6002 |  |  |  | 1310 | [10 empty] | 62.92 |  |  |  | 66.66 | [5 empty] | 61.26 |  |  | 68.52 |  |  |  | 12.67 |  | 9.67 | [8 empty] | 23.66 |  |  |  |  | 3.75
1996 |  |  |  | 9016.38 |  |  | 7549 |  |  |  | 1310 | [10 empty] | 83.58 |  |  |  | 84.69 | [5 empty] | 78.36 |  |  | 85.94 |  |  |  | 3.50 |  | 3.07 | [8 empty] | 12.24 |  |  |  |  | 1.11
1997 |  |  |  | 8649.91 |  |  | 7414 |  |  |  | 1310 | [10 empty] | 80.22 |  |  |  | 83.68 | [5 empty] | 75.38 |  |  | 84.63 |  |  |  | 5.05 |  | 4.45 | [8 empty] | 11.87 |  |  |  |  | 3.47
1998 |  |  |  | 8359.56 |  |  | 7222 |  |  |  | 1310 | [10 empty] | 82.89 |  |  |  | 85.07 | [5 empty] | 72.85 |  |  | 82.44 |  |  |  | 6.43 |  | 5.84 | [8 empty] | 9.09 |  |  |  |  | 2.17
1999 |  |  |  | 9516.92 |  |  | 8407 |  |  |  | 1310 | [10 empty] | 97.70 |  |  |  | 98.02 | [5 empty] | 82.93 |  |  | 95.97 |  |  |  | 1.16 |  | 1.15 | [8 empty] | 0.82 |  |  |  |  | 0.32
2000 |  |  |  | 8877.61 |  |  | 7535 |  |  |  | 1310 | [10 empty] | 81.82 |  |  |  | 84.45 | [5 empty] | 77.15 |  |  | 85.78 |  |  |  | 1.43 |  | 1.23 | [8 empty] | 14.32 |  |  |  |  | 2.64
2001 |  |  |  | 8958.29 |  |  | 7586 |  |  |  | 1310 | [10 empty] | 84.33 |  |  |  | 85.31 | [5 empty] | 78.06 |  |  | 86.60 |  |  |  | 2.14 |  | 1.87 | [8 empty] | 12.82 |  |  |  |  | 0.98
2002 |  |  |  | 9847.13 |  |  | 8553 |  |  |  | 1310 | [10 empty] | 97.32 |  |  |  | 97.32 | [5 empty] | 85.81 |  |  | 97.64 |  |  |  | 2.30 |  | 2.29 | [8 empty] | 0.40 |  |  |  |  | 0.00
2003 |  |  |  | 7614.92 |  |  | 7115 |  |  |  | 1310 | [10 empty] | 75.24 |  |  |  | 77.69 | [5 empty] | 66.36 |  |  | 81.22 |  |  |  | 11.19 |  | 9.79 | [8 empty] | 12.52 |  |  |  |  | 2.45
2004 |  |  |  | 7093.66 |  |  | 6129 |  |  |  | 1310 | [10 empty] | 65.70 |  |  |  | 65.72 | [5 empty] | 61.65 |  |  | 69.77 |  |  |  | 5.74 |  | 4.00 | [8 empty] | 30.28 |  |  |  |  | 0.02
2005 |  |  |  | 9936.28 |  |  | 8715 |  |  |  | 1310 | [10 empty] | 98.89 |  |  |  | 99.19 | [5 empty] | 86.58 |  |  | 99.47 |  |  |  | 0.79 |  | 0.79 | [8 empty] | 0.02 |  |  |  |  | 0.30
2006 |  |  |  | 8516.61 |  |  | 7150 |  |  |  | 1310 | [10 empty] | 78.24 |  |  |  | 84.83 | [5 empty] | 74.21 |  |  | 81.62 |  |  |  | 1.10 |  | 0.94 | [8 empty] | 14.23 |  |  |  |  | 6.59
2007 |  |  |  | 9922.05 |  |  | 8026 |  |  |  | 1310 | [10 empty] | 90.15 |  |  |  | 90.86 | [5 empty] | 86.46 |  |  | 91.62 |  |  |  | 0.49 |  | 0.48 | [8 empty] | 8.66 |  |  |  |  | 0.71
2008 |  |  |  | 8484.22 |  |  | 7095 |  |  |  | 1310 | [10 empty] | 76.69 |  |  |  | 79.15 | [5 empty] | 73.73 |  |  | 80.77 |  |  |  | 2.28 |  | 6.43 | [8 empty] | 14.41 |  |  |  |  | 2.46
2009 |  |  |  | 9982.79 |  |  | 8301 |  |  |  | 1310 | [10 empty] | 96.63 |  |  |  | 99.53 | [5 empty] | 86.99 |  |  | 94.76 |  |  |  | 0.45 |  | 0.45 | [8 empty] | 0.02 |  |  |  |  | 2.90
2010 |  |  |  | 9076.12 |  |  | 7574 |  |  |  | 1310 | [10 empty] | 83.62 |  |  |  | 85.83 | [5 empty] | 79.09 |  |  | 86.46 |  |  |  | 0.56 |  | 2.20 | [8 empty] | 11.98 |  |  |  |  | 2.21
2011 |  |  |  | 8848.37 |  |  | 7177 |  |  |  | 1310 | [10 empty] | 80.20 |  |  |  | 81.36 | [5 empty] | 77.11 |  |  | 81.93 |  |  |  | 0.60 |  | 5.97 | [8 empty] | 12.68 |  |  |  |  | 1.16
2012 |  |  |  | 8580.05 |  |  | 7152 |  |  |  | 1310 | [10 empty] | 81.00 |  |  |  | 81.03 | [5 empty] | 74.56 |  |  | 81.42 |  |  |  | 0.07 |  | 6.90 | [8 empty] | 12.07 |  |  |  |  | 0.03
2013 |  |  |  | 9498.61 |  |  | 8292 |  |  |  | 1310 | [10 empty] | 96.15 |  |  |  | 96.15 | [5 empty] | 82.77 |  |  | 94.66 |  |  |  | 3.83 |  | 3.82 | [8 empty] | 0.03 |  |  |  |  | 0.00
2014 |  |  |  | 6885.14 |  |  | 5885 |  |  |  | 1310 | [10 empty] | 64.88 |  |  |  | 66.94 | [5 empty] | 60.00 |  |  | 67.18 |  |  |  | 0.42 |  | 3.33 | [8 empty] | 29.73 |  |  |  |  | 2.05
2015 |  |  |  | 8751.76 |  |  | 7332 |  |  |  | 1310 | [10 empty] | 82.56 |  |  |  | 82.90 | [5 empty] | 76.26 |  |  | 83.70 |  |  |  | 0.40 |  | 0.33 | [8 empty] | 16.77 |  |  |  |  | 0.34
2016 |  |  |  | 9963.09 |  |  | 8765 |  |  |  | 1310 | [10 empty] | 98.52 |  |  |  | 99.60 | [5 empty] | 86.58 |  |  | 99.78 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.04 |  |  |  |  | 1.08
2017 |  |  |  | 9551.16 |  |  | 7756 |  |  |  | 1310 | [10 empty] | 85.41 |  |  |  | 88.04 | [5 empty] | 83.23 |  |  | 88.54 |  |  |  | 1.73 |  | 2.33 | [8 empty] | 9.63 |  |  |  |  | 2.63
2018 |  |  |  | 8054.15 |  |  | 6380 |  |  |  | 1310 | [10 empty] | 70.73 |  |  |  | 71.79 | [5 empty] | 70.19 |  |  | 72.83 |  |  |  | 1.27 |  | 8.38 | [8 empty] | 19.84 |  |  |  |  | 1.06
2019 |  |  |  | 8734.82 |  |  | 7205 |  |  |  | 1310 | [10 empty] | 81.66 |  |  |  | 83.43 | [5 empty] | 76.12 |  |  | 82.25 |  |  |  | 1.22 |  | 6.40 | [8 empty] | 10.17 |  |  |  |  | 1.77
2020 |  |  |  | 9160.17 |  |  | 8144 |  |  |  | 1310 | [10 empty] | 92.19 |  |  |  | 94.18 | [5 empty] | 79.60 |  |  | 92.71 |  |  |  | 5.75 |  | 5.74 | [8 empty] | 0.08 |  |  |  |  | 1.99
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1994 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 278
B. |  | Refuelling without maintenance | [35 empty] | 131
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 746 |  |  |  | 1
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 5
E. |  | Testing of plant systems or components | [35 empty] | 33
H. |  | Nuclear regulatory requirements | [39 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 16
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 12
O. |  | Load dispatching, prioritization | [51 empty] | 3
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 24 | [11 empty] | 4
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 3 | [11 empty] | 2
Z. |  | Other | [39 empty] | 9 | [11 empty] | 16
Subtotal | [37 empty] | 915 |  |  |  | 332 | [11 empty] | 38
Total | [22 empty] | 0 | [14 empty] | 1285
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1994 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 36
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 7
16. |  |  | Steam generation systems | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 85
41. |  |  | Main Generator Systems | [34 empty] | 92
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 273

## GRAVELINES-1
2020 Operating Experience
FR-20 | [8 empty] | GRAVELINES-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-02-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-03-13
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-11-25
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5590.4 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 8.97 %
Energy Availability Factor (EAF) | [18 empty] | : | 70.85 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 14.15 %
Unit Capability Factor (UCF) | [18 empty] | : | 72.28 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.58 %
Load Factor (LF) | [18 empty] | : | 69.94 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.42 %
Operating Factor (OF) | [18 empty] | : | 76.66 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2050 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 573.49 | 619.52 |  |  |  | 578.34 |  | 627.85 | [8 empty] | 613.06 |  |  | 339.73 | [6 empty] | 617.14 |  | 412.71 |  |  |  | 0.00 |  |  | 0.00 |  |  | 539.94 | [9 empty] | 668.62 |  |  | 5590.40
EAF [%] |  |  |  |  | 85.17 | 99.90 |  |  |  | 88.52 |  | 97.40 | [8 empty] | 91.54 |  |  | 51.99 | [6 empty] | 91.15 |  | 60.96 |  |  |  | 0.00 |  |  | 0.01 |  |  | 84.19 | [9 empty] | 99.80 |  |  | 70.85
UCF [%] |  |  |  |  | 99.92 | 99.90 |  |  |  | 88.52 |  | 97.40 | [8 empty] | 92.02 |  |  | 52.07 | [6 empty] | 91.15 |  | 60.96 |  |  |  | 0.00 |  |  | 1.48 |  |  | 84.20 | [9 empty] | 99.80 |  |  | 72.28
LF [%] |  |  |  |  | 84.71 | 97.81 |  |  |  | 85.54 |  | 95.83 | [8 empty] | 90.55 |  |  | 51.85 | [6 empty] | 91.15 |  | 60.96 |  |  |  | 0.00 |  |  | 0.00 |  |  | 82.41 | [9 empty] | 98.76 |  |  | 69.94
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 96.37 |  | 100.00 | [8 empty] | 100.00 |  |  | 60.42 | [6 empty] | 100.00 |  | 67.88 |  |  |  | 0.00 |  |  | 0.00 |  |  | 95.28 | [9 empty] | 100.00 |  |  | 76.66
FLR [%] |  |  |  |  | 0.06 | 0.10 |  |  |  | 11.30 |  | 2.56 | [8 empty] | 7.92 |  |  | 47.93 | [6 empty] | 8.85 |  | 9.95 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.22 | [9 empty] | 0.19 |  |  | 8.97
UCL [%] |  |  |  |  | 0.06 | 0.10 |  |  |  | 11.28 |  | 2.55 | [8 empty] | 7.92 |  |  | 47.93 | [6 empty] | 8.85 |  | 6.74 |  |  |  | 0.00 |  |  | 79.33 |  |  | 3.75 | [9 empty] | 0.19 |  |  | 14.15
PUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.20 |  | 0.05 | [8 empty] | 0.06 |  |  | 0.00 | [6 empty] | 0.00 |  | 32.30 |  |  |  | 100.00 |  |  | 19.19 |  |  | 12.06 | [9 empty] | 0.02 |  |  | 13.58
XUF [%] |  |  |  |  | 14.75 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.49 |  |  | 0.08 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 1.47 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 1.42
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 224753.61 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.78 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.47 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.17 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.46 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 69.88 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.91 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.18 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 1466.00 |  |  | 2477 |  |  |  | 918 | [10 empty] | 72.30 |  |  |  | 72.30 | [5 empty] | 72.03 |  |  | 74.06 |  |  |  | 21.78 |  | 20.13 | [8 empty] | 7.57 |  |  |  |  | 0.00
1981 |  |  |  | 5001.80 |  |  | 5785 |  |  |  | 920 | [10 empty] | 63.25 |  |  |  | 63.25 | [5 empty] | 62.06 |  |  | 66.04 |  |  |  | 11.18 |  | 7.96 | [8 empty] | 28.79 |  |  |  |  | 0.00
1982 |  |  |  | 2987.50 |  |  | 3602 |  |  |  | 910 | [10 empty] | 38.24 |  |  |  | 38.24 | [5 empty] | 37.48 |  |  | 41.12 |  |  |  | 59.89 |  | 57.10 | [8 empty] | 4.65 |  |  |  |  | 0.00
1983 |  |  |  | 5537.00 |  |  | 6237 |  |  |  | 910 | [10 empty] | 69.92 |  |  |  | 69.92 | [5 empty] | 69.46 |  |  | 71.20 |  |  |  | 4.66 |  | 3.42 | [8 empty] | 26.66 |  |  |  |  | 0.00
1984 |  |  |  | 6617.00 |  |  | 7654 |  |  |  | 910 | [10 empty] | 86.22 |  |  |  | 86.22 | [5 empty] | 82.78 |  |  | 87.14 |  |  |  | 5.90 |  | 5.40 | [8 empty] | 8.38 |  |  |  |  | 0.00
1985 |  |  |  | 6211.70 |  |  | 7218 |  |  |  | 910 | [10 empty] | 80.31 |  |  |  | 81.27 | [5 empty] | 77.92 |  |  | 82.40 |  |  |  | 3.98 |  | 3.37 | [8 empty] | 15.36 |  |  |  |  | 0.96
1986 |  |  |  | 5725.50 |  |  | 6508 |  |  |  | 910 | [10 empty] | 73.40 |  |  |  | 74.80 | [5 empty] | 71.82 |  |  | 74.29 |  |  |  | 10.69 |  | 8.95 | [8 empty] | 16.24 |  |  |  |  | 1.40
1987 |  |  |  | 4650.10 |  |  | 5895 |  |  |  | 910 | [10 empty] | 89.01 |  |  |  | 89.34 | [5 empty] | 58.33 |  |  | 67.29 |  |  |  | 4.67 |  | 4.38 | [8 empty] | 6.28 |  |  |  |  | 0.33
1988 |  |  |  | 4289.00 |  |  | 5306 |  |  |  | 910 | [10 empty] | 56.96 |  |  |  | 57.63 | [5 empty] | 53.66 |  |  | 60.41 |  |  |  | 34.00 |  | 29.69 | [8 empty] | 12.69 |  |  |  |  | 0.66
1989 |  |  |  | 5109.64 |  |  | 6224 |  |  |  | 910 | [10 empty] | 67.66 |  |  |  | 67.68 | [5 empty] | 64.10 |  |  | 71.05 |  |  |  | 22.39 |  | 19.52 | [8 empty] | 12.80 |  |  |  |  | 0.02
1990 |  |  |  | 4463.57 |  |  | 5425 |  |  |  | 910 | [10 empty] | 59.17 |  |  |  | 61.27 | [5 empty] | 55.99 |  |  | 61.93 |  |  |  | 14.31 |  | 10.23 | [8 empty] | 28.50 |  |  |  |  | 2.10
1991 |  |  |  | 5675.04 |  |  | 6619 |  |  |  | 910 | [10 empty] | 73.35 |  |  |  | 74.00 | [5 empty] | 71.19 |  |  | 75.56 |  |  |  | 14.90 |  | 12.96 | [8 empty] | 13.05 |  |  |  |  | 0.64
1992 |  |  |  | 5834.68 |  |  | 7250 |  |  |  | 910 | [10 empty] | 80.65 |  |  |  | 84.00 | [5 empty] | 72.99 |  |  | 82.54 |  |  |  | 3.31 |  | 2.88 | [8 empty] | 13.12 |  |  |  |  | 3.35
1993 |  |  |  | 5866.85 |  |  | 7794 |  |  |  | 910 | [10 empty] | 80.54 |  |  |  | 93.84 | [5 empty] | 73.60 |  |  | 88.97 |  |  |  | 2.71 |  | 2.62 | [8 empty] | 3.54 |  |  |  |  | 13.30
1994 |  |  |  | 4657.72 |  |  | 5729 |  |  |  | 910 | [10 empty] | 67.67 |  |  |  | 68.60 | [5 empty] | 58.43 |  |  | 65.40 |  |  |  | 3.77 |  | 2.69 | [8 empty] | 28.71 |  |  |  |  | 0.93
1995 |  |  |  | 6123.14 |  |  | 7461 |  |  |  | 910 | [10 empty] | 82.76 |  |  |  | 83.75 | [5 empty] | 76.81 |  |  | 85.17 |  |  |  | 6.18 |  | 5.52 | [8 empty] | 10.73 |  |  |  |  | 0.99
1996 |  |  |  | 6089.15 |  |  | 7357 |  |  |  | 910 | [10 empty] | 80.34 |  |  |  | 83.55 | [5 empty] | 76.18 |  |  | 83.75 |  |  |  | 4.70 |  | 4.12 | [8 empty] | 12.33 |  |  |  |  | 3.21
1997 |  |  |  | 5860.44 |  |  | 7236 |  |  |  | 910 | [10 empty] | 81.72 |  |  |  | 82.89 | [5 empty] | 73.52 |  |  | 82.60 |  |  |  | 5.61 |  | 4.93 | [8 empty] | 12.18 |  |  |  |  | 1.17
1998 |  |  |  | 6321.38 |  |  | 7622 |  |  |  | 910 | [10 empty] | 83.74 |  |  |  | 87.05 | [5 empty] | 79.30 |  |  | 87.01 |  |  |  | 3.19 |  | 2.87 | [8 empty] | 10.07 |  |  |  |  | 3.32
1999 |  |  |  | 5841.29 |  |  | 7116 |  |  |  | 910 | [10 empty] | 78.55 |  |  |  | 80.27 | [5 empty] | 73.28 |  |  | 81.23 |  |  |  | 2.16 |  | 1.78 | [8 empty] | 17.95 |  |  |  |  | 1.72
2000 |  |  |  | 6531.94 |  |  | 7705 |  |  |  | 910 | [10 empty] | 88.11 |  |  |  | 88.20 | [5 empty] | 81.72 |  |  | 87.72 |  |  |  | 0.99 |  | 0.88 | [8 empty] | 10.91 |  |  |  |  | 0.09
2001 |  |  |  | 5289.37 |  |  | 6034 |  |  |  | 910 | [10 empty] | 66.69 |  |  |  | 67.59 | [5 empty] | 66.35 |  |  | 68.88 |  |  |  | 7.47 |  | 5.46 | [8 empty] | 26.96 |  |  |  |  | 0.90
2002 |  |  |  | 5769.34 |  |  | 7057 |  |  |  | 910 | [10 empty] | 86.32 |  |  |  | 88.64 | [5 empty] | 72.37 |  |  | 80.56 |  |  |  | 0.63 |  | 0.56 | [8 empty] | 10.80 |  |  |  |  | 2.32
2003 |  |  |  | 5919.51 |  |  | 7420 |  |  |  | 910 | [10 empty] | 85.05 |  |  |  | 85.70 | [5 empty] | 74.26 |  |  | 84.70 |  |  |  | 0.99 |  | 0.85 | [8 empty] | 13.44 |  |  |  |  | 0.65
2004 |  |  |  | 6213.89 |  |  | 7664 |  |  |  | 910 | [10 empty] | 86.23 |  |  |  | 86.35 | [5 empty] | 77.74 |  |  | 87.25 |  |  |  | 5.06 |  | 4.60 | [8 empty] | 9.04 |  |  |  |  | 0.13
2005 |  |  |  | 6188.68 |  |  | 7400 |  |  |  | 910 | [10 empty] | 82.51 |  |  |  | 84.55 | [5 empty] | 77.63 |  |  | 84.47 |  |  |  | 1.18 |  | 2.46 | [8 empty] | 12.99 |  |  |  |  | 2.04
2006 |  |  |  | 6244.37 |  |  | 7567 |  |  |  | 910 | [10 empty] | 82.81 |  |  |  | 84.92 | [5 empty] | 78.33 |  |  | 86.38 |  |  |  | 2.54 |  | 7.15 | [8 empty] | 7.93 |  |  |  |  | 2.11
2007 |  |  |  | 6168.23 |  |  | 7312 |  |  |  | 910 | [10 empty] | 80.11 |  |  |  | 82.37 | [5 empty] | 77.38 |  |  | 83.47 |  |  |  | 1.38 |  | 4.00 | [8 empty] | 13.64 |  |  |  |  | 2.26
2008 |  |  |  | 6716.74 |  |  | 8146 |  |  |  | 910 | [10 empty] | 89.12 |  |  |  | 91.78 | [5 empty] | 84.03 |  |  | 92.74 |  |  |  | 0.35 |  | 1.30 | [8 empty] | 6.92 |  |  |  |  | 2.66
2009 |  |  |  | 5348.22 |  |  | 6527 |  |  |  | 910 | [10 empty] | 70.03 |  |  |  | 72.56 | [5 empty] | 67.09 |  |  | 74.51 |  |  |  | 0.53 |  | 13.64 | [8 empty] | 13.80 |  |  |  |  | 2.54
2010 |  |  |  | 6334.91 |  |  | 7348 |  |  |  | 910 | [10 empty] | 82.04 |  |  |  | 82.67 | [5 empty] | 79.47 |  |  | 83.88 |  |  |  | 9.70 |  | 10.14 | [8 empty] | 7.19 |  |  |  |  | 0.63
2011 |  |  |  | 4173.88 |  |  | 4827 |  |  |  | 910 | [10 empty] | 53.96 |  |  |  | 54.47 | [5 empty] | 52.36 |  |  | 55.10 |  |  |  | 4.82 |  | 21.39 | [8 empty] | 24.15 |  |  |  |  | 0.50
2012 |  |  |  | 4856.13 |  |  | 5711 |  |  |  | 910 | [10 empty] | 61.43 |  |  |  | 62.36 | [5 empty] | 60.75 |  |  | 65.02 |  |  |  | 18.32 |  | 35.99 | [8 empty] | 1.65 |  |  |  |  | 0.93
2013 |  |  |  | 5462.13 |  |  | 6283 |  |  |  | 910 | [10 empty] | 68.89 |  |  |  | 75.07 | [5 empty] | 68.52 |  |  | 71.72 |  |  |  | 5.15 |  | 9.73 | [8 empty] | 15.20 |  |  |  |  | 6.18
2014 |  |  |  | 6111.90 |  |  | 7416 |  |  |  | 910 | [10 empty] | 82.59 |  |  |  | 83.30 | [5 empty] | 76.67 |  |  | 84.66 |  |  |  | 3.26 |  | 2.81 | [8 empty] | 13.89 |  |  |  |  | 0.71
2015 |  |  |  | 5575.19 |  |  | 6554 |  |  |  | 910 | [10 empty] | 71.34 |  |  |  | 75.34 | [5 empty] | 69.94 |  |  | 74.82 |  |  |  | 3.19 |  | 2.93 | [8 empty] | 21.73 |  |  |  |  | 3.99
2016 |  |  |  | 4673.39 |  |  | 5763 |  |  |  | 910 | [10 empty] | 59.92 |  |  |  | 70.41 | [5 empty] | 58.47 |  |  | 65.61 |  |  |  | 2.00 |  | 2.73 | [8 empty] | 26.86 |  |  |  |  | 10.49
2017 |  |  |  | 5397.15 |  |  | 6249 |  |  |  | 910 | [10 empty] | 68.65 |  |  |  | 68.97 | [5 empty] | 67.70 |  |  | 71.34 |  |  |  | 1.77 |  | 13.22 | [8 empty] | 17.81 |  |  |  |  | 0.32
2018 |  |  |  | 6553.27 |  |  | 7548 |  |  |  | 910 | [10 empty] | 84.31 |  |  |  | 84.97 | [5 empty] | 82.21 |  |  | 86.16 |  |  |  | 2.50 |  | 5.72 | [8 empty] | 9.31 |  |  |  |  | 0.65
2019 |  |  |  | 5041.04 |  |  | 5827 |  |  |  | 910 | [10 empty] | 64.56 |  |  |  | 65.44 | [5 empty] | 63.24 |  |  | 66.52 |  |  |  | 2.62 |  | 15.61 | [8 empty] | 18.95 |  |  |  |  | 0.87
2020 |  |  |  | 5590.40 |  |  | 6734 |  |  |  | 910 | [10 empty] | 70.85 |  |  |  | 72.28 | [5 empty] | 69.94 |  |  | 76.66 |  |  |  | 8.97 |  | 14.15 | [8 empty] | 13.58 |  |  |  |  | 1.42
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1980 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 609
B. |  | Refuelling without maintenance | [35 empty] | 140
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1027 |  |  |  | 12
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 19 |  |  |  | 3
E. |  | Testing of plant systems or components | [35 empty] | 11 |  |  |  | 4
H. |  | Nuclear regulatory requirements | [39 empty] | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 8
L. |  | Human factor related | [39 empty] | 13
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 0 | [11 empty] | 24
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 16
Z. |  | Other | [39 empty] | 36 | [11 empty] | 3
Subtotal | [37 empty] | 1197 |  |  |  | 682 | [11 empty] | 53
Total | [22 empty] | 0 | [14 empty] | 1932
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1980 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 197
12. |  |  | Reactor I&C Systems | [34 empty] | 10
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 16
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 73
16. |  |  | Steam generation systems | [34 empty] | 71
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 35
32. |  |  | Feedwater and Main Steam System | [34 empty] | 46
33. |  |  | Circulating Water System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 104
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 10
42. |  |  | Electrical Power Supply Systems | [34 empty] | 26
Total | [37 empty] | 604

## GRAVELINES-2
2020 Operating Experience
FR-21 | [8 empty] | GRAVELINES-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-03-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-08-26
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-12-01
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5847.85 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 9.1 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.3 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 12.86 %
Unit Capability Factor (UCF) | [18 empty] | : | 76.38 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.76 %
Load Factor (LF) | [18 empty] | : | 73.16 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.09 %
Operating Factor (OF) | [18 empty] | : | 75.89 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2118 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 672.53 | 546.53 |  |  |  | 236.27 |  | 0.00 | [8 empty] | 169.16 |  |  | 598.19 | [6 empty] | 428.18 |  | 658.51 |  |  |  | 641.06 |  |  | 672.59 |  |  | 654.30 | [9 empty] | 570.54 |  |  | 5847.85
EAF [%] |  |  |  |  | 99.47 | 97.88 |  |  |  | 34.95 |  | 0.01 | [8 empty] | 25.02 |  |  | 91.39 | [6 empty] | 65.47 |  | 97.38 |  |  |  | 97.96 |  |  | 99.34 |  |  | 99.90 | [9 empty] | 83.98 |  |  | 74.30
UCF [%] |  |  |  |  | 99.47 | 97.95 |  |  |  | 35.73 |  | 13.33 | [8 empty] | 31.06 |  |  | 92.07 | [6 empty] | 66.33 |  | 99.20 |  |  |  | 99.14 |  |  | 99.67 |  |  | 99.94 | [9 empty] | 83.98 |  |  | 76.38
LF [%] |  |  |  |  | 99.33 | 86.29 |  |  |  | 34.94 |  | 0.00 | [8 empty] | 24.99 |  |  | 91.30 | [6 empty] | 63.24 |  | 97.26 |  |  |  | 97.84 |  |  | 99.21 |  |  | 99.86 | [9 empty] | 84.27 |  |  | 73.16
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 35.80 |  | 0.00 | [8 empty] | 32.39 |  |  | 93.47 | [6 empty] | 65.05 |  | 100.00 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 85.22 |  |  | 75.89
FLR [%] |  |  |  |  | 0.40 | 2.05 |  |  |  | 44.70 |  | 0.00 | [8 empty] | 0.24 |  |  | 7.85 | [6 empty] | 33.59 |  | 0.78 |  |  |  | 0.86 |  |  | 0.20 |  |  | 0.06 | [9 empty] | 16.00 |  |  | 9.10
UCL [%] |  |  |  |  | 0.40 | 2.05 |  |  |  | 28.88 |  | 0.00 | [8 empty] | 61.69 |  |  | 7.84 | [6 empty] | 33.55 |  | 0.78 |  |  |  | 0.86 |  |  | 0.20 |  |  | 0.06 | [9 empty] | 15.99 |  |  | 12.86
PUF [%] |  |  |  |  | 0.14 | 0.00 |  |  |  | 35.40 |  | 86.67 | [8 empty] | 7.26 |  |  | 0.09 | [6 empty] | 0.12 |  | 0.02 |  |  |  | 0.00 |  |  | 0.13 |  |  | 0.00 | [9 empty] | 0.03 |  |  | 10.76
XUF [%] |  |  |  |  | 0.00 | 0.06 |  |  |  | 0.78 |  | 13.33 | [8 empty] | 6.04 |  |  | 0.68 | [6 empty] | 0.86 |  | 1.82 |  |  |  | 1.18 |  |  | 0.33 |  |  | 0.05 | [9 empty] | 0.00 |  |  | 2.09
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 233370.78 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.65 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.24 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.45 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.4 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.75 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.21 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 1282.00 |  |  | 1916 |  |  |  | 914 | [10 empty] | 74.70 |  |  |  | 74.70 | [5 empty] | 75.24 |  |  | 76.75 |  |  |  | 25.30 |  | 25.30 | [8 empty] | 0.00 |  |  |  |  | 0.00
1981 |  |  |  | 5949.20 |  |  | 7276 |  |  |  | 920 | [10 empty] | 81.21 |  |  |  | 81.21 | [5 empty] | 73.82 |  |  | 83.06 |  |  |  | 2.26 |  | 1.88 | [8 empty] | 16.91 |  |  |  |  | 0.00
1982 |  |  |  | 2118.50 |  |  | 2732 |  |  |  | 910 | [10 empty] | 29.21 |  |  |  | 29.21 | [5 empty] | 26.58 |  |  | 31.19 |  |  |  | 37.78 |  | 17.73 | [8 empty] | 53.06 |  |  |  |  | 0.00
1983 |  |  |  | 6130.00 |  |  | 6917 |  |  |  | 910 | [10 empty] | 77.92 |  |  |  | 77.92 | [5 empty] | 76.90 |  |  | 78.96 |  |  |  | 2.89 |  | 2.32 | [8 empty] | 19.76 |  |  |  |  | 0.00
1984 |  |  |  | 5749.00 |  |  | 6751 |  |  |  | 910 | [10 empty] | 82.03 |  |  |  | 82.03 | [5 empty] | 71.92 |  |  | 76.86 |  |  |  | 5.46 |  | 4.74 | [8 empty] | 13.23 |  |  |  |  | 0.00
1985 |  |  |  | 6829.70 |  |  | 7950 |  |  |  | 910 | [10 empty] | 89.65 |  |  |  | 90.22 | [5 empty] | 85.68 |  |  | 90.75 |  |  |  | 3.69 |  | 3.45 | [8 empty] | 6.33 |  |  |  |  | 0.56
1986 |  |  |  | 6422.00 |  |  | 7956 |  |  |  | 910 | [10 empty] | 96.41 |  |  |  | 96.56 | [5 empty] | 80.56 |  |  | 90.82 |  |  |  | 3.44 |  | 3.44 | [8 empty] | 0.00 |  |  |  |  | 0.14
1987 |  |  |  | 5357.90 |  |  | 6807 |  |  |  | 910 | [10 empty] | 75.18 |  |  |  | 77.39 | [5 empty] | 67.21 |  |  | 77.71 |  |  |  | 7.43 |  | 6.21 | [8 empty] | 16.40 |  |  |  |  | 2.22
1988 |  |  |  | 5577.00 |  |  | 7227 |  |  |  | 910 | [10 empty] | 77.16 |  |  |  | 81.27 | [5 empty] | 69.77 |  |  | 82.27 |  |  |  | 7.78 |  | 6.86 | [8 empty] | 11.87 |  |  |  |  | 4.12
1989 |  |  |  | 6412.93 |  |  | 7460 |  |  |  | 910 | [10 empty] | 83.57 |  |  |  | 84.61 | [5 empty] | 80.45 |  |  | 85.16 |  |  |  | 3.29 |  | 2.88 | [8 empty] | 12.51 |  |  |  |  | 1.04
1990 |  |  |  | 6143.08 |  |  | 7164 |  |  |  | 910 | [10 empty] | 79.64 |  |  |  | 80.59 | [5 empty] | 77.06 |  |  | 81.78 |  |  |  | 5.17 |  | 4.39 | [8 empty] | 15.01 |  |  |  |  | 0.96
1991 |  |  |  | 4915.91 |  |  | 5648 |  |  |  | 910 | [10 empty] | 62.98 |  |  |  | 63.55 | [5 empty] | 61.67 |  |  | 64.47 |  |  |  | 9.87 |  | 6.96 | [8 empty] | 29.49 |  |  |  |  | 0.58
1992 |  |  |  | 6124.15 |  |  | 7149 |  |  |  | 910 | [10 empty] | 78.18 |  |  |  | 80.61 | [5 empty] | 76.61 |  |  | 81.39 |  |  |  | 1.08 |  | 0.88 | [8 empty] | 18.51 |  |  |  |  | 2.43
1993 |  |  |  | 6219.87 |  |  | 7297 |  |  |  | 910 | [10 empty] | 79.28 |  |  |  | 82.31 | [5 empty] | 78.03 |  |  | 83.30 |  |  |  | 5.01 |  | 4.34 | [8 empty] | 13.34 |  |  |  |  | 3.03
1994 |  |  |  | 6293.68 |  |  | 7638 |  |  |  | 910 | [10 empty] | 82.69 |  |  |  | 86.25 | [5 empty] | 78.95 |  |  | 87.19 |  |  |  | 2.15 |  | 1.90 | [8 empty] | 11.86 |  |  |  |  | 3.56
1995 |  |  |  | 5599.66 |  |  | 6735 |  |  |  | 910 | [10 empty] | 74.61 |  |  |  | 75.59 | [5 empty] | 70.25 |  |  | 76.88 |  |  |  | 14.78 |  | 13.11 | [8 empty] | 11.30 |  |  |  |  | 0.98
1996 |  |  |  | 5235.92 |  |  | 6361 |  |  |  | 910 | [10 empty] | 69.71 |  |  |  | 70.72 | [5 empty] | 65.50 |  |  | 72.42 |  |  |  | 1.04 |  | 0.74 | [8 empty] | 28.54 |  |  |  |  | 1.01
1997 |  |  |  | 6641.23 |  |  | 8006 |  |  |  | 910 | [10 empty] | 97.85 |  |  |  | 97.96 | [5 empty] | 83.31 |  |  | 91.39 |  |  |  | 2.03 |  | 2.03 | [8 empty] | 0.01 |  |  |  |  | 0.11
1998 |  |  |  | 5531.44 |  |  | 6896 |  |  |  | 910 | [10 empty] | 82.10 |  |  |  | 82.22 | [5 empty] | 69.39 |  |  | 78.72 |  |  |  | 2.16 |  | 1.81 | [8 empty] | 15.97 |  |  |  |  | 0.11
1999 |  |  |  | 6394.43 |  |  | 7705 |  |  |  | 910 | [10 empty] | 85.34 |  |  |  | 87.76 | [5 empty] | 80.22 |  |  | 87.96 |  |  |  | 1.37 |  | 1.22 | [8 empty] | 11.02 |  |  |  |  | 2.42
2000 |  |  |  | 5582.71 |  |  | 6952 |  |  |  | 910 | [10 empty] | 77.30 |  |  |  | 80.54 | [5 empty] | 69.84 |  |  | 79.14 |  |  |  | 2.81 |  | 2.33 | [8 empty] | 17.13 |  |  |  |  | 3.24
2001 |  |  |  | 5984.52 |  |  | 7601 |  |  |  | 910 | [10 empty] | 85.00 |  |  |  | 85.49 | [5 empty] | 75.07 |  |  | 86.77 |  |  |  | 3.62 |  | 3.21 | [8 empty] | 11.30 |  |  |  |  | 0.49
2002 |  |  |  | 5254.30 |  |  | 6658 |  |  |  | 910 | [10 empty] | 72.30 |  |  |  | 74.31 | [5 empty] | 65.91 |  |  | 76.00 |  |  |  | 0.34 |  | 0.25 | [8 empty] | 25.44 |  |  |  |  | 2.01
2003 |  |  |  | 6553.92 |  |  | 7986 |  |  |  | 910 | [10 empty] | 89.20 |  |  |  | 89.61 | [5 empty] | 82.22 |  |  | 91.16 |  |  |  | 1.65 |  | 1.50 | [8 empty] | 8.89 |  |  |  |  | 0.41
2004 |  |  |  | 6009.04 |  |  | 7262 |  |  |  | 910 | [10 empty] | 80.44 |  |  |  | 81.80 | [5 empty] | 75.17 |  |  | 82.67 |  |  |  | 6.42 |  | 5.61 | [8 empty] | 12.59 |  |  |  |  | 1.36
2005 |  |  |  | 6622.59 |  |  | 7880 |  |  |  | 910 | [10 empty] | 86.64 |  |  |  | 88.22 | [5 empty] | 83.07 |  |  | 89.94 |  |  |  | 2.62 |  | 2.53 | [8 empty] | 9.26 |  |  |  |  | 1.58
2006 |  |  |  | 6222.36 |  |  | 7369 |  |  |  | 910 | [10 empty] | 79.61 |  |  |  | 81.73 | [5 empty] | 78.06 |  |  | 84.12 |  |  |  | 3.93 |  | 5.18 | [8 empty] | 13.09 |  |  |  |  | 2.13
2007 |  |  |  | 6522.56 |  |  | 7796 |  |  |  | 910 | [10 empty] | 86.44 |  |  |  | 87.98 | [5 empty] | 81.82 |  |  | 89.00 |  |  |  | 2.20 |  | 4.21 | [8 empty] | 7.81 |  |  |  |  | 1.54
2008 |  |  |  | 6124.09 |  |  | 7271 |  |  |  | 910 | [10 empty] | 78.32 |  |  |  | 80.70 | [5 empty] | 76.61 |  |  | 82.78 |  |  |  | 2.30 |  | 6.57 | [8 empty] | 12.73 |  |  |  |  | 2.38
2009 |  |  |  | 6537.36 |  |  | 7696 |  |  |  | 910 | [10 empty] | 84.50 |  |  |  | 86.53 | [5 empty] | 82.01 |  |  | 87.85 |  |  |  | 2.00 |  | 5.28 | [8 empty] | 8.20 |  |  |  |  | 2.03
2010 |  |  |  | 5223.13 |  |  | 6149 |  |  |  | 910 | [10 empty] | 67.71 |  |  |  | 68.74 | [5 empty] | 65.52 |  |  | 70.19 |  |  |  | 11.95 |  | 17.41 | [8 empty] | 13.85 |  |  |  |  | 1.03
2011 |  |  |  | 6861.91 |  |  | 7723 |  |  |  | 910 | [10 empty] | 86.35 |  |  |  | 87.50 | [5 empty] | 86.08 |  |  | 88.16 |  |  |  | 0.30 |  | 4.31 | [8 empty] | 8.18 |  |  |  |  | 1.15
2012 |  |  |  | 5832.88 |  |  | 6776 |  |  |  | 910 | [10 empty] | 73.13 |  |  |  | 73.81 | [5 empty] | 72.97 |  |  | 77.14 |  |  |  | 8.56 |  | 11.94 | [8 empty] | 14.25 |  |  |  |  | 0.68
2013 |  |  |  | 3895.35 |  |  | 4421 |  |  |  | 910 | [10 empty] | 49.04 |  |  |  | 51.94 | [5 empty] | 48.87 |  |  | 50.47 |  |  |  | 3.09 |  | 25.15 | [8 empty] | 22.91 |  |  |  |  | 2.90
2014 |  |  |  | 6274.40 |  |  | 7318 |  |  |  | 910 | [10 empty] | 83.17 |  |  |  | 83.47 | [5 empty] | 78.71 |  |  | 83.54 |  |  |  | 4.72 |  | 7.14 | [8 empty] | 9.40 |  |  |  |  | 0.30
2015 |  |  |  | 5211.80 |  |  | 5969 |  |  |  | 910 | [10 empty] | 66.65 |  |  |  | 69.37 | [5 empty] | 65.38 |  |  | 68.14 |  |  |  | 1.07 |  | 8.57 | [8 empty] | 22.06 |  |  |  |  | 2.72
2016 |  |  |  | 5282.11 |  |  | 6349 |  |  |  | 910 | [10 empty] | 68.63 |  |  |  | 83.43 | [5 empty] | 66.08 |  |  | 72.28 |  |  |  | 1.99 |  | 7.89 | [8 empty] | 8.68 |  |  |  |  | 14.80
2017 |  |  |  | 5611.13 |  |  | 6531 |  |  |  | 910 | [10 empty] | 72.19 |  |  |  | 74.06 | [5 empty] | 70.39 |  |  | 74.55 |  |  |  | 1.30 |  | 9.61 | [8 empty] | 16.33 |  |  |  |  | 1.87
2018 |  |  |  | 6258.08 |  |  | 7767 |  |  |  | 910 | [10 empty] | 81.64 |  |  |  | 99.35 | [5 empty] | 78.50 |  |  | 88.66 |  |  |  | 0.32 |  | 0.32 | [8 empty] | 0.33 |  |  |  |  | 17.71
2019 |  |  |  | 4834.97 |  |  | 5890 |  |  |  | 910 | [10 empty] | 62.58 |  |  |  | 65.56 | [5 empty] | 60.65 |  |  | 67.24 |  |  |  | 11.33 |  | 15.73 | [8 empty] | 18.71 |  |  |  |  | 2.98
2020 |  |  |  | 5847.85 |  |  | 6666 |  |  |  | 910 | [10 empty] | 74.30 |  |  |  | 76.38 | [5 empty] | 73.16 |  |  | 75.89 |  |  |  | 9.10 |  | 12.86 | [8 empty] | 10.76 |  |  |  |  | 2.09
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1980 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 329
B. |  | Refuelling without maintenance | [35 empty] | 102
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 970 |  |  |  | 32
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 55
E. |  | Testing of plant systems or components | [35 empty] | 20
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 8
L. |  | Human factor related | [39 empty] | 11
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 40
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 25
Z. |  | Other | [35 empty] | 15 |  |  |  | 45 | [11 empty] | 41
Subtotal | [37 empty] | 1162 |  |  |  | 418 | [11 empty] | 119
Total | [22 empty] | 0 | [14 empty] | 1699
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1980 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 11
12. |  |  | Reactor I&C Systems | [34 empty] | 21
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 18
16. |  |  | Steam generation systems | [34 empty] | 45
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 20
32. |  |  | Feedwater and Main Steam System | [34 empty] | 20
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 139
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 28
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [37 empty] | 356

## GRAVELINES-3
2020 Operating Experience
FR-27 | [8 empty] | GRAVELINES-3 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-12-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-12-12
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-06-01
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.5
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 45 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4907.62 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 5.88 %
Energy Availability Factor (EAF) | [18 empty] | : | 61.5 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 12.3 %
Unit Capability Factor (UCF) | [18 empty] | : | 67.15 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.54 %
Load Factor (LF) | [18 empty] | : | 61.4 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 5.66 %
Operating Factor (OF) | [18 empty] | : | 66.95 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2903 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 489.46 | 398.28 |  |  |  | 636.52 |  | 521.57 | [8 empty] | 676.91 |  |  | 652.07 | [6 empty] | 665.72 |  | 643.84 |  |  |  | 223.26 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4907.62
EAF [%] |  |  |  |  | 72.28 | 63.76 |  |  |  | 93.79 |  | 80.33 | [8 empty] | 99.89 |  |  | 99.54 | [6 empty] | 98.34 |  | 95.11 |  |  |  | 34.08 |  |  | 0.00 |  |  | 0.10 | [9 empty] | 0.01 |  |  | 61.50
UCF [%] |  |  |  |  | 99.55 | 81.03 |  |  |  | 93.79 |  | 80.33 | [8 empty] | 99.89 |  |  | 100.00 | [6 empty] | 99.71 |  | 96.12 |  |  |  | 34.08 |  |  | 0.00 |  |  | 14.66 | [9 empty] | 6.46 |  |  | 67.15
LF [%] |  |  |  |  | 72.29 | 62.88 |  |  |  | 94.14 |  | 79.61 | [8 empty] | 99.98 |  |  | 99.52 | [6 empty] | 98.33 |  | 95.10 |  |  |  | 34.07 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 61.40
OF [%] |  |  |  |  | 100.00 | 78.45 |  |  |  | 100.00 |  | 87.78 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 36.67 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 66.95
FLR [%] |  |  |  |  | 0.17 | 18.97 |  |  |  | 6.21 |  | 19.67 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.07 |  | 3.88 |  |  |  | 6.84 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.88
UCL [%] |  |  |  |  | 0.17 | 18.97 |  |  |  | 6.21 |  | 19.67 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.07 |  | 3.88 |  |  |  | 2.50 |  |  | 0.00 |  |  | 2.25 | [9 empty] | 93.54 |  |  | 12.30
PUF [%] |  |  |  |  | 0.28 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.11 |  |  | 0.00 | [6 empty] | 0.23 |  | 0.00 |  |  |  | 63.42 |  |  | 100.00 |  |  | 83.10 | [9 empty] | 0.00 |  |  | 20.54
XUF [%] |  |  |  |  | 27.27 | 17.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.46 | [6 empty] | 1.36 |  | 1.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 14.56 | [9 empty] | 6.45 |  |  | 5.66
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 233508.97 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.55 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.78 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.89 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.47 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.49 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.92 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 5170.10 |  |  | 6405 |  |  |  | 920 | [10 empty] | 84.42 |  |  |  | 84.42 | [5 empty] | 78.30 |  |  | 86.88 |  |  |  | 14.93 |  | 14.82 | [8 empty] | 0.76 |  |  |  |  | 0.00
1982 |  |  |  | 3445.00 |  |  | 4260 |  |  |  | 910 | [10 empty] | 47.62 |  |  |  | 47.62 | [5 empty] | 43.22 |  |  | 48.63 |  |  |  | 27.74 |  | 18.28 | [8 empty] | 34.10 |  |  |  |  | 0.00
1983 |  |  |  | 6006.00 |  |  | 7194 |  |  |  | 910 | [10 empty] | 78.49 |  |  |  | 78.58 | [5 empty] | 75.34 |  |  | 82.12 |  |  |  | 10.51 |  | 9.23 | [8 empty] | 12.19 |  |  |  |  | 0.08
1984 |  |  |  | 6746.00 |  |  | 7505 |  |  |  | 910 | [10 empty] | 83.87 |  |  |  | 83.87 | [5 empty] | 84.39 |  |  | 85.44 |  |  |  | 5.25 |  | 4.65 | [8 empty] | 11.48 |  |  |  |  | 0.00
1985 |  |  |  | 6294.40 |  |  | 7151 |  |  |  | 910 | [10 empty] | 80.09 |  |  |  | 80.13 | [5 empty] | 78.96 |  |  | 81.63 |  |  |  | 9.61 |  | 8.52 | [8 empty] | 11.36 |  |  |  |  | 0.04
1986 |  |  |  | 6504.50 |  |  | 7335 |  |  |  | 910 | [10 empty] | 81.73 |  |  |  | 81.73 | [5 empty] | 81.60 |  |  | 83.73 |  |  |  | 10.22 |  | 9.30 | [8 empty] | 8.97 |  |  |  |  | 0.00
1987 |  |  |  | 5382.90 |  |  | 6188 |  |  |  | 910 | [10 empty] | 74.28 |  |  |  | 75.54 | [5 empty] | 67.53 |  |  | 70.64 |  |  |  | 9.24 |  | 7.69 | [8 empty] | 16.76 |  |  |  |  | 1.27
1988 |  |  |  | 4819.00 |  |  | 6724 |  |  |  | 910 | [10 empty] | 95.45 |  |  |  | 96.20 | [5 empty] | 60.29 |  |  | 76.55 |  |  |  | 3.80 |  | 3.80 | [8 empty] | 0.00 |  |  |  |  | 0.75
1989 |  |  |  | 6307.71 |  |  | 7320 |  |  |  | 910 | [10 empty] | 79.49 |  |  |  | 82.34 | [5 empty] | 79.13 |  |  | 83.56 |  |  |  | 5.72 |  | 5.00 | [8 empty] | 12.66 |  |  |  |  | 2.85
1990 |  |  |  | 6121.52 |  |  | 7114 |  |  |  | 910 | [10 empty] | 77.61 |  |  |  | 80.65 | [5 empty] | 76.79 |  |  | 81.21 |  |  |  | 7.42 |  | 6.47 | [8 empty] | 12.89 |  |  |  |  | 3.03
1991 |  |  |  | 6306.28 |  |  | 7086 |  |  |  | 910 | [10 empty] | 80.52 |  |  |  | 81.34 | [5 empty] | 79.11 |  |  | 80.89 |  |  |  | 6.85 |  | 5.98 | [8 empty] | 12.67 |  |  |  |  | 0.82
1992 |  |  |  | 4772.40 |  |  | 5388 |  |  |  | 910 | [10 empty] | 59.96 |  |  |  | 60.35 | [5 empty] | 59.70 |  |  | 61.34 |  |  |  | 15.94 |  | 11.44 | [8 empty] | 28.21 |  |  |  |  | 0.39
1993 |  |  |  | 6588.06 |  |  | 7567 |  |  |  | 910 | [10 empty] | 82.87 |  |  |  | 85.16 | [5 empty] | 82.64 |  |  | 86.38 |  |  |  | 4.38 |  | 3.90 | [8 empty] | 10.95 |  |  |  |  | 2.29
1994 |  |  |  | 6308.88 |  |  | 7116 |  |  |  | 910 | [10 empty] | 82.95 |  |  |  | 83.80 | [5 empty] | 79.14 |  |  | 81.23 |  |  |  | 3.56 |  | 3.09 | [8 empty] | 13.10 |  |  |  |  | 0.85
1995 |  |  |  | 6221.69 |  |  | 7326 |  |  |  | 910 | [10 empty] | 83.00 |  |  |  | 84.33 | [5 empty] | 78.05 |  |  | 83.63 |  |  |  | 5.09 |  | 4.53 | [8 empty] | 11.15 |  |  |  |  | 1.33
1996 |  |  |  | 5937.24 |  |  | 7377 |  |  |  | 910 | [10 empty] | 83.00 |  |  |  | 85.91 | [5 empty] | 74.28 |  |  | 83.98 |  |  |  | 2.37 |  | 2.08 | [8 empty] | 12.01 |  |  |  |  | 2.91
1997 |  |  |  | 5752.68 |  |  | 6938 |  |  |  | 910 | [10 empty] | 78.88 |  |  |  | 81.12 | [5 empty] | 72.16 |  |  | 79.20 |  |  |  | 5.88 |  | 5.06 | [8 empty] | 13.81 |  |  |  |  | 2.24
1998 |  |  |  | 6152.36 |  |  | 7330 |  |  |  | 910 | [10 empty] | 82.99 |  |  |  | 83.86 | [5 empty] | 77.18 |  |  | 83.68 |  |  |  | 2.09 |  | 1.79 | [8 empty] | 14.35 |  |  |  |  | 0.86
1999 |  |  |  | 5412.92 |  |  | 6709 |  |  |  | 910 | [10 empty] | 76.90 |  |  |  | 79.13 | [5 empty] | 67.90 |  |  | 76.59 |  |  |  | 10.46 |  | 9.24 | [8 empty] | 11.63 |  |  |  |  | 2.23
2000 |  |  |  | 6112.36 |  |  | 7396 |  |  |  | 910 | [10 empty] | 82.92 |  |  |  | 84.60 | [5 empty] | 76.47 |  |  | 84.20 |  |  |  | 2.99 |  | 2.60 | [8 empty] | 12.79 |  |  |  |  | 1.69
2001 |  |  |  | 6198.04 |  |  | 7597 |  |  |  | 910 | [10 empty] | 83.91 |  |  |  | 92.64 | [5 empty] | 77.75 |  |  | 86.72 |  |  |  | 2.14 |  | 2.02 | [8 empty] | 5.34 |  |  |  |  | 8.73
2002 |  |  |  | 5282.46 |  |  | 6401 |  |  |  | 910 | [10 empty] | 76.78 |  |  |  | 76.80 | [5 empty] | 66.27 |  |  | 73.07 |  |  |  | 2.52 |  | 1.98 | [8 empty] | 21.22 |  |  |  |  | 0.01
2003 |  |  |  | 6045.52 |  |  | 7482 |  |  |  | 910 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 75.84 |  |  | 85.41 |  |  |  | 1.88 |  | 1.64 | [8 empty] | 12.57 |  |  |  |  | 0.00
2004 |  |  |  | 6393.08 |  |  | 7499 |  |  |  | 910 | [10 empty] | 83.78 |  |  |  | 83.86 | [5 empty] | 79.98 |  |  | 85.37 |  |  |  | 6.69 |  | 6.01 | [8 empty] | 10.13 |  |  |  |  | 0.08
2005 |  |  |  | 6075.92 |  |  | 7126 |  |  |  | 910 | [10 empty] | 77.24 |  |  |  | 78.93 | [5 empty] | 76.21 |  |  | 81.34 |  |  |  | 2.84 |  | 8.64 | [8 empty] | 12.44 |  |  |  |  | 1.69
2006 |  |  |  | 6501.20 |  |  | 7834 |  |  |  | 910 | [10 empty] | 85.66 |  |  |  | 86.65 | [5 empty] | 81.55 |  |  | 89.43 |  |  |  | 3.94 |  | 4.03 | [8 empty] | 9.32 |  |  |  |  | 0.99
2007 |  |  |  | 6265.62 |  |  | 7267 |  |  |  | 910 | [10 empty] | 79.59 |  |  |  | 81.38 | [5 empty] | 78.59 |  |  | 82.95 |  |  |  | 1.02 |  | 4.26 | [8 empty] | 14.36 |  |  |  |  | 1.79
2008 |  |  |  | 6027.10 |  |  | 7335 |  |  |  | 910 | [10 empty] | 76.49 |  |  |  | 78.58 | [5 empty] | 75.40 |  |  | 83.50 |  |  |  | 10.88 |  | 12.43 | [8 empty] | 8.99 |  |  |  |  | 2.08
2009 |  |  |  | 5272.78 |  |  | 6303 |  |  |  | 910 | [10 empty] | 66.68 |  |  |  | 68.82 | [5 empty] | 66.14 |  |  | 71.95 |  |  |  | 18.00 |  | 18.22 | [8 empty] | 12.97 |  |  |  |  | 2.13
2010 |  |  |  | 5689.33 |  |  | 6550 |  |  |  | 910 | [10 empty] | 71.72 |  |  |  | 73.16 | [5 empty] | 71.37 |  |  | 74.77 |  |  |  | 6.04 |  | 9.83 | [8 empty] | 17.01 |  |  |  |  | 1.44
2011 |  |  |  | 6227.87 |  |  | 7117 |  |  |  | 910 | [10 empty] | 78.51 |  |  |  | 80.39 | [5 empty] | 78.13 |  |  | 81.24 |  |  |  | 4.80 |  | 4.33 | [8 empty] | 15.27 |  |  |  |  | 1.89
2012 |  |  |  | 3423.44 |  |  | 4028 |  |  |  | 910 | [10 empty] | 43.10 |  |  |  | 44.54 | [5 empty] | 42.83 |  |  | 45.86 |  |  |  | 3.38 |  | 13.66 | [8 empty] | 41.80 |  |  |  |  | 1.44
2013 |  |  |  | 6407.37 |  |  | 7268 |  |  |  | 910 | [10 empty] | 81.27 |  |  |  | 82.58 | [5 empty] | 80.38 |  |  | 82.97 |  |  |  | 0.83 |  | 8.92 | [8 empty] | 8.50 |  |  |  |  | 1.30
2014 |  |  |  | 5818.43 |  |  | 6694 |  |  |  | 910 | [10 empty] | 74.63 |  |  |  | 75.40 | [5 empty] | 72.99 |  |  | 76.42 |  |  |  | 5.71 |  | 8.50 | [8 empty] | 16.10 |  |  |  |  | 0.76
2015 |  |  |  | 6840.51 |  |  | 7929 |  |  |  | 910 | [10 empty] | 88.19 |  |  |  | 89.51 | [5 empty] | 85.81 |  |  | 90.51 |  |  |  | 1.75 |  | 1.82 | [8 empty] | 8.68 |  |  |  |  | 1.32
2016 |  |  |  | 6043.29 |  |  | 7044 |  |  |  | 910 | [10 empty] | 76.35 |  |  |  | 76.78 | [5 empty] | 75.60 |  |  | 80.19 |  |  |  | 4.10 |  | 6.57 | [8 empty] | 16.65 |  |  |  |  | 0.42
2017 |  |  |  | 6722.26 |  |  | 7620 |  |  |  | 910 | [10 empty] | 85.99 |  |  |  | 87.22 | [5 empty] | 84.33 |  |  | 86.99 |  |  |  | 0.73 |  | 4.00 | [8 empty] | 8.79 |  |  |  |  | 1.23
2018 |  |  |  | 5466.29 |  |  | 6525 |  |  |  | 910 | [10 empty] | 70.81 |  |  |  | 73.03 | [5 empty] | 68.57 |  |  | 74.49 |  |  |  | 3.18 |  | 9.66 | [8 empty] | 17.31 |  |  |  |  | 2.22
2019 |  |  |  | 5539.99 |  |  | 6877 |  |  |  | 910 | [10 empty] | 69.60 |  |  |  | 69.61 | [5 empty] | 69.50 |  |  | 78.50 |  |  |  | 19.25 |  | 20.06 | [8 empty] | 10.33 |  |  |  |  | 0.02
2020 |  |  |  | 4907.62 |  |  | 5881 |  |  |  | 910 | [10 empty] | 61.50 |  |  |  | 67.15 | [5 empty] | 61.40 |  |  | 66.95 |  |  |  | 5.88 |  | 12.30 | [8 empty] | 20.54 |  |  |  |  | 5.66
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 400
B. |  | Refuelling without maintenance | [35 empty] | 149
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 959 |  |  |  | 20
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 1
E. |  | Testing of plant systems or components | [35 empty] | 6 |  |  |  | 1 | [11 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 11 | [11 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 5
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 1
Z. |  | Other | [39 empty] | 38 | [11 empty] | 45
Subtotal | [37 empty] | 1115 |  |  |  | 472 | [11 empty] | 62
Total | [22 empty] | 0 | [14 empty] | 1649
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
12. |  |  | Reactor I&C Systems | [34 empty] | 21
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 18
14. |  |  | Safety Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 28
16. |  |  | Steam generation systems | [34 empty] | 53
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 21
34. |  |  | Miscellaneous Systems | [34 empty] | 89
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 84
42. |  |  | Electrical Power Supply Systems | [34 empty] | 24
Total | [37 empty] | 402

## GRAVELINES-4
2020 Operating Experience
FR-28 | [8 empty] | GRAVELINES-4 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-04-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-06-14
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-10-01
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.5
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 45 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6658.46 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.12 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.63 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 8.53 %
Unit Capability Factor (UCF) | [18 empty] | : | 80.75 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.72 %
Load Factor (LF) | [18 empty] | : | 83.3 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.12 %
Operating Factor (OF) | [18 empty] | : | 81.45 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1629 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 703.34 | 661.62 |  |  |  | 702.92 |  | 667.07 | [8 empty] | 627.39 |  |  | 0.00 | [6 empty] | 0.00 |  | 530.89 |  |  |  | 674.58 |  |  | 702.60 |  |  | 683.31 | [9 empty] | 704.72 |  |  | 6658.46
EAF [%] |  |  |  |  | 99.62 | 100.00 |  |  |  | 99.93 |  | 99.36 | [8 empty] | 92.07 |  |  | 0.00 | [6 empty] | 0.01 |  | 77.23 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.85 |  |  | 80.63
UCF [%] |  |  |  |  | 99.62 | 100.00 |  |  |  | 99.93 |  | 99.36 | [8 empty] | 93.44 |  |  | 0.00 | [6 empty] | 0.01 |  | 77.23 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.85 |  |  | 80.75
LF [%] |  |  |  |  | 103.89 | 104.46 |  |  |  | 103.96 |  | 101.81 | [8 empty] | 92.67 |  |  | 0.00 | [6 empty] | 0.00 |  | 78.41 |  |  |  | 102.96 |  |  | 103.64 |  |  | 104.29 | [9 empty] | 104.09 |  |  | 83.30
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 93.55 |  |  | 0.00 | [6 empty] | 0.00 |  | 84.41 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.45
FLR [%] |  |  |  |  | 0.38 | 0.00 |  |  |  | 0.06 |  | 0.64 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.06 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.12
UCL [%] |  |  |  |  | 0.38 | 0.00 |  |  |  | 0.06 |  | 0.64 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 84.07 |  | 15.62 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.53
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 6.56 |  |  | 100.00 | [6 empty] | 15.92 |  | 7.15 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.15 |  |  | 10.72
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.37 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.12
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 238125.3 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.19 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.75 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.93 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.84 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.82 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.48 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.26 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 2636.60 |  |  | 3434 |  |  |  | 915 | [10 empty] | 85.39 |  |  |  | 85.39 | [5 empty] | 84.78 |  |  | 91.98 |  |  |  | 2.84 |  | 2.50 | [8 empty] | 12.12 |  |  |  |  | 0.00
1982 |  |  |  | 5498.20 |  |  | 7193 |  |  |  | 910 | [10 empty] | 80.76 |  |  |  | 80.76 | [5 empty] | 68.97 |  |  | 82.11 |  |  |  | 19.24 |  | 19.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 4062.00 |  |  | 4986 |  |  |  | 910 | [10 empty] | 54.50 |  |  |  | 54.50 | [5 empty] | 50.96 |  |  | 56.92 |  |  |  | 12.53 |  | 7.81 | [8 empty] | 37.69 |  |  |  |  | 0.01
1984 |  |  |  | 6006.00 |  |  | 7173 |  |  |  | 910 | [10 empty] | 82.77 |  |  |  | 82.77 | [5 empty] | 75.14 |  |  | 81.66 |  |  |  | 7.35 |  | 6.57 | [8 empty] | 10.67 |  |  |  |  | 0.00
1985 |  |  |  | 6178.80 |  |  | 7387 |  |  |  | 910 | [10 empty] | 80.87 |  |  |  | 83.60 | [5 empty] | 77.51 |  |  | 84.33 |  |  |  | 5.89 |  | 5.23 | [8 empty] | 11.17 |  |  |  |  | 2.74
1986 |  |  |  | 6556.60 |  |  | 7862 |  |  |  | 910 | [10 empty] | 88.64 |  |  |  | 88.70 | [5 empty] | 82.25 |  |  | 89.75 |  |  |  | 2.14 |  | 1.94 | [8 empty] | 9.35 |  |  |  |  | 0.06
1987 |  |  |  | 5472.80 |  |  | 6787 |  |  |  | 910 | [10 empty] | 75.78 |  |  |  | 77.16 | [5 empty] | 68.65 |  |  | 77.48 |  |  |  | 7.48 |  | 6.24 | [8 empty] | 16.61 |  |  |  |  | 1.37
1988 |  |  |  | 6221.00 |  |  | 7789 |  |  |  | 910 | [10 empty] | 85.93 |  |  |  | 87.85 | [5 empty] | 77.83 |  |  | 88.67 |  |  |  | 1.83 |  | 1.64 | [8 empty] | 10.51 |  |  |  |  | 1.93
1989 |  |  |  | 4982.33 |  |  | 6025 |  |  |  | 910 | [10 empty] | 66.86 |  |  |  | 67.37 | [5 empty] | 62.50 |  |  | 68.78 |  |  |  | 16.17 |  | 12.99 | [8 empty] | 19.64 |  |  |  |  | 0.50
1990 |  |  |  | 6151.73 |  |  | 7058 |  |  |  | 910 | [10 empty] | 77.18 |  |  |  | 79.44 | [5 empty] | 77.17 |  |  | 80.57 |  |  |  | 9.13 |  | 7.98 | [8 empty] | 12.58 |  |  |  |  | 2.26
1991 |  |  |  | 6261.99 |  |  | 7067 |  |  |  | 910 | [10 empty] | 80.47 |  |  |  | 81.82 | [5 empty] | 78.55 |  |  | 80.67 |  |  |  | 6.36 |  | 5.55 | [8 empty] | 12.63 |  |  |  |  | 1.35
1992 |  |  |  | 6419.80 |  |  | 7137 |  |  |  | 910 | [10 empty] | 80.20 |  |  |  | 81.01 | [5 empty] | 80.31 |  |  | 81.25 |  |  |  | 2.41 |  | 2.00 | [8 empty] | 16.98 |  |  |  |  | 0.82
1993 |  |  |  | 4680.57 |  |  | 6112 |  |  |  | 910 | [10 empty] | 75.31 |  |  |  | 76.47 | [5 empty] | 58.72 |  |  | 69.77 |  |  |  | 13.65 |  | 12.08 | [8 empty] | 11.45 |  |  |  |  | 1.16
1994 |  |  |  | 6039.34 |  |  | 6824 |  |  |  | 910 | [10 empty] | 82.47 |  |  |  | 83.27 | [5 empty] | 75.76 |  |  | 77.90 |  |  |  | 6.37 |  | 5.67 | [8 empty] | 11.07 |  |  |  |  | 0.80
1995 |  |  |  | 6289.53 |  |  | 7313 |  |  |  | 910 | [10 empty] | 85.42 |  |  |  | 86.42 | [5 empty] | 78.90 |  |  | 83.48 |  |  |  | 3.40 |  | 3.04 | [8 empty] | 10.54 |  |  |  |  | 1.00
1996 |  |  |  | 6288.41 |  |  | 7552 |  |  |  | 910 | [10 empty] | 83.16 |  |  |  | 85.50 | [5 empty] | 78.67 |  |  | 85.97 |  |  |  | 4.28 |  | 3.82 | [8 empty] | 10.68 |  |  |  |  | 2.34
1997 |  |  |  | 5986.68 |  |  | 7206 |  |  |  | 910 | [10 empty] | 80.46 |  |  |  | 81.31 | [5 empty] | 75.10 |  |  | 82.26 |  |  |  | 2.57 |  | 2.15 | [8 empty] | 16.54 |  |  |  |  | 0.85
1998 |  |  |  | 6519.35 |  |  | 7570 |  |  |  | 910 | [10 empty] | 84.10 |  |  |  | 85.44 | [5 empty] | 81.78 |  |  | 86.42 |  |  |  | 1.97 |  | 1.72 | [8 empty] | 12.84 |  |  |  |  | 1.35
1999 |  |  |  | 5550.87 |  |  | 6734 |  |  |  | 910 | [10 empty] | 74.28 |  |  |  | 76.41 | [5 empty] | 69.63 |  |  | 76.87 |  |  |  | 11.82 |  | 10.24 | [8 empty] | 13.35 |  |  |  |  | 2.13
2000 |  |  |  | 4563.64 |  |  | 5453 |  |  |  | 910 | [10 empty] | 57.74 |  |  |  | 69.50 | [5 empty] | 57.09 |  |  | 62.08 |  |  |  | 0.50 |  | 0.35 | [8 empty] | 30.15 |  |  |  |  | 11.76
2001 |  |  |  | 5990.69 |  |  | 7094 |  |  |  | 910 | [10 empty] | 78.26 |  |  |  | 79.76 | [5 empty] | 75.15 |  |  | 80.98 |  |  |  | 8.38 |  | 7.29 | [8 empty] | 12.95 |  |  |  |  | 1.50
2002 |  |  |  | 6028.10 |  |  | 7219 |  |  |  | 910 | [10 empty] | 80.04 |  |  |  | 81.12 | [5 empty] | 75.62 |  |  | 82.41 |  |  |  | 9.31 |  | 8.32 | [8 empty] | 10.55 |  |  |  |  | 1.08
2003 |  |  |  | 5701.86 |  |  | 6589 |  |  |  | 910 | [10 empty] | 74.19 |  |  |  | 74.19 | [5 empty] | 71.53 |  |  | 75.22 |  |  |  | 1.28 |  | 0.96 | [8 empty] | 24.84 |  |  |  |  | 0.00
2004 |  |  |  | 6544.62 |  |  | 7693 |  |  |  | 910 | [10 empty] | 85.39 |  |  |  | 85.39 | [5 empty] | 81.87 |  |  | 87.58 |  |  |  | 5.42 |  | 4.90 | [8 empty] | 9.71 |  |  |  |  | 0.00
2005 |  |  |  | 6437.07 |  |  | 7354 |  |  |  | 910 | [10 empty] | 81.75 |  |  |  | 82.20 | [5 empty] | 80.75 |  |  | 83.95 |  |  |  | 4.33 |  | 5.72 | [8 empty] | 12.09 |  |  |  |  | 0.45
2006 |  |  |  | 7123.08 |  |  | 8079 |  |  |  | 910 | [10 empty] | 89.94 |  |  |  | 91.49 | [5 empty] | 89.36 |  |  | 92.23 |  |  |  | 0.19 |  | 0.82 | [8 empty] | 7.69 |  |  |  |  | 1.55
2007 |  |  |  | 6341.02 |  |  | 7164 |  |  |  | 910 | [10 empty] | 79.79 |  |  |  | 81.07 | [5 empty] | 79.54 |  |  | 81.77 |  |  |  | 3.88 |  | 7.20 | [8 empty] | 11.73 |  |  |  |  | 1.28
2008 |  |  |  | 6663.01 |  |  | 7678 |  |  |  | 910 | [10 empty] | 85.04 |  |  |  | 85.78 | [5 empty] | 83.36 |  |  | 87.41 |  |  |  | 5.01 |  | 4.71 | [8 empty] | 9.52 |  |  |  |  | 0.73
2009 |  |  |  | 6312.54 |  |  | 7342 |  |  |  | 910 | [10 empty] | 81.40 |  |  |  | 83.61 | [5 empty] | 79.19 |  |  | 83.81 |  |  |  | 0.60 |  | 4.37 | [8 empty] | 12.02 |  |  |  |  | 2.22
2010 |  |  |  | 6785.73 |  |  | 7958 |  |  |  | 910 | [10 empty] | 88.51 |  |  |  | 89.11 | [5 empty] | 85.12 |  |  | 90.84 |  |  |  | 1.18 |  | 3.23 | [8 empty] | 7.66 |  |  |  |  | 0.59
2011 |  |  |  | 6464.37 |  |  | 7383 |  |  |  | 910 | [10 empty] | 82.01 |  |  |  | 83.66 | [5 empty] | 81.09 |  |  | 84.28 |  |  |  | 0.22 |  | 3.16 | [8 empty] | 13.18 |  |  |  |  | 1.66
2012 |  |  |  | 6669.67 |  |  | 7612 |  |  |  | 910 | [10 empty] | 83.89 |  |  |  | 84.85 | [5 empty] | 83.44 |  |  | 86.66 |  |  |  | 5.09 |  | 7.62 | [8 empty] | 7.52 |  |  |  |  | 0.96
2013 |  |  |  | 6120.30 |  |  | 6967 |  |  |  | 910 | [10 empty] | 77.10 |  |  |  | 80.44 | [5 empty] | 76.78 |  |  | 79.53 |  |  |  | 1.80 |  | 7.01 | [8 empty] | 12.55 |  |  |  |  | 3.34
2014 |  |  |  | 4797.97 |  |  | 5335 |  |  |  | 910 | [10 empty] | 59.73 |  |  |  | 60.73 | [5 empty] | 60.19 |  |  | 60.90 |  |  |  | 6.39 |  | 9.88 | [8 empty] | 29.39 |  |  |  |  | 1.00
2015 |  |  |  | 6476.69 |  |  | 7127 |  |  |  | 910 | [10 empty] | 80.29 |  |  |  | 80.52 | [5 empty] | 81.25 |  |  | 81.36 |  |  |  | 1.96 |  | 3.57 | [8 empty] | 15.91 |  |  |  |  | 0.22
2016 |  |  |  | 6716.29 |  |  | 7445 |  |  |  | 910 | [10 empty] | 82.50 |  |  |  | 89.06 | [5 empty] | 84.02 |  |  | 84.76 |  |  |  | 0.76 |  | 2.05 | [8 empty] | 8.88 |  |  |  |  | 6.56
2017 |  |  |  | 5517.18 |  |  | 6063 |  |  |  | 910 | [10 empty] | 67.52 |  |  |  | 69.95 | [5 empty] | 69.21 |  |  | 69.21 |  |  |  | 2.19 |  | 12.36 | [8 empty] | 17.69 |  |  |  |  | 2.43
2018 |  |  |  | 6884.99 |  |  | 7474 |  |  |  | 910 | [10 empty] | 84.81 |  |  |  | 84.81 | [5 empty] | 86.37 |  |  | 85.32 |  |  |  | 4.34 |  | 6.19 | [8 empty] | 9.00 |  |  |  |  | 0.00
2019 |  |  |  | 5724.80 |  |  | 6192 |  |  |  | 910 | [10 empty] | 69.76 |  |  |  | 69.91 | [5 empty] | 71.81 |  |  | 70.68 |  |  |  | 3.50 |  | 7.85 | [8 empty] | 22.24 |  |  |  |  | 0.15
2020 |  |  |  | 6658.46 |  |  | 7155 |  |  |  | 910 | [10 empty] | 80.63 |  |  |  | 80.75 | [5 empty] | 83.30 |  |  | 81.45 |  |  |  | 0.12 |  | 8.53 | [8 empty] | 10.72 |  |  |  |  | 0.12
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 409
B. |  | Refuelling without maintenance | [35 empty] | 104
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1011 |  |  |  | 7
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 5 |  |  |  | 3
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 1 | [11 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 7
I. |  | Grid capacity limitation | [51 empty] | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 7
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 0 | [11 empty] | 29
Z. |  | Other | [39 empty] | 16 | [11 empty] | 23
Subtotal | [37 empty] | 1124 |  |  |  | 450 | [11 empty] | 55
Total | [22 empty] | 0 | [14 empty] | 1629
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 26
12. |  |  | Reactor I&C Systems | [34 empty] | 44
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [34 empty] | 25
16. |  |  | Steam generation systems | [34 empty] | 65
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 23
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 81
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 40
42. |  |  | Electrical Power Supply Systems | [34 empty] | 58
Total | [37 empty] | 429

## GRAVELINES-5
2020 Operating Experience
FR-51 | [8 empty] | GRAVELINES-5 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-10-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-08-28
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-01-15
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.85 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 36 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5493.2 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 11.28 %
Energy Availability Factor (EAF) | [18 empty] | : | 71.15 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 23.73 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.5 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 1.77 %
Load Factor (LF) | [18 empty] | : | 68.72 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.35 %
Operating Factor (OF) | [18 empty] | : | 74.8 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2214 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 9.18 |  |  |  | 527.62 |  | 612.73 | [8 empty] | 519.83 |  |  | 584.30 | [6 empty] | 653.85 |  | 518.85 |  |  |  | 607.79 |  |  | 640.27 |  |  | 594.56 | [9 empty] | 224.22 |  |  | 5493.20
EAF [%] |  |  |  |  | 0.01 | 1.47 |  |  |  | 79.50 |  | 93.52 | [8 empty] | 79.59 |  |  | 98.56 | [6 empty] | 96.89 |  | 77.13 |  |  |  | 95.80 |  |  | 98.73 |  |  | 98.25 | [9 empty] | 33.11 |  |  | 71.15
UCF [%] |  |  |  |  | 16.14 | 3.05 |  |  |  | 79.50 |  | 93.52 | [8 empty] | 99.63 |  |  | 98.73 | [6 empty] | 96.99 |  | 78.11 |  |  |  | 96.44 |  |  | 98.73 |  |  | 98.25 | [9 empty] | 33.12 |  |  | 74.50
LF [%] |  |  |  |  | 0.00 | 1.45 |  |  |  | 78.04 |  | 93.52 | [8 empty] | 76.78 |  |  | 89.18 | [6 empty] | 96.57 |  | 76.64 |  |  |  | 92.76 |  |  | 94.44 |  |  | 90.75 | [9 empty] | 33.12 |  |  | 68.72
OF [%] |  |  |  |  | 0.00 | 8.05 |  |  |  | 84.52 |  | 97.50 | [8 empty] | 87.50 |  |  | 100.00 | [6 empty] | 100.00 |  | 85.35 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 33.60 |  |  | 74.80
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 12.17 |  | 2.87 | [8 empty] | 0.32 |  |  | 1.24 | [6 empty] | 2.88 |  | 21.82 |  |  |  | 3.38 |  |  | 0.56 |  |  | 1.28 | [9 empty] | 66.88 |  |  | 11.28
UCL [%] |  |  |  |  | 83.86 | 90.36 |  |  |  | 11.02 |  | 2.76 | [8 empty] | 0.32 |  |  | 1.24 | [6 empty] | 2.87 |  | 21.81 |  |  |  | 3.38 |  |  | 0.56 |  |  | 1.27 | [9 empty] | 66.88 |  |  | 23.73
PUF [%] |  |  |  |  | 0.00 | 6.59 |  |  |  | 9.48 |  | 3.72 | [8 empty] | 0.05 |  |  | 0.03 | [6 empty] | 0.14 |  | 0.09 |  |  |  | 0.18 |  |  | 0.71 |  |  | 0.48 | [9 empty] | 0.00 |  |  | 1.77
XUF [%] |  |  |  |  | 16.12 | 1.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.04 |  |  | 0.18 | [6 empty] | 0.10 |  | 0.97 |  |  |  | 0.64 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 3.35
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 209390.8 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.94 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.57 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.65 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.3 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.05 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.64 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.73 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.57 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 6768.40 |  |  | 7785 |  |  |  | 910 | [10 empty] | 90.02 |  |  |  | 90.06 | [5 empty] | 84.91 |  |  | 88.87 |  |  |  | 9.94 |  | 9.94 | [8 empty] | 0.00 |  |  |  |  | 0.04
1986 |  |  |  | 5152.60 |  |  | 6673 |  |  |  | 910 | [10 empty] | 75.24 |  |  |  | 77.10 | [5 empty] | 64.64 |  |  | 76.18 |  |  |  | 3.23 |  | 2.57 | [8 empty] | 20.33 |  |  |  |  | 1.86
1987 |  |  |  | 5236.50 |  |  | 6818 |  |  |  | 910 | [10 empty] | 80.63 |  |  |  | 81.53 | [5 empty] | 65.69 |  |  | 77.83 |  |  |  | 8.13 |  | 7.21 | [8 empty] | 11.26 |  |  |  |  | 0.90
1988 |  |  |  | 4964.00 |  |  | 6306 |  |  |  | 910 | [10 empty] | 71.75 |  |  |  | 75.25 | [5 empty] | 62.10 |  |  | 71.79 |  |  |  | 7.10 |  | 5.75 | [8 empty] | 18.99 |  |  |  |  | 3.50
1989 |  |  |  | 6020.57 |  |  | 7198 |  |  |  | 910 | [10 empty] | 80.64 |  |  |  | 80.98 | [5 empty] | 75.53 |  |  | 82.17 |  |  |  | 11.01 |  | 10.02 | [8 empty] | 9.00 |  |  |  |  | 0.34
1990 |  |  |  | 5992.77 |  |  | 7367 |  |  |  | 910 | [10 empty] | 80.68 |  |  |  | 83.24 | [5 empty] | 75.18 |  |  | 84.10 |  |  |  | 4.58 |  | 3.99 | [8 empty] | 12.77 |  |  |  |  | 2.56
1991 |  |  |  | 5276.17 |  |  | 6352 |  |  |  | 910 | [10 empty] | 69.61 |  |  |  | 72.16 | [5 empty] | 66.19 |  |  | 72.51 |  |  |  | 4.86 |  | 3.68 | [8 empty] | 24.16 |  |  |  |  | 2.55
1992 |  |  |  | 6308.02 |  |  | 7361 |  |  |  | 910 | [10 empty] | 82.64 |  |  |  | 82.65 | [5 empty] | 78.91 |  |  | 83.80 |  |  |  | 3.06 |  | 2.61 | [8 empty] | 14.74 |  |  |  |  | 0.00
1993 |  |  |  | 6180.53 |  |  | 7290 |  |  |  | 910 | [10 empty] | 78.59 |  |  |  | 82.73 | [5 empty] | 77.53 |  |  | 83.22 |  |  |  | 6.30 |  | 5.56 | [8 empty] | 11.71 |  |  |  |  | 4.15
1994 |  |  |  | 5793.25 |  |  | 7147 |  |  |  | 910 | [10 empty] | 83.21 |  |  |  | 84.37 | [5 empty] | 72.67 |  |  | 81.59 |  |  |  | 3.60 |  | 3.15 | [8 empty] | 12.48 |  |  |  |  | 1.16
1995 |  |  |  | 6180.98 |  |  | 7704 |  |  |  | 910 | [10 empty] | 85.99 |  |  |  | 87.59 | [5 empty] | 77.54 |  |  | 87.95 |  |  |  | 2.11 |  | 1.88 | [8 empty] | 10.52 |  |  |  |  | 1.60
1996 |  |  |  | 5495.18 |  |  | 6652 |  |  |  | 910 | [10 empty] | 72.12 |  |  |  | 75.29 | [5 empty] | 68.75 |  |  | 75.73 |  |  |  | 6.30 |  | 5.06 | [8 empty] | 19.65 |  |  |  |  | 3.17
1997 |  |  |  | 6429.86 |  |  | 7586 |  |  |  | 910 | [10 empty] | 86.07 |  |  |  | 87.63 | [5 empty] | 80.66 |  |  | 86.60 |  |  |  | 2.13 |  | 1.91 | [8 empty] | 10.46 |  |  |  |  | 1.56
1998 |  |  |  | 6884.31 |  |  | 8286 |  |  |  | 910 | [10 empty] | 95.83 |  |  |  | 97.34 | [5 empty] | 86.36 |  |  | 94.59 |  |  |  | 2.05 |  | 2.04 | [8 empty] | 0.62 |  |  |  |  | 1.52
1999 |  |  |  | 5124.26 |  |  | 6127 |  |  |  | 910 | [10 empty] | 67.03 |  |  |  | 68.06 | [5 empty] | 64.28 |  |  | 69.94 |  |  |  | 21.44 |  | 18.57 | [8 empty] | 13.37 |  |  |  |  | 1.03
2000 |  |  |  | 5985.50 |  |  | 7444 |  |  |  | 910 | [10 empty] | 81.45 |  |  |  | 84.37 | [5 empty] | 74.88 |  |  | 84.74 |  |  |  | 4.94 |  | 4.38 | [8 empty] | 11.25 |  |  |  |  | 2.92
2001 |  |  |  | 5762.64 |  |  | 6990 |  |  |  | 910 | [10 empty] | 78.23 |  |  |  | 80.15 | [5 empty] | 72.29 |  |  | 79.79 |  |  |  | 8.59 |  | 7.54 | [8 empty] | 12.31 |  |  |  |  | 1.93
2002 |  |  |  | 6423.39 |  |  | 7662 |  |  |  | 910 | [10 empty] | 84.68 |  |  |  | 85.83 | [5 empty] | 80.58 |  |  | 87.47 |  |  |  | 4.07 |  | 3.64 | [8 empty] | 10.52 |  |  |  |  | 1.15
2003 |  |  |  | 6473.43 |  |  | 7518 |  |  |  | 910 | [10 empty] | 84.32 |  |  |  | 85.14 | [5 empty] | 81.21 |  |  | 85.82 |  |  |  | 1.24 |  | 1.07 | [8 empty] | 13.79 |  |  |  |  | 0.83
2004 |  |  |  | 6613.48 |  |  | 7836 |  |  |  | 910 | [10 empty] | 86.25 |  |  |  | 88.79 | [5 empty] | 82.74 |  |  | 89.21 |  |  |  | 2.01 |  | 1.82 | [8 empty] | 9.38 |  |  |  |  | 2.55
2005 |  |  |  | 6410.04 |  |  | 7524 |  |  |  | 910 | [10 empty] | 81.68 |  |  |  | 84.01 | [5 empty] | 80.40 |  |  | 85.88 |  |  |  | 2.21 |  | 2.47 | [8 empty] | 13.51 |  |  |  |  | 2.33
2006 |  |  |  | 5313.17 |  |  | 6313 |  |  |  | 910 | [10 empty] | 68.84 |  |  |  | 69.82 | [5 empty] | 66.65 |  |  | 72.07 |  |  |  | 7.46 |  | 6.54 | [8 empty] | 23.64 |  |  |  |  | 0.97
2007 |  |  |  | 6510.19 |  |  | 7592 |  |  |  | 910 | [10 empty] | 83.46 |  |  |  | 85.36 | [5 empty] | 81.66 |  |  | 86.66 |  |  |  | 4.99 |  | 7.39 | [8 empty] | 7.24 |  |  |  |  | 1.90
2008 |  |  |  | 6357.76 |  |  | 7352 |  |  |  | 910 | [10 empty] | 81.16 |  |  |  | 82.33 | [5 empty] | 79.54 |  |  | 83.70 |  |  |  | 4.48 |  | 5.29 | [8 empty] | 12.38 |  |  |  |  | 1.17
2009 |  |  |  | 6652.21 |  |  | 7846 |  |  |  | 910 | [10 empty] | 85.54 |  |  |  | 88.33 | [5 empty] | 83.45 |  |  | 89.57 |  |  |  | 0.88 |  | 4.13 | [8 empty] | 7.54 |  |  |  |  | 2.79
2010 |  |  |  | 6228.43 |  |  | 7120 |  |  |  | 910 | [10 empty] | 79.28 |  |  |  | 80.20 | [5 empty] | 78.13 |  |  | 81.28 |  |  |  | 2.02 |  | 5.32 | [8 empty] | 14.47 |  |  |  |  | 0.92
2011 |  |  |  | 6859.22 |  |  | 7807 |  |  |  | 910 | [10 empty] | 87.04 |  |  |  | 88.52 | [5 empty] | 86.05 |  |  | 89.12 |  |  |  | 0.02 |  | 3.77 | [8 empty] | 7.71 |  |  |  |  | 1.48
2012 |  |  |  | 5099.17 |  |  | 5943 |  |  |  | 910 | [10 empty] | 64.29 |  |  |  | 65.27 | [5 empty] | 63.79 |  |  | 67.66 |  |  |  | 7.74 |  | 21.09 | [8 empty] | 13.64 |  |  |  |  | 0.99
2013 |  |  |  | 6635.01 |  |  | 7427 |  |  |  | 910 | [10 empty] | 83.51 |  |  |  | 84.20 | [5 empty] | 83.23 |  |  | 84.78 |  |  |  | 1.29 |  | 8.42 | [8 empty] | 7.38 |  |  |  |  | 0.69
2014 |  |  |  | 6114.63 |  |  | 6972 |  |  |  | 910 | [10 empty] | 77.24 |  |  |  | 78.28 | [5 empty] | 76.71 |  |  | 79.59 |  |  |  | 1.17 |  | 2.71 | [8 empty] | 19.01 |  |  |  |  | 1.04
2015 |  |  |  | 6727.72 |  |  | 7810 |  |  |  | 910 | [10 empty] | 87.21 |  |  |  | 88.12 | [5 empty] | 84.40 |  |  | 89.16 |  |  |  | 1.06 |  | 2.26 | [8 empty] | 9.62 |  |  |  |  | 0.91
2016 |  |  |  | 2133.02 |  |  | 2378 |  |  |  | 910 | [10 empty] | 26.98 |  |  |  | 26.99 | [5 empty] | 26.68 |  |  | 27.07 |  |  |  | 0.11 |  | 50.31 | [8 empty] | 22.70 |  |  |  |  | 0.01
2017 |  |  |  | 2547.59 |  |  | 3150 |  |  |  | 910 | [10 empty] | 32.12 |  |  |  | 36.86 | [5 empty] | 31.96 |  |  | 35.96 |  |  |  | 5.90 |  | 51.76 | [8 empty] | 11.38 |  |  |  |  | 4.73
2018 |  |  |  | 6253.07 |  |  | 7131 |  |  |  | 910 | [10 empty] | 78.87 |  |  |  | 79.07 | [5 empty] | 78.44 |  |  | 81.40 |  |  |  | 1.64 |  | 5.31 | [8 empty] | 15.62 |  |  |  |  | 0.20
2019 |  |  |  | 4192.74 |  |  | 4915 |  |  |  | 910 | [10 empty] | 53.33 |  |  |  | 56.72 | [5 empty] | 52.60 |  |  | 56.11 |  |  |  | 6.87 |  | 8.43 | [8 empty] | 34.85 |  |  |  |  | 3.39
2020 |  |  |  | 5493.20 |  |  | 6570 |  |  |  | 910 | [10 empty] | 71.15 |  |  |  | 74.50 | [5 empty] | 68.72 |  |  | 74.80 |  |  |  | 11.28 |  | 23.73 | [8 empty] | 1.77 |  |  |  |  | 3.35
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 360
B. |  | Refuelling without maintenance | [35 empty] | 123
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 944 |  |  |  | 18
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 2
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 240
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 15
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 16
Z. |  | Other | [39 empty] | 14
Subtotal | [37 empty] | 1072 |  |  |  | 648 | [11 empty] | 20
Total | [22 empty] | 0 | [14 empty] | 1740
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 24
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 63
16. |  |  | Steam generation systems | [34 empty] | 255
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 33
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 69
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 52
42. |  |  | Electrical Power Supply Systems | [34 empty] | 48
Total | [37 empty] | 604

## GRAVELINES-6
2020 Operating Experience
FR-52 | [8 empty] | GRAVELINES-6 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-10-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-08-01
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-10-25
Reference unit power (net) | [12 empty] | : |  |  | 910 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.85 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 36 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4343.71 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.9 %
Energy Availability Factor (EAF) | [18 empty] | : | 54.51 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 16.86 %
Unit Capability Factor (UCF) | [18 empty] | : | 56.83 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 26.3 %
Load Factor (LF) | [18 empty] | : | 54.34 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.32 %
Operating Factor (OF) | [18 empty] | : | 55.57 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3903 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 687.77 | 643.67 |  |  |  | 661.21 |  | 664.89 | [8 empty] | 553.46 |  |  | 236.46 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 274.63 | [9 empty] | 621.64 |  |  | 4343.71
EAF [%] |  |  |  |  | 100.00 | 99.79 |  |  |  | 99.94 |  | 99.91 | [8 empty] | 81.49 |  |  | 36.09 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.03 |  |  | 7.53 |  |  | 41.40 | [9 empty] | 89.73 |  |  | 54.51
UCF [%] |  |  |  |  | 100.00 | 99.79 |  |  |  | 99.94 |  | 99.91 | [8 empty] | 83.03 |  |  | 39.90 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 20.26 |  |  | 10.08 |  |  | 41.40 | [9 empty] | 89.73 |  |  | 56.83
LF [%] |  |  |  |  | 101.58 | 101.63 |  |  |  | 97.79 |  | 101.48 | [8 empty] | 81.75 |  |  | 36.09 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 41.92 | [9 empty] | 91.82 |  |  | 54.34
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 83.60 |  |  | 40.14 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 54.31 | [9 empty] | 90.86 |  |  | 55.57
FLR [%] |  |  |  |  | 0.00 | 0.05 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 16.97 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 10.15 |  |  | 3.90
UCL [%] |  |  |  |  | 0.00 | 0.05 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 16.97 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 38.82 |  |  | 89.92 |  |  | 45.72 | [9 empty] | 10.13 |  |  | 16.86
PUF [%] |  |  |  |  | 0.00 | 0.16 |  |  |  | 0.00 |  | 0.04 | [8 empty] | 0.00 |  |  | 60.10 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 40.92 |  |  | 0.00 |  |  | 12.89 | [9 empty] | 0.14 |  |  | 26.30
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.53 |  |  | 3.81 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 20.23 |  |  | 2.55 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.32
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 214938.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.78 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.69 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.28 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.56 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.28 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.6 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.44 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 2337.10 |  |  | 3111 |  |  |  | 910 | [10 empty] | 97.26 |  |  |  | 97.26 | [5 empty] | 94.68 |  |  | 97.61 |  |  |  | 2.74 |  | 2.74 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 5540.40 |  |  | 6677 |  |  |  | 910 | [10 empty] | 75.88 |  |  |  | 76.32 | [5 empty] | 69.50 |  |  | 76.22 |  |  |  | 3.96 |  | 3.15 | [8 empty] | 20.53 |  |  |  |  | 0.44
1987 |  |  |  | 5583.90 |  |  | 7031 |  |  |  | 910 | [10 empty] | 80.14 |  |  |  | 80.57 | [5 empty] | 70.05 |  |  | 80.26 |  |  |  | 9.39 |  | 8.34 | [8 empty] | 11.09 |  |  |  |  | 0.42
1988 |  |  |  | 6490.00 |  |  | 7453 |  |  |  | 910 | [10 empty] | 81.43 |  |  |  | 83.77 | [5 empty] | 81.19 |  |  | 84.85 |  |  |  | 14.30 |  | 13.97 | [8 empty] | 2.25 |  |  |  |  | 2.34
1989 |  |  |  | 5177.26 |  |  | 6274 |  |  |  | 910 | [10 empty] | 71.08 |  |  |  | 71.17 | [5 empty] | 64.95 |  |  | 71.62 |  |  |  | 9.18 |  | 7.19 | [8 empty] | 21.63 |  |  |  |  | 0.09
1990 |  |  |  | 6120.26 |  |  | 7553 |  |  |  | 910 | [10 empty] | 87.07 |  |  |  | 87.56 | [5 empty] | 76.78 |  |  | 86.22 |  |  |  | 12.41 |  | 12.41 | [8 empty] | 0.03 |  |  |  |  | 0.49
1991 |  |  |  | 5888.22 |  |  | 6953 |  |  |  | 910 | [10 empty] | 77.47 |  |  |  | 78.53 | [5 empty] | 73.86 |  |  | 79.37 |  |  |  | 9.62 |  | 8.36 | [8 empty] | 13.11 |  |  |  |  | 1.06
1992 |  |  |  | 5085.13 |  |  | 6246 |  |  |  | 910 | [10 empty] | 69.03 |  |  |  | 70.27 | [5 empty] | 63.62 |  |  | 71.11 |  |  |  | 11.78 |  | 9.38 | [8 empty] | 20.35 |  |  |  |  | 1.24
1993 |  |  |  | 5293.57 |  |  | 6751 |  |  |  | 910 | [10 empty] | 73.42 |  |  |  | 82.03 | [5 empty] | 66.41 |  |  | 77.07 |  |  |  | 7.24 |  | 6.40 | [8 empty] | 11.57 |  |  |  |  | 8.61
1994 |  |  |  | 6053.73 |  |  | 7487 |  |  |  | 910 | [10 empty] | 83.89 |  |  |  | 86.00 | [5 empty] | 75.94 |  |  | 85.47 |  |  |  | 1.80 |  | 1.58 | [8 empty] | 12.42 |  |  |  |  | 2.11
1995 |  |  |  | 6769.36 |  |  | 7922 |  |  |  | 910 | [10 empty] | 88.83 |  |  |  | 89.78 | [5 empty] | 84.92 |  |  | 90.43 |  |  |  | 0.95 |  | 0.86 | [8 empty] | 9.36 |  |  |  |  | 0.95
1996 |  |  |  | 6609.47 |  |  | 7755 |  |  |  | 910 | [10 empty] | 86.39 |  |  |  | 86.77 | [5 empty] | 82.69 |  |  | 88.29 |  |  |  | 3.48 |  | 3.13 | [8 empty] | 10.11 |  |  |  |  | 0.37
1997 |  |  |  | 4545.45 |  |  | 5437 |  |  |  | 910 | [10 empty] | 59.49 |  |  |  | 60.58 | [5 empty] | 57.02 |  |  | 62.07 |  |  |  | 23.50 |  | 18.61 | [8 empty] | 20.81 |  |  |  |  | 1.09
1998 |  |  |  | 6531.81 |  |  | 7746 |  |  |  | 910 | [10 empty] | 86.08 |  |  |  | 88.53 | [5 empty] | 81.94 |  |  | 88.42 |  |  |  | 1.63 |  | 1.47 | [8 empty] | 10.00 |  |  |  |  | 2.45
1999 |  |  |  | 6141.43 |  |  | 7222 |  |  |  | 910 | [10 empty] | 80.29 |  |  |  | 80.92 | [5 empty] | 77.04 |  |  | 82.44 |  |  |  | 4.70 |  | 3.99 | [8 empty] | 15.10 |  |  |  |  | 0.63
2000 |  |  |  | 6720.94 |  |  | 7887 |  |  |  | 910 | [10 empty] | 87.03 |  |  |  | 88.68 | [5 empty] | 84.08 |  |  | 89.79 |  |  |  | 0.35 |  | 0.32 | [8 empty] | 11.01 |  |  |  |  | 1.65
2001 |  |  |  | 6148.66 |  |  | 7265 |  |  |  | 910 | [10 empty] | 80.24 |  |  |  | 82.23 | [5 empty] | 77.13 |  |  | 82.93 |  |  |  | 5.74 |  | 5.01 | [8 empty] | 12.76 |  |  |  |  | 1.99
2002 |  |  |  | 6690.91 |  |  | 7784 |  |  |  | 910 | [10 empty] | 86.02 |  |  |  | 87.49 | [5 empty] | 83.93 |  |  | 88.86 |  |  |  | 3.39 |  | 3.07 | [8 empty] | 9.44 |  |  |  |  | 1.48
2003 |  |  |  | 6462.57 |  |  | 7410 |  |  |  | 910 | [10 empty] | 82.50 |  |  |  | 83.26 | [5 empty] | 81.07 |  |  | 84.59 |  |  |  | 1.98 |  | 1.69 | [8 empty] | 15.05 |  |  |  |  | 0.76
2004 |  |  |  | 6936.10 |  |  | 7850 |  |  |  | 910 | [10 empty] | 86.85 |  |  |  | 88.32 | [5 empty] | 86.77 |  |  | 89.37 |  |  |  | 4.00 |  | 3.68 | [8 empty] | 8.00 |  |  |  |  | 1.47
2005 |  |  |  | 6536.49 |  |  | 7511 |  |  |  | 910 | [10 empty] | 82.35 |  |  |  | 84.30 | [5 empty] | 82.00 |  |  | 85.74 |  |  |  | 1.97 |  | 1.69 | [8 empty] | 14.01 |  |  |  |  | 1.95
2006 |  |  |  | 7058.37 |  |  | 7907 |  |  |  | 910 | [10 empty] | 88.25 |  |  |  | 89.35 | [5 empty] | 88.54 |  |  | 90.26 |  |  |  | 1.41 |  | 1.98 | [8 empty] | 8.68 |  |  |  |  | 1.09
2007 |  |  |  | 5455.66 |  |  | 6087 |  |  |  | 910 | [10 empty] | 68.42 |  |  |  | 69.10 | [5 empty] | 68.44 |  |  | 69.49 |  |  |  | 1.42 |  | 7.46 | [8 empty] | 23.44 |  |  |  |  | 0.68
2008 |  |  |  | 5792.75 |  |  | 6383 |  |  |  | 910 | [10 empty] | 71.49 |  |  |  | 71.53 | [5 empty] | 72.47 |  |  | 72.67 |  |  |  | 2.96 |  | 18.85 | [8 empty] | 9.62 |  |  |  |  | 0.04
2009 |  |  |  | 7108.24 |  |  | 7866 |  |  |  | 910 | [10 empty] | 88.95 |  |  |  | 89.00 | [5 empty] | 89.17 |  |  | 89.79 |  |  |  | 0.12 |  | 3.34 | [8 empty] | 7.66 |  |  |  |  | 0.04
2010 |  |  |  | 6363.90 |  |  | 7125 |  |  |  | 910 | [10 empty] | 80.15 |  |  |  | 80.86 | [5 empty] | 79.83 |  |  | 81.34 |  |  |  | 1.53 |  | 3.12 | [8 empty] | 16.02 |  |  |  |  | 0.71
2011 |  |  |  | 7101.91 |  |  | 7859 |  |  |  | 910 | [10 empty] | 89.19 |  |  |  | 89.51 | [5 empty] | 89.09 |  |  | 89.71 |  |  |  | 0.11 |  | 2.52 | [8 empty] | 7.97 |  |  |  |  | 0.32
2012 |  |  |  | 6115.18 |  |  | 6810 |  |  |  | 910 | [10 empty] | 76.26 |  |  |  | 76.97 | [5 empty] | 76.50 |  |  | 77.53 |  |  |  | 1.43 |  | 7.81 | [8 empty] | 15.22 |  |  |  |  | 0.71
2013 |  |  |  | 6773.04 |  |  | 7544 |  |  |  | 910 | [10 empty] | 84.27 |  |  |  | 84.52 | [5 empty] | 84.96 |  |  | 86.12 |  |  |  | 3.46 |  | 5.58 | [8 empty] | 9.90 |  |  |  |  | 0.26
2014 |  |  |  | 5768.07 |  |  | 6619 |  |  |  | 910 | [10 empty] | 74.93 |  |  |  | 75.30 | [5 empty] | 72.36 |  |  | 75.56 |  |  |  | 9.21 |  | 7.64 | [8 empty] | 17.06 |  |  |  |  | 0.37
2015 |  |  |  | 6824.41 |  |  | 7703 |  |  |  | 910 | [10 empty] | 85.51 |  |  |  | 97.72 | [5 empty] | 85.61 |  |  | 87.93 |  |  |  | 2.25 |  | 2.25 | [8 empty] | 0.04 |  |  |  |  | 12.21
2016 |  |  |  | 6544.45 |  |  | 7506 |  |  |  | 910 | [10 empty] | 82.51 |  |  |  | 83.79 | [5 empty] | 81.87 |  |  | 85.45 |  |  |  | 1.87 |  | 1.60 | [8 empty] | 14.61 |  |  |  |  | 1.28
2017 |  |  |  | 5875.43 |  |  | 6627 |  |  |  | 910 | [10 empty] | 72.85 |  |  |  | 75.77 | [5 empty] | 73.70 |  |  | 75.65 |  |  |  | 1.93 |  | 7.68 | [8 empty] | 16.54 |  |  |  |  | 2.93
2018 |  |  |  | 3320.31 |  |  | 3714 |  |  |  | 910 | [10 empty] | 41.15 |  |  |  | 42.63 | [5 empty] | 41.65 |  |  | 42.40 |  |  |  | 1.19 |  | 11.55 | [8 empty] | 45.82 |  |  |  |  | 1.48
2019 |  |  |  | 6947.55 |  |  | 7703 |  |  |  | 910 | [10 empty] | 87.09 |  |  |  | 87.16 | [5 empty] | 87.15 |  |  | 87.93 |  |  |  | 1.39 |  | 3.38 | [8 empty] | 9.47 |  |  |  |  | 0.07
2020 |  |  |  | 4343.71 |  |  | 4881 |  |  |  | 910 | [10 empty] | 54.51 |  |  |  | 56.83 | [5 empty] | 54.34 |  |  | 55.57 |  |  |  | 3.90 |  | 16.86 | [8 empty] | 26.30 |  |  |  |  | 2.32
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 372
B. |  | Refuelling without maintenance | [35 empty] | 99
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 953 |  |  |  | 21
D. |  | Inspection, maintenance or repair without refuelling | [39 empty] | 15
E. |  | Testing of plant systems or components | [35 empty] | 8
H. |  | Nuclear regulatory requirements | [39 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 16 | [11 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 3 | [11 empty] | 10
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 25
Z. |  | Other | [39 empty] | 32 | [11 empty] | 1
Subtotal | [37 empty] | 1060 |  |  |  | 463 | [11 empty] | 40
Total | [22 empty] | 0 | [14 empty] | 1563
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 33
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 62
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 24
16. |  |  | Steam generation systems | [34 empty] | 5
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 58
32. |  |  | Feedwater and Main Steam System | [34 empty] | 18
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 95
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 15
42. |  |  | Electrical Power Supply Systems | [34 empty] | 37
Total | [37 empty] | 372

## NOGENT-1
2020 Operating Experience
FR-58 | [8 empty] | NOGENT-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-05-26
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-10-21
Gross electrical power | [12 empty] | : |  |  | 1363 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-02-24
Reference unit power (net) | [12 empty] | : |  |  | 1310 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.05
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9822.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.24 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.24 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.71 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.06 %
Load Factor (LF) | [18 empty] | : | 85.36 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.19 %
Operating Factor (OF) | [18 empty] | : | 99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 88 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 853.21 | 775.83 |  |  |  | 789.53 |  | 684.93 | [8 empty] | 630.48 |  |  | 714.18 | [6 empty] | 864.88 |  | 879.37 |  |  |  | 865.35 |  |  | 894.74 |  |  | 906.12 | [9 empty] | 963.64 |  |  | 9822.26
EAF [%] |  |  |  |  | 91.48 | 98.66 |  |  |  | 99.08 |  | 97.56 | [8 empty] | 99.16 |  |  | 90.49 | [6 empty] | 98.73 |  | 98.91 |  |  |  | 98.71 |  |  | 99.48 |  |  | 99.02 | [9 empty] | 98.89 |  |  | 97.52
UCF [%] |  |  |  |  | 92.65 | 99.67 |  |  |  | 99.18 |  | 97.75 | [8 empty] | 99.41 |  |  | 99.56 | [6 empty] | 99.30 |  | 99.59 |  |  |  | 99.41 |  |  | 99.69 |  |  | 99.27 | [9 empty] | 99.10 |  |  | 98.71
LF [%] |  |  |  |  | 87.54 | 85.09 |  |  |  | 81.12 |  | 72.62 | [8 empty] | 64.69 |  |  | 75.72 | [6 empty] | 88.74 |  | 90.23 |  |  |  | 91.75 |  |  | 91.68 |  |  | 96.07 | [9 empty] | 98.87 |  |  | 85.36
OF [%] |  |  |  |  | 96.10 | 100.00 |  |  |  | 100.00 |  | 98.89 | [8 empty] | 100.00 |  |  | 93.06 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.00
FLR [%] |  |  |  |  | 7.35 | 0.28 |  |  |  | 0.65 |  | 2.23 | [8 empty] | 0.55 |  |  | 0.44 | [6 empty] | 0.58 |  | 0.39 |  |  |  | 0.44 |  |  | 0.29 |  |  | 0.65 | [9 empty] | 0.87 |  |  | 1.24
UCL [%] |  |  |  |  | 7.35 | 0.28 |  |  |  | 0.65 |  | 2.23 | [8 empty] | 0.55 |  |  | 0.44 | [6 empty] | 0.58 |  | 0.39 |  |  |  | 0.44 |  |  | 0.29 |  |  | 0.65 | [9 empty] | 0.87 |  |  | 1.24
PUF [%] |  |  |  |  | 0.00 | 0.04 |  |  |  | 0.17 |  | 0.01 | [8 empty] | 0.03 |  |  | 0.00 | [6 empty] | 0.12 |  | 0.01 |  |  |  | 0.15 |  |  | 0.02 |  |  | 0.08 | [9 empty] | 0.04 |  |  | 0.06
XUF [%] |  |  |  |  | 1.17 | 1.01 |  |  |  | 0.10 |  | 0.19 | [8 empty] | 0.25 |  |  | 9.07 | [6 empty] | 0.57 |  | 0.68 |  |  |  | 0.71 |  |  | 0.21 |  |  | 0.25 | [9 empty] | 0.20 |  |  | 1.19
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 274715.98 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.47 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.57 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.64 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.6 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.76 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.39 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.74 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 7715.00 |  |  | 7324 |  |  |  | 1310 | [10 empty] | 86.78 |  |  |  | 87.76 | [5 empty] | 63.93 |  |  | 81.77 |  |  |  | 12.24 |  | 12.24 | [8 empty] | 0.00 |  |  |  |  | 0.98
1989 |  |  |  | 3172.66 |  |  | 2663 |  |  |  | 1310 | [10 empty] | 28.26 |  |  |  | 30.25 | [5 empty] | 27.65 |  |  | 30.40 |  |  |  | 57.21 |  | 40.43 | [8 empty] | 29.32 |  |  |  |  | 1.99
1990 |  |  |  | 6614.12 |  |  | 5590 |  |  |  | 1310 | [10 empty] | 67.54 |  |  |  | 67.68 | [5 empty] | 57.64 |  |  | 63.81 |  |  |  | 23.93 |  | 21.29 | [8 empty] | 11.03 |  |  |  |  | 0.14
1991 |  |  |  | 6868.61 |  |  | 5768 |  |  |  | 1310 | [10 empty] | 62.93 |  |  |  | 64.20 | [5 empty] | 59.85 |  |  | 65.84 |  |  |  | 12.05 |  | 8.79 | [8 empty] | 27.00 |  |  |  |  | 1.27
1992 |  |  |  | 7812.47 |  |  | 6386 |  |  |  | 1310 | [10 empty] | 70.41 |  |  |  | 71.52 | [5 empty] | 67.89 |  |  | 72.70 |  |  |  | 12.10 |  | 9.85 | [8 empty] | 18.63 |  |  |  |  | 1.10
1993 |  |  |  | 7705.63 |  |  | 6432 |  |  |  | 1310 | [10 empty] | 68.47 |  |  |  | 72.17 | [5 empty] | 67.15 |  |  | 73.42 |  |  |  | 16.38 |  | 14.14 | [8 empty] | 13.70 |  |  |  |  | 3.69
1994 |  |  |  | 8292.35 |  |  | 7429 |  |  |  | 1310 | [10 empty] | 80.05 |  |  |  | 83.16 | [5 empty] | 72.26 |  |  | 84.81 |  |  |  | 1.39 |  | 1.17 | [8 empty] | 15.67 |  |  |  |  | 3.11
1995 |  |  |  | 7358.33 |  |  | 6946 |  |  |  | 1310 | [10 empty] | 83.91 |  |  |  | 84.35 | [5 empty] | 64.12 |  |  | 79.29 |  |  |  | 15.64 |  | 15.63 | [8 empty] | 0.02 |  |  |  |  | 0.44
1996 |  |  |  | 8227.87 |  |  | 7222 |  |  |  | 1310 | [10 empty] | 79.58 |  |  |  | 81.08 | [5 empty] | 71.50 |  |  | 82.22 |  |  |  | 2.34 |  | 1.94 | [8 empty] | 16.98 |  |  |  |  | 1.50
1997 |  |  |  | 8571.62 |  |  | 7488 |  |  |  | 1310 | [10 empty] | 81.11 |  |  |  | 83.70 | [5 empty] | 74.69 |  |  | 85.48 |  |  |  | 3.33 |  | 2.89 | [8 empty] | 13.41 |  |  |  |  | 2.59
1998 |  |  |  | 6585.51 |  |  | 5334 |  |  |  | 1310 | [10 empty] | 57.17 |  |  |  | 59.18 | [5 empty] | 57.39 |  |  | 60.89 |  |  |  | 21.82 |  | 16.52 | [8 empty] | 24.30 |  |  |  |  | 2.01
1999 |  |  |  | 9704.97 |  |  | 8284 |  |  |  | 1310 | [10 empty] | 91.77 |  |  |  | 92.53 | [5 empty] | 84.57 |  |  | 94.57 |  |  |  | 5.53 |  | 5.42 | [8 empty] | 2.05 |  |  |  |  | 0.76
2000 |  |  |  | 9088.25 |  |  | 7626 |  |  |  | 1310 | [10 empty] | 83.03 |  |  |  | 85.17 | [5 empty] | 78.98 |  |  | 86.82 |  |  |  | 0.64 |  | 0.54 | [8 empty] | 14.28 |  |  |  |  | 2.15
2001 |  |  |  | 9142.69 |  |  | 7580 |  |  |  | 1310 | [10 empty] | 83.82 |  |  |  | 84.71 | [5 empty] | 79.67 |  |  | 86.53 |  |  |  | 1.51 |  | 1.30 | [8 empty] | 13.99 |  |  |  |  | 0.89
2002 |  |  |  | 9010.98 |  |  | 7738 |  |  |  | 1310 | [10 empty] | 87.13 |  |  |  | 87.25 | [5 empty] | 78.52 |  |  | 88.33 |  |  |  | 0.45 |  | 0.39 | [8 empty] | 12.36 |  |  |  |  | 0.12
2003 |  |  |  | 9974.35 |  |  | 8621 |  |  |  | 1310 | [10 empty] | 98.03 |  |  |  | 98.28 | [5 empty] | 86.92 |  |  | 98.41 |  |  |  | 1.11 |  | 1.10 | [8 empty] | 0.62 |  |  |  |  | 0.25
2004 |  |  |  | 8535.34 |  |  | 7152 |  |  |  | 1310 | [10 empty] | 77.82 |  |  |  | 80.97 | [5 empty] | 74.17 |  |  | 81.42 |  |  |  | 5.44 |  | 4.66 | [8 empty] | 14.37 |  |  |  |  | 3.15
2005 |  |  |  | 8534.36 |  |  | 6803 |  |  |  | 1310 | [10 empty] | 75.13 |  |  |  | 76.47 | [5 empty] | 74.37 |  |  | 77.66 |  |  |  | 0.72 |  | 2.46 | [8 empty] | 21.07 |  |  |  |  | 1.34
2006 |  |  |  | 9284.82 |  |  | 7331 |  |  |  | 1310 | [10 empty] | 82.89 |  |  |  | 82.89 | [5 empty] | 80.91 |  |  | 83.69 |  |  |  | 7.77 |  | 8.62 | [8 empty] | 8.49 |  |  |  |  | 0.00
2007 |  |  |  | 10831.76 |  |  | 8484 |  |  |  | 1310 | [10 empty] | 94.48 |  |  |  | 96.54 | [5 empty] | 94.39 |  |  | 96.85 |  |  |  | 3.37 |  | 3.37 | [8 empty] | 0.09 |  |  |  |  | 2.06
2008 |  |  |  | 8553.25 |  |  | 7052 |  |  |  | 1310 | [10 empty] | 74.93 |  |  |  | 77.96 | [5 empty] | 74.33 |  |  | 80.28 |  |  |  | 5.79 |  | 10.52 | [8 empty] | 11.52 |  |  |  |  | 3.03
2009 |  |  |  | 7308.98 |  |  | 5871 |  |  |  | 1310 | [10 empty] | 64.72 |  |  |  | 73.79 | [5 empty] | 63.69 |  |  | 67.02 |  |  |  | 1.07 |  | 2.16 | [8 empty] | 24.05 |  |  |  |  | 9.07
2010 |  |  |  | 10382.38 |  |  | 8482 |  |  |  | 1310 | [10 empty] | 96.38 |  |  |  | 97.19 | [5 empty] | 90.47 |  |  | 96.83 |  |  |  | 2.78 |  | 2.78 | [8 empty] | 0.03 |  |  |  |  | 0.81
2011 |  |  |  | 9001.39 |  |  | 7562 |  |  |  | 1310 | [10 empty] | 84.76 |  |  |  | 86.91 | [5 empty] | 78.44 |  |  | 86.32 |  |  |  | 2.50 |  | 5.14 | [8 empty] | 7.95 |  |  |  |  | 2.15
2012 |  |  |  | 6456.97 |  |  | 5429 |  |  |  | 1310 | [10 empty] | 57.68 |  |  |  | 60.02 | [5 empty] | 56.11 |  |  | 61.81 |  |  |  | 4.10 |  | 25.93 | [8 empty] | 14.05 |  |  |  |  | 2.34
2013 |  |  |  | 9487.59 |  |  | 8116 |  |  |  | 1310 | [10 empty] | 92.95 |  |  |  | 99.38 | [5 empty] | 82.68 |  |  | 92.65 |  |  |  | 0.59 |  | 0.59 | [8 empty] | 0.03 |  |  |  |  | 6.43
2014 |  |  |  | 8980.03 |  |  | 7826 |  |  |  | 1310 | [10 empty] | 83.31 |  |  |  | 88.17 | [5 empty] | 78.25 |  |  | 89.34 |  |  |  | 0.75 |  | 1.08 | [8 empty] | 10.75 |  |  |  |  | 4.86
2015 |  |  |  | 8678.84 |  |  | 6948 |  |  |  | 1310 | [10 empty] | 77.18 |  |  |  | 77.21 | [5 empty] | 75.63 |  |  | 79.32 |  |  |  | 1.01 |  | 2.01 | [8 empty] | 20.78 |  |  |  |  | 0.02
2016 |  |  |  | 9891.23 |  |  | 7916 |  |  |  | 1310 | [10 empty] | 86.86 |  |  |  | 87.29 | [5 empty] | 85.96 |  |  | 90.12 |  |  |  | 1.54 |  | 2.58 | [8 empty] | 10.13 |  |  |  |  | 0.43
2017 |  |  |  | 9040.03 |  |  | 7190 |  |  |  | 1310 | [10 empty] | 79.92 |  |  |  | 80.83 | [5 empty] | 78.78 |  |  | 82.08 |  |  |  | 0.54 |  | 0.44 | [8 empty] | 18.73 |  |  |  |  | 0.91
2018 |  |  |  | 7865.33 |  |  | 6508 |  |  |  | 1310 | [10 empty] | 69.43 |  |  |  | 74.96 | [5 empty] | 68.54 |  |  | 74.29 |  |  |  | 25.00 |  | 24.98 | [8 empty] | 0.06 |  |  |  |  | 5.53
2019 |  |  |  | 6030.72 |  |  | 5050 |  |  |  | 1310 | [10 empty] | 55.31 |  |  |  | 55.96 | [5 empty] | 52.55 |  |  | 57.65 |  |  |  | 0.93 |  | 0.53 | [8 empty] | 43.51 |  |  |  |  | 0.66
2020 |  |  |  | 9822.26 |  |  | 8696 |  |  |  | 1310 | [10 empty] | 97.52 |  |  |  | 98.71 | [5 empty] | 85.36 |  |  | 99.00 |  |  |  | 1.24 |  | 1.24 | [8 empty] | 0.06 |  |  |  |  | 1.19
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 502
B. |  | Refuelling without maintenance | [35 empty] | 50
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 970 |  |  |  | 1
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 53
E. |  | Testing of plant systems or components | [35 empty] | 47 | [15 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 10
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 45 | [11 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 36
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 19
Z. |  | Other | [39 empty] | 6 | [11 empty] | 2
Subtotal | [37 empty] | 1120 |  |  |  | 564 | [11 empty] | 61
Total | [22 empty] | 0 | [14 empty] | 1745
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 50
12. |  |  | Reactor I&C Systems | [34 empty] | 95
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 19
16. |  |  | Steam generation systems | [34 empty] | 78
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 10
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 6
31. |  |  | Turbine and auxiliaries | [34 empty] | 47
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
33. |  |  | Circulating Water System | [34 empty] | 51
34. |  |  | Miscellaneous Systems | [34 empty] | 22
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 83
42. |  |  | Electrical Power Supply Systems | [34 empty] | 17
Total | [37 empty] | 498

## NOGENT-2
2020 Operating Experience
FR-59 | [8 empty] | NOGENT-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-01-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-12-14
Gross electrical power | [12 empty] | : |  |  | 1363 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-05-01
Reference unit power (net) | [12 empty] | : |  |  | 1310 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5223.23 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.12 %
Energy Availability Factor (EAF) | [18 empty] | : | 48 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.36 %
Unit Capability Factor (UCF) | [18 empty] | : | 54.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 42.82 %
Load Factor (LF) | [18 empty] | : | 45.39 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 6.82 %
Operating Factor (OF) | [18 empty] | : | 50.71 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4330 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 856.02 | 204.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 649.01 |  |  |  | 861.13 |  |  | 877.00 |  |  | 869.26 | [9 empty] | 906.79 |  |  | 5223.23
EAF [%] |  |  |  |  | 87.84 | 23.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 70.94 |  |  |  | 97.54 |  |  | 95.36 |  |  | 99.75 | [9 empty] | 99.63 |  |  | 48.00
UCF [%] |  |  |  |  | 100.00 | 28.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 45.03 |  | 87.47 |  |  |  | 98.37 |  |  | 95.96 |  |  | 99.90 | [9 empty] | 99.88 |  |  | 54.82
LF [%] |  |  |  |  | 87.83 | 22.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 66.59 |  |  |  | 91.30 |  |  | 89.86 |  |  | 92.16 | [9 empty] | 93.04 |  |  | 45.39
OF [%] |  |  |  |  | 100.00 | 28.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 83.47 |  |  |  | 99.17 |  |  | 95.97 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 50.71
FLR [%] |  |  |  |  | 0.00 | 40.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 4.51 |  |  |  | 1.54 |  |  | 3.98 |  |  | 0.05 | [9 empty] | 0.12 |  |  | 4.12
UCL [%] |  |  |  |  | 0.00 | 19.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 4.13 |  |  |  | 1.54 |  |  | 3.98 |  |  | 0.05 | [9 empty] | 0.12 |  |  | 2.36
PUF [%] |  |  |  |  | 0.00 | 51.94 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 54.97 |  | 8.40 |  |  |  | 0.09 |  |  | 0.06 |  |  | 0.05 | [9 empty] | 0.01 |  |  | 42.82
XUF [%] |  |  |  |  | 12.16 | 5.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 45.02 |  | 16.53 |  |  |  | 0.83 |  |  | 0.60 |  |  | 0.15 | [9 empty] | 0.25 |  |  | 6.82
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 272174.42 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.1 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.95 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.26 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.4 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.29 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.83 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 7470.05 |  |  | 6660 |  |  |  | 1310 | [10 empty] | 78.93 |  |  |  | 78.94 | [5 empty] | 72.84 |  |  | 80.67 |  |  |  | 21.06 |  | 21.05 | [8 empty] | 0.01 |  |  |  |  | 0.01
1990 |  |  |  | 7532.95 |  |  | 6094 |  |  |  | 1310 | [10 empty] | 68.29 |  |  |  | 69.37 | [5 empty] | 65.64 |  |  | 69.57 |  |  |  | 3.95 |  | 2.85 | [8 empty] | 27.78 |  |  |  |  | 1.07
1991 |  |  |  | 8331.15 |  |  | 7008 |  |  |  | 1310 | [10 empty] | 73.49 |  |  |  | 78.80 | [5 empty] | 72.60 |  |  | 80.00 |  |  |  | 7.15 |  | 6.07 | [8 empty] | 15.12 |  |  |  |  | 5.31
1992 |  |  |  | 8312.33 |  |  | 6937 |  |  |  | 1310 | [10 empty] | 74.10 |  |  |  | 77.44 | [5 empty] | 72.24 |  |  | 78.97 |  |  |  | 5.17 |  | 4.22 | [8 empty] | 18.34 |  |  |  |  | 3.34
1993 |  |  |  | 9191.68 |  |  | 7594 |  |  |  | 1310 | [10 empty] | 80.77 |  |  |  | 85.85 | [5 empty] | 80.10 |  |  | 86.69 |  |  |  | 1.34 |  | 1.17 | [8 empty] | 12.98 |  |  |  |  | 5.08
1994 |  |  |  | 6483.02 |  |  | 6027 |  |  |  | 1310 | [10 empty] | 94.82 |  |  |  | 98.01 | [5 empty] | 56.49 |  |  | 68.80 |  |  |  | 1.95 |  | 1.95 | [8 empty] | 0.05 |  |  |  |  | 3.19
1995 |  |  |  | 7545.41 |  |  | 6862 |  |  |  | 1310 | [10 empty] | 75.87 |  |  |  | 78.45 | [5 empty] | 65.75 |  |  | 78.33 |  |  |  | 9.48 |  | 8.22 | [8 empty] | 13.33 |  |  |  |  | 2.58
1996 |  |  |  | 8477.02 |  |  | 7229 |  |  |  | 1310 | [10 empty] | 76.95 |  |  |  | 80.52 | [5 empty] | 73.67 |  |  | 82.30 |  |  |  | 5.35 |  | 4.55 | [8 empty] | 14.93 |  |  |  |  | 3.57
1997 |  |  |  | 8925.81 |  |  | 7656 |  |  |  | 1310 | [10 empty] | 81.96 |  |  |  | 85.98 | [5 empty] | 77.78 |  |  | 87.40 |  |  |  | 1.49 |  | 1.30 | [8 empty] | 12.72 |  |  |  |  | 4.02
1998 |  |  |  | 8830.03 |  |  | 7386 |  |  |  | 1310 | [10 empty] | 97.77 |  |  |  | 98.00 | [5 empty] | 76.95 |  |  | 84.32 |  |  |  | 1.67 |  | 1.67 | [8 empty] | 0.33 |  |  |  |  | 0.23
1999 |  |  |  | 7957.34 |  |  | 6732 |  |  |  | 1310 | [10 empty] | 74.70 |  |  |  | 76.24 | [5 empty] | 69.34 |  |  | 76.85 |  |  |  | 0.52 |  | 0.40 | [8 empty] | 23.37 |  |  |  |  | 1.54
2000 |  |  |  | 9672.12 |  |  | 7654 |  |  |  | 1310 | [10 empty] | 84.62 |  |  |  | 85.92 | [5 empty] | 84.05 |  |  | 87.14 |  |  |  | 0.69 |  | 0.60 | [8 empty] | 13.48 |  |  |  |  | 1.31
2001 |  |  |  | 9378.95 |  |  | 7589 |  |  |  | 1310 | [10 empty] | 83.40 |  |  |  | 85.15 | [5 empty] | 81.73 |  |  | 86.63 |  |  |  | 0.97 |  | 0.83 | [8 empty] | 14.02 |  |  |  |  | 1.74
2002 |  |  |  | 8205.53 |  |  | 7241 |  |  |  | 1310 | [10 empty] | 84.15 |  |  |  | 84.17 | [5 empty] | 71.50 |  |  | 82.66 |  |  |  | 5.01 |  | 4.44 | [8 empty] | 11.39 |  |  |  |  | 0.02
2003 |  |  |  | 9447.11 |  |  | 7954 |  |  |  | 1310 | [10 empty] | 91.51 |  |  |  | 91.53 | [5 empty] | 82.32 |  |  | 90.80 |  |  |  | 2.07 |  | 1.93 | [8 empty] | 6.54 |  |  |  |  | 0.02
2004 |  |  |  | 8216.70 |  |  | 7044 |  |  |  | 1310 | [10 empty] | 75.14 |  |  |  | 78.65 | [5 empty] | 71.41 |  |  | 80.19 |  |  |  | 9.24 |  | 8.01 | [8 empty] | 13.34 |  |  |  |  | 3.51
2005 |  |  |  | 8393.26 |  |  | 6907 |  |  |  | 1310 | [10 empty] | 76.14 |  |  |  | 77.20 | [5 empty] | 73.14 |  |  | 78.85 |  |  |  | 5.27 |  | 4.30 | [8 empty] | 18.50 |  |  |  |  | 1.06
2006 |  |  |  | 10046.50 |  |  | 7854 |  |  |  | 1310 | [10 empty] | 89.52 |  |  |  | 89.52 | [5 empty] | 87.55 |  |  | 89.66 |  |  |  | 10.45 |  | 10.45 | [8 empty] | 0.04 |  |  |  |  | 0.00
2007 |  |  |  | 9885.89 |  |  | 7918 |  |  |  | 1310 | [10 empty] | 86.86 |  |  |  | 89.52 | [5 empty] | 86.15 |  |  | 90.39 |  |  |  | 1.09 |  | 2.19 | [8 empty] | 8.29 |  |  |  |  | 2.67
2008 |  |  |  | 7594.22 |  |  | 6175 |  |  |  | 1310 | [10 empty] | 67.01 |  |  |  | 68.79 | [5 empty] | 66.00 |  |  | 70.30 |  |  |  | 1.40 |  | 20.02 | [8 empty] | 11.18 |  |  |  |  | 1.79
2009 |  |  |  | 7156.37 |  |  | 6227 |  |  |  | 1310 | [10 empty] | 66.02 |  |  |  | 67.32 | [5 empty] | 62.36 |  |  | 71.08 |  |  |  | 32.67 |  | 32.66 | [8 empty] | 0.01 |  |  |  |  | 1.30
2010 |  |  |  | 8055.24 |  |  | 6576 |  |  |  | 1310 | [10 empty] | 73.65 |  |  |  | 73.69 | [5 empty] | 70.19 |  |  | 75.07 |  |  |  | 1.92 |  | 1.45 | [8 empty] | 24.87 |  |  |  |  | 0.04
2011 |  |  |  | 9424.39 |  |  | 7468 |  |  |  | 1310 | [10 empty] | 84.47 |  |  |  | 84.67 | [5 empty] | 82.13 |  |  | 85.25 |  |  |  | 0.24 |  | 6.03 | [8 empty] | 9.30 |  |  |  |  | 0.20
2012 |  |  |  | 9853.20 |  |  | 7964 |  |  |  | 1310 | [10 empty] | 89.02 |  |  |  | 91.21 | [5 empty] | 85.63 |  |  | 90.66 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 8.77 |  |  |  |  | 2.19
2013 |  |  |  | 9161.96 |  |  | 7595 |  |  |  | 1310 | [10 empty] | 85.62 |  |  |  | 86.80 | [5 empty] | 79.84 |  |  | 86.70 |  |  |  | 1.87 |  | 6.70 | [8 empty] | 6.50 |  |  |  |  | 1.19
2014 |  |  |  | 7715.38 |  |  | 6584 |  |  |  | 1310 | [10 empty] | 84.99 |  |  |  | 84.99 | [5 empty] | 67.23 |  |  | 75.16 |  |  |  | 2.73 |  | 4.61 | [8 empty] | 10.40 |  |  |  |  | 0.00
2015 |  |  |  | 7148.17 |  |  | 5730 |  |  |  | 1310 | [10 empty] | 64.79 |  |  |  | 64.79 | [5 empty] | 62.29 |  |  | 65.41 |  |  |  | 19.00 |  | 15.20 | [8 empty] | 20.01 |  |  |  |  | 0.00
2016 |  |  |  | 10673.55 |  |  | 8665 |  |  |  | 1310 | [10 empty] | 96.88 |  |  |  | 98.45 | [5 empty] | 92.76 |  |  | 98.65 |  |  |  | 0.97 |  | 0.96 | [8 empty] | 0.59 |  |  |  |  | 1.57
2017 |  |  |  | 9933.24 |  |  | 7797 |  |  |  | 1310 | [10 empty] | 86.90 |  |  |  | 88.39 | [5 empty] | 86.56 |  |  | 89.01 |  |  |  | 0.98 |  | 1.86 | [8 empty] | 9.75 |  |  |  |  | 1.49
2018 |  |  |  | 8618.65 |  |  | 6984 |  |  |  | 1310 | [10 empty] | 75.45 |  |  |  | 78.64 | [5 empty] | 75.10 |  |  | 79.73 |  |  |  | 2.24 |  | 1.80 | [8 empty] | 19.56 |  |  |  |  | 3.18
2019 |  |  |  | 9599.33 |  |  | 7762 |  |  |  | 1310 | [10 empty] | 86.29 |  |  |  | 98.63 | [5 empty] | 83.65 |  |  | 88.61 |  |  |  | 1.34 |  | 1.34 | [8 empty] | 0.03 |  |  |  |  | 12.34
2020 |  |  |  | 5223.23 |  |  | 4454 |  |  |  | 1310 | [10 empty] | 48.00 |  |  |  | 54.82 | [5 empty] | 45.39 |  |  | 50.71 |  |  |  | 4.12 |  | 2.36 | [8 empty] | 42.82 |  |  |  |  | 6.82
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 396
B. |  | Refuelling without maintenance | [35 empty] | 50
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 822
E. |  | Testing of plant systems or components | [35 empty] | 25
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 31
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 6
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 28
Z. |  | Other | [39 empty] | 35
Subtotal | [37 empty] | 897 |  |  |  | 439 | [11 empty] | 70
Total | [22 empty] | 0 | [14 empty] | 1406
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 28
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 24
15. |  |  | Reactor Cooling Systems | [34 empty] | 20
16. |  |  | Steam generation systems | [34 empty] | 28
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 56
31. |  |  | Turbine and auxiliaries | [34 empty] | 18
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 27
34. |  |  | Miscellaneous Systems | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 10
41. |  |  | Main Generator Systems | [34 empty] | 138
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [37 empty] | 392

## PALUEL-1
2020 Operating Experience
FR-36 | [8 empty] | PALUEL-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-08-15
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-06-22
Gross electrical power | [12 empty] | : |  |  | 1382 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-12-01
Reference unit power (net) | [12 empty] | : |  |  | 1330 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.2
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9093.82 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.82 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.47 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.81 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.09 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.09 %
Load Factor (LF) | [18 empty] | : | 77.84 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 11.62 %
Operating Factor (OF) | [18 empty] | : | 87.8 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1072 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 782.02 | 754.22 |  |  |  | 833.33 |  | 236.10 | [8 empty] | 266.09 |  |  | 796.30 | [6 empty] | 872.01 |  | 889.27 |  |  |  | 875.74 |  |  | 937.11 |  |  | 904.50 | [9 empty] | 947.11 |  |  | 9093.82
EAF [%] |  |  |  |  | 79.91 | 95.41 |  |  |  | 99.64 |  | 33.09 | [8 empty] | 45.14 |  |  | 91.23 | [6 empty] | 96.09 |  | 98.28 |  |  |  | 97.95 |  |  | 96.06 |  |  | 95.70 | [9 empty] | 97.05 |  |  | 85.47
UCF [%] |  |  |  |  | 91.85 | 96.31 |  |  |  | 99.64 |  | 99.95 | [8 empty] | 99.22 |  |  | 91.93 | [6 empty] | 97.63 |  | 99.16 |  |  |  | 98.64 |  |  | 97.01 |  |  | 96.44 | [9 empty] | 97.23 |  |  | 97.09
LF [%] |  |  |  |  | 79.03 | 81.48 |  |  |  | 84.33 |  | 24.66 | [8 empty] | 26.89 |  |  | 83.16 | [6 empty] | 88.12 |  | 89.87 |  |  |  | 91.45 |  |  | 94.58 |  |  | 94.45 | [9 empty] | 95.71 |  |  | 77.84
OF [%] |  |  |  |  | 83.47 | 95.98 |  |  |  | 100.00 |  | 33.33 | [8 empty] | 46.24 |  |  | 94.44 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.80
FLR [%] |  |  |  |  | 7.60 | 3.69 |  |  |  | 0.31 |  | 0.05 | [8 empty] | 0.60 |  |  | 8.07 | [6 empty] | 2.34 |  | 0.84 |  |  |  | 1.36 |  |  | 2.99 |  |  | 3.44 | [9 empty] | 2.64 |  |  | 2.82
UCL [%] |  |  |  |  | 7.55 | 3.69 |  |  |  | 0.31 |  | 0.05 | [8 empty] | 0.60 |  |  | 8.07 | [6 empty] | 2.34 |  | 0.84 |  |  |  | 1.36 |  |  | 2.99 |  |  | 3.43 | [9 empty] | 2.64 |  |  | 2.81
PUF [%] |  |  |  |  | 0.59 | 0.00 |  |  |  | 0.05 |  | 0.00 | [8 empty] | 0.19 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.13 | [9 empty] | 0.12 |  |  | 0.09
XUF [%] |  |  |  |  | 11.94 | 0.90 |  |  |  | 0.00 |  | 66.86 | [8 empty] | 54.08 |  |  | 0.70 | [6 empty] | 1.54 |  | 0.88 |  |  |  | 0.69 |  |  | 0.95 |  |  | 0.74 | [9 empty] | 0.18 |  |  | 11.62
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 295183.27 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.26 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.31 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.85 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.96 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.69 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.03 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4685.80 |  |  | 4104 |  |  |  | 1290 | [10 empty] | 94.92 |  |  |  | 94.92 | [5 empty] | 98.72 |  |  | 98.25 |  |  |  | 5.08 |  | 5.08 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 5169.70 |  |  | 4455 |  |  |  | 1290 | [10 empty] | 50.23 |  |  |  | 52.32 | [5 empty] | 45.75 |  |  | 50.86 |  |  |  | 26.61 |  | 18.97 | [8 empty] | 28.71 |  |  |  |  | 2.09
1987 |  |  |  | 8184.80 |  |  | 6527 |  |  |  | 1330 | [10 empty] | 76.58 |  |  |  | 76.96 | [5 empty] | 70.25 |  |  | 74.51 |  |  |  | 7.69 |  | 6.41 | [8 empty] | 16.63 |  |  |  |  | 0.38
1988 |  |  |  | 9291.00 |  |  | 7332 |  |  |  | 1330 | [10 empty] | 95.28 |  |  |  | 96.82 | [5 empty] | 79.53 |  |  | 83.47 |  |  |  | 3.13 |  | 3.12 | [8 empty] | 0.05 |  |  |  |  | 1.55
1989 |  |  |  | 7902.78 |  |  | 6567 |  |  |  | 1330 | [10 empty] | 70.38 |  |  |  | 72.57 | [5 empty] | 67.83 |  |  | 74.97 |  |  |  | 9.49 |  | 7.61 | [8 empty] | 19.82 |  |  |  |  | 2.19
1990 |  |  |  | 7323.87 |  |  | 6288 |  |  |  | 1330 | [10 empty] | 66.40 |  |  |  | 70.07 | [5 empty] | 62.86 |  |  | 71.78 |  |  |  | 15.18 |  | 12.54 | [8 empty] | 17.39 |  |  |  |  | 3.67
1991 |  |  |  | 7159.94 |  |  | 5987 |  |  |  | 1330 | [10 empty] | 63.19 |  |  |  | 66.65 | [5 empty] | 61.45 |  |  | 68.34 |  |  |  | 13.16 |  | 10.10 | [8 empty] | 23.25 |  |  |  |  | 3.47
1992 |  |  |  | 8640.41 |  |  | 6858 |  |  |  | 1330 | [10 empty] | 76.61 |  |  |  | 76.62 | [5 empty] | 73.96 |  |  | 78.07 |  |  |  | 5.82 |  | 4.74 | [8 empty] | 18.65 |  |  |  |  | 0.01
1993 |  |  |  | 8068.09 |  |  | 6906 |  |  |  | 1330 | [10 empty] | 70.88 |  |  |  | 77.24 | [5 empty] | 69.25 |  |  | 78.84 |  |  |  | 4.94 |  | 4.02 | [8 empty] | 18.74 |  |  |  |  | 6.36
1994 |  |  |  | 6549.93 |  |  | 5790 |  |  |  | 1330 | [10 empty] | 76.95 |  |  |  | 77.10 | [5 empty] | 56.22 |  |  | 66.10 |  |  |  | 22.88 |  | 22.88 | [8 empty] | 0.02 |  |  |  |  | 0.15
1995 |  |  |  | 8768.17 |  |  | 7292 |  |  |  | 1330 | [10 empty] | 79.61 |  |  |  | 82.18 | [5 empty] | 75.26 |  |  | 83.24 |  |  |  | 4.24 |  | 3.64 | [8 empty] | 14.18 |  |  |  |  | 2.58
1996 |  |  |  | 5483.15 |  |  | 4763 |  |  |  | 1330 | [10 empty] | 48.69 |  |  |  | 52.72 | [5 empty] | 46.93 |  |  | 54.22 |  |  |  | 26.24 |  | 18.76 | [8 empty] | 28.52 |  |  |  |  | 4.04
1997 |  |  |  | 9019.66 |  |  | 7537 |  |  |  | 1330 | [10 empty] | 83.76 |  |  |  | 84.49 | [5 empty] | 77.42 |  |  | 86.04 |  |  |  | 5.67 |  | 5.08 | [8 empty] | 10.43 |  |  |  |  | 0.72
1998 |  |  |  | 9718.11 |  |  | 8132 |  |  |  | 1330 | [10 empty] | 91.25 |  |  |  | 91.28 | [5 empty] | 83.41 |  |  | 92.83 |  |  |  | 5.26 |  | 5.07 | [8 empty] | 3.65 |  |  |  |  | 0.03
1999 |  |  |  | 8181.87 |  |  | 6938 |  |  |  | 1330 | [10 empty] | 76.15 |  |  |  | 78.56 | [5 empty] | 70.23 |  |  | 79.20 |  |  |  | 4.32 |  | 3.55 | [8 empty] | 17.89 |  |  |  |  | 2.41
2000 |  |  |  | 9088.99 |  |  | 7533 |  |  |  | 1330 | [10 empty] | 83.48 |  |  |  | 83.97 | [5 empty] | 77.80 |  |  | 85.76 |  |  |  | 2.13 |  | 1.83 | [8 empty] | 14.20 |  |  |  |  | 0.49
2001 |  |  |  | 9752.15 |  |  | 8382 |  |  |  | 1330 | [10 empty] | 97.58 |  |  |  | 98.29 | [5 empty] | 83.70 |  |  | 95.68 |  |  |  | 1.51 |  | 1.51 | [8 empty] | 0.20 |  |  |  |  | 0.72
2002 |  |  |  | 7153.91 |  |  | 6081 |  |  |  | 1330 | [10 empty] | 66.55 |  |  |  | 68.27 | [5 empty] | 61.40 |  |  | 69.42 |  |  |  | 12.86 |  | 10.07 | [8 empty] | 21.66 |  |  |  |  | 1.72
2003 |  |  |  | 8526.18 |  |  | 6882 |  |  |  | 1330 | [10 empty] | 77.18 |  |  |  | 77.59 | [5 empty] | 73.18 |  |  | 78.56 |  |  |  | 11.48 |  | 10.06 | [8 empty] | 12.35 |  |  |  |  | 0.41
2004 |  |  |  | 8596.32 |  |  | 7103 |  |  |  | 1330 | [10 empty] | 77.37 |  |  |  | 79.37 | [5 empty] | 73.58 |  |  | 80.86 |  |  |  | 5.53 |  | 4.64 | [8 empty] | 15.99 |  |  |  |  | 1.99
2005 |  |  |  | 10565.55 |  |  | 8654 |  |  |  | 1330 | [10 empty] | 97.86 |  |  |  | 98.39 | [5 empty] | 90.69 |  |  | 98.79 |  |  |  | 1.49 |  | 1.49 | [8 empty] | 0.12 |  |  |  |  | 0.53
2006 |  |  |  | 7437.70 |  |  | 6133 |  |  |  | 1330 | [10 empty] | 65.98 |  |  |  | 68.61 | [5 empty] | 63.84 |  |  | 70.01 |  |  |  | 1.80 |  | 2.61 | [8 empty] | 28.79 |  |  |  |  | 2.63
2007 |  |  |  | 8135.11 |  |  | 6641 |  |  |  | 1330 | [10 empty] | 73.26 |  |  |  | 75.11 | [5 empty] | 69.82 |  |  | 75.81 |  |  |  | 3.73 |  | 9.76 | [8 empty] | 15.13 |  |  |  |  | 1.84
2008 |  |  |  | 9808.67 |  |  | 8116 |  |  |  | 1330 | [10 empty] | 90.35 |  |  |  | 91.10 | [5 empty] | 83.96 |  |  | 92.40 |  |  |  | 2.16 |  | 8.06 | [8 empty] | 0.84 |  |  |  |  | 0.75
2009 |  |  |  | 7469.32 |  |  | 6108 |  |  |  | 1330 | [10 empty] | 66.51 |  |  |  | 86.13 | [5 empty] | 64.11 |  |  | 69.73 |  |  |  | 1.75 |  | 6.06 | [8 empty] | 7.81 |  |  |  |  | 19.61
2010 |  |  |  | 8295.24 |  |  | 6661 |  |  |  | 1330 | [10 empty] | 74.55 |  |  |  | 77.25 | [5 empty] | 71.20 |  |  | 76.04 |  |  |  | 0.75 |  | 7.55 | [8 empty] | 15.20 |  |  |  |  | 2.70
2011 |  |  |  | 10184.08 |  |  | 8349 |  |  |  | 1330 | [10 empty] | 94.32 |  |  |  | 94.98 | [5 empty] | 87.41 |  |  | 95.31 |  |  |  | 1.04 |  | 1.00 | [8 empty] | 4.02 |  |  |  |  | 0.66
2012 |  |  |  | 9140.88 |  |  | 7351 |  |  |  | 1330 | [10 empty] | 80.57 |  |  |  | 82.60 | [5 empty] | 78.24 |  |  | 83.69 |  |  |  | 4.02 |  | 9.04 | [8 empty] | 8.36 |  |  |  |  | 2.03
2013 |  |  |  | 7888.06 |  |  | 6203 |  |  |  | 1330 | [10 empty] | 69.21 |  |  |  | 70.62 | [5 empty] | 67.70 |  |  | 70.81 |  |  |  | 0.12 |  | 9.95 | [8 empty] | 19.43 |  |  |  |  | 1.41
2014 |  |  |  | 9615.90 |  |  | 7567 |  |  |  | 1330 | [10 empty] | 84.41 |  |  |  | 85.21 | [5 empty] | 82.53 |  |  | 86.38 |  |  |  | 4.29 |  | 4.98 | [8 empty] | 9.82 |  |  |  |  | 0.79
2015 |  |  |  | 9949.97 |  |  | 8222 |  |  |  | 1330 | [10 empty] | 93.87 |  |  |  | 99.04 | [5 empty] | 85.40 |  |  | 93.86 |  |  |  | 0.91 |  | 0.91 | [8 empty] | 0.05 |  |  |  |  | 5.17
2016 |  |  |  | 4050.04 |  |  | 3503 |  |  |  | 1330 | [10 empty] | 35.15 |  |  |  | 37.84 | [5 empty] | 34.67 |  |  | 39.88 |  |  |  | 4.48 |  | 23.46 | [8 empty] | 38.70 |  |  |  |  | 2.70
2017 |  |  |  | 10013.99 |  |  | 8379 |  |  |  | 1330 | [10 empty] | 94.17 |  |  |  | 98.22 | [5 empty] | 85.95 |  |  | 95.65 |  |  |  | 1.71 |  | 1.71 | [8 empty] | 0.07 |  |  |  |  | 4.05
2018 |  |  |  | 8993.47 |  |  | 7597 |  |  |  | 1330 | [10 empty] | 83.95 |  |  |  | 85.74 | [5 empty] | 77.19 |  |  | 86.72 |  |  |  | 3.08 |  | 4.15 | [8 empty] | 10.11 |  |  |  |  | 1.79
2019 |  |  |  | 5834.12 |  |  | 4711 |  |  |  | 1330 | [10 empty] | 50.93 |  |  |  | 51.95 | [5 empty] | 50.07 |  |  | 53.78 |  |  |  | 4.45 |  | 27.16 | [8 empty] | 20.89 |  |  |  |  | 1.03
2020 |  |  |  | 9093.82 |  |  | 7712 |  |  |  | 1330 | [10 empty] | 85.47 |  |  |  | 97.09 | [5 empty] | 77.84 |  |  | 87.80 |  |  |  | 2.82 |  | 2.81 | [8 empty] | 0.09 |  |  |  |  | 11.62
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 484 | [11 empty] | 2
B. |  | Refuelling without maintenance | [35 empty] | 65
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 992 |  |  |  | 40
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 103
E. |  | Testing of plant systems or components | [35 empty] | 19 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 10
H. |  | Nuclear regulatory requirements | [39 empty] | 11
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 32
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 57
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 23
Z. |  | Other | [39 empty] | 66
Subtotal | [37 empty] | 1189 |  |  |  | 634 | [11 empty] | 86
Total | [22 empty] | 0 | [14 empty] | 1909
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 38
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 27
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 10
16. |  |  | Steam generation systems | [34 empty] | 15
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 38
32. |  |  | Feedwater and Main Steam System | [34 empty] | 27
33. |  |  | Circulating Water System | [34 empty] | 14
34. |  |  | Miscellaneous Systems | [34 empty] | 161
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 94
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [37 empty] | 469

## PALUEL-2
2020 Operating Experience
FR-37 | [8 empty] | PALUEL-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-01-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-09-14
Gross electrical power | [12 empty] | : |  |  | 1382 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-12-01
Reference unit power (net) | [12 empty] | : |  |  | 1330 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.2
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0.06 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 93.81 %
Unit Capability Factor (UCF) | [18 empty] | : | 6.19 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 6.13 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.06 | 0.05 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 0.06 |  |  | 0.03 | [6 empty] | 0.04 |  | 0.06 |  |  |  | 0.07 |  |  | 0.06 |  |  | 0.06 | [9 empty] | 0.07 |  |  | 0.06
UCF [%] |  |  |  |  | 0.06 | 0.05 |  |  |  | 20.91 |  | 53.35 | [8 empty] | 0.06 |  |  | 0.03 | [6 empty] | 0.04 |  | 0.06 |  |  |  | 0.07 |  |  | 0.06 |  |  | 0.06 | [9 empty] | 0.07 |  |  | 6.19
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 99.94 | 99.95 |  |  |  | 79.09 |  | 46.65 | [8 empty] | 99.94 |  |  | 99.97 | [6 empty] | 99.96 |  | 99.94 |  |  |  | 99.93 |  |  | 99.94 |  |  | 99.94 | [9 empty] | 99.93 |  |  | 93.81
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 20.84 |  | 53.29 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.13
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 260010.28 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.04 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 66.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 17.62 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 68.89 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.49 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 62.27 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.96 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 69 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 5997.80 |  |  | 5548 |  |  |  | 1290 | [10 empty] | 99.64 |  |  |  | 99.64 | [5 empty] | 103.20 |  |  | 100.00 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 6040.90 |  |  | 4804 |  |  |  | 1290 | [10 empty] | 52.22 |  |  |  | 52.33 | [5 empty] | 53.46 |  |  | 54.84 |  |  |  | 19.74 |  | 12.87 | [8 empty] | 34.80 |  |  |  |  | 0.12
1987 |  |  |  | 8859.60 |  |  | 6837 |  |  |  | 1290 | [10 empty] | 76.84 |  |  |  | 77.30 | [5 empty] | 78.40 |  |  | 78.05 |  |  |  | 8.19 |  | 6.90 | [8 empty] | 15.80 |  |  |  |  | 0.46
1988 |  |  |  | 7725.00 |  |  | 6017 |  |  |  | 1330 | [10 empty] | 73.49 |  |  |  | 75.49 | [5 empty] | 66.12 |  |  | 68.50 |  |  |  | 6.03 |  | 4.84 | [8 empty] | 19.66 |  |  |  |  | 2.00
1989 |  |  |  | 8956.44 |  |  | 7358 |  |  |  | 1330 | [10 empty] | 80.09 |  |  |  | 83.35 | [5 empty] | 76.87 |  |  | 84.00 |  |  |  | 12.29 |  | 11.68 | [8 empty] | 4.96 |  |  |  |  | 3.26
1990 |  |  |  | 6496.27 |  |  | 5328 |  |  |  | 1330 | [10 empty] | 59.05 |  |  |  | 59.09 | [5 empty] | 55.76 |  |  | 60.82 |  |  |  | 20.84 |  | 15.56 | [8 empty] | 25.35 |  |  |  |  | 0.04
1991 |  |  |  | 6140.31 |  |  | 4996 |  |  |  | 1330 | [10 empty] | 54.92 |  |  |  | 55.13 | [5 empty] | 52.70 |  |  | 57.03 |  |  |  | 28.23 |  | 21.68 | [8 empty] | 23.19 |  |  |  |  | 0.21
1992 |  |  |  | 6906.92 |  |  | 5618 |  |  |  | 1330 | [10 empty] | 61.74 |  |  |  | 63.63 | [5 empty] | 59.12 |  |  | 63.96 |  |  |  | 20.80 |  | 16.71 | [8 empty] | 19.67 |  |  |  |  | 1.89
1993 |  |  |  | 7954.42 |  |  | 7217 |  |  |  | 1330 | [10 empty] | 76.90 |  |  |  | 87.91 | [5 empty] | 68.27 |  |  | 82.39 |  |  |  | 10.19 |  | 9.98 | [8 empty] | 2.11 |  |  |  |  | 11.01
1994 |  |  |  | 7115.24 |  |  | 6671 |  |  |  | 1330 | [10 empty] | 74.52 |  |  |  | 77.62 | [5 empty] | 61.07 |  |  | 76.15 |  |  |  | 4.06 |  | 3.28 | [8 empty] | 19.10 |  |  |  |  | 3.10
1995 |  |  |  | 6934.50 |  |  | 6252 |  |  |  | 1330 | [10 empty] | 65.76 |  |  |  | 70.46 | [5 empty] | 59.52 |  |  | 71.37 |  |  |  | 2.39 |  | 1.72 | [8 empty] | 27.82 |  |  |  |  | 4.69
1996 |  |  |  | 8407.42 |  |  | 7195 |  |  |  | 1330 | [10 empty] | 78.51 |  |  |  | 83.80 | [5 empty] | 71.96 |  |  | 81.91 |  |  |  | 6.22 |  | 5.56 | [8 empty] | 10.64 |  |  |  |  | 5.29
1997 |  |  |  | 8139.80 |  |  | 7182 |  |  |  | 1330 | [10 empty] | 83.47 |  |  |  | 83.90 | [5 empty] | 69.86 |  |  | 81.99 |  |  |  | 15.12 |  | 14.94 | [8 empty] | 1.16 |  |  |  |  | 0.43
1998 |  |  |  | 7300.40 |  |  | 6583 |  |  |  | 1330 | [10 empty] | 69.09 |  |  |  | 73.11 | [5 empty] | 62.66 |  |  | 75.15 |  |  |  | 11.87 |  | 9.84 | [8 empty] | 17.05 |  |  |  |  | 4.02
1999 |  |  |  | 9243.77 |  |  | 7705 |  |  |  | 1330 | [10 empty] | 84.11 |  |  |  | 85.59 | [5 empty] | 79.34 |  |  | 87.96 |  |  |  | 1.64 |  | 1.42 | [8 empty] | 12.98 |  |  |  |  | 1.49
2000 |  |  |  | 9849.89 |  |  | 8271 |  |  |  | 1330 | [10 empty] | 94.43 |  |  |  | 96.04 | [5 empty] | 84.31 |  |  | 94.16 |  |  |  | 3.55 |  | 3.54 | [8 empty] | 0.42 |  |  |  |  | 1.61
2001 |  |  |  | 7843.13 |  |  | 6861 |  |  |  | 1330 | [10 empty] | 76.04 |  |  |  | 76.68 | [5 empty] | 67.32 |  |  | 78.32 |  |  |  | 8.36 |  | 6.99 | [8 empty] | 16.33 |  |  |  |  | 0.64
2002 |  |  |  | 7984.37 |  |  | 6569 |  |  |  | 1330 | [10 empty] | 72.01 |  |  |  | 73.19 | [5 empty] | 68.53 |  |  | 74.99 |  |  |  | 11.67 |  | 9.67 | [8 empty] | 17.14 |  |  |  |  | 1.18
2003 |  |  |  | 8814.93 |  |  | 7490 |  |  |  | 1330 | [10 empty] | 81.14 |  |  |  | 82.10 | [5 empty] | 75.66 |  |  | 85.50 |  |  |  | 6.51 |  | 5.72 | [8 empty] | 12.18 |  |  |  |  | 0.95
2004 |  |  |  | 9562.68 |  |  | 8039 |  |  |  | 1330 | [10 empty] | 89.87 |  |  |  | 92.58 | [5 empty] | 81.85 |  |  | 91.52 |  |  |  | 6.49 |  | 6.42 | [8 empty] | 1.00 |  |  |  |  | 2.71
2005 |  |  |  | 7246.43 |  |  | 5823 |  |  |  | 1330 | [10 empty] | 64.47 |  |  |  | 65.28 | [5 empty] | 62.19 |  |  | 66.47 |  |  |  | 3.68 |  | 6.15 | [8 empty] | 28.56 |  |  |  |  | 0.81
2006 |  |  |  | 8143.51 |  |  | 6673 |  |  |  | 1330 | [10 empty] | 73.89 |  |  |  | 74.40 | [5 empty] | 69.90 |  |  | 76.18 |  |  |  | 11.60 |  | 10.70 | [8 empty] | 14.90 |  |  |  |  | 0.51
2007 |  |  |  | 7558.05 |  |  | 6021 |  |  |  | 1330 | [10 empty] | 66.80 |  |  |  | 68.30 | [5 empty] | 64.87 |  |  | 68.73 |  |  |  | 31.67 |  | 31.65 | [8 empty] | 0.06 |  |  |  |  | 1.49
2008 |  |  |  | 9315.58 |  |  | 7595 |  |  |  | 1330 | [10 empty] | 83.97 |  |  |  | 85.07 | [5 empty] | 79.74 |  |  | 86.46 |  |  |  | 3.03 |  | 5.92 | [8 empty] | 9.01 |  |  |  |  | 1.09
2009 |  |  |  | 8393.37 |  |  | 6815 |  |  |  | 1330 | [10 empty] | 74.97 |  |  |  | 78.79 | [5 empty] | 72.04 |  |  | 77.80 |  |  |  | 2.23 |  | 7.58 | [8 empty] | 13.63 |  |  |  |  | 3.82
2010 |  |  |  | 10209.97 |  |  | 8496 |  |  |  | 1330 | [10 empty] | 95.98 |  |  |  | 96.93 | [5 empty] | 87.63 |  |  | 96.99 |  |  |  | 3.04 |  | 3.04 | [8 empty] | 0.03 |  |  |  |  | 0.96
2011 |  |  |  | 8868.96 |  |  | 7697 |  |  |  | 1330 | [10 empty] | 84.55 |  |  |  | 87.68 | [5 empty] | 76.12 |  |  | 87.87 |  |  |  | 1.01 |  | 4.10 | [8 empty] | 8.22 |  |  |  |  | 3.13
2012 |  |  |  | 7298.37 |  |  | 6084 |  |  |  | 1330 | [10 empty] | 67.34 |  |  |  | 68.96 | [5 empty] | 62.47 |  |  | 69.26 |  |  |  | 1.66 |  | 14.03 | [8 empty] | 17.01 |  |  |  |  | 1.61
2013 |  |  |  | 10778.91 |  |  | 8675 |  |  |  | 1330 | [10 empty] | 97.70 |  |  |  | 98.86 | [5 empty] | 92.52 |  |  | 99.03 |  |  |  | 1.11 |  | 1.11 | [8 empty] | 0.03 |  |  |  |  | 1.16
2014 |  |  |  | 9113.01 |  |  | 7499 |  |  |  | 1330 | [10 empty] | 83.67 |  |  |  | 85.18 | [5 empty] | 78.22 |  |  | 85.61 |  |  |  | 1.93 |  | 4.13 | [8 empty] | 10.69 |  |  |  |  | 1.51
2015 |  |  |  | 4064.60 |  |  | 3217 |  |  |  | 1330 | [10 empty] | 36.33 |  |  |  | 36.48 | [5 empty] | 34.89 |  |  | 36.72 |  |  |  | 0.79 |  | 0.29 | [8 empty] | 63.23 |  |  |  |  | 0.15
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1330 | [10 empty] | 0.04 |  |  |  | 0.04 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 94.22 | [8 empty] | 5.73 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1330 | [10 empty] | 0.02 |  |  |  | 0.02 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 99.98 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 3289.82 |  |  | 2950 |  |  |  | 1330 | [10 empty] | 28.54 |  |  |  | 28.64 | [5 empty] | 28.24 |  |  | 33.68 |  |  |  | 29.16 |  | 67.65 | [8 empty] | 3.71 |  |  |  |  | 0.11
2019 |  |  |  | 8734.15 |  |  | 6924 |  |  |  | 1330 | [10 empty] | 77.44 |  |  |  | 78.36 | [5 empty] | 74.97 |  |  | 79.04 |  |  |  | 3.53 |  | 3.67 | [8 empty] | 17.97 |  |  |  |  | 0.92
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1330 | [10 empty] | 0.06 |  |  |  | 6.19 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 93.81 | [8 empty] | 0.00 |  |  |  |  | 6.13
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1149 | [11 empty] | 2
B. |  | Refuelling without maintenance | [35 empty] | 134
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 742 |  |  |  | 83
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 33 |  |  |  | 7
E. |  | Testing of plant systems or components | [35 empty] | 14 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 172
H. |  | Nuclear regulatory requirements | [39 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 9
P. |  | Fire | [39 empty] | 48
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 5
Z. |  | Other | [39 empty] | 32 | [11 empty] | 1
Subtotal | [37 empty] | 1095 |  |  |  | 1336 | [11 empty] | 14
Total | [22 empty] | 0 | [14 empty] | 2445
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 15
12. |  |  | Reactor I&C Systems | [34 empty] | 76
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 21
15. |  |  | Reactor Cooling Systems | [34 empty] | 56
16. |  |  | Steam generation systems | [34 empty] | 581
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 39
32. |  |  | Feedwater and Main Steam System | [34 empty] | 30
33. |  |  | Circulating Water System | [34 empty] | 44
34. |  |  | Miscellaneous Systems | [34 empty] | 47
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 162
42. |  |  | Electrical Power Supply Systems | [34 empty] | 27
Total | [37 empty] | 1116

## PALUEL-3
2020 Operating Experience
FR-38 | [8 empty] | PALUEL-3 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-02-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-09-30
Gross electrical power | [12 empty] | : |  |  | 1382 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-02-01
Reference unit power (net) | [12 empty] | : |  |  | 1330 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.2
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6577.17 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.53 %
Energy Availability Factor (EAF) | [18 empty] | : | 57.82 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.18 %
Unit Capability Factor (UCF) | [18 empty] | : | 62.09 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 30.73 %
Load Factor (LF) | [18 empty] | : | 56.3 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 4.26 %
Operating Factor (OF) | [18 empty] | : | 62.4 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3303 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 885.45 | 862.85 |  |  |  | 938.52 |  | 883.71 | [8 empty] | 849.58 |  |  | 461.32 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 142.29 |  |  | 861.70 | [9 empty] | 691.74 |  |  | 6577.17
EAF [%] |  |  |  |  | 92.40 | 98.99 |  |  |  | 98.79 |  | 96.68 | [8 empty] | 86.18 |  |  | 48.19 | [6 empty] | 0.05 |  | 0.06 |  |  |  | 0.05 |  |  | 14.43 |  |  | 90.50 | [9 empty] | 70.43 |  |  | 57.82
UCF [%] |  |  |  |  | 98.82 | 99.63 |  |  |  | 99.47 |  | 99.63 | [8 empty] | 100.00 |  |  | 63.03 | [6 empty] | 0.05 |  | 0.06 |  |  |  | 0.05 |  |  | 20.73 |  |  | 92.65 | [9 empty] | 73.66 |  |  | 62.09
LF [%] |  |  |  |  | 89.48 | 93.21 |  |  |  | 94.97 |  | 92.28 | [8 empty] | 85.86 |  |  | 48.17 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 14.36 |  |  | 89.99 | [9 empty] | 69.91 |  |  | 56.30
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 63.33 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 20.40 |  |  | 94.44 | [9 empty] | 73.39 |  |  | 62.40
FLR [%] |  |  |  |  | 1.18 | 0.34 |  |  |  | 0.51 |  | 0.38 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 6.31 | [9 empty] | 26.34 |  |  | 4.53
UCL [%] |  |  |  |  | 1.18 | 0.34 |  |  |  | 0.51 |  | 0.38 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 49.97 |  |  | 6.24 | [9 empty] | 26.34 |  |  | 7.18
PUF [%] |  |  |  |  | 0.00 | 0.03 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 36.97 | [6 empty] | 99.95 |  | 99.94 |  |  |  | 99.95 |  |  | 29.30 |  |  | 1.10 | [9 empty] | 0.00 |  |  | 30.73
XUF [%] |  |  |  |  | 6.42 | 0.64 |  |  |  | 0.68 |  | 2.94 | [8 empty] | 13.82 |  |  | 14.84 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 6.30 |  |  | 2.15 | [9 empty] | 3.22 |  |  | 4.26
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 274760.35 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.6 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.62 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 12.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.14 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.09 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.52 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.44 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 8321.70 |  |  | 6503 |  |  |  | 1290 | [10 empty] | 72.10 |  |  |  | 72.10 | [5 empty] | 71.52 |  |  | 71.84 |  |  |  | 7.84 |  | 6.13 | [8 empty] | 21.77 |  |  |  |  | 0.00
1987 |  |  |  | 7716.60 |  |  | 6104 |  |  |  | 1290 | [10 empty] | 78.31 |  |  |  | 78.35 | [5 empty] | 68.29 |  |  | 69.68 |  |  |  | 15.09 |  | 13.93 | [8 empty] | 7.72 |  |  |  |  | 0.04
1988 |  |  |  | 6763.00 |  |  | 5413 |  |  |  | 1330 | [10 empty] | 59.22 |  |  |  | 68.73 | [5 empty] | 57.89 |  |  | 61.62 |  |  |  | 16.92 |  | 14.00 | [8 empty] | 17.27 |  |  |  |  | 9.51
1989 |  |  |  | 8124.44 |  |  | 6288 |  |  |  | 1330 | [10 empty] | 70.16 |  |  |  | 70.70 | [5 empty] | 69.73 |  |  | 71.78 |  |  |  | 14.82 |  | 12.30 | [8 empty] | 17.00 |  |  |  |  | 0.54
1990 |  |  |  | 7321.98 |  |  | 6008 |  |  |  | 1330 | [10 empty] | 66.25 |  |  |  | 67.22 | [5 empty] | 62.85 |  |  | 68.58 |  |  |  | 2.17 |  | 1.49 | [8 empty] | 31.29 |  |  |  |  | 0.97
1991 |  |  |  | 9587.15 |  |  | 7634 |  |  |  | 1330 | [10 empty] | 86.25 |  |  |  | 86.48 | [5 empty] | 82.29 |  |  | 87.15 |  |  |  | 10.69 |  | 10.36 | [8 empty] | 3.16 |  |  |  |  | 0.23
1992 |  |  |  | 6886.61 |  |  | 5671 |  |  |  | 1330 | [10 empty] | 62.95 |  |  |  | 63.20 | [5 empty] | 58.95 |  |  | 64.56 |  |  |  | 24.89 |  | 20.94 | [8 empty] | 15.86 |  |  |  |  | 0.24
1993 |  |  |  | 8459.03 |  |  | 6951 |  |  |  | 1330 | [10 empty] | 73.36 |  |  |  | 77.52 | [5 empty] | 72.60 |  |  | 79.35 |  |  |  | 2.29 |  | 1.81 | [8 empty] | 20.67 |  |  |  |  | 4.16
1994 |  |  |  | 6703.62 |  |  | 5590 |  |  |  | 1330 | [10 empty] | 61.83 |  |  |  | 63.39 | [5 empty] | 57.54 |  |  | 63.81 |  |  |  | 23.27 |  | 19.22 | [8 empty] | 17.39 |  |  |  |  | 1.56
1995 |  |  |  | 8733.26 |  |  | 7598 |  |  |  | 1330 | [10 empty] | 84.09 |  |  |  | 85.55 | [5 empty] | 74.96 |  |  | 86.74 |  |  |  | 1.21 |  | 1.05 | [8 empty] | 13.40 |  |  |  |  | 1.47
1996 |  |  |  | 8027.69 |  |  | 7261 |  |  |  | 1330 | [10 empty] | 84.55 |  |  |  | 84.90 | [5 empty] | 68.71 |  |  | 82.66 |  |  |  | 15.07 |  | 15.07 | [8 empty] | 0.03 |  |  |  |  | 0.35
1997 |  |  |  | 7618.80 |  |  | 6494 |  |  |  | 1330 | [10 empty] | 72.79 |  |  |  | 73.18 | [5 empty] | 65.39 |  |  | 74.13 |  |  |  | 1.57 |  | 1.17 | [8 empty] | 25.65 |  |  |  |  | 0.39
1998 |  |  |  | 8327.02 |  |  | 6913 |  |  |  | 1330 | [10 empty] | 76.12 |  |  |  | 77.61 | [5 empty] | 71.47 |  |  | 78.92 |  |  |  | 6.54 |  | 5.43 | [8 empty] | 16.96 |  |  |  |  | 1.49
1999 |  |  |  | 7636.71 |  |  | 6505 |  |  |  | 1330 | [10 empty] | 73.75 |  |  |  | 76.13 | [5 empty] | 65.55 |  |  | 74.26 |  |  |  | 12.58 |  | 10.95 | [8 empty] | 12.92 |  |  |  |  | 2.38
2000 |  |  |  | 9819.79 |  |  | 8199 |  |  |  | 1330 | [10 empty] | 94.42 |  |  |  | 94.73 | [5 empty] | 84.05 |  |  | 93.34 |  |  |  | 4.34 |  | 4.30 | [8 empty] | 0.97 |  |  |  |  | 0.31
2001 |  |  |  | 7815.94 |  |  | 6796 |  |  |  | 1330 | [10 empty] | 79.62 |  |  |  | 81.62 | [5 empty] | 67.09 |  |  | 77.58 |  |  |  | 1.48 |  | 1.23 | [8 empty] | 17.15 |  |  |  |  | 2.00
2002 |  |  |  | 8900.48 |  |  | 7366 |  |  |  | 1330 | [10 empty] | 80.37 |  |  |  | 82.28 | [5 empty] | 76.39 |  |  | 84.09 |  |  |  | 6.38 |  | 5.61 | [8 empty] | 12.11 |  |  |  |  | 1.92
2003 |  |  |  | 8181.73 |  |  | 6567 |  |  |  | 1330 | [10 empty] | 74.26 |  |  |  | 74.87 | [5 empty] | 70.22 |  |  | 74.97 |  |  |  | 24.57 |  | 24.39 | [8 empty] | 0.74 |  |  |  |  | 0.61
2004 |  |  |  | 6395.50 |  |  | 5147 |  |  |  | 1330 | [10 empty] | 56.04 |  |  |  | 57.01 | [5 empty] | 54.74 |  |  | 58.60 |  |  |  | 31.91 |  | 26.71 | [8 empty] | 16.28 |  |  |  |  | 0.97
2005 |  |  |  | 8157.60 |  |  | 6573 |  |  |  | 1330 | [10 empty] | 73.15 |  |  |  | 76.92 | [5 empty] | 70.02 |  |  | 75.03 |  |  |  | 10.52 |  | 9.74 | [8 empty] | 13.33 |  |  |  |  | 3.78
2006 |  |  |  | 10549.56 |  |  | 8671 |  |  |  | 1330 | [10 empty] | 96.79 |  |  |  | 98.63 | [5 empty] | 90.55 |  |  | 98.98 |  |  |  | 1.32 |  | 1.32 | [8 empty] | 0.05 |  |  |  |  | 1.84
2007 |  |  |  | 3908.79 |  |  | 3402 |  |  |  | 1330 | [10 empty] | 34.75 |  |  |  | 36.28 | [5 empty] | 33.55 |  |  | 38.84 |  |  |  | 14.66 |  | 37.58 | [8 empty] | 26.14 |  |  |  |  | 1.52
2008 |  |  |  | 10106.55 |  |  | 8570 |  |  |  | 1330 | [10 empty] | 96.59 |  |  |  | 98.00 | [5 empty] | 86.51 |  |  | 97.56 |  |  |  | 1.92 |  | 1.92 | [8 empty] | 0.08 |  |  |  |  | 1.41
2009 |  |  |  | 4214.55 |  |  | 3670 |  |  |  | 1330 | [10 empty] | 38.84 |  |  |  | 42.69 | [5 empty] | 36.17 |  |  | 41.89 |  |  |  | 39.64 |  | 44.94 | [8 empty] | 12.38 |  |  |  |  | 3.84
2010 |  |  |  | 6850.05 |  |  | 5394 |  |  |  | 1330 | [10 empty] | 60.64 |  |  |  | 61.91 | [5 empty] | 58.79 |  |  | 61.58 |  |  |  | 38.08 |  | 38.07 | [8 empty] | 0.02 |  |  |  |  | 1.27
2011 |  |  |  | 9475.26 |  |  | 7462 |  |  |  | 1330 | [10 empty] | 81.69 |  |  |  | 84.03 | [5 empty] | 81.33 |  |  | 85.18 |  |  |  | 2.90 |  | 6.26 | [8 empty] | 9.70 |  |  |  |  | 2.34
2012 |  |  |  | 7592.85 |  |  | 5934 |  |  |  | 1330 | [10 empty] | 66.60 |  |  |  | 66.86 | [5 empty] | 64.99 |  |  | 67.55 |  |  |  | 1.33 |  | 15.83 | [8 empty] | 17.31 |  |  |  |  | 0.26
2013 |  |  |  | 9162.71 |  |  | 7299 |  |  |  | 1330 | [10 empty] | 80.52 |  |  |  | 82.69 | [5 empty] | 78.64 |  |  | 83.32 |  |  |  | 1.31 |  | 7.61 | [8 empty] | 9.70 |  |  |  |  | 2.17
2014 |  |  |  | 10592.86 |  |  | 8460 |  |  |  | 1330 | [10 empty] | 93.80 |  |  |  | 94.80 | [5 empty] | 90.92 |  |  | 96.58 |  |  |  | 5.05 |  | 5.04 | [8 empty] | 0.17 |  |  |  |  | 0.99
2015 |  |  |  | 6436.51 |  |  | 5656 |  |  |  | 1330 | [10 empty] | 62.88 |  |  |  | 70.74 | [5 empty] | 55.25 |  |  | 64.57 |  |  |  | 0.57 |  | 8.37 | [8 empty] | 20.89 |  |  |  |  | 7.86
2016 |  |  |  | 8209.45 |  |  | 7250 |  |  |  | 1330 | [10 empty] | 73.38 |  |  |  | 94.35 | [5 empty] | 70.27 |  |  | 82.54 |  |  |  | 5.61 |  | 5.61 | [8 empty] | 0.04 |  |  |  |  | 20.98
2017 |  |  |  | 2121.65 |  |  | 1858 |  |  |  | 1330 | [10 empty] | 18.27 |  |  |  | 22.19 | [5 empty] | 18.21 |  |  | 21.21 |  |  |  | 3.59 |  | 23.29 | [8 empty] | 54.52 |  |  |  |  | 3.92
2018 |  |  |  | 8399.29 |  |  | 6597 |  |  |  | 1330 | [10 empty] | 72.81 |  |  |  | 73.40 | [5 empty] | 72.09 |  |  | 75.31 |  |  |  | 1.48 |  | 15.69 | [8 empty] | 10.91 |  |  |  |  | 0.59
2019 |  |  |  | 9886.14 |  |  | 8227 |  |  |  | 1330 | [10 empty] | 91.83 |  |  |  | 93.43 | [5 empty] | 84.85 |  |  | 93.92 |  |  |  | 6.27 |  | 6.25 | [8 empty] | 0.32 |  |  |  |  | 1.60
2020 |  |  |  | 6577.17 |  |  | 5481 |  |  |  | 1330 | [10 empty] | 57.82 |  |  |  | 62.09 | [5 empty] | 56.30 |  |  | 62.40 |  |  |  | 4.53 |  | 7.18 | [8 empty] | 30.73 |  |  |  |  | 4.26
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 912
B. |  | Refuelling without maintenance | [35 empty] | 97
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 916 |  |  |  | 28
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 29
E. |  | Testing of plant systems or components | [35 empty] | 25 |  |  |  | 8
H. |  | Nuclear regulatory requirements | [39 empty] | 3
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 1 | [11 empty] | 30
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 67
Z. |  | Other | [39 empty] | 24
Subtotal | [37 empty] | 1067 |  |  |  | 984 | [11 empty] | 104
Total | [22 empty] | 0 | [14 empty] | 2155
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 37
12. |  |  | Reactor I&C Systems | [34 empty] | 69
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 40
14. |  |  | Safety Systems | [34 empty] | 32
15. |  |  | Reactor Cooling Systems | [34 empty] | 125
16. |  |  | Steam generation systems | [34 empty] | 7
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 11
31. |  |  | Turbine and auxiliaries | [34 empty] | 39
32. |  |  | Feedwater and Main Steam System | [34 empty] | 56
33. |  |  | Circulating Water System | [34 empty] | 37
34. |  |  | Miscellaneous Systems | [34 empty] | 128
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 263
42. |  |  | Electrical Power Supply Systems | [34 empty] | 67
Total | [37 empty] | 913

## PALUEL-4
2020 Operating Experience
FR-39 | [8 empty] | PALUEL-4 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-02-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-04-11
Gross electrical power | [12 empty] | : |  |  | 1382 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-06-01
Reference unit power (net) | [12 empty] | : |  |  | 1330 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.2
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 36 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9859.6 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 8.84 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.5 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 8.82 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.96 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.23 %
Load Factor (LF) | [18 empty] | : | 84.39 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.46 %
Operating Factor (OF) | [18 empty] | : | 91.46 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 750 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 950.26 | 739.42 |  |  |  | 519.40 |  | 650.77 | [8 empty] | 813.15 |  |  | 903.78 | [6 empty] | 849.94 |  | 926.40 |  |  |  | 866.00 |  |  | 950.37 |  |  | 920.76 | [9 empty] | 769.36 |  |  | 9859.60
EAF [%] |  |  |  |  | 96.76 | 82.51 |  |  |  | 56.16 |  | 88.69 | [8 empty] | 89.78 |  |  | 95.33 | [6 empty] | 86.35 |  | 93.92 |  |  |  | 90.59 |  |  | 96.07 |  |  | 96.27 | [9 empty] | 77.88 |  |  | 87.50
UCF [%] |  |  |  |  | 97.70 | 90.83 |  |  |  | 67.70 |  | 89.24 | [8 empty] | 90.94 |  |  | 97.33 | [6 empty] | 89.17 |  | 97.55 |  |  |  | 93.09 |  |  | 98.04 |  |  | 97.82 | [9 empty] | 82.48 |  |  | 90.96
LF [%] |  |  |  |  | 96.03 | 79.88 |  |  |  | 52.56 |  | 67.96 | [8 empty] | 82.18 |  |  | 94.38 | [6 empty] | 85.89 |  | 93.62 |  |  |  | 90.43 |  |  | 95.91 |  |  | 96.15 | [9 empty] | 77.75 |  |  | 84.39
OF [%] |  |  |  |  | 100.00 | 85.92 |  |  |  | 57.34 |  | 90.42 | [8 empty] | 93.15 |  |  | 100.00 | [6 empty] | 90.99 |  | 100.00 |  |  |  | 99.17 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 81.05 |  |  | 91.46
FLR [%] |  |  |  |  | 1.36 | 9.17 |  |  |  | 32.27 |  | 10.76 | [8 empty] | 8.62 |  |  | 2.67 | [6 empty] | 10.79 |  | 2.45 |  |  |  | 6.70 |  |  | 1.28 |  |  | 1.99 | [9 empty] | 17.47 |  |  | 8.84
UCL [%] |  |  |  |  | 1.34 | 9.17 |  |  |  | 32.26 |  | 10.76 | [8 empty] | 8.58 |  |  | 2.67 | [6 empty] | 10.79 |  | 2.45 |  |  |  | 6.69 |  |  | 1.27 |  |  | 1.99 | [9 empty] | 17.46 |  |  | 8.82
PUF [%] |  |  |  |  | 0.96 | 0.00 |  |  |  | 0.03 |  | 0.00 | [8 empty] | 0.48 |  |  | 0.00 | [6 empty] | 0.04 |  | 0.00 |  |  |  | 0.22 |  |  | 0.68 |  |  | 0.19 | [9 empty] | 0.06 |  |  | 0.23
XUF [%] |  |  |  |  | 0.94 | 8.32 |  |  |  | 11.54 |  | 0.55 | [8 empty] | 1.16 |  |  | 2.01 | [6 empty] | 2.83 |  | 3.63 |  |  |  | 2.50 |  |  | 1.98 |  |  | 1.55 | [9 empty] | 4.61 |  |  | 3.46
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 285130.87 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.54 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.24 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.65 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.39 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.96 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.57 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.15 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.52 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 6118.60 |  |  | 5343 |  |  |  | 1300 | [10 empty] | 85.21 |  |  |  | 85.69 | [5 empty] | 78.04 |  |  | 83.67 |  |  |  | 14.30 |  | 14.30 | [8 empty] | 0.02 |  |  |  |  | 0.48
1987 |  |  |  | 8014.60 |  |  | 6289 |  |  |  | 1290 | [10 empty] | 69.74 |  |  |  | 69.84 | [5 empty] | 70.92 |  |  | 71.79 |  |  |  | 15.59 |  | 12.90 | [8 empty] | 17.25 |  |  |  |  | 0.11
1988 |  |  |  | 5909.00 |  |  | 4812 |  |  |  | 1330 | [10 empty] | 53.58 |  |  |  | 54.01 | [5 empty] | 50.58 |  |  | 54.78 |  |  |  | 26.16 |  | 19.13 | [8 empty] | 26.86 |  |  |  |  | 0.43
1989 |  |  |  | 8268.30 |  |  | 6349 |  |  |  | 1330 | [10 empty] | 70.98 |  |  |  | 72.12 | [5 empty] | 70.97 |  |  | 72.48 |  |  |  | 14.06 |  | 11.80 | [8 empty] | 16.07 |  |  |  |  | 1.14
1990 |  |  |  | 8067.69 |  |  | 6770 |  |  |  | 1330 | [10 empty] | 78.49 |  |  |  | 78.70 | [5 empty] | 69.25 |  |  | 77.28 |  |  |  | 11.57 |  | 10.30 | [8 empty] | 11.00 |  |  |  |  | 0.21
1991 |  |  |  | 8325.58 |  |  | 6677 |  |  |  | 1330 | [10 empty] | 74.20 |  |  |  | 74.52 | [5 empty] | 71.46 |  |  | 76.22 |  |  |  | 8.12 |  | 6.58 | [8 empty] | 18.89 |  |  |  |  | 0.32
1992 |  |  |  | 5553.31 |  |  | 4529 |  |  |  | 1330 | [10 empty] | 48.65 |  |  |  | 48.93 | [5 empty] | 47.53 |  |  | 51.56 |  |  |  | 35.83 |  | 27.32 | [8 empty] | 23.75 |  |  |  |  | 0.28
1993 |  |  |  | 8683.78 |  |  | 6938 |  |  |  | 1330 | [10 empty] | 75.35 |  |  |  | 77.78 | [5 empty] | 74.53 |  |  | 79.20 |  |  |  | 3.29 |  | 2.65 | [8 empty] | 19.57 |  |  |  |  | 2.43
1994 |  |  |  | 8329.73 |  |  | 6945 |  |  |  | 1330 | [10 empty] | 76.49 |  |  |  | 77.31 | [5 empty] | 71.49 |  |  | 79.28 |  |  |  | 7.70 |  | 6.45 | [8 empty] | 16.24 |  |  |  |  | 0.82
1995 |  |  |  | 8346.82 |  |  | 7354 |  |  |  | 1330 | [10 empty] | 88.12 |  |  |  | 88.46 | [5 empty] | 71.64 |  |  | 83.95 |  |  |  | 11.52 |  | 11.52 | [8 empty] | 0.03 |  |  |  |  | 0.34
1996 |  |  |  | 7848.12 |  |  | 6745 |  |  |  | 1330 | [10 empty] | 72.36 |  |  |  | 75.21 | [5 empty] | 67.18 |  |  | 76.79 |  |  |  | 13.07 |  | 11.31 | [8 empty] | 13.48 |  |  |  |  | 2.85
1997 |  |  |  | 8633.65 |  |  | 7219 |  |  |  | 1330 | [10 empty] | 78.22 |  |  |  | 81.91 | [5 empty] | 74.10 |  |  | 82.41 |  |  |  | 6.09 |  | 5.31 | [8 empty] | 12.78 |  |  |  |  | 3.70
1998 |  |  |  | 7776.71 |  |  | 6506 |  |  |  | 1330 | [10 empty] | 68.32 |  |  |  | 71.17 | [5 empty] | 66.75 |  |  | 74.27 |  |  |  | 4.80 |  | 3.59 | [8 empty] | 25.24 |  |  |  |  | 2.85
1999 |  |  |  | 9879.73 |  |  | 8345 |  |  |  | 1330 | [10 empty] | 94.56 |  |  |  | 96.10 | [5 empty] | 84.80 |  |  | 95.26 |  |  |  | 3.08 |  | 3.05 | [8 empty] | 0.85 |  |  |  |  | 1.53
2000 |  |  |  | 8358.80 |  |  | 7532 |  |  |  | 1330 | [10 empty] | 84.44 |  |  |  | 86.05 | [5 empty] | 71.55 |  |  | 85.75 |  |  |  | 1.37 |  | 1.19 | [8 empty] | 12.76 |  |  |  |  | 1.60
2001 |  |  |  | 8581.02 |  |  | 7489 |  |  |  | 1330 | [10 empty] | 82.14 |  |  |  | 84.54 | [5 empty] | 73.65 |  |  | 85.49 |  |  |  | 1.24 |  | 1.06 | [8 empty] | 14.40 |  |  |  |  | 2.40
2002 |  |  |  | 9303.30 |  |  | 8216 |  |  |  | 1330 | [10 empty] | 92.67 |  |  |  | 95.66 | [5 empty] | 79.85 |  |  | 93.79 |  |  |  | 0.70 |  | 0.67 | [8 empty] | 3.67 |  |  |  |  | 2.99
2003 |  |  |  | 7960.72 |  |  | 7307 |  |  |  | 1330 | [10 empty] | 81.93 |  |  |  | 82.79 | [5 empty] | 68.33 |  |  | 83.41 |  |  |  | 8.86 |  | 8.05 | [8 empty] | 9.17 |  |  |  |  | 0.86
2004 |  |  |  | 7138.56 |  |  | 6027 |  |  |  | 1330 | [10 empty] | 64.63 |  |  |  | 67.89 | [5 empty] | 61.10 |  |  | 68.61 |  |  |  | 18.67 |  | 15.58 | [8 empty] | 16.52 |  |  |  |  | 3.26
2005 |  |  |  | 9682.12 |  |  | 7949 |  |  |  | 1330 | [10 empty] | 89.18 |  |  |  | 93.34 | [5 empty] | 83.09 |  |  | 90.73 |  |  |  | 6.61 |  | 6.60 | [8 empty] | 0.05 |  |  |  |  | 4.16
2006 |  |  |  | 8270.83 |  |  | 7320 |  |  |  | 1330 | [10 empty] | 77.23 |  |  |  | 81.37 | [5 empty] | 70.99 |  |  | 83.56 |  |  |  | 1.70 |  | 1.70 | [8 empty] | 16.93 |  |  |  |  | 4.14
2007 |  |  |  | 8421.51 |  |  | 6824 |  |  |  | 1330 | [10 empty] | 73.68 |  |  |  | 76.85 | [5 empty] | 72.28 |  |  | 77.90 |  |  |  | 1.26 |  | 8.29 | [8 empty] | 14.86 |  |  |  |  | 3.16
2008 |  |  |  | 7962.59 |  |  | 6286 |  |  |  | 1330 | [10 empty] | 69.59 |  |  |  | 70.82 | [5 empty] | 68.16 |  |  | 71.56 |  |  |  | 0.21 |  | 3.72 | [8 empty] | 25.46 |  |  |  |  | 1.23
2009 |  |  |  | 9337.13 |  |  | 7944 |  |  |  | 1330 | [10 empty] | 88.89 |  |  |  | 91.39 | [5 empty] | 80.14 |  |  | 90.68 |  |  |  | 8.56 |  | 8.55 | [8 empty] | 0.06 |  |  |  |  | 2.50
2010 |  |  |  | 7709.46 |  |  | 6085 |  |  |  | 1330 | [10 empty] | 67.44 |  |  |  | 68.90 | [5 empty] | 66.17 |  |  | 69.46 |  |  |  | 2.78 |  | 18.44 | [8 empty] | 12.66 |  |  |  |  | 1.46
2011 |  |  |  | 9571.58 |  |  | 7835 |  |  |  | 1330 | [10 empty] | 87.90 |  |  |  | 88.66 | [5 empty] | 82.15 |  |  | 89.44 |  |  |  | 0.57 |  | 2.65 | [8 empty] | 8.69 |  |  |  |  | 0.76
2012 |  |  |  | 10040.06 |  |  | 8467 |  |  |  | 1330 | [10 empty] | 97.16 |  |  |  | 97.73 | [5 empty] | 85.94 |  |  | 96.39 |  |  |  | 2.25 |  | 2.25 | [8 empty] | 0.03 |  |  |  |  | 0.57
2013 |  |  |  | 7036.36 |  |  | 5984 |  |  |  | 1330 | [10 empty] | 64.01 |  |  |  | 66.26 | [5 empty] | 60.39 |  |  | 68.31 |  |  |  | 6.36 |  | 14.57 | [8 empty] | 19.18 |  |  |  |  | 2.25
2014 |  |  |  | 8962.84 |  |  | 7539 |  |  |  | 1330 | [10 empty] | 84.83 |  |  |  | 85.39 | [5 empty] | 76.93 |  |  | 86.06 |  |  |  | 1.21 |  | 1.04 | [8 empty] | 13.56 |  |  |  |  | 0.56
2015 |  |  |  | 8807.53 |  |  | 7649 |  |  |  | 1330 | [10 empty] | 89.81 |  |  |  | 99.80 | [5 empty] | 75.60 |  |  | 87.32 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 0.06 |  |  |  |  | 9.99
2016 |  |  |  | 7284.06 |  |  | 6369 |  |  |  | 1330 | [10 empty] | 65.14 |  |  |  | 67.12 | [5 empty] | 62.35 |  |  | 72.51 |  |  |  | 12.58 |  | 13.54 | [8 empty] | 19.35 |  |  |  |  | 1.98
2017 |  |  |  | 9082.31 |  |  | 7455 |  |  |  | 1330 | [10 empty] | 80.97 |  |  |  | 84.31 | [5 empty] | 77.95 |  |  | 85.10 |  |  |  | 4.09 |  | 5.11 | [8 empty] | 10.58 |  |  |  |  | 3.35
2018 |  |  |  | 10041.61 |  |  | 8304 |  |  |  | 1330 | [10 empty] | 91.73 |  |  |  | 96.68 | [5 empty] | 86.19 |  |  | 94.79 |  |  |  | 3.21 |  | 3.21 | [8 empty] | 0.12 |  |  |  |  | 4.95
2019 |  |  |  | 1977.33 |  |  | 1688 |  |  |  | 1330 | [10 empty] | 17.03 |  |  |  | 18.47 | [5 empty] | 16.97 |  |  | 19.27 |  |  |  | 6.39 |  | 33.73 | [8 empty] | 47.80 |  |  |  |  | 1.44
2020 |  |  |  | 9859.60 |  |  | 8034 |  |  |  | 1330 | [10 empty] | 87.50 |  |  |  | 90.96 | [5 empty] | 84.39 |  |  | 91.46 |  |  |  | 8.84 |  | 8.82 | [8 empty] | 0.23 |  |  |  |  | 3.46
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 566 | [11 empty] | 1
B. |  | Refuelling without maintenance | [35 empty] | 115
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 909 |  |  |  | 9
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 26
E. |  | Testing of plant systems or components | [35 empty] | 14 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 3
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 17
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
O. |  | Load dispatching, prioritization | [51 empty] | 3
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 11 | [11 empty] | 10
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 30
Z. |  | Other | [39 empty] | 59 | [11 empty] | 2
Subtotal | [37 empty] | 1064 |  |  |  | 665 | [11 empty] | 59
Total | [22 empty] | 0 | [14 empty] | 1788
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 100
12. |  |  | Reactor I&C Systems | [34 empty] | 29
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
14. |  |  | Safety Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 25
16. |  |  | Steam generation systems | [34 empty] | 49
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 11
31. |  |  | Turbine and auxiliaries | [34 empty] | 47
32. |  |  | Feedwater and Main Steam System | [34 empty] | 21
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 142
41. |  |  | Main Generator Systems | [34 empty] | 97
42. |  |  | Electrical Power Supply Systems | [34 empty] | 25
Total | [37 empty] | 565

## PENLY-1
2020 Operating Experience
FR-63 | [8 empty] | PENLY-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-09-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-05-04
Gross electrical power | [12 empty] | : |  |  | 1382 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-12-01
Reference unit power (net) | [12 empty] | : |  |  | 1330 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6249.27 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.42 %
Energy Availability Factor (EAF) | [18 empty] | : | 53.91 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 11.92 %
Unit Capability Factor (UCF) | [18 empty] | : | 56.99 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 31.09 %
Load Factor (LF) | [18 empty] | : | 53.49 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.08 %
Operating Factor (OF) | [18 empty] | : | 58.29 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3664 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 938.30 | 885.05 |  |  |  | 958.16 |  | 913.51 | [8 empty] | 417.94 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 467.61 |  |  | 773.00 | [9 empty] | 895.70 |  |  | 6249.27
EAF [%] |  |  |  |  | 95.54 | 97.54 |  |  |  | 98.39 |  | 95.52 | [8 empty] | 42.24 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.01 |  |  | 47.31 |  |  | 80.99 | [9 empty] | 90.93 |  |  | 53.91
UCF [%] |  |  |  |  | 98.18 | 99.65 |  |  |  | 99.57 |  | 99.89 | [8 empty] | 48.41 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 11.87 |  |  | 47.38 |  |  | 80.99 | [9 empty] | 99.58 |  |  | 56.99
LF [%] |  |  |  |  | 94.82 | 95.61 |  |  |  | 96.96 |  | 95.40 | [8 empty] | 42.24 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 47.19 |  |  | 80.72 | [9 empty] | 90.52 |  |  | 53.49
OF [%] |  |  |  |  | 99.19 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 48.66 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 53.29 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 58.29
FLR [%] |  |  |  |  | 1.75 | 0.28 |  |  |  | 0.37 |  | 0.10 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 5.68 |  |  | 18.89 | [9 empty] | 0.27 |  |  | 3.42
UCL [%] |  |  |  |  | 1.74 | 0.28 |  |  |  | 0.37 |  | 0.10 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 74.78 |  |  | 47.29 |  |  | 18.86 | [9 empty] | 0.27 |  |  | 11.92
PUF [%] |  |  |  |  | 0.08 | 0.06 |  |  |  | 0.06 |  | 0.01 | [8 empty] | 51.59 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 13.35 |  |  | 5.33 |  |  | 0.15 | [9 empty] | 0.15 |  |  | 31.09
XUF [%] |  |  |  |  | 2.64 | 2.11 |  |  |  | 1.18 |  | 4.37 | [8 empty] | 6.17 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 11.86 |  |  | 0.06 |  |  | 0.00 | [9 empty] | 8.65 |  |  | 3.08
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 267311.82 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.66 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.71 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.43 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.09 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.49 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.72 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.37 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.3 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 2887.12 |  |  | 3100 |  |  |  | 1330 | [10 empty] | 98.94 |  |  |  | 98.94 | [5 empty] | 98.15 |  |  | 99.19 |  |  |  | 0.96 |  | 0.96 | [8 empty] | 0.10 |  |  |  |  | 0.00
1991 |  |  |  | 8436.71 |  |  | 6645 |  |  |  | 1330 | [10 empty] | 74.23 |  |  |  | 74.27 | [5 empty] | 72.41 |  |  | 75.86 |  |  |  | 10.99 |  | 9.17 | [8 empty] | 16.56 |  |  |  |  | 0.04
1992 |  |  |  | 7922.21 |  |  | 6315 |  |  |  | 1330 | [10 empty] | 70.91 |  |  |  | 71.23 | [5 empty] | 67.81 |  |  | 71.89 |  |  |  | 3.72 |  | 2.75 | [8 empty] | 26.02 |  |  |  |  | 0.32
1993 |  |  |  | 8023.87 |  |  | 7298 |  |  |  | 1330 | [10 empty] | 71.90 |  |  |  | 84.61 | [5 empty] | 68.87 |  |  | 83.31 |  |  |  | 0.95 |  | 0.81 | [8 empty] | 14.58 |  |  |  |  | 12.70
1994 |  |  |  | 7969.13 |  |  | 6654 |  |  |  | 1330 | [10 empty] | 85.04 |  |  |  | 86.07 | [5 empty] | 68.40 |  |  | 75.96 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 13.75 |  |  |  |  | 1.03
1995 |  |  |  | 8879.06 |  |  | 7248 |  |  |  | 1330 | [10 empty] | 80.78 |  |  |  | 81.87 | [5 empty] | 76.21 |  |  | 82.74 |  |  |  | 3.62 |  | 3.08 | [8 empty] | 15.05 |  |  |  |  | 1.09
1996 |  |  |  | 9530.76 |  |  | 7625 |  |  |  | 1330 | [10 empty] | 85.23 |  |  |  | 85.71 | [5 empty] | 81.58 |  |  | 86.81 |  |  |  | 2.07 |  | 1.81 | [8 empty] | 12.48 |  |  |  |  | 0.48
1997 |  |  |  | 8503.41 |  |  | 6872 |  |  |  | 1330 | [10 empty] | 76.69 |  |  |  | 77.50 | [5 empty] | 72.99 |  |  | 78.45 |  |  |  | 11.41 |  | 9.98 | [8 empty] | 12.52 |  |  |  |  | 0.80
1998 |  |  |  | 9965.66 |  |  | 8140 |  |  |  | 1330 | [10 empty] | 97.87 |  |  |  | 97.97 | [5 empty] | 85.54 |  |  | 92.92 |  |  |  | 1.07 |  | 1.06 | [8 empty] | 0.98 |  |  |  |  | 0.10
1999 |  |  |  | 7998.46 |  |  | 6633 |  |  |  | 1330 | [10 empty] | 71.52 |  |  |  | 74.38 | [5 empty] | 68.65 |  |  | 75.72 |  |  |  | 12.99 |  | 11.11 | [8 empty] | 14.51 |  |  |  |  | 2.87
2000 |  |  |  | 8271.73 |  |  | 6640 |  |  |  | 1330 | [10 empty] | 73.67 |  |  |  | 73.85 | [5 empty] | 70.80 |  |  | 75.59 |  |  |  | 13.80 |  | 11.82 | [8 empty] | 14.34 |  |  |  |  | 0.17
2001 |  |  |  | 9825.84 |  |  | 8304 |  |  |  | 1330 | [10 empty] | 98.40 |  |  |  | 98.69 | [5 empty] | 84.34 |  |  | 94.79 |  |  |  | 0.55 |  | 0.55 | [8 empty] | 0.76 |  |  |  |  | 0.29
2002 |  |  |  | 7146.66 |  |  | 5948 |  |  |  | 1330 | [10 empty] | 66.91 |  |  |  | 67.24 | [5 empty] | 61.34 |  |  | 67.90 |  |  |  | 6.95 |  | 5.02 | [8 empty] | 27.74 |  |  |  |  | 0.34
2003 |  |  |  | 9290.83 |  |  | 7525 |  |  |  | 1330 | [10 empty] | 84.64 |  |  |  | 84.64 | [5 empty] | 79.74 |  |  | 85.90 |  |  |  | 3.49 |  | 3.06 | [8 empty] | 12.30 |  |  |  |  | 0.00
2004 |  |  |  | 10500.23 |  |  | 8733 |  |  |  | 1330 | [10 empty] | 98.57 |  |  |  | 98.93 | [5 empty] | 89.88 |  |  | 99.42 |  |  |  | 0.74 |  | 0.74 | [8 empty] | 0.33 |  |  |  |  | 0.37
2005 |  |  |  | 8491.26 |  |  | 7104 |  |  |  | 1330 | [10 empty] | 76.88 |  |  |  | 79.06 | [5 empty] | 72.88 |  |  | 81.10 |  |  |  | 4.78 |  | 5.86 | [8 empty] | 15.08 |  |  |  |  | 2.18
2006 |  |  |  | 9533.15 |  |  | 7656 |  |  |  | 1330 | [10 empty] | 83.60 |  |  |  | 86.07 | [5 empty] | 81.82 |  |  | 87.40 |  |  |  | 4.87 |  | 5.09 | [8 empty] | 8.84 |  |  |  |  | 2.46
2007 |  |  |  | 9243.57 |  |  | 7356 |  |  |  | 1330 | [10 empty] | 82.07 |  |  |  | 82.73 | [5 empty] | 79.34 |  |  | 83.97 |  |  |  | 1.85 |  | 2.32 | [8 empty] | 14.95 |  |  |  |  | 0.66
2008 |  |  |  | 10743.35 |  |  | 8424 |  |  |  | 1330 | [10 empty] | 95.24 |  |  |  | 95.53 | [5 empty] | 91.96 |  |  | 95.90 |  |  |  | 4.45 |  | 4.45 | [8 empty] | 0.03 |  |  |  |  | 0.29
2009 |  |  |  | 8878.54 |  |  | 7217 |  |  |  | 1330 | [10 empty] | 80.49 |  |  |  | 81.76 | [5 empty] | 76.21 |  |  | 82.39 |  |  |  | 1.22 |  | 1.36 | [8 empty] | 16.87 |  |  |  |  | 1.28
2010 |  |  |  | 6627.27 |  |  | 5280 |  |  |  | 1330 | [10 empty] | 59.23 |  |  |  | 60.38 | [5 empty] | 56.88 |  |  | 60.27 |  |  |  | 32.32 |  | 30.00 | [8 empty] | 9.62 |  |  |  |  | 1.15
2011 |  |  |  | 7976.85 |  |  | 6332 |  |  |  | 1330 | [10 empty] | 71.30 |  |  |  | 71.41 | [5 empty] | 68.47 |  |  | 72.28 |  |  |  | 0.85 |  | 3.00 | [8 empty] | 25.59 |  |  |  |  | 0.11
2012 |  |  |  | 10476.99 |  |  | 8525 |  |  |  | 1330 | [10 empty] | 95.85 |  |  |  | 96.05 | [5 empty] | 89.68 |  |  | 97.05 |  |  |  | 3.88 |  | 3.88 | [8 empty] | 0.07 |  |  |  |  | 0.19
2013 |  |  |  | 9001.96 |  |  | 7536 |  |  |  | 1330 | [10 empty] | 84.12 |  |  |  | 85.74 | [5 empty] | 77.26 |  |  | 86.03 |  |  |  | 0.67 |  | 6.26 | [8 empty] | 7.99 |  |  |  |  | 1.63
2014 |  |  |  | 8406.70 |  |  | 6939 |  |  |  | 1330 | [10 empty] | 77.63 |  |  |  | 78.26 | [5 empty] | 72.16 |  |  | 79.21 |  |  |  | 0.78 |  | 1.15 | [8 empty] | 20.59 |  |  |  |  | 0.63
2015 |  |  |  | 10162.55 |  |  | 8623 |  |  |  | 1330 | [10 empty] | 97.69 |  |  |  | 98.37 | [5 empty] | 87.23 |  |  | 98.44 |  |  |  | 1.54 |  | 1.54 | [8 empty] | 0.09 |  |  |  |  | 0.68
2016 |  |  |  | 9489.07 |  |  | 7812 |  |  |  | 1330 | [10 empty] | 83.87 |  |  |  | 85.65 | [5 empty] | 81.22 |  |  | 88.93 |  |  |  | 1.56 |  | 1.36 | [8 empty] | 12.99 |  |  |  |  | 1.78
2017 |  |  |  | 7829.20 |  |  | 6376 |  |  |  | 1330 | [10 empty] | 69.30 |  |  |  | 71.90 | [5 empty] | 67.20 |  |  | 72.79 |  |  |  | 1.56 |  | 8.37 | [8 empty] | 19.73 |  |  |  |  | 2.60
2018 |  |  |  | 8796.74 |  |  | 7044 |  |  |  | 1330 | [10 empty] | 78.37 |  |  |  | 79.72 | [5 empty] | 75.50 |  |  | 80.41 |  |  |  | 2.90 |  | 10.61 | [8 empty] | 9.67 |  |  |  |  | 1.35
2019 |  |  |  | 10462.26 |  |  | 8383 |  |  |  | 1330 | [10 empty] | 93.91 |  |  |  | 94.57 | [5 empty] | 89.80 |  |  | 95.70 |  |  |  | 1.07 |  | 4.91 | [8 empty] | 0.53 |  |  |  |  | 0.66
2020 |  |  |  | 6249.27 |  |  | 5120 |  |  |  | 1330 | [10 empty] | 53.91 |  |  |  | 56.99 | [5 empty] | 53.49 |  |  | 58.29 |  |  |  | 3.42 |  | 11.92 | [8 empty] | 31.09 |  |  |  |  | 3.08
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1990 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 374 | [11 empty] | 0
B. |  | Refuelling without maintenance | [35 empty] | 112
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 754 |  |  |  | 1
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 129
E. |  | Testing of plant systems or components | [35 empty] | 14 | [15 empty] | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 3
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 8
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 1
Z. |  | Other | [39 empty] | 5
Subtotal | [37 empty] | 1009 |  |  |  | 385 | [11 empty] | 10
Total | [22 empty] | 0 | [14 empty] | 1404
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1990 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 27
12. |  |  | Reactor I&C Systems | [34 empty] | 22
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 26
14. |  |  | Safety Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 31
16. |  |  | Steam generation systems | [34 empty] | 29
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 33
32. |  |  | Feedwater and Main Steam System | [34 empty] | 24
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 68
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 88
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [37 empty] | 374

## PENLY-2
2020 Operating Experience
FR-64 | [8 empty] | PENLY-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-08-01
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1992-02-04
Gross electrical power | [12 empty] | : |  |  | 1382 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1992-11-01
Reference unit power (net) | [12 empty] | : |  |  | 1330 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 28 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 804 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10224.76 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.16 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.37 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.64 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.77 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.59 %
Load Factor (LF) | [18 empty] | : | 87.52 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.4 %
Operating Factor (OF) | [18 empty] | : | 97.76 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 197 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 761.66 | 855.64 |  |  |  | 767.15 |  | 825.02 | [8 empty] | 765.79 |  |  | 857.47 | [6 empty] | 901.13 |  | 905.56 |  |  |  | 879.53 |  |  | 895.82 |  |  | 888.50 | [9 empty] | 921.47 |  |  | 10224.76
EAF [%] |  |  |  |  | 76.98 | 98.89 |  |  |  | 90.44 |  | 99.55 | [8 empty] | 99.24 |  |  | 98.89 | [6 empty] | 99.07 |  | 98.42 |  |  |  | 98.86 |  |  | 99.38 |  |  | 99.02 | [9 empty] | 98.20 |  |  | 96.37
UCF [%] |  |  |  |  | 76.98 | 98.89 |  |  |  | 91.09 |  | 99.55 | [8 empty] | 99.53 |  |  | 99.29 | [6 empty] | 99.59 |  | 99.24 |  |  |  | 99.37 |  |  | 99.58 |  |  | 99.02 | [9 empty] | 99.53 |  |  | 96.77
LF [%] |  |  |  |  | 76.97 | 92.43 |  |  |  | 77.63 |  | 86.16 | [8 empty] | 77.39 |  |  | 89.54 | [6 empty] | 91.07 |  | 91.52 |  |  |  | 91.85 |  |  | 90.41 |  |  | 92.78 | [9 empty] | 93.12 |  |  | 87.52
OF [%] |  |  |  |  | 82.26 | 100.00 |  |  |  | 91.39 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.76
FLR [%] |  |  |  |  | 0.00 | 0.45 |  |  |  | 8.84 |  | 0.34 | [8 empty] | 0.41 |  |  | 0.55 | [6 empty] | 0.36 |  | 0.70 |  |  |  | 0.54 |  |  | 0.37 |  |  | 0.58 | [9 empty] | 0.42 |  |  | 1.16
UCL [%] |  |  |  |  | 17.73 | 0.45 |  |  |  | 8.84 |  | 0.34 | [8 empty] | 0.41 |  |  | 0.55 | [6 empty] | 0.36 |  | 0.70 |  |  |  | 0.54 |  |  | 0.37 |  |  | 0.58 | [9 empty] | 0.42 |  |  | 2.64
PUF [%] |  |  |  |  | 5.29 | 0.66 |  |  |  | 0.07 |  | 0.11 | [8 empty] | 0.06 |  |  | 0.16 | [6 empty] | 0.05 |  | 0.06 |  |  |  | 0.09 |  |  | 0.05 |  |  | 0.40 | [9 empty] | 0.05 |  |  | 0.59
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.65 |  | 0.00 | [8 empty] | 0.29 |  |  | 0.40 | [6 empty] | 0.52 |  | 0.83 |  |  |  | 0.52 |  |  | 0.20 |  |  | 0.00 | [9 empty] | 1.33 |  |  | 0.40
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 254001.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.85 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.26 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.16 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.62 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.23 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.36 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.01 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1992 |  |  |  | 5149.77 |  |  | 4796 |  |  |  | 1330 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 101.22 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
1993 |  |  |  | 8611.76 |  |  | 6658 |  |  |  | 1330 | [10 empty] | 74.40 |  |  |  | 75.16 | [5 empty] | 73.92 |  |  | 76.00 |  |  |  | 0.54 |  | 0.41 | [8 empty] | 24.43 |  |  |  |  | 0.76
1994 |  |  |  | 8759.66 |  |  | 7228 |  |  |  | 1330 | [10 empty] | 77.57 |  |  |  | 81.28 | [5 empty] | 75.19 |  |  | 82.51 |  |  |  | 3.58 |  | 3.01 | [8 empty] | 15.71 |  |  |  |  | 3.70
1995 |  |  |  | 8169.73 |  |  | 6574 |  |  |  | 1330 | [10 empty] | 73.77 |  |  |  | 73.98 | [5 empty] | 70.12 |  |  | 75.05 |  |  |  | 16.06 |  | 14.16 | [8 empty] | 11.86 |  |  |  |  | 0.21
1996 |  |  |  | 9757.97 |  |  | 8025 |  |  |  | 1330 | [10 empty] | 89.29 |  |  |  | 91.33 | [5 empty] | 83.52 |  |  | 91.36 |  |  |  | 8.62 |  | 8.61 | [8 empty] | 0.06 |  |  |  |  | 2.04
1997 |  |  |  | 8068.94 |  |  | 7186 |  |  |  | 1330 | [10 empty] | 82.95 |  |  |  | 84.26 | [5 empty] | 69.26 |  |  | 82.03 |  |  |  | 4.09 |  | 3.60 | [8 empty] | 12.14 |  |  |  |  | 1.32
1998 |  |  |  | 8877.52 |  |  | 7318 |  |  |  | 1330 | [10 empty] | 81.07 |  |  |  | 82.94 | [5 empty] | 76.20 |  |  | 83.54 |  |  |  | 4.74 |  | 4.12 | [8 empty] | 12.93 |  |  |  |  | 1.87
1999 |  |  |  | 8636.97 |  |  | 7203 |  |  |  | 1330 | [10 empty] | 79.35 |  |  |  | 81.27 | [5 empty] | 74.13 |  |  | 82.23 |  |  |  | 5.19 |  | 4.45 | [8 empty] | 14.28 |  |  |  |  | 1.92
2000 |  |  |  | 9584.47 |  |  | 8393 |  |  |  | 1330 | [10 empty] | 96.84 |  |  |  | 97.11 | [5 empty] | 82.04 |  |  | 95.55 |  |  |  | 2.85 |  | 2.85 | [8 empty] | 0.04 |  |  |  |  | 0.27
2001 |  |  |  | 8816.23 |  |  | 7333 |  |  |  | 1330 | [10 empty] | 80.24 |  |  |  | 82.09 | [5 empty] | 75.67 |  |  | 83.71 |  |  |  | 4.63 |  | 3.98 | [8 empty] | 13.93 |  |  |  |  | 1.85
2002 |  |  |  | 8464.26 |  |  | 6890 |  |  |  | 1330 | [10 empty] | 78.98 |  |  |  | 79.07 | [5 empty] | 72.65 |  |  | 78.65 |  |  |  | 9.06 |  | 7.88 | [8 empty] | 13.06 |  |  |  |  | 0.09
2003 |  |  |  | 10207.81 |  |  | 8603 |  |  |  | 1330 | [10 empty] | 97.65 |  |  |  | 97.65 | [5 empty] | 87.61 |  |  | 98.21 |  |  |  | 1.90 |  | 1.89 | [8 empty] | 0.47 |  |  |  |  | 0.00
2004 |  |  |  | 7225.85 |  |  | 6231 |  |  |  | 1330 | [10 empty] | 69.09 |  |  |  | 69.21 | [5 empty] | 61.85 |  |  | 70.94 |  |  |  | 2.04 |  | 1.44 | [8 empty] | 29.35 |  |  |  |  | 0.12
2005 |  |  |  | 9102.59 |  |  | 7546 |  |  |  | 1330 | [10 empty] | 84.01 |  |  |  | 84.78 | [5 empty] | 78.13 |  |  | 86.14 |  |  |  | 2.96 |  | 4.86 | [8 empty] | 10.36 |  |  |  |  | 0.78
2006 |  |  |  | 9885.16 |  |  | 8447 |  |  |  | 1330 | [10 empty] | 96.99 |  |  |  | 97.73 | [5 empty] | 84.85 |  |  | 96.43 |  |  |  | 2.24 |  | 2.23 | [8 empty] | 0.03 |  |  |  |  | 0.74
2007 |  |  |  | 8718.65 |  |  | 7081 |  |  |  | 1330 | [10 empty] | 76.70 |  |  |  | 79.44 | [5 empty] | 74.83 |  |  | 80.83 |  |  |  | 4.06 |  | 3.36 | [8 empty] | 17.20 |  |  |  |  | 2.73
2008 |  |  |  | 9474.85 |  |  | 7590 |  |  |  | 1330 | [10 empty] | 85.00 |  |  |  | 86.11 | [5 empty] | 81.10 |  |  | 86.41 |  |  |  | 1.39 |  | 4.70 | [8 empty] | 9.18 |  |  |  |  | 1.11
2009 |  |  |  | 8954.23 |  |  | 7258 |  |  |  | 1330 | [10 empty] | 80.32 |  |  |  | 81.97 | [5 empty] | 76.86 |  |  | 82.85 |  |  |  | 1.70 |  | 3.81 | [8 empty] | 14.22 |  |  |  |  | 1.64
2010 |  |  |  | 9986.96 |  |  | 8571 |  |  |  | 1330 | [10 empty] | 96.52 |  |  |  | 97.72 | [5 empty] | 85.72 |  |  | 97.84 |  |  |  | 2.25 |  | 2.25 | [8 empty] | 0.03 |  |  |  |  | 1.20
2011 |  |  |  | 9873.06 |  |  | 7931 |  |  |  | 1330 | [10 empty] | 87.16 |  |  |  | 89.53 | [5 empty] | 84.74 |  |  | 90.54 |  |  |  | 1.03 |  | 2.42 | [8 empty] | 8.05 |  |  |  |  | 2.37
2012 |  |  |  | 7151.26 |  |  | 5802 |  |  |  | 1330 | [10 empty] | 65.28 |  |  |  | 65.59 | [5 empty] | 61.21 |  |  | 66.05 |  |  |  | 19.48 |  | 21.64 | [8 empty] | 12.76 |  |  |  |  | 0.31
2013 |  |  |  | 10253.29 |  |  | 8413 |  |  |  | 1330 | [10 empty] | 92.59 |  |  |  | 99.11 | [5 empty] | 88.00 |  |  | 96.04 |  |  |  | 0.46 |  | 0.45 | [8 empty] | 0.43 |  |  |  |  | 6.52
2014 |  |  |  | 7123.77 |  |  | 5722 |  |  |  | 1330 | [10 empty] | 62.89 |  |  |  | 64.90 | [5 empty] | 61.14 |  |  | 65.32 |  |  |  | 2.68 |  | 5.99 | [8 empty] | 29.11 |  |  |  |  | 2.01
2015 |  |  |  | 9204.63 |  |  | 7743 |  |  |  | 1330 | [10 empty] | 87.14 |  |  |  | 87.26 | [5 empty] | 79.00 |  |  | 88.39 |  |  |  | 0.94 |  | 1.91 | [8 empty] | 10.83 |  |  |  |  | 0.12
2016 |  |  |  | 8682.34 |  |  | 6925 |  |  |  | 1330 | [10 empty] | 76.22 |  |  |  | 77.01 | [5 empty] | 74.32 |  |  | 78.84 |  |  |  | 1.05 |  | 3.70 | [8 empty] | 19.30 |  |  |  |  | 0.78
2017 |  |  |  | 10308.82 |  |  | 8697 |  |  |  | 1330 | [10 empty] | 98.33 |  |  |  | 99.03 | [5 empty] | 88.48 |  |  | 99.28 |  |  |  | 0.91 |  | 0.91 | [8 empty] | 0.05 |  |  |  |  | 0.70
2018 |  |  |  | 8627.09 |  |  | 7065 |  |  |  | 1330 | [10 empty] | 77.84 |  |  |  | 80.27 | [5 empty] | 74.05 |  |  | 80.65 |  |  |  | 1.78 |  | 6.64 | [8 empty] | 13.09 |  |  |  |  | 2.43
2019 |  |  |  | 6201.08 |  |  | 4943 |  |  |  | 1330 | [10 empty] | 55.63 |  |  |  | 55.93 | [5 empty] | 53.22 |  |  | 56.43 |  |  |  | 1.31 |  | 21.30 | [8 empty] | 22.78 |  |  |  |  | 0.30
2020 |  |  |  | 10224.76 |  |  | 8587 |  |  |  | 1330 | [10 empty] | 96.37 |  |  |  | 96.77 | [5 empty] | 87.52 |  |  | 97.76 |  |  |  | 1.16 |  | 2.64 | [8 empty] | 0.59 |  |  |  |  | 0.40
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1992 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 471
B. |  | Refuelling without maintenance | [35 empty] | 122
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 797
E. |  | Testing of plant systems or components | [35 empty] | 30
H. |  | Nuclear regulatory requirements | [39 empty] | 12
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 2 | [11 empty] | 4
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 12
Z. |  | Other | [39 empty] | 2
Subtotal | [37 empty] | 949 |  |  |  | 489 | [11 empty] | 25
Total | [22 empty] | 0 | [14 empty] | 1463
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1992 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 25
12. |  |  | Reactor I&C Systems | [34 empty] | 17
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 17
14. |  |  | Safety Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 77
16. |  |  | Steam generation systems | [34 empty] | 11
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 35
32. |  |  | Feedwater and Main Steam System | [34 empty] | 17
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 111
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 110
Total | [37 empty] | 460

## ST. ALBAN-1
2020 Operating Experience
FR-48 | [8 empty] | ST. ALBAN-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-01-29
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-08-30
Gross electrical power | [12 empty] | : |  |  | 1381 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-05-01
Reference unit power (net) | [12 empty] | : |  |  | 1335 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7603.38 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.63 %
Energy Availability Factor (EAF) | [18 empty] | : | 65.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.53 %
Unit Capability Factor (UCF) | [18 empty] | : | 70.87 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 24.6 %
Load Factor (LF) | [18 empty] | : | 64.84 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 5.36 %
Operating Factor (OF) | [18 empty] | : | 68.69 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2750 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 984.95 | 923.58 |  |  |  | 932.06 |  | 640.81 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 375.89 |  |  |  | 896.25 |  |  | 982.76 |  |  | 913.00 | [9 empty] | 954.09 |  |  | 7603.38
EAF [%] |  |  |  |  | 99.25 | 99.47 |  |  |  | 93.98 |  | 66.68 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 37.85 |  |  |  | 93.55 |  |  | 98.95 |  |  | 98.98 | [9 empty] | 99.59 |  |  | 65.52
UCF [%] |  |  |  |  | 99.50 | 99.69 |  |  |  | 99.97 |  | 79.63 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 38.40 |  | 40.32 |  |  |  | 95.39 |  |  | 99.45 |  |  | 99.90 | [9 empty] | 99.81 |  |  | 70.87
LF [%] |  |  |  |  | 99.17 | 99.40 |  |  |  | 93.97 |  | 66.67 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 37.85 |  |  |  | 93.24 |  |  | 98.81 |  |  | 94.99 | [9 empty] | 96.06 |  |  | 64.84
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 80.28 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 49.33 |  |  |  | 96.94 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 68.69
FLR [%] |  |  |  |  | 0.37 | 0.21 |  |  |  | 0.03 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.25 |  |  |  | 4.10 |  |  | 0.42 |  |  | 0.10 | [9 empty] | 0.14 |  |  | 0.63
UCL [%] |  |  |  |  | 0.37 | 0.21 |  |  |  | 0.03 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 48.23 |  |  |  | 4.08 |  |  | 0.42 |  |  | 0.10 | [9 empty] | 0.14 |  |  | 4.53
PUF [%] |  |  |  |  | 0.13 | 0.10 |  |  |  | 0.00 |  | 20.36 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 61.60 |  | 11.45 |  |  |  | 0.53 |  |  | 0.13 |  |  | 0.00 | [9 empty] | 0.05 |  |  | 24.60
XUF [%] |  |  |  |  | 0.26 | 0.22 |  |  |  | 5.99 |  | 12.95 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 38.39 |  | 2.46 |  |  |  | 1.84 |  |  | 0.49 |  |  | 0.92 | [9 empty] | 0.22 |  |  | 5.36
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 278552.2 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.17 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.73 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.09 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.06 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.85 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.82 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.33 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.74 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 6722.90 |  |  | 5449 |  |  |  | 1300 | [10 empty] | 66.38 |  |  |  | 67.62 | [5 empty] | 51.14 |  |  | 54.11 |  |  |  | 17.05 |  | 13.90 | [8 empty] | 18.48 |  |  |  |  | 1.24
1987 |  |  |  | 6101.60 |  |  | 4944 |  |  |  | 1300 | [10 empty] | 56.16 |  |  |  | 56.61 | [5 empty] | 53.58 |  |  | 56.44 |  |  |  | 20.02 |  | 14.17 | [8 empty] | 29.21 |  |  |  |  | 0.45
1988 |  |  |  | 4562.00 |  |  | 3721 |  |  |  | 1335 | [10 empty] | 82.37 |  |  |  | 83.39 | [5 empty] | 38.90 |  |  | 42.36 |  |  |  | 11.01 |  | 10.32 | [8 empty] | 6.29 |  |  |  |  | 1.01
1989 |  |  |  | 6781.29 |  |  | 5907 |  |  |  | 1335 | [10 empty] | 63.54 |  |  |  | 70.68 | [5 empty] | 57.99 |  |  | 67.43 |  |  |  | 10.17 |  | 8.00 | [8 empty] | 21.32 |  |  |  |  | 7.14
1990 |  |  |  | 7799.06 |  |  | 6295 |  |  |  | 1335 | [10 empty] | 68.64 |  |  |  | 70.38 | [5 empty] | 66.69 |  |  | 71.86 |  |  |  | 15.39 |  | 12.81 | [8 empty] | 16.81 |  |  |  |  | 1.74
1991 |  |  |  | 7935.34 |  |  | 6380 |  |  |  | 1335 | [10 empty] | 73.32 |  |  |  | 74.44 | [5 empty] | 67.85 |  |  | 72.83 |  |  |  | 12.62 |  | 10.75 | [8 empty] | 14.82 |  |  |  |  | 1.11
1992 |  |  |  | 4812.15 |  |  | 3775 |  |  |  | 1335 | [10 empty] | 42.11 |  |  |  | 42.12 | [5 empty] | 41.04 |  |  | 42.98 |  |  |  | 45.73 |  | 35.50 | [8 empty] | 22.38 |  |  |  |  | 0.01
1993 |  |  |  | 7376.03 |  |  | 6010 |  |  |  | 1335 | [10 empty] | 65.75 |  |  |  | 68.18 | [5 empty] | 63.07 |  |  | 68.61 |  |  |  | 17.44 |  | 14.40 | [8 empty] | 17.42 |  |  |  |  | 2.43
1994 |  |  |  | 7575.62 |  |  | 6777 |  |  |  | 1335 | [10 empty] | 93.82 |  |  |  | 94.52 | [5 empty] | 64.78 |  |  | 77.36 |  |  |  | 5.46 |  | 5.45 | [8 empty] | 0.02 |  |  |  |  | 0.70
1995 |  |  |  | 8535.72 |  |  | 7197 |  |  |  | 1335 | [10 empty] | 78.17 |  |  |  | 81.11 | [5 empty] | 72.99 |  |  | 82.16 |  |  |  | 2.27 |  | 1.88 | [8 empty] | 17.00 |  |  |  |  | 2.95
1996 |  |  |  | 8126.62 |  |  | 6950 |  |  |  | 1335 | [10 empty] | 83.10 |  |  |  | 83.67 | [5 empty] | 69.30 |  |  | 79.12 |  |  |  | 3.91 |  | 3.40 | [8 empty] | 12.92 |  |  |  |  | 0.57
1997 |  |  |  | 7112.76 |  |  | 5833 |  |  |  | 1335 | [10 empty] | 63.62 |  |  |  | 65.48 | [5 empty] | 60.82 |  |  | 66.59 |  |  |  | 12.82 |  | 9.63 | [8 empty] | 24.89 |  |  |  |  | 1.86
1998 |  |  |  | 8255.92 |  |  | 6802 |  |  |  | 1335 | [10 empty] | 89.95 |  |  |  | 90.64 | [5 empty] | 70.60 |  |  | 77.65 |  |  |  | 8.95 |  | 8.91 | [8 empty] | 0.45 |  |  |  |  | 0.69
1999 |  |  |  | 9240.59 |  |  | 7656 |  |  |  | 1335 | [10 empty] | 85.68 |  |  |  | 86.27 | [5 empty] | 79.02 |  |  | 87.40 |  |  |  | 2.52 |  | 2.23 | [8 empty] | 11.50 |  |  |  |  | 0.59
2000 |  |  |  | 8027.83 |  |  | 6494 |  |  |  | 1335 | [10 empty] | 71.39 |  |  |  | 72.16 | [5 empty] | 68.46 |  |  | 73.93 |  |  |  | 12.97 |  | 10.76 | [8 empty] | 17.08 |  |  |  |  | 0.77
2001 |  |  |  | 9298.49 |  |  | 7843 |  |  |  | 1335 | [10 empty] | 89.61 |  |  |  | 89.84 | [5 empty] | 79.51 |  |  | 89.53 |  |  |  | 9.55 |  | 9.49 | [8 empty] | 0.68 |  |  |  |  | 0.23
2002 |  |  |  | 8768.82 |  |  | 7275 |  |  |  | 1335 | [10 empty] | 79.60 |  |  |  | 81.04 | [5 empty] | 74.98 |  |  | 83.05 |  |  |  | 6.57 |  | 5.70 | [8 empty] | 13.26 |  |  |  |  | 1.44
2003 |  |  |  | 8691.94 |  |  | 7029 |  |  |  | 1335 | [10 empty] | 78.00 |  |  |  | 80.58 | [5 empty] | 74.32 |  |  | 80.24 |  |  |  | 2.24 |  | 1.85 | [8 empty] | 17.58 |  |  |  |  | 2.57
2004 |  |  |  | 10127.42 |  |  | 8283 |  |  |  | 1335 | [10 empty] | 95.28 |  |  |  | 96.62 | [5 empty] | 86.36 |  |  | 94.30 |  |  |  | 3.37 |  | 3.37 | [8 empty] | 0.02 |  |  |  |  | 1.33
2005 |  |  |  | 9697.02 |  |  | 7949 |  |  |  | 1335 | [10 empty] | 85.96 |  |  |  | 88.64 | [5 empty] | 82.91 |  |  | 90.73 |  |  |  | 1.71 |  | 1.54 | [8 empty] | 9.81 |  |  |  |  | 2.69
2006 |  |  |  | 8882.10 |  |  | 7342 |  |  |  | 1335 | [10 empty] | 78.35 |  |  |  | 82.46 | [5 empty] | 75.95 |  |  | 83.81 |  |  |  | 3.41 |  | 2.91 | [8 empty] | 14.63 |  |  |  |  | 4.11
2007 |  |  |  | 6342.04 |  |  | 4987 |  |  |  | 1335 | [10 empty] | 54.55 |  |  |  | 55.89 | [5 empty] | 54.23 |  |  | 56.93 |  |  |  | 5.08 |  | 3.40 | [8 empty] | 40.71 |  |  |  |  | 1.34
2008 |  |  |  | 5610.15 |  |  | 4577 |  |  |  | 1335 | [10 empty] | 49.16 |  |  |  | 49.33 | [5 empty] | 47.84 |  |  | 52.11 |  |  |  | 46.41 |  | 49.43 | [8 empty] | 1.25 |  |  |  |  | 0.17
2009 |  |  |  | 8681.78 |  |  | 6881 |  |  |  | 1335 | [10 empty] | 74.60 |  |  |  | 76.69 | [5 empty] | 74.24 |  |  | 78.55 |  |  |  | 7.66 |  | 13.97 | [8 empty] | 9.34 |  |  |  |  | 2.09
2010 |  |  |  | 10759.91 |  |  | 8465 |  |  |  | 1335 | [10 empty] | 92.33 |  |  |  | 93.10 | [5 empty] | 92.01 |  |  | 96.63 |  |  |  | 6.86 |  | 6.86 | [8 empty] | 0.03 |  |  |  |  | 0.77
2011 |  |  |  | 5946.79 |  |  | 5202 |  |  |  | 1335 | [10 empty] | 54.57 |  |  |  | 57.07 | [5 empty] | 50.85 |  |  | 59.38 |  |  |  | 7.51 |  | 21.77 | [8 empty] | 21.15 |  |  |  |  | 2.50
2012 |  |  |  | 9171.05 |  |  | 7422 |  |  |  | 1335 | [10 empty] | 82.81 |  |  |  | 83.11 | [5 empty] | 78.21 |  |  | 84.49 |  |  |  | 2.45 |  | 8.60 | [8 empty] | 8.29 |  |  |  |  | 0.30
2013 |  |  |  | 10069.65 |  |  | 8498 |  |  |  | 1335 | [10 empty] | 97.38 |  |  |  | 98.71 | [5 empty] | 86.11 |  |  | 97.01 |  |  |  | 1.26 |  | 1.26 | [8 empty] | 0.03 |  |  |  |  | 1.34
2014 |  |  |  | 6739.26 |  |  | 5918 |  |  |  | 1335 | [10 empty] | 72.44 |  |  |  | 73.89 | [5 empty] | 57.63 |  |  | 67.56 |  |  |  | 2.82 |  | 2.42 | [8 empty] | 23.69 |  |  |  |  | 1.45
2015 |  |  |  | 9047.80 |  |  | 7538 |  |  |  | 1335 | [10 empty] | 81.10 |  |  |  | 86.97 | [5 empty] | 77.37 |  |  | 86.05 |  |  |  | 3.07 |  | 2.76 | [8 empty] | 10.27 |  |  |  |  | 5.88
2016 |  |  |  | 9010.70 |  |  | 8069 |  |  |  | 1335 | [10 empty] | 86.46 |  |  |  | 98.38 | [5 empty] | 76.84 |  |  | 91.86 |  |  |  | 1.55 |  | 1.55 | [8 empty] | 0.07 |  |  |  |  | 11.93
2017 |  |  |  | 5900.57 |  |  | 5100 |  |  |  | 1335 | [10 empty] | 51.39 |  |  |  | 55.80 | [5 empty] | 50.46 |  |  | 58.22 |  |  |  | 1.92 |  | 1.09 | [8 empty] | 43.11 |  |  |  |  | 4.41
2018 |  |  |  | 8028.05 |  |  | 6361 |  |  |  | 1335 | [10 empty] | 69.66 |  |  |  | 74.70 | [5 empty] | 68.65 |  |  | 72.61 |  |  |  | 6.39 |  | 7.74 | [8 empty] | 17.56 |  |  |  |  | 5.04
2019 |  |  |  | 10312.99 |  |  | 8456 |  |  |  | 1335 | [10 empty] | 89.47 |  |  |  | 92.44 | [5 empty] | 88.19 |  |  | 96.53 |  |  |  | 7.47 |  | 7.46 | [8 empty] | 0.10 |  |  |  |  | 2.97
2020 |  |  |  | 7603.38 |  |  | 6034 |  |  |  | 1335 | [10 empty] | 65.52 |  |  |  | 70.87 | [5 empty] | 64.84 |  |  | 68.69 |  |  |  | 0.63 |  | 4.53 | [8 empty] | 24.60 |  |  |  |  | 5.36
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 644
B. |  | Refuelling without maintenance | [35 empty] | 125
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 927 |  |  |  | 7
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 47 |  |  |  | 0
E. |  | Testing of plant systems or components | [35 empty] | 25
H. |  | Nuclear regulatory requirements | [39 empty] | 41
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 19
L. |  | Human factor related | [39 empty] | 5
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 13
O. |  | Load dispatching, prioritization | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 8 | [11 empty] | 7
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 0 | [11 empty] | 39
Z. |  | Other | [39 empty] | 14 | [11 empty] | 0
Subtotal | [37 empty] | 1124 |  |  |  | 719 | [11 empty] | 79
Total | [22 empty] | 0 | [14 empty] | 1922
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 42
12. |  |  | Reactor I&C Systems | [34 empty] | 26
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 19
14. |  |  | Safety Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 81
16. |  |  | Steam generation systems | [34 empty] | 5
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 115
32. |  |  | Feedwater and Main Steam System | [34 empty] | 56
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 61
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 163
42. |  |  | Electrical Power Supply Systems | [34 empty] | 45
Total | [37 empty] | 639

## ST. ALBAN-2
2020 Operating Experience
FR-49 | [8 empty] | ST. ALBAN-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / P4 REP 1300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-07-31
Thermal power | [12 empty] | : |  |  | 3817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-07-03
Gross electrical power | [12 empty] | : |  |  | 1381 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-03-01
Reference unit power (net) | [12 empty] | : |  |  | 1335 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.1
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.95
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9928.37 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.16 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.94 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.06 %
Load Factor (LF) | [18 empty] | : | 84.67 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.78 %
Operating Factor (OF) | [18 empty] | : | 98.46 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 135 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 790.82 | 666.52 |  |  |  | 815.72 |  | 758.75 | [8 empty] | 793.89 |  |  | 868.53 | [6 empty] | 878.27 |  | 862.46 |  |  |  | 742.32 |  |  | 890.70 |  |  | 887.93 | [9 empty] | 972.45 |  |  | 9928.37
EAF [%] |  |  |  |  | 81.93 | 82.06 |  |  |  | 96.91 |  | 99.23 | [8 empty] | 99.18 |  |  | 98.44 | [6 empty] | 94.48 |  | 95.95 |  |  |  | 84.14 |  |  | 99.09 |  |  | 98.98 | [9 empty] | 98.92 |  |  | 94.16
UCF [%] |  |  |  |  | 99.61 | 86.42 |  |  |  | 99.67 |  | 99.67 | [8 empty] | 99.57 |  |  | 99.43 | [6 empty] | 95.52 |  | 98.90 |  |  |  | 98.93 |  |  | 99.10 |  |  | 98.98 | [9 empty] | 98.92 |  |  | 97.94
LF [%] |  |  |  |  | 79.62 | 71.73 |  |  |  | 82.24 |  | 78.94 | [8 empty] | 79.93 |  |  | 90.36 | [6 empty] | 88.42 |  | 86.83 |  |  |  | 77.23 |  |  | 89.56 |  |  | 92.38 | [9 empty] | 97.91 |  |  | 84.67
OF [%] |  |  |  |  | 100.00 | 87.50 |  |  |  | 100.00 |  | 96.67 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 96.91 |  | 100.00 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.46
FLR [%] |  |  |  |  | 0.37 | 13.53 |  |  |  | 0.33 |  | 0.27 | [8 empty] | 0.37 |  |  | 0.57 | [6 empty] | 4.44 |  | 1.10 |  |  |  | 0.86 |  |  | 0.70 |  |  | 0.97 | [9 empty] | 1.08 |  |  | 2.00
UCL [%] |  |  |  |  | 0.37 | 13.53 |  |  |  | 0.33 |  | 0.27 | [8 empty] | 0.37 |  |  | 0.57 | [6 empty] | 4.44 |  | 1.10 |  |  |  | 0.86 |  |  | 0.70 |  |  | 0.97 | [9 empty] | 1.08 |  |  | 2.00
PUF [%] |  |  |  |  | 0.03 | 0.05 |  |  |  | 0.00 |  | 0.06 | [8 empty] | 0.06 |  |  | 0.00 | [6 empty] | 0.04 |  | 0.00 |  |  |  | 0.21 |  |  | 0.20 |  |  | 0.05 | [9 empty] | 0.00 |  |  | 0.06
XUF [%] |  |  |  |  | 17.68 | 4.36 |  |  |  | 2.77 |  | 0.44 | [8 empty] | 0.39 |  |  | 0.98 | [6 empty] | 1.05 |  | 2.95 |  |  |  | 14.79 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.78
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 273193.02 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 8.77 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.37 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.46 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.16 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.38 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 68.51 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.79 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 6952.20 |  |  | 6094 |  |  |  | 1300 | [10 empty] | 79.01 |  |  |  | 79.06 | [5 empty] | 59.07 |  |  | 68.27 |  |  |  | 20.94 |  | 20.94 | [8 empty] | 0.00 |  |  |  |  | 0.05
1988 |  |  |  | 5185.00 |  |  | 4308 |  |  |  | 1335 | [10 empty] | 46.48 |  |  |  | 47.29 | [5 empty] | 44.22 |  |  | 49.04 |  |  |  | 31.63 |  | 21.88 | [8 empty] | 30.83 |  |  |  |  | 0.81
1989 |  |  |  | 6126.50 |  |  | 4806 |  |  |  | 1335 | [10 empty] | 56.23 |  |  |  | 57.46 | [5 empty] | 52.39 |  |  | 54.86 |  |  |  | 33.18 |  | 28.53 | [8 empty] | 14.01 |  |  |  |  | 1.23
1990 |  |  |  | 6070.64 |  |  | 5146 |  |  |  | 1335 | [10 empty] | 56.52 |  |  |  | 60.26 | [5 empty] | 51.91 |  |  | 58.74 |  |  |  | 23.59 |  | 18.60 | [8 empty] | 21.14 |  |  |  |  | 3.74
1991 |  |  |  | 7962.55 |  |  | 6484 |  |  |  | 1335 | [10 empty] | 71.13 |  |  |  | 73.29 | [5 empty] | 68.09 |  |  | 74.02 |  |  |  | 8.73 |  | 7.01 | [8 empty] | 19.70 |  |  |  |  | 2.16
1992 |  |  |  | 6375.15 |  |  | 5405 |  |  |  | 1335 | [10 empty] | 62.34 |  |  |  | 64.33 | [5 empty] | 54.36 |  |  | 61.53 |  |  |  | 20.15 |  | 16.23 | [8 empty] | 19.44 |  |  |  |  | 1.99
1993 |  |  |  | 6433.10 |  |  | 6121 |  |  |  | 1335 | [10 empty] | 83.07 |  |  |  | 90.86 | [5 empty] | 55.01 |  |  | 69.87 |  |  |  | 8.11 |  | 8.02 | [8 empty] | 1.12 |  |  |  |  | 7.78
1994 |  |  |  | 7125.76 |  |  | 6074 |  |  |  | 1335 | [10 empty] | 73.00 |  |  |  | 74.87 | [5 empty] | 60.93 |  |  | 69.34 |  |  |  | 6.29 |  | 5.02 | [8 empty] | 20.11 |  |  |  |  | 1.86
1995 |  |  |  | 7751.41 |  |  | 6763 |  |  |  | 1335 | [10 empty] | 72.69 |  |  |  | 76.09 | [5 empty] | 66.28 |  |  | 77.20 |  |  |  | 10.39 |  | 8.82 | [8 empty] | 15.09 |  |  |  |  | 3.40
1996 |  |  |  | 8344.63 |  |  | 7247 |  |  |  | 1335 | [10 empty] | 79.67 |  |  |  | 81.54 | [5 empty] | 71.16 |  |  | 82.50 |  |  |  | 3.68 |  | 3.11 | [8 empty] | 15.34 |  |  |  |  | 1.88
1997 |  |  |  | 8049.72 |  |  | 7072 |  |  |  | 1335 | [10 empty] | 91.80 |  |  |  | 92.33 | [5 empty] | 68.83 |  |  | 80.73 |  |  |  | 7.25 |  | 7.21 | [8 empty] | 0.46 |  |  |  |  | 0.53
1998 |  |  |  | 6555.74 |  |  | 5654 |  |  |  | 1335 | [10 empty] | 63.23 |  |  |  | 66.72 | [5 empty] | 56.06 |  |  | 64.54 |  |  |  | 11.90 |  | 9.02 | [8 empty] | 24.26 |  |  |  |  | 3.49
1999 |  |  |  | 8606.97 |  |  | 7188 |  |  |  | 1335 | [10 empty] | 79.30 |  |  |  | 80.33 | [5 empty] | 73.60 |  |  | 82.05 |  |  |  | 8.76 |  | 7.71 | [8 empty] | 11.96 |  |  |  |  | 1.03
2000 |  |  |  | 8729.60 |  |  | 7202 |  |  |  | 1335 | [10 empty] | 79.03 |  |  |  | 86.47 | [5 empty] | 74.44 |  |  | 81.99 |  |  |  | 3.56 |  | 3.19 | [8 empty] | 10.34 |  |  |  |  | 7.45
2001 |  |  |  | 8654.77 |  |  | 7657 |  |  |  | 1335 | [10 empty] | 91.30 |  |  |  | 91.41 | [5 empty] | 74.01 |  |  | 87.41 |  |  |  | 2.03 |  | 1.89 | [8 empty] | 6.69 |  |  |  |  | 0.11
2002 |  |  |  | 8290.64 |  |  | 6950 |  |  |  | 1335 | [10 empty] | 75.20 |  |  |  | 77.33 | [5 empty] | 70.89 |  |  | 79.34 |  |  |  | 6.52 |  | 5.39 | [8 empty] | 17.28 |  |  |  |  | 2.13
2003 |  |  |  | 9254.77 |  |  | 7558 |  |  |  | 1335 | [10 empty] | 83.01 |  |  |  | 87.77 | [5 empty] | 79.14 |  |  | 86.28 |  |  |  | 0.52 |  | 0.45 | [8 empty] | 11.77 |  |  |  |  | 4.76
2004 |  |  |  | 10476.49 |  |  | 8709 |  |  |  | 1335 | [10 empty] | 97.73 |  |  |  | 97.77 | [5 empty] | 89.34 |  |  | 99.15 |  |  |  | 1.74 |  | 1.73 | [8 empty] | 0.49 |  |  |  |  | 0.04
2005 |  |  |  | 7237.98 |  |  | 6361 |  |  |  | 1335 | [10 empty] | 65.22 |  |  |  | 70.61 | [5 empty] | 61.88 |  |  | 72.61 |  |  |  | 16.03 |  | 13.68 | [8 empty] | 15.71 |  |  |  |  | 5.38
2006 |  |  |  | 7584.24 |  |  | 6292 |  |  |  | 1335 | [10 empty] | 67.40 |  |  |  | 69.14 | [5 empty] | 64.85 |  |  | 71.83 |  |  |  | 21.25 |  | 19.57 | [8 empty] | 11.28 |  |  |  |  | 1.74
2007 |  |  |  | 10476.05 |  |  | 8660 |  |  |  | 1335 | [10 empty] | 95.02 |  |  |  | 95.65 | [5 empty] | 89.58 |  |  | 98.86 |  |  |  | 4.33 |  | 4.33 | [8 empty] | 0.02 |  |  |  |  | 0.62
2008 |  |  |  | 6270.91 |  |  | 5320 |  |  |  | 1335 | [10 empty] | 54.70 |  |  |  | 58.09 | [5 empty] | 53.48 |  |  | 60.56 |  |  |  | 5.25 |  | 8.33 | [8 empty] | 33.58 |  |  |  |  | 3.39
2009 |  |  |  | 8753.18 |  |  | 7052 |  |  |  | 1335 | [10 empty] | 78.37 |  |  |  | 81.82 | [5 empty] | 74.85 |  |  | 80.50 |  |  |  | 9.69 |  | 10.26 | [8 empty] | 7.92 |  |  |  |  | 3.45
2010 |  |  |  | 8297.53 |  |  | 6659 |  |  |  | 1335 | [10 empty] | 73.03 |  |  |  | 76.19 | [5 empty] | 70.95 |  |  | 76.02 |  |  |  | 2.30 |  | 9.78 | [8 empty] | 14.03 |  |  |  |  | 3.16
2011 |  |  |  | 10599.69 |  |  | 8474 |  |  |  | 1335 | [10 empty] | 94.13 |  |  |  | 95.33 | [5 empty] | 90.64 |  |  | 96.74 |  |  |  | 4.55 |  | 4.55 | [8 empty] | 0.12 |  |  |  |  | 1.20
2012 |  |  |  | 8662.28 |  |  | 7044 |  |  |  | 1335 | [10 empty] | 77.41 |  |  |  | 78.39 | [5 empty] | 73.87 |  |  | 80.19 |  |  |  | 1.24 |  | 12.13 | [8 empty] | 9.47 |  |  |  |  | 0.98
2013 |  |  |  | 7287.87 |  |  | 6032 |  |  |  | 1335 | [10 empty] | 66.54 |  |  |  | 66.80 | [5 empty] | 62.32 |  |  | 68.86 |  |  |  | 9.50 |  | 11.95 | [8 empty] | 21.25 |  |  |  |  | 0.26
2014 |  |  |  | 10438.17 |  |  | 8684 |  |  |  | 1335 | [10 empty] | 96.57 |  |  |  | 97.45 | [5 empty] | 89.26 |  |  | 99.13 |  |  |  | 2.36 |  | 2.35 | [8 empty] | 0.19 |  |  |  |  | 0.89
2015 |  |  |  | 9426.74 |  |  | 7930 |  |  |  | 1335 | [10 empty] | 85.74 |  |  |  | 89.08 | [5 empty] | 80.61 |  |  | 90.53 |  |  |  | 1.02 |  | 0.92 | [8 empty] | 10.00 |  |  |  |  | 3.34
2016 |  |  |  | 8339.93 |  |  | 7056 |  |  |  | 1335 | [10 empty] | 75.04 |  |  |  | 77.18 | [5 empty] | 71.12 |  |  | 80.33 |  |  |  | 3.19 |  | 2.56 | [8 empty] | 20.26 |  |  |  |  | 2.14
2017 |  |  |  | 8493.06 |  |  | 7023 |  |  |  | 1335 | [10 empty] | 77.61 |  |  |  | 92.52 | [5 empty] | 72.62 |  |  | 80.17 |  |  |  | 7.37 |  | 7.36 | [8 empty] | 0.13 |  |  |  |  | 14.91
2018 |  |  |  | 5530.66 |  |  | 4805 |  |  |  | 1335 | [10 empty] | 48.84 |  |  |  | 51.97 | [5 empty] | 47.29 |  |  | 54.85 |  |  |  | 2.44 |  | 1.42 | [8 empty] | 46.61 |  |  |  |  | 3.13
2019 |  |  |  | 8171.02 |  |  | 6622 |  |  |  | 1335 | [10 empty] | 72.77 |  |  |  | 74.32 | [5 empty] | 69.87 |  |  | 75.59 |  |  |  | 4.87 |  | 3.81 | [8 empty] | 21.87 |  |  |  |  | 1.55
2020 |  |  |  | 9928.37 |  |  | 8649 |  |  |  | 1335 | [10 empty] | 94.16 |  |  |  | 97.94 | [5 empty] | 84.67 |  |  | 98.46 |  |  |  | 2.00 |  | 2.00 | [8 empty] | 0.06 |  |  |  |  | 3.78
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 631
B. |  | Refuelling without maintenance | [35 empty] | 65
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 977 |  |  |  | 20
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 58
E. |  | Testing of plant systems or components | [35 empty] | 43 |  |  |  | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 20 | [11 empty] | 0
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 24
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 1 | [11 empty] | 16
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 33
Z. |  | Other | [39 empty] | 10 | [11 empty] | 0
Subtotal | [37 empty] | 1143 |  |  |  | 683 | [11 empty] | 78
Total | [22 empty] | 0 | [14 empty] | 1904
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 41
12. |  |  | Reactor I&C Systems | [34 empty] | 63
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 16
15. |  |  | Reactor Cooling Systems | [34 empty] | 36
16. |  |  | Steam generation systems | [34 empty] | 82
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 20
31. |  |  | Turbine and auxiliaries | [34 empty] | 101
32. |  |  | Feedwater and Main Steam System | [34 empty] | 50
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 53
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 114
42. |  |  | Electrical Power Supply Systems | [34 empty] | 30
Total | [37 empty] | 624

## ST. LAURENT B-1
2020 Operating Experience
FR-17 | [8 empty] | ST. LAURENT B-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP2 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-05-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-01-21
Gross electrical power | [12 empty] | : |  |  | 956 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-08-01
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5698.35 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 9.56 %
Energy Availability Factor (EAF) | [18 empty] | : | 71.59 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 15.06 %
Unit Capability Factor (UCF) | [18 empty] | : | 73.83 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.12 %
Load Factor (LF) | [18 empty] | : | 70.9 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.24 %
Operating Factor (OF) | [18 empty] | : | 77.3 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1994 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 579.19 | 597.52 |  |  |  | 652.41 |  | 578.08 | [8 empty] | 621.51 |  |  | 305.37 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 493.19 |  |  | 609.45 |  |  | 609.99 | [9 empty] | 651.66 |  |  | 5698.35
EAF [%] |  |  |  |  | 85.58 | 94.04 |  |  |  | 97.64 |  | 92.40 | [8 empty] | 91.75 |  |  | 46.40 | [6 empty] | 0.03 |  | 0.01 |  |  |  | 74.99 |  |  | 89.60 |  |  | 92.80 | [9 empty] | 95.95 |  |  | 71.59
UCF [%] |  |  |  |  | 97.86 | 97.22 |  |  |  | 97.90 |  | 93.98 | [8 empty] | 93.39 |  |  | 48.03 | [6 empty] | 0.03 |  | 0.01 |  |  |  | 76.44 |  |  | 91.15 |  |  | 93.71 | [9 empty] | 98.26 |  |  | 73.83
LF [%] |  |  |  |  | 85.08 | 93.83 |  |  |  | 95.96 |  | 87.75 | [8 empty] | 91.30 |  |  | 46.35 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 74.86 |  |  | 89.40 |  |  | 92.59 | [9 empty] | 95.73 |  |  | 70.90
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 48.89 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 87.92 |  |  | 93.15 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 77.30
FLR [%] |  |  |  |  | 1.67 | 2.67 |  |  |  | 1.61 |  | 5.93 | [8 empty] | 6.49 |  |  | 51.92 | [6 empty] | 99.55 |  | 0.00 |  |  |  | 1.43 |  |  | 8.74 |  |  | 6.03 | [9 empty] | 1.63 |  |  | 9.56
UCL [%] |  |  |  |  | 1.66 | 2.66 |  |  |  | 1.60 |  | 5.92 | [8 empty] | 6.48 |  |  | 51.86 | [6 empty] | 6.72 |  | 73.92 |  |  |  | 13.22 |  |  | 8.72 |  |  | 6.02 | [9 empty] | 1.63 |  |  | 15.06
PUF [%] |  |  |  |  | 0.49 | 0.11 |  |  |  | 0.51 |  | 0.10 | [8 empty] | 0.13 |  |  | 0.11 | [6 empty] | 93.25 |  | 26.07 |  |  |  | 10.34 |  |  | 0.13 |  |  | 0.27 | [9 empty] | 0.11 |  |  | 11.12
XUF [%] |  |  |  |  | 12.27 | 3.18 |  |  |  | 0.26 |  | 1.58 | [8 empty] | 1.64 |  |  | 1.63 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 1.45 |  |  | 1.55 |  |  | 0.91 | [9 empty] | 2.31 |  |  | 2.24
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 219938.53 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.64 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.87 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.1 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.23 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.38 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 3670.00 |  |  | 4382 |  |  |  | 880 | [10 empty] | 91.99 |  |  |  | 91.99 | [5 empty] | 91.89 |  |  | 93.85 |  |  |  | 8.01 |  | 8.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 4401.00 |  |  | 5042 |  |  |  | 880 | [10 empty] | 55.95 |  |  |  | 55.95 | [5 empty] | 56.93 |  |  | 57.40 |  |  |  | 22.37 |  | 16.12 | [8 empty] | 27.92 |  |  |  |  | 0.00
1985 |  |  |  | 5630.40 |  |  | 6827 |  |  |  | 880 | [10 empty] | 75.00 |  |  |  | 76.09 | [5 empty] | 73.04 |  |  | 77.93 |  |  |  | 10.66 |  | 9.08 | [8 empty] | 14.83 |  |  |  |  | 1.09
1986 |  |  |  | 5476.40 |  |  | 7144 |  |  |  | 880 | [10 empty] | 79.72 |  |  |  | 79.78 | [5 empty] | 71.04 |  |  | 81.55 |  |  |  | 10.61 |  | 9.47 | [8 empty] | 10.75 |  |  |  |  | 0.06
1987 |  |  |  | 5171.30 |  |  | 6667 |  |  |  | 880 | [10 empty] | 76.14 |  |  |  | 76.83 | [5 empty] | 67.08 |  |  | 76.11 |  |  |  | 9.98 |  | 8.51 | [8 empty] | 14.66 |  |  |  |  | 0.69
1988 |  |  |  | 5721.00 |  |  | 6464 |  |  |  | 915 | [10 empty] | 75.95 |  |  |  | 76.30 | [5 empty] | 71.18 |  |  | 73.59 |  |  |  | 15.48 |  | 13.97 | [8 empty] | 9.73 |  |  |  |  | 0.35
1989 |  |  |  | 6609.76 |  |  | 7699 |  |  |  | 915 | [10 empty] | 82.69 |  |  |  | 85.43 | [5 empty] | 82.46 |  |  | 87.89 |  |  |  | 9.30 |  | 8.76 | [8 empty] | 5.81 |  |  |  |  | 2.73
1990 |  |  |  | 6113.67 |  |  | 7089 |  |  |  | 915 | [10 empty] | 84.12 |  |  |  | 86.26 | [5 empty] | 76.27 |  |  | 80.92 |  |  |  | 7.98 |  | 7.48 | [8 empty] | 6.26 |  |  |  |  | 2.15
1991 |  |  |  | 4005.40 |  |  | 4736 |  |  |  | 915 | [10 empty] | 52.29 |  |  |  | 53.65 | [5 empty] | 49.97 |  |  | 54.06 |  |  |  | 32.18 |  | 25.46 | [8 empty] | 20.89 |  |  |  |  | 1.36
1992 |  |  |  | 5621.12 |  |  | 6690 |  |  |  | 915 | [10 empty] | 74.05 |  |  |  | 75.42 | [5 empty] | 69.94 |  |  | 76.16 |  |  |  | 9.59 |  | 8.00 | [8 empty] | 16.58 |  |  |  |  | 1.37
1993 |  |  |  | 5668.51 |  |  | 6821 |  |  |  | 915 | [10 empty] | 72.38 |  |  |  | 75.27 | [5 empty] | 70.72 |  |  | 77.87 |  |  |  | 11.93 |  | 10.20 | [8 empty] | 14.54 |  |  |  |  | 2.89
1994 |  |  |  | 6095.73 |  |  | 7252 |  |  |  | 915 | [10 empty] | 85.11 |  |  |  | 87.05 | [5 empty] | 76.05 |  |  | 82.79 |  |  |  | 1.53 |  | 1.35 | [8 empty] | 11.60 |  |  |  |  | 1.93
1995 |  |  |  | 4442.99 |  |  | 5211 |  |  |  | 915 | [10 empty] | 60.27 |  |  |  | 64.30 | [5 empty] | 55.43 |  |  | 59.49 |  |  |  | 0.89 |  | 0.58 | [8 empty] | 35.13 |  |  |  |  | 4.03
1996 |  |  |  | 5541.09 |  |  | 6888 |  |  |  | 915 | [10 empty] | 78.78 |  |  |  | 79.06 | [5 empty] | 68.94 |  |  | 78.42 |  |  |  | 17.99 |  | 17.34 | [8 empty] | 3.60 |  |  |  |  | 0.27
1997 |  |  |  | 5132.60 |  |  | 6404 |  |  |  | 915 | [10 empty] | 75.43 |  |  |  | 76.15 | [5 empty] | 64.03 |  |  | 73.11 |  |  |  | 14.88 |  | 13.31 | [8 empty] | 10.54 |  |  |  |  | 0.72
1998 |  |  |  | 6030.71 |  |  | 7366 |  |  |  | 915 | [10 empty] | 82.11 |  |  |  | 84.57 | [5 empty] | 75.24 |  |  | 84.09 |  |  |  | 0.83 |  | 0.71 | [8 empty] | 14.72 |  |  |  |  | 2.45
1999 |  |  |  | 5062.64 |  |  | 6207 |  |  |  | 915 | [10 empty] | 67.92 |  |  |  | 69.71 | [5 empty] | 63.16 |  |  | 70.86 |  |  |  | 21.66 |  | 19.28 | [8 empty] | 11.02 |  |  |  |  | 1.78
2000 |  |  |  | 5086.74 |  |  | 5957 |  |  |  | 915 | [10 empty] | 65.97 |  |  |  | 66.43 | [5 empty] | 63.29 |  |  | 67.82 |  |  |  | 22.62 |  | 19.42 | [8 empty] | 14.15 |  |  |  |  | 0.46
2001 |  |  |  | 6814.76 |  |  | 7735 |  |  |  | 915 | [10 empty] | 86.40 |  |  |  | 86.84 | [5 empty] | 85.02 |  |  | 88.30 |  |  |  | 2.69 |  | 2.40 | [8 empty] | 10.76 |  |  |  |  | 0.44
2002 |  |  |  | 6637.03 |  |  | 7592 |  |  |  | 915 | [10 empty] | 83.36 |  |  |  | 85.56 | [5 empty] | 82.80 |  |  | 86.67 |  |  |  | 1.31 |  | 1.13 | [8 empty] | 13.31 |  |  |  |  | 2.20
2003 |  |  |  | 6630.44 |  |  | 7658 |  |  |  | 915 | [10 empty] | 82.81 |  |  |  | 86.53 | [5 empty] | 82.72 |  |  | 87.42 |  |  |  | 2.33 |  | 2.06 | [8 empty] | 11.40 |  |  |  |  | 3.73
2004 |  |  |  | 6364.19 |  |  | 7356 |  |  |  | 915 | [10 empty] | 80.41 |  |  |  | 82.41 | [5 empty] | 79.18 |  |  | 83.74 |  |  |  | 1.06 |  | 0.88 | [8 empty] | 16.71 |  |  |  |  | 2.00
2005 |  |  |  | 5384.07 |  |  | 6186 |  |  |  | 915 | [10 empty] | 68.11 |  |  |  | 69.53 | [5 empty] | 67.16 |  |  | 70.61 |  |  |  | 0.86 |  | 4.54 | [8 empty] | 25.93 |  |  |  |  | 1.43
2006 |  |  |  | 6914.14 |  |  | 7973 |  |  |  | 915 | [10 empty] | 88.21 |  |  |  | 88.91 | [5 empty] | 86.26 |  |  | 91.02 |  |  |  | 2.53 |  | 2.75 | [8 empty] | 8.34 |  |  |  |  | 0.70
2007 |  |  |  | 6426.68 |  |  | 7380 |  |  |  | 915 | [10 empty] | 80.55 |  |  |  | 83.06 | [5 empty] | 80.18 |  |  | 84.25 |  |  |  | 2.74 |  | 3.35 | [8 empty] | 13.58 |  |  |  |  | 2.52
2008 |  |  |  | 6894.13 |  |  | 8034 |  |  |  | 915 | [10 empty] | 88.62 |  |  |  | 90.77 | [5 empty] | 85.78 |  |  | 91.46 |  |  |  | 0.51 |  | 1.36 | [8 empty] | 7.87 |  |  |  |  | 2.15
2009 |  |  |  | 6241.46 |  |  | 7298 |  |  |  | 915 | [10 empty] | 78.42 |  |  |  | 83.22 | [5 empty] | 77.87 |  |  | 83.31 |  |  |  | 2.19 |  | 3.01 | [8 empty] | 13.77 |  |  |  |  | 4.79
2010 |  |  |  | 6802.10 |  |  | 7967 |  |  |  | 915 | [10 empty] | 84.89 |  |  |  | 89.81 | [5 empty] | 84.86 |  |  | 90.95 |  |  |  | 1.61 |  | 3.07 | [8 empty] | 7.13 |  |  |  |  | 4.91
2011 |  |  |  | 5947.96 |  |  | 7000 |  |  |  | 915 | [10 empty] | 74.24 |  |  |  | 78.71 | [5 empty] | 74.21 |  |  | 79.91 |  |  |  | 3.25 |  | 5.47 | [8 empty] | 15.82 |  |  |  |  | 4.47
2012 |  |  |  | 6577.57 |  |  | 7708 |  |  |  | 915 | [10 empty] | 83.89 |  |  |  | 89.34 | [5 empty] | 81.84 |  |  | 87.75 |  |  |  | 0.48 |  | 2.61 | [8 empty] | 8.06 |  |  |  |  | 5.45
2013 |  |  |  | 4822.46 |  |  | 5662 |  |  |  | 915 | [10 empty] | 60.34 |  |  |  | 64.38 | [5 empty] | 60.16 |  |  | 64.63 |  |  |  | 0.07 |  | 22.44 | [8 empty] | 13.18 |  |  |  |  | 4.05
2014 |  |  |  | 6259.24 |  |  | 7417 |  |  |  | 915 | [10 empty] | 79.08 |  |  |  | 82.18 | [5 empty] | 78.09 |  |  | 84.67 |  |  |  | 8.07 |  | 8.52 | [8 empty] | 9.30 |  |  |  |  | 3.10
2015 |  |  |  | 4480.02 |  |  | 5185 |  |  |  | 915 | [10 empty] | 56.68 |  |  |  | 57.45 | [5 empty] | 55.89 |  |  | 59.19 |  |  |  | 4.48 |  | 13.81 | [8 empty] | 28.74 |  |  |  |  | 0.77
2016 |  |  |  | 6385.17 |  |  | 7366 |  |  |  | 915 | [10 empty] | 80.74 |  |  |  | 88.45 | [5 empty] | 79.44 |  |  | 83.86 |  |  |  | 1.44 |  | 3.03 | [8 empty] | 8.52 |  |  |  |  | 7.71
2017 |  |  |  | 5955.70 |  |  | 6794 |  |  |  | 915 | [10 empty] | 75.48 |  |  |  | 78.39 | [5 empty] | 74.30 |  |  | 77.56 |  |  |  | 1.75 |  | 3.53 | [8 empty] | 18.07 |  |  |  |  | 2.92
2018 |  |  |  | 6516.26 |  |  | 7535 |  |  |  | 915 | [10 empty] | 82.17 |  |  |  | 84.33 | [5 empty] | 81.30 |  |  | 86.02 |  |  |  | 4.55 |  | 4.02 | [8 empty] | 11.66 |  |  |  |  | 2.16
2019 |  |  |  | 5581.31 |  |  | 6561 |  |  |  | 915 | [10 empty] | 70.25 |  |  |  | 71.36 | [5 empty] | 69.63 |  |  | 74.90 |  |  |  | 8.72 |  | 10.03 | [8 empty] | 18.61 |  |  |  |  | 1.11
2020 |  |  |  | 5698.35 |  |  | 6790 |  |  |  | 915 | [10 empty] | 71.59 |  |  |  | 73.83 | [5 empty] | 70.90 |  |  | 77.30 |  |  |  | 9.56 |  | 15.06 | [8 empty] | 11.12 |  |  |  |  | 2.24
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 516
B. |  | Refuelling without maintenance | [35 empty] | 112
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1116 |  |  |  | 15
E. |  | Testing of plant systems or components | [35 empty] | 8 |  |  |  | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 7
L. |  | Human factor related | [39 empty] | 5
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 24 | [11 empty] | 40
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 239 | [11 empty] | 1
Z. |  | Other | [39 empty] | 7 | [11 empty] | 1
Subtotal | [37 empty] | 1236 |  |  |  | 809 | [11 empty] | 49
Total | [22 empty] | 0 | [14 empty] | 2094
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 11
12. |  |  | Reactor I&C Systems | [34 empty] | 30
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 16
14. |  |  | Safety Systems | [34 empty] | 30
15. |  |  | Reactor Cooling Systems | [34 empty] | 9
16. |  |  | Steam generation systems | [34 empty] | 77
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 52
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 138
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 117
42. |  |  | Electrical Power Supply Systems | [34 empty] | 9
Total | [37 empty] | 519

## ST. LAURENT B-2
2020 Operating Experience
FR-23 | [8 empty] | ST. LAURENT B-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP2 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-07-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-06-01
Gross electrical power | [12 empty] | : |  |  | 956 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-08-01
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6094.77 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 7.26 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.83 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.23 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.29 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.48 %
Load Factor (LF) | [18 empty] | : | 75.83 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 13.46 %
Operating Factor (OF) | [18 empty] | : | 88.87 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 978 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 561.05 | 589.55 |  |  |  | 630.86 |  | 470.75 | [8 empty] | 224.12 |  |  | 188.00 | [6 empty] | 277.61 |  | 609.42 |  |  |  | 620.04 |  |  | 649.85 |  |  | 626.39 | [9 empty] | 647.14 |  |  | 6094.77
EAF [%] |  |  |  |  | 82.83 | 93.41 |  |  |  | 96.43 |  | 91.09 | [8 empty] | 33.39 |  |  | 33.46 | [6 empty] | 40.82 |  | 90.18 |  |  |  | 94.95 |  |  | 96.08 |  |  | 96.60 | [9 empty] | 97.67 |  |  | 78.83
UCF [%] |  |  |  |  | 83.39 | 99.33 |  |  |  | 98.81 |  | 97.44 | [8 empty] | 99.42 |  |  | 98.97 | [6 empty] | 44.78 |  | 93.61 |  |  |  | 97.98 |  |  | 98.31 |  |  | 98.12 | [9 empty] | 98.57 |  |  | 92.29
LF [%] |  |  |  |  | 82.42 | 92.57 |  |  |  | 92.79 |  | 71.46 | [8 empty] | 32.92 |  |  | 28.54 | [6 empty] | 40.78 |  | 89.52 |  |  |  | 94.12 |  |  | 95.33 |  |  | 95.08 | [9 empty] | 95.06 |  |  | 75.83
OF [%] |  |  |  |  | 97.45 | 100.00 |  |  |  | 100.00 |  | 95.28 | [8 empty] | 36.56 |  |  | 37.22 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.87
FLR [%] |  |  |  |  | 13.36 | 0.51 |  |  |  | 1.11 |  | 2.46 | [8 empty] | 0.53 |  |  | 1.03 | [6 empty] | 54.97 |  | 6.08 |  |  |  | 1.91 |  |  | 1.59 |  |  | 1.56 | [9 empty] | 1.35 |  |  | 7.26
UCL [%] |  |  |  |  | 12.86 | 0.51 |  |  |  | 1.11 |  | 2.46 | [8 empty] | 0.53 |  |  | 1.03 | [6 empty] | 54.66 |  | 6.06 |  |  |  | 1.91 |  |  | 1.59 |  |  | 1.55 | [9 empty] | 1.35 |  |  | 7.23
PUF [%] |  |  |  |  | 3.75 | 0.16 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 0.05 |  |  | 0.00 | [6 empty] | 0.56 |  | 0.34 |  |  |  | 0.11 |  |  | 0.10 |  |  | 0.33 | [9 empty] | 0.08 |  |  | 0.48
XUF [%] |  |  |  |  | 0.56 | 5.92 |  |  |  | 2.37 |  | 6.35 | [8 empty] | 66.03 |  |  | 65.50 | [6 empty] | 3.96 |  | 3.43 |  |  |  | 3.03 |  |  | 2.22 |  |  | 1.52 | [9 empty] | 0.90 |  |  | 13.46
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 216763.24 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.28 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.64 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.72 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.64 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.9 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.38 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.02 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 4123.00 |  |  | 4839 |  |  |  | 880 | [10 empty] | 16.06 |  |  |  | 16.06 | [5 empty] | 15.84 |  |  | 16.74 |  |  |  | 34.68 |  | 8.53 | [8 empty] | 75.41 |  |  |  |  | 0.00
1984 |  |  |  | 5724.00 |  |  | 7237 |  |  |  | 880 | [10 empty] | 88.88 |  |  |  | 88.88 | [5 empty] | 74.05 |  |  | 82.39 |  |  |  | 11.08 |  | 11.07 | [8 empty] | 0.05 |  |  |  |  | 0.00
1985 |  |  |  | 5295.60 |  |  | 6806 |  |  |  | 880 | [10 empty] | 75.70 |  |  |  | 77.55 | [5 empty] | 68.70 |  |  | 77.69 |  |  |  | 9.43 |  | 8.08 | [8 empty] | 14.37 |  |  |  |  | 1.86
1986 |  |  |  | 5662.80 |  |  | 7337 |  |  |  | 880 | [10 empty] | 79.78 |  |  |  | 81.74 | [5 empty] | 73.46 |  |  | 83.76 |  |  |  | 9.65 |  | 8.73 | [8 empty] | 9.53 |  |  |  |  | 1.96
1987 |  |  |  | 5060.20 |  |  | 6798 |  |  |  | 880 | [10 empty] | 79.41 |  |  |  | 79.86 | [5 empty] | 65.64 |  |  | 77.60 |  |  |  | 10.75 |  | 9.62 | [8 empty] | 10.52 |  |  |  |  | 0.45
1988 |  |  |  | 5108.00 |  |  | 6262 |  |  |  | 880 | [10 empty] | 69.57 |  |  |  | 69.61 | [5 empty] | 66.08 |  |  | 71.29 |  |  |  | 12.35 |  | 9.81 | [8 empty] | 20.58 |  |  |  |  | 0.04
1989 |  |  |  | 5034.03 |  |  | 6490 |  |  |  | 880 | [10 empty] | 75.92 |  |  |  | 81.39 | [5 empty] | 65.30 |  |  | 74.09 |  |  |  | 8.36 |  | 7.42 | [8 empty] | 11.19 |  |  |  |  | 5.47
1990 |  |  |  | 5165.86 |  |  | 6212 |  |  |  | 915 | [10 empty] | 71.29 |  |  |  | 73.78 | [5 empty] | 64.45 |  |  | 70.91 |  |  |  | 15.77 |  | 13.81 | [8 empty] | 12.41 |  |  |  |  | 2.49
1991 |  |  |  | 6043.04 |  |  | 7374 |  |  |  | 915 | [10 empty] | 84.25 |  |  |  | 86.09 | [5 empty] | 75.39 |  |  | 84.18 |  |  |  | 4.84 |  | 4.38 | [8 empty] | 9.53 |  |  |  |  | 1.84
1992 |  |  |  | 5490.13 |  |  | 6982 |  |  |  | 915 | [10 empty] | 79.41 |  |  |  | 80.61 | [5 empty] | 68.31 |  |  | 79.49 |  |  |  | 10.42 |  | 9.38 | [8 empty] | 10.01 |  |  |  |  | 1.20
1993 |  |  |  | 5042.24 |  |  | 6149 |  |  |  | 915 | [10 empty] | 64.11 |  |  |  | 68.73 | [5 empty] | 62.91 |  |  | 70.19 |  |  |  | 9.30 |  | 7.04 | [8 empty] | 24.23 |  |  |  |  | 4.61
1994 |  |  |  | 6322.70 |  |  | 7406 |  |  |  | 915 | [10 empty] | 81.17 |  |  |  | 83.73 | [5 empty] | 78.88 |  |  | 84.54 |  |  |  | 5.20 |  | 4.60 | [8 empty] | 11.67 |  |  |  |  | 2.56
1995 |  |  |  | 5311.31 |  |  | 6720 |  |  |  | 915 | [10 empty] | 72.12 |  |  |  | 72.87 | [5 empty] | 66.26 |  |  | 76.71 |  |  |  | 17.25 |  | 15.19 | [8 empty] | 11.94 |  |  |  |  | 0.75
1996 |  |  |  | 6057.67 |  |  | 7303 |  |  |  | 915 | [10 empty] | 80.85 |  |  |  | 82.22 | [5 empty] | 75.37 |  |  | 83.14 |  |  |  | 5.77 |  | 5.04 | [8 empty] | 12.74 |  |  |  |  | 1.37
1997 |  |  |  | 5960.69 |  |  | 7147 |  |  |  | 915 | [10 empty] | 78.13 |  |  |  | 80.78 | [5 empty] | 74.37 |  |  | 81.59 |  |  |  | 1.01 |  | 0.82 | [8 empty] | 18.39 |  |  |  |  | 2.66
1998 |  |  |  | 6415.27 |  |  | 7585 |  |  |  | 915 | [10 empty] | 83.15 |  |  |  | 85.68 | [5 empty] | 80.04 |  |  | 86.59 |  |  |  | 4.51 |  | 4.05 | [8 empty] | 10.27 |  |  |  |  | 2.52
1999 |  |  |  | 5845.85 |  |  | 7013 |  |  |  | 915 | [10 empty] | 77.25 |  |  |  | 79.00 | [5 empty] | 72.93 |  |  | 80.06 |  |  |  | 7.64 |  | 6.54 | [8 empty] | 14.47 |  |  |  |  | 1.74
2000 |  |  |  | 5134.00 |  |  | 6069 |  |  |  | 915 | [10 empty] | 66.99 |  |  |  | 67.63 | [5 empty] | 63.88 |  |  | 69.09 |  |  |  | 21.60 |  | 18.64 | [8 empty] | 13.74 |  |  |  |  | 0.64
2001 |  |  |  | 6046.65 |  |  | 7226 |  |  |  | 915 | [10 empty] | 80.11 |  |  |  | 81.74 | [5 empty] | 75.44 |  |  | 82.49 |  |  |  | 3.42 |  | 2.89 | [8 empty] | 15.37 |  |  |  |  | 1.63
2002 |  |  |  | 6215.02 |  |  | 7434 |  |  |  | 915 | [10 empty] | 82.66 |  |  |  | 82.67 | [5 empty] | 77.54 |  |  | 84.86 |  |  |  | 5.88 |  | 5.17 | [8 empty] | 12.16 |  |  |  |  | 0.01
2003 |  |  |  | 4702.44 |  |  | 5580 |  |  |  | 915 | [10 empty] | 61.64 |  |  |  | 61.64 | [5 empty] | 58.67 |  |  | 63.70 |  |  |  | 9.15 |  | 6.21 | [8 empty] | 32.14 |  |  |  |  | 0.00
2004 |  |  |  | 6468.60 |  |  | 7838 |  |  |  | 915 | [10 empty] | 85.64 |  |  |  | 87.62 | [5 empty] | 80.48 |  |  | 89.23 |  |  |  | 5.79 |  | 5.38 | [8 empty] | 7.00 |  |  |  |  | 1.99
2005 |  |  |  | 5728.05 |  |  | 7038 |  |  |  | 915 | [10 empty] | 76.98 |  |  |  | 78.63 | [5 empty] | 71.45 |  |  | 80.33 |  |  |  | 8.53 |  | 9.59 | [8 empty] | 11.77 |  |  |  |  | 1.66
2006 |  |  |  | 6004.32 |  |  | 7580 |  |  |  | 915 | [10 empty] | 88.27 |  |  |  | 89.77 | [5 empty] | 74.91 |  |  | 86.53 |  |  |  | 1.61 |  | 1.96 | [8 empty] | 8.27 |  |  |  |  | 1.51
2007 |  |  |  | 5906.81 |  |  | 6949 |  |  |  | 915 | [10 empty] | 74.73 |  |  |  | 77.72 | [5 empty] | 73.69 |  |  | 79.33 |  |  |  | 4.74 |  | 7.85 | [8 empty] | 14.43 |  |  |  |  | 2.99
2008 |  |  |  | 6581.43 |  |  | 7784 |  |  |  | 915 | [10 empty] | 86.07 |  |  |  | 88.03 | [5 empty] | 81.89 |  |  | 88.62 |  |  |  | 0.97 |  | 2.59 | [8 empty] | 9.37 |  |  |  |  | 1.97
2009 |  |  |  | 6175.76 |  |  | 7086 |  |  |  | 915 | [10 empty] | 77.33 |  |  |  | 80.73 | [5 empty] | 77.05 |  |  | 80.89 |  |  |  | 1.94 |  | 5.29 | [8 empty] | 13.98 |  |  |  |  | 3.40
2010 |  |  |  | 6694.83 |  |  | 7737 |  |  |  | 915 | [10 empty] | 83.59 |  |  |  | 87.63 | [5 empty] | 83.52 |  |  | 88.32 |  |  |  | 1.99 |  | 2.77 | [8 empty] | 9.60 |  |  |  |  | 4.03
2011 |  |  |  | 5285.01 |  |  | 6171 |  |  |  | 915 | [10 empty] | 66.20 |  |  |  | 69.40 | [5 empty] | 65.94 |  |  | 70.45 |  |  |  | 13.86 |  | 16.81 | [8 empty] | 13.78 |  |  |  |  | 3.20
2012 |  |  |  | 6501.97 |  |  | 7591 |  |  |  | 915 | [10 empty] | 81.35 |  |  |  | 85.32 | [5 empty] | 80.90 |  |  | 86.42 |  |  |  | 0.76 |  | 5.18 | [8 empty] | 9.50 |  |  |  |  | 3.98
2013 |  |  |  | 3380.08 |  |  | 3990 |  |  |  | 915 | [10 empty] | 42.44 |  |  |  | 44.40 | [5 empty] | 42.17 |  |  | 45.55 |  |  |  | 3.05 |  | 28.42 | [8 empty] | 27.18 |  |  |  |  | 1.97
2014 |  |  |  | 5991.68 |  |  | 7035 |  |  |  | 915 | [10 empty] | 75.25 |  |  |  | 78.52 | [5 empty] | 74.75 |  |  | 80.31 |  |  |  | 5.04 |  | 11.92 | [8 empty] | 9.56 |  |  |  |  | 3.26
2015 |  |  |  | 6132.94 |  |  | 7188 |  |  |  | 915 | [10 empty] | 79.00 |  |  |  | 81.43 | [5 empty] | 76.51 |  |  | 82.05 |  |  |  | 0.84 |  | 4.22 | [8 empty] | 14.35 |  |  |  |  | 2.42
2016 |  |  |  | 5812.80 |  |  | 6867 |  |  |  | 915 | [10 empty] | 74.58 |  |  |  | 77.94 | [5 empty] | 72.32 |  |  | 78.18 |  |  |  | 1.21 |  | 4.26 | [8 empty] | 17.79 |  |  |  |  | 3.37
2017 |  |  |  | 6252.54 |  |  | 7246 |  |  |  | 915 | [10 empty] | 79.24 |  |  |  | 82.02 | [5 empty] | 78.01 |  |  | 82.72 |  |  |  | 1.47 |  | 9.23 | [8 empty] | 8.74 |  |  |  |  | 2.78
2018 |  |  |  | 5268.72 |  |  | 6257 |  |  |  | 915 | [10 empty] | 66.58 |  |  |  | 67.98 | [5 empty] | 65.73 |  |  | 71.43 |  |  |  | 6.91 |  | 13.35 | [8 empty] | 18.67 |  |  |  |  | 1.40
2019 |  |  |  | 4987.68 |  |  | 6030 |  |  |  | 915 | [10 empty] | 63.60 |  |  |  | 65.28 | [5 empty] | 62.23 |  |  | 68.84 |  |  |  | 15.74 |  | 25.18 | [8 empty] | 9.54 |  |  |  |  | 1.68
2020 |  |  |  | 6094.77 |  |  | 7806 |  |  |  | 915 | [10 empty] | 78.83 |  |  |  | 92.29 | [5 empty] | 75.83 |  |  | 88.87 |  |  |  | 7.26 |  | 7.23 | [8 empty] | 0.48 |  |  |  |  | 13.46
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 697
B. |  | Refuelling without maintenance | [35 empty] | 95
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1024 |  |  |  | 11
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 5
E. |  | Testing of plant systems or components | [35 empty] | 12 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 11
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 14
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 15
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 86 | [11 empty] | 2
Z. |  | Other | [39 empty] | 31
Subtotal | [37 empty] | 1136 |  |  |  | 851 | [11 empty] | 22
Total | [22 empty] | 0 | [14 empty] | 2009
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 16
14. |  |  | Safety Systems | [34 empty] | 47
15. |  |  | Reactor Cooling Systems | [34 empty] | 35
16. |  |  | Steam generation systems | [34 empty] | 34
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 19
31. |  |  | Turbine and auxiliaries | [34 empty] | 214
32. |  |  | Feedwater and Main Steam System | [34 empty] | 24
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 188
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 54
42. |  |  | Electrical Power Supply Systems | [34 empty] | 16
Total | [37 empty] | 683

## TRICASTIN-1
2020 Operating Experience
FR-18 | [8 empty] | TRICASTIN-1 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-11-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-05-31
Gross electrical power | [12 empty] | : |  |  | 955 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-12-01
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 42000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 45 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6655.75 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.43 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.13 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.17 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.16 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.67 %
Load Factor (LF) | [18 empty] | : | 82.81 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.03 %
Operating Factor (OF) | [18 empty] | : | 89.31 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 939 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 526.02 | 587.18 |  |  |  | 647.79 |  | 586.65 | [8 empty] | 620.08 |  |  | 625.36 | [6 empty] | 647.78 |  | 648.29 |  |  |  | 637.55 |  |  | 192.25 |  |  | 315.36 | [9 empty] | 621.44 |  |  | 6655.75
EAF [%] |  |  |  |  | 77.42 | 95.21 |  |  |  | 99.78 |  | 98.32 | [8 empty] | 98.77 |  |  | 98.61 | [6 empty] | 97.45 |  | 96.85 |  |  |  | 97.97 |  |  | 28.26 |  |  | 47.98 | [9 empty] | 97.56 |  |  | 86.13
UCF [%] |  |  |  |  | 77.42 | 96.40 |  |  |  | 99.87 |  | 98.45 | [8 empty] | 99.28 |  |  | 99.57 | [6 empty] | 99.63 |  | 99.72 |  |  |  | 99.89 |  |  | 28.66 |  |  | 47.98 | [9 empty] | 99.70 |  |  | 87.16
LF [%] |  |  |  |  | 77.27 | 92.20 |  |  |  | 95.29 |  | 89.05 | [8 empty] | 91.09 |  |  | 94.92 | [6 empty] | 95.16 |  | 95.23 |  |  |  | 96.77 |  |  | 28.20 |  |  | 47.87 | [9 empty] | 91.29 |  |  | 82.81
OF [%] |  |  |  |  | 89.38 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 28.72 |  |  | 54.31 | [9 empty] | 100.00 |  |  | 89.31
FLR [%] |  |  |  |  | 18.86 | 2.92 |  |  |  | 0.13 |  | 1.52 | [8 empty] | 0.21 |  |  | 0.43 | [6 empty] | 0.28 |  | 0.28 |  |  |  | 0.11 |  |  | 0.03 |  |  | 3.54 | [9 empty] | 0.30 |  |  | 2.43
UCL [%] |  |  |  |  | 18.00 | 2.90 |  |  |  | 0.13 |  | 1.52 | [8 empty] | 0.21 |  |  | 0.43 | [6 empty] | 0.28 |  | 0.28 |  |  |  | 0.11 |  |  | 0.01 |  |  | 1.76 | [9 empty] | 0.30 |  |  | 2.17
PUF [%] |  |  |  |  | 4.59 | 0.71 |  |  |  | 0.00 |  | 0.03 | [8 empty] | 0.51 |  |  | 0.00 | [6 empty] | 0.09 |  | 0.00 |  |  |  | 0.00 |  |  | 71.33 |  |  | 50.26 | [9 empty] | 0.00 |  |  | 10.67
XUF [%] |  |  |  |  | 0.00 | 1.19 |  |  |  | 0.09 |  | 0.13 | [8 empty] | 0.51 |  |  | 0.96 | [6 empty] | 2.18 |  | 2.87 |  |  |  | 1.92 |  |  | 0.40 |  |  | 0.00 | [9 empty] | 2.13 |  |  | 1.03
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 231505.47 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.15 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.3 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.91 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.8 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.82 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.74 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 2468.00 |  |  | 3412 |  |  |  | 918 | [10 empty] | 56.60 |  |  |  | 56.60 | [5 empty] | 95.84 |  |  | 97.04 |  |  |  | 43.40 |  | 43.40 | [8 empty] | 0.00 |  |  |  |  | 0.00
1981 |  |  |  | 4416.00 |  |  | 5176 |  |  |  | 920 | [10 empty] | 56.33 |  |  |  | 56.33 | [5 empty] | 54.79 |  |  | 59.09 |  |  |  | 20.34 |  | 14.39 | [8 empty] | 29.28 |  |  |  |  | 0.00
1982 |  |  |  | 5909.80 |  |  | 8151 |  |  |  | 915 | [10 empty] | 81.86 |  |  |  | 82.78 | [5 empty] | 73.73 |  |  | 93.05 |  |  |  | 17.22 |  | 17.22 | [8 empty] | 0.00 |  |  |  |  | 0.92
1983 |  |  |  | 5111.00 |  |  | 6097 |  |  |  | 915 | [10 empty] | 67.24 |  |  |  | 67.24 | [5 empty] | 63.76 |  |  | 69.60 |  |  |  | 12.27 |  | 9.41 | [8 empty] | 23.35 |  |  |  |  | 0.00
1984 |  |  |  | 6468.00 |  |  | 7662 |  |  |  | 915 | [10 empty] | 86.67 |  |  |  | 86.67 | [5 empty] | 80.47 |  |  | 87.23 |  |  |  | 2.06 |  | 1.82 | [8 empty] | 11.51 |  |  |  |  | 0.00
1985 |  |  |  | 6217.90 |  |  | 7560 |  |  |  | 915 | [10 empty] | 81.64 |  |  |  | 85.97 | [5 empty] | 77.57 |  |  | 86.30 |  |  |  | 2.01 |  | 1.77 | [8 empty] | 12.27 |  |  |  |  | 4.33
1986 |  |  |  | 5880.30 |  |  | 7188 |  |  |  | 915 | [10 empty] | 77.05 |  |  |  | 79.44 | [5 empty] | 73.36 |  |  | 82.05 |  |  |  | 7.60 |  | 6.54 | [8 empty] | 14.02 |  |  |  |  | 2.39
1987 |  |  |  | 5978.10 |  |  | 7360 |  |  |  | 915 | [10 empty] | 78.15 |  |  |  | 83.46 | [5 empty] | 74.58 |  |  | 84.02 |  |  |  | 6.66 |  | 5.96 | [8 empty] | 10.58 |  |  |  |  | 5.31
1988 |  |  |  | 5836.00 |  |  | 7200 |  |  |  | 915 | [10 empty] | 76.70 |  |  |  | 79.77 | [5 empty] | 72.61 |  |  | 81.97 |  |  |  | 5.40 |  | 4.55 | [8 empty] | 15.68 |  |  |  |  | 3.07
1989 |  |  |  | 5830.15 |  |  | 7550 |  |  |  | 915 | [10 empty] | 83.17 |  |  |  | 83.31 | [5 empty] | 72.74 |  |  | 86.19 |  |  |  | 4.50 |  | 3.92 | [8 empty] | 12.76 |  |  |  |  | 0.14
1990 |  |  |  | 5099.69 |  |  | 6377 |  |  |  | 915 | [10 empty] | 65.08 |  |  |  | 68.77 | [5 empty] | 63.62 |  |  | 72.80 |  |  |  | 6.40 |  | 4.70 | [8 empty] | 26.53 |  |  |  |  | 3.69
1991 |  |  |  | 5909.12 |  |  | 7262 |  |  |  | 915 | [10 empty] | 77.01 |  |  |  | 83.18 | [5 empty] | 73.72 |  |  | 82.90 |  |  |  | 4.86 |  | 4.25 | [8 empty] | 12.57 |  |  |  |  | 6.17
1992 |  |  |  | 5659.31 |  |  | 7573 |  |  |  | 915 | [10 empty] | 82.99 |  |  |  | 85.27 | [5 empty] | 70.41 |  |  | 86.21 |  |  |  | 2.21 |  | 1.92 | [8 empty] | 12.81 |  |  |  |  | 2.27
1993 |  |  |  | 6134.82 |  |  | 7393 |  |  |  | 915 | [10 empty] | 77.71 |  |  |  | 83.93 | [5 empty] | 76.54 |  |  | 84.39 |  |  |  | 4.55 |  | 4.00 | [8 empty] | 12.07 |  |  |  |  | 6.22
1994 |  |  |  | 5008.42 |  |  | 6458 |  |  |  | 915 | [10 empty] | 70.27 |  |  |  | 75.44 | [5 empty] | 62.48 |  |  | 73.72 |  |  |  | 13.11 |  | 11.39 | [8 empty] | 13.17 |  |  |  |  | 5.17
1995 |  |  |  | 5372.68 |  |  | 6374 |  |  |  | 915 | [10 empty] | 70.60 |  |  |  | 71.28 | [5 empty] | 67.03 |  |  | 72.76 |  |  |  | 17.56 |  | 15.19 | [8 empty] | 13.53 |  |  |  |  | 0.68
1996 |  |  |  | 7302.13 |  |  | 8448 |  |  |  | 915 | [10 empty] | 93.78 |  |  |  | 94.47 | [5 empty] | 90.85 |  |  | 96.17 |  |  |  | 4.85 |  | 4.82 | [8 empty] | 0.71 |  |  |  |  | 0.69
1997 |  |  |  | 5548.30 |  |  | 6711 |  |  |  | 915 | [10 empty] | 72.49 |  |  |  | 73.13 | [5 empty] | 69.22 |  |  | 76.61 |  |  |  | 9.22 |  | 7.42 | [8 empty] | 19.45 |  |  |  |  | 0.64
1998 |  |  |  | 5503.66 |  |  | 7075 |  |  |  | 915 | [10 empty] | 71.03 |  |  |  | 71.03 | [5 empty] | 68.66 |  |  | 80.76 |  |  |  | 16.38 |  | 13.92 | [8 empty] | 15.05 |  |  |  |  | 0.00
1999 |  |  |  | 3426.65 |  |  | 4016 |  |  |  | 915 | [10 empty] | 44.51 |  |  |  | 44.90 | [5 empty] | 42.75 |  |  | 45.84 |  |  |  | 41.81 |  | 32.27 | [8 empty] | 22.83 |  |  |  |  | 0.40
2000 |  |  |  | 6644.86 |  |  | 7842 |  |  |  | 915 | [10 empty] | 87.15 |  |  |  | 87.68 | [5 empty] | 82.67 |  |  | 89.28 |  |  |  | 2.36 |  | 2.12 | [8 empty] | 10.21 |  |  |  |  | 0.53
2001 |  |  |  | 6053.29 |  |  | 7261 |  |  |  | 915 | [10 empty] | 82.03 |  |  |  | 83.19 | [5 empty] | 75.52 |  |  | 82.89 |  |  |  | 0.83 |  | 0.69 | [8 empty] | 16.12 |  |  |  |  | 1.15
2002 |  |  |  | 6384.56 |  |  | 7778 |  |  |  | 915 | [10 empty] | 86.67 |  |  |  | 87.67 | [5 empty] | 79.65 |  |  | 88.79 |  |  |  | 1.48 |  | 1.32 | [8 empty] | 11.01 |  |  |  |  | 1.01
2003 |  |  |  | 5670.06 |  |  | 7029 |  |  |  | 915 | [10 empty] | 73.02 |  |  |  | 85.15 | [5 empty] | 70.74 |  |  | 80.24 |  |  |  | 1.26 |  | 1.08 | [8 empty] | 13.76 |  |  |  |  | 12.13
2004 |  |  |  | 6832.46 |  |  | 8049 |  |  |  | 915 | [10 empty] | 89.00 |  |  |  | 91.54 | [5 empty] | 85.01 |  |  | 91.63 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 8.30 |  |  |  |  | 2.54
2005 |  |  |  | 5830.97 |  |  | 7007 |  |  |  | 915 | [10 empty] | 73.98 |  |  |  | 85.33 | [5 empty] | 72.74 |  |  | 79.98 |  |  |  | 2.29 |  | 2.64 | [8 empty] | 12.02 |  |  |  |  | 11.35
2006 |  |  |  | 6466.79 |  |  | 7989 |  |  |  | 915 | [10 empty] | 87.40 |  |  |  | 90.66 | [5 empty] | 80.68 |  |  | 91.20 |  |  |  | 0.04 |  | 1.97 | [8 empty] | 7.36 |  |  |  |  | 3.26
2007 |  |  |  | 6344.72 |  |  | 7496 |  |  |  | 915 | [10 empty] | 82.55 |  |  |  | 84.84 | [5 empty] | 79.16 |  |  | 85.57 |  |  |  | 1.43 |  | 3.66 | [8 empty] | 11.49 |  |  |  |  | 2.29
2008 |  |  |  | 6808.19 |  |  | 7950 |  |  |  | 915 | [10 empty] | 87.86 |  |  |  | 89.74 | [5 empty] | 84.71 |  |  | 90.51 |  |  |  | 0.20 |  | 3.68 | [8 empty] | 6.58 |  |  |  |  | 1.88
2009 |  |  |  | 4655.39 |  |  | 5435 |  |  |  | 915 | [10 empty] | 59.21 |  |  |  | 63.45 | [5 empty] | 58.08 |  |  | 62.04 |  |  |  | 8.56 |  | 14.84 | [8 empty] | 21.71 |  |  |  |  | 4.24
2010 |  |  |  | 6688.43 |  |  | 7755 |  |  |  | 915 | [10 empty] | 86.65 |  |  |  | 87.51 | [5 empty] | 83.44 |  |  | 88.53 |  |  |  | 2.34 |  | 6.00 | [8 empty] | 6.49 |  |  |  |  | 0.86
2011 |  |  |  | 5580.09 |  |  | 6483 |  |  |  | 915 | [10 empty] | 76.43 |  |  |  | 77.39 | [5 empty] | 69.62 |  |  | 74.01 |  |  |  | 0.25 |  | 9.31 | [8 empty] | 13.30 |  |  |  |  | 0.96
2012 |  |  |  | 6339.05 |  |  | 7345 |  |  |  | 915 | [10 empty] | 80.56 |  |  |  | 82.92 | [5 empty] | 78.87 |  |  | 83.62 |  |  |  | 4.22 |  | 8.55 | [8 empty] | 8.54 |  |  |  |  | 2.36
2013 |  |  |  | 5868.42 |  |  | 6741 |  |  |  | 915 | [10 empty] | 74.66 |  |  |  | 76.70 | [5 empty] | 73.21 |  |  | 76.95 |  |  |  | 1.82 |  | 7.97 | [8 empty] | 15.33 |  |  |  |  | 2.04
2014 |  |  |  | 6743.76 |  |  | 7683 |  |  |  | 915 | [10 empty] | 85.74 |  |  |  | 86.92 | [5 empty] | 84.14 |  |  | 87.71 |  |  |  | 3.18 |  | 4.24 | [8 empty] | 8.84 |  |  |  |  | 1.18
2015 |  |  |  | 5751.37 |  |  | 6557 |  |  |  | 915 | [10 empty] | 73.07 |  |  |  | 74.21 | [5 empty] | 71.75 |  |  | 74.85 |  |  |  | 2.79 |  | 7.58 | [8 empty] | 18.20 |  |  |  |  | 1.14
2016 |  |  |  | 4576.92 |  |  | 5400 |  |  |  | 915 | [10 empty] | 58.84 |  |  |  | 59.37 | [5 empty] | 56.95 |  |  | 61.48 |  |  |  | 3.78 |  | 32.71 | [8 empty] | 7.91 |  |  |  |  | 0.53
2017 |  |  |  | 4029.83 |  |  | 4975 |  |  |  | 915 | [10 empty] | 53.33 |  |  |  | 69.61 | [5 empty] | 50.28 |  |  | 56.79 |  |  |  | 29.14 |  | 29.98 | [8 empty] | 0.40 |  |  |  |  | 16.28
2018 |  |  |  | 5586.73 |  |  | 6477 |  |  |  | 915 | [10 empty] | 70.79 |  |  |  | 73.09 | [5 empty] | 69.70 |  |  | 73.94 |  |  |  | 4.87 |  | 9.93 | [8 empty] | 16.98 |  |  |  |  | 2.30
2019 |  |  |  | 2843.84 |  |  | 3231 |  |  |  | 915 | [10 empty] | 35.70 |  |  |  | 37.49 | [5 empty] | 35.48 |  |  | 36.88 |  |  |  | 16.76 |  | 12.76 | [8 empty] | 49.75 |  |  |  |  | 1.79
2020 |  |  |  | 6655.75 |  |  | 7845 |  |  |  | 915 | [10 empty] | 86.13 |  |  |  | 87.16 | [5 empty] | 82.81 |  |  | 89.31 |  |  |  | 2.43 |  | 2.17 | [8 empty] | 10.67 |  |  |  |  | 1.03
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1980 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 404 | [11 empty] | 1
B. |  | Refuelling without maintenance | [35 empty] | 79
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1050 |  |  |  | 8
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 15 |  |  |  | 2
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 124
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 12
L. |  | Human factor related | [39 empty] | 9
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 16 | [11 empty] | 15
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 29
Z. |  | Other | [39 empty] | 27
Subtotal | [37 empty] | 1148 |  |  |  | 591 | [11 empty] | 59
Total | [22 empty] | 0 | [14 empty] | 1798
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1980 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 72
12. |  |  | Reactor I&C Systems | [34 empty] | 10
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 65
15. |  |  | Reactor Cooling Systems | [34 empty] | 19
16. |  |  | Steam generation systems | [34 empty] | 92
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [34 empty] | 45
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 92
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 67
42. |  |  | Electrical Power Supply Systems | [34 empty] | 38
Total | [37 empty] | 524

## TRICASTIN-2
2020 Operating Experience
FR-19 | [8 empty] | TRICASTIN-2 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-12-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-08-07
Gross electrical power | [12 empty] | : |  |  | 955 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-12-01
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 45 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6937 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.12 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.66 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.11 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.26 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.63 %
Load Factor (LF) | [18 empty] | : | 86.31 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 4.61 %
Operating Factor (OF) | [18 empty] | : | 86.42 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1193 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 680.65 | 654.90 |  |  |  | 137.13 |  | 84.13 | [8 empty] | 688.45 |  |  | 656.75 | [6 empty] | 681.24 |  | 681.36 |  |  |  | 663.28 |  |  | 672.58 |  |  | 651.96 | [9 empty] | 684.55 |  |  | 6937.00
EAF [%] |  |  |  |  | 98.44 | 99.90 |  |  |  | 19.55 |  | 12.74 | [8 empty] | 99.92 |  |  | 100.00 | [6 empty] | 99.48 |  | 99.81 |  |  |  | 99.98 |  |  | 99.19 |  |  | 98.74 | [9 empty] | 99.95 |  |  | 85.66
UCF [%] |  |  |  |  | 99.99 | 99.90 |  |  |  | 19.55 |  | 65.99 | [8 empty] | 99.92 |  |  | 100.00 | [6 empty] | 99.49 |  | 99.89 |  |  |  | 99.98 |  |  | 99.19 |  |  | 99.99 | [9 empty] | 99.95 |  |  | 90.26
LF [%] |  |  |  |  | 99.98 | 102.84 |  |  |  | 20.17 |  | 12.77 | [8 empty] | 101.13 |  |  | 99.69 | [6 empty] | 100.07 |  | 100.09 |  |  |  | 100.68 |  |  | 98.67 |  |  | 98.96 | [9 empty] | 100.56 |  |  | 86.31
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 19.78 |  | 17.22 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.42
FLR [%] |  |  |  |  | 0.00 | 0.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.51 |  | 0.02 |  |  |  | 0.02 |  |  | 0.72 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 0.12
UCL [%] |  |  |  |  | 0.00 | 0.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.51 |  | 0.02 |  |  |  | 0.02 |  |  | 0.72 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 0.11
PUF [%] |  |  |  |  | 0.01 | 0.08 |  |  |  | 80.45 |  | 34.01 | [8 empty] | 0.08 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.09 |  |  |  | 0.00 |  |  | 0.09 |  |  | 0.00 | [9 empty] | 0.05 |  |  | 9.63
XUF [%] |  |  |  |  | 1.55 | 0.00 |  |  |  | 0.00 |  | 53.26 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.02 |  | 0.07 |  |  |  | 0.01 |  |  | 0.00 |  |  | 1.25 | [9 empty] | 0.00 |  |  | 4.61
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 233097.73 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.42 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.56 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.06 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.5 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 1614.00 |  |  | 2559 |  |  |  | 917 | [10 empty] | 68.70 |  |  |  | 68.70 | [5 empty] | 68.08 |  |  | 76.34 |  |  |  | 9.91 |  | 7.56 | [8 empty] | 23.74 |  |  |  |  | 0.00
1981 |  |  |  | 6155.10 |  |  | 7819 |  |  |  | 920 | [10 empty] | 82.33 |  |  |  | 82.33 | [5 empty] | 76.37 |  |  | 89.26 |  |  |  | 4.42 |  | 3.81 | [8 empty] | 13.87 |  |  |  |  | 0.00
1982 |  |  |  | 4056.20 |  |  | 5932 |  |  |  | 915 | [10 empty] | 63.03 |  |  |  | 63.03 | [5 empty] | 50.61 |  |  | 67.72 |  |  |  | 11.83 |  | 8.46 | [8 empty] | 28.51 |  |  |  |  | 0.00
1983 |  |  |  | 5624.00 |  |  | 7245 |  |  |  | 915 | [10 empty] | 81.92 |  |  |  | 81.92 | [5 empty] | 70.16 |  |  | 82.71 |  |  |  | 1.75 |  | 1.46 | [8 empty] | 16.62 |  |  |  |  | 0.00
1984 |  |  |  | 6603.00 |  |  | 7684 |  |  |  | 915 | [10 empty] | 87.18 |  |  |  | 87.18 | [5 empty] | 82.15 |  |  | 87.48 |  |  |  | 4.50 |  | 4.11 | [8 empty] | 8.72 |  |  |  |  | 0.00
1985 |  |  |  | 6261.70 |  |  | 7375 |  |  |  | 915 | [10 empty] | 79.37 |  |  |  | 86.02 | [5 empty] | 78.12 |  |  | 84.19 |  |  |  | 4.24 |  | 3.81 | [8 empty] | 10.17 |  |  |  |  | 6.64
1986 |  |  |  | 6286.60 |  |  | 7631 |  |  |  | 915 | [10 empty] | 82.60 |  |  |  | 85.78 | [5 empty] | 78.43 |  |  | 87.11 |  |  |  | 4.14 |  | 3.71 | [8 empty] | 10.51 |  |  |  |  | 3.18
1987 |  |  |  | 5302.30 |  |  | 6500 |  |  |  | 915 | [10 empty] | 69.61 |  |  |  | 73.17 | [5 empty] | 66.15 |  |  | 74.20 |  |  |  | 10.08 |  | 8.20 | [8 empty] | 18.63 |  |  |  |  | 3.56
1988 |  |  |  | 4896.00 |  |  | 6628 |  |  |  | 915 | [10 empty] | 73.08 |  |  |  | 76.03 | [5 empty] | 60.92 |  |  | 75.46 |  |  |  | 13.58 |  | 11.95 | [8 empty] | 12.02 |  |  |  |  | 2.95
1989 |  |  |  | 5164.73 |  |  | 6650 |  |  |  | 915 | [10 empty] | 71.40 |  |  |  | 74.33 | [5 empty] | 64.44 |  |  | 75.91 |  |  |  | 25.15 |  | 24.97 | [8 empty] | 0.70 |  |  |  |  | 2.93
1990 |  |  |  | 5614.37 |  |  | 7177 |  |  |  | 915 | [10 empty] | 72.54 |  |  |  | 80.90 | [5 empty] | 70.04 |  |  | 81.93 |  |  |  | 2.87 |  | 2.39 | [8 empty] | 16.70 |  |  |  |  | 8.36
1991 |  |  |  | 4459.14 |  |  | 5429 |  |  |  | 915 | [10 empty] | 58.16 |  |  |  | 60.81 | [5 empty] | 55.63 |  |  | 61.97 |  |  |  | 15.63 |  | 11.26 | [8 empty] | 27.93 |  |  |  |  | 2.65
1992 |  |  |  | 6099.10 |  |  | 7118 |  |  |  | 915 | [10 empty] | 78.72 |  |  |  | 79.95 | [5 empty] | 75.88 |  |  | 81.03 |  |  |  | 8.45 |  | 7.38 | [8 empty] | 12.67 |  |  |  |  | 1.24
1993 |  |  |  | 5777.08 |  |  | 6876 |  |  |  | 915 | [10 empty] | 72.92 |  |  |  | 77.31 | [5 empty] | 72.07 |  |  | 78.49 |  |  |  | 12.48 |  | 11.03 | [8 empty] | 11.66 |  |  |  |  | 4.39
1994 |  |  |  | 6216.70 |  |  | 7222 |  |  |  | 915 | [10 empty] | 79.09 |  |  |  | 81.66 | [5 empty] | 77.56 |  |  | 82.44 |  |  |  | 6.02 |  | 5.24 | [8 empty] | 13.10 |  |  |  |  | 2.57
1995 |  |  |  | 6312.32 |  |  | 7504 |  |  |  | 915 | [10 empty] | 81.63 |  |  |  | 84.62 | [5 empty] | 78.75 |  |  | 85.66 |  |  |  | 3.01 |  | 2.63 | [8 empty] | 12.75 |  |  |  |  | 2.99
1996 |  |  |  | 6391.27 |  |  | 7615 |  |  |  | 915 | [10 empty] | 82.08 |  |  |  | 84.90 | [5 empty] | 79.52 |  |  | 86.69 |  |  |  | 1.18 |  | 1.02 | [8 empty] | 14.08 |  |  |  |  | 2.83
1997 |  |  |  | 5218.84 |  |  | 6107 |  |  |  | 915 | [10 empty] | 66.82 |  |  |  | 68.49 | [5 empty] | 65.11 |  |  | 69.71 |  |  |  | 1.07 |  | 0.74 | [8 empty] | 30.77 |  |  |  |  | 1.67
1998 |  |  |  | 6293.90 |  |  | 7354 |  |  |  | 915 | [10 empty] | 81.20 |  |  |  | 83.02 | [5 empty] | 78.52 |  |  | 83.95 |  |  |  | 7.01 |  | 6.26 | [8 empty] | 10.72 |  |  |  |  | 1.82
1999 |  |  |  | 5661.49 |  |  | 6674 |  |  |  | 915 | [10 empty] | 73.01 |  |  |  | 74.99 | [5 empty] | 70.63 |  |  | 76.19 |  |  |  | 11.30 |  | 9.55 | [8 empty] | 15.45 |  |  |  |  | 1.98
2000 |  |  |  | 4293.76 |  |  | 5092 |  |  |  | 915 | [10 empty] | 55.29 |  |  |  | 56.70 | [5 empty] | 53.42 |  |  | 57.97 |  |  |  | 23.28 |  | 17.20 | [8 empty] | 26.10 |  |  |  |  | 1.41
2001 |  |  |  | 6710.46 |  |  | 7779 |  |  |  | 915 | [10 empty] | 87.14 |  |  |  | 87.24 | [5 empty] | 83.72 |  |  | 88.80 |  |  |  | 2.49 |  | 2.23 | [8 empty] | 10.54 |  |  |  |  | 0.10
2002 |  |  |  | 6593.92 |  |  | 7714 |  |  |  | 915 | [10 empty] | 86.87 |  |  |  | 87.14 | [5 empty] | 82.27 |  |  | 88.06 |  |  |  | 0.23 |  | 0.20 | [8 empty] | 12.66 |  |  |  |  | 0.28
2003 |  |  |  | 6195.95 |  |  | 7521 |  |  |  | 915 | [10 empty] | 84.36 |  |  |  | 88.44 | [5 empty] | 77.30 |  |  | 85.86 |  |  |  | 0.76 |  | 0.68 | [8 empty] | 10.88 |  |  |  |  | 4.07
2004 |  |  |  | 5684.23 |  |  | 7271 |  |  |  | 915 | [10 empty] | 80.68 |  |  |  | 86.42 | [5 empty] | 70.72 |  |  | 82.78 |  |  |  | 2.15 |  | 1.90 | [8 empty] | 11.67 |  |  |  |  | 5.74
2005 |  |  |  | 5878.67 |  |  | 7128 |  |  |  | 915 | [10 empty] | 77.85 |  |  |  | 82.60 | [5 empty] | 73.33 |  |  | 81.36 |  |  |  | 9.85 |  | 9.87 | [8 empty] | 7.53 |  |  |  |  | 4.75
2006 |  |  |  | 6221.30 |  |  | 7366 |  |  |  | 915 | [10 empty] | 80.69 |  |  |  | 83.01 | [5 empty] | 77.62 |  |  | 84.09 |  |  |  | 1.78 |  | 1.91 | [8 empty] | 15.09 |  |  |  |  | 2.31
2007 |  |  |  | 6910.13 |  |  | 7989 |  |  |  | 915 | [10 empty] | 89.26 |  |  |  | 90.37 | [5 empty] | 86.20 |  |  | 91.19 |  |  |  | 0.27 |  | 0.82 | [8 empty] | 8.81 |  |  |  |  | 1.10
2008 |  |  |  | 4884.40 |  |  | 5768 |  |  |  | 915 | [10 empty] | 63.59 |  |  |  | 65.13 | [5 empty] | 60.77 |  |  | 65.66 |  |  |  | 1.42 |  | 22.37 | [8 empty] | 12.50 |  |  |  |  | 1.54
2009 |  |  |  | 6083.60 |  |  | 7028 |  |  |  | 915 | [10 empty] | 76.12 |  |  |  | 79.58 | [5 empty] | 75.90 |  |  | 80.23 |  |  |  | 1.98 |  | 13.57 | [8 empty] | 6.85 |  |  |  |  | 3.46
2010 |  |  |  | 6467.47 |  |  | 7629 |  |  |  | 915 | [10 empty] | 84.84 |  |  |  | 87.15 | [5 empty] | 80.69 |  |  | 87.09 |  |  |  | 12.52 |  | 12.47 | [8 empty] | 0.38 |  |  |  |  | 2.31
2011 |  |  |  | 4690.91 |  |  | 5560 |  |  |  | 915 | [10 empty] | 60.94 |  |  |  | 62.96 | [5 empty] | 58.52 |  |  | 63.47 |  |  |  | 1.11 |  | 11.80 | [8 empty] | 25.23 |  |  |  |  | 2.03
2012 |  |  |  | 6847.18 |  |  | 7806 |  |  |  | 915 | [10 empty] | 86.09 |  |  |  | 87.67 | [5 empty] | 85.19 |  |  | 88.87 |  |  |  | 0.98 |  | 3.71 | [8 empty] | 8.63 |  |  |  |  | 1.58
2013 |  |  |  | 5664.14 |  |  | 6607 |  |  |  | 915 | [10 empty] | 71.85 |  |  |  | 73.76 | [5 empty] | 70.67 |  |  | 75.42 |  |  |  | 6.53 |  | 8.27 | [8 empty] | 17.96 |  |  |  |  | 1.91
2014 |  |  |  | 6417.13 |  |  | 7593 |  |  |  | 915 | [10 empty] | 82.09 |  |  |  | 87.19 | [5 empty] | 80.06 |  |  | 86.68 |  |  |  | 0.54 |  | 4.44 | [8 empty] | 8.38 |  |  |  |  | 5.10
2015 |  |  |  | 6224.43 |  |  | 6828 |  |  |  | 915 | [10 empty] | 77.05 |  |  |  | 77.38 | [5 empty] | 77.66 |  |  | 77.95 |  |  |  | 0.21 |  | 4.59 | [8 empty] | 18.02 |  |  |  |  | 0.33
2016 |  |  |  | 7208.49 |  |  | 7948 |  |  |  | 915 | [10 empty] | 88.24 |  |  |  | 91.29 | [5 empty] | 89.69 |  |  | 90.48 |  |  |  | 0.43 |  | 0.39 | [8 empty] | 8.32 |  |  |  |  | 3.05
2017 |  |  |  | 3839.11 |  |  | 4529 |  |  |  | 915 | [10 empty] | 47.96 |  |  |  | 53.48 | [5 empty] | 47.90 |  |  | 51.70 |  |  |  | 32.46 |  | 29.21 | [8 empty] | 17.30 |  |  |  |  | 5.52
2018 |  |  |  | 4365.93 |  |  | 5046 |  |  |  | 915 | [10 empty] | 56.03 |  |  |  | 94.64 | [5 empty] | 54.47 |  |  | 57.60 |  |  |  | 5.35 |  | 5.35 | [8 empty] | 0.01 |  |  |  |  | 38.61
2019 |  |  |  | 5126.60 |  |  | 5725 |  |  |  | 915 | [10 empty] | 63.55 |  |  |  | 64.50 | [5 empty] | 63.96 |  |  | 65.35 |  |  |  | 3.01 |  | 16.84 | [8 empty] | 18.66 |  |  |  |  | 0.95
2020 |  |  |  | 6937.00 |  |  | 7591 |  |  |  | 915 | [10 empty] | 85.66 |  |  |  | 90.26 | [5 empty] | 86.31 |  |  | 86.42 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 9.63 |  |  |  |  | 4.61
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1980 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 451
B. |  | Refuelling without maintenance | [35 empty] | 66
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1012 |  |  |  | 26
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 26
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 39
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 22
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 10
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 46
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 83
Z. |  | Other | [39 empty] | 29
Subtotal | [37 empty] | 1108 |  |  |  | 568 | [11 empty] | 139
Total | [22 empty] | 0 | [14 empty] | 1815
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1980 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 67
12. |  |  | Reactor I&C Systems | [34 empty] | 30
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 58
15. |  |  | Reactor Cooling Systems | [34 empty] | 30
16. |  |  | Steam generation systems | [34 empty] | 26
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 64
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
33. |  |  | Circulating Water System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 127
41. |  |  | Main Generator Systems | [34 empty] | 31
42. |  |  | Electrical Power Supply Systems | [34 empty] | 32
Total | [37 empty] | 496

## TRICASTIN-3
2020 Operating Experience
FR-25 | [8 empty] | TRICASTIN-3 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-04-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-02-10
Gross electrical power | [12 empty] | : |  |  | 955 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-05-11
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 45 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4987.94 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.4 %
Energy Availability Factor (EAF) | [18 empty] | : | 61.67 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.82 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.21 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.97 %
Load Factor (LF) | [18 empty] | : | 62.06 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 12.54 %
Operating Factor (OF) | [18 empty] | : | 63.51 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3205 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 679.15 | 554.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 542.29 |  | 661.75 |  |  |  | 518.30 |  |  | 686.41 |  |  | 663.41 | [9 empty] | 681.67 |  |  | 4987.94
EAF [%] |  |  |  |  | 98.97 | 87.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 79.66 |  | 97.35 |  |  |  | 78.62 |  |  | 99.91 |  |  | 99.61 | [9 empty] | 98.03 |  |  | 61.67
UCF [%] |  |  |  |  | 100.00 | 96.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 58.02 |  |  | 78.39 | [6 empty] | 80.09 |  | 98.42 |  |  |  | 79.32 |  |  | 99.95 |  |  | 100.00 | [9 empty] | 99.95 |  |  | 74.21
LF [%] |  |  |  |  | 99.76 | 87.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 79.66 |  | 97.21 |  |  |  | 78.67 |  |  | 100.69 |  |  | 100.70 | [9 empty] | 100.13 |  |  | 62.06
OF [%] |  |  |  |  | 100.00 | 96.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 85.62 |  | 100.00 |  |  |  | 79.58 |  |  | 99.87 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 63.51
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 1.57 |  |  |  | 20.68 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.40
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 21.61 | [6 empty] | 14.38 |  | 1.57 |  |  |  | 20.68 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.82
PUF [%] |  |  |  |  | 0.00 | 3.54 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 41.98 |  |  | 0.00 | [6 empty] | 5.53 |  | 0.01 |  |  |  | 0.00 |  |  | 0.05 |  |  | 0.00 | [9 empty] | 0.05 |  |  | 20.97
XUF [%] |  |  |  |  | 1.03 | 9.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 58.01 |  |  | 78.39 | [6 empty] | 0.42 |  | 1.07 |  |  |  | 0.70 |  |  | 0.04 |  |  | 0.39 | [9 empty] | 1.92 |  |  | 12.54
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 236376.67 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.62 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.67 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.43 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.26 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.31 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.03 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.59 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.48 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 4917.60 |  |  | 6463 |  |  |  | 919 | [10 empty] | 78.00 |  |  |  | 78.00 | [5 empty] | 73.91 |  |  | 81.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.00 |  |  |  |  | 0.00
1982 |  |  |  | 5067.30 |  |  | 5966 |  |  |  | 915 | [10 empty] | 65.83 |  |  |  | 65.83 | [5 empty] | 63.22 |  |  | 68.11 |  |  |  | 7.17 |  | 5.08 | [8 empty] | 29.09 |  |  |  |  | 0.00
1983 |  |  |  | 6342.00 |  |  | 7544 |  |  |  | 915 | [10 empty] | 82.77 |  |  |  | 82.77 | [5 empty] | 79.12 |  |  | 86.12 |  |  |  | 4.29 |  | 3.71 | [8 empty] | 13.52 |  |  |  |  | 0.00
1984 |  |  |  | 6682.00 |  |  | 7668 |  |  |  | 915 | [10 empty] | 85.11 |  |  |  | 85.11 | [5 empty] | 83.14 |  |  | 87.30 |  |  |  | 2.01 |  | 1.74 | [8 empty] | 13.14 |  |  |  |  | 0.00
1985 |  |  |  | 7166.00 |  |  | 8518 |  |  |  | 915 | [10 empty] | 94.29 |  |  |  | 97.06 | [5 empty] | 89.40 |  |  | 97.24 |  |  |  | 0.89 |  | 0.87 | [8 empty] | 2.06 |  |  |  |  | 2.77
1986 |  |  |  | 6230.40 |  |  | 7704 |  |  |  | 915 | [10 empty] | 83.48 |  |  |  | 86.83 | [5 empty] | 77.73 |  |  | 87.95 |  |  |  | 3.18 |  | 2.85 | [8 empty] | 10.32 |  |  |  |  | 3.34
1987 |  |  |  | 5654.30 |  |  | 6810 |  |  |  | 915 | [10 empty] | 75.37 |  |  |  | 76.85 | [5 empty] | 70.54 |  |  | 77.74 |  |  |  | 8.05 |  | 6.73 | [8 empty] | 16.42 |  |  |  |  | 1.48
1988 |  |  |  | 5722.00 |  |  | 7106 |  |  |  | 915 | [10 empty] | 77.98 |  |  |  | 80.29 | [5 empty] | 71.19 |  |  | 80.90 |  |  |  | 8.35 |  | 7.32 | [8 empty] | 12.39 |  |  |  |  | 2.31
1989 |  |  |  | 5834.63 |  |  | 7188 |  |  |  | 915 | [10 empty] | 75.88 |  |  |  | 80.92 | [5 empty] | 72.79 |  |  | 82.05 |  |  |  | 2.34 |  | 1.94 | [8 empty] | 17.14 |  |  |  |  | 5.04
1990 |  |  |  | 6457.21 |  |  | 7671 |  |  |  | 915 | [10 empty] | 84.62 |  |  |  | 85.77 | [5 empty] | 80.56 |  |  | 87.57 |  |  |  | 2.00 |  | 1.75 | [8 empty] | 12.48 |  |  |  |  | 1.15
1991 |  |  |  | 4746.80 |  |  | 5941 |  |  |  | 915 | [10 empty] | 62.06 |  |  |  | 66.50 | [5 empty] | 59.22 |  |  | 67.82 |  |  |  | 23.92 |  | 20.91 | [8 empty] | 12.59 |  |  |  |  | 4.43
1992 |  |  |  | 5198.98 |  |  | 6010 |  |  |  | 915 | [10 empty] | 66.63 |  |  |  | 67.55 | [5 empty] | 64.69 |  |  | 68.42 |  |  |  | 6.11 |  | 4.39 | [8 empty] | 28.06 |  |  |  |  | 0.92
1993 |  |  |  | 6423.91 |  |  | 7373 |  |  |  | 915 | [10 empty] | 81.39 |  |  |  | 83.29 | [5 empty] | 80.14 |  |  | 84.17 |  |  |  | 5.63 |  | 4.97 | [8 empty] | 11.74 |  |  |  |  | 1.89
1994 |  |  |  | 6496.49 |  |  | 7641 |  |  |  | 915 | [10 empty] | 83.59 |  |  |  | 86.27 | [5 empty] | 81.05 |  |  | 87.23 |  |  |  | 2.85 |  | 2.53 | [8 empty] | 11.20 |  |  |  |  | 2.68
1995 |  |  |  | 6494.69 |  |  | 7675 |  |  |  | 915 | [10 empty] | 85.14 |  |  |  | 86.97 | [5 empty] | 81.03 |  |  | 87.61 |  |  |  | 2.11 |  | 1.88 | [8 empty] | 11.15 |  |  |  |  | 1.83
1996 |  |  |  | 5806.69 |  |  | 7172 |  |  |  | 915 | [10 empty] | 76.16 |  |  |  | 79.30 | [5 empty] | 72.25 |  |  | 81.65 |  |  |  | 7.59 |  | 6.51 | [8 empty] | 14.19 |  |  |  |  | 3.13
1997 |  |  |  | 6192.76 |  |  | 7331 |  |  |  | 915 | [10 empty] | 79.06 |  |  |  | 82.57 | [5 empty] | 77.26 |  |  | 83.69 |  |  |  | 8.25 |  | 7.42 | [8 empty] | 10.01 |  |  |  |  | 3.51
1998 |  |  |  | 6359.54 |  |  | 7375 |  |  |  | 915 | [10 empty] | 80.49 |  |  |  | 82.28 | [5 empty] | 79.34 |  |  | 84.19 |  |  |  | 6.55 |  | 5.77 | [8 empty] | 11.96 |  |  |  |  | 1.79
1999 |  |  |  | 5731.67 |  |  | 6828 |  |  |  | 915 | [10 empty] | 74.01 |  |  |  | 76.65 | [5 empty] | 71.51 |  |  | 77.95 |  |  |  | 11.85 |  | 10.31 | [8 empty] | 13.04 |  |  |  |  | 2.64
2000 |  |  |  | 5985.21 |  |  | 7325 |  |  |  | 915 | [10 empty] | 78.99 |  |  |  | 82.30 | [5 empty] | 74.47 |  |  | 83.39 |  |  |  | 8.50 |  | 7.65 | [8 empty] | 10.05 |  |  |  |  | 3.32
2001 |  |  |  | 4929.48 |  |  | 5777 |  |  |  | 915 | [10 empty] | 65.18 |  |  |  | 65.77 | [5 empty] | 61.50 |  |  | 65.95 |  |  |  | 15.73 |  | 12.27 | [8 empty] | 21.96 |  |  |  |  | 0.59
2002 |  |  |  | 5976.06 |  |  | 7140 |  |  |  | 915 | [10 empty] | 80.19 |  |  |  | 80.44 | [5 empty] | 74.56 |  |  | 81.51 |  |  |  | 1.24 |  | 1.01 | [8 empty] | 18.55 |  |  |  |  | 0.25
2003 |  |  |  | 6144.89 |  |  | 7607 |  |  |  | 915 | [10 empty] | 79.71 |  |  |  | 86.93 | [5 empty] | 76.66 |  |  | 86.84 |  |  |  | 4.69 |  | 4.28 | [8 empty] | 8.79 |  |  |  |  | 7.23
2004 |  |  |  | 6377.15 |  |  | 7455 |  |  |  | 915 | [10 empty] | 82.86 |  |  |  | 84.34 | [5 empty] | 79.34 |  |  | 84.87 |  |  |  | 3.69 |  | 3.23 | [8 empty] | 12.43 |  |  |  |  | 1.47
2005 |  |  |  | 6563.04 |  |  | 7981 |  |  |  | 915 | [10 empty] | 86.14 |  |  |  | 90.44 | [5 empty] | 81.87 |  |  | 91.10 |  |  |  | 0.74 |  | 1.69 | [8 empty] | 7.87 |  |  |  |  | 4.30
2006 |  |  |  | 6006.89 |  |  | 7488 |  |  |  | 915 | [10 empty] | 81.28 |  |  |  | 86.47 | [5 empty] | 74.94 |  |  | 85.48 |  |  |  | 1.44 |  | 1.78 | [8 empty] | 11.75 |  |  |  |  | 5.18
2007 |  |  |  | 6775.03 |  |  | 7862 |  |  |  | 915 | [10 empty] | 87.57 |  |  |  | 88.96 | [5 empty] | 84.53 |  |  | 89.75 |  |  |  | 2.62 |  | 3.78 | [8 empty] | 7.26 |  |  |  |  | 1.39
2008 |  |  |  | 6185.23 |  |  | 7030 |  |  |  | 915 | [10 empty] | 78.59 |  |  |  | 79.66 | [5 empty] | 76.96 |  |  | 80.03 |  |  |  | 0.32 |  | 8.87 | [8 empty] | 11.48 |  |  |  |  | 1.06
2009 |  |  |  | 5750.65 |  |  | 6608 |  |  |  | 915 | [10 empty] | 73.61 |  |  |  | 75.88 | [5 empty] | 71.74 |  |  | 75.43 |  |  |  | 16.37 |  | 18.01 | [8 empty] | 6.11 |  |  |  |  | 2.27
2010 |  |  |  | 6257.49 |  |  | 7089 |  |  |  | 915 | [10 empty] | 79.10 |  |  |  | 80.07 | [5 empty] | 78.07 |  |  | 80.92 |  |  |  | 1.30 |  | 5.87 | [8 empty] | 14.05 |  |  |  |  | 0.98
2011 |  |  |  | 5827.60 |  |  | 6507 |  |  |  | 915 | [10 empty] | 72.83 |  |  |  | 73.42 | [5 empty] | 72.71 |  |  | 74.28 |  |  |  | 17.38 |  | 18.27 | [8 empty] | 8.31 |  |  |  |  | 0.59
2012 |  |  |  | 4959.82 |  |  | 5534 |  |  |  | 915 | [10 empty] | 61.47 |  |  |  | 61.93 | [5 empty] | 61.71 |  |  | 63.00 |  |  |  | 1.39 |  | 13.77 | [8 empty] | 24.31 |  |  |  |  | 0.45
2013 |  |  |  | 6912.58 |  |  | 7765 |  |  |  | 915 | [10 empty] | 87.60 |  |  |  | 87.87 | [5 empty] | 86.24 |  |  | 88.64 |  |  |  | 0.83 |  | 3.52 | [8 empty] | 8.61 |  |  |  |  | 0.28
2014 |  |  |  | 5763.72 |  |  | 6369 |  |  |  | 915 | [10 empty] | 71.84 |  |  |  | 72.39 | [5 empty] | 71.91 |  |  | 72.71 |  |  |  | 7.95 |  | 11.53 | [8 empty] | 16.08 |  |  |  |  | 0.55
2015 |  |  |  | 7186.07 |  |  | 7928 |  |  |  | 915 | [10 empty] | 89.05 |  |  |  | 89.64 | [5 empty] | 89.65 |  |  | 90.50 |  |  |  | 0.48 |  | 1.58 | [8 empty] | 8.77 |  |  |  |  | 0.59
2016 |  |  |  | 2863.03 |  |  | 3168 |  |  |  | 915 | [10 empty] | 35.34 |  |  |  | 77.34 | [5 empty] | 35.62 |  |  | 36.07 |  |  |  | 0.00 |  | 5.73 | [8 empty] | 16.94 |  |  |  |  | 42.00
2017 |  |  |  | 6042.82 |  |  | 6785 |  |  |  | 915 | [10 empty] | 75.80 |  |  |  | 76.75 | [5 empty] | 75.39 |  |  | 77.45 |  |  |  | 2.57 |  | 12.33 | [8 empty] | 10.91 |  |  |  |  | 0.95
2018 |  |  |  | 5453.10 |  |  | 6019 |  |  |  | 915 | [10 empty] | 68.17 |  |  |  | 68.32 | [5 empty] | 68.03 |  |  | 68.71 |  |  |  | 18.45 |  | 15.46 | [8 empty] | 16.21 |  |  |  |  | 0.16
2019 |  |  |  | 6032.36 |  |  | 7059 |  |  |  | 915 | [10 empty] | 78.63 |  |  |  | 95.75 | [5 empty] | 75.26 |  |  | 80.58 |  |  |  | 1.18 |  | 3.13 | [8 empty] | 1.12 |  |  |  |  | 17.13
2020 |  |  |  | 4987.94 |  |  | 5579 |  |  |  | 915 | [10 empty] | 61.67 |  |  |  | 74.21 | [5 empty] | 62.06 |  |  | 63.51 |  |  |  | 2.40 |  | 4.82 | [8 empty] | 20.97 |  |  |  |  | 12.54
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 408
B. |  | Refuelling without maintenance | [35 empty] | 89
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 945 |  |  |  | 7
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 24
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 24
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 25
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 16 | [11 empty] | 98
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 35
Z. |  | Other | [39 empty] | 24
Subtotal | [37 empty] | 1062 |  |  |  | 505 | [11 empty] | 137
Total | [22 empty] | 0 | [14 empty] | 1704
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 31
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 19
14. |  |  | Safety Systems | [34 empty] | 46
15. |  |  | Reactor Cooling Systems | [34 empty] | 39
16. |  |  | Steam generation systems | [34 empty] | 93
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 96
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 70
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 88
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 519

## TRICASTIN-4
2020 Operating Experience
FR-26 | [8 empty] | TRICASTIN-4 | [26 empty] | FRANCE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Owner | [7 empty] | : | EDF (ÉLECTRICITÉ DE FRANCE )
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CP1 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-05-01
Thermal power | [12 empty] | : |  |  | 2785 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-06-12
Gross electrical power | [12 empty] | : |  |  | 955 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-11-01
Reference unit power (net) | [12 empty] | : |  |  | 915 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33735 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 45 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5432.69 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 6.78 %
Energy Availability Factor (EAF) | [18 empty] | : | 68.21 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.27 %
Unit Capability Factor (UCF) | [18 empty] | : | 72.47 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 22.26 %
Load Factor (LF) | [18 empty] | : | 67.59 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 4.27 %
Operating Factor (OF) | [18 empty] | : | 70.75 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2569 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 637.66 | 547.87 |  |  |  | 583.02 |  | 452.73 | [8 empty] | 682.33 |  |  | 456.87 | [6 empty] | 55.34 |  | 0.00 |  |  |  | 122.81 |  |  | 679.99 |  |  | 544.27 | [9 empty] | 669.81 |  |  | 5432.69
EAF [%] |  |  |  |  | 93.41 | 92.20 |  |  |  | 84.23 |  | 72.34 | [8 empty] | 99.47 |  |  | 69.41 | [6 empty] | 8.14 |  | 0.00 |  |  |  | 18.55 |  |  | 99.85 |  |  | 82.32 | [9 empty] | 99.10 |  |  | 68.21
UCF [%] |  |  |  |  | 97.11 | 92.20 |  |  |  | 90.55 |  | 89.96 | [8 empty] | 100.00 |  |  | 83.25 | [6 empty] | 9.64 |  | 0.00 |  |  |  | 25.55 |  |  | 99.85 |  |  | 82.73 | [9 empty] | 99.80 |  |  | 72.47
LF [%] |  |  |  |  | 93.67 | 86.03 |  |  |  | 85.76 |  | 68.72 | [8 empty] | 100.23 |  |  | 69.35 | [6 empty] | 8.13 |  | 0.00 |  |  |  | 18.64 |  |  | 99.75 |  |  | 82.62 | [9 empty] | 98.39 |  |  | 67.59
OF [%] |  |  |  |  | 100.00 | 92.82 |  |  |  | 85.06 |  | 71.67 | [8 empty] | 100.00 |  |  | 83.19 | [6 empty] | 9.81 |  | 0.00 |  |  |  | 24.17 |  |  | 99.87 |  |  | 83.19 | [9 empty] | 100.00 |  |  | 70.75
FLR [%] |  |  |  |  | 2.89 | 7.75 |  |  |  | 9.45 |  | 10.04 | [8 empty] | 0.00 |  |  | 16.75 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 17.27 | [9 empty] | 0.06 |  |  | 6.78
UCL [%] |  |  |  |  | 2.89 | 7.74 |  |  |  | 9.45 |  | 10.04 | [8 empty] | 0.00 |  |  | 16.75 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 17.27 | [9 empty] | 0.06 |  |  | 5.27
PUF [%] |  |  |  |  | 0.00 | 0.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 90.36 |  | 100.00 |  |  |  | 74.45 |  |  | 0.15 |  |  | 0.00 | [9 empty] | 0.14 |  |  | 22.26
XUF [%] |  |  |  |  | 3.70 | 0.00 |  |  |  | 6.32 |  | 17.62 | [8 empty] | 0.53 |  |  | 13.84 | [6 empty] | 1.50 |  | 0.00 |  |  |  | 7.00 |  |  | 0.00 |  |  | 0.41 | [9 empty] | 0.70 |  |  | 4.27
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 234774.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.81 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.61 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.67 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.17 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.39 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.57 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.99 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 2480.00 |  |  | 3883 |  |  |  | 917 | [10 empty] | 97.21 |  |  |  | 97.21 | [5 empty] | 95.30 |  |  | 99.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.79 |  |  |  |  | 0.00
1982 |  |  |  | 5470.50 |  |  | 6311 |  |  |  | 915 | [10 empty] | 69.85 |  |  |  | 69.85 | [5 empty] | 68.25 |  |  | 72.04 |  |  |  | 5.62 |  | 4.16 | [8 empty] | 25.99 |  |  |  |  | 0.00
1983 |  |  |  | 6170.00 |  |  | 7386 |  |  |  | 915 | [10 empty] | 80.67 |  |  |  | 80.67 | [5 empty] | 76.98 |  |  | 84.32 |  |  |  | 3.68 |  | 3.08 | [8 empty] | 16.25 |  |  |  |  | 0.00
1984 |  |  |  | 5446.00 |  |  | 7587 |  |  |  | 915 | [10 empty] | 87.08 |  |  |  | 87.08 | [5 empty] | 67.76 |  |  | 86.37 |  |  |  | 4.70 |  | 4.30 | [8 empty] | 8.62 |  |  |  |  | 0.00
1985 |  |  |  | 6161.70 |  |  | 7816 |  |  |  | 915 | [10 empty] | 84.80 |  |  |  | 91.35 | [5 empty] | 76.87 |  |  | 89.22 |  |  |  | 0.51 |  | 0.47 | [8 empty] | 8.19 |  |  |  |  | 6.54
1986 |  |  |  | 5873.90 |  |  | 7568 |  |  |  | 915 | [10 empty] | 81.78 |  |  |  | 85.70 | [5 empty] | 73.28 |  |  | 86.39 |  |  |  | 0.52 |  | 0.45 | [8 empty] | 13.85 |  |  |  |  | 3.92
1987 |  |  |  | 5725.70 |  |  | 7257 |  |  |  | 915 | [10 empty] | 80.12 |  |  |  | 84.16 | [5 empty] | 71.43 |  |  | 82.84 |  |  |  | 5.52 |  | 4.92 | [8 empty] | 10.93 |  |  |  |  | 4.04
1988 |  |  |  | 3770.00 |  |  | 4772 |  |  |  | 915 | [10 empty] | 66.25 |  |  |  | 67.65 | [5 empty] | 46.91 |  |  | 54.33 |  |  |  | 19.52 |  | 16.41 | [8 empty] | 15.94 |  |  |  |  | 1.41
1989 |  |  |  | 5729.11 |  |  | 7335 |  |  |  | 915 | [10 empty] | 79.80 |  |  |  | 82.94 | [5 empty] | 71.48 |  |  | 83.73 |  |  |  | 3.98 |  | 3.44 | [8 empty] | 13.62 |  |  |  |  | 3.14
1990 |  |  |  | 5201.58 |  |  | 7329 |  |  |  | 915 | [10 empty] | 77.42 |  |  |  | 82.72 | [5 empty] | 64.89 |  |  | 83.66 |  |  |  | 5.39 |  | 4.71 | [8 empty] | 12.57 |  |  |  |  | 5.30
1991 |  |  |  | 5742.81 |  |  | 6838 |  |  |  | 915 | [10 empty] | 74.55 |  |  |  | 77.09 | [5 empty] | 71.65 |  |  | 78.06 |  |  |  | 11.76 |  | 10.27 | [8 empty] | 12.64 |  |  |  |  | 2.54
1992 |  |  |  | 6459.26 |  |  | 7968 |  |  |  | 915 | [10 empty] | 86.69 |  |  |  | 90.20 | [5 empty] | 80.37 |  |  | 90.71 |  |  |  | 0.54 |  | 0.49 | [8 empty] | 9.31 |  |  |  |  | 3.51
1993 |  |  |  | 5302.81 |  |  | 6842 |  |  |  | 915 | [10 empty] | 70.89 |  |  |  | 80.08 | [5 empty] | 66.16 |  |  | 78.11 |  |  |  | 2.01 |  | 1.64 | [8 empty] | 18.27 |  |  |  |  | 9.19
1994 |  |  |  | 5952.97 |  |  | 7049 |  |  |  | 915 | [10 empty] | 77.80 |  |  |  | 80.87 | [5 empty] | 74.27 |  |  | 80.47 |  |  |  | 7.76 |  | 6.81 | [8 empty] | 12.33 |  |  |  |  | 3.06
1995 |  |  |  | 6208.92 |  |  | 7562 |  |  |  | 915 | [10 empty] | 81.99 |  |  |  | 85.67 | [5 empty] | 77.46 |  |  | 86.32 |  |  |  | 4.77 |  | 4.29 | [8 empty] | 10.04 |  |  |  |  | 3.69
1996 |  |  |  | 6700.35 |  |  | 7774 |  |  |  | 915 | [10 empty] | 86.55 |  |  |  | 87.59 | [5 empty] | 83.37 |  |  | 88.50 |  |  |  | 1.75 |  | 1.56 | [8 empty] | 10.85 |  |  |  |  | 1.04
1997 |  |  |  | 6488.77 |  |  | 7595 |  |  |  | 915 | [10 empty] | 84.84 |  |  |  | 86.00 | [5 empty] | 80.95 |  |  | 86.70 |  |  |  | 1.26 |  | 1.09 | [8 empty] | 12.90 |  |  |  |  | 1.17
1998 |  |  |  | 5912.98 |  |  | 7138 |  |  |  | 915 | [10 empty] | 76.19 |  |  |  | 80.45 | [5 empty] | 73.77 |  |  | 81.48 |  |  |  | 9.79 |  | 8.73 | [8 empty] | 10.82 |  |  |  |  | 4.25
1999 |  |  |  | 5887.87 |  |  | 7158 |  |  |  | 915 | [10 empty] | 77.95 |  |  |  | 80.49 | [5 empty] | 73.46 |  |  | 81.71 |  |  |  | 11.36 |  | 10.31 | [8 empty] | 9.20 |  |  |  |  | 2.53
2000 |  |  |  | 5780.25 |  |  | 6873 |  |  |  | 915 | [10 empty] | 75.76 |  |  |  | 77.41 | [5 empty] | 71.92 |  |  | 78.24 |  |  |  | 5.60 |  | 4.59 | [8 empty] | 18.00 |  |  |  |  | 1.65
2001 |  |  |  | 6036.95 |  |  | 7138 |  |  |  | 915 | [10 empty] | 81.25 |  |  |  | 83.00 | [5 empty] | 75.32 |  |  | 81.48 |  |  |  | 6.39 |  | 5.67 | [8 empty] | 11.34 |  |  |  |  | 1.75
2002 |  |  |  | 6260.60 |  |  | 7168 |  |  |  | 915 | [10 empty] | 81.89 |  |  |  | 83.97 | [5 empty] | 78.11 |  |  | 81.83 |  |  |  | 4.25 |  | 3.73 | [8 empty] | 12.31 |  |  |  |  | 2.08
2003 |  |  |  | 6387.89 |  |  | 7399 |  |  |  | 915 | [10 empty] | 79.89 |  |  |  | 82.88 | [5 empty] | 79.70 |  |  | 84.46 |  |  |  | 5.91 |  | 5.20 | [8 empty] | 11.92 |  |  |  |  | 2.99
2004 |  |  |  | 4724.06 |  |  | 5359 |  |  |  | 915 | [10 empty] | 58.84 |  |  |  | 59.83 | [5 empty] | 58.78 |  |  | 61.01 |  |  |  | 2.24 |  | 1.37 | [8 empty] | 38.80 |  |  |  |  | 0.99
2005 |  |  |  | 6501.37 |  |  | 7728 |  |  |  | 915 | [10 empty] | 83.63 |  |  |  | 88.80 | [5 empty] | 81.10 |  |  | 88.21 |  |  |  | 4.04 |  | 3.74 | [8 empty] | 7.46 |  |  |  |  | 5.16
2006 |  |  |  | 6410.44 |  |  | 7412 |  |  |  | 915 | [10 empty] | 82.98 |  |  |  | 84.10 | [5 empty] | 79.98 |  |  | 84.61 |  |  |  | 2.81 |  | 4.73 | [8 empty] | 11.17 |  |  |  |  | 1.12
2007 |  |  |  | 7046.97 |  |  | 8096 |  |  |  | 915 | [10 empty] | 90.42 |  |  |  | 92.18 | [5 empty] | 87.91 |  |  | 92.41 |  |  |  | 0.13 |  | 0.96 | [8 empty] | 6.86 |  |  |  |  | 1.75
2008 |  |  |  | 6016.61 |  |  | 6867 |  |  |  | 915 | [10 empty] | 76.42 |  |  |  | 77.35 | [5 empty] | 74.86 |  |  | 78.18 |  |  |  | 2.16 |  | 9.14 | [8 empty] | 13.51 |  |  |  |  | 0.93
2009 |  |  |  | 6536.71 |  |  | 7630 |  |  |  | 915 | [10 empty] | 84.80 |  |  |  | 86.48 | [5 empty] | 81.55 |  |  | 87.10 |  |  |  | 0.89 |  | 6.30 | [8 empty] | 7.23 |  |  |  |  | 1.67
2010 |  |  |  | 6263.83 |  |  | 7275 |  |  |  | 915 | [10 empty] | 79.97 |  |  |  | 82.28 | [5 empty] | 78.15 |  |  | 83.05 |  |  |  | 0.31 |  | 3.51 | [8 empty] | 14.21 |  |  |  |  | 2.31
2011 |  |  |  | 6477.78 |  |  | 7589 |  |  |  | 915 | [10 empty] | 84.30 |  |  |  | 86.18 | [5 empty] | 80.82 |  |  | 86.63 |  |  |  | 4.34 |  | 7.46 | [8 empty] | 6.36 |  |  |  |  | 1.87
2012 |  |  |  | 5937.33 |  |  | 7062 |  |  |  | 915 | [10 empty] | 78.04 |  |  |  | 82.15 | [5 empty] | 73.87 |  |  | 80.40 |  |  |  | 0.43 |  | 4.83 | [8 empty] | 13.02 |  |  |  |  | 4.10
2013 |  |  |  | 6556.13 |  |  | 7607 |  |  |  | 915 | [10 empty] | 84.21 |  |  |  | 87.24 | [5 empty] | 81.79 |  |  | 86.84 |  |  |  | 1.34 |  | 6.41 | [8 empty] | 6.35 |  |  |  |  | 3.03
2014 |  |  |  | 5218.80 |  |  | 5828 |  |  |  | 915 | [10 empty] | 65.48 |  |  |  | 66.62 | [5 empty] | 65.11 |  |  | 66.53 |  |  |  | 0.01 |  | 3.98 | [8 empty] | 29.40 |  |  |  |  | 1.14
2015 |  |  |  | 6538.75 |  |  | 7080 |  |  |  | 915 | [10 empty] | 79.60 |  |  |  | 80.15 | [5 empty] | 81.58 |  |  | 80.82 |  |  |  | 2.51 |  | 11.24 | [8 empty] | 8.61 |  |  |  |  | 0.55
2016 |  |  |  | 6420.53 |  |  | 6914 |  |  |  | 915 | [10 empty] | 78.13 |  |  |  | 82.46 | [5 empty] | 79.88 |  |  | 78.71 |  |  |  | 1.98 |  | 1.67 | [8 empty] | 15.88 |  |  |  |  | 4.33
2017 |  |  |  | 5531.81 |  |  | 6267 |  |  |  | 915 | [10 empty] | 69.86 |  |  |  | 70.95 | [5 empty] | 69.01 |  |  | 71.54 |  |  |  | 25.20 |  | 28.63 | [8 empty] | 0.42 |  |  |  |  | 1.09
2018 |  |  |  | 5916.77 |  |  | 6699 |  |  |  | 915 | [10 empty] | 74.10 |  |  |  | 75.71 | [5 empty] | 73.82 |  |  | 76.47 |  |  |  | 3.43 |  | 7.69 | [8 empty] | 16.60 |  |  |  |  | 1.61
2019 |  |  |  | 6228.37 |  |  | 7130 |  |  |  | 915 | [10 empty] | 79.65 |  |  |  | 80.42 | [5 empty] | 77.71 |  |  | 81.39 |  |  |  | 3.51 |  | 8.92 | [8 empty] | 10.65 |  |  |  |  | 0.77
2020 |  |  |  | 5432.69 |  |  | 6215 |  |  |  | 915 | [10 empty] | 68.21 |  |  |  | 72.47 | [5 empty] | 67.59 |  |  | 70.75 |  |  |  | 6.78 |  | 5.27 | [8 empty] | 22.26 |  |  |  |  | 4.27
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 297 | [11 empty] | 1
B. |  | Refuelling without maintenance | [35 empty] | 67
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 966 |  |  |  | 8
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 15
E. |  | Testing of plant systems or components | [35 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 46
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 18
L. |  | Human factor related | [39 empty] | 20
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
O. |  | Load dispatching, prioritization | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 22 | [11 empty] | 28
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 2
Z. |  | Other | [39 empty] | 33 | [11 empty] | 0
Subtotal | [37 empty] | 1050 |  |  |  | 426 | [11 empty] | 53
Total | [22 empty] | 0 | [14 empty] | 1529
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 21
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 75
15. |  |  | Reactor Cooling Systems | [34 empty] | 15
16. |  |  | Steam generation systems | [34 empty] | 32
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 23
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 97
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 33
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [37 empty] | 353