## GENKAI-3
2020 Operating Experience
JP-45 | [8 empty] | GENKAI-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Owner | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (4-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1988-06-01
Thermal power | [12 empty] | : |  |  | 3423 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-06-15
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-03-18
Reference unit power (net) | [12 empty] | : |  |  | 1127 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 46 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.76
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8236.08 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.29 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 81.29 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 18.71 %
Load Factor (LF) | [18 empty] | : | 83.2 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 81.82 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1597 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 4.1 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 861.91 | 806.36 |  |  |  | 861.40 |  | 833.38 | [8 empty] | 861.23 |  |  | 832.00 | [6 empty] | 857.85 |  | 851.61 |  |  |  | 465.49 |  |  | 0.00 |  |  | 151.19 | [9 empty] | 853.67 |  |  | 8236.09
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 56.36 |  |  | 0.00 |  |  | 18.69 | [9 empty] | 100.00 |  |  | 81.29
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 56.36 |  |  | 0.00 |  |  | 18.69 | [9 empty] | 100.00 |  |  | 81.29
LF [%] |  |  |  |  | 102.79 | 102.80 |  |  |  | 102.73 |  | 102.70 | [8 empty] | 102.71 |  |  | 102.53 | [6 empty] | 102.31 |  | 101.56 |  |  |  | 57.37 |  |  | 0.00 |  |  | 18.63 | [9 empty] | 101.81 |  |  | 83.20
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 56.81 |  |  | 0.00 |  |  | 24.72 | [9 empty] | 100.00 |  |  | 81.82
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 43.64 |  |  | 100.00 |  |  | 81.31 | [9 empty] | 0.00 |  |  | 18.71
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 172860.08 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.33 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 61.95 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 61.95 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 37.85 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 62.91 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 62.23 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 8795.82 |  |  | 7828 |  |  |  | 1127 | [10 empty] | 96.91 |  |  |  | 96.91 | [5 empty] | 97.39 |  |  | 97.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.09 |  |  |  |  | 0.00
1995 |  |  |  | 7356.33 |  |  | 6588 |  |  |  | 1127 | [10 empty] | 74.14 |  |  |  | 74.14 | [5 empty] | 74.51 |  |  | 75.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.86 |  |  |  |  | 0.00
1996 |  |  |  | 7444.90 |  |  | 6663 |  |  |  | 1127 | [10 empty] | 74.86 |  |  |  | 74.86 | [5 empty] | 75.20 |  |  | 75.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.14 |  |  |  |  | 0.00
1997 |  |  |  | 8259.94 |  |  | 7358 |  |  |  | 1127 | [10 empty] | 83.29 |  |  |  | 83.29 | [5 empty] | 83.67 |  |  | 84.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.71 |  |  |  |  | 0.00
1998 |  |  |  | 9633.13 |  |  | 8514 |  |  |  | 1127 | [10 empty] | 97.14 |  |  |  | 97.14 | [5 empty] | 97.58 |  |  | 97.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.86 |  |  |  |  | 0.00
1999 |  |  |  | 7999.83 |  |  | 7068 |  |  |  | 1127 | [10 empty] | 80.67 |  |  |  | 80.67 | [5 empty] | 81.03 |  |  | 80.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.33 |  |  |  |  | 0.00
2000 |  |  |  | 8109.74 |  |  | 7164 |  |  |  | 1127 | [10 empty] | 81.55 |  |  |  | 81.55 | [5 empty] | 81.92 |  |  | 81.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.45 |  |  |  |  | 0.00
2001 |  |  |  | 8205.05 |  |  | 7249 |  |  |  | 1127 | [10 empty] | 82.74 |  |  |  | 82.74 | [5 empty] | 83.11 |  |  | 82.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.26 |  |  |  |  | 0.00
2002 |  |  |  | 9561.54 |  |  | 8446 |  |  |  | 1127 | [10 empty] | 96.40 |  |  |  | 96.40 | [5 empty] | 96.85 |  |  | 96.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.60 |  |  |  |  | 0.00
2003 |  |  |  | 8667.78 |  |  | 7497 |  |  |  | 1127 | [10 empty] | 85.59 |  |  |  | 85.59 | [5 empty] | 87.80 |  |  | 85.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.41 |  |  |  |  | 0.00
2004 |  |  |  | 8121.12 |  |  | 7015 |  |  |  | 1127 | [10 empty] | 79.87 |  |  |  | 79.87 | [5 empty] | 82.04 |  |  | 79.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.13 |  |  |  |  | 0.00
2005 |  |  |  | 8658.87 |  |  | 7523 |  |  |  | 1127 | [10 empty] | 85.32 |  |  |  | 85.32 | [5 empty] | 87.71 |  |  | 85.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.68 |  |  |  |  | 0.00
2006 |  |  |  | 9725.17 |  |  | 8401 |  |  |  | 1127 | [10 empty] | 95.86 |  |  |  | 95.86 | [5 empty] | 98.51 |  |  | 95.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.14 |  |  |  |  | 0.00
2007 |  |  |  | 7988.29 |  |  | 6987 |  |  |  | 1127 | [10 empty] | 79.11 |  |  |  | 79.11 | [5 empty] | 80.91 |  |  | 79.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.89 |  |  |  |  | 0.00
2008 |  |  |  | 8259.64 |  |  | 7211 |  |  |  | 1127 | [10 empty] | 81.57 |  |  |  | 81.57 | [5 empty] | 83.43 |  |  | 82.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.43 |  |  |  |  | 0.00
2009 |  |  |  | 8061.86 |  |  | 7043 |  |  |  | 1127 | [10 empty] | 79.87 |  |  |  | 79.87 | [5 empty] | 81.66 |  |  | 80.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.13 |  |  |  |  | 0.00
2010 |  |  |  | 9506.52 |  |  | 8257 |  |  |  | 1127 | [10 empty] | 94.22 |  |  |  | 94.22 | [5 empty] | 96.29 |  |  | 94.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.78 |  |  |  |  | 0.00
2011 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 7143.28 |  |  | 6313 |  |  |  | 1127 | [10 empty] | 70.82 |  |  |  | 70.82 | [5 empty] | 72.36 |  |  | 72.07 |  |  |  | 7.13 |  | 5.44 | [8 empty] | 23.74 |  |  |  |  | 0.00
2019 |  |  |  | 8106.36 |  |  | 7067 |  |  |  | 1127 | [10 empty] | 80.14 |  |  |  | 80.14 | [5 empty] | 82.11 |  |  | 80.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.86 |  |  |  |  | 0.00
2020 |  |  |  | 8236.08 |  |  | 7187 |  |  |  | 1127 | [10 empty] | 81.29 |  |  |  | 81.29 | [5 empty] | 83.20 |  |  | 81.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.71 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1994 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 16
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1597 | [14 empty] | 1017
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 2282
Subtotal | [22 empty] | 1597 | [14 empty] | 3299 |  |  |  | 16
Total | [22 empty] | 1597 | [14 empty] | 3315
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1994 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
Total | [37 empty] | 16

## GENKAI-4
2020 Operating Experience
JP-46 | [8 empty] | GENKAI-4 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Owner | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (4-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1992-07-15
Thermal power | [12 empty] | : |  |  | 3423 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1996-11-12
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1997-07-25
Reference unit power (net) | [12 empty] | : |  |  | 1127 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 24 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 46 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.76
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9703.45 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.42 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.42 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 3.58 %
Load Factor (LF) | [18 empty] | : | 98.02 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 96.46 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 311 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 1.39 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 854.57 | 799.52 |  |  |  | 854.51 |  | 826.93 | [8 empty] | 854.09 |  |  | 825.51 | [6 empty] | 851.76 |  | 846.79 |  |  |  | 822.17 |  |  | 852.06 |  |  | 823.54 | [9 empty] | 492.00 |  |  | 9703.45
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 57.76 |  |  | 96.42
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 57.76 |  |  | 96.42
LF [%] |  |  |  |  | 101.92 | 101.93 |  |  |  | 101.91 |  | 101.91 | [8 empty] | 101.86 |  |  | 101.73 | [6 empty] | 101.58 |  | 100.99 |  |  |  | 101.32 |  |  | 101.62 |  |  | 101.49 | [9 empty] | 58.68 |  |  | 98.02
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 58.20 |  |  | 96.46
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 42.24 |  |  | 3.58
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 148909.45 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.1 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 62.57 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 62.57 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 36.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 63.46 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 62.83 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1997 |  |  |  | 5841.01 |  |  | 5901 |  |  |  | 1127 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.73 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1998 |  |  |  | 7634.53 |  |  | 6783 |  |  |  | 1127 | [10 empty] | 76.75 |  |  |  | 76.75 | [5 empty] | 77.33 |  |  | 77.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.25 |  |  |  |  | 0.00
1999 |  |  |  | 9716.30 |  |  | 8559 |  |  |  | 1127 | [10 empty] | 97.69 |  |  |  | 97.69 | [5 empty] | 98.42 |  |  | 97.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.31 |  |  |  |  | 0.00
2000 |  |  |  | 8181.18 |  |  | 7205 |  |  |  | 1127 | [10 empty] | 82.02 |  |  |  | 82.02 | [5 empty] | 82.64 |  |  | 82.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.98 |  |  |  |  | 0.00
2001 |  |  |  | 8107.23 |  |  | 7142 |  |  |  | 1127 | [10 empty] | 81.51 |  |  |  | 81.51 | [5 empty] | 82.12 |  |  | 81.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.49 |  |  |  |  | 0.00
2002 |  |  |  | 8208.29 |  |  | 7217 |  |  |  | 1127 | [10 empty] | 82.37 |  |  |  | 82.37 | [5 empty] | 83.14 |  |  | 82.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.63 |  |  |  |  | 0.00
2003 |  |  |  | 9678.75 |  |  | 8422 |  |  |  | 1127 | [10 empty] | 96.12 |  |  |  | 96.12 | [5 empty] | 98.04 |  |  | 96.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.88 |  |  |  |  | 0.00
2004 |  |  |  | 8330.56 |  |  | 7243 |  |  |  | 1127 | [10 empty] | 82.44 |  |  |  | 82.44 | [5 empty] | 84.15 |  |  | 82.46 |  |  |  | 4.05 |  | 3.48 | [8 empty] | 14.09 |  |  |  |  | 0.00
2005 |  |  |  | 8572.52 |  |  | 7499 |  |  |  | 1127 | [10 empty] | 85.04 |  |  |  | 85.04 | [5 empty] | 86.83 |  |  | 85.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.96 |  |  |  |  | 0.00
2006 |  |  |  | 7765.58 |  |  | 6813 |  |  |  | 1127 | [10 empty] | 76.97 |  |  |  | 76.97 | [5 empty] | 78.66 |  |  | 77.77 |  |  |  | 3.64 |  | 2.91 | [8 empty] | 20.12 |  |  |  |  | 0.00
2007 |  |  |  | 10025.27 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.55 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 7695.98 |  |  | 6797 |  |  |  | 1127 | [10 empty] | 76.61 |  |  |  | 76.61 | [5 empty] | 77.74 |  |  | 77.38 |  |  |  | 2.15 |  | 1.69 | [8 empty] | 21.71 |  |  |  |  | 0.00
2009 |  |  |  | 8325.59 |  |  | 7331 |  |  |  | 1127 | [10 empty] | 83.07 |  |  |  | 83.07 | [5 empty] | 84.33 |  |  | 83.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.93 |  |  |  |  | 0.00
2010 |  |  |  | 8365.65 |  |  | 7355 |  |  |  | 1127 | [10 empty] | 83.43 |  |  |  | 83.43 | [5 empty] | 84.74 |  |  | 83.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.57 |  |  |  |  | 0.00
2011 |  |  |  | 8999.40 |  |  | 7918 |  |  |  | 1127 | [10 empty] | 90.09 |  |  |  | 90.09 | [5 empty] | 91.16 |  |  | 90.39 |  |  |  | 8.35 |  | 8.21 | [8 empty] | 1.70 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 5269.18 |  |  | 4706 |  |  |  | 1127 | [10 empty] | 52.56 |  |  |  | 52.56 | [5 empty] | 53.37 |  |  | 53.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 47.44 |  |  |  |  | 0.00
2019 |  |  |  | 8067.74 |  |  | 7091 |  |  |  | 1127 | [10 empty] | 80.41 |  |  |  | 80.41 | [5 empty] | 81.72 |  |  | 80.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.59 |  |  |  |  | 0.00
2020 |  |  |  | 9703.45 |  |  | 8473 |  |  |  | 1127 | [10 empty] | 96.42 |  |  |  | 96.42 | [5 empty] | 98.02 |  |  | 96.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.58 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1997 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 59
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 311 | [14 empty] | 914
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 2351
Subtotal | [22 empty] | 311 | [14 empty] | 3265 |  |  |  | 59
Total | [22 empty] | 311 | [14 empty] | 3324
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1997 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 30
41. |  |  | Main Generator Systems | [34 empty] | 19
Total | [37 empty] | 59

## HAMAOKA-3
2020 Operating Experience
JP-36 | [8 empty] | HAMAOKA-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CHUBU (CHUBU ELECTRIC POWER CO., INC.)
Owner | [7 empty] | : | CHUBU (CHUBU ELECTRIC POWER CO., INC.)
Reactor Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Turbine Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1983-04-18
Thermal power | [12 empty] | : |  |  | 3293 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-01-20
Gross electrical power | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-08-28
Reference unit power (net) | [12 empty] | : |  |  | 1056 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6.93
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.43
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.0 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 29500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 171104 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.8 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 54.73 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 54.82 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 40.02 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 54.39 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.09 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 55.07 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 5586.64 |  |  | 6360 |  |  |  | 1066 | [10 empty] | 99.37 |  |  |  | 99.37 | [5 empty] | 98.37 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.63 |  |  |  |  | 0.00
1988 |  |  |  | 7066.77 |  |  | 6862 |  |  |  | 1066 | [10 empty] | 75.79 |  |  |  | 75.79 | [5 empty] | 75.47 |  |  | 78.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.21 |  |  |  |  | 0.00
1989 |  |  |  | 8541.99 |  |  | 8167 |  |  |  | 1066 | [10 empty] | 92.38 |  |  |  | 92.38 | [5 empty] | 91.47 |  |  | 93.23 |  |  |  | 7.24 |  | 7.21 | [8 empty] | 0.41 |  |  |  |  | 0.00
1990 |  |  |  | 6601.27 |  |  | 6366 |  |  |  | 1056 | [10 empty] | 71.36 |  |  |  | 71.36 | [5 empty] | 71.36 |  |  | 72.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.64 |  |  |  |  | 0.00
1991 |  |  |  | 6763.14 |  |  | 6472 |  |  |  | 1056 | [10 empty] | 73.47 |  |  |  | 73.50 | [5 empty] | 73.11 |  |  | 73.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.50 |  |  |  |  | 0.03
1992 |  |  |  | 6585.40 |  |  | 6371 |  |  |  | 1056 | [10 empty] | 71.37 |  |  |  | 71.69 | [5 empty] | 70.99 |  |  | 72.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.31 |  |  |  |  | 0.32
1993 |  |  |  | 8767.99 |  |  | 8359 |  |  |  | 1056 | [10 empty] | 95.33 |  |  |  | 95.33 | [5 empty] | 94.78 |  |  | 95.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.67 |  |  |  |  | 0.00
1994 |  |  |  | 6490.47 |  |  | 6784 |  |  |  | 1056 | [10 empty] | 77.43 |  |  |  | 77.43 | [5 empty] | 70.16 |  |  | 77.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.57 |  |  |  |  | 0.00
1995 |  |  |  | 7725.72 |  |  | 7429 |  |  |  | 1056 | [10 empty] | 84.11 |  |  |  | 84.65 | [5 empty] | 83.52 |  |  | 84.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.35 |  |  |  |  | 0.53
1996 |  |  |  | 6891.56 |  |  | 6573 |  |  |  | 1056 | [10 empty] | 74.72 |  |  |  | 74.82 | [5 empty] | 74.30 |  |  | 74.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.18 |  |  |  |  | 0.09
1997 |  |  |  | 8109.71 |  |  | 7863 |  |  |  | 1056 | [10 empty] | 88.32 |  |  |  | 88.32 | [5 empty] | 87.67 |  |  | 89.76 |  |  |  | 1.32 |  | 1.19 | [8 empty] | 10.50 |  |  |  |  | 0.00
1998 |  |  |  | 9200.69 |  |  | 8760 |  |  |  | 1056 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.46 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 7618.28 |  |  | 7255 |  |  |  | 1056 | [10 empty] | 82.81 |  |  |  | 82.81 | [5 empty] | 82.35 |  |  | 82.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.19 |  |  |  |  | 0.00
2000 |  |  |  | 7705.98 |  |  | 7340 |  |  |  | 1056 | [10 empty] | 83.56 |  |  |  | 83.56 | [5 empty] | 83.08 |  |  | 83.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.44 |  |  |  |  | 0.00
2001 |  |  |  | 6476.81 |  |  | 6171 |  |  |  | 1056 | [10 empty] | 70.42 |  |  |  | 70.44 | [5 empty] | 70.02 |  |  | 70.45 |  |  |  | 1.91 |  | 1.37 | [8 empty] | 28.19 |  |  |  |  | 0.02
2002 |  |  |  | 6350.93 |  |  | 6044 |  |  |  | 1056 | [10 empty] | 68.99 |  |  |  | 68.99 | [5 empty] | 68.65 |  |  | 69.00 |  |  |  | 28.89 |  | 28.02 | [8 empty] | 2.99 |  |  |  |  | 0.00
2003 |  |  |  | 1486.62 |  |  | 1403 |  |  |  | 1056 | [10 empty] | 16.14 |  |  |  | 16.14 | [5 empty] | 16.07 |  |  | 16.02 |  |  |  | 45.91 |  | 50.41 | [8 empty] | 33.45 |  |  |  |  | 0.00
2004 |  |  |  | 9342.48 |  |  | 8784 |  |  |  | 1056 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.72 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 5793.39 |  |  | 5473 |  |  |  | 1056 | [10 empty] | 62.12 |  |  |  | 62.18 | [5 empty] | 62.63 |  |  | 62.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.82 |  |  |  |  | 0.05
2006 |  |  |  | 6396.90 |  |  | 6081 |  |  |  | 1056 | [10 empty] | 68.72 |  |  |  | 69.19 | [5 empty] | 69.15 |  |  | 69.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.81 |  |  |  |  | 0.47
2007 |  |  |  | 9196.54 |  |  | 8760 |  |  |  | 1056 | [10 empty] | 99.19 |  |  |  | 99.99 | [5 empty] | 99.42 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.80
2008 |  |  |  | 6882.87 |  |  | 6625 |  |  |  | 1056 | [10 empty] | 74.05 |  |  |  | 74.81 | [5 empty] | 74.20 |  |  | 75.42 |  |  |  | 1.48 |  | 1.12 | [8 empty] | 24.07 |  |  |  |  | 0.76
2009 |  |  |  | 6437.10 |  |  | 6085 |  |  |  | 1056 | [10 empty] | 69.22 |  |  |  | 69.22 | [5 empty] | 69.59 |  |  | 69.46 |  |  |  | 0.00 |  | 11.43 | [8 empty] | 19.35 |  |  |  |  | 0.00
2010 |  |  |  | 8434.81 |  |  | 7974 |  |  |  | 1056 | [10 empty] | 90.98 |  |  |  | 90.98 | [5 empty] | 91.18 |  |  | 91.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.02 |  |  |  |  | 0.00
2011 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1056 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 71.23 | [8 empty] | 28.77 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1056 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1056 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1056 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1056 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1056 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1056 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1056 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1056 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1056 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 137
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1085
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 21 |  |  |  | 4
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 2367
H. |  | Nuclear regulatory requirements | [39 empty] | 187
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [39 empty] | 30
Z. |  | Other | [39 empty] | 110
Subtotal | [22 empty] | 8784 | [14 empty] | 3473 |  |  |  | 468
Total | [22 empty] | 8784 | [14 empty] | 3941
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 115
15. |  |  | Reactor Cooling Systems | [34 empty] | 108
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 17
35. |  |  | All other I&C Systems | [34 empty] | 0
Total | [37 empty] | 242

## HAMAOKA-4
2020 Operating Experience
JP-49 | [8 empty] | HAMAOKA-4 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CHUBU (CHUBU ELECTRIC POWER CO., INC.)
Owner | [7 empty] | : | CHUBU (CHUBU ELECTRIC POWER CO., INC.)
Reactor Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Turbine Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1989-10-13
Thermal power | [12 empty] | : |  |  | 3293 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-01-27
Gross electrical power | [12 empty] | : |  |  | 1137 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-09-03
Reference unit power (net) | [12 empty] | : |  |  | 1092 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6.93
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.43
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.44 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 39500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 130349 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.98 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 51.66 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.78 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 52.09 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 44.12 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 51.65 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.43 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 52 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 5877.56 |  |  | 6326 |  |  |  | 1092 | [10 empty] | 99.93 |  |  |  | 99.93 | [5 empty] | 99.65 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.07 |  |  |  |  | 0.00
1994 |  |  |  | 7110.42 |  |  | 6576 |  |  |  | 1092 | [10 empty] | 74.66 |  |  |  | 74.90 | [5 empty] | 74.33 |  |  | 75.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.10 |  |  |  |  | 0.24
1995 |  |  |  | 9545.99 |  |  | 8760 |  |  |  | 1092 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.79 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 8301.28 |  |  | 7615 |  |  |  | 1092 | [10 empty] | 86.68 |  |  |  | 86.68 | [5 empty] | 86.54 |  |  | 86.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.32 |  |  |  |  | 0.00
1997 |  |  |  | 7882.99 |  |  | 7302 |  |  |  | 1092 | [10 empty] | 82.61 |  |  |  | 83.07 | [5 empty] | 82.41 |  |  | 83.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.93 |  |  |  |  | 0.46
1998 |  |  |  | 7154.09 |  |  | 6604 |  |  |  | 1092 | [10 empty] | 74.92 |  |  |  | 74.95 | [5 empty] | 74.79 |  |  | 75.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.05 |  |  |  |  | 0.03
1999 |  |  |  | 9545.08 |  |  | 8760 |  |  |  | 1092 | [10 empty] | 99.95 |  |  |  | 99.95 | [5 empty] | 99.78 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  |  |  | 0.00
2000 |  |  |  | 8233.65 |  |  | 7577 |  |  |  | 1092 | [10 empty] | 85.97 |  |  |  | 86.26 | [5 empty] | 85.84 |  |  | 86.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.74 |  |  |  |  | 0.29
2001 |  |  |  | 8773.52 |  |  | 8046 |  |  |  | 1092 | [10 empty] | 91.85 |  |  |  | 91.85 | [5 empty] | 91.72 |  |  | 91.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.15 |  |  |  |  | 0.00
2002 |  |  |  | 6436.42 |  |  | 5906 |  |  |  | 1092 | [10 empty] | 67.42 |  |  |  | 67.42 | [5 empty] | 67.28 |  |  | 67.42 |  |  |  | 0.00 |  | 12.05 | [8 empty] | 20.53 |  |  |  |  | 0.00
2003 |  |  |  | 3729.78 |  |  | 3415 |  |  |  | 1092 | [10 empty] | 39.09 |  |  |  | 39.11 | [5 empty] | 38.99 |  |  | 38.98 |  |  |  | 0.00 |  | 58.07 | [8 empty] | 2.82 |  |  |  |  | 0.02
2004 |  |  |  | 7279.71 |  |  | 6668 |  |  |  | 1092 | [10 empty] | 75.76 |  |  |  | 75.79 | [5 empty] | 75.89 |  |  | 75.91 |  |  |  | 0.00 |  | 0.02 | [8 empty] | 24.19 |  |  |  |  | 0.03
2005 |  |  |  | 9595.62 |  |  | 8760 |  |  |  | 1092 | [10 empty] | 99.99 |  |  |  | 100.00 | [5 empty] | 100.31 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.01
2006 |  |  |  | 6523.51 |  |  | 6423 |  |  |  | 1092 | [10 empty] | 68.23 |  |  |  | 68.24 | [5 empty] | 68.20 |  |  | 73.32 |  |  |  | 6.58 |  | 4.80 | [8 empty] | 26.95 |  |  |  |  | 0.01
2007 |  |  |  | 7720.91 |  |  | 7098 |  |  |  | 1092 | [10 empty] | 80.45 |  |  |  | 80.65 | [5 empty] | 80.71 |  |  | 81.03 |  |  |  | 0.52 |  | 4.96 | [8 empty] | 14.39 |  |  |  |  | 0.19
2008 |  |  |  | 9293.57 |  |  | 8512 |  |  |  | 1092 | [10 empty] | 96.47 |  |  |  | 96.48 | [5 empty] | 96.89 |  |  | 96.90 |  |  |  | 3.52 |  | 3.52 | [8 empty] | 0.01 |  |  |  |  | 0.01
2009 |  |  |  | 4847.54 |  |  | 4480 |  |  |  | 1092 | [10 empty] | 50.48 |  |  |  | 60.89 | [5 empty] | 50.68 |  |  | 51.14 |  |  |  | 24.79 |  | 20.08 | [8 empty] | 19.03 |  |  |  |  | 10.41
2010 |  |  |  | 7512.95 |  |  | 6870 |  |  |  | 1092 | [10 empty] | 78.33 |  |  |  | 78.38 | [5 empty] | 78.54 |  |  | 78.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.62 |  |  |  |  | 0.05
2011 |  |  |  | 2486.88 |  |  | 2297 |  |  |  | 1092 | [10 empty] | 26.00 |  |  |  | 26.00 | [5 empty] | 26.00 |  |  | 26.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 74.00 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1092 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1092 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1092 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1092 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1092 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1092 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1092 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1092 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1092 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1993 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 284
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 753
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 22
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 3129
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 33
Z. |  | Other | [39 empty] | 39
Subtotal | [22 empty] | 8784 | [14 empty] | 3904 |  |  |  | 323 | [11 empty] | 33
Total | [22 empty] | 8784 | [14 empty] | 4260
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1993 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 233
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 15
31. |  |  | Turbine and auxiliaries | [34 empty] | 65
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
Total | [37 empty] | 323

## HAMAOKA-5
2020 Operating Experience
JP-60 | [8 empty] | HAMAOKA-5 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CHUBU (CHUBU ELECTRIC POWER CO., INC.)
Owner | [7 empty] | : | CHUBU (CHUBU ELECTRIC POWER CO., INC.)
Reactor Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Turbine Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / ABWR | [11 empty] | Construction Date | [15 empty] | : |  |  | 2000-07-12
Thermal power | [12 empty] | : |  |  | 3926 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2004-04-30
Gross electrical power | [12 empty] | : |  |  | 1380 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2005-01-18
Reference unit power (net) | [12 empty] | : |  |  | 1325 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 16 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.7 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 5.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.69
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 872 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 205 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 38950 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 24.69 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 18.37 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.74 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 21.88 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 66.38 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 18.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.51 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 18.92 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2005 |  |  |  | 11870.42 |  |  | 8760 |  |  |  | 1325 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.23 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 3385.19 |  |  | 2515 |  |  |  | 1325 | [10 empty] | 28.51 |  |  |  | 28.51 | [5 empty] | 29.17 |  |  | 28.71 |  |  |  | 65.74 |  | 54.69 | [8 empty] | 16.81 |  |  |  |  | 0.00
2007 |  |  |  | 7652.74 |  |  | 6159 |  |  |  | 1212 | [10 empty] | 68.64 |  |  |  | 68.83 | [5 empty] | 71.01 |  |  | 70.31 |  |  |  | 16.47 |  | 13.58 | [8 empty] | 17.60 |  |  |  |  | 0.18
2008 |  |  |  | 7516.25 |  |  | 6075 |  |  |  | 1212 | [10 empty] | 68.33 |  |  |  | 68.80 | [5 empty] | 70.60 |  |  | 69.16 |  |  |  | 0.00 |  | 15.32 | [8 empty] | 15.89 |  |  |  |  | 0.47
2009 |  |  |  | 1338.27 |  |  | 1076 |  |  |  | 1212 | [10 empty] | 12.17 |  |  |  | 51.29 | [5 empty] | 12.60 |  |  | 12.28 |  |  |  | 48.71 |  | 48.70 | [8 empty] | 0.00 |  |  |  |  | 39.12
2010 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1212 | [10 empty] | 0.00 |  |  |  | 20.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 62.47 | [8 empty] | 17.53 |  |  |  |  | 20.00
2011 |  |  |  | 3353.43 |  |  | 2557 |  |  |  | 1325 | [10 empty] | 29.11 |  |  |  | 29.11 | [5 empty] | 29.10 |  |  | 29.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 70.89 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1325 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1325 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1325 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1325 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1325 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1325 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1325 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1325 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1325 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2005 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 763
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 293
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 146
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 5631
H. |  | Nuclear regulatory requirements | [39 empty] | 365
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 345
Subtotal | [22 empty] | 8784 | [14 empty] | 6070 |  |  |  | 1128 | [11 empty] | 345
Total | [22 empty] | 8784 | [14 empty] | 7543
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2005 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 763
Total | [37 empty] | 763

## HIGASHI DORI-1 (TOHOKU)
2020 Operating Experience
JP-58 | [7 empty] | HIGASHI DORI-1 (TOHOKU) | [26 empty] | JAPAN
Status at end of year | [6 empty] | : | Operational
Operator | [6 empty] | : | TOHOKU (Tohoku Electric Power Co., Inc)
Owner | [6 empty] | : | TOHOKU (Tohoku Electric Power Co., Inc)
Reactor Supplier | [6 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Turbine Supplier | [6 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Reactor Unit Details | [26 empty] | Key Dates
Reactor type and model | [11 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2000-11-07
Thermal power | [11 empty] | : |  |  | 3293 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2005-03-09
Gross electrical power | [11 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2005-12-08
Reference unit power (net) | [11 empty] | : |  |  | 1067 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 15 years
Design Characteristics
| Primary Systems | [27 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6.93
| Reactor vessel centreline orientation | [12 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [12 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [12 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [12 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.43
| Average fuel enrichment [% of U235] | [12 empty] | : |  |  | 3.7 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [12 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [12 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [12 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [12 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [12 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 19
| Number of fissile fuel assemblies/bundles | [12 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [12 empty] | : |  |  | 15.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [12 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [12 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [12 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [17 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [17 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [17 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [17 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [17 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
|  |  |  | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [12 empty] | : |  |  | 41897 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [12 empty] | : |  |  | 28.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.59 %
Cumulative Unit Capability Factor (UCF) | [12 empty] | : |  |  | 28.35 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 71.05 %
Cumulative Load Factor (LF) | [12 empty] | : |  |  | 28.05 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [12 empty] | : |  |  | 28.31 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2005 |  |  | 2749.61 |  |  | 3536 |  |  |  | 1067 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 76.90 |  |  | 77.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  | 9269.32 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 99.74 |  |  |  | 100.00 | [5 empty] | 99.17 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.26
2007 |  |  | 6150.83 |  |  | 5827 |  |  |  | 1067 | [10 empty] | 66.18 |  |  |  | 66.18 | [5 empty] | 65.81 |  |  | 66.52 |  |  |  | 0.00 |  | 8.93 | [8 empty] | 24.90 |  |  |  |  | 0.00
2008 |  |  | 6274.76 |  |  | 5947 |  |  |  | 1067 | [10 empty] | 67.31 |  |  |  | 67.31 | [5 empty] | 66.95 |  |  | 67.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.69 |  |  |  |  | 0.00
2009 |  |  | 7064.53 |  |  | 6696 |  |  |  | 1067 | [10 empty] | 76.03 |  |  |  | 76.07 | [5 empty] | 75.58 |  |  | 76.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.93 |  |  |  |  | 0.03
2010 |  |  | 9298.98 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.49 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  | 911.00 |  |  | 865 |  |  |  | 1067 | [10 empty] | 9.81 |  |  |  | 9.81 | [5 empty] | 9.75 |  |  | 9.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 90.19 |  |  |  |  | 0.00
2012 |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[22 empty] | 2020 | [14 empty] | 2005 to 2020
Outage Cause | [21 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[22 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [34 empty] | 649 |  |  |  | 52
D. |  | Inspection, maintenance or repair without refuelling | [34 empty] | 99
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [19 empty] | 8784 | [14 empty] | 5510
Subtotal | [21 empty] | 8784 | [14 empty] | 6258 |  |  |  | 52
Total | [21 empty] | 8784 | [14 empty] | 6310
Equipment Related Unplanned Full Outages, Analysis by System
System | [21 empty] | 2020 | [14 empty] | 2005 to 2020
[22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
Total
Highlights (2020)
Implementation of safety measure for considering the new regulatory requirements.

## IKATA-3
2020 Operating Experience
JP-47 | [8 empty] | IKATA-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SHIKOKU (SHIKOKU ELECTRIC POWER CO., INC)
Owner | [7 empty] | : | SHIKOKU (SHIKOKU ELECTRIC POWER CO., INC)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1990-10-01
Thermal power | [12 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1994-03-29
Gross electrical power | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-12-15
Reference unit power (net) | [12 empty] | : |  |  | 846 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 26 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.283
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 48000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.1
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 3.57 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 125606 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.78 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 66.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.76 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 66.3 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 32.95 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.08 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 63.33 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 2195.52 |  |  | 3669 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.17 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 7491.81 |  |  | 8760 |  |  |  | 846 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 101.09 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1996 |  |  |  | 5578.21 |  |  | 6621 |  |  |  | 846 | [10 empty] | 74.23 |  |  |  | 74.23 | [5 empty] | 75.06 |  |  | 75.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.76 |  |  |  |  | 0.00
1997 |  |  |  | 6134.74 |  |  | 7242 |  |  |  | 846 | [10 empty] | 81.87 |  |  |  | 81.87 | [5 empty] | 82.78 |  |  | 82.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.13 |  |  |  |  | 0.00
1998 |  |  |  | 6250.38 |  |  | 7374 |  |  |  | 846 | [10 empty] | 83.43 |  |  |  | 83.43 | [5 empty] | 84.34 |  |  | 84.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.57 |  |  |  |  | 0.00
1999 |  |  |  | 6298.35 |  |  | 7368 |  |  |  | 846 | [10 empty] | 84.09 |  |  |  | 84.09 | [5 empty] | 84.99 |  |  | 84.11 |  |  |  | 3.16 |  | 2.74 | [8 empty] | 13.17 |  |  |  |  | 0.00
2000 |  |  |  | 6660.35 |  |  | 7790 |  |  |  | 846 | [10 empty] | 88.68 |  |  |  | 88.68 | [5 empty] | 89.63 |  |  | 88.68 |  |  |  | 10.78 |  | 10.71 | [8 empty] | 0.61 |  |  |  |  | 0.00
2001 |  |  |  | 6210.74 |  |  | 7267 |  |  |  | 846 | [10 empty] | 82.94 |  |  |  | 82.94 | [5 empty] | 83.80 |  |  | 82.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.06 |  |  |  |  | 0.00
2002 |  |  |  | 6599.51 |  |  | 7518 |  |  |  | 846 | [10 empty] | 85.82 |  |  |  | 85.82 | [5 empty] | 89.05 |  |  | 85.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.18 |  |  |  |  | 0.00
2003 |  |  |  | 5862.10 |  |  | 6560 |  |  |  | 846 | [10 empty] | 74.86 |  |  |  | 74.86 | [5 empty] | 79.10 |  |  | 74.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.14 |  |  |  |  | 0.00
2004 |  |  |  | 7828.92 |  |  | 8784 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.35 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 6699.37 |  |  | 7637 |  |  |  | 846 | [10 empty] | 86.84 |  |  |  | 86.84 | [5 empty] | 90.40 |  |  | 87.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.16 |  |  |  |  | 0.00
2006 |  |  |  | 6134.56 |  |  | 6990 |  |  |  | 846 | [10 empty] | 79.53 |  |  |  | 79.53 | [5 empty] | 82.78 |  |  | 79.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.47 |  |  |  |  | 0.00
2007 |  |  |  | 6869.33 |  |  | 7813 |  |  |  | 846 | [10 empty] | 88.88 |  |  |  | 88.88 | [5 empty] | 92.69 |  |  | 89.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.12 |  |  |  |  | 0.00
2008 |  |  |  | 6392.97 |  |  | 7282 |  |  |  | 846 | [10 empty] | 82.57 |  |  |  | 82.57 | [5 empty] | 86.03 |  |  | 82.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.43 |  |  |  |  | 0.00
2009 |  |  |  | 7716.65 |  |  | 8760 |  |  |  | 846 | [10 empty] | 99.96 |  |  |  | 99.96 | [5 empty] | 104.12 |  |  | 100.00 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 6490.71 |  |  | 7410 |  |  |  | 846 | [10 empty] | 84.34 |  |  |  | 84.34 | [5 empty] | 87.58 |  |  | 84.59 |  |  |  | 0.00 |  | 1.71 | [8 empty] | 13.95 |  |  |  |  | 0.00
2011 |  |  |  | 2511.01 |  |  | 2852 |  |  |  | 846 | [10 empty] | 32.58 |  |  |  | 32.58 | [5 empty] | 33.88 |  |  | 32.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 67.42 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.06 |  |  |  | 0.06 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 99.94 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 2848.03 |  |  | 3322 |  |  |  | 846 | [10 empty] | 37.02 |  |  |  | 37.02 | [5 empty] | 38.32 |  |  | 37.82 |  |  |  | 0.00 |  | 4.53 | [8 empty] | 58.45 |  |  |  |  | 0.00
2017 |  |  |  | 5802.18 |  |  | 6600 |  |  |  | 846 | [10 empty] | 75.32 |  |  |  | 75.32 | [5 empty] | 78.29 |  |  | 75.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.68 |  |  |  |  | 0.00
2018 |  |  |  | 1306.34 |  |  | 1511 |  |  |  | 846 | [10 empty] | 99.72 |  |  |  | 99.72 | [5 empty] | 17.63 |  |  | 17.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.28 |  |  |  |  | 0.00
2019 |  |  |  | 7570.95 |  |  | 8616 |  |  |  | 846 | [10 empty] | 98.34 |  |  |  | 98.34 | [5 empty] | 102.16 |  |  | 98.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.66 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1994 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 47
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 8784 | [14 empty] | 1212
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 1786
M. |  | Governmental requirements or court decisions | [51 empty] | 290
Z. |  | Other | [39 empty] | 22
Subtotal | [22 empty] | 8784 | [14 empty] | 2998 |  |  |  | 69 | [11 empty] | 290
Total | [22 empty] | 8784 | [14 empty] | 3357
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1994 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 16
41. |  |  | Main Generator Systems | [34 empty] | 10
42. |  |  | Electrical Power Supply Systems | [34 empty] | 38
Total | [37 empty] | 64
Highlights (2020)
Prolonged periodical inspection and refueling due to the court decision.

## KASHIWAZAKI KARIWA-1
KA
2020 Operating Experience
| JP-33 | [8 empty] | KASHIWAZAKI KARIWA-1 | [26 empty] | JAPAN
| Status at end of year | [7 empty] | : | Operational
| Operator | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
| Owner | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
| Reactor Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
| Turbine Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
| Reactor Unit Details | [27 empty] | Key Dates
| Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-06-05
| Thermal power | [12 empty] | : |  |  | 3293 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-02-13
| Gross electrical power | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-09-18
| Reference unit power (net) | [12 empty] | : |  |  | 1067 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
|  | Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
|  | Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
|  | Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
|  | Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
|  | Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.28
|  | Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.70 | [11 empty] | Secondary systems
|  | Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
|  | Part of the core refuelled [%] | [13 empty] | : |  |  | 24 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
|  | Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
|  | Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
|  | Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 19
|  | Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
|  | Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
|  | Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
|  | Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
|  | Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
| Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
| Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
| Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
| Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
| Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[6 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
| GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
| EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
| UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
| LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
| OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
| FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
| UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
| PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
| XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
| Lifetime energy generation | [13 empty] | : |  |  | 160133 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.09 %
| Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 48.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.56 %
| Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 49.11 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 47.33 %
| Cumulative Load Factor (LF) | [13 empty] | : |  |  | 47.77 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.82 %
| Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 48.6 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
| Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
[5 empty] | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
| 1985 |  |  |  | 4960.19 |  |  | 5793 |  |  |  | 1067 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.80 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
| 1986 |  |  |  | 6703.73 |  |  | 6463 |  |  |  | 1067 | [10 empty] | 73.03 |  |  |  | 73.03 | [5 empty] | 71.72 |  |  | 73.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.97 |  |  |  |  | 0.00
| 1987 |  |  |  | 9195.47 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.38 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
| 1988 |  |  |  | 6959.75 |  |  | 6660 |  |  |  | 1067 | [10 empty] | 75.04 |  |  |  | 75.04 | [5 empty] | 74.26 |  |  | 75.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.96 |  |  |  |  | 0.00
| 1989 |  |  |  | 6442.33 |  |  | 6236 |  |  |  | 1067 | [10 empty] | 69.67 |  |  |  | 69.67 | [5 empty] | 68.92 |  |  | 71.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.33 |  |  |  |  | 0.00
| 1990 |  |  |  | 5987.40 |  |  | 5711 |  |  |  | 1067 | [10 empty] | 64.97 |  |  |  | 64.97 | [5 empty] | 64.06 |  |  | 65.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 35.03 |  |  |  |  | 0.00
| 1991 |  |  |  | 9031.56 |  |  | 8618 |  |  |  | 1067 | [10 empty] | 97.86 |  |  |  | 97.86 | [5 empty] | 96.63 |  |  | 98.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.14 |  |  |  |  | 0.00
| 1992 |  |  |  | 6958.10 |  |  | 6728 |  |  |  | 1067 | [10 empty] | 75.37 |  |  |  | 75.84 | [5 empty] | 74.24 |  |  | 76.59 |  |  |  | 2.17 |  | 1.68 | [8 empty] | 22.48 |  |  |  |  | 0.47
| 1993 |  |  |  | 6874.29 |  |  | 6575 |  |  |  | 1067 | [10 empty] | 74.74 |  |  |  | 74.74 | [5 empty] | 73.55 |  |  | 75.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.26 |  |  |  |  | 0.00
| 1994 |  |  |  | 7020.25 |  |  | 6744 |  |  |  | 1067 | [10 empty] | 76.11 |  |  |  | 76.11 | [5 empty] | 75.11 |  |  | 76.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.89 |  |  |  |  | 0.00
| 1995 |  |  |  | 9235.21 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 98.80 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
| 1996 |  |  |  | 6814.36 |  |  | 6469 |  |  |  | 1067 | [10 empty] | 73.64 |  |  |  | 73.64 | [5 empty] | 72.71 |  |  | 73.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.36 |  |  |  |  | 0.00
| 1997 |  |  |  | 7899.88 |  |  | 7525 |  |  |  | 1067 | [10 empty] | 85.68 |  |  |  | 85.68 | [5 empty] | 84.52 |  |  | 85.90 |  |  |  | 0.25 |  | 0.22 | [8 empty] | 14.10 |  |  |  |  | 0.00
| 1998 |  |  |  | 6176.21 |  |  | 5960 |  |  |  | 1067 | [10 empty] | 67.36 |  |  |  | 67.36 | [5 empty] | 66.08 |  |  | 68.04 |  |  |  | 14.53 |  | 11.46 | [8 empty] | 21.18 |  |  |  |  | 0.00
| 1999 |  |  |  | 9198.85 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 99.68 |  |  |  | 99.75 | [5 empty] | 98.42 |  |  | 100.00 |  |  |  | 0.25 |  | 0.25 | [8 empty] | 0.00 |  |  |  |  | 0.06
| 2000 |  |  |  | 7714.74 |  |  | 7346 |  |  |  | 1067 | [10 empty] | 83.62 |  |  |  | 83.63 | [5 empty] | 82.31 |  |  | 83.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.37 |  |  |  |  | 0.00
| 2001 |  |  |  | 7070.55 |  |  | 6743 |  |  |  | 1067 | [10 empty] | 76.91 |  |  |  | 76.92 | [5 empty] | 75.65 |  |  | 76.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.08 |  |  |  |  | 0.01
| 2002 |  |  |  | 5906.21 |  |  | 5628 |  |  |  | 1067 | [10 empty] | 64.23 |  |  |  | 64.23 | [5 empty] | 63.19 |  |  | 64.25 |  |  |  | 11.79 |  | 22.56 | [8 empty] | 13.21 |  |  |  |  | 0.00
| 2003 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 52.07 | [8 empty] | 47.93 |  |  |  |  | 0.00
| 2004 |  |  |  | 6496.73 |  |  | 6171 |  |  |  | 1067 | [10 empty] | 69.21 |  |  |  | 69.21 | [5 empty] | 69.32 |  |  | 70.25 |  |  |  | 4.89 |  | 18.05 | [8 empty] | 12.74 |  |  |  |  | 0.00
| 2005 |  |  |  | 3125.94 |  |  | 3051 |  |  |  | 1067 | [10 empty] | 33.53 |  |  |  | 33.53 | [5 empty] | 33.44 |  |  | 34.83 |  |  |  | 25.16 |  | 11.27 | [8 empty] | 55.20 |  |  |  |  | 0.00
| 2006 |  |  |  | 6299.43 |  |  | 5899 |  |  |  | 1067 | [10 empty] | 67.07 |  |  |  | 67.07 | [5 empty] | 67.40 |  |  | 67.34 |  |  |  | 0.00 |  | 8.11 | [8 empty] | 24.82 |  |  |  |  | 0.00
| 2007 |  |  |  | 3165.81 |  |  | 2952 |  |  |  | 1067 | [10 empty] | 33.64 |  |  |  | 62.14 | [5 empty] | 33.87 |  |  | 33.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.86 |  |  |  |  | 28.49
| 2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
| 2009 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
| 2010 |  |  |  | 5290.82 |  |  | 5022 |  |  |  | 1067 | [10 empty] | 56.31 |  |  |  | 56.31 | [5 empty] | 56.60 |  |  | 57.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 43.69 |  |  |  |  | 0.00
| 2011 |  |  |  | 5605.55 |  |  | 5208 |  |  |  | 1067 | [10 empty] | 59.38 |  |  |  | 59.38 | [5 empty] | 59.97 |  |  | 59.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 40.62 |  |  |  |  | 0.00
| 2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
| 2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
| 2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
| 2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
| 2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
| 2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
| 2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
| 2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
| 2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[24 empty] | 2020 | [14 empty] | 1985 to 2020
| Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[24 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
| A. |  | Plant equipment problem/failure | [39 empty] | 257
| C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1215
| D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 25
| G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 2924
| N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 71
| Z. |  | Other | [39 empty] | 52
| Subtotal | [22 empty] | 8784 | [14 empty] | 4164 |  |  |  | 309 | [11 empty] | 71
| Total | [22 empty] | 8784 | [14 empty] | 4544
Equipment Related Unplanned Full Outages, Analysis by System
| System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[24 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
| 11. |  |  | Reactor and Accessories | [34 empty] | 77
| 12. |  |  | Reactor I&C Systems | [34 empty] | 130
| 15. |  |  | Reactor Cooling Systems | [34 empty] | 31
| 32. |  |  | Feedwater and Main Steam System | [34 empty] | 27
| 41. |  |  | Main Generator Systems | [34 empty] | 6
| Total | [37 empty] | 271
Highlights (2020)
Implementation of emergency safety measures for considering the Accident of Fukushima Dai-ichi Nuclear Power Stations.

## KASHIWAZAKI KARIWA-2
2020 Operating Experience
JP-39 | [8 empty] | KASHIWAZAKI KARIWA-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Owner | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Reactor Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Turbine Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-11-18
Thermal power | [12 empty] | : |  |  | 3293 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-02-08
Gross electrical power | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-09-28
Reference unit power (net) | [12 empty] | : |  |  | 1067 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.70 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 24 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 19
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 120879 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.48 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 41.64 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.62 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 41.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 53.73 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 41.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 41.79 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 5386.27 |  |  | 6071 |  |  |  | 1067 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.64 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 6642.43 |  |  | 6440 |  |  |  | 1067 | [10 empty] | 72.39 |  |  |  | 72.39 | [5 empty] | 71.07 |  |  | 73.52 |  |  |  | 3.01 |  | 2.24 | [8 empty] | 25.37 |  |  |  |  | 0.00
1992 |  |  |  | 9046.85 |  |  | 8623 |  |  |  | 1067 | [10 empty] | 97.93 |  |  |  | 97.94 | [5 empty] | 96.53 |  |  | 98.17 |  |  |  | 2.00 |  | 2.00 | [8 empty] | 0.06 |  |  |  |  | 0.01
1993 |  |  |  | 7212.57 |  |  | 6911 |  |  |  | 1067 | [10 empty] | 78.27 |  |  |  | 78.48 | [5 empty] | 77.17 |  |  | 78.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.52 |  |  |  |  | 0.21
1994 |  |  |  | 7291.14 |  |  | 6962 |  |  |  | 1067 | [10 empty] | 79.05 |  |  |  | 79.05 | [5 empty] | 78.01 |  |  | 79.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.95 |  |  |  |  | 0.00
1995 |  |  |  | 7696.75 |  |  | 7329 |  |  |  | 1067 | [10 empty] | 83.43 |  |  |  | 83.43 | [5 empty] | 82.35 |  |  | 83.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.57 |  |  |  |  | 0.00
1996 |  |  |  | 8811.08 |  |  | 8396 |  |  |  | 1067 | [10 empty] | 95.24 |  |  |  | 95.25 | [5 empty] | 94.01 |  |  | 95.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.75 |  |  |  |  | 0.01
1997 |  |  |  | 7284.36 |  |  | 6913 |  |  |  | 1067 | [10 empty] | 79.08 |  |  |  | 79.08 | [5 empty] | 77.93 |  |  | 78.92 |  |  |  | 2.76 |  | 2.24 | [8 empty] | 18.68 |  |  |  |  | 0.00
1998 |  |  |  | 8142.05 |  |  | 7769 |  |  |  | 1067 | [10 empty] | 88.43 |  |  |  | 88.43 | [5 empty] | 87.11 |  |  | 88.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.57 |  |  |  |  | 0.00
1999 |  |  |  | 8208.83 |  |  | 7814 |  |  |  | 1067 | [10 empty] | 89.15 |  |  |  | 89.20 | [5 empty] | 87.82 |  |  | 89.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.80 |  |  |  |  | 0.05
2000 |  |  |  | 8140.00 |  |  | 7760 |  |  |  | 1067 | [10 empty] | 88.25 |  |  |  | 88.27 | [5 empty] | 86.85 |  |  | 88.34 |  |  |  | 3.73 |  | 3.42 | [8 empty] | 8.30 |  |  |  |  | 0.02
2001 |  |  |  | 7595.48 |  |  | 7223 |  |  |  | 1067 | [10 empty] | 82.45 |  |  |  | 82.45 | [5 empty] | 81.26 |  |  | 82.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.55 |  |  |  |  | 0.00
2002 |  |  |  | 5866.21 |  |  | 5532 |  |  |  | 1067 | [10 empty] | 63.12 |  |  |  | 63.12 | [5 empty] | 62.76 |  |  | 63.15 |  |  |  | 30.77 |  | 28.05 | [8 empty] | 8.82 |  |  |  |  | 0.00
2003 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 38.09 | [8 empty] | 61.91 |  |  |  |  | 0.00
2004 |  |  |  | 4660.28 |  |  | 4361 |  |  |  | 1067 | [10 empty] | 49.63 |  |  |  | 49.63 | [5 empty] | 49.72 |  |  | 49.65 |  |  |  | 0.00 |  | 13.94 | [8 empty] | 36.42 |  |  |  |  | 0.00
2005 |  |  |  | 6388.39 |  |  | 6035 |  |  |  | 1067 | [10 empty] | 68.41 |  |  |  | 68.42 | [5 empty] | 68.35 |  |  | 68.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.58 |  |  |  |  | 0.01
2006 |  |  |  | 9330.75 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 99.81 |  |  |  | 99.81 | [5 empty] | 99.83 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.18 |  |  |  |  | 0.00
2007 |  |  |  | 1830.29 |  |  | 1786 |  |  |  | 1067 | [10 empty] | 19.78 |  |  |  | 19.78 | [5 empty] | 19.58 |  |  | 20.39 |  |  |  | 71.38 |  | 49.93 | [8 empty] | 30.29 |  |  |  |  | 0.00
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2009 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2010 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2011 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1990 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 364
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 936
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 8
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 3799
L. |  | Human factor related | [39 empty] | 6
Z. |  | Other | [39 empty] | 42
Subtotal | [22 empty] | 8784 | [14 empty] | 4743 |  |  |  | 412
Total | [22 empty] | 8784 | [14 empty] | 5155
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1990 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 2
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 193
31. |  |  | Turbine and auxiliaries | [34 empty] | 167
Total | [37 empty] | 369
Highlights (2020)
Implementation of emergency safety measures for considering the Accident of Fukushima Dai-ichi Nuclear Power Stations.

## KASHIWAZAKI KARIWA-3
2020 Operating Experience
JP-52 | [8 empty] | KASHIWAZAKI KARIWA-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Owner | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Reactor Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Turbine Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1989-03-07
Thermal power | [12 empty] | : |  |  | 3293 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1992-12-08
Gross electrical power | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-08-11
Reference unit power (net) | [12 empty] | : |  |  | 1067 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 28 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.68 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 24 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 19
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 100277 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.53 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 38.39 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.99 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 39.04 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 56.97 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 38.06 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.65 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 38.49 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 6488.42 |  |  | 6755 |  |  |  | 1067 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.92 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 7264.43 |  |  | 6961 |  |  |  | 1067 | [10 empty] | 78.92 |  |  |  | 78.92 | [5 empty] | 77.72 |  |  | 79.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.08 |  |  |  |  | 0.00
1995 |  |  |  | 9253.86 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.00 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 7921.58 |  |  | 7508 |  |  |  | 1067 | [10 empty] | 85.47 |  |  |  | 85.47 | [5 empty] | 84.52 |  |  | 85.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.53 |  |  |  |  | 0.00
1997 |  |  |  | 8016.22 |  |  | 7601 |  |  |  | 1067 | [10 empty] | 86.76 |  |  |  | 86.76 | [5 empty] | 85.76 |  |  | 86.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.24 |  |  |  |  | 0.00
1998 |  |  |  | 6748.02 |  |  | 6467 |  |  |  | 1067 | [10 empty] | 73.09 |  |  |  | 73.09 | [5 empty] | 72.20 |  |  | 73.82 |  |  |  | 3.78 |  | 2.87 | [8 empty] | 24.03 |  |  |  |  | 0.00
1999 |  |  |  | 9028.26 |  |  | 8568 |  |  |  | 1067 | [10 empty] | 97.68 |  |  |  | 97.75 | [5 empty] | 96.59 |  |  | 97.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.25 |  |  |  |  | 0.07
2000 |  |  |  | 7945.09 |  |  | 7539 |  |  |  | 1067 | [10 empty] | 85.82 |  |  |  | 85.82 | [5 empty] | 84.77 |  |  | 85.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.18 |  |  |  |  | 0.00
2001 |  |  |  | 6985.69 |  |  | 6639 |  |  |  | 1067 | [10 empty] | 75.76 |  |  |  | 75.77 | [5 empty] | 74.74 |  |  | 75.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.23 |  |  |  |  | 0.00
2002 |  |  |  | 5575.54 |  |  | 5300 |  |  |  | 1067 | [10 empty] | 60.35 |  |  |  | 60.35 | [5 empty] | 59.65 |  |  | 60.50 |  |  |  | 0.21 |  | 26.98 | [8 empty] | 12.67 |  |  |  |  | 0.00
2003 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 62.48 | [8 empty] | 37.52 |  |  |  |  | 0.00
2004 |  |  |  | 6549.98 |  |  | 6093 |  |  |  | 1067 | [10 empty] | 69.94 |  |  |  | 69.94 | [5 empty] | 69.88 |  |  | 69.36 |  |  |  | 0.00 |  | 13.83 | [8 empty] | 16.23 |  |  |  |  | 0.00
2005 |  |  |  | 6061.72 |  |  | 5772 |  |  |  | 1067 | [10 empty] | 64.94 |  |  |  | 64.94 | [5 empty] | 64.85 |  |  | 65.89 |  |  |  | 3.99 |  | 3.23 | [8 empty] | 31.83 |  |  |  |  | 0.00
2006 |  |  |  | 7331.42 |  |  | 6924 |  |  |  | 1067 | [10 empty] | 78.33 |  |  |  | 78.33 | [5 empty] | 78.44 |  |  | 79.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.67 |  |  |  |  | 0.00
2007 |  |  |  | 5054.10 |  |  | 4714 |  |  |  | 1067 | [10 empty] | 53.73 |  |  |  | 71.43 | [5 empty] | 54.07 |  |  | 53.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.57 |  |  |  |  | 17.69
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2009 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2010 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2011 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1993 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 310
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 842
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 4221
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 57
Z. |  | Other | [39 empty] | 52
Subtotal | [22 empty] | 8784 | [14 empty] | 5063 |  |  |  | 362 | [11 empty] | 57
Total | [22 empty] | 8784 | [14 empty] | 5482
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1993 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 290
15. |  |  | Reactor Cooling Systems | [34 empty] | 21
Total | [37 empty] | 311
Highlights (2020)
Implementation of emergency safety measures for considering the Accident of Fukushima Dai-ichi Nuclear Power Stations.

## KASHIWAZAKI KARIWA-4
2020 Operating Experience
JP-53 | [8 empty] | KASHIWAZAKI KARIWA-4 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Owner | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Reactor Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Turbine Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1990-03-05
Thermal power | [12 empty] | : |  |  | 3293 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-12-21
Gross electrical power | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-08-11
Reference unit power (net) | [12 empty] | : |  |  | 1067 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.70 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 24 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 19
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 91851 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.24 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 36.6 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.02 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 38.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 58.6 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 36.29 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.78 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 36.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 6040.10 |  |  | 6638 |  |  |  | 1067 | [10 empty] | 99.76 |  |  |  | 99.76 | [5 empty] | 98.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.24 |  |  |  |  | 0.00
1995 |  |  |  | 6182.46 |  |  | 5889 |  |  |  | 1067 | [10 empty] | 66.99 |  |  |  | 66.99 | [5 empty] | 66.14 |  |  | 67.23 |  |  |  | 12.76 |  | 9.80 | [8 empty] | 23.22 |  |  |  |  | 0.00
1996 |  |  |  | 8067.98 |  |  | 7651 |  |  |  | 1067 | [10 empty] | 87.05 |  |  |  | 87.05 | [5 empty] | 86.08 |  |  | 87.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.95 |  |  |  |  | 0.00
1997 |  |  |  | 7516.71 |  |  | 7207 |  |  |  | 1067 | [10 empty] | 81.53 |  |  |  | 81.67 | [5 empty] | 80.42 |  |  | 82.27 |  |  |  | 7.22 |  | 6.36 | [8 empty] | 11.98 |  |  |  |  | 0.14
1998 |  |  |  | 9258.69 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 99.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1999 |  |  |  | 8141.74 |  |  | 7719 |  |  |  | 1067 | [10 empty] | 88.09 |  |  |  | 88.09 | [5 empty] | 87.11 |  |  | 88.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.91 |  |  |  |  | 0.00
2000 |  |  |  | 6918.93 |  |  | 6602 |  |  |  | 1067 | [10 empty] | 75.13 |  |  |  | 75.14 | [5 empty] | 73.82 |  |  | 75.16 |  |  |  | 14.59 |  | 12.83 | [8 empty] | 12.02 |  |  |  |  | 0.02
2001 |  |  |  | 5591.43 |  |  | 5343 |  |  |  | 1067 | [10 empty] | 60.60 |  |  |  | 60.60 | [5 empty] | 59.82 |  |  | 60.99 |  |  |  | 20.74 |  | 15.86 | [8 empty] | 23.53 |  |  |  |  | 0.00
2002 |  |  |  | 9239.86 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 99.91 |  |  |  | 99.96 | [5 empty] | 98.85 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  |  |  | 0.06
2003 |  |  |  | 4185.83 |  |  | 3946 |  |  |  | 1067 | [10 empty] | 44.96 |  |  |  | 45.05 | [5 empty] | 44.78 |  |  | 45.05 |  |  |  | 0.00 |  | 25.92 | [8 empty] | 29.03 |  |  |  |  | 0.09
2004 |  |  |  | 5623.72 |  |  | 5258 |  |  |  | 1067 | [10 empty] | 59.86 |  |  |  | 59.87 | [5 empty] | 60.00 |  |  | 59.86 |  |  |  | 0.00 |  | 6.56 | [8 empty] | 33.57 |  |  |  |  | 0.00
2005 |  |  |  | 7192.00 |  |  | 6755 |  |  |  | 1067 | [10 empty] | 76.79 |  |  |  | 76.79 | [5 empty] | 76.95 |  |  | 77.11 |  |  |  | 0.00 |  | 2.37 | [8 empty] | 20.83 |  |  |  |  | 0.00
2006 |  |  |  | 2816.50 |  |  | 2772 |  |  |  | 1067 | [10 empty] | 30.41 |  |  |  | 31.04 | [5 empty] | 30.13 |  |  | 31.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 68.96 |  |  |  |  | 0.63
2007 |  |  |  | 5061.67 |  |  | 4714 |  |  |  | 1067 | [10 empty] | 53.81 |  |  |  | 99.99 | [5 empty] | 54.15 |  |  | 53.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 46.18
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2009 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2010 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2011 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1994 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 235
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 832 |  |  |  | 11
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 4384
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 156
Z. |  | Other | [39 empty] | 24
Subtotal | [22 empty] | 8784 | [14 empty] | 5216 |  |  |  | 270 | [11 empty] | 156
Total | [22 empty] | 8784 | [14 empty] | 5642
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1994 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 110
14. |  |  | Safety Systems | [34 empty] | 11
31. |  |  | Turbine and auxiliaries | [34 empty] | 19
41. |  |  | Main Generator Systems | [34 empty] | 72
42. |  |  | Electrical Power Supply Systems | [34 empty] | 33
Total | [37 empty] | 245
Highlights (2020)
Implementation of emergency safety measures for considering the Accident of Fukushima Dai-ichi Nuclear Power Stations.

## KASHIWAZAKI KARIWA-5
2020 Operating Experience
JP-40 | [8 empty] | KASHIWAZAKI KARIWA-5 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Owner | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Reactor Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Turbine Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-06-20
Thermal power | [12 empty] | : |  |  | 3293 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1989-09-12
Gross electrical power | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-04-10
Reference unit power (net) | [12 empty] | : |  |  | 1067 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.68 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 24 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 19
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 136968 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.15 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 47.32 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.25 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 48.99 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 48.76 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 46.92 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.67 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 47.52 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 7910.63 |  |  | 7597 |  |  |  | 1067 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.74 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 7093.33 |  |  | 6789 |  |  |  | 1067 | [10 empty] | 76.70 |  |  |  | 76.70 | [5 empty] | 75.89 |  |  | 77.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.30 |  |  |  |  | 0.00
1992 |  |  |  | 6977.48 |  |  | 6715 |  |  |  | 1067 | [10 empty] | 75.46 |  |  |  | 75.50 | [5 empty] | 74.45 |  |  | 76.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.50 |  |  |  |  | 0.04
1993 |  |  |  | 9238.24 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 99.89 |  |  |  | 99.90 | [5 empty] | 98.84 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.10 |  |  |  |  | 0.01
1994 |  |  |  | 7154.70 |  |  | 6825 |  |  |  | 1067 | [10 empty] | 77.50 |  |  |  | 77.50 | [5 empty] | 76.55 |  |  | 77.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.50 |  |  |  |  | 0.00
1995 |  |  |  | 7508.33 |  |  | 7183 |  |  |  | 1067 | [10 empty] | 81.46 |  |  |  | 81.46 | [5 empty] | 80.33 |  |  | 82.00 |  |  |  | 1.95 |  | 1.62 | [8 empty] | 16.92 |  |  |  |  | 0.00
1996 |  |  |  | 7905.83 |  |  | 7524 |  |  |  | 1067 | [10 empty] | 85.64 |  |  |  | 85.64 | [5 empty] | 84.35 |  |  | 85.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.36 |  |  |  |  | 0.00
1997 |  |  |  | 8919.12 |  |  | 8472 |  |  |  | 1067 | [10 empty] | 96.63 |  |  |  | 96.63 | [5 empty] | 95.42 |  |  | 96.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.37 |  |  |  |  | 0.00
1998 |  |  |  | 7352.55 |  |  | 6995 |  |  |  | 1067 | [10 empty] | 79.63 |  |  |  | 79.63 | [5 empty] | 78.66 |  |  | 79.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.37 |  |  |  |  | 0.00
1999 |  |  |  | 7771.81 |  |  | 7383 |  |  |  | 1067 | [10 empty] | 84.27 |  |  |  | 84.27 | [5 empty] | 83.15 |  |  | 84.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.73 |  |  |  |  | 0.00
2000 |  |  |  | 7042.75 |  |  | 6712 |  |  |  | 1067 | [10 empty] | 76.30 |  |  |  | 76.40 | [5 empty] | 75.14 |  |  | 76.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.60 |  |  |  |  | 0.11
2001 |  |  |  | 9198.56 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 99.61 |  |  |  | 99.61 | [5 empty] | 98.41 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.39 |  |  |  |  | 0.00
2002 |  |  |  | 8191.05 |  |  | 7743 |  |  |  | 1067 | [10 empty] | 88.31 |  |  |  | 88.31 | [5 empty] | 87.63 |  |  | 88.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.69 |  |  |  |  | 0.00
2003 |  |  |  | 1503.10 |  |  | 1392 |  |  |  | 1067 | [10 empty] | 16.07 |  |  |  | 16.07 | [5 empty] | 16.08 |  |  | 15.89 |  |  |  | 0.00 |  | 55.08 | [8 empty] | 28.85 |  |  |  |  | 0.00
2004 |  |  |  | 6134.80 |  |  | 5738 |  |  |  | 1067 | [10 empty] | 65.26 |  |  |  | 65.26 | [5 empty] | 65.46 |  |  | 65.32 |  |  |  | 0.01 |  | 11.17 | [8 empty] | 23.57 |  |  |  |  | 0.00
2005 |  |  |  | 6852.88 |  |  | 6446 |  |  |  | 1067 | [10 empty] | 72.99 |  |  |  | 72.99 | [5 empty] | 73.32 |  |  | 73.58 |  |  |  | 0.15 |  | 0.95 | [8 empty] | 26.06 |  |  |  |  | 0.00
2006 |  |  |  | 8400.48 |  |  | 7848 |  |  |  | 1067 | [10 empty] | 89.45 |  |  |  | 89.45 | [5 empty] | 89.87 |  |  | 89.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.55 |  |  |  |  | 0.00
2007 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 50.96 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 49.04 |  |  |  |  | 50.96
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2009 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2010 |  |  |  | 780.14 |  |  | 888 |  |  |  | 1067 | [10 empty] | 8.55 |  |  |  | 8.55 | [5 empty] | 8.35 |  |  | 10.14 |  |  |  | 5.20 |  | 0.47 | [8 empty] | 90.98 |  |  |  |  | 0.00
2011 |  |  |  | 9402.07 |  |  | 8760 |  |  |  | 1067 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.59 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2012 |  |  |  | 589.21 |  |  | 576 |  |  |  | 1067 | [10 empty] | 6.37 |  |  |  | 6.51 | [5 empty] | 6.29 |  |  | 6.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 93.49 |  |  |  |  | 0.14
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1067 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1990 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 170
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 905
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 8
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 274
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 3185
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 149
Z. |  | Other | [39 empty] | 33
Subtotal | [22 empty] | 8784 | [14 empty] | 4372 |  |  |  | 203 | [11 empty] | 149
Total | [22 empty] | 8784 | [14 empty] | 4724
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1990 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 166
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
Total | [37 empty] | 170
Highlights (2020)
Implementation of emergency safety measures for considering the Accident of Fukushima Dai-ichi Nuclear Power Stations.

## KASHIWAZAKI KARIWA-6
2020 Operating Experience
JP-55 | [8 empty] | KASHIWAZAKI KARIWA-6 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Owner | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Reactor Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / ABWR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1992-11-03
Thermal power | [12 empty] | : |  |  | 3926 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1996-01-29
Gross electrical power | [12 empty] | : |  |  | 1356 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1996-11-07
Reference unit power (net) | [12 empty] | : |  |  | 1315 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 24 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.75 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 24 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 5.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.69
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 872 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 205 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 133581 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.74 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 46.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.56 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 47.8 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 50.64 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 46.64 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.71 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 46.22 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1996 |  |  |  | 5663.21 |  |  | 5240 |  |  |  | 1315 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.77 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 10161.45 |  |  | 7752 |  |  |  | 1315 | [10 empty] | 88.44 |  |  |  | 88.44 | [5 empty] | 88.21 |  |  | 88.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.56 |  |  |  |  | 0.00
1998 |  |  |  | 10702.27 |  |  | 8217 |  |  |  | 1315 | [10 empty] | 93.26 |  |  |  | 93.26 | [5 empty] | 92.91 |  |  | 93.80 |  |  |  | 1.32 |  | 1.25 | [8 empty] | 5.49 |  |  |  |  | 0.00
1999 |  |  |  | 9710.40 |  |  | 7480 |  |  |  | 1315 | [10 empty] | 84.76 |  |  |  | 84.76 | [5 empty] | 84.30 |  |  | 85.39 |  |  |  | 2.80 |  | 2.45 | [8 empty] | 12.80 |  |  |  |  | 0.00
2000 |  |  |  | 9411.59 |  |  | 7183 |  |  |  | 1315 | [10 empty] | 81.76 |  |  |  | 81.76 | [5 empty] | 81.48 |  |  | 81.77 |  |  |  | 4.49 |  | 3.84 | [8 empty] | 14.39 |  |  |  |  | 0.00
2001 |  |  |  | 9269.97 |  |  | 7079 |  |  |  | 1315 | [10 empty] | 80.74 |  |  |  | 80.74 | [5 empty] | 80.47 |  |  | 80.81 |  |  |  | 1.17 |  | 0.95 | [8 empty] | 18.30 |  |  |  |  | 0.00
2002 |  |  |  | 11504.14 |  |  | 8760 |  |  |  | 1315 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.87 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 8401.23 |  |  | 6163 |  |  |  | 1315 | [10 empty] | 71.53 |  |  |  | 71.53 | [5 empty] | 72.93 |  |  | 70.35 |  |  |  | 0.00 |  | 10.92 | [8 empty] | 17.55 |  |  |  |  | 0.00
2004 |  |  |  | 8635.19 |  |  | 6410 |  |  |  | 1315 | [10 empty] | 72.69 |  |  |  | 72.69 | [5 empty] | 74.76 |  |  | 72.97 |  |  |  | 0.41 |  | 6.55 | [8 empty] | 20.76 |  |  |  |  | 0.00
2005 |  |  |  | 11126.45 |  |  | 8232 |  |  |  | 1315 | [10 empty] | 93.88 |  |  |  | 93.88 | [5 empty] | 96.59 |  |  | 93.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.12 |  |  |  |  | 0.00
2006 |  |  |  | 8446.71 |  |  | 6301 |  |  |  | 1315 | [10 empty] | 71.41 |  |  |  | 71.41 | [5 empty] | 73.33 |  |  | 71.93 |  |  |  | 0.25 |  | 0.18 | [8 empty] | 28.41 |  |  |  |  | 0.00
2007 |  |  |  | 3758.17 |  |  | 2787 |  |  |  | 1315 | [10 empty] | 31.64 |  |  |  | 73.01 | [5 empty] | 32.62 |  |  | 31.82 |  |  |  | 9.34 |  | 7.52 | [8 empty] | 19.47 |  |  |  |  | 41.37
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2009 |  |  |  | 3653.77 |  |  | 2818 |  |  |  | 1315 | [10 empty] | 30.88 |  |  |  | 30.88 | [5 empty] | 31.72 |  |  | 32.17 |  |  |  | 5.10 |  | 1.66 | [8 empty] | 67.46 |  |  |  |  | 0.00
2010 |  |  |  | 9522.09 |  |  | 7089 |  |  |  | 1315 | [10 empty] | 80.65 |  |  |  | 80.65 | [5 empty] | 82.66 |  |  | 80.92 |  |  |  | 2.75 |  | 2.28 | [8 empty] | 17.08 |  |  |  |  | 0.00
2011 |  |  |  | 10960.32 |  |  | 8147 |  |  |  | 1315 | [10 empty] | 92.74 |  |  |  | 92.74 | [5 empty] | 95.15 |  |  | 93.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.26 |  |  |  |  | 0.00
2012 |  |  |  | 2756.33 |  |  | 2040 |  |  |  | 1315 | [10 empty] | 23.13 |  |  |  | 23.13 | [5 empty] | 23.86 |  |  | 23.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 76.87 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1996 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 71
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 647
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 281
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 3531
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 151
Z. |  | Other | [39 empty] | 68
Subtotal | [22 empty] | 8784 | [14 empty] | 4459 |  |  |  | 139 | [11 empty] | 151
Total | [22 empty] | 8784 | [14 empty] | 4749
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1996 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 14
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 44
32. |  |  | Feedwater and Main Steam System | [34 empty] | 27
41. |  |  | Main Generator Systems | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 116
Highlights (2020)
Implementation of emergency safety measures for considering the Accident of Fukushima Dai-ichi Nuclear Power Stations.

## KASHIWAZAKI KARIWA-7
2020 Operating Experience
JP-56 | [8 empty] | KASHIWAZAKI KARIWA-7 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Owner | [7 empty] | : | TEPCO (Tokyo Electric Power Company Holdings, Inc.)
Reactor Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / ABWR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1993-07-01
Thermal power | [12 empty] | : |  |  | 3926 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1996-12-17
Gross electrical power | [12 empty] | : |  |  | 1356 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1997-07-02
Reference unit power (net) | [12 empty] | : |  |  | 1315 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 24 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.75 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 24 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 5.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.69
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 872 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 205 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 116411 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.77 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 41.74 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.79 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 43.31 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 54.9 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 42.11 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.58 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 42.26 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1997 |  |  |  | 8127.93 |  |  | 6764 |  |  |  | 1315 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 9715.61 |  |  | 7452 |  |  |  | 1315 | [10 empty] | 84.66 |  |  |  | 84.66 | [5 empty] | 84.34 |  |  | 85.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.34 |  |  |  |  | 0.00
1999 |  |  |  | 8445.43 |  |  | 6458 |  |  |  | 1315 | [10 empty] | 73.66 |  |  |  | 73.66 | [5 empty] | 73.31 |  |  | 73.72 |  |  |  | 15.86 |  | 13.88 | [8 empty] | 12.45 |  |  |  |  | 0.00
2000 |  |  |  | 11240.18 |  |  | 8587 |  |  |  | 1315 | [10 empty] | 97.62 |  |  |  | 97.62 | [5 empty] | 97.31 |  |  | 97.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.38 |  |  |  |  | 0.00
2001 |  |  |  | 10078.37 |  |  | 7752 |  |  |  | 1315 | [10 empty] | 87.76 |  |  |  | 87.76 | [5 empty] | 87.49 |  |  | 88.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.24 |  |  |  |  | 0.00
2002 |  |  |  | 7989.96 |  |  | 6089 |  |  |  | 1315 | [10 empty] | 68.95 |  |  |  | 69.51 | [5 empty] | 69.36 |  |  | 69.51 |  |  |  | 0.00 |  | 5.50 | [8 empty] | 24.99 |  |  |  |  | 0.56
2003 |  |  |  | 5778.49 |  |  | 4302 |  |  |  | 1315 | [10 empty] | 49.19 |  |  |  | 49.19 | [5 empty] | 50.16 |  |  | 49.11 |  |  |  | 0.00 |  | 16.37 | [8 empty] | 34.44 |  |  |  |  | 0.00
2004 |  |  |  | 10805.16 |  |  | 8057 |  |  |  | 1315 | [10 empty] | 91.59 |  |  |  | 94.46 | [5 empty] | 93.54 |  |  | 91.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.54 |  |  |  |  | 2.87
2005 |  |  |  | 7977.49 |  |  | 6007 |  |  |  | 1315 | [10 empty] | 68.00 |  |  |  | 68.00 | [5 empty] | 69.25 |  |  | 68.57 |  |  |  | 0.00 |  | 1.92 | [8 empty] | 30.08 |  |  |  |  | 0.00
2006 |  |  |  | 8166.24 |  |  | 6250 |  |  |  | 1315 | [10 empty] | 69.53 |  |  |  | 69.86 | [5 empty] | 70.89 |  |  | 71.35 |  |  |  | 1.39 |  | 0.98 | [8 empty] | 29.15 |  |  |  |  | 0.33
2007 |  |  |  | 6358.57 |  |  | 4714 |  |  |  | 1315 | [10 empty] | 53.82 |  |  |  | 87.12 | [5 empty] | 55.20 |  |  | 53.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.88 |  |  |  |  | 33.31
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2009 |  |  |  | 5366.30 |  |  | 4338 |  |  |  | 1315 | [10 empty] | 45.84 |  |  |  | 45.84 | [5 empty] | 46.58 |  |  | 49.52 |  |  |  | 2.13 |  | 1.00 | [8 empty] | 53.16 |  |  |  |  | 0.00
2010 |  |  |  | 9033.86 |  |  | 7041 |  |  |  | 1315 | [10 empty] | 77.23 |  |  |  | 77.23 | [5 empty] | 78.42 |  |  | 80.38 |  |  |  | 3.07 |  | 2.45 | [8 empty] | 20.33 |  |  |  |  | 0.00
2011 |  |  |  | 7348.67 |  |  | 5616 |  |  |  | 1315 | [10 empty] | 62.90 |  |  |  | 62.90 | [5 empty] | 63.79 |  |  | 64.11 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 37.07 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1315 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1997 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 136
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 795
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 42
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 49
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 4005
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 138
Z. |  | Other | [39 empty] | 17
Subtotal | [22 empty] | 8784 | [14 empty] | 4891 |  |  |  | 153 | [11 empty] | 138
Total | [22 empty] | 8784 | [14 empty] | 5182
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1997 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 47
12. |  |  | Reactor I&C Systems | [34 empty] | 41
15. |  |  | Reactor Cooling Systems | [34 empty] | 48
Total | [37 empty] | 136
Highlights (2020)
Implementation of emergency safety measures for considering the Accident of Fukushima Dai-ichi and Dai-ni Nuclear Power Stations.

## MIHAMA-3
2020 Operating Experience
JP-14 | [8 empty] | MIHAMA-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-08-07
Thermal power | [12 empty] | : |  |  | 2440 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-02-19
Gross electrical power | [12 empty] | : |  |  | 826 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-12-01
Reference unit power (net) | [12 empty] | : |  |  | 780 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.24
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.0 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.64 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 168850 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.89 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 55.42 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.34 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 55.44 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 43.23 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 56.01 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 56.16 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | 2615.00 |  |  | 5285 |  |  |  | 780 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 85.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.90 |  |  |  |  | 0.00
1977 |  |  |  | 4498.50 |  |  | 6159 |  |  |  | 780 | [10 empty] | 65.85 |  |  |  | 65.85 | [5 empty] | 65.84 |  |  | 70.31 |  |  |  | 1.27 |  | 0.85 | [8 empty] | 33.31 |  |  |  |  | 0.00
1978 |  |  |  | 4166.60 |  |  | 5537 |  |  |  | 780 | [10 empty] | 59.52 |  |  |  | 59.52 | [5 empty] | 60.98 |  |  | 63.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 40.48 |  |  |  |  | 0.00
1979 |  |  |  | 1697.40 |  |  | 2307 |  |  |  | 780 | [10 empty] | 24.85 |  |  |  | 24.85 | [5 empty] | 24.84 |  |  | 26.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 75.15 |  |  |  |  | 0.00
1980 |  |  |  | 4597.70 |  |  | 5964 |  |  |  | 780 | [10 empty] | 67.00 |  |  |  | 67.00 | [5 empty] | 67.10 |  |  | 67.90 |  |  |  | 1.17 |  | 0.79 | [8 empty] | 32.21 |  |  |  |  | 0.00
1981 |  |  |  | 5832.90 |  |  | 7607 |  |  |  | 780 | [10 empty] | 85.16 |  |  |  | 85.16 | [5 empty] | 85.37 |  |  | 86.84 |  |  |  | 0.33 |  | 0.28 | [8 empty] | 14.55 |  |  |  |  | 0.00
1982 |  |  |  | 5239.10 |  |  | 6952 |  |  |  | 780 | [10 empty] | 76.38 |  |  |  | 76.38 | [5 empty] | 76.68 |  |  | 79.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.62 |  |  |  |  | 0.00
1983 |  |  |  | 4818.00 |  |  | 6330 |  |  |  | 780 | [10 empty] | 70.63 |  |  |  | 70.63 | [5 empty] | 70.51 |  |  | 72.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.37 |  |  |  |  | 0.00
1984 |  |  |  | 5353.73 |  |  | 6906 |  |  |  | 780 | [10 empty] | 77.82 |  |  |  | 77.82 | [5 empty] | 78.14 |  |  | 78.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.18 |  |  |  |  | 0.00
1985 |  |  |  | 4971.94 |  |  | 6426 |  |  |  | 780 | [10 empty] | 72.65 |  |  |  | 72.65 | [5 empty] | 72.77 |  |  | 73.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.35 |  |  |  |  | 0.00
1986 |  |  |  | 6848.35 |  |  | 8760 |  |  |  | 780 | [10 empty] | 99.78 |  |  |  | 99.78 | [5 empty] | 100.23 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.22 |  |  |  |  | 0.00
1987 |  |  |  | 4822.71 |  |  | 6268 |  |  |  | 780 | [10 empty] | 71.55 |  |  |  | 71.55 | [5 empty] | 70.58 |  |  | 71.55 |  |  |  | 3.89 |  | 2.90 | [8 empty] | 25.55 |  |  |  |  | 0.00
1988 |  |  |  | 4261.32 |  |  | 5625 |  |  |  | 780 | [10 empty] | 64.04 |  |  |  | 64.04 | [5 empty] | 62.20 |  |  | 64.04 |  |  |  | 5.10 |  | 3.44 | [8 empty] | 32.53 |  |  |  |  | 0.00
1989 |  |  |  | 5299.69 |  |  | 6834 |  |  |  | 780 | [10 empty] | 78.01 |  |  |  | 78.01 | [5 empty] | 77.56 |  |  | 78.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.99 |  |  |  |  | 0.00
1990 |  |  |  | 6867.04 |  |  | 8760 |  |  |  | 780 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 100.50 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
1991 |  |  |  | 4246.18 |  |  | 5495 |  |  |  | 780 | [10 empty] | 59.68 |  |  |  | 59.68 | [5 empty] | 62.14 |  |  | 62.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 40.32 |  |  |  |  | 0.00
1992 |  |  |  | 4709.88 |  |  | 6095 |  |  |  | 780 | [10 empty] | 68.54 |  |  |  | 68.54 | [5 empty] | 68.74 |  |  | 69.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.46 |  |  |  |  | 0.00
1993 |  |  |  | 4526.62 |  |  | 5951 |  |  |  | 780 | [10 empty] | 66.11 |  |  |  | 66.42 | [5 empty] | 66.25 |  |  | 67.93 |  |  |  | 0.74 |  | 0.50 | [8 empty] | 33.08 |  |  |  |  | 0.31
1994 |  |  |  | 6623.04 |  |  | 8486 |  |  |  | 780 | [10 empty] | 96.81 |  |  |  | 96.83 | [5 empty] | 96.93 |  |  | 96.87 |  |  |  | 1.78 |  | 1.76 | [8 empty] | 1.42 |  |  |  |  | 0.01
1995 |  |  |  | 3389.17 |  |  | 4534 |  |  |  | 780 | [10 empty] | 49.61 |  |  |  | 49.74 | [5 empty] | 49.60 |  |  | 51.76 |  |  |  | 21.69 |  | 13.77 | [8 empty] | 36.49 |  |  |  |  | 0.13
1996 |  |  |  | 4491.42 |  |  | 5760 |  |  |  | 780 | [10 empty] | 65.30 |  |  |  | 65.50 | [5 empty] | 65.55 |  |  | 65.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 34.50 |  |  |  |  | 0.19
1997 |  |  |  | 6262.81 |  |  | 7963 |  |  |  | 780 | [10 empty] | 91.24 |  |  |  | 91.24 | [5 empty] | 91.66 |  |  | 90.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.76 |  |  |  |  | 0.00
1998 |  |  |  | 5979.86 |  |  | 7788 |  |  |  | 780 | [10 empty] | 87.10 |  |  |  | 87.10 | [5 empty] | 87.52 |  |  | 88.90 |  |  |  | 1.39 |  | 1.23 | [8 empty] | 11.66 |  |  |  |  | 0.00
1999 |  |  |  | 5795.30 |  |  | 7398 |  |  |  | 780 | [10 empty] | 84.44 |  |  |  | 84.44 | [5 empty] | 84.82 |  |  | 84.45 |  |  |  | 3.45 |  | 3.01 | [8 empty] | 12.54 |  |  |  |  | 0.00
2000 |  |  |  | 4784.98 |  |  | 6117 |  |  |  | 780 | [10 empty] | 69.60 |  |  |  | 69.61 | [5 empty] | 69.84 |  |  | 69.64 |  |  |  | 15.88 |  | 13.15 | [8 empty] | 17.25 |  |  |  |  | 0.00
2001 |  |  |  | 6853.68 |  |  | 8760 |  |  |  | 780 | [10 empty] | 99.96 |  |  |  | 99.99 | [5 empty] | 100.31 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.03
2002 |  |  |  | 5248.01 |  |  | 6732 |  |  |  | 780 | [10 empty] | 76.84 |  |  |  | 76.84 | [5 empty] | 76.81 |  |  | 76.85 |  |  |  | 5.19 |  | 4.21 | [8 empty] | 18.95 |  |  |  |  | 0.00
2003 |  |  |  | 6111.49 |  |  | 7701 |  |  |  | 780 | [10 empty] | 87.91 |  |  |  | 87.91 | [5 empty] | 89.44 |  |  | 87.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.09 |  |  |  |  | 0.00
2004 |  |  |  | 4301.26 |  |  | 5319 |  |  |  | 780 | [10 empty] | 60.48 |  |  |  | 60.48 | [5 empty] | 62.78 |  |  | 60.55 |  |  |  | 2.06 |  | 13.02 | [8 empty] | 26.50 |  |  |  |  | 0.00
2005 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2006 |  |  |  | 92.08 |  |  | 181 |  |  |  | 780 | [10 empty] | 1.35 |  |  |  | 1.35 | [5 empty] | 1.35 |  |  | 2.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 98.65 |  |  |  |  | 0.00
2007 |  |  |  | 4943.91 |  |  | 6190 |  |  |  | 780 | [10 empty] | 69.45 |  |  |  | 69.45 | [5 empty] | 72.36 |  |  | 70.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.55 |  |  |  |  | 0.00
2008 |  |  |  | 5725.55 |  |  | 7049 |  |  |  | 780 | [10 empty] | 79.72 |  |  |  | 79.72 | [5 empty] | 83.57 |  |  | 80.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.28 |  |  |  |  | 0.00
2009 |  |  |  | 6795.53 |  |  | 8315 |  |  |  | 780 | [10 empty] | 94.86 |  |  |  | 94.86 | [5 empty] | 99.45 |  |  | 94.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.14 |  |  |  |  | 0.00
2010 |  |  |  | 5541.00 |  |  | 6823 |  |  |  | 780 | [10 empty] | 77.39 |  |  |  | 77.39 | [5 empty] | 81.09 |  |  | 77.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.61 |  |  |  |  | 0.00
2011 |  |  |  | 2637.14 |  |  | 3203 |  |  |  | 780 | [10 empty] | 36.51 |  |  |  | 36.51 | [5 empty] | 38.60 |  |  | 36.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 63.49 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1976 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 99
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1855
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 3
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 1884
L. |  | Human factor related | [39 empty] | 6
Subtotal | [22 empty] | 8784 | [14 empty] | 3739 |  |  |  | 108
Total | [22 empty] | 8784 | [14 empty] | 3847
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1976 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 25
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 25
32. |  |  | Feedwater and Main Steam System | [34 empty] | 46
34. |  |  | Miscellaneous Systems | [34 empty] | 3
Total | [37 empty] | 107

## OHI-3
2020 Operating Experience
JP-50 | [8 empty] | OHI-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (4-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1987-10-03
Thermal power | [12 empty] | : |  |  | 3423 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1991-06-07
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1991-12-18
Reference unit power (net) | [12 empty] | : |  |  | 1127 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 29 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5627.87 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 54.99 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 54.99 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 45.01 %
Load Factor (LF) | [18 empty] | : | 56.85 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 55.03 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3950 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 18.06 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 871.75 | 816.24 |  |  |  | 872.27 |  | 842.84 | [8 empty] | 866.56 |  |  | 828.52 | [6 empty] | 529.68 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5627.87
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 62.16 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 54.99
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 62.16 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 54.99
LF [%] |  |  |  |  | 103.97 | 104.06 |  |  |  | 104.03 |  | 103.87 | [8 empty] | 103.35 |  |  | 102.10 | [6 empty] | 63.17 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 56.85
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 62.63 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 55.03
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 37.84 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 45.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 189436.87 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.88 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 65.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.63 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 65.12 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 30.25 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.96 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 65.38 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1991 |  |  |  | 2524.41 |  |  | 3228 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 9954.69 |  |  | 8784 |  |  |  | 1127 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 100.56 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
1993 |  |  |  | 7863.69 |  |  | 7025 |  |  |  | 1127 | [10 empty] | 79.43 |  |  |  | 79.43 | [5 empty] | 79.65 |  |  | 80.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.57 |  |  |  |  | 0.00
1994 |  |  |  | 8139.08 |  |  | 7265 |  |  |  | 1127 | [10 empty] | 82.53 |  |  |  | 82.53 | [5 empty] | 82.44 |  |  | 82.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.47 |  |  |  |  | 0.00
1995 |  |  |  | 7701.72 |  |  | 6887 |  |  |  | 1127 | [10 empty] | 77.82 |  |  |  | 77.82 | [5 empty] | 78.01 |  |  | 78.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.18 |  |  |  |  | 0.00
1996 |  |  |  | 9957.45 |  |  | 8784 |  |  |  | 1127 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.58 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1997 |  |  |  | 8333.01 |  |  | 7385 |  |  |  | 1127 | [10 empty] | 83.88 |  |  |  | 83.88 | [5 empty] | 84.41 |  |  | 84.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.12 |  |  |  |  | 0.00
1998 |  |  |  | 8872.74 |  |  | 7867 |  |  |  | 1127 | [10 empty] | 89.30 |  |  |  | 89.30 | [5 empty] | 89.87 |  |  | 89.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.70 |  |  |  |  | 0.00
1999 |  |  |  | 8892.35 |  |  | 7875 |  |  |  | 1127 | [10 empty] | 89.52 |  |  |  | 89.89 | [5 empty] | 90.07 |  |  | 89.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.11 |  |  |  |  | 0.37
2000 |  |  |  | 8868.86 |  |  | 7824 |  |  |  | 1127 | [10 empty] | 89.06 |  |  |  | 89.06 | [5 empty] | 89.59 |  |  | 89.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.94 |  |  |  |  | 0.00
2001 |  |  |  | 8474.65 |  |  | 7481 |  |  |  | 1127 | [10 empty] | 85.38 |  |  |  | 85.38 | [5 empty] | 85.84 |  |  | 85.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.62 |  |  |  |  | 0.01
2002 |  |  |  | 9918.68 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.47 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2003 |  |  |  | 8683.19 |  |  | 7525 |  |  |  | 1127 | [10 empty] | 85.89 |  |  |  | 85.89 | [5 empty] | 87.95 |  |  | 85.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.11 |  |  |  |  | 0.00
2004 |  |  |  | 3040.18 |  |  | 2634 |  |  |  | 1127 | [10 empty] | 30.01 |  |  |  | 30.01 | [5 empty] | 30.71 |  |  | 29.99 |  |  |  | 0.00 |  | 59.84 | [8 empty] | 10.15 |  |  |  |  | 0.00
2005 |  |  |  | 7834.00 |  |  | 6968 |  |  |  | 1127 | [10 empty] | 77.64 |  |  |  | 77.64 | [5 empty] | 79.35 |  |  | 79.54 |  |  |  | 7.12 |  | 9.73 | [8 empty] | 12.63 |  |  |  |  | 0.00
2006 |  |  |  | 8012.30 |  |  | 7001 |  |  |  | 1127 | [10 empty] | 79.62 |  |  |  | 79.62 | [5 empty] | 81.16 |  |  | 79.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.38 |  |  |  |  | 0.00
2007 |  |  |  | 10080.14 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 102.10 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2008 |  |  |  | 2355.61 |  |  | 2081 |  |  |  | 1127 | [10 empty] | 23.36 |  |  |  | 23.36 | [5 empty] | 23.80 |  |  | 23.69 |  |  |  | 0.00 |  | 53.75 | [8 empty] | 22.90 |  |  |  |  | 0.00
2009 |  |  |  | 8335.16 |  |  | 7282 |  |  |  | 1127 | [10 empty] | 83.08 |  |  |  | 83.08 | [5 empty] | 84.43 |  |  | 83.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.92 |  |  |  |  | 0.00
2010 |  |  |  | 8297.03 |  |  | 7299 |  |  |  | 1127 | [10 empty] | 82.76 |  |  |  | 82.76 | [5 empty] | 84.04 |  |  | 83.32 |  |  |  | 11.51 |  | 10.76 | [8 empty] | 6.48 |  |  |  |  | 0.00
2011 |  |  |  | 2104.70 |  |  | 1834 |  |  |  | 1127 | [10 empty] | 20.89 |  |  |  | 20.89 | [5 empty] | 21.32 |  |  | 20.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 79.11 |  |  |  |  | 0.00
2012 |  |  |  | 4925.65 |  |  | 4325 |  |  |  | 1127 | [10 empty] | 48.78 |  |  |  | 48.78 | [5 empty] | 49.76 |  |  | 49.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 51.22 |  |  |  |  | 0.00
2013 |  |  |  | 6779.28 |  |  | 5879 |  |  |  | 1127 | [10 empty] | 66.75 |  |  |  | 67.10 | [5 empty] | 68.67 |  |  | 67.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.90 |  |  |  |  | 0.36
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 8009.80 |  |  | 6967 |  |  |  | 1127 | [10 empty] | 79.13 |  |  |  | 79.13 | [5 empty] | 81.13 |  |  | 79.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.87 |  |  |  |  | 0.00
2019 |  |  |  | 7928.91 |  |  | 6881 |  |  |  | 1127 | [10 empty] | 78.12 |  |  |  | 78.12 | [5 empty] | 80.31 |  |  | 78.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.88 |  |  |  |  | 0.00
2020 |  |  |  | 5627.87 |  |  | 4834 |  |  |  | 1127 | [10 empty] | 54.99 |  |  |  | 54.99 | [5 empty] | 56.85 |  |  | 55.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 45.01 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1991 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 386
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 3950 | [14 empty] | 989
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 729
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 1017
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 33
Subtotal | [22 empty] | 3950 | [14 empty] | 2735 |  |  |  | 419
Total | [22 empty] | 3950 | [14 empty] | 3154
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1991 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 232
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 18
15. |  |  | Reactor Cooling Systems | [34 empty] | 169
Total | [37 empty] | 419

## OHI-4
2020 Operating Experience
JP-51 | [8 empty] | OHI-4 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (4-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1988-06-13
Thermal power | [12 empty] | : |  |  | 3423 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1992-06-19
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-02-02
Reference unit power (net) | [12 empty] | : |  |  | 1127 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 28 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8481.35 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.95 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.95 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.05 %
Load Factor (LF) | [18 empty] | : | 85.67 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 83.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1406 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 866.66 | 810.23 |  |  |  | 866.26 |  | 837.13 | [8 empty] | 862.94 |  |  | 828.12 | [6 empty] | 847.36 |  | 840.70 |  |  |  | 815.47 |  |  | 844.43 |  |  | 62.05 | [9 empty] | 0.00 |  |  | 8481.35
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 7.56 | [9 empty] | 0.00 |  |  | 83.95
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 7.56 | [9 empty] | 0.00 |  |  | 83.95
LF [%] |  |  |  |  | 103.36 | 103.29 |  |  |  | 103.31 |  | 103.17 | [8 empty] | 102.92 |  |  | 102.06 | [6 empty] | 101.06 |  | 100.26 |  |  |  | 100.50 |  |  | 100.71 |  |  | 7.65 | [9 empty] | 0.00 |  |  | 85.67
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 8.06 | [9 empty] | 0.00 |  |  | 83.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 92.44 | [9 empty] | 100.00 |  |  | 16.05
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 192161.35 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.23 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 68.56 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.57 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 68.58 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 29.86 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 69.67 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 68.75 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 9923.46 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 100.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
1994 |  |  |  | 7851.52 |  |  | 7063 |  |  |  | 1127 | [10 empty] | 79.68 |  |  |  | 79.68 | [5 empty] | 79.53 |  |  | 80.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.32 |  |  |  |  | 0.00
1995 |  |  |  | 7495.11 |  |  | 6695 |  |  |  | 1127 | [10 empty] | 75.63 |  |  |  | 75.63 | [5 empty] | 75.92 |  |  | 76.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.37 |  |  |  |  | 0.00
1996 |  |  |  | 7051.09 |  |  | 6221 |  |  |  | 1127 | [10 empty] | 70.81 |  |  |  | 70.81 | [5 empty] | 71.23 |  |  | 70.82 |  |  |  | 16.12 |  | 13.61 | [8 empty] | 15.58 |  |  |  |  | 0.00
1997 |  |  |  | 7660.20 |  |  | 6756 |  |  |  | 1127 | [10 empty] | 77.10 |  |  |  | 77.10 | [5 empty] | 77.59 |  |  | 77.12 |  |  |  | 22.89 |  | 22.89 | [8 empty] | 0.01 |  |  |  |  | 0.00
1998 |  |  |  | 8839.42 |  |  | 7835 |  |  |  | 1127 | [10 empty] | 88.96 |  |  |  | 88.96 | [5 empty] | 89.54 |  |  | 89.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.04 |  |  |  |  | 0.00
1999 |  |  |  | 8903.44 |  |  | 7872 |  |  |  | 1127 | [10 empty] | 89.54 |  |  |  | 89.85 | [5 empty] | 90.18 |  |  | 89.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.15 |  |  |  |  | 0.31
2000 |  |  |  | 8649.77 |  |  | 7629 |  |  |  | 1127 | [10 empty] | 86.83 |  |  |  | 86.83 | [5 empty] | 87.38 |  |  | 86.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.17 |  |  |  |  | 0.00
2001 |  |  |  | 9283.56 |  |  | 8179 |  |  |  | 1127 | [10 empty] | 93.36 |  |  |  | 93.36 | [5 empty] | 94.03 |  |  | 93.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.64 |  |  |  |  | 0.00
2002 |  |  |  | 9217.09 |  |  | 8017 |  |  |  | 1127 | [10 empty] | 91.50 |  |  |  | 91.50 | [5 empty] | 93.36 |  |  | 91.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.50 |  |  |  |  | 0.00
2003 |  |  |  | 8762.57 |  |  | 7557 |  |  |  | 1127 | [10 empty] | 86.26 |  |  |  | 86.26 | [5 empty] | 88.76 |  |  | 86.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.74 |  |  |  |  | 0.00
2004 |  |  |  | 8318.19 |  |  | 7186 |  |  |  | 1127 | [10 empty] | 81.78 |  |  |  | 81.78 | [5 empty] | 84.03 |  |  | 81.81 |  |  |  | 7.44 |  | 6.57 | [8 empty] | 11.65 |  |  |  |  | 0.00
2005 |  |  |  | 9929.00 |  |  | 8657 |  |  |  | 1127 | [10 empty] | 98.77 |  |  |  | 98.77 | [5 empty] | 100.57 |  |  | 98.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.23 |  |  |  |  | 0.00
2006 |  |  |  | 8163.92 |  |  | 7087 |  |  |  | 1127 | [10 empty] | 80.66 |  |  |  | 80.66 | [5 empty] | 82.69 |  |  | 80.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.34 |  |  |  |  | 0.00
2007 |  |  |  | 7978.56 |  |  | 6934 |  |  |  | 1127 | [10 empty] | 78.87 |  |  |  | 78.87 | [5 empty] | 80.82 |  |  | 79.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.13 |  |  |  |  | 0.00
2008 |  |  |  | 7642.69 |  |  | 6654 |  |  |  | 1127 | [10 empty] | 75.41 |  |  |  | 75.41 | [5 empty] | 77.20 |  |  | 75.75 |  |  |  | 0.79 |  | 0.60 | [8 empty] | 23.98 |  |  |  |  | 0.00
2009 |  |  |  | 10097.36 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 102.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2010 |  |  |  | 6977.31 |  |  | 6109 |  |  |  | 1127 | [10 empty] | 69.41 |  |  |  | 69.41 | [5 empty] | 70.67 |  |  | 69.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.59 |  |  |  |  | 0.00
2011 |  |  |  | 5599.90 |  |  | 4872 |  |  |  | 1127 | [10 empty] | 55.56 |  |  |  | 55.56 | [5 empty] | 56.72 |  |  | 55.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 44.44 |  |  |  |  | 0.00
2012 |  |  |  | 4486.58 |  |  | 3941 |  |  |  | 1127 | [10 empty] | 44.41 |  |  |  | 44.41 | [5 empty] | 45.32 |  |  | 44.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 55.59 |  |  |  |  | 0.00
2013 |  |  |  | 7167.72 |  |  | 6191 |  |  |  | 1127 | [10 empty] | 70.67 |  |  |  | 70.67 | [5 empty] | 72.60 |  |  | 70.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.33 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 6428.38 |  |  | 5623 |  |  |  | 1127 | [10 empty] | 63.79 |  |  |  | 63.79 | [5 empty] | 65.11 |  |  | 64.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.21 |  |  |  |  | 0.00
2019 |  |  |  | 8077.29 |  |  | 7011 |  |  |  | 1127 | [10 empty] | 79.65 |  |  |  | 79.65 | [5 empty] | 81.82 |  |  | 80.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.35 |  |  |  |  | 0.00
2020 |  |  |  | 8481.35 |  |  | 7378 |  |  |  | 1127 | [10 empty] | 83.95 |  |  |  | 83.95 | [5 empty] | 85.67 |  |  | 83.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.05 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1993 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 121
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1406 | [14 empty] | 940
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 744
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 1007
Z. |  | Other | [39 empty] | 21
Subtotal | [22 empty] | 1406 | [14 empty] | 2691 |  |  |  | 142
Total | [22 empty] | 1406 | [14 empty] | 2833
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1993 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 21
41. |  |  | Main Generator Systems | [34 empty] | 118
Total | [37 empty] | 141

## ONAGAWA-2
2020 Operating Experience
JP-54 | [8 empty] | ONAGAWA-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TOHOKU (Tohoku Electric Power Co., Inc)
Owner | [7 empty] | : | TOHOKU (Tohoku Electric Power Co., Inc)
Reactor Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Turbine Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1991-04-12
Thermal power | [12 empty] | : |  |  | 2436 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1994-12-23
Gross electrical power | [12 empty] | : |  |  | 825 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1995-07-28
Reference unit power (net) | [12 empty] | : |  |  | 796 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 26 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6.93
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.43
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.7 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 4.07 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 17
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [13 empty] | : |  |  | 137 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 81165 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.56 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 44.8 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.34 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 48.28 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 47.39 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 44.9 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.47 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 44.96 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1995 |  |  |  | 4496.61 |  |  | 6510 |  |  |  | 796 | [10 empty] | 95.35 |  |  |  | 95.35 | [5 empty] | 94.74 |  |  | 95.59 |  |  |  | 4.55 |  | 4.55 | [8 empty] | 0.10 |  |  |  |  | 0.00
1996 |  |  |  | 5175.27 |  |  | 6545 |  |  |  | 796 | [10 empty] | 74.44 |  |  |  | 74.44 | [5 empty] | 74.02 |  |  | 74.51 |  |  |  | 2.69 |  | 2.06 | [8 empty] | 23.50 |  |  |  |  | 0.00
1997 |  |  |  | 6931.60 |  |  | 8760 |  |  |  | 796 | [10 empty] | 99.91 |  |  |  | 99.92 | [5 empty] | 99.41 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.08 |  |  |  |  | 0.01
1998 |  |  |  | 5647.72 |  |  | 7185 |  |  |  | 796 | [10 empty] | 81.11 |  |  |  | 81.12 | [5 empty] | 80.99 |  |  | 82.02 |  |  |  | 2.63 |  | 2.19 | [8 empty] | 16.69 |  |  |  |  | 0.00
1999 |  |  |  | 5841.18 |  |  | 7383 |  |  |  | 796 | [10 empty] | 84.23 |  |  |  | 84.23 | [5 empty] | 83.77 |  |  | 84.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.77 |  |  |  |  | 0.00
2000 |  |  |  | 5858.59 |  |  | 7402 |  |  |  | 796 | [10 empty] | 84.25 |  |  |  | 84.25 | [5 empty] | 83.79 |  |  | 84.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.75 |  |  |  |  | 0.00
2001 |  |  |  | 6521.16 |  |  | 8238 |  |  |  | 796 | [10 empty] | 93.96 |  |  |  | 93.96 | [5 empty] | 93.52 |  |  | 94.04 |  |  |  | 2.96 |  | 2.87 | [8 empty] | 3.17 |  |  |  |  | 0.00
2002 |  |  |  | 5242.91 |  |  | 6368 |  |  |  | 796 | [10 empty] | 72.44 |  |  |  | 72.44 | [5 empty] | 75.19 |  |  | 72.69 |  |  |  | 3.21 |  | 8.96 | [8 empty] | 18.60 |  |  |  |  | 0.00
2003 |  |  |  | 3272.36 |  |  | 4139 |  |  |  | 796 | [10 empty] | 47.17 |  |  |  | 47.28 | [5 empty] | 46.93 |  |  | 47.25 |  |  |  | 0.00 |  | 37.62 | [8 empty] | 15.11 |  |  |  |  | 0.11
2004 |  |  |  | 7040.38 |  |  | 8784 |  |  |  | 796 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.69 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 1877.27 |  |  | 2367 |  |  |  | 796 | [10 empty] | 26.78 |  |  |  | 64.46 | [5 empty] | 26.92 |  |  | 27.02 |  |  |  | 0.00 |  | 8.20 | [8 empty] | 27.34 |  |  |  |  | 37.68
2006 |  |  |  | 2484.73 |  |  | 3188 |  |  |  | 796 | [10 empty] | 35.56 |  |  |  | 38.88 | [5 empty] | 35.63 |  |  | 36.39 |  |  |  | 33.66 |  | 40.74 | [8 empty] | 20.37 |  |  |  |  | 3.33
2007 |  |  |  | 5184.62 |  |  | 6491 |  |  |  | 796 | [10 empty] | 73.83 |  |  |  | 73.83 | [5 empty] | 74.35 |  |  | 74.10 |  |  |  | 1.47 |  | 4.65 | [8 empty] | 21.51 |  |  |  |  | 0.00
2008 |  |  |  | 6453.43 |  |  | 8086 |  |  |  | 796 | [10 empty] | 91.76 |  |  |  | 91.76 | [5 empty] | 92.30 |  |  | 92.05 |  |  |  | 0.00 |  | 0.11 | [8 empty] | 8.13 |  |  |  |  | 0.00
2009 |  |  |  | 3430.26 |  |  | 4330 |  |  |  | 796 | [10 empty] | 48.98 |  |  |  | 49.01 | [5 empty] | 49.19 |  |  | 49.43 |  |  |  | 0.00 |  | 0.87 | [8 empty] | 50.11 |  |  |  |  | 0.04
2010 |  |  |  | 5905.54 |  |  | 7417 |  |  |  | 796 | [10 empty] | 84.40 |  |  |  | 84.62 | [5 empty] | 84.69 |  |  | 84.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.38 |  |  |  |  | 0.22
2011 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 46.95 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.17 | [8 empty] | 52.88 |  |  |  |  | 46.95
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1995 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 370
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 900 |  |  |  | 4
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 24
E. |  | Testing of plant systems or components | [39 empty] | 7
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 3222
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 303
Subtotal | [22 empty] | 8784 | [14 empty] | 4146 |  |  |  | 381 | [11 empty] | 303
Total | [22 empty] | 8784 | [14 empty] | 4830
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1995 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 34
12. |  |  | Reactor I&C Systems | [34 empty] | 71
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 61
15. |  |  | Reactor Cooling Systems | [34 empty] | 156
31. |  |  | Turbine and auxiliaries | [34 empty] | 13
32. |  |  | Feedwater and Main Steam System | [34 empty] | 29
34. |  |  | Miscellaneous Systems | [34 empty] | 4
Total | [37 empty] | 368
Highlights (2020)
Implementation of safety measure for considering the new regulatory requirements.

## ONAGAWA-3
2020 Operating Experience
JP-57 | [8 empty] | ONAGAWA-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TOHOKU (Tohoku Electric Power Co., Inc)
Owner | [7 empty] | : | TOHOKU (Tohoku Electric Power Co., Inc)
Reactor Supplier | [7 empty] | : | TOSHIBA (TOSHIBA CORPORATION)
Turbine Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1998-01-23
Thermal power | [12 empty] | : |  |  | 2436 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2001-05-30
Gross electrical power | [12 empty] | : |  |  | 825 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-01-30
Reference unit power (net) | [12 empty] | : |  |  | 796 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 19 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6.93
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.43
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.7 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 4.07 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [13 empty] | : |  |  | 137 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 43740 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.85 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 32.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 35.64 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 57.35 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 33.3 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.3 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 32.6 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 6652.52 |  |  | 8064 |  |  |  | 796 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.64 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 5978.24 |  |  | 7332 |  |  |  | 796 | [10 empty] | 83.70 |  |  |  | 84.66 | [5 empty] | 85.73 |  |  | 83.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.34 |  |  |  |  | 0.96
2004 |  |  |  | 5348.70 |  |  | 6548 |  |  |  | 796 | [10 empty] | 74.41 |  |  |  | 74.56 | [5 empty] | 76.50 |  |  | 74.54 |  |  |  | 0.00 |  | 11.18 | [8 empty] | 14.26 |  |  |  |  | 0.15
2005 |  |  |  | 4381.83 |  |  | 5460 |  |  |  | 796 | [10 empty] | 61.22 |  |  |  | 72.69 | [5 empty] | 62.84 |  |  | 62.33 |  |  |  | 1.50 |  | 6.31 | [8 empty] | 20.99 |  |  |  |  | 11.48
2006 |  |  |  | 2798.13 |  |  | 3476 |  |  |  | 796 | [10 empty] | 38.96 |  |  |  | 38.96 | [5 empty] | 40.13 |  |  | 39.68 |  |  |  | 50.01 |  | 60.86 | [8 empty] | 0.18 |  |  |  |  | 0.00
2007 |  |  |  | 2261.42 |  |  | 2887 |  |  |  | 796 | [10 empty] | 31.70 |  |  |  | 31.70 | [5 empty] | 32.43 |  |  | 32.96 |  |  |  | 15.96 |  | 24.00 | [8 empty] | 44.30 |  |  |  |  | 0.00
2008 |  |  |  | 6502.19 |  |  | 7921 |  |  |  | 796 | [10 empty] | 90.12 |  |  |  | 90.12 | [5 empty] | 92.99 |  |  | 90.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.88 |  |  |  |  | 0.00
2009 |  |  |  | 3405.82 |  |  | 4202 |  |  |  | 796 | [10 empty] | 47.48 |  |  |  | 47.48 | [5 empty] | 48.84 |  |  | 47.97 |  |  |  | 5.35 |  | 29.31 | [8 empty] | 23.21 |  |  |  |  | 0.00
2010 |  |  |  | 5342.77 |  |  | 6540 |  |  |  | 796 | [10 empty] | 74.22 |  |  |  | 74.22 | [5 empty] | 76.62 |  |  | 74.66 |  |  |  | 0.17 |  | 0.13 | [8 empty] | 25.65 |  |  |  |  | 0.00
2011 |  |  |  | 1315.85 |  |  | 1671 |  |  |  | 796 | [10 empty] | 18.37 |  |  |  | 68.34 | [5 empty] | 18.87 |  |  | 19.08 |  |  |  | 1.02 |  | 0.70 | [8 empty] | 30.96 |  |  |  |  | 49.97
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 796 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2002 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 123
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 745 |  |  |  | 109
E. |  | Testing of plant systems or components | [39 empty] | 245
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 151
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 4384
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 304
Z. |  | Other | [39 empty] | 155
Subtotal | [22 empty] | 8784 | [14 empty] | 5280 |  |  |  | 632 | [11 empty] | 304
Total | [22 empty] | 8784 | [14 empty] | 6216
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2002 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 32
31. |  |  | Turbine and auxiliaries | [34 empty] | 25
32. |  |  | Feedwater and Main Steam System | [34 empty] | 255
34. |  |  | Miscellaneous Systems | [34 empty] | 57
Total | [37 empty] | 369
Highlights (2020)
Implementation of safety measure for considering the new regulatory requirements.

## SENDAI-1
2020 Operating Experience
JP-28 | [8 empty] | SENDAI-1 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Owner | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-12-15
Thermal power | [12 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-09-16
Gross electrical power | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-07-04
Reference unit power (net) | [12 empty] | : |  |  | 846 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.22
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 49000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.07
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2552.25 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 31.58 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 31.58 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 68.42 %
Load Factor (LF) | [18 empty] | : | 34.34 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 32.08 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 5966 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 687.23 | 643.16 |  |  |  | 337.92 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 199.00 | [9 empty] | 684.95 |  |  | 2552.25
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 49.16 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 31.20 | [9 empty] | 100.00 |  |  | 31.58
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 49.16 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 31.20 | [9 empty] | 100.00 |  |  | 31.58
LF [%] |  |  |  |  | 109.18 | 109.23 |  |  |  | 53.69 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 32.67 | [9 empty] | 108.82 |  |  | 34.34
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 49.60 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 36.81 | [9 empty] | 100.00 |  |  | 32.08
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 50.84 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 68.80 | [9 empty] | 0.00 |  |  | 68.42
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 204288.25 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.56 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.15 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.76 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 71.15 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 28.09 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 71.67 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 6069.77 |  |  | 7487 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 5890.27 |  |  | 6964 |  |  |  | 846 | [10 empty] | 78.68 |  |  |  | 78.68 | [5 empty] | 79.48 |  |  | 79.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.32 |  |  |  |  | 0.00
1986 |  |  |  | 6084.02 |  |  | 7224 |  |  |  | 846 | [10 empty] | 81.36 |  |  |  | 81.36 | [5 empty] | 82.09 |  |  | 82.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.64 |  |  |  |  | 0.00
1987 |  |  |  | 6113.36 |  |  | 7261 |  |  |  | 846 | [10 empty] | 81.74 |  |  |  | 81.74 | [5 empty] | 82.49 |  |  | 82.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.26 |  |  |  |  | 0.00
1988 |  |  |  | 5683.09 |  |  | 6756 |  |  |  | 846 | [10 empty] | 75.81 |  |  |  | 75.81 | [5 empty] | 76.48 |  |  | 76.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.19 |  |  |  |  | 0.00
1989 |  |  |  | 7381.33 |  |  | 8641 |  |  |  | 846 | [10 empty] | 98.69 |  |  |  | 98.69 | [5 empty] | 99.60 |  |  | 98.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.31 |  |  |  |  | 0.00
1990 |  |  |  | 6154.95 |  |  | 7307 |  |  |  | 846 | [10 empty] | 82.31 |  |  |  | 82.31 | [5 empty] | 83.05 |  |  | 83.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.69 |  |  |  |  | 0.00
1991 |  |  |  | 5590.69 |  |  | 6684 |  |  |  | 846 | [10 empty] | 74.76 |  |  |  | 74.76 | [5 empty] | 75.44 |  |  | 76.30 |  |  |  | 1.23 |  | 0.93 | [8 empty] | 24.31 |  |  |  |  | 0.00
1992 |  |  |  | 5713.89 |  |  | 6780 |  |  |  | 846 | [10 empty] | 76.08 |  |  |  | 76.08 | [5 empty] | 76.89 |  |  | 77.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.92 |  |  |  |  | 0.00
1993 |  |  |  | 6619.24 |  |  | 7753 |  |  |  | 846 | [10 empty] | 88.43 |  |  |  | 88.43 | [5 empty] | 89.32 |  |  | 88.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.57 |  |  |  |  | 0.00
1994 |  |  |  | 5778.34 |  |  | 6762 |  |  |  | 846 | [10 empty] | 77.17 |  |  |  | 77.17 | [5 empty] | 77.97 |  |  | 77.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.83 |  |  |  |  | 0.00
1995 |  |  |  | 5780.32 |  |  | 6863 |  |  |  | 846 | [10 empty] | 77.28 |  |  |  | 77.28 | [5 empty] | 78.00 |  |  | 78.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.72 |  |  |  |  | 0.00
1996 |  |  |  | 5185.37 |  |  | 6157 |  |  |  | 846 | [10 empty] | 69.09 |  |  |  | 69.09 | [5 empty] | 69.78 |  |  | 70.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.91 |  |  |  |  | 0.00
1997 |  |  |  | 7216.68 |  |  | 8449 |  |  |  | 846 | [10 empty] | 96.40 |  |  |  | 96.40 | [5 empty] | 97.38 |  |  | 96.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.60 |  |  |  |  | 0.00
1998 |  |  |  | 5291.22 |  |  | 6311 |  |  |  | 846 | [10 empty] | 70.64 |  |  |  | 70.64 | [5 empty] | 71.40 |  |  | 72.04 |  |  |  | 4.67 |  | 3.46 | [8 empty] | 25.90 |  |  |  |  | 0.00
1999 |  |  |  | 6057.57 |  |  | 7082 |  |  |  | 846 | [10 empty] | 80.83 |  |  |  | 80.83 | [5 empty] | 81.74 |  |  | 80.84 |  |  |  | 3.06 |  | 2.55 | [8 empty] | 16.62 |  |  |  |  | 0.00
2000 |  |  |  | 5654.00 |  |  | 6609 |  |  |  | 846 | [10 empty] | 75.23 |  |  |  | 75.23 | [5 empty] | 76.08 |  |  | 75.24 |  |  |  | 9.23 |  | 7.65 | [8 empty] | 17.12 |  |  |  |  | 0.00
2001 |  |  |  | 7367.04 |  |  | 8614 |  |  |  | 846 | [10 empty] | 98.31 |  |  |  | 98.31 | [5 empty] | 99.41 |  |  | 98.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.69 |  |  |  |  | 0.00
2002 |  |  |  | 6323.03 |  |  | 7333 |  |  |  | 846 | [10 empty] | 83.68 |  |  |  | 83.68 | [5 empty] | 85.32 |  |  | 83.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.32 |  |  |  |  | 0.00
2003 |  |  |  | 6282.06 |  |  | 7278 |  |  |  | 846 | [10 empty] | 83.08 |  |  |  | 83.08 | [5 empty] | 84.77 |  |  | 83.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.92 |  |  |  |  | 0.00
2004 |  |  |  | 6080.79 |  |  | 7043 |  |  |  | 846 | [10 empty] | 80.15 |  |  |  | 80.15 | [5 empty] | 81.83 |  |  | 80.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.85 |  |  |  |  | 0.00
2005 |  |  |  | 7155.81 |  |  | 8305 |  |  |  | 846 | [10 empty] | 94.74 |  |  |  | 94.74 | [5 empty] | 96.56 |  |  | 94.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.26 |  |  |  |  | 0.00
2006 |  |  |  | 6436.58 |  |  | 7330 |  |  |  | 846 | [10 empty] | 82.92 |  |  |  | 82.92 | [5 empty] | 86.85 |  |  | 83.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.08 |  |  |  |  | 0.00
2007 |  |  |  | 5868.86 |  |  | 6660 |  |  |  | 846 | [10 empty] | 75.21 |  |  |  | 75.21 | [5 empty] | 79.19 |  |  | 76.03 |  |  |  | 0.00 |  | 8.05 | [8 empty] | 16.74 |  |  |  |  | 0.00
2008 |  |  |  | 5665.09 |  |  | 6396 |  |  |  | 846 | [10 empty] | 71.92 |  |  |  | 71.92 | [5 empty] | 76.23 |  |  | 72.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.08 |  |  |  |  | 0.00
2009 |  |  |  | 7880.10 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 106.33 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 4919.57 |  |  | 5571 |  |  |  | 846 | [10 empty] | 62.67 |  |  |  | 62.67 | [5 empty] | 66.38 |  |  | 63.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.33 |  |  |  |  | 0.00
2011 |  |  |  | 2823.75 |  |  | 3097 |  |  |  | 846 | [10 empty] | 35.32 |  |  |  | 35.32 | [5 empty] | 38.10 |  |  | 35.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 64.68 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 2893.82 |  |  | 3351 |  |  |  | 846 | [10 empty] | 36.84 |  |  |  | 36.84 | [5 empty] | 39.05 |  |  | 38.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 63.16 |  |  |  |  | 0.00
2016 |  |  |  | 6452.27 |  |  | 7188 |  |  |  | 846 | [10 empty] | 81.16 |  |  |  | 81.16 | [5 empty] | 86.83 |  |  | 81.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.84 |  |  |  |  | 0.00
2017 |  |  |  | 8007.73 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 108.05 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 5186.62 |  |  | 5756 |  |  |  | 846 | [10 empty] | 65.03 |  |  |  | 65.03 | [5 empty] | 69.99 |  |  | 65.71 |  |  |  | 0.00 |  | 5.10 | [8 empty] | 29.87 |  |  |  |  | 0.00
2019 |  |  |  | 6434.71 |  |  | 7058 |  |  |  | 846 | [10 empty] | 80.07 |  |  |  | 80.07 | [5 empty] | 86.83 |  |  | 80.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.93 |  |  |  |  | 0.00
2020 |  |  |  | 2552.25 |  |  | 2818 |  |  |  | 846 | [10 empty] | 31.58 |  |  |  | 31.58 | [5 empty] | 34.34 |  |  | 32.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 68.42 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 64
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 5966 | [14 empty] | 1482
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 990
Subtotal | [22 empty] | 5966 | [14 empty] | 2472 |  |  |  | 64
Total | [22 empty] | 5966 | [14 empty] | 2536
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 12
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
16. |  |  | Steam generation systems | [34 empty] | 19
31. |  |  | Turbine and auxiliaries | [34 empty] | 6
32. |  |  | Feedwater and Main Steam System | [34 empty] | 18
Total | [37 empty] | 63

## SENDAI-2
2020 Operating Experience
JP-37 | [8 empty] | SENDAI-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Owner | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-10-12
Thermal power | [12 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-04-05
Gross electrical power | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-11-28
Reference unit power (net) | [12 empty] | : |  |  | 846 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.22
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 49000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.07
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3197.98 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 39.82 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 39.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 60.18 %
Load Factor (LF) | [18 empty] | : | 43.03 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 40.28 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 5246 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 683.55 | 638.89 |  |  |  | 681.61 |  | 658.64 | [8 empty] | 420.81 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 114.47 |  |  | 3197.98
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 62.07 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 17.72 |  |  | 39.82
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 62.07 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 17.72 |  |  | 39.82
LF [%] |  |  |  |  | 108.60 | 108.50 |  |  |  | 108.29 |  | 108.13 | [8 empty] | 66.86 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 18.19 |  |  | 43.03
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 62.50 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 22.72 |  |  | 40.28
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.93 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 82.28 |  |  | 60.18
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 191241.98 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.04 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.03 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 72.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 27.68 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.02 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.71 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 2816.07 |  |  | 4327 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.22 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 5996.37 |  |  | 7112 |  |  |  | 846 | [10 empty] | 80.14 |  |  |  | 80.14 | [5 empty] | 80.91 |  |  | 81.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.86 |  |  |  |  | 0.00
1987 |  |  |  | 6080.60 |  |  | 7211 |  |  |  | 846 | [10 empty] | 81.18 |  |  |  | 81.18 | [5 empty] | 82.05 |  |  | 82.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.82 |  |  |  |  | 0.00
1988 |  |  |  | 7409.79 |  |  | 8665 |  |  |  | 846 | [10 empty] | 98.70 |  |  |  | 98.70 | [5 empty] | 99.71 |  |  | 98.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.30 |  |  |  |  | 0.00
1989 |  |  |  | 4999.37 |  |  | 5950 |  |  |  | 846 | [10 empty] | 66.84 |  |  |  | 66.84 | [5 empty] | 67.46 |  |  | 67.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.16 |  |  |  |  | 0.00
1990 |  |  |  | 6160.14 |  |  | 7309 |  |  |  | 846 | [10 empty] | 82.37 |  |  |  | 82.37 | [5 empty] | 83.12 |  |  | 83.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.63 |  |  |  |  | 0.00
1991 |  |  |  | 5665.26 |  |  | 6732 |  |  |  | 846 | [10 empty] | 75.72 |  |  |  | 75.72 | [5 empty] | 76.44 |  |  | 76.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.28 |  |  |  |  | 0.00
1992 |  |  |  | 7385.32 |  |  | 8639 |  |  |  | 846 | [10 empty] | 98.30 |  |  |  | 98.30 | [5 empty] | 99.38 |  |  | 98.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.70 |  |  |  |  | 0.00
1993 |  |  |  | 5821.98 |  |  | 6632 |  |  |  | 846 | [10 empty] | 77.69 |  |  |  | 77.69 | [5 empty] | 78.56 |  |  | 75.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.31 |  |  |  |  | 0.00
1994 |  |  |  | 5568.78 |  |  | 6557 |  |  |  | 846 | [10 empty] | 74.30 |  |  |  | 74.30 | [5 empty] | 75.14 |  |  | 74.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.70 |  |  |  |  | 0.00
1995 |  |  |  | 5658.40 |  |  | 6709 |  |  |  | 846 | [10 empty] | 75.50 |  |  |  | 75.50 | [5 empty] | 76.35 |  |  | 76.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.50 |  |  |  |  | 0.00
1996 |  |  |  | 7359.31 |  |  | 8617 |  |  |  | 846 | [10 empty] | 98.05 |  |  |  | 98.05 | [5 empty] | 99.03 |  |  | 98.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.95 |  |  |  |  | 0.00
1997 |  |  |  | 5950.29 |  |  | 7034 |  |  |  | 846 | [10 empty] | 79.44 |  |  |  | 79.44 | [5 empty] | 80.29 |  |  | 80.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.56 |  |  |  |  | 0.00
1998 |  |  |  | 5899.10 |  |  | 6973 |  |  |  | 846 | [10 empty] | 78.72 |  |  |  | 78.72 | [5 empty] | 79.60 |  |  | 79.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.28 |  |  |  |  | 0.00
1999 |  |  |  | 5658.29 |  |  | 6612 |  |  |  | 846 | [10 empty] | 75.47 |  |  |  | 75.47 | [5 empty] | 76.35 |  |  | 75.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.53 |  |  |  |  | 0.00
2000 |  |  |  | 7370.17 |  |  | 8614 |  |  |  | 846 | [10 empty] | 98.04 |  |  |  | 98.04 | [5 empty] | 99.18 |  |  | 98.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.96 |  |  |  |  | 0.00
2001 |  |  |  | 6210.15 |  |  | 7260 |  |  |  | 846 | [10 empty] | 82.86 |  |  |  | 82.86 | [5 empty] | 83.80 |  |  | 82.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.14 |  |  |  |  | 0.00
2002 |  |  |  | 6255.46 |  |  | 7257 |  |  |  | 846 | [10 empty] | 82.83 |  |  |  | 82.83 | [5 empty] | 84.41 |  |  | 82.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.17 |  |  |  |  | 0.00
2003 |  |  |  | 6348.77 |  |  | 7315 |  |  |  | 846 | [10 empty] | 83.38 |  |  |  | 83.38 | [5 empty] | 85.67 |  |  | 83.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.62 |  |  |  |  | 0.00
2004 |  |  |  | 6762.55 |  |  | 7774 |  |  |  | 846 | [10 empty] | 88.48 |  |  |  | 88.48 | [5 empty] | 91.00 |  |  | 88.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.52 |  |  |  |  | 0.00
2005 |  |  |  | 6752.80 |  |  | 7895 |  |  |  | 846 | [10 empty] | 88.94 |  |  |  | 88.94 | [5 empty] | 91.12 |  |  | 90.13 |  |  |  | 1.17 |  | 1.05 | [8 empty] | 10.01 |  |  |  |  | 0.00
2006 |  |  |  | 6464.16 |  |  | 7548 |  |  |  | 846 | [10 empty] | 85.35 |  |  |  | 85.35 | [5 empty] | 87.22 |  |  | 86.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.65 |  |  |  |  | 0.00
2007 |  |  |  | 5989.31 |  |  | 6996 |  |  |  | 846 | [10 empty] | 79.05 |  |  |  | 79.05 | [5 empty] | 80.82 |  |  | 79.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.95 |  |  |  |  | 0.00
2008 |  |  |  | 6824.28 |  |  | 7897 |  |  |  | 846 | [10 empty] | 89.86 |  |  |  | 89.86 | [5 empty] | 91.83 |  |  | 89.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.14 |  |  |  |  | 0.00
2009 |  |  |  | 6320.24 |  |  | 7355 |  |  |  | 846 | [10 empty] | 83.19 |  |  |  | 83.19 | [5 empty] | 85.28 |  |  | 83.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.81 |  |  |  |  | 0.00
2010 |  |  |  | 5767.52 |  |  | 6630 |  |  |  | 846 | [10 empty] | 74.78 |  |  |  | 74.78 | [5 empty] | 77.82 |  |  | 75.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.22 |  |  |  |  | 0.00
2011 |  |  |  | 5216.82 |  |  | 5833 |  |  |  | 846 | [10 empty] | 66.55 |  |  |  | 66.55 | [5 empty] | 70.39 |  |  | 66.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.45 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 1452.66 |  |  | 1729 |  |  |  | 846 | [10 empty] | 18.63 |  |  |  | 18.63 | [5 empty] | 19.60 |  |  | 19.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 81.37 |  |  |  |  | 0.00
2016 |  |  |  | 7468.59 |  |  | 8401 |  |  |  | 846 | [10 empty] | 95.60 |  |  |  | 95.60 | [5 empty] | 100.50 |  |  | 95.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.40 |  |  |  |  | 0.00
2017 |  |  |  | 6554.16 |  |  | 7401 |  |  |  | 846 | [10 empty] | 83.87 |  |  |  | 83.87 | [5 empty] | 88.44 |  |  | 84.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.13 |  |  |  |  | 0.00
2018 |  |  |  | 5016.93 |  |  | 5618 |  |  |  | 846 | [10 empty] | 63.46 |  |  |  | 63.46 | [5 empty] | 67.70 |  |  | 64.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.54 |  |  |  |  | 0.00
2019 |  |  |  | 6381.17 |  |  | 7082 |  |  |  | 846 | [10 empty] | 80.38 |  |  |  | 80.38 | [5 empty] | 86.10 |  |  | 80.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.62 |  |  |  |  | 0.00
2020 |  |  |  | 3197.98 |  |  | 3538 |  |  |  | 846 | [10 empty] | 39.82 |  |  |  | 39.82 | [5 empty] | 43.03 |  |  | 40.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 60.18 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 3
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 5246 | [14 empty] | 1441
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 977
Subtotal | [22 empty] | 5246 | [14 empty] | 2418 |  |  |  | 3
Total | [22 empty] | 5246 | [14 empty] | 2421
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
Total | [37 empty] | 3

## SHIKA-1
2020 Operating Experience
JP-48 | [8 empty] | SHIKA-1 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | HOKURIKU (HOKURIKU ELECTRIC POWER CO.)
Owner | [7 empty] | : | HOKURIKU (HOKURIKU ELECTRIC POWER CO.)
Reactor Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Turbine Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1989-07-01
Thermal power | [12 empty] | : |  |  | 1593 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-01-12
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-07-30
Reference unit power (net) | [12 empty] | : |  |  | 505 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6.93
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.427
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 15 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.30 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 368 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 56333 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.15 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 45.67 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 45.67 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 50.8 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 45.62 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 45.58 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 2834.34 |  |  | 6576 |  |  |  | 505 | [10 empty] | 99.72 |  |  |  | 99.72 | [5 empty] | 99.82 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.28 |  |  |  |  | 0.00
1994 |  |  |  | 3312.39 |  |  | 6584 |  |  |  | 505 | [10 empty] | 75.02 |  |  |  | 75.02 | [5 empty] | 74.88 |  |  | 75.16 |  |  |  | 5.32 |  | 4.21 | [8 empty] | 20.77 |  |  |  |  | 0.00
1995 |  |  |  | 3497.23 |  |  | 6974 |  |  |  | 505 | [10 empty] | 79.05 |  |  |  | 79.05 | [5 empty] | 79.05 |  |  | 79.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.95 |  |  |  |  | 0.00
1996 |  |  |  | 3454.70 |  |  | 6848 |  |  |  | 505 | [10 empty] | 77.91 |  |  |  | 77.91 | [5 empty] | 77.88 |  |  | 77.96 |  |  |  | 4.07 |  | 3.31 | [8 empty] | 18.78 |  |  |  |  | 0.00
1997 |  |  |  | 4431.84 |  |  | 8760 |  |  |  | 505 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 100.18 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
1998 |  |  |  | 3530.63 |  |  | 7047 |  |  |  | 505 | [10 empty] | 80.04 |  |  |  | 80.04 | [5 empty] | 79.81 |  |  | 80.45 |  |  |  | 2.22 |  | 1.82 | [8 empty] | 18.15 |  |  |  |  | 0.00
1999 |  |  |  | 3325.67 |  |  | 6607 |  |  |  | 505 | [10 empty] | 75.42 |  |  |  | 75.42 | [5 empty] | 75.18 |  |  | 75.42 |  |  |  | 4.34 |  | 3.42 | [8 empty] | 21.16 |  |  |  |  | 0.00
2000 |  |  |  | 3763.08 |  |  | 7462 |  |  |  | 505 | [10 empty] | 84.89 |  |  |  | 84.89 | [5 empty] | 84.83 |  |  | 84.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.11 |  |  |  |  | 0.00
2001 |  |  |  | 4427.41 |  |  | 8760 |  |  |  | 505 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 100.08 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.00
2002 |  |  |  | 3537.07 |  |  | 7010 |  |  |  | 505 | [10 empty] | 80.01 |  |  |  | 80.01 | [5 empty] | 79.96 |  |  | 80.02 |  |  |  | 4.02 |  | 3.35 | [8 empty] | 16.64 |  |  |  |  | 0.00
2003 |  |  |  | 1523.80 |  |  | 3029 |  |  |  | 505 | [10 empty] | 34.56 |  |  |  | 34.56 | [5 empty] | 34.45 |  |  | 34.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 65.44 |  |  |  |  | 0.00
2004 |  |  |  | 3534.94 |  |  | 6958 |  |  |  | 505 | [10 empty] | 78.75 |  |  |  | 78.75 | [5 empty] | 79.69 |  |  | 79.21 |  |  |  | 0.88 |  | 0.70 | [8 empty] | 20.55 |  |  |  |  | 0.00
2005 |  |  |  | 4203.80 |  |  | 8226 |  |  |  | 505 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 95.03 |  |  | 93.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2006 |  |  |  | 2908.09 |  |  | 5777 |  |  |  | 505 | [10 empty] | 65.34 |  |  |  | 65.34 | [5 empty] | 65.74 |  |  | 65.95 |  |  |  | 7.22 |  | 5.09 | [8 empty] | 29.57 |  |  |  |  | 0.00
2007 |  |  |  | 908.38 |  |  | 1778 |  |  |  | 505 | [10 empty] | 20.23 |  |  |  | 20.23 | [5 empty] | 20.53 |  |  | 20.30 |  |  |  | 26.87 |  | 7.43 | [8 empty] | 72.33 |  |  |  |  | 0.00
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 505 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2009 |  |  |  | 3247.93 |  |  | 6367 |  |  |  | 505 | [10 empty] | 72.28 |  |  |  | 72.28 | [5 empty] | 73.42 |  |  | 72.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.72 |  |  |  |  | 0.00
2010 |  |  |  | 3191.56 |  |  | 6287 |  |  |  | 505 | [10 empty] | 71.09 |  |  |  | 71.09 | [5 empty] | 72.15 |  |  | 71.77 |  |  |  | 8.51 |  | 6.96 | [8 empty] | 21.95 |  |  |  |  | 0.00
2011 |  |  |  | 729.57 |  |  | 1416 |  |  |  | 505 | [10 empty] | 16.11 |  |  |  | 16.11 | [5 empty] | 16.49 |  |  | 16.16 |  |  |  | 79.00 |  | 60.60 | [8 empty] | 23.29 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 505 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 505 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 505 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 505 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 505 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 505 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 505 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 505 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 505 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1993 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 285
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1186
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 325
E. |  | Testing of plant systems or components | [35 empty] | 76
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 2928
H. |  | Nuclear regulatory requirements | [39 empty] | 25
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 23
Subtotal | [22 empty] | 8784 | [14 empty] | 4515 |  |  |  | 310 | [11 empty] | 23
Total | [22 empty] | 8784 | [14 empty] | 4848
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1993 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 243
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 16
42. |  |  | Electrical Power Supply Systems | [34 empty] | 11
Total | [37 empty] | 287
Highlights (2020)
Implementation of safety mesures for considering the Accident of Fukushima Dai-ichi and Dai-ni Nuclear Power Stations.

## SHIKA-2
2020 Operating Experience
JP-59 | [8 empty] | SHIKA-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | HOKURIKU (HOKURIKU ELECTRIC POWER CO.)
Owner | [7 empty] | : | HOKURIKU (HOKURIKU ELECTRIC POWER CO.)
Reactor Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Turbine Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / ABWR | [11 empty] | Construction Date | [15 empty] | : |  |  | 2001-08-20
Thermal power | [12 empty] | : |  |  | 3926 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2005-07-04
Gross electrical power | [12 empty] | : |  |  | 1206 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2006-03-15
Reference unit power (net) | [12 empty] | : |  |  | 1108 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 15 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.310
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 15 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 5.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.69
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 872 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [13 empty] | : |  |  | 205 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 29296 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 43.46 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 17.38 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 14.32 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 17.39 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 68.3 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 18.02 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 17.67 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2006 |  |  |  | 4547.85 |  |  | 3539 |  |  |  | 1304 | [10 empty] | 41.15 |  |  |  | 41.15 | [5 empty] | 41.29 |  |  | 41.26 |  |  |  | 58.85 |  | 58.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1304 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 6381.93 |  |  | 5610 |  |  |  | 1108 | [10 empty] | 58.53 |  |  |  | 58.53 | [5 empty] | 61.08 |  |  | 63.87 |  |  |  | 0.00 |  | 13.53 | [8 empty] | 27.93 |  |  |  |  | 0.00
2009 |  |  |  | 5647.06 |  |  | 5044 |  |  |  | 1108 | [10 empty] | 55.95 |  |  |  | 55.95 | [5 empty] | 58.18 |  |  | 57.58 |  |  |  | 20.80 |  | 14.69 | [8 empty] | 29.36 |  |  |  |  | 0.00
2010 |  |  |  | 9279.20 |  |  | 8038 |  |  |  | 1108 | [10 empty] | 91.50 |  |  |  | 91.50 | [5 empty] | 95.60 |  |  | 91.76 |  |  |  | 8.49 |  | 8.49 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 1408.12 |  |  | 1263 |  |  |  | 1108 | [10 empty] | 14.03 |  |  |  | 14.03 | [5 empty] | 14.51 |  |  | 14.42 |  |  |  | 25.48 |  | 4.80 | [8 empty] | 81.17 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2006 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 217
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 478
E. |  | Testing of plant systems or components | [35 empty] | 61
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 5640
H. |  | Nuclear regulatory requirements | [39 empty] | 881
L. |  | Human factor related | [39 empty] | 2
Subtotal | [22 empty] | 8784 | [14 empty] | 6179 |  |  |  | 1100
Total | [22 empty] | 8784 | [14 empty] | 7279
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2006 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 26
31. |  |  | Turbine and auxiliaries | [34 empty] | 934
42. |  |  | Electrical Power Supply Systems | [34 empty] | 126
Total | [37 empty] | 1086
Highlights (2020)
Implementation of safety measures for considering the Accident of Fukushima Dai-ichi and Dai-ni Nuclear Power Stations.

## SHIMANE-2
2020 Operating Experience
JP-41 | [8 empty] | SHIMANE-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CHUGOKU (THE CHUGOKU ELECTRIC POWER CO., INC.)
Owner | [7 empty] | : | CHUGOKU (THE CHUGOKU ELECTRIC POWER CO., INC.)
Reactor Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Turbine Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-02-02
Thermal power | [12 empty] | : |  |  | 2436 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-07-11
Gross electrical power | [12 empty] | : |  |  | 820 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-02-10
Reference unit power (net) | [12 empty] | : |  |  | 789 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6.93
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.427
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.7 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 14 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.07 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 44.0 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 137 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 129177 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 57.84 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.61 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 57.86 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 39.53 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 57.76 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 58.08 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 5852.06 |  |  | 7485 |  |  |  | 790 | [10 empty] | 89.20 |  |  |  | 89.20 | [5 empty] | 88.79 |  |  | 89.56 |  |  |  | 10.80 |  | 10.80 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 5123.51 |  |  | 6592 |  |  |  | 790 | [10 empty] | 74.03 |  |  |  | 74.03 | [5 empty] | 74.03 |  |  | 75.25 |  |  |  | 7.01 |  | 5.58 | [8 empty] | 20.38 |  |  |  |  | 0.00
1991 |  |  |  | 5544.50 |  |  | 7121 |  |  |  | 790 | [10 empty] | 80.12 |  |  |  | 80.12 | [5 empty] | 80.12 |  |  | 81.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.88 |  |  |  |  | 0.00
1992 |  |  |  | 5516.14 |  |  | 7072 |  |  |  | 790 | [10 empty] | 79.69 |  |  |  | 79.69 | [5 empty] | 79.49 |  |  | 80.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.31 |  |  |  |  | 0.00
1993 |  |  |  | 6756.90 |  |  | 8592 |  |  |  | 790 | [10 empty] | 97.78 |  |  |  | 97.78 | [5 empty] | 97.64 |  |  | 98.08 |  |  |  | 1.86 |  | 1.85 | [8 empty] | 0.37 |  |  |  |  | 0.00
1994 |  |  |  | 5547.27 |  |  | 7071 |  |  |  | 790 | [10 empty] | 80.55 |  |  |  | 80.62 | [5 empty] | 80.16 |  |  | 80.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.38 |  |  |  |  | 0.07
1995 |  |  |  | 5363.61 |  |  | 6888 |  |  |  | 790 | [10 empty] | 77.85 |  |  |  | 77.86 | [5 empty] | 77.50 |  |  | 78.63 |  |  |  | 1.86 |  | 1.48 | [8 empty] | 20.66 |  |  |  |  | 0.01
1996 |  |  |  | 5583.69 |  |  | 7166 |  |  |  | 790 | [10 empty] | 80.83 |  |  |  | 80.83 | [5 empty] | 80.46 |  |  | 81.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.17 |  |  |  |  | 0.00
1997 |  |  |  | 6903.19 |  |  | 8760 |  |  |  | 789 | [10 empty] | 99.97 |  |  |  | 99.98 | [5 empty] | 99.88 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.01 |  |  |  |  | 0.00
1998 |  |  |  | 5962.47 |  |  | 7600 |  |  |  | 789 | [10 empty] | 86.46 |  |  |  | 86.50 | [5 empty] | 86.27 |  |  | 86.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.50 |  |  |  |  | 0.03
1999 |  |  |  | 5758.72 |  |  | 7319 |  |  |  | 789 | [10 empty] | 83.50 |  |  |  | 83.50 | [5 empty] | 83.32 |  |  | 83.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.50 |  |  |  |  | 0.00
2000 |  |  |  | 6083.96 |  |  | 7747 |  |  |  | 789 | [10 empty] | 88.12 |  |  |  | 88.17 | [5 empty] | 87.78 |  |  | 88.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.83 |  |  |  |  | 0.05
2001 |  |  |  | 6901.04 |  |  | 8760 |  |  |  | 789 | [10 empty] | 99.95 |  |  |  | 99.98 | [5 empty] | 99.85 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.03
2002 |  |  |  | 6055.09 |  |  | 7678 |  |  |  | 789 | [10 empty] | 87.61 |  |  |  | 87.64 | [5 empty] | 87.61 |  |  | 87.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.36 |  |  |  |  | 0.03
2003 |  |  |  | 4836.24 |  |  | 6133 |  |  |  | 789 | [10 empty] | 70.00 |  |  |  | 70.06 | [5 empty] | 69.97 |  |  | 70.01 |  |  |  | 0.00 |  | 6.82 | [8 empty] | 23.13 |  |  |  |  | 0.05
2004 |  |  |  | 4097.56 |  |  | 5202 |  |  |  | 789 | [10 empty] | 58.97 |  |  |  | 58.97 | [5 empty] | 59.12 |  |  | 59.22 |  |  |  | 13.59 |  | 10.64 | [8 empty] | 30.40 |  |  |  |  | 0.00
2005 |  |  |  | 5907.46 |  |  | 7544 |  |  |  | 789 | [10 empty] | 85.36 |  |  |  | 85.56 | [5 empty] | 85.47 |  |  | 86.12 |  |  |  | 4.96 |  | 4.46 | [8 empty] | 9.97 |  |  |  |  | 0.21
2006 |  |  |  | 5085.40 |  |  | 6469 |  |  |  | 789 | [10 empty] | 73.61 |  |  |  | 73.61 | [5 empty] | 73.58 |  |  | 73.85 |  |  |  | 0.00 |  | 1.77 | [8 empty] | 24.62 |  |  |  |  | 0.00
2007 |  |  |  | 5462.01 |  |  | 6970 |  |  |  | 789 | [10 empty] | 79.52 |  |  |  | 79.52 | [5 empty] | 79.03 |  |  | 79.57 |  |  |  | 0.00 |  | 0.29 | [8 empty] | 20.20 |  |  |  |  | 0.00
2008 |  |  |  | 4703.60 |  |  | 6001 |  |  |  | 789 | [10 empty] | 68.25 |  |  |  | 68.25 | [5 empty] | 67.87 |  |  | 68.32 |  |  |  | 0.00 |  | 1.37 | [8 empty] | 30.38 |  |  |  |  | 0.00
2009 |  |  |  | 5373.85 |  |  | 6799 |  |  |  | 789 | [10 empty] | 77.46 |  |  |  | 77.46 | [5 empty] | 77.75 |  |  | 77.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.54 |  |  |  |  | 0.00
2010 |  |  |  | 1924.42 |  |  | 2438 |  |  |  | 789 | [10 empty] | 27.61 |  |  |  | 27.61 | [5 empty] | 27.84 |  |  | 27.83 |  |  |  | 0.00 |  | 39.32 | [8 empty] | 33.07 |  |  |  |  | 0.00
2011 |  |  |  | 6921.96 |  |  | 8760 |  |  |  | 789 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 100.15 |  |  | 100.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.01 |  |  |  |  | 0.00
2012 |  |  |  | 491.69 |  |  | 625 |  |  |  | 789 | [10 empty] | 7.06 |  |  |  | 7.06 | [5 empty] | 7.09 |  |  | 7.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 92.94 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 789 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 789 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 789 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 789 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 789 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 789 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 789 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 789 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 95
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 995 |  |  |  | 5
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 4
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 2453
H. |  | Nuclear regulatory requirements | [39 empty] | 109
L. |  | Human factor related | [39 empty] | 4
Z. |  | Other | [39 empty] | 19
Subtotal | [22 empty] | 8784 | [14 empty] | 3452 |  |  |  | 232
Total | [22 empty] | 8784 | [14 empty] | 3684
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 30
12. |  |  | Reactor I&C Systems | [34 empty] | 3
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 50
Total | [37 empty] | 94
Highlights (2020)
Highlights for the year:Implementaion of emergency safety measures for considering the Accident of Fukushima Dai-ichi and Dai-ni Nuclear Power Station

## TAKAHAMA-1
2020 Operating Experience
JP-8 | [8 empty] | TAKAHAMA-1 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | WH/MHI (WESTINGHOUSE ELECTRIC CORPORATION / MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-04-25
Thermal power | [12 empty] | : |  |  | 2440 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-03-27
Gross electrical power | [12 empty] | : |  |  | 826 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-11-14
Reference unit power (net) | [12 empty] | : |  |  | 780 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.24
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.0 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.64 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 174314 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.4 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 54.48 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.78 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 54.5 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 41.71 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 55.26 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 55.41 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 2660.40 |  |  | 4392 |  |  |  | 780 | [10 empty] | 94.03 |  |  |  | 94.03 | [5 empty] | 92.81 |  |  | 93.99 |  |  |  | 5.08 |  | 5.03 | [8 empty] | 0.93 |  |  |  |  | 0.00
1975 |  |  |  | 4980.40 |  |  | 6938 |  |  |  | 780 | [10 empty] | 72.81 |  |  |  | 72.81 | [5 empty] | 72.89 |  |  | 79.20 |  |  |  | 12.81 |  | 10.70 | [8 empty] | 16.49 |  |  |  |  | 0.00
1976 |  |  |  | 3170.10 |  |  | 4900 |  |  |  | 780 | [10 empty] | 46.19 |  |  |  | 46.19 | [5 empty] | 46.27 |  |  | 55.78 |  |  |  | 19.20 |  | 10.98 | [8 empty] | 42.83 |  |  |  |  | 0.00
1977 |  |  |  | 383.80 |  |  | 569 |  |  |  | 780 | [10 empty] | 5.61 |  |  |  | 5.61 | [5 empty] | 5.62 |  |  | 6.50 |  |  |  | 94.39 |  | 94.39 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 2762.50 |  |  | 4088 |  |  |  | 780 | [10 empty] | 40.42 |  |  |  | 40.42 | [5 empty] | 40.43 |  |  | 46.67 |  |  |  | 5.59 |  | 2.39 | [8 empty] | 57.18 |  |  |  |  | 0.00
1979 |  |  |  | 1648.90 |  |  | 2269 |  |  |  | 780 | [10 empty] | 24.14 |  |  |  | 24.14 | [5 empty] | 24.13 |  |  | 25.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 75.86 |  |  |  |  | 0.00
1980 |  |  |  | 2705.10 |  |  | 3604 |  |  |  | 780 | [10 empty] | 39.42 |  |  |  | 39.42 | [5 empty] | 39.48 |  |  | 41.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 60.58 |  |  |  |  | 0.00
1981 |  |  |  | 3990.20 |  |  | 5180 |  |  |  | 780 | [10 empty] | 58.33 |  |  |  | 58.33 | [5 empty] | 58.40 |  |  | 59.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 41.67 |  |  |  |  | 0.00
1982 |  |  |  | 3872.10 |  |  | 5085 |  |  |  | 780 | [10 empty] | 56.50 |  |  |  | 56.50 | [5 empty] | 56.67 |  |  | 58.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 43.50 |  |  |  |  | 0.00
1983 |  |  |  | 5716.20 |  |  | 7403 |  |  |  | 780 | [10 empty] | 83.72 |  |  |  | 83.72 | [5 empty] | 83.66 |  |  | 84.51 |  |  |  | 0.65 |  | 0.54 | [8 empty] | 15.74 |  |  |  |  | 0.00
1984 |  |  |  | 3537.44 |  |  | 4586 |  |  |  | 780 | [10 empty] | 51.41 |  |  |  | 51.41 | [5 empty] | 51.63 |  |  | 52.21 |  |  |  | 0.54 |  | 0.28 | [8 empty] | 48.31 |  |  |  |  | 0.00
1985 |  |  |  | 5000.77 |  |  | 6473 |  |  |  | 780 | [10 empty] | 72.84 |  |  |  | 72.84 | [5 empty] | 73.19 |  |  | 73.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.16 |  |  |  |  | 0.00
1986 |  |  |  | 5070.31 |  |  | 6507 |  |  |  | 780 | [10 empty] | 73.86 |  |  |  | 73.86 | [5 empty] | 74.21 |  |  | 74.28 |  |  |  | 1.25 |  | 0.94 | [8 empty] | 25.21 |  |  |  |  | 0.00
1987 |  |  |  | 4701.39 |  |  | 6148 |  |  |  | 780 | [10 empty] | 70.18 |  |  |  | 70.18 | [5 empty] | 68.81 |  |  | 70.18 |  |  |  | 18.82 |  | 16.27 | [8 empty] | 13.55 |  |  |  |  | 0.00
1988 |  |  |  | 4147.14 |  |  | 5351 |  |  |  | 780 | [10 empty] | 60.92 |  |  |  | 60.92 | [5 empty] | 60.53 |  |  | 60.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 39.08 |  |  |  |  | 0.00
1989 |  |  |  | 4877.26 |  |  | 6311 |  |  |  | 780 | [10 empty] | 72.04 |  |  |  | 72.04 | [5 empty] | 71.38 |  |  | 72.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.96 |  |  |  |  | 0.00
1990 |  |  |  | 6265.50 |  |  | 8002 |  |  |  | 780 | [10 empty] | 90.76 |  |  |  | 90.76 | [5 empty] | 91.70 |  |  | 91.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.24 |  |  |  |  | 0.00
1991 |  |  |  | 4795.05 |  |  | 6202 |  |  |  | 780 | [10 empty] | 68.25 |  |  |  | 68.25 | [5 empty] | 70.18 |  |  | 70.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.75 |  |  |  |  | 0.00
1992 |  |  |  | 4644.96 |  |  | 6051 |  |  |  | 780 | [10 empty] | 67.62 |  |  |  | 67.62 | [5 empty] | 67.79 |  |  | 68.89 |  |  |  | 1.28 |  | 0.88 | [8 empty] | 31.50 |  |  |  |  | 0.00
1993 |  |  |  | 3299.67 |  |  | 4458 |  |  |  | 780 | [10 empty] | 48.36 |  |  |  | 48.36 | [5 empty] | 48.29 |  |  | 50.89 |  |  |  | 30.51 |  | 21.23 | [8 empty] | 30.41 |  |  |  |  | 0.00
1994 |  |  |  | 4024.04 |  |  | 5146 |  |  |  | 780 | [10 empty] | 58.84 |  |  |  | 58.84 | [5 empty] | 58.89 |  |  | 58.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 41.16 |  |  |  |  | 0.00
1995 |  |  |  | 6585.13 |  |  | 8485 |  |  |  | 780 | [10 empty] | 96.05 |  |  |  | 96.05 | [5 empty] | 96.38 |  |  | 96.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.95 |  |  |  |  | 0.00
1996 |  |  |  | 3358.80 |  |  | 4331 |  |  |  | 780 | [10 empty] | 48.81 |  |  |  | 48.82 | [5 empty] | 49.02 |  |  | 49.31 |  |  |  | 8.78 |  | 4.70 | [8 empty] | 46.48 |  |  |  |  | 0.01
1997 |  |  |  | 4674.40 |  |  | 6000 |  |  |  | 780 | [10 empty] | 68.10 |  |  |  | 68.10 | [5 empty] | 68.41 |  |  | 68.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.90 |  |  |  |  | 0.00
1998 |  |  |  | 6856.82 |  |  | 8760 |  |  |  | 780 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.35 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1999 |  |  |  | 5704.24 |  |  | 7291 |  |  |  | 780 | [10 empty] | 83.22 |  |  |  | 84.30 | [5 empty] | 83.48 |  |  | 83.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.70 |  |  |  |  | 1.08
2000 |  |  |  | 6008.07 |  |  | 7716 |  |  |  | 780 | [10 empty] | 87.42 |  |  |  | 87.42 | [5 empty] | 87.69 |  |  | 87.84 |  |  |  | 0.47 |  | 0.41 | [8 empty] | 12.17 |  |  |  |  | 0.00
2001 |  |  |  | 6005.80 |  |  | 7731 |  |  |  | 780 | [10 empty] | 87.62 |  |  |  | 87.62 | [5 empty] | 87.90 |  |  | 88.25 |  |  |  | 0.70 |  | 0.62 | [8 empty] | 11.76 |  |  |  |  | 0.00
2002 |  |  |  | 6056.31 |  |  | 7749 |  |  |  | 780 | [10 empty] | 88.44 |  |  |  | 88.44 | [5 empty] | 88.64 |  |  | 88.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.56 |  |  |  |  | 0.00
2003 |  |  |  | 6247.16 |  |  | 7637 |  |  |  | 780 | [10 empty] | 87.17 |  |  |  | 87.17 | [5 empty] | 91.43 |  |  | 87.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.83 |  |  |  |  | 0.00
2004 |  |  |  | 5539.92 |  |  | 6785 |  |  |  | 780 | [10 empty] | 77.21 |  |  |  | 77.21 | [5 empty] | 80.86 |  |  | 77.24 |  |  |  | 4.89 |  | 3.97 | [8 empty] | 18.81 |  |  |  |  | 0.00
2005 |  |  |  | 6222.49 |  |  | 7659 |  |  |  | 780 | [10 empty] | 87.07 |  |  |  | 87.07 | [5 empty] | 91.07 |  |  | 87.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.93 |  |  |  |  | 0.00
2006 |  |  |  | 6347.13 |  |  | 7811 |  |  |  | 780 | [10 empty] | 89.16 |  |  |  | 89.16 | [5 empty] | 92.89 |  |  | 89.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.84 |  |  |  |  | 0.00
2007 |  |  |  | 6012.94 |  |  | 7399 |  |  |  | 780 | [10 empty] | 84.15 |  |  |  | 84.15 | [5 empty] | 88.00 |  |  | 84.46 |  |  |  | 0.00 |  | 2.66 | [8 empty] | 13.19 |  |  |  |  | 0.00
2008 |  |  |  | 4935.75 |  |  | 6077 |  |  |  | 780 | [10 empty] | 68.84 |  |  |  | 68.84 | [5 empty] | 72.04 |  |  | 69.18 |  |  |  | 4.11 |  | 2.95 | [8 empty] | 28.21 |  |  |  |  | 0.00
2009 |  |  |  | 5870.09 |  |  | 7193 |  |  |  | 780 | [10 empty] | 81.73 |  |  |  | 81.73 | [5 empty] | 85.91 |  |  | 82.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.27 |  |  |  |  | 0.00
2010 |  |  |  | 7193.46 |  |  | 8760 |  |  |  | 780 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 105.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2011 |  |  |  | 183.43 |  |  | 226 |  |  |  | 780 | [10 empty] | 2.53 |  |  |  | 2.53 | [5 empty] | 2.68 |  |  | 2.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 97.47 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 297
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1561
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 154
E. |  | Testing of plant systems or components | [35 empty] | 0
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 39
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 1855
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 1
Z. |  | Other | [39 empty] | 8
Subtotal | [22 empty] | 8784 | [14 empty] | 3609 |  |  |  | 306 | [11 empty] | 2
Total | [22 empty] | 8784 | [14 empty] | 3917
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 5
15. |  |  | Reactor Cooling Systems | [34 empty] | 75
16. |  |  | Steam generation systems | [34 empty] | 175
31. |  |  | Turbine and auxiliaries | [34 empty] | 20
32. |  |  | Feedwater and Main Steam System | [34 empty] | 19
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 301

## TAKAHAMA-2
2020 Operating Experience
JP-13 | [8 empty] | TAKAHAMA-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-03-09
Thermal power | [12 empty] | : |  |  | 2440 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-01-17
Gross electrical power | [12 empty] | : |  |  | 826 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-11-14
Reference unit power (net) | [12 empty] | : |  |  | 780 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.24
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.0 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.64 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 172658 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.67 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 54.89 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 54.97 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 42.03 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 55.95 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.08 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 56.06 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 3168.50 |  |  | 5532 |  |  |  | 780 | [10 empty] | 99.55 |  |  |  | 99.55 | [5 empty] | 100.44 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.45 |  |  |  |  | 0.00
1976 |  |  |  | 3728.80 |  |  | 6214 |  |  |  | 780 | [10 empty] | 54.17 |  |  |  | 54.17 | [5 empty] | 54.42 |  |  | 70.74 |  |  |  | 23.83 |  | 16.94 | [8 empty] | 28.89 |  |  |  |  | 0.00
1977 |  |  |  | 4742.00 |  |  | 6429 |  |  |  | 780 | [10 empty] | 69.40 |  |  |  | 69.40 | [5 empty] | 69.40 |  |  | 73.39 |  |  |  | 0.11 |  | 0.08 | [8 empty] | 30.52 |  |  |  |  | 0.00
1978 |  |  |  | 4170.30 |  |  | 5751 |  |  |  | 780 | [10 empty] | 61.04 |  |  |  | 61.04 | [5 empty] | 61.03 |  |  | 65.65 |  |  |  | 0.59 |  | 0.37 | [8 empty] | 38.59 |  |  |  |  | 0.00
1979 |  |  |  | 1281.00 |  |  | 1826 |  |  |  | 780 | [10 empty] | 18.75 |  |  |  | 18.75 | [5 empty] | 18.75 |  |  | 20.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 81.25 |  |  |  |  | 0.00
1980 |  |  |  | 5751.10 |  |  | 7450 |  |  |  | 780 | [10 empty] | 83.72 |  |  |  | 83.72 | [5 empty] | 83.94 |  |  | 84.81 |  |  |  | 0.92 |  | 0.78 | [8 empty] | 15.51 |  |  |  |  | 0.00
1981 |  |  |  | 4763.20 |  |  | 6198 |  |  |  | 780 | [10 empty] | 69.55 |  |  |  | 69.55 | [5 empty] | 69.71 |  |  | 70.75 |  |  |  | 0.30 |  | 0.21 | [8 empty] | 30.23 |  |  |  |  | 0.00
1982 |  |  |  | 4133.90 |  |  | 5407 |  |  |  | 780 | [10 empty] | 60.26 |  |  |  | 60.26 | [5 empty] | 60.50 |  |  | 61.72 |  |  |  | 0.62 |  | 0.37 | [8 empty] | 39.36 |  |  |  |  | 0.00
1983 |  |  |  | 3549.40 |  |  | 4645 |  |  |  | 780 | [10 empty] | 51.74 |  |  |  | 51.74 | [5 empty] | 51.95 |  |  | 53.03 |  |  |  | 0.80 |  | 0.42 | [8 empty] | 47.84 |  |  |  |  | 0.00
1984 |  |  |  | 4503.14 |  |  | 5746 |  |  |  | 780 | [10 empty] | 65.38 |  |  |  | 65.38 | [5 empty] | 65.72 |  |  | 65.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 34.62 |  |  |  |  | 0.00
1985 |  |  |  | 4967.39 |  |  | 6466 |  |  |  | 780 | [10 empty] | 72.38 |  |  |  | 72.38 | [5 empty] | 72.70 |  |  | 73.81 |  |  |  | 18.83 |  | 16.79 | [8 empty] | 10.83 |  |  |  |  | 0.00
1986 |  |  |  | 3997.83 |  |  | 5183 |  |  |  | 780 | [10 empty] | 58.37 |  |  |  | 58.37 | [5 empty] | 58.51 |  |  | 59.17 |  |  |  | 0.81 |  | 0.48 | [8 empty] | 41.16 |  |  |  |  | 0.00
1987 |  |  |  | 4621.76 |  |  | 6154 |  |  |  | 780 | [10 empty] | 67.31 |  |  |  | 70.25 | [5 empty] | 67.64 |  |  | 70.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.75 |  |  |  |  | 2.94
1988 |  |  |  | 3071.35 |  |  | 4001 |  |  |  | 780 | [10 empty] | 45.55 |  |  |  | 45.55 | [5 empty] | 44.83 |  |  | 45.55 |  |  |  | 10.15 |  | 5.15 | [8 empty] | 49.31 |  |  |  |  | 0.00
1989 |  |  |  | 3991.50 |  |  | 5213 |  |  |  | 780 | [10 empty] | 59.51 |  |  |  | 59.51 | [5 empty] | 58.42 |  |  | 59.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 40.49 |  |  |  |  | 0.00
1990 |  |  |  | 1727.89 |  |  | 2218 |  |  |  | 780 | [10 empty] | 20.85 |  |  |  | 20.85 | [5 empty] | 25.29 |  |  | 25.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 79.15 |  |  |  |  | 0.00
1991 |  |  |  | 2265.80 |  |  | 3054 |  |  |  | 780 | [10 empty] | 32.25 |  |  |  | 32.25 | [5 empty] | 33.16 |  |  | 34.86 |  |  |  | 23.38 |  | 9.84 | [8 empty] | 57.91 |  |  |  |  | 0.00
1992 |  |  |  | 4873.75 |  |  | 6226 |  |  |  | 780 | [10 empty] | 70.80 |  |  |  | 70.80 | [5 empty] | 71.13 |  |  | 70.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.20 |  |  |  |  | 0.00
1993 |  |  |  | 5757.04 |  |  | 7426 |  |  |  | 780 | [10 empty] | 83.96 |  |  |  | 83.96 | [5 empty] | 84.26 |  |  | 84.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.04 |  |  |  |  | 0.00
1994 |  |  |  | 3357.26 |  |  | 4299 |  |  |  | 780 | [10 empty] | 49.29 |  |  |  | 49.29 | [5 empty] | 49.13 |  |  | 49.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 50.71 |  |  |  |  | 0.00
1995 |  |  |  | 4458.67 |  |  | 5906 |  |  |  | 780 | [10 empty] | 65.12 |  |  |  | 65.12 | [5 empty] | 65.25 |  |  | 67.42 |  |  |  | 5.98 |  | 4.14 | [8 empty] | 30.74 |  |  |  |  | 0.00
1996 |  |  |  | 6709.05 |  |  | 8629 |  |  |  | 780 | [10 empty] | 97.34 |  |  |  | 97.66 | [5 empty] | 97.92 |  |  | 98.24 |  |  |  | 2.33 |  | 2.33 | [8 empty] | 0.01 |  |  |  |  | 0.32
1997 |  |  |  | 4981.24 |  |  | 6306 |  |  |  | 780 | [10 empty] | 72.51 |  |  |  | 72.51 | [5 empty] | 72.90 |  |  | 71.99 |  |  |  | 0.54 |  | 0.39 | [8 empty] | 27.10 |  |  |  |  | 0.00
1998 |  |  |  | 5972.92 |  |  | 7657 |  |  |  | 780 | [10 empty] | 86.96 |  |  |  | 86.96 | [5 empty] | 87.42 |  |  | 87.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.04 |  |  |  |  | 0.00
1999 |  |  |  | 5989.80 |  |  | 7717 |  |  |  | 780 | [10 empty] | 87.17 |  |  |  | 87.20 | [5 empty] | 87.66 |  |  | 88.09 |  |  |  | 0.99 |  | 0.87 | [8 empty] | 11.93 |  |  |  |  | 0.03
2000 |  |  |  | 6849.93 |  |  | 8784 |  |  |  | 780 | [10 empty] | 99.50 |  |  |  | 99.50 | [5 empty] | 99.98 |  |  | 100.00 |  |  |  | 0.49 |  | 0.49 | [8 empty] | 0.01 |  |  |  |  | 0.00
2001 |  |  |  | 5900.98 |  |  | 7572 |  |  |  | 780 | [10 empty] | 85.99 |  |  |  | 85.99 | [5 empty] | 86.36 |  |  | 86.44 |  |  |  | 0.50 |  | 0.43 | [8 empty] | 13.57 |  |  |  |  | 0.00
2002 |  |  |  | 6097.67 |  |  | 7626 |  |  |  | 780 | [10 empty] | 87.04 |  |  |  | 87.04 | [5 empty] | 89.24 |  |  | 87.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.96 |  |  |  |  | 0.00
2003 |  |  |  | 5470.78 |  |  | 6717 |  |  |  | 780 | [10 empty] | 76.40 |  |  |  | 76.40 | [5 empty] | 80.07 |  |  | 76.68 |  |  |  | 1.39 |  | 1.33 | [8 empty] | 22.27 |  |  |  |  | 0.00
2004 |  |  |  | 6346.62 |  |  | 7839 |  |  |  | 780 | [10 empty] | 88.87 |  |  |  | 89.33 | [5 empty] | 92.63 |  |  | 89.24 |  |  |  | 7.07 |  | 6.80 | [8 empty] | 3.87 |  |  |  |  | 0.46
2005 |  |  |  | 6249.51 |  |  | 7625 |  |  |  | 780 | [10 empty] | 86.74 |  |  |  | 86.74 | [5 empty] | 91.46 |  |  | 87.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.26 |  |  |  |  | 0.00
2006 |  |  |  | 5653.43 |  |  | 6890 |  |  |  | 780 | [10 empty] | 78.31 |  |  |  | 78.31 | [5 empty] | 82.74 |  |  | 78.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.69 |  |  |  |  | 0.00
2007 |  |  |  | 4521.77 |  |  | 5483 |  |  |  | 780 | [10 empty] | 62.53 |  |  |  | 62.53 | [5 empty] | 66.18 |  |  | 62.59 |  |  |  | 0.00 |  | 23.29 | [8 empty] | 14.18 |  |  |  |  | 0.00
2008 |  |  |  | 4042.51 |  |  | 4949 |  |  |  | 780 | [10 empty] | 56.05 |  |  |  | 56.05 | [5 empty] | 59.00 |  |  | 56.34 |  |  |  | 0.00 |  | 43.66 | [8 empty] | 0.29 |  |  |  |  | 0.00
2009 |  |  |  | 5720.06 |  |  | 6978 |  |  |  | 780 | [10 empty] | 79.28 |  |  |  | 79.28 | [5 empty] | 83.71 |  |  | 79.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.72 |  |  |  |  | 0.00
2010 |  |  |  | 4935.20 |  |  | 6017 |  |  |  | 780 | [10 empty] | 68.28 |  |  |  | 68.28 | [5 empty] | 72.23 |  |  | 68.69 |  |  |  | 0.08 |  | 0.05 | [8 empty] | 31.66 |  |  |  |  | 0.00
2011 |  |  |  | 6502.50 |  |  | 7895 |  |  |  | 780 | [10 empty] | 90.06 |  |  |  | 90.06 | [5 empty] | 95.17 |  |  | 90.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.94 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 227
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1835
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 7
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 44
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 1729
L. |  | Human factor related | [39 empty] | 4
Z. |  | Other | [39 empty] | 13
Subtotal | [22 empty] | 8784 | [14 empty] | 3615 |  |  |  | 244
Total | [22 empty] | 8784 | [14 empty] | 3859
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 159
16. |  |  | Steam generation systems | [34 empty] | 59
31. |  |  | Turbine and auxiliaries | [34 empty] | 15
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [37 empty] | 244

## TAKAHAMA-3
2020 Operating Experience
JP-29 | [8 empty] | TAKAHAMA-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-12-12
Thermal power | [12 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-05-09
Gross electrical power | [12 empty] | : |  |  | 870 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-01-17
Reference unit power (net) | [12 empty] | : |  |  | 830 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.28
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.1
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 111.74 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 1.45 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 1.45 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 98.55 %
Load Factor (LF) | [18 empty] | : | 1.53 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 1.49 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8653 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 7.56 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 111.74 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 111.74
EAF [%] |  |  |  |  | 17.12 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.45
UCF [%] |  |  |  |  | 17.12 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.45
LF [%] |  |  |  |  | 18.09 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.53
OF [%] |  |  |  |  | 17.61 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.49
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 82.88 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.55
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 185129.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.3 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 70.77 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.49 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 70.8 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 28.71 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.7 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 69.01 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 6199.46 |  |  | 7426 |  |  |  | 830 | [10 empty] | 83.31 |  |  |  | 83.31 | [5 empty] | 84.14 |  |  | 83.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.69 |  |  |  |  | 0.00
1986 |  |  |  | 6833.58 |  |  | 8215 |  |  |  | 830 | [10 empty] | 93.08 |  |  |  | 93.08 | [5 empty] | 93.99 |  |  | 93.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.92 |  |  |  |  | 0.00
1987 |  |  |  | 6030.38 |  |  | 7265 |  |  |  | 830 | [10 empty] | 82.93 |  |  |  | 82.93 | [5 empty] | 82.94 |  |  | 82.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.07 |  |  |  |  | 0.00
1988 |  |  |  | 5743.18 |  |  | 6948 |  |  |  | 830 | [10 empty] | 79.10 |  |  |  | 79.10 | [5 empty] | 78.77 |  |  | 79.10 |  |  |  | 0.42 |  | 0.33 | [8 empty] | 20.57 |  |  |  |  | 0.00
1989 |  |  |  | 5987.22 |  |  | 7138 |  |  |  | 830 | [10 empty] | 81.48 |  |  |  | 81.48 | [5 empty] | 82.35 |  |  | 81.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.52 |  |  |  |  | 0.00
1990 |  |  |  | 6775.04 |  |  | 8143 |  |  |  | 830 | [10 empty] | 91.88 |  |  |  | 91.88 | [5 empty] | 93.18 |  |  | 92.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.12 |  |  |  |  | 0.00
1991 |  |  |  | 5513.55 |  |  | 6641 |  |  |  | 830 | [10 empty] | 73.86 |  |  |  | 73.86 | [5 empty] | 75.83 |  |  | 75.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.14 |  |  |  |  | 0.00
1992 |  |  |  | 6059.91 |  |  | 7292 |  |  |  | 830 | [10 empty] | 82.22 |  |  |  | 82.22 | [5 empty] | 83.12 |  |  | 83.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.78 |  |  |  |  | 0.00
1993 |  |  |  | 5804.78 |  |  | 6983 |  |  |  | 830 | [10 empty] | 77.57 |  |  |  | 77.57 | [5 empty] | 79.84 |  |  | 79.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.43 |  |  |  |  | 0.00
1994 |  |  |  | 7361.14 |  |  | 8760 |  |  |  | 830 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.24 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 5662.92 |  |  | 6809 |  |  |  | 830 | [10 empty] | 77.00 |  |  |  | 77.00 | [5 empty] | 77.89 |  |  | 77.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.00 |  |  |  |  | 0.00
1996 |  |  |  | 5479.31 |  |  | 6576 |  |  |  | 830 | [10 empty] | 74.24 |  |  |  | 74.24 | [5 empty] | 75.15 |  |  | 74.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.76 |  |  |  |  | 0.00
1997 |  |  |  | 6028.89 |  |  | 7206 |  |  |  | 830 | [10 empty] | 81.88 |  |  |  | 81.88 | [5 empty] | 82.92 |  |  | 82.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.12 |  |  |  |  | 0.00
1998 |  |  |  | 6853.72 |  |  | 8161 |  |  |  | 830 | [10 empty] | 93.11 |  |  |  | 93.11 | [5 empty] | 94.26 |  |  | 93.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.89 |  |  |  |  | 0.00
1999 |  |  |  | 6833.42 |  |  | 8131 |  |  |  | 830 | [10 empty] | 92.80 |  |  |  | 93.85 | [5 empty] | 93.98 |  |  | 92.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.15 |  |  |  |  | 1.05
2000 |  |  |  | 5898.88 |  |  | 7023 |  |  |  | 830 | [10 empty] | 79.94 |  |  |  | 79.94 | [5 empty] | 80.91 |  |  | 79.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.06 |  |  |  |  | 0.00
2001 |  |  |  | 6167.20 |  |  | 7340 |  |  |  | 830 | [10 empty] | 83.77 |  |  |  | 83.77 | [5 empty] | 84.82 |  |  | 83.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.23 |  |  |  |  | 0.00
2002 |  |  |  | 6463.31 |  |  | 7654 |  |  |  | 830 | [10 empty] | 87.35 |  |  |  | 87.35 | [5 empty] | 88.89 |  |  | 87.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.65 |  |  |  |  | 0.00
2003 |  |  |  | 7355.67 |  |  | 8421 |  |  |  | 830 | [10 empty] | 96.11 |  |  |  | 96.11 | [5 empty] | 101.17 |  |  | 96.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.89 |  |  |  |  | 0.00
2004 |  |  |  | 5625.10 |  |  | 6512 |  |  |  | 830 | [10 empty] | 74.11 |  |  |  | 74.11 | [5 empty] | 77.15 |  |  | 74.13 |  |  |  | 8.83 |  | 11.68 | [8 empty] | 14.21 |  |  |  |  | 0.00
2005 |  |  |  | 5738.44 |  |  | 6656 |  |  |  | 830 | [10 empty] | 75.61 |  |  |  | 75.61 | [5 empty] | 78.92 |  |  | 75.98 |  |  |  | 0.00 |  | 4.58 | [8 empty] | 19.81 |  |  |  |  | 0.00
2006 |  |  |  | 5702.85 |  |  | 6604 |  |  |  | 830 | [10 empty] | 75.04 |  |  |  | 75.04 | [5 empty] | 78.43 |  |  | 75.39 |  |  |  | 0.02 |  | 0.82 | [8 empty] | 24.14 |  |  |  |  | 0.00
2007 |  |  |  | 6847.38 |  |  | 7834 |  |  |  | 830 | [10 empty] | 89.37 |  |  |  | 89.37 | [5 empty] | 94.18 |  |  | 89.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.63 |  |  |  |  | 0.00
2008 |  |  |  | 3102.63 |  |  | 3608 |  |  |  | 830 | [10 empty] | 40.65 |  |  |  | 40.65 | [5 empty] | 42.56 |  |  | 41.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 59.35 |  |  |  |  | 0.00
2009 |  |  |  | 5738.94 |  |  | 6525 |  |  |  | 830 | [10 empty] | 74.19 |  |  |  | 74.19 | [5 empty] | 78.93 |  |  | 74.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.81 |  |  |  |  | 0.00
2010 |  |  |  | 6212.08 |  |  | 7006 |  |  |  | 830 | [10 empty] | 79.70 |  |  |  | 79.70 | [5 empty] | 85.44 |  |  | 79.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.30 |  |  |  |  | 0.00
2011 |  |  |  | 7828.83 |  |  | 8760 |  |  |  | 830 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 107.67 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2012 |  |  |  | 1079.91 |  |  | 1223 |  |  |  | 830 | [10 empty] | 13.92 |  |  |  | 13.92 | [5 empty] | 14.81 |  |  | 13.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 86.08 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 768.25 |  |  | 915 |  |  |  | 830 | [10 empty] | 84.77 |  |  |  | 84.77 | [5 empty] | 10.54 |  |  | 10.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.23 |  |  |  |  | 0.00
2017 |  |  |  | 4284.64 |  |  | 4944 |  |  |  | 830 | [10 empty] | 56.03 |  |  |  | 56.03 | [5 empty] | 58.93 |  |  | 56.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 43.97 |  |  |  |  | 0.00
2018 |  |  |  | 5595.11 |  |  | 6402 |  |  |  | 830 | [10 empty] | 72.75 |  |  |  | 72.75 | [5 empty] | 76.95 |  |  | 73.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.25 |  |  |  |  | 0.00
2019 |  |  |  | 7651.68 |  |  | 8760 |  |  |  | 830 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 105.24 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2020 |  |  |  | 111.74 |  |  | 131 |  |  |  | 830 | [10 empty] | 1.45 |  |  |  | 1.45 | [5 empty] | 1.53 |  |  | 1.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 98.55 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 3
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 8653 | [14 empty] | 1538
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 18
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 945
H. |  | Nuclear regulatory requirements | [39 empty] | 11
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
M. |  | Governmental requirements or court decisions | [51 empty] | 183
Z. |  | Other | [39 empty] | 29
Subtotal | [22 empty] | 8653 | [14 empty] | 2501 |  |  |  | 43 | [11 empty] | 186
Total | [22 empty] | 8653 | [14 empty] | 2730
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
16. |  |  | Steam generation systems | [34 empty] | 11
31. |  |  | Turbine and auxiliaries | [34 empty] | 18
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
Total | [37 empty] | 43

## TAKAHAMA-4
2020 Operating Experience
JP-30 | [8 empty] | TAKAHAMA-4 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-03-19
Thermal power | [12 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-11-01
Gross electrical power | [12 empty] | : |  |  | 870 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-06-05
Reference unit power (net) | [12 empty] | : |  |  | 830 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.28
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.21
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5187.9 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 67.55 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 67.55 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 32.45 %
Load Factor (LF) | [18 empty] | : | 71.16 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 67.95 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2815 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 568.14 |  |  |  | 655.82 |  | 634.84 | [8 empty] | 654.65 |  |  | 629.62 | [6 empty] | 647.74 |  | 641.42 |  |  |  | 623.93 |  |  | 131.74 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5187.90
EAF [%] |  |  |  |  | 0.00 | 92.91 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 99.98 |  |  | 20.35 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 67.55
UCF [%] |  |  |  |  | 0.00 | 92.91 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 99.98 |  |  | 20.35 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 67.55
LF [%] |  |  |  |  | 0.00 | 98.35 |  |  |  | 106.20 |  | 106.23 | [8 empty] | 106.01 |  |  | 105.36 | [6 empty] | 104.89 |  | 103.87 |  |  |  | 104.41 |  |  | 21.33 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 71.16
OF [%] |  |  |  |  | 0.00 | 97.41 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 20.83 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 67.95
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 7.09 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.02 |  | 0.00 |  |  |  | 0.02 |  |  | 79.65 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 32.45
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 184097.9 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.37 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.12 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.37 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 72.16 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 27.47 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.1 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 69.47 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 5479.31 |  |  | 6887 |  |  |  | 830 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.21 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 5864.02 |  |  | 7073 |  |  |  | 830 | [10 empty] | 79.59 |  |  |  | 79.59 | [5 empty] | 80.65 |  |  | 80.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.41 |  |  |  |  | 0.00
1987 |  |  |  | 5588.52 |  |  | 6743 |  |  |  | 830 | [10 empty] | 76.97 |  |  |  | 76.97 | [5 empty] | 76.86 |  |  | 76.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.03 |  |  |  |  | 0.00
1988 |  |  |  | 6437.90 |  |  | 7666 |  |  |  | 830 | [10 empty] | 87.27 |  |  |  | 87.27 | [5 empty] | 88.30 |  |  | 87.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.73 |  |  |  |  | 0.00
1989 |  |  |  | 6802.70 |  |  | 8167 |  |  |  | 830 | [10 empty] | 93.23 |  |  |  | 93.23 | [5 empty] | 93.56 |  |  | 93.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.77 |  |  |  |  | 0.00
1990 |  |  |  | 5174.56 |  |  | 6233 |  |  |  | 830 | [10 empty] | 68.98 |  |  |  | 68.98 | [5 empty] | 71.17 |  |  | 71.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.02 |  |  |  |  | 0.00
1991 |  |  |  | 6170.12 |  |  | 7409 |  |  |  | 830 | [10 empty] | 83.05 |  |  |  | 83.05 | [5 empty] | 84.86 |  |  | 84.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.95 |  |  |  |  | 0.00
1992 |  |  |  | 6048.41 |  |  | 7265 |  |  |  | 830 | [10 empty] | 81.93 |  |  |  | 81.93 | [5 empty] | 82.96 |  |  | 82.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.07 |  |  |  |  | 0.00
1993 |  |  |  | 7210.91 |  |  | 8578 |  |  |  | 830 | [10 empty] | 97.86 |  |  |  | 97.86 | [5 empty] | 99.18 |  |  | 97.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.14 |  |  |  |  | 0.00
1994 |  |  |  | 5767.17 |  |  | 6861 |  |  |  | 830 | [10 empty] | 78.51 |  |  |  | 78.51 | [5 empty] | 79.32 |  |  | 78.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.49 |  |  |  |  | 0.00
1995 |  |  |  | 5651.76 |  |  | 6785 |  |  |  | 830 | [10 empty] | 76.72 |  |  |  | 76.72 | [5 empty] | 77.73 |  |  | 77.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.28 |  |  |  |  | 0.00
1996 |  |  |  | 5666.52 |  |  | 6785 |  |  |  | 830 | [10 empty] | 76.68 |  |  |  | 76.68 | [5 empty] | 77.72 |  |  | 77.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.32 |  |  |  |  | 0.00
1997 |  |  |  | 7367.27 |  |  | 8760 |  |  |  | 830 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 101.33 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1998 |  |  |  | 6470.18 |  |  | 7727 |  |  |  | 830 | [10 empty] | 87.79 |  |  |  | 87.79 | [5 empty] | 88.99 |  |  | 88.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.21 |  |  |  |  | 0.00
1999 |  |  |  | 5500.34 |  |  | 6542 |  |  |  | 830 | [10 empty] | 74.64 |  |  |  | 75.83 | [5 empty] | 75.65 |  |  | 74.68 |  |  |  | 3.70 |  | 2.92 | [8 empty] | 21.25 |  |  |  |  | 1.20
2000 |  |  |  | 6099.01 |  |  | 7254 |  |  |  | 830 | [10 empty] | 82.57 |  |  |  | 82.57 | [5 empty] | 83.65 |  |  | 82.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.43 |  |  |  |  | 0.00
2001 |  |  |  | 7364.55 |  |  | 8760 |  |  |  | 830 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 101.29 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2002 |  |  |  | 6145.46 |  |  | 7316 |  |  |  | 830 | [10 empty] | 83.50 |  |  |  | 83.50 | [5 empty] | 84.52 |  |  | 83.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.50 |  |  |  |  | 0.00
2003 |  |  |  | 6490.21 |  |  | 7531 |  |  |  | 830 | [10 empty] | 85.98 |  |  |  | 85.98 | [5 empty] | 89.26 |  |  | 85.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.02 |  |  |  |  | 0.00
2004 |  |  |  | 5987.82 |  |  | 6868 |  |  |  | 830 | [10 empty] | 78.17 |  |  |  | 78.17 | [5 empty] | 82.13 |  |  | 78.19 |  |  |  | 0.00 |  | 3.71 | [8 empty] | 18.12 |  |  |  |  | 0.00
2005 |  |  |  | 6633.20 |  |  | 7657 |  |  |  | 830 | [10 empty] | 87.35 |  |  |  | 87.35 | [5 empty] | 91.23 |  |  | 87.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.65 |  |  |  |  | 0.00
2006 |  |  |  | 6589.83 |  |  | 7612 |  |  |  | 830 | [10 empty] | 86.56 |  |  |  | 86.56 | [5 empty] | 90.63 |  |  | 86.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.44 |  |  |  |  | 0.00
2007 |  |  |  | 5787.60 |  |  | 6688 |  |  |  | 830 | [10 empty] | 76.04 |  |  |  | 76.04 | [5 empty] | 79.60 |  |  | 76.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.96 |  |  |  |  | 0.00
2008 |  |  |  | 5009.76 |  |  | 5825 |  |  |  | 830 | [10 empty] | 65.56 |  |  |  | 65.56 | [5 empty] | 68.71 |  |  | 66.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 34.44 |  |  |  |  | 0.00
2009 |  |  |  | 7584.98 |  |  | 8760 |  |  |  | 830 | [10 empty] | 99.67 |  |  |  | 99.67 | [5 empty] | 104.32 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.33 |  |  |  |  | 0.00
2010 |  |  |  | 5379.61 |  |  | 6130 |  |  |  | 830 | [10 empty] | 69.45 |  |  |  | 69.45 | [5 empty] | 73.99 |  |  | 69.98 |  |  |  | 5.60 |  | 4.12 | [8 empty] | 26.43 |  |  |  |  | 0.00
2011 |  |  |  | 4320.16 |  |  | 4847 |  |  |  | 830 | [10 empty] | 55.29 |  |  |  | 55.29 | [5 empty] | 59.42 |  |  | 55.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 44.71 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 81.24 |  |  |  | 81.24 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 2.96 |  | 2.48 | [8 empty] | 16.28 |  |  |  |  | 0.00
2017 |  |  |  | 4636.34 |  |  | 5362 |  |  |  | 830 | [10 empty] | 84.51 |  |  |  | 84.51 | [5 empty] | 63.77 |  |  | 61.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.49 |  |  |  |  | 0.00
2018 |  |  |  | 5374.49 |  |  | 6167 |  |  |  | 830 | [10 empty] | 70.04 |  |  |  | 70.04 | [5 empty] | 73.92 |  |  | 70.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.96 |  |  |  |  | 0.00
2019 |  |  |  | 5463.11 |  |  | 6251 |  |  |  | 830 | [10 empty] | 71.31 |  |  |  | 71.31 | [5 empty] | 75.14 |  |  | 71.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.69 |  |  |  |  | 0.00
2020 |  |  |  | 5187.90 |  |  | 5969 |  |  |  | 830 | [10 empty] | 67.55 |  |  |  | 67.55 | [5 empty] | 71.16 |  |  | 67.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.45 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 24
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2816 | [14 empty] | 1352
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 1086
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
M. |  | Governmental requirements or court decisions | [51 empty] | 263
Z. |  | Other | [39 empty] | 9
Subtotal | [22 empty] | 2816 | [14 empty] | 2438 |  |  |  | 33 | [11 empty] | 266
Total | [22 empty] | 2816 | [14 empty] | 2737
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 9
41. |  |  | Main Generator Systems | [34 empty] | 16
Total | [37 empty] | 33

## TOKAI-2
2020 Operating Experience
JP-21 | [8 empty] | TOKAI-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JAPCO (JAPAN ATOMIC POWER CO.)
Owner | [7 empty] | : | JAPCO (JAPAN ATOMIC POWER CO.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE/H (GENERAL ELECTRIC CO./ HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-10-03
Thermal power | [12 empty] | : |  |  | 3293 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-03-13
Gross electrical power | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1978-11-28
Reference unit power (net) | [12 empty] | : |  |  | 1060 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6.93
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.385
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.7 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 22 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.68
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 19
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 221610 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.1 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 55.71 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.35 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 56.25 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 39.39 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 55.96 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.54 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 56.4 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1978 |  |  |  | Data not provided
1979 |  |  |  | 5209.50 |  |  | 5481 |  |  |  | 1056 | [10 empty] | 56.32 |  |  |  | 56.32 | [5 empty] | 56.32 |  |  | 62.57 |  |  |  | 9.83 |  | 6.14 | [8 empty] | 37.55 |  |  |  |  | 0.00
1980 |  |  |  | 6743.20 |  |  | 6597 |  |  |  | 1056 | [10 empty] | 72.59 |  |  |  | 72.59 | [5 empty] | 72.70 |  |  | 75.10 |  |  |  | 1.40 |  | 1.03 | [8 empty] | 26.38 |  |  |  |  | 0.00
1981 |  |  |  | 6059.10 |  |  | 6037 |  |  |  | 1056 | [10 empty] | 65.32 |  |  |  | 65.32 | [5 empty] | 65.50 |  |  | 68.92 |  |  |  | 7.15 |  | 5.03 | [8 empty] | 29.65 |  |  |  |  | 0.00
1982 |  |  |  | 5571.60 |  |  | 5338 |  |  |  | 1056 | [10 empty] | 59.60 |  |  |  | 59.60 | [5 empty] | 60.23 |  |  | 60.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 40.40 |  |  |  |  | 0.00
1983 |  |  |  | 6556.64 |  |  | 6327 |  |  |  | 1056 | [10 empty] | 70.45 |  |  |  | 70.45 | [5 empty] | 70.88 |  |  | 72.23 |  |  |  | 4.32 |  | 3.18 | [8 empty] | 26.37 |  |  |  |  | 0.00
1984 |  |  |  | 8695.17 |  |  | 8240 |  |  |  | 1056 | [10 empty] | 93.46 |  |  |  | 93.46 | [5 empty] | 93.74 |  |  | 93.81 |  |  |  | 1.09 |  | 1.03 | [8 empty] | 5.51 |  |  |  |  | 0.00
1985 |  |  |  | 6957.48 |  |  | 6625 |  |  |  | 1056 | [10 empty] | 75.03 |  |  |  | 75.03 | [5 empty] | 75.21 |  |  | 75.63 |  |  |  | 2.53 |  | 1.94 | [8 empty] | 23.02 |  |  |  |  | 0.00
1986 |  |  |  | 5797.62 |  |  | 5508 |  |  |  | 1056 | [10 empty] | 62.46 |  |  |  | 62.46 | [5 empty] | 62.67 |  |  | 62.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.54 |  |  |  |  | 0.00
1987 |  |  |  | 7040.45 |  |  | 6776 |  |  |  | 1056 | [10 empty] | 76.46 |  |  |  | 76.46 | [5 empty] | 76.11 |  |  | 77.35 |  |  |  | 1.72 |  | 1.34 | [8 empty] | 22.20 |  |  |  |  | 0.00
1988 |  |  |  | 6088.38 |  |  | 5872 |  |  |  | 1056 | [10 empty] | 65.97 |  |  |  | 65.97 | [5 empty] | 65.64 |  |  | 66.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 34.03 |  |  |  |  | 0.00
1989 |  |  |  | 8434.97 |  |  | 8006 |  |  |  | 1056 | [10 empty] | 91.22 |  |  |  | 91.22 | [5 empty] | 91.18 |  |  | 91.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.78 |  |  |  |  | 0.00
1990 |  |  |  | 7291.60 |  |  | 6948 |  |  |  | 1056 | [10 empty] | 78.90 |  |  |  | 78.90 | [5 empty] | 78.82 |  |  | 79.32 |  |  |  | 3.85 |  | 3.16 | [8 empty] | 17.94 |  |  |  |  | 0.00
1991 |  |  |  | 7025.25 |  |  | 6716 |  |  |  | 1056 | [10 empty] | 76.07 |  |  |  | 76.07 | [5 empty] | 75.94 |  |  | 76.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.93 |  |  |  |  | 0.00
1992 |  |  |  | 6307.75 |  |  | 5990 |  |  |  | 1080 | [10 empty] | 68.46 |  |  |  | 68.64 | [5 empty] | 66.49 |  |  | 68.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.36 |  |  |  |  | 0.18
1993 |  |  |  | 8707.18 |  |  | 8252 |  |  |  | 1080 | [10 empty] | 93.84 |  |  |  | 93.84 | [5 empty] | 92.03 |  |  | 94.20 |  |  |  | 2.88 |  | 2.78 | [8 empty] | 3.37 |  |  |  |  | 0.00
1994 |  |  |  | 7325.77 |  |  | 6938 |  |  |  | 1056 | [10 empty] | 78.85 |  |  |  | 78.87 | [5 empty] | 79.19 |  |  | 79.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.13 |  |  |  |  | 0.01
1995 |  |  |  | 6845.05 |  |  | 6488 |  |  |  | 1056 | [10 empty] | 73.66 |  |  |  | 73.69 | [5 empty] | 74.00 |  |  | 74.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.31 |  |  |  |  | 0.03
1996 |  |  |  | 7562.05 |  |  | 7169 |  |  |  | 1056 | [10 empty] | 80.75 |  |  |  | 80.79 | [5 empty] | 81.52 |  |  | 81.61 |  |  |  | 1.39 |  | 1.14 | [8 empty] | 18.07 |  |  |  |  | 0.04
1997 |  |  |  | 8884.54 |  |  | 8404 |  |  |  | 1056 | [10 empty] | 95.60 |  |  |  | 95.70 | [5 empty] | 96.04 |  |  | 95.94 |  |  |  | 4.28 |  | 4.28 | [8 empty] | 0.02 |  |  |  |  | 0.10
1998 |  |  |  | 6999.42 |  |  | 6642 |  |  |  | 1056 | [10 empty] | 74.97 |  |  |  | 75.07 | [5 empty] | 75.66 |  |  | 75.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.93 |  |  |  |  | 0.10
1999 |  |  |  | 2316.08 |  |  | 2228 |  |  |  | 1056 | [10 empty] | 24.95 |  |  |  | 25.37 | [5 empty] | 25.04 |  |  | 25.43 |  |  |  | 63.91 |  | 44.93 | [8 empty] | 29.70 |  |  |  |  | 0.42
2000 |  |  |  | 7031.57 |  |  | 6626 |  |  |  | 1056 | [10 empty] | 75.40 |  |  |  | 76.28 | [5 empty] | 75.80 |  |  | 75.43 |  |  |  | 23.71 |  | 23.71 | [8 empty] | 0.02 |  |  |  |  | 0.87
2001 |  |  |  | 5833.18 |  |  | 5641 |  |  |  | 1056 | [10 empty] | 62.68 |  |  |  | 62.69 | [5 empty] | 63.06 |  |  | 64.39 |  |  |  | 11.40 |  | 8.07 | [8 empty] | 29.25 |  |  |  |  | 0.00
2002 |  |  |  | 6420.06 |  |  | 6061 |  |  |  | 1056 | [10 empty] | 68.93 |  |  |  | 69.96 | [5 empty] | 69.40 |  |  | 69.19 |  |  |  | 8.63 |  | 6.61 | [8 empty] | 23.43 |  |  |  |  | 1.03
2003 |  |  |  | 9176.55 |  |  | 8635 |  |  |  | 1056 | [10 empty] | 98.51 |  |  |  | 98.56 | [5 empty] | 99.20 |  |  | 98.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.44 |  |  |  |  | 0.05
2004 |  |  |  | 7195.36 |  |  | 6723 |  |  |  | 1060 | [10 empty] | 76.33 |  |  |  | 76.50 | [5 empty] | 77.28 |  |  | 76.54 |  |  |  | 0.00 |  | 10.33 | [8 empty] | 13.17 |  |  |  |  | 0.17
2005 |  |  |  | 5259.48 |  |  | 4914 |  |  |  | 1060 | [10 empty] | 55.84 |  |  |  | 55.84 | [5 empty] | 56.64 |  |  | 56.10 |  |  |  | 0.00 |  | 18.78 | [8 empty] | 25.38 |  |  |  |  | 0.00
2006 |  |  |  | 8186.87 |  |  | 7704 |  |  |  | 1060 | [10 empty] | 87.33 |  |  |  | 87.90 | [5 empty] | 88.17 |  |  | 87.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.10 |  |  |  |  | 0.57
2007 |  |  |  | 7518.75 |  |  | 7048 |  |  |  | 1060 | [10 empty] | 79.98 |  |  |  | 79.98 | [5 empty] | 80.97 |  |  | 80.46 |  |  |  | 9.32 |  | 8.22 | [8 empty] | 11.79 |  |  |  |  | 0.00
2008 |  |  |  | 6545.88 |  |  | 6132 |  |  |  | 1060 | [10 empty] | 68.76 |  |  |  | 68.76 | [5 empty] | 70.30 |  |  | 69.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.24 |  |  |  |  | 0.00
2009 |  |  |  | 5587.41 |  |  | 5169 |  |  |  | 1060 | [10 empty] | 58.70 |  |  |  | 58.70 | [5 empty] | 60.17 |  |  | 59.01 |  |  |  | 13.89 |  | 9.47 | [8 empty] | 31.83 |  |  |  |  | 0.00
2010 |  |  |  | 5137.03 |  |  | 4763 |  |  |  | 1060 | [10 empty] | 53.90 |  |  |  | 53.90 | [5 empty] | 55.32 |  |  | 54.37 |  |  |  | 28.74 |  | 21.74 | [8 empty] | 24.36 |  |  |  |  | 0.00
2011 |  |  |  | 1819.07 |  |  | 1670 |  |  |  | 1060 | [10 empty] | 19.07 |  |  |  | 38.36 | [5 empty] | 19.59 |  |  | 19.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 61.64 |  |  |  |  | 19.28
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1978 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 310
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1491
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 23 |  |  |  | 7
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 1906
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 0
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 42
Z. |  | Other | [39 empty] | 8
Subtotal | [22 empty] | 8784 | [14 empty] | 3420 |  |  |  | 325 | [11 empty] | 44
Total | [22 empty] | 8784 | [14 empty] | 3789
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1978 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [34 empty] | 142
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 48
14. |  |  | Safety Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 29
31. |  |  | Turbine and auxiliaries | [34 empty] | 29
32. |  |  | Feedwater and Main Steam System | [34 empty] | 38
42. |  |  | Electrical Power Supply Systems | [34 empty] | 10
Total | [37 empty] | 325
Highlights (2020)
Appropriate Implementation in new regulatory law

## TOMARI-1
2020 Operating Experience
JP-43 | [8 empty] | TOMARI-1 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | HEPCO (HOKKAIDO ELECTRIC POWER CO., INC.)
Owner | [7 empty] | : | HEPCO (HOKKAIDO ELECTRIC POWER CO., INC.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (2-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-04-18
Thermal power | [12 empty] | : |  |  | 1650 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-12-06
Gross electrical power | [12 empty] | : |  |  | 579 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-06-22
Reference unit power (net) | [12 empty] | : |  |  | 550 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.254
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 41000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.64 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 19
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 90971 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.89 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 58.8 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 58.8 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 40.67 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 59.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 59.1 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 3607.01 |  |  | 7095 |  |  |  | 550 | [10 empty] | 99.57 |  |  |  | 99.57 | [5 empty] | 99.57 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.43 |  |  |  |  | 0.00
1990 |  |  |  | 3830.69 |  |  | 7092 |  |  |  | 550 | [10 empty] | 79.51 |  |  |  | 79.51 | [5 empty] | 79.51 |  |  | 80.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.49 |  |  |  |  | 0.00
1991 |  |  |  | 3540.38 |  |  | 6588 |  |  |  | 550 | [10 empty] | 73.48 |  |  |  | 73.48 | [5 empty] | 73.48 |  |  | 75.21 |  |  |  | 8.90 |  | 7.18 | [8 empty] | 19.34 |  |  |  |  | 0.00
1992 |  |  |  | 3646.36 |  |  | 6780 |  |  |  | 550 | [10 empty] | 75.86 |  |  |  | 75.86 | [5 empty] | 75.48 |  |  | 77.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.14 |  |  |  |  | 0.00
1993 |  |  |  | 4795.23 |  |  | 8760 |  |  |  | 550 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 99.53 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1994 |  |  |  | 3903.95 |  |  | 7208 |  |  |  | 550 | [10 empty] | 81.38 |  |  |  | 81.38 | [5 empty] | 81.03 |  |  | 82.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.62 |  |  |  |  | 0.00
1995 |  |  |  | 3946.25 |  |  | 7175 |  |  |  | 550 | [10 empty] | 81.85 |  |  |  | 81.85 | [5 empty] | 81.91 |  |  | 81.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.15 |  |  |  |  | 0.00
1996 |  |  |  | 3750.44 |  |  | 6920 |  |  |  | 550 | [10 empty] | 78.06 |  |  |  | 78.06 | [5 empty] | 77.63 |  |  | 78.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.94 |  |  |  |  | 0.00
1997 |  |  |  | 4795.59 |  |  | 8760 |  |  |  | 550 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 99.53 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1998 |  |  |  | 4239.09 |  |  | 7373 |  |  |  | 550 | [10 empty] | 83.12 |  |  |  | 83.12 | [5 empty] | 87.98 |  |  | 84.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.88 |  |  |  |  | 0.00
1999 |  |  |  | 4074.58 |  |  | 6986 |  |  |  | 550 | [10 empty] | 79.73 |  |  |  | 79.73 | [5 empty] | 84.57 |  |  | 79.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.27 |  |  |  |  | 0.00
2000 |  |  |  | 4168.52 |  |  | 7598 |  |  |  | 550 | [10 empty] | 86.49 |  |  |  | 86.49 | [5 empty] | 86.28 |  |  | 86.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.51 |  |  |  |  | 0.00
2001 |  |  |  | 4803.96 |  |  | 8760 |  |  |  | 550 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 99.71 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2002 |  |  |  | 4177.26 |  |  | 7614 |  |  |  | 550 | [10 empty] | 86.91 |  |  |  | 86.91 | [5 empty] | 86.70 |  |  | 86.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.09 |  |  |  |  | 0.00
2003 |  |  |  | 3821.66 |  |  | 6893 |  |  |  | 550 | [10 empty] | 78.69 |  |  |  | 78.69 | [5 empty] | 79.32 |  |  | 78.69 |  |  |  | 7.30 |  | 6.20 | [8 empty] | 15.11 |  |  |  |  | 0.00
2004 |  |  |  | 3788.84 |  |  | 6762 |  |  |  | 550 | [10 empty] | 76.97 |  |  |  | 76.97 | [5 empty] | 78.42 |  |  | 76.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.03 |  |  |  |  | 0.00
2005 |  |  |  | 4818.78 |  |  | 8616 |  |  |  | 550 | [10 empty] | 98.30 |  |  |  | 98.30 | [5 empty] | 100.02 |  |  | 98.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.70 |  |  |  |  | 0.00
2006 |  |  |  | 4236.75 |  |  | 7643 |  |  |  | 550 | [10 empty] | 86.89 |  |  |  | 86.89 | [5 empty] | 87.94 |  |  | 87.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.11 |  |  |  |  | 0.00
2007 |  |  |  | 3952.55 |  |  | 7121 |  |  |  | 550 | [10 empty] | 80.61 |  |  |  | 80.61 | [5 empty] | 82.04 |  |  | 81.29 |  |  |  | 3.88 |  | 3.25 | [8 empty] | 16.13 |  |  |  |  | 0.00
2008 |  |  |  | 3111.15 |  |  | 5578 |  |  |  | 550 | [10 empty] | 63.10 |  |  |  | 63.10 | [5 empty] | 64.40 |  |  | 63.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.90 |  |  |  |  | 0.00
2009 |  |  |  | 4928.21 |  |  | 8760 |  |  |  | 550 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.29 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 3994.56 |  |  | 7156 |  |  |  | 550 | [10 empty] | 81.28 |  |  |  | 81.28 | [5 empty] | 82.91 |  |  | 81.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.72 |  |  |  |  | 0.00
2011 |  |  |  | 1496.72 |  |  | 2664 |  |  |  | 550 | [10 empty] | 30.36 |  |  |  | 30.36 | [5 empty] | 31.07 |  |  | 30.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 69.64 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 24
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 925
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 2676
Z. |  | Other | [39 empty] | 18
Subtotal | [22 empty] | 8784 | [14 empty] | 3601 |  |  |  | 42
Total | [22 empty] | 8784 | [14 empty] | 3643
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 24
Highlights (2020)
Implementation of emergency safety measures for considering the Accident of Fukushima Dai-ich and Dai-ni Nuclear Power Stations Enforcement of Comprehensive Assessment for the Safety of Nuclear Power Reactor Facility(so-called Stress Test)

## TOMARI-2
2020 Operating Experience
JP-44 | [8 empty] | TOMARI-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | HEPCO (HOKKAIDO ELECTRIC POWER CO., INC.)
Owner | [7 empty] | : | HEPCO (HOKKAIDO ELECTRIC POWER CO., INC.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (2-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-06-13
Thermal power | [12 empty] | : |  |  | 1650 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-08-27
Gross electrical power | [12 empty] | : |  |  | 579 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1991-04-12
Reference unit power (net) | [12 empty] | : |  |  | 550 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.254
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 41000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.64 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 19
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 83574 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.14 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 56.94 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.66 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 56.94 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 42.4 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 57.79 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 57.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1991 |  |  |  | 3277.78 |  |  | 6061 |  |  |  | 550 | [10 empty] | 76.03 |  |  |  | 76.03 | [5 empty] | 76.02 |  |  | 76.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.97 |  |  |  |  | 0.00
1992 |  |  |  | 3639.56 |  |  | 6756 |  |  |  | 550 | [10 empty] | 75.48 |  |  |  | 75.48 | [5 empty] | 75.33 |  |  | 76.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.52 |  |  |  |  | 0.00
1993 |  |  |  | 3847.52 |  |  | 7092 |  |  |  | 550 | [10 empty] | 80.03 |  |  |  | 80.03 | [5 empty] | 79.86 |  |  | 80.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.97 |  |  |  |  | 0.00
1994 |  |  |  | 4511.59 |  |  | 8232 |  |  |  | 550 | [10 empty] | 93.91 |  |  |  | 93.91 | [5 empty] | 93.64 |  |  | 93.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.09 |  |  |  |  | 0.00
1995 |  |  |  | 4161.85 |  |  | 7567 |  |  |  | 550 | [10 empty] | 85.55 |  |  |  | 85.55 | [5 empty] | 86.38 |  |  | 86.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.45 |  |  |  |  | 0.00
1996 |  |  |  | 3933.63 |  |  | 7232 |  |  |  | 550 | [10 empty] | 81.54 |  |  |  | 81.54 | [5 empty] | 81.42 |  |  | 82.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.46 |  |  |  |  | 0.00
1997 |  |  |  | 3775.23 |  |  | 6943 |  |  |  | 550 | [10 empty] | 78.47 |  |  |  | 78.47 | [5 empty] | 78.36 |  |  | 79.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.53 |  |  |  |  | 0.00
1998 |  |  |  | 5071.63 |  |  | 8760 |  |  |  | 550 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 105.26 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1999 |  |  |  | 4273.16 |  |  | 7344 |  |  |  | 550 | [10 empty] | 83.82 |  |  |  | 83.82 | [5 empty] | 88.69 |  |  | 83.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.18 |  |  |  |  | 0.00
2000 |  |  |  | 4107.46 |  |  | 7477 |  |  |  | 550 | [10 empty] | 85.11 |  |  |  | 85.11 | [5 empty] | 85.02 |  |  | 85.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.89 |  |  |  |  | 0.00
2001 |  |  |  | 3971.26 |  |  | 7235 |  |  |  | 550 | [10 empty] | 82.58 |  |  |  | 82.58 | [5 empty] | 82.43 |  |  | 82.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.42 |  |  |  |  | 0.00
2002 |  |  |  | 4516.13 |  |  | 8228 |  |  |  | 550 | [10 empty] | 93.92 |  |  |  | 93.92 | [5 empty] | 93.73 |  |  | 93.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.08 |  |  |  |  | 0.00
2003 |  |  |  | 3542.02 |  |  | 6300 |  |  |  | 550 | [10 empty] | 71.91 |  |  |  | 71.91 | [5 empty] | 73.52 |  |  | 71.92 |  |  |  | 21.43 |  | 19.62 | [8 empty] | 8.47 |  |  |  |  | 0.00
2004 |  |  |  | 3864.74 |  |  | 6862 |  |  |  | 550 | [10 empty] | 78.10 |  |  |  | 78.10 | [5 empty] | 80.00 |  |  | 78.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.90 |  |  |  |  | 0.00
2005 |  |  |  | 4252.61 |  |  | 7571 |  |  |  | 550 | [10 empty] | 85.99 |  |  |  | 85.99 | [5 empty] | 88.27 |  |  | 86.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.01 |  |  |  |  | 0.00
2006 |  |  |  | 4316.86 |  |  | 7704 |  |  |  | 550 | [10 empty] | 87.90 |  |  |  | 87.90 | [5 empty] | 89.60 |  |  | 87.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.10 |  |  |  |  | 0.00
2007 |  |  |  | 4663.24 |  |  | 8339 |  |  |  | 550 | [10 empty] | 94.82 |  |  |  | 94.82 | [5 empty] | 96.79 |  |  | 95.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.18 |  |  |  |  | 0.00
2008 |  |  |  | 3018.25 |  |  | 5411 |  |  |  | 550 | [10 empty] | 61.45 |  |  |  | 61.45 | [5 empty] | 62.47 |  |  | 61.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 38.55 |  |  |  |  | 0.00
2009 |  |  |  | 3436.45 |  |  | 6131 |  |  |  | 550 | [10 empty] | 69.58 |  |  |  | 69.58 | [5 empty] | 71.33 |  |  | 69.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.42 |  |  |  |  | 0.00
2010 |  |  |  | 4043.32 |  |  | 7232 |  |  |  | 550 | [10 empty] | 82.14 |  |  |  | 82.14 | [5 empty] | 83.92 |  |  | 82.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.86 |  |  |  |  | 0.00
2011 |  |  |  | 3194.68 |  |  | 5688 |  |  |  | 550 | [10 empty] | 64.88 |  |  |  | 64.88 | [5 empty] | 66.31 |  |  | 64.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 35.12 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 550 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1991 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 58
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 960
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 51
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 2687
Subtotal | [22 empty] | 8784 | [14 empty] | 3698 |  |  |  | 58
Total | [22 empty] | 8784 | [14 empty] | 3756
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1991 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 57
Total | [37 empty] | 57
Highlights (2020)
Implementation of emergency safety measures for considering the Accident of Fukushima Dai-ich and Dai-ni Nuclear Power Stations Enforcement of Comprehensive Assessment for the Safety of Nuclear Power Reactor Facility(so-called Stress Test)

## TOMARI-3
2020 Operating Experience
JP-64 | [7 empty] | TOMARI-3 | [26 empty] | JAPAN
Status at end of year | [6 empty] | : | Operational
Operator | [6 empty] | : | HEPCO (HOKKAIDO ELECTRIC POWER CO., INC.)
Owner | [6 empty] | : | HEPCO (HOKKAIDO ELECTRIC POWER CO., INC.)
Reactor Supplier | [6 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [6 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [26 empty] | Key Dates
Reactor type and model | [11 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 2004-11-18
Thermal power | [11 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2009-03-20
Gross electrical power | [11 empty] | : |  |  | 912 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2009-12-22
Reference unit power (net) | [11 empty] | : |  |  | 866 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 11 years
Design Characteristics
| Primary Systems | [27 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [12 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [12 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [12 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [12 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.283
| Average fuel enrichment [% of U235] | [12 empty] | : |  |  | 4.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [12 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [12 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [12 empty] | : |  |  | 49000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [12 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.48
| Active core height/length [m] | [12 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 21
| Number of fissile fuel assemblies/bundles | [12 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [12 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [12 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [12 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [12 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [17 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [17 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [17 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [17 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [17 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
|  |  |  | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [12 empty] | : |  |  | 19620 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [12 empty] | : |  |  | 19.74 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [12 empty] | : |  |  | 19.74 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 80.26 %
Cumulative Load Factor (LF) | [12 empty] | : |  |  | 20.59 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [12 empty] | : |  |  | 19.77 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2009 |  |  | 2426.85 |  |  | 3603 |  |  |  | 866 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  | 7904.94 |  |  | 8760 |  |  |  | 866 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 104.20 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  | 6556.84 |  |  | 7283 |  |  |  | 866 | [10 empty] | 82.88 |  |  |  | 82.88 | [5 empty] | 86.43 |  |  | 83.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.12 |  |  |  |  | 0.00
2012 |  |  | 2731.82 |  |  | 3023 |  |  |  | 866 | [10 empty] | 34.36 |  |  |  | 34.37 | [5 empty] | 35.91 |  |  | 34.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 65.63 |  |  |  |  | 0.01
2013 |  |  | 0.00 |  |  | 0 |  |  |  | 866 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  | 0.00 |  |  | 0 |  |  |  | 866 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  | 0.00 |  |  | 0 |  |  |  | 866 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  | 0.00 |  |  | 0 |  |  |  | 866 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  | 0.00 |  |  | 0 |  |  |  | 866 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  | 0.00 |  |  | 0 |  |  |  | 866 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  | 0.00 |  |  | 0 |  |  |  | 866 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  | 0.00 |  |  | 0 |  |  |  | 866 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[22 empty] | 2020 | [14 empty] | 2009 to 2020
Outage Cause | [21 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[22 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [34 empty] | 316
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [19 empty] | 8784 | [14 empty] | 7421
Subtotal | [21 empty] | 8784 | [14 empty] | 7737
Total | [21 empty] | 8784 | [14 empty] | 7737
Equipment Related Unplanned Full Outages, Analysis by System
System | [21 empty] | 2020 | [14 empty] | 2009 to 2020
[22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
Total
Highlights (2020)
Implementation of emergency safety measures for considering the Accident of Fukushima Dai-ich and Dai-ni Nuclear Power Stations Enforcement of Comprehensive Assessment for the Safety of Nuclear Power Reactor Facility(so-called Stress Test)

## TSURUGA-2
2020 Operating Experience
JP-34 | [8 empty] | TSURUGA-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JAPCO (JAPAN ATOMIC POWER CO.)
Owner | [7 empty] | : | JAPCO (JAPAN ATOMIC POWER CO.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (4-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-11-06
Thermal power | [12 empty] | : |  |  | 3411 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-06-19
Gross electrical power | [12 empty] | : |  |  | 1160 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-02-17
Reference unit power (net) | [12 empty] | : |  |  | 1108 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.07 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.76
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 185893 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.38 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 55.56 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.8 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 55.67 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 39.53 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 55.78 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.11 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 55.76 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 8751.33 |  |  | 8028 |  |  |  | 1115 | [10 empty] | 94.99 |  |  |  | 94.99 | [5 empty] | 94.65 |  |  | 95.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.01 |  |  |  |  | 0.00
1988 |  |  |  | 7939.68 |  |  | 7243 |  |  |  | 1115 | [10 empty] | 81.26 |  |  |  | 81.26 | [5 empty] | 81.07 |  |  | 82.46 |  |  |  | 2.39 |  | 1.99 | [8 empty] | 16.75 |  |  |  |  | 0.00
1989 |  |  |  | 7507.68 |  |  | 6814 |  |  |  | 1115 | [10 empty] | 77.03 |  |  |  | 77.03 | [5 empty] | 76.86 |  |  | 77.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.97 |  |  |  |  | 0.00
1990 |  |  |  | 7200.99 |  |  | 6462 |  |  |  | 1115 | [10 empty] | 72.87 |  |  |  | 72.87 | [5 empty] | 73.72 |  |  | 73.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.13 |  |  |  |  | 0.00
1991 |  |  |  | 9259.18 |  |  | 8338 |  |  |  | 1115 | [10 empty] | 95.07 |  |  |  | 95.07 | [5 empty] | 94.80 |  |  | 95.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.93 |  |  |  |  | 0.00
1992 |  |  |  | 8118.69 |  |  | 7310 |  |  |  | 1115 | [10 empty] | 82.52 |  |  |  | 82.52 | [5 empty] | 82.89 |  |  | 83.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.48 |  |  |  |  | 0.00
1993 |  |  |  | 7844.10 |  |  | 7086 |  |  |  | 1115 | [10 empty] | 80.15 |  |  |  | 80.15 | [5 empty] | 80.31 |  |  | 80.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.85 |  |  |  |  | 0.00
1994 |  |  |  | 7814.60 |  |  | 7080 |  |  |  | 1115 | [10 empty] | 80.23 |  |  |  | 80.23 | [5 empty] | 80.01 |  |  | 80.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.77 |  |  |  |  | 0.00
1995 |  |  |  | 9220.46 |  |  | 8290 |  |  |  | 1115 | [10 empty] | 94.55 |  |  |  | 94.55 | [5 empty] | 94.40 |  |  | 94.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.45 |  |  |  |  | 0.00
1996 |  |  |  | 8092.28 |  |  | 7325 |  |  |  | 1115 | [10 empty] | 82.96 |  |  |  | 82.96 | [5 empty] | 82.62 |  |  | 83.39 |  |  |  | 2.36 |  | 2.00 | [8 empty] | 15.03 |  |  |  |  | 0.00
1997 |  |  |  | 6522.19 |  |  | 5946 |  |  |  | 1115 | [10 empty] | 66.98 |  |  |  | 66.98 | [5 empty] | 66.78 |  |  | 67.88 |  |  |  | 10.59 |  | 7.93 | [8 empty] | 25.08 |  |  |  |  | 0.00
1998 |  |  |  | 8534.55 |  |  | 7724 |  |  |  | 1115 | [10 empty] | 91.96 |  |  |  | 91.96 | [5 empty] | 87.38 |  |  | 88.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.04 |  |  |  |  | 0.00
1999 |  |  |  | 5131.68 |  |  | 4615 |  |  |  | 1115 | [10 empty] | 52.68 |  |  |  | 52.68 | [5 empty] | 52.54 |  |  | 52.68 |  |  |  | 41.73 |  | 37.73 | [8 empty] | 9.60 |  |  |  |  | 0.00
2000 |  |  |  | 8993.76 |  |  | 8087 |  |  |  | 1115 | [10 empty] | 92.06 |  |  |  | 92.06 | [5 empty] | 91.83 |  |  | 92.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.94 |  |  |  |  | 0.00
2001 |  |  |  | 8072.72 |  |  | 7267 |  |  |  | 1115 | [10 empty] | 82.95 |  |  |  | 82.95 | [5 empty] | 82.65 |  |  | 82.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.05 |  |  |  |  | 0.00
2002 |  |  |  | 8695.54 |  |  | 7742 |  |  |  | 1115 | [10 empty] | 88.36 |  |  |  | 88.36 | [5 empty] | 89.03 |  |  | 88.38 |  |  |  | 3.67 |  | 3.37 | [8 empty] | 8.28 |  |  |  |  | 0.00
2003 |  |  |  | 8460.92 |  |  | 7418 |  |  |  | 1115 | [10 empty] | 84.67 |  |  |  | 84.67 | [5 empty] | 86.62 |  |  | 84.68 |  |  |  | 0.00 |  | 4.85 | [8 empty] | 10.48 |  |  |  |  | 0.00
2004 |  |  |  | 9447.05 |  |  | 8367 |  |  |  | 1115 | [10 empty] | 95.24 |  |  |  | 95.24 | [5 empty] | 96.46 |  |  | 95.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.76 |  |  |  |  | 0.00
2005 |  |  |  | 7693.61 |  |  | 6854 |  |  |  | 1115 | [10 empty] | 77.59 |  |  |  | 77.59 | [5 empty] | 78.77 |  |  | 78.24 |  |  |  | 7.98 |  | 6.73 | [8 empty] | 15.68 |  |  |  |  | 0.00
2006 |  |  |  | 6250.76 |  |  | 5634 |  |  |  | 1110 | [10 empty] | 63.34 |  |  |  | 63.34 | [5 empty] | 64.28 |  |  | 64.32 |  |  |  | 21.62 |  | 25.03 | [8 empty] | 11.62 |  |  |  |  | 0.00
2007 |  |  |  | 6065.32 |  |  | 5688 |  |  |  | 1110 | [10 empty] | 61.18 |  |  |  | 64.86 | [5 empty] | 62.38 |  |  | 64.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 35.14 |  |  |  |  | 3.68
2008 |  |  |  | 992.70 |  |  | 957 |  |  |  | 1110 | [10 empty] | 10.04 |  |  |  | 10.04 | [5 empty] | 10.18 |  |  | 10.89 |  |  |  | 74.44 |  | 29.24 | [8 empty] | 60.72 |  |  |  |  | 0.00
2009 |  |  |  | 8701.08 |  |  | 7680 |  |  |  | 1108 | [10 empty] | 87.34 |  |  |  | 87.34 | [5 empty] | 89.65 |  |  | 87.67 |  |  |  | 12.66 |  | 12.65 | [8 empty] | 0.01 |  |  |  |  | 0.00
2010 |  |  |  | 6178.19 |  |  | 5446 |  |  |  | 1108 | [10 empty] | 61.65 |  |  |  | 61.65 | [5 empty] | 63.65 |  |  | 62.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 38.35 |  |  |  |  | 0.00
2011 |  |  |  | 3526.88 |  |  | 3041 |  |  |  | 1108 | [10 empty] | 34.65 |  |  |  | 34.65 | [5 empty] | 36.34 |  |  | 34.71 |  |  |  | 47.29 |  | 31.10 | [8 empty] | 34.25 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1108 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 405
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1127
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 8784 | [14 empty] | 2341
L. |  | Human factor related | [39 empty] | 4
P. |  | Fire | [39 empty] | 9
Subtotal | [22 empty] | 8784 | [14 empty] | 3468 |  |  |  | 418
Total | [22 empty] | 8784 | [14 empty] | 3886
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 80
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 157
14. |  |  | Safety Systems | [34 empty] | 18
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
31. |  |  | Turbine and auxiliaries | [34 empty] | 116
32. |  |  | Feedwater and Main Steam System | [34 empty] | 28
Total | [37 empty] | 411
Highlights (2020)
Appropriate for implementation in new regulatory standards