## LAGUNA VERDE-1
2020 Operating Experience
MX-1 | [8 empty] | LAGUNA VERDE-1 | [26 empty] | MEXICO
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CFE (COMISION FEDERAL DE ELECTRICIDAD)
Owner | [7 empty] | : | CFE (COMISION FEDERAL DE ELECTRICIDAD)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-10-01
Thermal power | [12 empty] | : |  |  | 2317 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1989-04-13
Gross electrical power | [12 empty] | : |  |  | 805 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-07-29
Reference unit power (net) | [12 empty] | : |  |  | 777 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 278
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.81 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 17.5 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 3
| Part of the core refuelled [%] | [13 empty] | : |  |  | 28.83 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 42635.75 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.62 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.15
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 444 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.06 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 109 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5394.16 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.57 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.8 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.99 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.69 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.32 %
Load Factor (LF) | [18 empty] | : | 79.03 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 6.88 %
Operating Factor (OF) | [18 empty] | : | 86.85 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1155 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 581.25 | 543.30 |  |  |  | 575.85 |  | 553.90 | [8 empty] | 493.65 |  |  | 406.49 | [6 empty] | 421.72 |  | 179.19 |  |  |  | 0.00 |  |  | 523.09 |  |  | 541.77 | [9 empty] | 573.96 |  |  | 5394.16
EAF [%] |  |  |  |  | 99.65 | 99.36 |  |  |  | 99.14 |  | 99.15 | [8 empty] | 85.39 |  |  | 72.66 | [6 empty] | 72.95 |  | 31.00 |  |  |  | 0.00 |  |  | 90.50 |  |  | 96.84 | [9 empty] | 98.83 |  |  | 78.80
UCF [%] |  |  |  |  | 99.65 | 99.36 |  |  |  | 99.14 |  | 99.46 | [8 empty] | 99.88 |  |  | 99.95 | [6 empty] | 99.82 |  | 43.79 |  |  |  | 0.00 |  |  | 90.85 |  |  | 96.89 | [9 empty] | 98.83 |  |  | 85.69
LF [%] |  |  |  |  | 100.55 | 100.46 |  |  |  | 99.61 |  | 99.15 | [8 empty] | 85.39 |  |  | 72.66 | [6 empty] | 72.95 |  | 31.00 |  |  |  | 0.00 |  |  | 90.36 |  |  | 96.84 | [9 empty] | 99.29 |  |  | 79.03
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 45.43 |  |  |  | 0.00 |  |  | 96.11 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.85
FLR [%] |  |  |  |  | 0.00 | 0.23 |  |  |  | 0.05 |  | 0.21 | [8 empty] | 0.07 |  |  | 0.00 | [6 empty] | 0.06 |  | 3.21 |  |  |  | 0.00 |  |  | 0.89 |  |  | 2.76 | [9 empty] | 0.29 |  |  | 0.57
UCL [%] |  |  |  |  | 0.00 | 0.23 |  |  |  | 0.05 |  | 0.21 | [8 empty] | 0.07 |  |  | 0.00 | [6 empty] | 0.06 |  | 1.45 |  |  |  | 51.00 |  |  | 4.59 |  |  | 2.75 | [9 empty] | 0.29 |  |  | 4.99
PUF [%] |  |  |  |  | 0.34 | 0.41 |  |  |  | 0.81 |  | 0.32 | [8 empty] | 0.05 |  |  | 0.05 | [6 empty] | 0.12 |  | 54.76 |  |  |  | 49.00 |  |  | 4.56 |  |  | 0.35 | [9 empty] | 0.88 |  |  | 9.32
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.31 | [8 empty] | 14.49 |  |  | 27.29 | [6 empty] | 26.87 |  | 12.79 |  |  |  | 0.00 |  |  | 0.35 |  |  | 0.05 | [9 empty] | 0.00 |  |  | 6.88
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 141120.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.61 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.04 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.48 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.35 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.17 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.91 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.31 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.54 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 2775.82 |  |  | 5370 |  |  |  | 640 | [10 empty] | 87.58 |  |  |  | 87.58 | [5 empty] | 86.55 |  |  | 96.68 |  |  |  | 11.65 |  | 11.55 | [8 empty] | 0.87 |  |  |  |  | 0.00
1991 |  |  |  | 4062.09 |  |  | 7022 |  |  |  | 640 | [10 empty] | 74.45 |  |  |  | 74.45 | [5 empty] | 72.45 |  |  | 80.16 |  |  |  | 2.12 |  | 1.61 | [8 empty] | 23.94 |  |  |  |  | 0.00
1992 |  |  |  | 3746.44 |  |  | 7024 |  |  |  | 654 | [10 empty] | 70.41 |  |  |  | 70.41 | [5 empty] | 65.22 |  |  | 79.96 |  |  |  | 16.16 |  | 13.57 | [8 empty] | 16.02 |  |  |  |  | 0.00
1993 |  |  |  | 4724.42 |  |  | 7851 |  |  |  | 654 | [10 empty] | 90.57 |  |  |  | 90.57 | [5 empty] | 82.46 |  |  | 89.62 |  |  |  | 8.80 |  | 8.74 | [8 empty] | 0.68 |  |  |  |  | 0.00
1994 |  |  |  | 4061.96 |  |  | 7095 |  |  |  | 628 | [10 empty] | 73.84 |  |  |  | 77.82 | [5 empty] | 73.84 |  |  | 80.99 |  |  |  | 10.85 |  | 9.47 | [8 empty] | 12.71 |  |  |  |  | 3.99
1995 |  |  |  | 4154.06 |  |  | 7128 |  |  |  | 628 | [10 empty] | 75.51 |  |  |  | 78.07 | [5 empty] | 75.51 |  |  | 81.37 |  |  |  | 10.00 |  | 8.67 | [8 empty] | 13.26 |  |  |  |  | 2.56
1996 |  |  |  | 3442.34 |  |  | 6628 |  |  |  | 655 | [10 empty] | 68.80 |  |  |  | 68.81 | [5 empty] | 59.83 |  |  | 75.46 |  |  |  | 8.93 |  | 6.75 | [8 empty] | 24.44 |  |  |  |  | 0.01
1997 |  |  |  | 5218.80 |  |  | 8577 |  |  |  | 615 | [10 empty] | 95.87 |  |  |  | 95.97 | [5 empty] | 96.87 |  |  | 97.91 |  |  |  | 3.71 |  | 3.70 | [8 empty] | 0.33 |  |  |  |  | 0.10
1998 |  |  |  | 4412.45 |  |  | 7359 |  |  |  | 655 | [10 empty] | 81.67 |  |  |  | 82.19 | [5 empty] | 76.90 |  |  | 84.01 |  |  |  | 8.24 |  | 7.38 | [8 empty] | 10.43 |  |  |  |  | 0.52
1999 |  |  |  | 4450.97 |  |  | 7466 |  |  |  | 670 | [10 empty] | 81.47 |  |  |  | 82.84 | [5 empty] | 75.79 |  |  | 85.23 |  |  |  | 6.08 |  | 5.36 | [8 empty] | 11.80 |  |  |  |  | 1.36
2000 |  |  |  | 4577.65 |  |  | 7409 |  |  |  | 645 | [10 empty] | 80.27 |  |  |  | 80.56 | [5 empty] | 80.80 |  |  | 84.35 |  |  |  | 5.08 |  | 4.31 | [8 empty] | 15.13 |  |  |  |  | 0.29
2001 |  |  |  | 4144.30 |  |  | 6808 |  |  |  | 645 | [10 empty] | 73.16 |  |  |  | 74.88 | [5 empty] | 73.35 |  |  | 77.72 |  |  |  | 9.31 |  | 7.68 | [8 empty] | 17.43 |  |  |  |  | 1.72
2002 |  |  |  | 4196.25 |  |  | 6876 |  |  |  | 680 | [10 empty] | 75.83 |  |  |  | 76.41 | [5 empty] | 70.44 |  |  | 78.49 |  |  |  | 5.49 |  | 10.73 | [8 empty] | 12.87 |  |  |  |  | 0.58
2003 |  |  |  | 5415.44 |  |  | 8642 |  |  |  | 680 | [10 empty] | 97.60 |  |  |  | 97.94 | [5 empty] | 90.91 |  |  | 98.65 |  |  |  | 1.69 |  | 1.69 | [8 empty] | 0.37 |  |  |  |  | 0.34
2004 |  |  |  | 4168.90 |  |  | 6818 |  |  |  | 680 | [10 empty] | 75.16 |  |  |  | 75.94 | [5 empty] | 69.79 |  |  | 77.62 |  |  |  | 4.48 |  | 11.20 | [8 empty] | 12.86 |  |  |  |  | 0.78
2005 |  |  |  | 5007.75 |  |  | 7884 |  |  |  | 680 | [10 empty] | 88.20 |  |  |  | 88.82 | [5 empty] | 84.07 |  |  | 90.00 |  |  |  | 2.94 |  | 2.69 | [8 empty] | 8.49 |  |  |  |  | 0.61
2006 |  |  |  | 5529.73 |  |  | 8624 |  |  |  | 680 | [10 empty] | 97.55 |  |  |  | 97.55 | [5 empty] | 92.83 |  |  | 98.45 |  |  |  | 1.20 |  | 1.19 | [8 empty] | 1.26 |  |  |  |  | 0.00
2007 |  |  |  | 5027.19 |  |  | 7963 |  |  |  | 680 | [10 empty] | 89.41 |  |  |  | 89.62 | [5 empty] | 84.39 |  |  | 90.90 |  |  |  | 1.82 |  | 1.66 | [8 empty] | 8.71 |  |  |  |  | 0.22
2008 |  |  |  | 3797.81 |  |  | 6169 |  |  |  | 650 | [10 empty] | 67.88 |  |  |  | 68.38 | [5 empty] | 66.52 |  |  | 70.23 |  |  |  | 3.83 |  | 16.89 | [8 empty] | 14.73 |  |  |  |  | 0.50
2009 |  |  |  | 5454.49 |  |  | 8534 |  |  |  | 650 | [10 empty] | 95.01 |  |  |  | 95.01 | [5 empty] | 95.79 |  |  | 97.42 |  |  |  | 4.20 |  | 4.17 | [8 empty] | 0.83 |  |  |  |  | 0.00
2010 |  |  |  | 1886.55 |  |  | 3391 |  |  |  | 650 | [10 empty] | 41.69 |  |  |  | 42.59 | [5 empty] | 33.13 |  |  | 38.71 |  |  |  | 15.71 |  | 34.61 | [8 empty] | 22.80 |  |  |  |  | 0.90
2011 |  |  |  | 4921.75 |  |  | 7598 |  |  |  | 650 | [10 empty] | 84.20 |  |  |  | 84.30 | [5 empty] | 86.44 |  |  | 86.74 |  |  |  | 14.51 |  | 14.31 | [8 empty] | 1.39 |  |  |  |  | 0.10
2012 |  |  |  | 3418.65 |  |  | 5209 |  |  |  | 765 | [10 empty] | 51.49 |  |  |  | 54.22 | [5 empty] | 51.53 |  |  | 59.30 |  |  |  | 11.86 |  | 27.76 | [8 empty] | 18.02 |  |  |  |  | 2.72
2013 |  |  |  | 5719.46 |  |  | 8585 |  |  |  | 665 | [10 empty] | 97.44 |  |  |  | 97.46 | [5 empty] | 98.18 |  |  | 98.00 |  |  |  | 2.41 |  | 2.40 | [8 empty] | 0.13 |  |  |  |  | 0.03
2014 |  |  |  | 4875.98 |  |  | 7461 |  |  |  | 665 | [10 empty] | 81.84 |  |  |  | 81.84 | [5 empty] | 83.71 |  |  | 85.18 |  |  |  | 5.41 |  | 5.42 | [8 empty] | 12.74 |  |  |  |  | 0.00
2015 |  |  |  | 4741.77 |  |  | 7033 |  |  |  | 665 | [10 empty] | 79.88 |  |  |  | 79.91 | [5 empty] | 81.41 |  |  | 80.29 |  |  |  | 0.87 |  | 2.07 | [8 empty] | 18.02 |  |  |  |  | 0.03
2016 |  |  |  | 5096.56 |  |  | 6716 |  |  |  | 777 | [10 empty] | 77.02 |  |  |  | 78.38 | [5 empty] | 77.45 |  |  | 76.46 |  |  |  | 0.49 |  | 21.00 | [8 empty] | 0.61 |  |  |  |  | 1.36
2017 |  |  |  | 5014.49 |  |  | 7454 |  |  |  | 777 | [10 empty] | 73.49 |  |  |  | 83.38 | [5 empty] | 73.67 |  |  | 85.09 |  |  |  | 3.15 |  | 5.03 | [8 empty] | 11.59 |  |  |  |  | 9.90
2018 |  |  |  | 6496.56 |  |  | 8523 |  |  |  | 777 | [10 empty] | 95.17 |  |  |  | 95.89 | [5 empty] | 95.45 |  |  | 97.29 |  |  |  | 3.84 |  | 3.83 | [8 empty] | 0.28 |  |  |  |  | 0.72
2019 |  |  |  | 5803.84 |  |  | 7754 |  |  |  | 777 | [10 empty] | 85.13 |  |  |  | 86.42 | [5 empty] | 85.27 |  |  | 88.52 |  |  |  | 1.66 |  | 3.35 | [8 empty] | 10.23 |  |  |  |  | 1.29
2020 |  |  |  | 5394.16 |  |  | 7629 |  |  |  | 777 | [10 empty] | 78.80 |  |  |  | 85.69 | [5 empty] | 79.03 |  |  | 86.85 |  |  |  | 0.57 |  | 4.99 | [8 empty] | 9.32 |  |  |  |  | 6.88
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1990 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 395 | [14 empty] | 520
B. |  | Refuelling without maintenance | [35 empty] | 23
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 758 | [14 empty] | 723 |  |  |  | 18
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 161
E. |  | Testing of plant systems or components | [35 empty] | 69 |  |  |  | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 31
L. |  | Human factor related | [39 empty] | 87
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Z. |  | Other | [39 empty] | 35
Subtotal | [22 empty] | 758 |  |  |  | 395 | [10 empty] | 976 |  |  |  | 665 | [11 empty] | 33
Total | [22 empty] | 1153 | [14 empty] | 1674
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1990 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
12. |  |  | Reactor I&C Systems | [34 empty] | 71
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 44
14. |  |  | Safety Systems | [34 empty] | 5
15. |  |  | Reactor Cooling Systems | [34 empty] | 24
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 74
31. |  |  | Turbine and auxiliaries | [19 empty] | 395 | [14 empty] | 94
32. |  |  | Feedwater and Main Steam System | [34 empty] | 73
33. |  |  | Circulating Water System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 21
41. |  |  | Main Generator Systems | [34 empty] | 17
42. |  |  | Electrical Power Supply Systems | [34 empty] | 170
Total | [22 empty] | 395 | [14 empty] | 607

## LAGUNA VERDE-2
2020 Operating Experience
MX-2 | [8 empty] | LAGUNA VERDE-2 | [26 empty] | MEXICO
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CFE (COMISION FEDERAL DE ELECTRICIDAD)
Owner | [7 empty] | : | CFE (COMISION FEDERAL DE ELECTRICIDAD)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-06-01
Thermal power | [12 empty] | : |  |  | 2317 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1994-11-11
Gross electrical power | [12 empty] | : |  |  | 803 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1995-04-10
Reference unit power (net) | [12 empty] | : |  |  | 775 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 26 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 278
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.88 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 17.5 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 3
| Part of the core refuelled [%] | [13 empty] | : |  |  | 32.43 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45314.13 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.62 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.15
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 444 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.06 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 109 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5470.11 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.99 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.23 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.38 %
Unit Capability Factor (UCF) | [18 empty] | : | 81.31 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.31 %
Load Factor (LF) | [18 empty] | : | 80.36 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.08 %
Operating Factor (OF) | [18 empty] | : | 84.65 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1348 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 507.52 | 539.31 |  |  |  | 566.45 |  | 550.03 | [8 empty] | 512.23 |  |  | 548.31 | [6 empty] | 568.80 |  | 563.08 |  |  |  | 502.85 |  |  | 466.88 |  |  | 144.64 | [9 empty] | 0.00 |  |  | 5470.11
EAF [%] |  |  |  |  | 87.57 | 99.52 |  |  |  | 98.24 |  | 98.71 | [8 empty] | 88.84 |  |  | 98.26 | [6 empty] | 98.65 |  | 97.12 |  |  |  | 90.12 |  |  | 80.84 |  |  | 25.92 | [9 empty] | 0.00 |  |  | 80.23
UCF [%] |  |  |  |  | 87.57 | 99.52 |  |  |  | 98.31 |  | 99.32 | [8 empty] | 89.49 |  |  | 99.64 | [6 empty] | 99.60 |  | 99.47 |  |  |  | 93.54 |  |  | 83.55 |  |  | 26.73 | [9 empty] | 0.00 |  |  | 81.31
LF [%] |  |  |  |  | 88.02 | 99.98 |  |  |  | 98.24 |  | 98.71 | [8 empty] | 88.84 |  |  | 98.26 | [6 empty] | 98.65 |  | 97.66 |  |  |  | 90.12 |  |  | 80.97 |  |  | 25.92 | [9 empty] | 0.00 |  |  | 80.36
OF [%] |  |  |  |  | 89.92 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 91.67 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 35.14 | [9 empty] | 0.00 |  |  | 84.65
FLR [%] |  |  |  |  | 12.12 | 0.00 |  |  |  | 0.00 |  | 0.51 | [8 empty] | 10.42 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.20 |  |  |  | 2.50 |  |  | 0.00 |  |  | 35.69 | [9 empty] | 0.00 |  |  | 3.99
UCL [%] |  |  |  |  | 12.08 | 0.00 |  |  |  | 0.00 |  | 0.51 | [8 empty] | 10.41 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.20 |  |  |  | 2.40 |  |  | 0.00 |  |  | 14.83 | [9 empty] | 0.00 |  |  | 3.38
PUF [%] |  |  |  |  | 0.35 | 0.48 |  |  |  | 1.69 |  | 0.17 | [8 empty] | 0.10 |  |  | 0.36 | [6 empty] | 0.40 |  | 0.33 |  |  |  | 4.06 |  |  | 16.45 |  |  | 58.44 | [9 empty] | 100.00 |  |  | 15.31
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.07 |  | 0.61 | [8 empty] | 0.65 |  |  | 1.38 | [6 empty] | 0.95 |  | 2.34 |  |  |  | 3.42 |  |  | 2.71 |  |  | 0.81 | [9 empty] | 0.00 |  |  | 1.08
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 126629.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.08 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.22 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.07 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.71 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.15 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1995 |  |  |  | 3379.40 |  |  | 5687 |  |  |  | 628 | [10 empty] | 84.48 |  |  |  | 85.92 | [5 empty] | 84.48 |  |  | 89.28 |  |  |  | 7.13 |  | 6.59 | [8 empty] | 7.49 |  |  |  |  | 1.44
1996 |  |  |  | 3668.41 |  |  | 6657 |  |  |  | 619 | [10 empty] | 70.97 |  |  |  | 71.67 | [5 empty] | 67.47 |  |  | 75.79 |  |  |  | 3.52 |  | 2.61 | [8 empty] | 25.71 |  |  |  |  | 0.71
1997 |  |  |  | 4805.53 |  |  | 7897 |  |  |  | 627 | [10 empty] | 88.94 |  |  |  | 89.04 | [5 empty] | 87.49 |  |  | 90.15 |  |  |  | 0.58 |  | 0.52 | [8 empty] | 10.44 |  |  |  |  | 0.10
1998 |  |  |  | 4411.90 |  |  | 7609 |  |  |  | 655 | [10 empty] | 83.02 |  |  |  | 85.58 | [5 empty] | 76.89 |  |  | 86.86 |  |  |  | 1.14 |  | 0.98 | [8 empty] | 13.44 |  |  |  |  | 2.56
1999 |  |  |  | 5110.57 |  |  | 8459 |  |  |  | 668 | [10 empty] | 92.29 |  |  |  | 93.25 | [5 empty] | 87.32 |  |  | 96.56 |  |  |  | 4.61 |  | 4.51 | [8 empty] | 2.24 |  |  |  |  | 0.96
2000 |  |  |  | 3339.07 |  |  | 5865 |  |  |  | 645 | [10 empty] | 56.63 |  |  |  | 58.56 | [5 empty] | 58.93 |  |  | 66.77 |  |  |  | 29.16 |  | 24.10 | [8 empty] | 17.34 |  |  |  |  | 1.93
2001 |  |  |  | 4228.06 |  |  | 6952 |  |  |  | 645 | [10 empty] | 74.74 |  |  |  | 74.80 | [5 empty] | 74.83 |  |  | 79.36 |  |  |  | 7.10 |  | 5.72 | [8 empty] | 19.48 |  |  |  |  | 0.06
2002 |  |  |  | 5161.00 |  |  | 8273 |  |  |  | 680 | [10 empty] | 91.49 |  |  |  | 91.54 | [5 empty] | 86.63 |  |  | 94.43 |  |  |  | 6.98 |  | 7.69 | [8 empty] | 0.77 |  |  |  |  | 0.05
2003 |  |  |  | 4604.83 |  |  | 7359 |  |  |  | 680 | [10 empty] | 82.15 |  |  |  | 82.49 | [5 empty] | 77.30 |  |  | 84.01 |  |  |  | 3.94 |  | 4.40 | [8 empty] | 13.11 |  |  |  |  | 0.34
2004 |  |  |  | 4578.18 |  |  | 7449 |  |  |  | 680 | [10 empty] | 82.97 |  |  |  | 83.80 | [5 empty] | 76.65 |  |  | 84.80 |  |  |  | 0.49 |  | 3.32 | [8 empty] | 12.88 |  |  |  |  | 0.82
2005 |  |  |  | 5310.30 |  |  | 8611 |  |  |  | 680 | [10 empty] | 96.48 |  |  |  | 96.90 | [5 empty] | 89.15 |  |  | 98.30 |  |  |  | 1.10 |  | 1.08 | [8 empty] | 2.02 |  |  |  |  | 0.42
2006 |  |  |  | 4870.21 |  |  | 8003 |  |  |  | 680 | [10 empty] | 90.25 |  |  |  | 90.34 | [5 empty] | 81.76 |  |  | 91.36 |  |  |  | 0.97 |  | 0.88 | [8 empty] | 8.78 |  |  |  |  | 0.09
2007 |  |  |  | 4920.19 |  |  | 8013 |  |  |  | 680 | [10 empty] | 89.94 |  |  |  | 90.13 | [5 empty] | 82.60 |  |  | 91.47 |  |  |  | 1.94 |  | 1.79 | [8 empty] | 8.09 |  |  |  |  | 0.19
2008 |  |  |  | 5560.95 |  |  | 8730 |  |  |  | 650 | [10 empty] | 98.29 |  |  |  | 98.29 | [5 empty] | 97.40 |  |  | 99.39 |  |  |  | 1.27 |  | 1.27 | [8 empty] | 0.44 |  |  |  |  | 0.00
2009 |  |  |  | 4653.65 |  |  | 7386 |  |  |  | 650 | [10 empty] | 81.93 |  |  |  | 82.40 | [5 empty] | 81.73 |  |  | 84.32 |  |  |  | 2.15 |  | 1.81 | [8 empty] | 15.79 |  |  |  |  | 0.48
2010 |  |  |  | 3705.88 |  |  | 6289 |  |  |  | 650 | [10 empty] | 65.40 |  |  |  | 66.85 | [5 empty] | 65.08 |  |  | 71.79 |  |  |  | 2.96 |  | 3.30 | [8 empty] | 29.85 |  |  |  |  | 1.44
2011 |  |  |  | 4391.62 |  |  | 7111 |  |  |  | 650 | [10 empty] | 75.73 |  |  |  | 75.95 | [5 empty] | 77.13 |  |  | 81.18 |  |  |  | 7.95 |  | 10.68 | [8 empty] | 13.37 |  |  |  |  | 0.22
2012 |  |  |  | 4993.39 |  |  | 6854 |  |  |  | 765 | [10 empty] | 73.60 |  |  |  | 74.46 | [5 empty] | 74.31 |  |  | 78.03 |  |  |  | 3.76 |  | 16.14 | [8 empty] | 9.41 |  |  |  |  | 0.86
2013 |  |  |  | 5657.68 |  |  | 8522 |  |  |  | 665 | [10 empty] | 97.76 |  |  |  | 97.79 | [5 empty] | 97.12 |  |  | 97.28 |  |  |  | 2.06 |  | 2.05 | [8 empty] | 0.16 |  |  |  |  | 0.03
2014 |  |  |  | 4435.62 |  |  | 6705 |  |  |  | 665 | [10 empty] | 74.95 |  |  |  | 75.25 | [5 empty] | 76.15 |  |  | 76.55 |  |  |  | 6.61 |  | 11.68 | [8 empty] | 13.07 |  |  |  |  | 0.30
2015 |  |  |  | 6442.96 |  |  | 8600 |  |  |  | 775 | [10 empty] | 94.98 |  |  |  | 95.59 | [5 empty] | 94.91 |  |  | 98.18 |  |  |  | 2.46 |  | 2.42 | [8 empty] | 2.00 |  |  |  |  | 0.61
2016 |  |  |  | 5175.73 |  |  | 7194 |  |  |  | 775 | [10 empty] | 76.05 |  |  |  | 80.56 | [5 empty] | 76.03 |  |  | 81.90 |  |  |  | 2.96 |  | 2.46 | [8 empty] | 16.98 |  |  |  |  | 4.51
2017 |  |  |  | 5557.43 |  |  | 7526 |  |  |  | 775 | [10 empty] | 81.66 |  |  |  | 84.57 | [5 empty] | 81.86 |  |  | 85.91 |  |  |  | 3.33 |  | 3.89 | [8 empty] | 11.54 |  |  |  |  | 2.91
2018 |  |  |  | 6703.77 |  |  | 8726 |  |  |  | 775 | [10 empty] | 98.48 |  |  |  | 99.16 | [5 empty] | 98.74 |  |  | 99.61 |  |  |  | 0.45 |  | 0.45 | [8 empty] | 0.38 |  |  |  |  | 0.68
2019 |  |  |  | 5076.89 |  |  | 7096 |  |  |  | 775 | [10 empty] | 74.68 |  |  |  | 76.97 | [5 empty] | 74.78 |  |  | 81.00 |  |  |  | 9.78 |  | 12.08 | [8 empty] | 10.95 |  |  |  |  | 2.29
2020 |  |  |  | 5470.11 |  |  | 7435 |  |  |  | 775 | [10 empty] | 80.23 |  |  |  | 81.31 | [5 empty] | 80.36 |  |  | 84.65 |  |  |  | 3.99 |  | 3.38 | [8 empty] | 15.31 |  |  |  |  | 1.08
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1995 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 221 | [14 empty] | 294
B. |  | Refuelling without maintenance | [35 empty] | 25
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1128 | [14 empty] | 738
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 23
E. |  | Testing of plant systems or components | [35 empty] | 35
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 6
Z. |  | Other | [39 empty] | 47
Subtotal | [22 empty] | 1128 |  |  |  | 221 | [10 empty] | 821 |  |  |  | 343 | [11 empty] | 10
Total | [22 empty] | 1349 | [14 empty] | 1174
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1995 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [19 empty] | 221 | [14 empty] | 27
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
16. |  |  | Steam generation systems | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 18
31. |  |  | Turbine and auxiliaries | [34 empty] | 50
32. |  |  | Feedwater and Main Steam System | [34 empty] | 32
33. |  |  | Circulating Water System | [34 empty] | 12
34. |  |  | Miscellaneous Systems | [34 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 28
42. |  |  | Electrical Power Supply Systems | [34 empty] | 99
Total | [22 empty] | 221 | [14 empty] | 292