## CHASNUPP-1
2020 Operating Experience
PK-2 | [8 empty] | CHASNUPP-1 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | STW (Shanghai Turbine Works)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1993-08-01
Thermal power | [12 empty] | : |  |  | 999 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2000-06-13
Gross electrical power | [12 empty] | : |  |  | 325 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2000-09-15
Reference unit power (net) | [12 empty] | : |  |  | 300 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 20 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.26
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 14 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 30000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.486 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.34
| Active core height/length [m] | [13 empty] | : |  |  | 2.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.59 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2277.56 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.31 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.43 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.15 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.65 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.2 %
Load Factor (LF) | [18 empty] | : | 86.43 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.22 %
Operating Factor (OF) | [18 empty] | : | 87.45 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1102 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 108.09 |  |  |  | 217.12 |  | 216.51 | [8 empty] | 222.25 |  |  | 214.62 | [6 empty] | 220.91 |  | 203.63 |  |  |  | 211.32 |  |  | 223.65 |  |  | 215.56 | [9 empty] | 223.91 |  |  | 2277.56
EAF [%] |  |  |  |  | 0.00 | 51.30 |  |  |  | 96.74 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.74 |  | 91.96 |  |  |  | 97.37 |  |  | 100.00 |  |  | 99.46 | [9 empty] | 100.00 |  |  | 86.43
UCF [%] |  |  |  |  | 0.00 | 51.30 |  |  |  | 96.74 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.74 |  | 91.96 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.46 | [9 empty] | 100.00 |  |  | 86.65
LF [%] |  |  |  |  | 0.00 | 51.77 |  |  |  | 97.28 |  | 100.23 | [8 empty] | 99.57 |  |  | 99.36 | [6 empty] | 98.97 |  | 91.23 |  |  |  | 97.83 |  |  | 100.20 |  |  | 99.80 | [9 empty] | 100.32 |  |  | 86.43
OF [%] |  |  |  |  | 0.00 | 56.47 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 92.61 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.45
FLR [%] |  |  |  |  | 0.00 | 10.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 8.04 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.31
UCL [%] |  |  |  |  | 0.00 | 5.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 8.04 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.15
PUF [%] |  |  |  |  | 100.00 | 42.80 |  |  |  | 3.26 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.26 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.54 | [9 empty] | 0.00 |  |  | 12.20
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 2.63 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.22
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 41135.46 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.24 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.64 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.02 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.78 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.68 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.38 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.7 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2000 |  |  |  | 529.15 |  |  | 1860 |  |  |  | 300 | [10 empty] | 72.19 |  |  |  | 72.19 | [5 empty] | 68.69 |  |  | 72.43 |  |  |  | 19.54 |  | 17.53 | [8 empty] | 10.28 |  |  |  |  | 0.00
2001 |  |  |  | 1581.75 |  |  | 5918 |  |  |  | 300 | [10 empty] | 60.06 |  |  |  | 62.44 | [5 empty] | 60.19 |  |  | 67.56 |  |  |  | 37.40 |  | 37.31 | [8 empty] | 0.25 |  |  |  |  | 2.38
2002 |  |  |  | 1356.00 |  |  | 4790 |  |  |  | 300 | [10 empty] | 52.25 |  |  |  | 53.69 | [5 empty] | 51.60 |  |  | 54.68 |  |  |  | 20.87 |  | 16.73 | [8 empty] | 29.58 |  |  |  |  | 1.44
2003 |  |  |  | 1809.80 |  |  | 6879 |  |  |  | 300 | [10 empty] | 68.85 |  |  |  | 68.85 | [5 empty] | 68.87 |  |  | 78.53 |  |  |  | 21.84 |  | 24.04 | [8 empty] | 7.11 |  |  |  |  | 0.00
2004 |  |  |  | 1750.71 |  |  | 5949 |  |  |  | 300 | [10 empty] | 66.35 |  |  |  | 68.12 | [5 empty] | 66.44 |  |  | 67.73 |  |  |  | 4.20 |  | 13.12 | [8 empty] | 18.76 |  |  |  |  | 1.77
2005 |  |  |  | 2155.19 |  |  | 7458 |  |  |  | 300 | [10 empty] | 81.92 |  |  |  | 81.92 | [5 empty] | 82.01 |  |  | 85.14 |  |  |  | 3.83 |  | 3.26 | [8 empty] | 14.82 |  |  |  |  | 0.00
2006 |  |  |  | 2532.91 |  |  | 8569 |  |  |  | 300 | [10 empty] | 98.19 |  |  |  | 98.19 | [5 empty] | 96.38 |  |  | 97.82 |  |  |  | 0.91 |  | 0.90 | [8 empty] | 0.91 |  |  |  |  | 0.00
2007 |  |  |  | 1949.13 |  |  | 6669 |  |  |  | 300 | [10 empty] | 75.22 |  |  |  | 75.55 | [5 empty] | 74.17 |  |  | 76.13 |  |  |  | 2.98 |  | 7.76 | [8 empty] | 16.69 |  |  |  |  | 0.33
2008 |  |  |  | 1356.45 |  |  | 4795 |  |  |  | 300 | [10 empty] | 52.25 |  |  |  | 52.40 | [5 empty] | 51.47 |  |  | 54.59 |  |  |  | 1.70 |  | 0.90 | [8 empty] | 46.69 |  |  |  |  | 0.15
2009 |  |  |  | 2145.87 |  |  | 7379 |  |  |  | 300 | [10 empty] | 82.80 |  |  |  | 82.82 | [5 empty] | 81.65 |  |  | 84.24 |  |  |  | 10.86 |  | 11.69 | [8 empty] | 5.49 |  |  |  |  | 0.02
2010 |  |  |  | 2095.76 |  |  | 7160 |  |  |  | 300 | [10 empty] | 80.66 |  |  |  | 80.66 | [5 empty] | 79.75 |  |  | 81.74 |  |  |  | 0.96 |  | 0.96 | [8 empty] | 18.37 |  |  |  |  | 0.00
2011 |  |  |  | 2061.67 |  |  | 7008 |  |  |  | 300 | [10 empty] | 79.31 |  |  |  | 79.31 | [5 empty] | 78.45 |  |  | 80.00 |  |  |  | 3.04 |  | 2.83 | [8 empty] | 17.87 |  |  |  |  | 0.00
2012 |  |  |  | 2489.25 |  |  | 8370 |  |  |  | 300 | [10 empty] | 94.74 |  |  |  | 94.79 | [5 empty] | 94.46 |  |  | 95.29 |  |  |  | 2.34 |  | 2.27 | [8 empty] | 2.94 |  |  |  |  | 0.05
2013 |  |  |  | 2189.64 |  |  | 7481 |  |  |  | 300 | [10 empty] | 84.04 |  |  |  | 84.04 | [5 empty] | 83.32 |  |  | 85.40 |  |  |  | 4.53 |  | 4.38 | [8 empty] | 11.59 |  |  |  |  | 0.00
2014 |  |  |  | 2178.22 |  |  | 7434 |  |  |  | 300 | [10 empty] | 85.57 |  |  |  | 85.61 | [5 empty] | 82.89 |  |  | 84.86 |  |  |  | 3.64 |  | 3.23 | [8 empty] | 11.16 |  |  |  |  | 0.04
2015 |  |  |  | 1627.53 |  |  | 5831 |  |  |  | 300 | [10 empty] | 64.28 |  |  |  | 65.44 | [5 empty] | 61.93 |  |  | 66.56 |  |  |  | 3.33 |  | 15.04 | [8 empty] | 19.52 |  |  |  |  | 1.17
2016 |  |  |  | 2326.46 |  |  | 8291 |  |  |  | 300 | [10 empty] | 89.27 |  |  |  | 89.27 | [5 empty] | 88.28 |  |  | 94.39 |  |  |  | 0.82 |  | 5.23 | [8 empty] | 5.50 |  |  |  |  | 0.00
2017 |  |  |  | 2157.86 |  |  | 7391 |  |  |  | 300 | [10 empty] | 82.53 |  |  |  | 82.55 | [5 empty] | 82.11 |  |  | 84.37 |  |  |  | 2.48 |  | 2.10 | [8 empty] | 15.36 |  |  |  |  | 0.01
2018 |  |  |  | 2017.02 |  |  | 6950 |  |  |  | 300 | [10 empty] | 79.42 |  |  |  | 79.52 | [5 empty] | 76.75 |  |  | 79.34 |  |  |  | 7.15 |  | 6.12 | [8 empty] | 14.36 |  |  |  |  | 0.10
2019 |  |  |  | 2335.20 |  |  | 7907 |  |  |  | 300 | [10 empty] | 90.23 |  |  |  | 90.33 | [5 empty] | 88.86 |  |  | 90.26 |  |  |  | 2.44 |  | 2.26 | [8 empty] | 7.41 |  |  |  |  | 0.10
2020 |  |  |  | 2277.56 |  |  | 7682 |  |  |  | 300 | [10 empty] | 86.43 |  |  |  | 86.65 | [5 empty] | 86.43 |  |  | 87.45 |  |  |  | 1.31 |  | 1.15 | [8 empty] | 12.20 |  |  |  |  | 0.22
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2000 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 68 | [14 empty] | 529
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1034 | [14 empty] | 1042 |  |  |  | 7
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 67
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 94
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 15
L. |  | Human factor related | [39 empty] | 5
P. |  | Fire | [39 empty] | 6
Z. |  | Other | [39 empty] | 23
Subtotal | [22 empty] | 1034 |  |  |  | 68 | [10 empty] | 1113 |  |  |  | 571 | [11 empty] | 109
Total | [22 empty] | 1102 | [14 empty] | 1793
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2000 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 44
12. |  |  | Reactor I&C Systems | [34 empty] | 27
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 41
15. |  |  | Reactor Cooling Systems | [34 empty] | 124
16. |  |  | Steam generation systems | [34 empty] | 7
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [19 empty] | 68 | [14 empty] | 137
32. |  |  | Feedwater and Main Steam System | [34 empty] | 27
33. |  |  | Circulating Water System | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 35
42. |  |  | Electrical Power Supply Systems | [34 empty] | 102
Total | [22 empty] | 68 | [14 empty] | 564
Highlights (2020)
in the year 2020. plant faced one auto scram and refueling outage continued from Dec 2019 to Feb 2020.

## CHASNUPP-2
2020 Operating Experience
PK-3 | [8 empty] | CHASNUPP-2 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2005-12-28
Thermal power | [12 empty] | : |  |  | 999 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2011-03-14
Gross electrical power | [12 empty] | : |  |  | 325 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2011-05-18
Reference unit power (net) | [12 empty] | : |  |  | 300 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.26
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 14 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 32000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.486 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.34
| Active core height/length [m] | [13 empty] | : |  |  | 2.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.59 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2167.47 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.82 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.33 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.21 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.13 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.66 %
Load Factor (LF) | [18 empty] | : | 82.25 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.8 %
Operating Factor (OF) | [18 empty] | : | 84.01 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1405 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 229.02 | 213.74 |  |  |  | 229.90 |  | 221.97 | [8 empty] | 229.01 |  |  | 219.20 | [6 empty] | 225.20 |  | 198.97 |  |  |  | 28.52 |  |  | 30.83 |  |  | 206.91 | [9 empty] | 134.19 |  |  | 2167.47
EAF [%] |  |  |  |  | 99.65 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.72 |  |  | 99.99 | [6 empty] | 100.00 |  | 89.39 |  |  |  | 13.06 |  |  | 13.55 |  |  | 100.00 | [9 empty] | 61.36 |  |  | 81.33
UCF [%] |  |  |  |  | 99.65 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.72 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 24.07 |  |  | 13.55 |  |  | 100.00 | [9 empty] | 61.36 |  |  | 83.13
LF [%] |  |  |  |  | 102.61 | 102.37 |  |  |  | 103.00 |  | 102.76 | [8 empty] | 102.60 |  |  | 101.48 | [6 empty] | 100.90 |  | 89.14 |  |  |  | 13.20 |  |  | 13.81 |  |  | 95.79 | [9 empty] | 60.12 |  |  | 82.25
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 24.44 |  |  | 20.16 |  |  | 100.00 | [9 empty] | 64.11 |  |  | 84.01
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 44.93 |  |  | 0.00 | [9 empty] | 38.64 |  |  | 4.82
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 11.05 |  |  | 0.00 | [9 empty] | 38.64 |  |  | 4.21
PUF [%] |  |  |  |  | 0.35 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.28 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 75.93 |  |  | 75.40 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.66
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 10.61 |  |  |  | 11.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.80
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 21686.37 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.81 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.01 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.37 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.26 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.36 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.99 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.25 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.74 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2011 |  |  |  | 1570.98 |  |  | 5766 |  |  |  | 300 | [10 empty] | 88.25 |  |  |  | 88.25 | [5 empty] | 85.28 |  |  | 86.94 |  |  |  | 7.81 |  | 9.56 | [8 empty] | 2.19 |  |  |  |  | 0.00
2012 |  |  |  | 2215.76 |  |  | 7864 |  |  |  | 300 | [10 empty] | 83.74 |  |  |  | 83.77 | [5 empty] | 84.08 |  |  | 89.53 |  |  |  | 12.44 |  | 11.96 | [8 empty] | 4.27 |  |  |  |  | 0.03
2013 |  |  |  | 1700.82 |  |  | 6308 |  |  |  | 300 | [10 empty] | 64.68 |  |  |  | 64.68 | [5 empty] | 64.72 |  |  | 72.01 |  |  |  | 7.80 |  | 13.73 | [8 empty] | 21.59 |  |  |  |  | 0.00
2014 |  |  |  | 2190.36 |  |  | 7546 |  |  |  | 300 | [10 empty] | 83.93 |  |  |  | 83.93 | [5 empty] | 83.35 |  |  | 86.14 |  |  |  | 3.49 |  | 3.04 | [8 empty] | 13.03 |  |  |  |  | 0.00
2015 |  |  |  | 2361.48 |  |  | 7855 |  |  |  | 300 | [10 empty] | 89.21 |  |  |  | 89.74 | [5 empty] | 89.86 |  |  | 89.67 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 10.24 |  |  |  |  | 0.54
2016 |  |  |  | 2335.43 |  |  | 7718 |  |  |  | 300 | [10 empty] | 88.18 |  |  |  | 88.18 | [5 empty] | 88.62 |  |  | 87.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.82 |  |  |  |  | 0.00
2017 |  |  |  | 2584.57 |  |  | 8520 |  |  |  | 300 | [10 empty] | 97.61 |  |  |  | 97.61 | [5 empty] | 98.35 |  |  | 97.26 |  |  |  | 0.87 |  | 0.86 | [8 empty] | 1.53 |  |  |  |  | 0.00
2018 |  |  |  | 2296.39 |  |  | 7679 |  |  |  | 300 | [10 empty] | 88.15 |  |  |  | 88.16 | [5 empty] | 87.38 |  |  | 87.66 |  |  |  | 1.05 |  | 0.94 | [8 empty] | 10.91 |  |  |  |  | 0.00
2019 |  |  |  | 2263.06 |  |  | 7573 |  |  |  | 300 | [10 empty] | 86.37 |  |  |  | 86.41 | [5 empty] | 86.11 |  |  | 86.45 |  |  |  | 1.79 |  | 1.57 | [8 empty] | 12.02 |  |  |  |  | 0.04
2020 |  |  |  | 2167.47 |  |  | 7379 |  |  |  | 300 | [10 empty] | 81.33 |  |  |  | 83.13 | [5 empty] | 82.25 |  |  | 84.01 |  |  |  | 4.82 |  | 4.21 | [8 empty] | 12.66 |  |  |  |  | 1.80
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2011 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 306 | [14 empty] | 335
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1100 | [14 empty] | 764
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 11
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 69
Subtotal | [22 empty] | 1100 |  |  |  | 306 | [10 empty] | 775 |  |  |  | 335 | [11 empty] | 69
Total | [22 empty] | 1406 | [14 empty] | 1179
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2011 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [19 empty] | 131 | [14 empty] | 33
15. |  |  | Reactor Cooling Systems | [34 empty] | 85
16. |  |  | Steam generation systems | [19 empty] | 18 | [14 empty] | 19
31. |  |  | Turbine and auxiliaries | [34 empty] | 38
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
33. |  |  | Circulating Water System | [34 empty] | 4
41. |  |  | Main Generator Systems | [19 empty] | 20 | [14 empty] | 54
42. |  |  | Electrical Power Supply Systems | [19 empty] | 136 | [14 empty] | 81
Total | [22 empty] | 305 | [14 empty] | 327
Highlights (2020)
In the year 2020, plant achieved 82% load factor and Operation Factor was 82%. Plant faced w auto scram and and Refueling outage in September 2020

## CHASNUPP-3
2020 Operating Experience
PK-4 | [8 empty] | CHASNUPP-3 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2011-05-28
Thermal power | [12 empty] | : |  |  | 999 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-10-15
Gross electrical power | [12 empty] | : |  |  | 340 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-12-06
Reference unit power (net) | [12 empty] | : |  |  | 315 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.26
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 14 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 32000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.486 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.34
| Active core height/length [m] | [13 empty] | : |  |  | 2.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.59 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2444.19 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.49 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.15 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.44 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.7 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.86 %
Load Factor (LF) | [18 empty] | : | 88.33 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.55 %
Operating Factor (OF) | [18 empty] | : | 90.29 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 853 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 220.25 | 218.11 |  |  |  | 232.77 |  | 223.78 | [8 empty] | 231.75 |  |  | 224.80 | [6 empty] | 230.39 |  | 230.12 |  |  |  | 217.53 |  |  | 230.39 |  |  | 26.25 | [9 empty] | 158.04 |  |  | 2444.19
EAF [%] |  |  |  |  | 94.30 | 100.00 |  |  |  | 99.85 |  | 99.42 | [8 empty] | 100.00 |  |  | 99.76 | [6 empty] | 99.77 |  | 99.72 |  |  |  | 97.89 |  |  | 98.05 |  |  | 11.44 | [9 empty] | 68.72 |  |  | 89.15
UCF [%] |  |  |  |  | 94.30 | 100.00 |  |  |  | 99.85 |  | 99.42 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 13.30 | [9 empty] | 68.72 |  |  | 89.70
LF [%] |  |  |  |  | 93.98 | 99.48 |  |  |  | 99.32 |  | 98.67 | [8 empty] | 98.88 |  |  | 99.12 | [6 empty] | 98.31 |  | 98.19 |  |  |  | 95.91 |  |  | 98.31 |  |  | 11.58 | [9 empty] | 67.44 |  |  | 88.33
OF [%] |  |  |  |  | 96.77 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 14.03 | [9 empty] | 71.77 |  |  | 90.29
FLR [%] |  |  |  |  | 5.25 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.49
UCL [%] |  |  |  |  | 5.22 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.44
PUF [%] |  |  |  |  | 0.48 | 0.00 |  |  |  | 0.15 |  | 0.58 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 86.70 | [9 empty] | 31.28 |  |  | 9.86
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.24 | [6 empty] | 0.23 |  | 0.28 |  |  |  | 2.11 |  |  | 1.95 |  |  | 1.86 | [9 empty] | 0.00 |  |  | 0.55
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 9733.99 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.72 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.55 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.13 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.32 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.79 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.22 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 344.98 |  |  | 1436 |  |  |  | 315 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.84 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 2542.08 |  |  | 8256 |  |  |  | 315 | [10 empty] | 93.53 |  |  |  | 94.13 | [5 empty] | 92.12 |  |  | 94.25 |  |  |  | 5.36 |  | 5.33 | [8 empty] | 0.54 |  |  |  |  | 0.60
2018 |  |  |  | 2145.22 |  |  | 7152 |  |  |  | 315 | [10 empty] | 80.37 |  |  |  | 81.52 | [5 empty] | 77.74 |  |  | 81.64 |  |  |  | 0.66 |  | 0.54 | [8 empty] | 17.94 |  |  |  |  | 1.16
2019 |  |  |  | 2247.57 |  |  | 7508 |  |  |  | 315 | [10 empty] | 85.26 |  |  |  | 86.16 | [5 empty] | 81.45 |  |  | 85.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.84 |  |  |  |  | 0.90
2020 |  |  |  | 2444.19 |  |  | 7931 |  |  |  | 315 | [10 empty] | 89.15 |  |  |  | 89.70 | [5 empty] | 88.33 |  |  | 90.29 |  |  |  | 0.49 |  | 0.44 | [8 empty] | 9.86 |  |  |  |  | 0.55
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 32 | [14 empty] | 123
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 829 | [14 empty] | 875
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 58
Subtotal | [22 empty] | 829 |  |  |  | 32 | [10 empty] | 875 |  |  |  | 123 | [11 empty] | 58
Total | [22 empty] | 861 | [14 empty] | 1056
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2016 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 42
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [19 empty] | 32 | [14 empty] | 56
31. |  |  | Turbine and auxiliaries | [34 empty] | 10
33. |  |  | Circulating Water System | [34 empty] | 7
Total | [22 empty] | 32 | [14 empty] | 123

## CHASNUPP-4
2020 Operating Experience
PK-5 | [8 empty] | CHASNUPP-4 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2011-12-18
Thermal power | [12 empty] | : |  |  | 999 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2017-06-25
Gross electrical power | [12 empty] | : |  |  | 340 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2017-09-19
Reference unit power (net) | [12 empty] | : |  |  | 313 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.26
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 14 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 32000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.486 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.34
| Active core height/length [m] | [13 empty] | : |  |  | 2.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.59 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 34 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2474.85 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.05 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.76 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.05 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.09 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.86 %
Load Factor (LF) | [18 empty] | : | 90.01 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.34 %
Operating Factor (OF) | [18 empty] | : | 91.85 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 716 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 231.68 | 218.01 |  |  |  | 233.13 |  | 223.70 | [8 empty] | 231.79 |  |  | 221.39 | [6 empty] | 39.03 |  | 184.31 |  |  |  | 220.52 |  |  | 231.40 |  |  | 214.57 | [9 empty] | 225.32 |  |  | 2474.85
EAF [%] |  |  |  |  | 98.78 | 99.99 |  |  |  | 100.00 |  | 99.36 | [8 empty] | 99.97 |  |  | 98.22 | [6 empty] | 16.69 |  | 79.71 |  |  |  | 99.33 |  |  | 99.19 |  |  | 100.00 | [9 empty] | 99.54 |  |  | 90.76
UCF [%] |  |  |  |  | 98.78 | 100.00 |  |  |  | 100.00 |  | 99.36 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 18.12 |  | 79.88 |  |  |  | 99.96 |  |  | 99.19 |  |  | 100.00 | [9 empty] | 99.54 |  |  | 91.09
LF [%] |  |  |  |  | 99.49 | 100.07 |  |  |  | 100.11 |  | 99.26 | [8 empty] | 99.54 |  |  | 98.24 | [6 empty] | 16.76 |  | 79.15 |  |  |  | 97.85 |  |  | 99.37 |  |  | 95.21 | [9 empty] | 96.76 |  |  | 90.01
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 20.16 |  | 83.60 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.85
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.11 |  |  | 0.00 | [9 empty] | 0.46 |  |  | 0.05
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.11 |  |  | 0.00 | [9 empty] | 0.46 |  |  | 0.05
PUF [%] |  |  |  |  | 1.22 | 0.00 |  |  |  | 0.00 |  | 0.64 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 81.88 |  | 20.12 |  |  |  | 0.04 |  |  | 0.70 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.86
XUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  | 1.78 | [6 empty] | 1.43 |  | 0.17 |  |  |  | 0.63 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.34
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 7698.85 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.52 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.8 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.47 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.13 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.54 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.68 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.28 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2017 |  |  |  | 484.17 |  |  | 1946 |  |  |  | 313 | [10 empty] | 95.21 |  |  |  | 95.22 | [5 empty] | 35.01 |  |  | 38.13 |  |  |  | 4.78 |  | 4.78 | [8 empty] | 0.00 |  |  |  |  | 0.01
2018 |  |  |  | 2557.08 |  |  | 8452 |  |  |  | 313 | [10 empty] | 95.74 |  |  |  | 97.25 | [5 empty] | 93.26 |  |  | 96.48 |  |  |  | 2.63 |  | 2.63 | [8 empty] | 0.12 |  |  |  |  | 1.51
2019 |  |  |  | 2181.00 |  |  | 7237 |  |  |  | 313 | [10 empty] | 81.52 |  |  |  | 81.88 | [5 empty] | 79.54 |  |  | 82.61 |  |  |  | 0.80 |  | 0.66 | [8 empty] | 17.46 |  |  |  |  | 0.36
2020 |  |  |  | 2474.85 |  |  | 8068 |  |  |  | 313 | [10 empty] | 90.76 |  |  |  | 91.09 | [5 empty] | 90.01 |  |  | 91.85 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 8.86 |  |  |  |  | 0.34
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2017 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 95
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 716 | [14 empty] | 676
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 434
Subtotal | [22 empty] | 716 | [14 empty] | 676 |  |  |  | 95 | [11 empty] | 434
Total | [22 empty] | 716 | [14 empty] | 1205
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2017 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 28
41. |  |  | Main Generator Systems | [34 empty] | 58
Total | [37 empty] | 86
Highlights (2020)
In the year 2020, plant load factor was 90% and operating factor was 92% Refueling outage was started in the month of July

## KANUPP-1
2020 Operating Experience
PK-1 | [8 empty] | KANUPP-1 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Turbine Supplier | [7 empty] | : | HITACHI (HITACHI, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU-137 MW | [11 empty] | Construction Date | [15 empty] | : |  |  | 1966-08-01
Thermal power | [12 empty] | : |  |  | 337 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1971-10-18
Gross electrical power | [12 empty] | : |  |  | 100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1972-12-07
Reference unit power (net) | [12 empty] | : |  |  | 90 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10.6
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.19
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8650 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.82 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.87
| Active core height/length [m] | [13 empty] | : |  |  | 4.87 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2277 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 4.13 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 4 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 274.92 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 44.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 44.41 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 34.93 %
Unit Capability Factor (UCF) | [18 empty] | : | 44.41 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.66 %
Load Factor (LF) | [18 empty] | : | 34.78 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 55.43 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3915 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 43.99 | 17.98 |  |  |  | 28.90 |  | 19.75 | [8 empty] | 7.31 |  |  | 25.75 | [6 empty] | 2.08 |  | 24.12 |  |  |  | 40.08 |  |  | 35.10 |  |  | 20.54 | [9 empty] | 9.31 |  |  | 274.92
EAF [%] |  |  |  |  | 65.70 | 28.70 |  |  |  | 43.17 |  | 30.49 | [8 empty] | 94.15 |  |  | 71.33 | [6 empty] | 3.10 |  | 36.02 |  |  |  | 61.85 |  |  | 52.42 |  |  | 31.70 | [9 empty] | 13.90 |  |  | 44.41
UCF [%] |  |  |  |  | 65.70 | 28.70 |  |  |  | 43.17 |  | 30.49 | [8 empty] | 94.15 |  |  | 71.33 | [6 empty] | 3.10 |  | 36.02 |  |  |  | 61.85 |  |  | 52.42 |  |  | 31.70 | [9 empty] | 13.90 |  |  | 44.41
LF [%] |  |  |  |  | 65.70 | 28.70 |  |  |  | 43.17 |  | 30.49 | [8 empty] | 10.92 |  |  | 39.74 | [6 empty] | 3.10 |  | 36.02 |  |  |  | 61.85 |  |  | 52.42 |  |  | 31.70 | [9 empty] | 13.90 |  |  | 34.78
OF [%] |  |  |  |  | 100.00 | 45.69 |  |  |  | 68.28 |  | 50.42 | [8 empty] | 16.80 |  |  | 68.47 | [6 empty] | 5.11 |  | 58.33 |  |  |  | 100.00 |  |  | 81.99 |  |  | 48.47 | [9 empty] | 22.45 |  |  | 55.43
FLR [%] |  |  |  |  | 0.00 | 65.44 |  |  |  | 42.36 |  | 61.89 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 96.83 |  | 53.63 |  |  |  | 0.00 |  |  | 25.52 |  |  | 61.90 | [9 empty] | 84.80 |  |  | 44.02
UCL [%] |  |  |  |  | 0.00 | 54.33 |  |  |  | 31.72 |  | 49.52 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 94.89 |  | 41.66 |  |  |  | 0.00 |  |  | 17.96 |  |  | 51.50 | [9 empty] | 77.56 |  |  | 34.93
PUF [%] |  |  |  |  | 34.30 | 16.97 |  |  |  | 25.11 |  | 20.00 | [8 empty] | 5.85 |  |  | 28.67 | [6 empty] | 2.01 |  | 22.32 |  |  |  | 38.15 |  |  | 29.62 |  |  | 16.80 | [9 empty] | 8.54 |  |  | 20.66
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 14786.02 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 43.94 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 31.85 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 25.66 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 32.74 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 41.6 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 29.47 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.89 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 55.7 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1972 |  |  |  | 232.70 |  |  | 3737 |  |  |  | 137 | [10 empty] | 38.70 |  |  |  | 38.70 | [5 empty] | 38.65 |  |  | 80.24 |  |  |  | 61.30 |  | 61.30 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 394.80 |  |  | 6197 |  |  |  | 126 | [10 empty] | 35.60 |  |  |  | 42.56 | [5 empty] | 35.77 |  |  | 70.74 |  |  |  | 41.76 |  | 30.52 | [8 empty] | 26.92 |  |  |  |  | 6.96
1974 |  |  |  | 583.90 |  |  | 6749 |  |  |  | 126 | [10 empty] | 52.75 |  |  |  | 52.75 | [5 empty] | 52.90 |  |  | 77.04 |  |  |  | 25.84 |  | 18.38 | [8 empty] | 28.87 |  |  |  |  | 0.00
1975 |  |  |  | 494.90 |  |  | 6375 |  |  |  | 126 | [10 empty] | 44.83 |  |  |  | 44.83 | [5 empty] | 44.84 |  |  | 72.77 |  |  |  | 47.38 |  | 40.37 | [8 empty] | 14.80 |  |  |  |  | 0.00
1976 |  |  |  | 487.30 |  |  | 6026 |  |  |  | 137 | [10 empty] | 40.49 |  |  |  | 40.49 | [5 empty] | 40.49 |  |  | 68.60 |  |  |  | 59.51 |  | 59.51 | [8 empty] | 0.00 |  |  |  |  | 0.00
1977 |  |  |  | 339.40 |  |  | 5290 |  |  |  | 126 | [10 empty] | 30.74 |  |  |  | 30.74 | [5 empty] | 30.75 |  |  | 60.39 |  |  |  | 58.92 |  | 44.09 | [8 empty] | 25.16 |  |  |  |  | 0.00
1978 |  |  |  | 228.40 |  |  | 4473 |  |  |  | 125 | [10 empty] | 20.88 |  |  |  | 20.88 | [5 empty] | 20.86 |  |  | 51.06 |  |  |  | 71.93 |  | 53.51 | [8 empty] | 25.61 |  |  |  |  | 0.00
1979 |  |  |  | 29.60 |  |  | 802 |  |  |  | 125 | [10 empty] | 2.70 |  |  |  | 2.70 | [5 empty] | 2.70 |  |  | 9.16 |  |  |  | 83.28 |  | 13.46 | [8 empty] | 83.84 |  |  |  |  | 0.00
1980 |  |  |  | 67.90 |  |  | 2427 |  |  |  | 125 | [10 empty] | 6.17 |  |  |  | 6.17 | [5 empty] | 6.18 |  |  | 27.63 |  |  |  | 92.43 |  | 75.36 | [8 empty] | 18.47 |  |  |  |  | 0.00
1981 |  |  |  | 192.20 |  |  | 5379 |  |  |  | 125 | [10 empty] | 17.55 |  |  |  | 17.55 | [5 empty] | 17.55 |  |  | 61.40 |  |  |  | 80.60 |  | 72.90 | [8 empty] | 9.55 |  |  |  |  | 0.00
1982 |  |  |  | 70.90 |  |  | 1801 |  |  |  | 125 | [10 empty] | 6.48 |  |  |  | 6.48 | [5 empty] | 6.47 |  |  | 20.56 |  |  |  | 90.55 |  | 62.08 | [8 empty] | 31.45 |  |  |  |  | 0.00
1983 |  |  |  | 194.00 |  |  | 4754 |  |  |  | 125 | [10 empty] | 17.70 |  |  |  | 17.70 | [5 empty] | 17.72 |  |  | 54.27 |  |  |  | 44.34 |  | 14.11 | [8 empty] | 68.19 |  |  |  |  | 0.00
1984 |  |  |  | 290.65 |  |  | 5592 |  |  |  | 137 | [10 empty] | 24.90 |  |  |  | 26.94 | [5 empty] | 24.15 |  |  | 63.66 |  |  |  | 9.51 |  | 2.83 | [8 empty] | 70.23 |  |  |  |  | 2.04
1985 |  |  |  | 261.96 |  |  | 3895 |  |  |  | 137 | [10 empty] | 21.83 |  |  |  | 22.69 | [5 empty] | 21.83 |  |  | 44.46 |  |  |  | 50.85 |  | 23.47 | [8 empty] | 53.83 |  |  |  |  | 0.87
1986 |  |  |  | 476.22 |  |  | 7211 |  |  |  | 125 | [10 empty] | 43.49 |  |  |  | 44.00 | [5 empty] | 43.49 |  |  | 82.32 |  |  |  | 56.00 |  | 56.00 | [8 empty] | 0.00 |  |  |  |  | 0.51
1987 |  |  |  | 274.77 |  |  | 4541 |  |  |  | 125 | [10 empty] | 25.09 |  |  |  | 25.58 | [5 empty] | 25.09 |  |  | 51.84 |  |  |  | 59.64 |  | 37.80 | [8 empty] | 36.61 |  |  |  |  | 0.49
1988 |  |  |  | 171.41 |  |  | 2962 |  |  |  | 125 | [10 empty] | 15.60 |  |  |  | 16.21 | [5 empty] | 15.61 |  |  | 33.72 |  |  |  | 53.71 |  | 18.82 | [8 empty] | 64.97 |  |  |  |  | 0.61
1989 |  |  |  | 60.86 |  |  | 1145 |  |  |  | 125 | [10 empty] | 5.56 |  |  |  | 5.56 | [5 empty] | 5.56 |  |  | 13.07 |  |  |  | 70.79 |  | 13.47 | [8 empty] | 80.97 |  |  |  |  | 0.00
1990 |  |  |  | 375.91 |  |  | 5331 |  |  |  | 125 | [10 empty] | 34.33 |  |  |  | 34.33 | [5 empty] | 34.33 |  |  | 60.86 |  |  |  | 60.06 |  | 51.62 | [8 empty] | 14.05 |  |  |  |  | 0.00
1991 |  |  |  | 370.30 |  |  | 6126 |  |  |  | 125 | [10 empty] | 33.82 |  |  |  | 34.79 | [5 empty] | 33.82 |  |  | 69.93 |  |  |  | 65.21 |  | 65.21 | [8 empty] | 0.00 |  |  |  |  | 0.97
1992 |  |  |  | 499.74 |  |  | 6396 |  |  |  | 125 | [10 empty] | 45.51 |  |  |  | 45.51 | [5 empty] | 45.51 |  |  | 72.81 |  |  |  | 47.81 |  | 41.70 | [8 empty] | 12.79 |  |  |  |  | 0.00
1993 |  |  |  | 369.60 |  |  | 4620 |  |  |  | 125 | [10 empty] | 33.75 |  |  |  | 35.76 | [5 empty] | 33.75 |  |  | 52.74 |  |  |  | 42.71 |  | 26.67 | [8 empty] | 37.57 |  |  |  |  | 2.01
1994 |  |  |  | 523.64 |  |  | 7518 |  |  |  | 125 | [10 empty] | 47.82 |  |  |  | 53.56 | [5 empty] | 47.82 |  |  | 85.82 |  |  |  | 13.63 |  | 8.45 | [8 empty] | 37.99 |  |  |  |  | 5.74
1995 |  |  |  | 461.04 |  |  | 7520 |  |  |  | 125 | [10 empty] | 42.10 |  |  |  | 44.03 | [5 empty] | 42.10 |  |  | 85.84 |  |  |  | 55.97 |  | 55.97 | [8 empty] | 0.00 |  |  |  |  | 1.93
1996 |  |  |  | 310.86 |  |  | 5291 |  |  |  | 125 | [10 empty] | 28.31 |  |  |  | 32.59 | [5 empty] | 28.31 |  |  | 60.23 |  |  |  | 41.29 |  | 22.93 | [8 empty] | 44.48 |  |  |  |  | 4.28
1997 |  |  |  | 386.12 |  |  | 6391 |  |  |  | 125 | [10 empty] | 35.26 |  |  |  | 36.84 | [5 empty] | 35.26 |  |  | 72.96 |  |  |  | 24.77 |  | 12.13 | [8 empty] | 51.02 |  |  |  |  | 1.58
1998 |  |  |  | 353.35 |  |  | 4799 |  |  |  | 125 | [10 empty] | 29.74 |  |  |  | 31.34 | [5 empty] | 32.27 |  |  | 54.78 |  |  |  | 25.91 |  | 10.96 | [8 empty] | 57.70 |  |  |  |  | 1.60
1999 |  |  |  | 68.99 |  |  | 1046 |  |  |  | 125 | [10 empty] | 11.93 |  |  |  | 11.93 | [5 empty] | 6.30 |  |  | 11.94 |  |  |  | 10.30 |  | 1.37 | [8 empty] | 86.70 |  |  |  |  | 0.00
2000 |  |  |  | 368.31 |  |  | 5078 |  |  |  | 125 | [10 empty] | 33.54 |  |  |  | 34.62 | [5 empty] | 33.54 |  |  | 57.81 |  |  |  | 20.65 |  | 9.01 | [8 empty] | 56.37 |  |  |  |  | 1.08
2001 |  |  |  | 399.46 |  |  | 6049 |  |  |  | 125 | [10 empty] | 36.48 |  |  |  | 45.11 | [5 empty] | 36.48 |  |  | 69.05 |  |  |  | 22.49 |  | 13.09 | [8 empty] | 41.80 |  |  |  |  | 8.63
2002 |  |  |  | 444.02 |  |  | 6601 |  |  |  | 125 | [10 empty] | 40.55 |  |  |  | 41.27 | [5 empty] | 40.55 |  |  | 75.35 |  |  |  | 14.70 |  | 7.11 | [8 empty] | 51.62 |  |  |  |  | 0.72
2003 |  |  |  | 0.00 |  |  | 0 |  |  |  | 125 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2004 |  |  |  | 183.00 |  |  | 6467 |  |  |  | 125 | [10 empty] | 24.71 |  |  |  | 25.51 | [5 empty] | 16.67 |  |  | 73.62 |  |  |  | 41.12 |  | 17.81 | [8 empty] | 56.68 |  |  |  |  | 0.79
2005 |  |  |  | 253.56 |  |  | 6633 |  |  |  | 125 | [10 empty] | 37.74 |  |  |  | 37.74 | [5 empty] | 23.16 |  |  | 75.72 |  |  |  | 10.07 |  | 4.23 | [8 empty] | 58.04 |  |  |  |  | 0.00
2006 |  |  |  | 14.99 |  |  | 408 |  |  |  | 125 | [10 empty] | 4.59 |  |  |  | 4.59 | [5 empty] | 1.37 |  |  | 4.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 95.41 |  |  |  |  | 0.00
2007 |  |  |  | 359.51 |  |  | 5989 |  |  |  | 125 | [10 empty] | 50.88 |  |  |  | 50.88 | [5 empty] | 32.83 |  |  | 68.37 |  |  |  | 21.07 |  | 13.58 | [8 empty] | 35.54 |  |  |  |  | 0.00
2008 |  |  |  | 384.80 |  |  | 5026 |  |  |  | 125 | [10 empty] | 63.36 |  |  |  | 63.36 | [5 empty] | 35.05 |  |  | 57.22 |  |  |  | 18.59 |  | 14.47 | [8 empty] | 22.17 |  |  |  |  | 0.00
2009 |  |  |  | 491.31 |  |  | 6282 |  |  |  | 125 | [10 empty] | 47.76 |  |  |  | 47.76 | [5 empty] | 44.87 |  |  | 71.71 |  |  |  | 21.70 |  | 13.23 | [8 empty] | 39.00 |  |  |  |  | 0.00
2010 |  |  |  | 464.57 |  |  | 6063 |  |  |  | 125 | [10 empty] | 43.35 |  |  |  | 43.35 | [5 empty] | 42.43 |  |  | 69.21 |  |  |  | 29.77 |  | 18.37 | [8 empty] | 38.28 |  |  |  |  | 0.00
2011 |  |  |  | 210.77 |  |  | 2768 |  |  |  | 125 | [10 empty] | 23.32 |  |  |  | 23.32 | [5 empty] | 19.25 |  |  | 31.60 |  |  |  | 45.86 |  | 19.76 | [8 empty] | 56.92 |  |  |  |  | 0.00
2012 |  |  |  | 566.40 |  |  | 7678 |  |  |  | 125 | [10 empty] | 60.43 |  |  |  | 60.43 | [5 empty] | 51.58 |  |  | 87.41 |  |  |  | 5.84 |  | 3.75 | [8 empty] | 35.82 |  |  |  |  | 0.00
2013 |  |  |  | 480.47 |  |  | 6802 |  |  |  | 90 | [10 empty] | 62.59 |  |  |  | 62.59 | [5 empty] | 60.94 |  |  | 77.65 |  |  |  | 24.85 |  | 20.70 | [8 empty] | 16.72 |  |  |  |  | 0.00
2014 |  |  |  | 208.95 |  |  | 3083 |  |  |  | 90 | [10 empty] | 28.65 |  |  |  | 28.65 | [5 empty] | 26.50 |  |  | 35.19 |  |  |  | 32.47 |  | 13.78 | [8 empty] | 57.57 |  |  |  |  | 0.00
2015 |  |  |  | 343.69 |  |  | 5468 |  |  |  | 90 | [10 empty] | 46.81 |  |  |  | 46.81 | [5 empty] | 43.59 |  |  | 62.42 |  |  |  | 27.79 |  | 18.01 | [8 empty] | 35.19 |  |  |  |  | 0.00
2016 |  |  |  | 432.03 |  |  | 7088 |  |  |  | 90 | [10 empty] | 56.29 |  |  |  | 56.29 | [5 empty] | 54.65 |  |  | 80.69 |  |  |  | 16.24 |  | 10.92 | [8 empty] | 32.80 |  |  |  |  | 0.00
2017 |  |  |  | 340.25 |  |  | 5721 |  |  |  | 90 | [10 empty] | 45.75 |  |  |  | 45.75 | [5 empty] | 43.16 |  |  | 65.31 |  |  |  | 36.63 |  | 26.44 | [8 empty] | 27.81 |  |  |  |  | 0.00
2018 |  |  |  | 273.96 |  |  | 4682 |  |  |  | 90 | [10 empty] | 37.48 |  |  |  | 37.48 | [5 empty] | 34.75 |  |  | 53.45 |  |  |  | 24.41 |  | 12.10 | [8 empty] | 50.41 |  |  |  |  | 0.00
2019 |  |  |  | 38.97 |  |  | 759 |  |  |  | 90 | [10 empty] | 4.94 |  |  |  | 4.94 | [5 empty] | 4.94 |  |  | 8.66 |  |  |  | 48.28 |  | 4.61 | [8 empty] | 90.44 |  |  |  |  | 0.00
2020 |  |  |  | 274.92 |  |  | 4869 |  |  |  | 90 | [10 empty] | 44.41 |  |  |  | 44.41 | [5 empty] | 34.78 |  |  | 55.43 |  |  |  | 44.02 |  | 34.93 | [8 empty] | 20.66 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1972 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 3068 | [14 empty] | 1249
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 89
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 1600
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 0
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 196
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 843 | [19 empty] | 268
L. |  | Human factor related | [39 empty] | 62
P. |  | Fire | [39 empty] | 3
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 205
Z. |  | Other | [35 empty] | 3 |  |  |  | 63
Subtotal | [26 empty] | 3068 | [6 empty] | 843 |  |  |  | 2093 |  |  |  | 1377 | [11 empty] | 268
Total | [22 empty] | 3911 | [14 empty] | 3738
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1972 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 43
12. |  |  | Reactor I&C Systems | [34 empty] | 104
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 367 | [14 empty] | 125
14. |  |  | Safety Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [19 empty] | 712 | [14 empty] | 198
16. |  |  | Steam generation systems | [19 empty] | 641 | [14 empty] | 297
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 114
31. |  |  | Turbine and auxiliaries | [19 empty] | 247 | [14 empty] | 41
32. |  |  | Feedwater and Main Steam System | [34 empty] | 73
33. |  |  | Circulating Water System | [19 empty] | 84 | [14 empty] | 34
34. |  |  | Miscellaneous Systems | [34 empty] | 113
41. |  |  | Main Generator Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [19 empty] | 1016 | [14 empty] | 192
Total | [22 empty] | 3067 | [14 empty] | 1353
Highlights (2020)
Plant operated at average load of 71.06 with availability factor of 55.43% , gross capacity factor 40.62% in the year 2020