## AKADEMIK LOMONOSOV-1
2020 Operating Experience
RU-151 | [8 empty] | AKADEMIK LOMONOSOV-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / KLT-40S 'Floating' | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-04-15
Thermal power | [12 empty] | : |  |  | 150 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-12-19
Gross electrical power | [12 empty] | : |  |  | 35 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2020-05-22
Reference unit power (net) | [12 empty] | : |  |  | 32 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 316
| Fuel material | [13 empty] | : |  |  | Other | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 14.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 29 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 100 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 68700 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | NA
| Active core diameter [m] | [13 empty] | : |  |  | 1.220 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.43
| Active core height/length [m] | [13 empty] | : |  |  | 1.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 10.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 11 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 64.94 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.3 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.38 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.27 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.38 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.34 %
Load Factor (LF) | [18 empty] | : | 28.76 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 71.63 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3646 hours
Annual Summary
[5 empty] | May | Jan |  |  |  | Feb |  | Mar | [8 empty] | Apr |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [23 empty] | 7.42 | [6 empty] | 9.18 |  | 8.03 |  |  |  | 0.17 |  |  | 7.51 |  |  | 9.77 | [9 empty] | 5.20 |  |  | 47.27
EAF [%] | [23 empty] | 100.00 | [6 empty] | 98.12 |  | 100.00 |  |  |  | 33.36 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.38
UCF [%] | [23 empty] | 100.00 | [6 empty] | 98.12 |  | 100.00 |  |  |  | 33.36 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.38
LF [%] | [23 empty] | 32.18 | [6 empty] | 38.54 |  | 33.71 |  |  |  | 0.72 |  |  | 31.55 |  |  | 42.41 | [9 empty] | 21.86 |  |  | 28.76
OF [%] | [23 empty] | 100.00 | [6 empty] | 99.19 |  | 83.60 |  |  |  | 2.50 |  |  | 70.97 |  |  | 98.61 | [9 empty] | 46.10 |  |  | 71.63
FLR [%] | [23 empty] | 0.00 | [6 empty] | 1.88 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.30
UCL [%] | [23 empty] | 0.00 | [6 empty] | 1.88 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.27
PUF [%] | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 66.64 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.34
XUF [%] | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 65.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.3 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.38 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.27 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.34 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 28.76 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 71.63 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2020 |  |  |  | 64.94 |  |  | 5138 |  |  |  | 32 | [10 empty] | 90.38 |  |  |  | 90.38 | [5 empty] | 28.76 |  |  | 71.63 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 9.34 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2020 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 480 | [14 empty] | 823
L. |  | Human factor related | [24 empty] | 12 | [14 empty] | 21
Subtotal | [22 empty] | 480 |  |  |  | 12 | [10 empty] | 823 |  |  |  | 21
Total | [22 empty] | 492 | [14 empty] | 844
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2020 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [19 empty] | 12 | [14 empty] | 12
Total | [22 empty] | 12 | [14 empty] | 12
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. The unit was in the routine maintenance from 2020.09.10 to 2020.09.03. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## AKADEMIK LOMONOSOV-2
2020 Operating Experience
RU-152 | [8 empty] | AKADEMIK LOMONOSOV-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / KLT-40S 'Floating' | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-04-15
Thermal power | [12 empty] | : |  |  | 150 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-12-19
Gross electrical power | [12 empty] | : |  |  | 35 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2020-05-22
Reference unit power (net) | [12 empty] | : |  |  | 32 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 316
| Fuel material | [13 empty] | : |  |  | Other | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 14.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 29 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 100 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 68700 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | NA
| Active core diameter [m] | [13 empty] | : |  |  | 1.220 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.43
| Active core height/length [m] | [13 empty] | : |  |  | 1.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 10.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 11 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 51.44 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 14.66 %
Energy Availability Factor (EAF) | [18 empty] | : | 77.36 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 13.29 %
Unit Capability Factor (UCF) | [18 empty] | : | 77.36 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.35 %
Load Factor (LF) | [18 empty] | : | 15.99 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 38.32 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4842 hours
Annual Summary
[5 empty] | May | Jan |  |  |  | Feb |  | Mar | [8 empty] | Apr |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 3.88 |  |  |  | 10.06 |  |  | 3.76 |  |  | 2.53 | [9 empty] | 6.04 |  |  | 26.27
EAF [%] | [23 empty] | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 97.36 |  |  | 35.47 |  |  | 32.80 | [9 empty] | 75.81 |  |  | 77.36
UCF [%] | [23 empty] | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 97.36 |  |  | 35.47 |  |  | 32.80 | [9 empty] | 75.81 |  |  | 77.36
LF [%] | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 16.31 |  |  |  | 43.67 |  |  | 15.78 |  |  | 10.98 | [9 empty] | 25.39 |  |  | 15.99
OF [%] | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 49.46 |  |  |  | 97.36 |  |  | 32.53 |  |  | 32.78 | [9 empty] | 56.59 |  |  | 38.32
FLR [%] | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 2.64 |  |  | 0.00 |  |  | 67.20 | [9 empty] | 24.19 |  |  | 14.66
UCL [%] | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 2.64 |  |  | 0.00 |  |  | 67.20 | [9 empty] | 24.19 |  |  | 13.29
PUF [%] | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 64.53 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.35
XUF [%] | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 53.56 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 14.66 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.36 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.36 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.35 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 15.99 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 38.32 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2020 |  |  |  | 51.44 |  |  | 3942 |  |  |  | 32 | [10 empty] | 77.36 |  |  |  | 77.36 | [5 empty] | 15.99 |  |  | 38.32 |  |  |  | 14.66 |  | 13.29 | [8 empty] | 9.35 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2020 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 696 | [14 empty] | 1193
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 600 | [14 empty] | 1029
L. |  | Human factor related | [24 empty] | 19 | [14 empty] | 33
Subtotal | [22 empty] | 600 |  |  |  | 715 | [10 empty] | 1029 |  |  |  | 1226
Total | [22 empty] | 1315 | [14 empty] | 2255
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2020 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [19 empty] | 696 | [14 empty] | 696
Total | [22 empty] | 696 | [14 empty] | 696
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. . The unit was in the routine maintenance from 2020.10.01 to 2020.10.20. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-1
2020 Operating Experience
RU-96 | [8 empty] | BALAKOVO-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-12-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-12-28
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-05-23
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7533.32 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.18 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.96 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.16 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.96 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.87 %
Load Factor (LF) | [18 empty] | : | 90.28 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 89.28 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 942 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 6.56 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 759.83 | 703.58 |  |  |  | 672.48 |  | 554.95 | [8 empty] | 287.39 |  |  | 124.22 | [6 empty] | 720.74 |  | 734.42 |  |  |  | 724.76 |  |  | 755.71 |  |  | 735.10 | [9 empty] | 760.14 |  |  | 7533.33
EAF [%] |  |  |  |  | 100.00 | 99.45 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 49.87 |  |  | 19.13 | [6 empty] | 98.61 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.96
UCF [%] |  |  |  |  | 100.00 | 99.45 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 49.87 |  |  | 19.13 | [6 empty] | 98.61 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.96
LF [%] |  |  |  |  | 107.50 | 106.41 |  |  |  | 95.14 |  | 81.13 | [8 empty] | 40.66 |  |  | 18.16 | [6 empty] | 101.97 |  | 103.91 |  |  |  | 105.96 |  |  | 106.92 |  |  | 107.47 | [9 empty] | 107.55 |  |  | 90.28
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 49.87 |  |  | 20.97 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.28
FLR [%] |  |  |  |  | 0.00 | 0.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.39 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.18
UCL [%] |  |  |  |  | 0.00 | 0.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.39 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.16
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 50.13 |  |  | 80.87 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.87
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 213728.73 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.62 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.21 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.47 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.98 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.57 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.77 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.33 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 4868.03 |  |  | 6082 |  |  |  | 950 | [10 empty] | 64.85 |  |  |  | 64.85 | [5 empty] | 64.46 |  |  | 69.51 |  |  |  | 17.62 |  | 13.87 | [8 empty] | 21.28 |  |  |  |  | 0.00
1987 |  |  |  | 4703.68 |  |  | 5302 |  |  |  | 1000 | [10 empty] | 57.40 |  |  |  | 57.40 | [5 empty] | 53.70 |  |  | 60.53 |  |  |  | 25.51 |  | 19.66 | [8 empty] | 22.95 |  |  |  |  | 0.00
1988 |  |  |  | 6476.87 |  |  | 7207 |  |  |  | 950 | [10 empty] | 80.93 |  |  |  | 80.93 | [5 empty] | 77.62 |  |  | 82.05 |  |  |  | 6.99 |  | 6.08 | [8 empty] | 12.99 |  |  |  |  | 0.00
1989 |  |  |  | 4473.90 |  |  | 5141 |  |  |  | 950 | [10 empty] | 56.34 |  |  |  | 56.37 | [5 empty] | 53.76 |  |  | 58.69 |  |  |  | 32.94 |  | 27.69 | [8 empty] | 15.95 |  |  |  |  | 0.03
1990 |  |  |  | 739.06 |  |  | 887 |  |  |  | 950 | [10 empty] | 9.09 |  |  |  | 9.09 | [5 empty] | 8.88 |  |  | 10.13 |  |  |  | 56.91 |  | 12.01 | [8 empty] | 78.90 |  |  |  |  | 0.00
1991 |  |  |  | 4951.60 |  |  | 5780 |  |  |  | 950 | [10 empty] | 59.85 |  |  |  | 60.19 | [5 empty] | 59.50 |  |  | 65.98 |  |  |  | 24.74 |  | 19.79 | [8 empty] | 20.02 |  |  |  |  | 0.35
1992 |  |  |  | 6352.28 |  |  | 7666 |  |  |  | 950 | [10 empty] | 76.31 |  |  |  | 76.38 | [5 empty] | 76.11 |  |  | 87.26 |  |  |  | 23.62 |  | 23.62 | [8 empty] | 0.00 |  |  |  |  | 0.07
1993 |  |  |  | 3326.09 |  |  | 4230 |  |  |  | 950 | [10 empty] | 39.88 |  |  |  | 46.10 | [5 empty] | 39.97 |  |  | 48.29 |  |  |  | 24.25 |  | 14.76 | [8 empty] | 39.14 |  |  |  |  | 6.22
1994 |  |  |  | 1759.54 |  |  | 2307 |  |  |  | 950 | [10 empty] | 77.30 |  |  |  | 77.30 | [5 empty] | 21.14 |  |  | 26.34 |  |  |  | 22.70 |  | 22.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 2017.98 |  |  | 4810 |  |  |  | 950 | [10 empty] | 28.57 |  |  |  | 28.57 | [5 empty] | 24.25 |  |  | 54.91 |  |  |  | 62.91 |  | 48.46 | [8 empty] | 22.97 |  |  |  |  | 0.00
1996 |  |  |  | 4872.54 |  |  | 5913 |  |  |  | 950 | [10 empty] | 59.00 |  |  |  | 86.47 | [5 empty] | 58.39 |  |  | 67.32 |  |  |  | 0.82 |  | 0.72 | [8 empty] | 12.81 |  |  |  |  | 27.47
1997 |  |  |  | 4728.99 |  |  | 5818 |  |  |  | 950 | [10 empty] | 57.24 |  |  |  | 60.37 | [5 empty] | 56.83 |  |  | 66.42 |  |  |  | 1.49 |  | 0.91 | [8 empty] | 38.72 |  |  |  |  | 3.13
1998 |  |  |  | 4329.83 |  |  | 5671 |  |  |  | 950 | [10 empty] | 52.16 |  |  |  | 55.84 | [5 empty] | 52.03 |  |  | 64.74 |  |  |  | 4.87 |  | 2.86 | [8 empty] | 41.30 |  |  |  |  | 3.68
1999 |  |  |  | 5141.31 |  |  | 6337 |  |  |  | 950 | [10 empty] | 62.09 |  |  |  | 65.56 | [5 empty] | 61.78 |  |  | 72.34 |  |  |  | 0.25 |  | 0.16 | [8 empty] | 34.28 |  |  |  |  | 3.47
2000 |  |  |  | 7247.37 |  |  | 7705 |  |  |  | 950 | [10 empty] | 86.49 |  |  |  | 87.54 | [5 empty] | 86.85 |  |  | 87.72 |  |  |  | 2.30 |  | 2.06 | [8 empty] | 10.40 |  |  |  |  | 1.05
2001 |  |  |  | 7407.90 |  |  | 8041 |  |  |  | 950 | [10 empty] | 88.19 |  |  |  | 91.57 | [5 empty] | 89.02 |  |  | 91.79 |  |  |  | 1.55 |  | 1.44 | [8 empty] | 6.98 |  |  |  |  | 3.38
2002 |  |  |  | 6785.73 |  |  | 7501 |  |  |  | 950 | [10 empty] | 80.48 |  |  |  | 86.52 | [5 empty] | 81.54 |  |  | 85.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.48 |  |  |  |  | 6.04
2003 |  |  |  | 7032.19 |  |  | 7460 |  |  |  | 950 | [10 empty] | 83.12 |  |  |  | 84.71 | [5 empty] | 84.50 |  |  | 85.16 |  |  |  | 0.75 |  | 0.64 | [8 empty] | 14.64 |  |  |  |  | 1.60
2004 |  |  |  | 6626.43 |  |  | 6901 |  |  |  | 950 | [10 empty] | 78.00 |  |  |  | 78.22 | [5 empty] | 79.41 |  |  | 78.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.78 |  |  |  |  | 0.22
2005 |  |  |  | 7312.72 |  |  | 7638 |  |  |  | 950 | [10 empty] | 86.24 |  |  |  | 86.58 | [5 empty] | 87.86 |  |  | 87.18 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 13.27 |  |  |  |  | 0.34
2006 |  |  |  | 7276.97 |  |  | 7517 |  |  |  | 950 | [10 empty] | 85.24 |  |  |  | 85.49 | [5 empty] | 87.44 |  |  | 85.81 |  |  |  | 0.70 |  | 0.60 | [8 empty] | 13.91 |  |  |  |  | 0.25
2007 |  |  |  | 7397.29 |  |  | 7731 |  |  |  | 950 | [10 empty] | 86.54 |  |  |  | 87.98 | [5 empty] | 88.89 |  |  | 88.25 |  |  |  | 0.39 |  | 0.34 | [8 empty] | 11.68 |  |  |  |  | 1.44
2008 |  |  |  | 6810.23 |  |  | 7283 |  |  |  | 950 | [10 empty] | 81.73 |  |  |  | 82.41 | [5 empty] | 81.61 |  |  | 82.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.59 |  |  |  |  | 0.68
2009 |  |  |  | 7948.45 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.61 |  |  |  | 99.74 | [5 empty] | 95.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.26 |  |  |  |  | 0.13
2010 |  |  |  | 6843.30 |  |  | 7069 |  |  |  | 950 | [10 empty] | 80.31 |  |  |  | 80.43 | [5 empty] | 82.23 |  |  | 80.70 |  |  |  | 0.00 |  | 7.09 | [8 empty] | 12.48 |  |  |  |  | 0.12
2011 |  |  |  | 7469.27 |  |  | 7573 |  |  |  | 950 | [10 empty] | 86.15 |  |  |  | 86.25 | [5 empty] | 89.76 |  |  | 86.46 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 13.73 |  |  |  |  | 0.10
2012 |  |  |  | 6322.13 |  |  | 6424 |  |  |  | 950 | [10 empty] | 72.90 |  |  |  | 73.02 | [5 empty] | 75.76 |  |  | 73.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.98 |  |  |  |  | 0.12
2013 |  |  |  | 8766.85 |  |  | 8726 |  |  |  | 950 | [10 empty] | 99.58 |  |  |  | 99.58 | [5 empty] | 105.35 |  |  | 99.61 |  |  |  | 0.42 |  | 0.42 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 7012.47 |  |  | 7077 |  |  |  | 950 | [10 empty] | 79.98 |  |  |  | 80.50 | [5 empty] | 84.25 |  |  | 80.78 |  |  |  | 0.09 |  | 0.07 | [8 empty] | 19.43 |  |  |  |  | 0.51
2015 |  |  |  | 7392.01 |  |  | 7481 |  |  |  | 950 | [10 empty] | 84.74 |  |  |  | 85.21 | [5 empty] | 88.82 |  |  | 85.40 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 14.77 |  |  |  |  | 0.47
2016 |  |  |  | 8880.23 |  |  | 8784 |  |  |  | 950 | [10 empty] | 99.94 |  |  |  | 99.94 | [5 empty] | 106.42 |  |  | 100.00 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7699.56 |  |  | 7887 |  |  |  | 950 | [10 empty] | 89.31 |  |  |  | 89.82 | [5 empty] | 92.52 |  |  | 90.03 |  |  |  | 1.64 |  | 1.50 | [8 empty] | 8.69 |  |  |  |  | 0.50
2018 |  |  |  | 6656.19 |  |  | 6737 |  |  |  | 950 | [10 empty] | 76.80 |  |  |  | 76.80 | [5 empty] | 79.98 |  |  | 76.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.20 |  |  |  |  | 0.00
2019 |  |  |  | 8783.41 |  |  | 8662 |  |  |  | 950 | [10 empty] | 98.87 |  |  |  | 98.87 | [5 empty] | 105.54 |  |  | 98.88 |  |  |  | 1.13 |  | 1.13 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7533.32 |  |  | 7842 |  |  |  | 950 | [10 empty] | 88.96 |  |  |  | 88.96 | [5 empty] | 90.28 |  |  | 89.28 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 10.87 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 313
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1010 | [14 empty] | 1243 |  |  |  | 11
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 265
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 139
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 71
Z. |  | Other | [39 empty] | 23
Subtotal | [22 empty] | 1010 | [14 empty] | 1509 |  |  |  | 356 | [11 empty] | 211
Total | [22 empty] | 1010 | [14 empty] | 2076
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 2
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 97
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 45
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 26
35. |  |  | All other I&C Systems | [34 empty] | 8
41. |  |  | Main Generator Systems | [34 empty] | 86
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [37 empty] | 315
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-April, June-December. Additional electricity generation amounted to 375537 MWh. The unit was in the intermediate outage from 2020.05.16 to 2020.06.27. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-2
2020 Operating Experience
RU-97 | [8 empty] | BALAKOVO-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-08-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-10-08
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-01-18
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7538.45 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.37 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.37 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.63 %
Load Factor (LF) | [18 empty] | : | 90.34 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 86.41 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1194 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 4.39 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 744.49 | 0.00 |  |  |  | 210.78 |  | 707.13 | [8 empty] | 733.30 |  |  | 711.87 | [6 empty] | 720.74 |  | 734.42 |  |  |  | 724.76 |  |  | 755.71 |  |  | 735.10 | [9 empty] | 760.14 |  |  | 7538.45
EAF [%] |  |  |  |  | 100.00 | 0.91 |  |  |  | 31.80 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.37
UCF [%] |  |  |  |  | 100.00 | 0.91 |  |  |  | 31.80 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.37
LF [%] |  |  |  |  | 105.33 | 0.00 |  |  |  | 29.82 |  | 103.38 | [8 empty] | 103.75 |  |  | 104.07 | [6 empty] | 101.97 |  | 103.91 |  |  |  | 105.96 |  |  | 106.92 |  |  | 107.47 | [9 empty] | 107.55 |  |  | 90.34
OF [%] |  |  |  |  | 100.00 | 1.58 |  |  |  | 31.59 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.41
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 99.09 |  |  |  | 68.20 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.63
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 205164 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.33 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.56 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.01 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.95 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.04 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.29 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.39 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.82 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 5978.43 |  |  | 6928 |  |  |  | 950 | [10 empty] | 75.49 |  |  |  | 75.49 | [5 empty] | 70.63 |  |  | 77.66 |  |  |  | 6.59 |  | 5.33 | [8 empty] | 19.18 |  |  |  |  | 0.00
1989 |  |  |  | 6703.63 |  |  | 7626 |  |  |  | 950 | [10 empty] | 84.75 |  |  |  | 84.77 | [5 empty] | 80.55 |  |  | 87.05 |  |  |  | 9.33 |  | 8.72 | [8 empty] | 6.51 |  |  |  |  | 0.02
1990 |  |  |  | 5476.67 |  |  | 6165 |  |  |  | 950 | [10 empty] | 66.35 |  |  |  | 66.53 | [5 empty] | 65.81 |  |  | 70.38 |  |  |  | 15.71 |  | 12.40 | [8 empty] | 21.07 |  |  |  |  | 0.18
1991 |  |  |  | 4308.38 |  |  | 4845 |  |  |  | 950 | [10 empty] | 51.23 |  |  |  | 51.52 | [5 empty] | 51.77 |  |  | 55.31 |  |  |  | 10.81 |  | 6.25 | [8 empty] | 42.23 |  |  |  |  | 0.29
1992 |  |  |  | 5958.20 |  |  | 6601 |  |  |  | 950 | [10 empty] | 70.60 |  |  |  | 70.60 | [5 empty] | 71.39 |  |  | 75.14 |  |  |  | 9.39 |  | 7.32 | [8 empty] | 22.08 |  |  |  |  | 0.00
1993 |  |  |  | 3776.17 |  |  | 4147 |  |  |  | 950 | [10 empty] | 44.25 |  |  |  | 46.97 | [5 empty] | 45.38 |  |  | 47.34 |  |  |  | 38.44 |  | 29.33 | [8 empty] | 23.69 |  |  |  |  | 2.72
1994 |  |  |  | 4778.52 |  |  | 8020 |  |  |  | 950 | [10 empty] | 73.08 |  |  |  | 83.53 | [5 empty] | 57.42 |  |  | 91.55 |  |  |  | 12.39 |  | 11.81 | [8 empty] | 4.66 |  |  |  |  | 10.45
1995 |  |  |  | 2204.81 |  |  | 3261 |  |  |  | 950 | [10 empty] | 30.13 |  |  |  | 30.13 | [5 empty] | 26.49 |  |  | 37.23 |  |  |  | 27.40 |  | 11.37 | [8 empty] | 58.50 |  |  |  |  | 0.00
1996 |  |  |  | 2227.25 |  |  | 2604 |  |  |  | 950 | [10 empty] | 26.71 |  |  |  | 26.71 | [5 empty] | 26.69 |  |  | 29.64 |  |  |  | 66.37 |  | 52.71 | [8 empty] | 20.58 |  |  |  |  | 0.00
1997 |  |  |  | 4015.92 |  |  | 6158 |  |  |  | 950 | [10 empty] | 55.66 |  |  |  | 63.92 | [5 empty] | 48.26 |  |  | 70.30 |  |  |  | 27.93 |  | 24.77 | [8 empty] | 11.31 |  |  |  |  | 8.26
1998 |  |  |  | 3293.76 |  |  | 4984 |  |  |  | 950 | [10 empty] | 40.24 |  |  |  | 50.96 | [5 empty] | 39.58 |  |  | 56.89 |  |  |  | 0.11 |  | 0.05 | [8 empty] | 48.98 |  |  |  |  | 10.72
1999 |  |  |  | 2927.12 |  |  | 3942 |  |  |  | 950 | [10 empty] | 35.40 |  |  |  | 40.27 | [5 empty] | 35.17 |  |  | 45.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 59.73 |  |  |  |  | 4.87
2000 |  |  |  | 5730.07 |  |  | 7646 |  |  |  | 950 | [10 empty] | 68.89 |  |  |  | 83.21 | [5 empty] | 68.67 |  |  | 87.04 |  |  |  | 1.61 |  | 1.36 | [8 empty] | 15.43 |  |  |  |  | 14.32
2001 |  |  |  | 6678.82 |  |  | 7415 |  |  |  | 950 | [10 empty] | 79.86 |  |  |  | 83.90 | [5 empty] | 80.25 |  |  | 84.65 |  |  |  | 0.82 |  | 0.70 | [8 empty] | 15.40 |  |  |  |  | 4.05
2002 |  |  |  | 6756.53 |  |  | 7408 |  |  |  | 950 | [10 empty] | 80.40 |  |  |  | 84.43 | [5 empty] | 81.19 |  |  | 84.57 |  |  |  | 2.74 |  | 2.38 | [8 empty] | 13.19 |  |  |  |  | 4.03
2003 |  |  |  | 6171.76 |  |  | 6467 |  |  |  | 950 | [10 empty] | 72.70 |  |  |  | 73.99 | [5 empty] | 74.16 |  |  | 73.82 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 25.99 |  |  |  |  | 1.29
2004 |  |  |  | 7010.41 |  |  | 7514 |  |  |  | 950 | [10 empty] | 82.36 |  |  |  | 85.00 | [5 empty] | 84.01 |  |  | 85.54 |  |  |  | 0.72 |  | 0.62 | [8 empty] | 14.38 |  |  |  |  | 2.64
2005 |  |  |  | 6948.86 |  |  | 7688 |  |  |  | 950 | [10 empty] | 82.48 |  |  |  | 86.92 | [5 empty] | 83.49 |  |  | 87.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.08 |  |  |  |  | 4.44
2006 |  |  |  | 7237.48 |  |  | 7710 |  |  |  | 950 | [10 empty] | 84.59 |  |  |  | 87.38 | [5 empty] | 86.97 |  |  | 88.01 |  |  |  | 0.41 |  | 0.36 | [8 empty] | 12.26 |  |  |  |  | 2.79
2007 |  |  |  | 6657.18 |  |  | 7327 |  |  |  | 950 | [10 empty] | 78.71 |  |  |  | 83.46 | [5 empty] | 79.99 |  |  | 83.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.54 |  |  |  |  | 4.75
2008 |  |  |  | 7451.24 |  |  | 7750 |  |  |  | 950 | [10 empty] | 87.71 |  |  |  | 87.82 | [5 empty] | 89.29 |  |  | 88.23 |  |  |  | 1.21 |  | 1.07 | [8 empty] | 11.11 |  |  |  |  | 0.11
2009 |  |  |  | 7630.69 |  |  | 7797 |  |  |  | 950 | [10 empty] | 88.63 |  |  |  | 88.78 | [5 empty] | 91.69 |  |  | 89.01 |  |  |  | 0.28 |  | 0.25 | [8 empty] | 10.97 |  |  |  |  | 0.15
2010 |  |  |  | 8683.93 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.86 |  |  |  | 100.00 | [5 empty] | 104.35 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.14
2011 |  |  |  | 7288.41 |  |  | 7531 |  |  |  | 950 | [10 empty] | 85.42 |  |  |  | 85.76 | [5 empty] | 87.59 |  |  | 85.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.24 |  |  |  |  | 0.35
2012 |  |  |  | 7706.49 |  |  | 7829 |  |  |  | 950 | [10 empty] | 88.30 |  |  |  | 88.99 | [5 empty] | 92.35 |  |  | 89.13 |  |  |  | 1.35 |  | 1.22 | [8 empty] | 9.79 |  |  |  |  | 0.70
2013 |  |  |  | 8222.79 |  |  | 8509 |  |  |  | 950 | [10 empty] | 95.56 |  |  |  | 96.54 | [5 empty] | 98.81 |  |  | 97.13 |  |  |  | 0.45 |  | 0.44 | [8 empty] | 3.02 |  |  |  |  | 0.98
2014 |  |  |  | 6497.72 |  |  | 6672 |  |  |  | 950 | [10 empty] | 75.62 |  |  |  | 75.62 | [5 empty] | 78.07 |  |  | 76.16 |  |  |  | 10.92 |  | 9.27 | [8 empty] | 15.11 |  |  |  |  | 0.00
2015 |  |  |  | 6850.26 |  |  | 6845 |  |  |  | 950 | [10 empty] | 78.02 |  |  |  | 78.03 | [5 empty] | 82.32 |  |  | 78.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.97 |  |  |  |  | 0.01
2016 |  |  |  | 7922.42 |  |  | 7900 |  |  |  | 950 | [10 empty] | 89.79 |  |  |  | 89.79 | [5 empty] | 94.94 |  |  | 89.94 |  |  |  | 10.21 |  | 10.21 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6880.73 |  |  | 6972 |  |  |  | 950 | [10 empty] | 79.07 |  |  |  | 79.07 | [5 empty] | 82.68 |  |  | 79.59 |  |  |  | 0.40 |  | 0.31 | [8 empty] | 20.61 |  |  |  |  | 0.00
2018 |  |  |  | 7858.92 |  |  | 7874 |  |  |  | 950 | [10 empty] | 89.46 |  |  |  | 89.82 | [5 empty] | 94.44 |  |  | 89.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.18 |  |  |  |  | 0.36
2019 |  |  |  | 8867.45 |  |  | 8760 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 106.55 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7538.45 |  |  | 7590 |  |  |  | 950 | [10 empty] | 86.37 |  |  |  | 86.37 | [5 empty] | 90.34 |  |  | 86.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.63 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 347
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1193 | [14 empty] | 1399 |  |  |  | 83
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 91
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 3
Z. |  | Other | [39 empty] | 13
Subtotal | [22 empty] | 1193 | [14 empty] | 1490 |  |  |  | 446 | [11 empty] | 6
Total | [22 empty] | 1193 | [14 empty] | 1942
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 243
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 17
35. |  |  | All other I&C Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 69
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 349
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January, March-Desember. Additional electricity generation amounted to 369536 MWh. The unit was in the overhaul outage from 2020.02.01 to 2020.03.22. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-3
2020 Operating Experience
RU-98 | [8 empty] | BALAKOVO-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-11-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-12-25
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-08
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6845.49 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.34 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 78.34 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.66 %
Load Factor (LF) | [18 empty] | : | 82.03 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 78.32 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1904 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 2.26 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 256.41 |  | 696.99 | [8 empty] | 730.79 |  |  | 698.78 | [6 empty] | 732.20 |  | 744.99 |  |  |  | 727.63 |  |  | 755.20 |  |  | 738.89 | [9 empty] | 763.60 |  |  | 6845.49
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 37.77 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.34
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 37.77 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.34
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 36.28 |  | 101.90 | [8 empty] | 103.39 |  |  | 102.16 | [6 empty] | 103.59 |  | 105.40 |  |  |  | 106.38 |  |  | 106.85 |  |  | 108.03 | [9 empty] | 108.04 |  |  | 82.03
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 37.63 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.32
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 62.23 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 21.66
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 203588.44 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.02 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.17 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.47 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.11 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.42 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.55 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.95 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.4 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 6621.41 |  |  | 7792 |  |  |  | 950 | [10 empty] | 88.36 |  |  |  | 88.36 | [5 empty] | 87.44 |  |  | 91.12 |  |  |  | 6.11 |  | 5.75 | [8 empty] | 5.90 |  |  |  |  | 0.00
1990 |  |  |  | 5718.71 |  |  | 6696 |  |  |  | 950 | [10 empty] | 67.84 |  |  |  | 68.04 | [5 empty] | 68.72 |  |  | 76.44 |  |  |  | 13.53 |  | 10.65 | [8 empty] | 21.31 |  |  |  |  | 0.19
1991 |  |  |  | 5403.35 |  |  | 6124 |  |  |  | 950 | [10 empty] | 64.23 |  |  |  | 67.13 | [5 empty] | 64.93 |  |  | 69.91 |  |  |  | 12.68 |  | 9.75 | [8 empty] | 23.13 |  |  |  |  | 2.90
1992 |  |  |  | 5545.43 |  |  | 6202 |  |  |  | 950 | [10 empty] | 64.77 |  |  |  | 66.42 | [5 empty] | 66.45 |  |  | 70.60 |  |  |  | 17.40 |  | 14.00 | [8 empty] | 19.59 |  |  |  |  | 1.65
1993 |  |  |  | 4378.64 |  |  | 5461 |  |  |  | 950 | [10 empty] | 52.73 |  |  |  | 61.63 | [5 empty] | 52.62 |  |  | 62.34 |  |  |  | 13.51 |  | 9.63 | [8 empty] | 28.74 |  |  |  |  | 8.90
1994 |  |  |  | 3340.14 |  |  | 5389 |  |  |  | 950 | [10 empty] | 70.66 |  |  |  | 70.69 | [5 empty] | 40.14 |  |  | 61.52 |  |  |  | 10.93 |  | 8.68 | [8 empty] | 20.64 |  |  |  |  | 0.03
1995 |  |  |  | 2674.65 |  |  | 5511 |  |  |  | 950 | [10 empty] | 47.52 |  |  |  | 53.12 | [5 empty] | 32.14 |  |  | 62.91 |  |  |  | 20.77 |  | 13.93 | [8 empty] | 32.95 |  |  |  |  | 5.60
1996 |  |  |  | 5315.40 |  |  | 7085 |  |  |  | 950 | [10 empty] | 64.26 |  |  |  | 75.94 | [5 empty] | 63.70 |  |  | 80.66 |  |  |  | 1.93 |  | 1.49 | [8 empty] | 22.57 |  |  |  |  | 11.68
1997 |  |  |  | 2058.79 |  |  | 3395 |  |  |  | 950 | [10 empty] | 25.29 |  |  |  | 38.78 | [5 empty] | 24.74 |  |  | 38.76 |  |  |  | 0.58 |  | 0.22 | [8 empty] | 60.99 |  |  |  |  | 13.49
1998 |  |  |  | 5348.52 |  |  | 7136 |  |  |  | 950 | [10 empty] | 64.42 |  |  |  | 73.01 | [5 empty] | 64.27 |  |  | 81.46 |  |  |  | 0.09 |  | 0.06 | [8 empty] | 26.93 |  |  |  |  | 8.59
1999 |  |  |  | 5457.98 |  |  | 6552 |  |  |  | 950 | [10 empty] | 65.61 |  |  |  | 71.98 | [5 empty] | 65.59 |  |  | 74.79 |  |  |  | 0.16 |  | 0.12 | [8 empty] | 27.91 |  |  |  |  | 6.37
2000 |  |  |  | 6482.85 |  |  | 7327 |  |  |  | 950 | [10 empty] | 77.18 |  |  |  | 82.00 | [5 empty] | 77.69 |  |  | 83.41 |  |  |  | 1.10 |  | 0.91 | [8 empty] | 17.09 |  |  |  |  | 4.82
2001 |  |  |  | 6050.74 |  |  | 6927 |  |  |  | 950 | [10 empty] | 72.10 |  |  |  | 78.65 | [5 empty] | 72.71 |  |  | 79.08 |  |  |  | 0.15 |  | 0.12 | [8 empty] | 21.23 |  |  |  |  | 6.55
2002 |  |  |  | 6926.31 |  |  | 7478 |  |  |  | 950 | [10 empty] | 81.99 |  |  |  | 85.35 | [5 empty] | 83.23 |  |  | 85.37 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 14.64 |  |  |  |  | 3.36
2003 |  |  |  | 7016.14 |  |  | 7471 |  |  |  | 950 | [10 empty] | 83.19 |  |  |  | 85.05 | [5 empty] | 84.31 |  |  | 85.29 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 14.86 |  |  |  |  | 1.86
2004 |  |  |  | 7227.76 |  |  | 7607 |  |  |  | 950 | [10 empty] | 85.13 |  |  |  | 86.38 | [5 empty] | 86.61 |  |  | 86.60 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 13.56 |  |  |  |  | 1.25
2005 |  |  |  | 6244.44 |  |  | 7060 |  |  |  | 950 | [10 empty] | 74.50 |  |  |  | 79.90 | [5 empty] | 75.04 |  |  | 80.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.10 |  |  |  |  | 5.40
2006 |  |  |  | 7741.84 |  |  | 8354 |  |  |  | 950 | [10 empty] | 91.38 |  |  |  | 95.30 | [5 empty] | 93.03 |  |  | 95.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.70 |  |  |  |  | 3.92
2007 |  |  |  | 7407.10 |  |  | 8050 |  |  |  | 950 | [10 empty] | 87.59 |  |  |  | 91.82 | [5 empty] | 89.01 |  |  | 91.89 |  |  |  | 0.68 |  | 0.63 | [8 empty] | 7.56 |  |  |  |  | 4.23
2008 |  |  |  | 7384.34 |  |  | 7693 |  |  |  | 950 | [10 empty] | 86.99 |  |  |  | 87.15 | [5 empty] | 88.49 |  |  | 87.58 |  |  |  | 1.09 |  | 0.96 | [8 empty] | 11.89 |  |  |  |  | 0.16
2009 |  |  |  | 6932.73 |  |  | 7276 |  |  |  | 950 | [10 empty] | 82.56 |  |  |  | 82.63 | [5 empty] | 83.31 |  |  | 83.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.37 |  |  |  |  | 0.08
2010 |  |  |  | 7649.62 |  |  | 7710 |  |  |  | 950 | [10 empty] | 87.13 |  |  |  | 87.75 | [5 empty] | 91.92 |  |  | 88.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.25 |  |  |  |  | 0.63
2011 |  |  |  | 8579.15 |  |  | 8627 |  |  |  | 950 | [10 empty] | 98.26 |  |  |  | 98.26 | [5 empty] | 103.10 |  |  | 98.49 |  |  |  | 1.61 |  | 1.61 | [8 empty] | 0.13 |  |  |  |  | 0.00
2012 |  |  |  | 7716.23 |  |  | 7854 |  |  |  | 950 | [10 empty] | 89.32 |  |  |  | 89.34 | [5 empty] | 92.47 |  |  | 89.41 |  |  |  | 0.59 |  | 0.53 | [8 empty] | 10.13 |  |  |  |  | 0.02
2013 |  |  |  | 7378.17 |  |  | 7481 |  |  |  | 950 | [10 empty] | 84.53 |  |  |  | 84.94 | [5 empty] | 88.66 |  |  | 85.40 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 14.97 |  |  |  |  | 0.41
2014 |  |  |  | 7746.92 |  |  | 7827 |  |  |  | 950 | [10 empty] | 88.55 |  |  |  | 88.82 | [5 empty] | 93.08 |  |  | 89.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.18 |  |  |  |  | 0.26
2015 |  |  |  | 8250.27 |  |  | 8415 |  |  |  | 950 | [10 empty] | 95.78 |  |  |  | 95.78 | [5 empty] | 99.14 |  |  | 96.06 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 4.16 |  |  |  |  | 0.00
2016 |  |  |  | 7307.38 |  |  | 7331 |  |  |  | 950 | [10 empty] | 82.96 |  |  |  | 83.26 | [5 empty] | 87.57 |  |  | 83.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.74 |  |  |  |  | 0.30
2017 |  |  |  | 8653.43 |  |  | 8727 |  |  |  | 950 | [10 empty] | 99.16 |  |  |  | 99.48 | [5 empty] | 103.98 |  |  | 99.62 |  |  |  | 0.41 |  | 0.40 | [8 empty] | 0.11 |  |  |  |  | 0.32
2018 |  |  |  | 7167.75 |  |  | 7163 |  |  |  | 950 | [10 empty] | 81.59 |  |  |  | 81.71 | [5 empty] | 86.13 |  |  | 81.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.29 |  |  |  |  | 0.12
2019 |  |  |  | 4983.36 |  |  | 4979 |  |  |  | 950 | [10 empty] | 56.33 |  |  |  | 56.84 | [5 empty] | 59.88 |  |  | 56.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 43.16 |  |  |  |  | 0.51
2020 |  |  |  | 6845.49 |  |  | 6880 |  |  |  | 950 | [10 empty] | 78.34 |  |  |  | 78.34 | [5 empty] | 82.03 |  |  | 78.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.66 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 74
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1903 | [14 empty] | 1395 |  |  |  | 21
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 169
E. |  | Testing of plant systems or components | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 46
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 1903 | [14 empty] | 1564 |  |  |  | 103 | [11 empty] | 47
Total | [22 empty] | 1903 | [14 empty] | 1714
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 24
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 9
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [37 empty] | 77
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in March-December. Additional electricity generation amounted to 355916 MWh. The unit was in the intermediate outage from 2020.01.01 to 2020.03.20. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-4
2020 Operating Experience
RU-99 | [8 empty] | BALAKOVO-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-04-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-04-11
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-12-22
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7368.35 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.11 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.11 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.87 %
Load Factor (LF) | [18 empty] | : | 88.3 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 83.19 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1477 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 4.1 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 768.46 | 719.90 |  |  |  | 728.12 |  | 684.35 | [8 empty] | 749.77 |  |  | 715.03 | [6 empty] | 750.64 |  | 761.36 |  |  |  | 748.34 |  |  | 742.39 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7368.35
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.71 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 97.63 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 83.11
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.71 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 97.63 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 83.11
LF [%] |  |  |  |  | 108.72 | 108.88 |  |  |  | 103.02 |  | 100.05 | [8 empty] | 106.08 |  |  | 104.54 | [6 empty] | 106.20 |  | 107.72 |  |  |  | 109.41 |  |  | 105.04 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 88.30
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 98.25 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 83.19
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.29 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.29 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 2.37 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 16.87
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 188323.96 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.41 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.5 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.71 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.09 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.12 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.21 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.95 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 3676.28 |  |  | 5206 |  |  |  | 950 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 3828.53 |  |  | 4604 |  |  |  | 950 | [10 empty] | 48.45 |  |  |  | 69.54 | [5 empty] | 46.00 |  |  | 52.56 |  |  |  | 1.58 |  | 1.12 | [8 empty] | 29.34 |  |  |  |  | 21.09
1995 |  |  |  | 5609.99 |  |  | 8760 |  |  |  | 950 | [10 empty] | 86.46 |  |  |  | 88.72 | [5 empty] | 67.41 |  |  | 100.00 |  |  |  | 11.28 |  | 11.28 | [8 empty] | 0.00 |  |  |  |  | 2.26
1996 |  |  |  | 4545.55 |  |  | 6652 |  |  |  | 950 | [10 empty] | 55.47 |  |  |  | 59.85 | [5 empty] | 54.47 |  |  | 75.73 |  |  |  | 13.90 |  | 9.66 | [8 empty] | 30.49 |  |  |  |  | 4.39
1997 |  |  |  | 4637.72 |  |  | 6637 |  |  |  | 950 | [10 empty] | 59.64 |  |  |  | 71.29 | [5 empty] | 55.73 |  |  | 75.76 |  |  |  | 0.16 |  | 0.11 | [8 empty] | 28.60 |  |  |  |  | 11.65
1998 |  |  |  | 5042.49 |  |  | 6936 |  |  |  | 950 | [10 empty] | 60.89 |  |  |  | 71.31 | [5 empty] | 60.59 |  |  | 79.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.69 |  |  |  |  | 10.42
1999 |  |  |  | 5803.91 |  |  | 7268 |  |  |  | 950 | [10 empty] | 69.59 |  |  |  | 77.55 | [5 empty] | 69.74 |  |  | 82.97 |  |  |  | 0.37 |  | 0.29 | [8 empty] | 22.17 |  |  |  |  | 7.95
2000 |  |  |  | 6665.85 |  |  | 7216 |  |  |  | 950 | [10 empty] | 78.95 |  |  |  | 80.96 | [5 empty] | 79.88 |  |  | 82.15 |  |  |  | 0.78 |  | 0.63 | [8 empty] | 18.40 |  |  |  |  | 2.01
2001 |  |  |  | 6578.09 |  |  | 7354 |  |  |  | 950 | [10 empty] | 78.30 |  |  |  | 83.91 | [5 empty] | 79.04 |  |  | 83.95 |  |  |  | 0.47 |  | 0.40 | [8 empty] | 15.69 |  |  |  |  | 5.61
2002 |  |  |  | 6292.92 |  |  | 6723 |  |  |  | 950 | [10 empty] | 72.80 |  |  |  | 77.28 | [5 empty] | 75.62 |  |  | 76.75 |  |  |  | 0.20 |  | 0.16 | [8 empty] | 22.57 |  |  |  |  | 4.47
2003 |  |  |  | 7223.84 |  |  | 7541 |  |  |  | 950 | [10 empty] | 84.64 |  |  |  | 85.84 | [5 empty] | 86.80 |  |  | 86.08 |  |  |  | 0.50 |  | 0.43 | [8 empty] | 13.73 |  |  |  |  | 1.20
2004 |  |  |  | 7022.94 |  |  | 7540 |  |  |  | 950 | [10 empty] | 82.51 |  |  |  | 85.37 | [5 empty] | 84.16 |  |  | 85.84 |  |  |  | 0.45 |  | 0.39 | [8 empty] | 14.24 |  |  |  |  | 2.86
2005 |  |  |  | 6938.28 |  |  | 7699 |  |  |  | 950 | [10 empty] | 82.14 |  |  |  | 87.62 | [5 empty] | 83.36 |  |  | 87.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.38 |  |  |  |  | 5.48
2006 |  |  |  | 6805.35 |  |  | 7230 |  |  |  | 950 | [10 empty] | 79.61 |  |  |  | 82.20 | [5 empty] | 81.78 |  |  | 82.53 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 17.74 |  |  |  |  | 2.58
2007 |  |  |  | 7153.35 |  |  | 7787 |  |  |  | 950 | [10 empty] | 84.70 |  |  |  | 88.53 | [5 empty] | 85.96 |  |  | 88.89 |  |  |  | 0.40 |  | 0.36 | [8 empty] | 11.11 |  |  |  |  | 3.83
2008 |  |  |  | 8330.42 |  |  | 8779 |  |  |  | 950 | [10 empty] | 99.71 |  |  |  | 99.73 | [5 empty] | 99.83 |  |  | 99.94 |  |  |  | 0.14 |  | 0.14 | [8 empty] | 0.13 |  |  |  |  | 0.02
2009 |  |  |  | 7409.95 |  |  | 7727 |  |  |  | 950 | [10 empty] | 87.83 |  |  |  | 87.83 | [5 empty] | 89.02 |  |  | 88.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.17 |  |  |  |  | 0.00
2010 |  |  |  | 7199.69 |  |  | 7168 |  |  |  | 950 | [10 empty] | 81.35 |  |  |  | 81.35 | [5 empty] | 86.51 |  |  | 81.83 |  |  |  | 2.02 |  | 1.68 | [8 empty] | 16.97 |  |  |  |  | 0.00
2011 |  |  |  | 7625.20 |  |  | 7619 |  |  |  | 950 | [10 empty] | 86.42 |  |  |  | 86.42 | [5 empty] | 91.64 |  |  | 86.98 |  |  |  | 2.50 |  | 2.22 | [8 empty] | 11.36 |  |  |  |  | 0.00
2012 |  |  |  | 8517.84 |  |  | 8608 |  |  |  | 950 | [10 empty] | 97.72 |  |  |  | 97.72 | [5 empty] | 102.07 |  |  | 98.00 |  |  |  | 2.08 |  | 2.07 | [8 empty] | 0.20 |  |  |  |  | 0.00
2013 |  |  |  | 7847.25 |  |  | 7847 |  |  |  | 950 | [10 empty] | 89.13 |  |  |  | 89.13 | [5 empty] | 94.30 |  |  | 89.58 |  |  |  | 0.61 |  | 0.54 | [8 empty] | 10.33 |  |  |  |  | 0.00
2014 |  |  |  | 7204.52 |  |  | 7173 |  |  |  | 950 | [10 empty] | 81.27 |  |  |  | 81.36 | [5 empty] | 86.56 |  |  | 81.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.64 |  |  |  |  | 0.09
2015 |  |  |  | 8800.05 |  |  | 8757 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.74 |  |  | 99.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 8006.24 |  |  | 8045 |  |  |  | 950 | [10 empty] | 91.07 |  |  |  | 91.58 | [5 empty] | 95.94 |  |  | 91.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.42 |  |  |  |  | 0.52
2017 |  |  |  | 7336.59 |  |  | 7386 |  |  |  | 950 | [10 empty] | 83.99 |  |  |  | 84.24 | [5 empty] | 88.16 |  |  | 84.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.76 |  |  |  |  | 0.25
2018 |  |  |  | 8777.02 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 105.47 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.00
2019 |  |  |  | 6075.81 |  |  | 5952 |  |  |  | 950 | [10 empty] | 67.76 |  |  |  | 67.76 | [5 empty] | 73.01 |  |  | 67.95 |  |  |  | 1.15 |  | 0.88 | [8 empty] | 31.36 |  |  |  |  | 0.00
2020 |  |  |  | 7368.35 |  |  | 7307 |  |  |  | 950 | [10 empty] | 83.11 |  |  |  | 83.11 | [5 empty] | 88.30 |  |  | 83.19 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 16.87 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1993 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 28
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1477 | [14 empty] | 1199
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 17
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 13
L. |  | Human factor related | [39 empty] | 0
Z. |  | Other | [51 empty] | 62
Subtotal | [22 empty] | 1477 | [14 empty] | 1216 |  |  |  | 28 | [11 empty] | 75
Total | [22 empty] | 1477 | [14 empty] | 1319
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1993 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 1
16. |  |  | Steam generation systems | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 28
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-October. Additional electricity generation amounted to 468553 MWh. The unit was in the overhaul outage from 2020.10.31 to 2021.01.01. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BELOYARSK-3
2020 Operating Experience
RU-21 | [8 empty] | BELOYARSK-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | FBR / BN-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1969-01-01
Thermal power | [12 empty] | : |  |  | 1470 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-04-08
Gross electrical power | [12 empty] | : |  |  | 600 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-11-01
Reference unit power (net) | [12 empty] | : |  |  | 560 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 8.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 550
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 5 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 3
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 100000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.05 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 13
| Active core height/length [m] | [13 empty] | : |  |  | 1.03 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 369 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 38 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 19 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | Na | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4169.76 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.47 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.6 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.22 %
Unit Capability Factor (UCF) | [18 empty] | : | 81.6 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 17.19 %
Load Factor (LF) | [18 empty] | : | 84.77 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 83.54 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1446 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 86.46 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 432.72 | 402.60 |  |  |  | 197.62 |  | 423.62 | [8 empty] | 436.42 |  |  | 419.83 | [6 empty] | 403.88 |  | 32.57 |  |  |  | 138.63 |  |  | 437.37 |  |  | 402.25 | [9 empty] | 442.25 |  |  | 4169.76
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 46.86 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 94.27 |  | 9.26 |  |  |  | 34.44 |  |  | 100.00 |  |  | 95.63 | [9 empty] | 100.00 |  |  | 81.60
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 46.86 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 94.27 |  | 9.26 |  |  |  | 34.44 |  |  | 100.00 |  |  | 95.63 | [9 empty] | 100.00 |  |  | 81.60
LF [%] |  |  |  |  | 103.86 | 103.29 |  |  |  | 47.43 |  | 105.06 | [8 empty] | 104.75 |  |  | 104.12 | [6 empty] | 96.94 |  | 7.82 |  |  |  | 34.38 |  |  | 104.97 |  |  | 99.76 | [9 empty] | 106.15 |  |  | 84.77
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 51.48 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 10.62 |  |  |  | 41.67 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.54
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 5.73 |  | 0.00 |  |  |  | 11.70 |  |  | 0.00 |  |  | 4.37 | [9 empty] | 0.00 |  |  | 1.47
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 5.73 |  | 0.00 |  |  |  | 4.57 |  |  | 0.00 |  |  | 4.37 | [9 empty] | 0.00 |  |  | 1.22
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 53.14 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 90.74 |  |  |  | 60.99 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 17.19
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 149131.03 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.68 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.73 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.99 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.26 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.75 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.53 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.77 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | Data not provided
1982 |  |  |  | 2771.00 |  |  | 5555 |  |  |  | 560 | [10 empty] | 59.25 |  |  |  | 59.25 | [5 empty] | 56.49 |  |  | 63.41 |  |  |  | 11.50 |  | 7.70 | [8 empty] | 33.05 |  |  |  |  | 0.00
1983 |  |  |  | 3545.21 |  |  | 6737 |  |  |  | 560 | [10 empty] | 72.72 |  |  |  | 73.35 | [5 empty] | 72.27 |  |  | 76.91 |  |  |  | 3.71 |  | 2.82 | [8 empty] | 23.83 |  |  |  |  | 0.63
1984 |  |  |  | 3584.11 |  |  | 6848 |  |  |  | 560 | [10 empty] | 73.29 |  |  |  | 73.29 | [5 empty] | 72.86 |  |  | 77.96 |  |  |  | 5.70 |  | 4.43 | [8 empty] | 22.28 |  |  |  |  | 0.00
1985 |  |  |  | 3561.83 |  |  | 6544 |  |  |  | 560 | [10 empty] | 72.85 |  |  |  | 72.85 | [5 empty] | 72.61 |  |  | 74.70 |  |  |  | 2.47 |  | 1.85 | [8 empty] | 25.30 |  |  |  |  | 0.00
1986 |  |  |  | 3600.73 |  |  | 6818 |  |  |  | 560 | [10 empty] | 73.82 |  |  |  | 74.28 | [5 empty] | 73.40 |  |  | 77.83 |  |  |  | 4.78 |  | 3.73 | [8 empty] | 21.99 |  |  |  |  | 0.46
1987 |  |  |  | 3894.99 |  |  | 6714 |  |  |  | 600 | [10 empty] | 75.93 |  |  |  | 75.93 | [5 empty] | 74.11 |  |  | 76.64 |  |  |  | 2.64 |  | 2.05 | [8 empty] | 22.02 |  |  |  |  | 0.00
1988 |  |  |  | 3762.19 |  |  | 6810 |  |  |  | 560 | [10 empty] | 76.97 |  |  |  | 76.97 | [5 empty] | 76.48 |  |  | 77.53 |  |  |  | 0.38 |  | 0.30 | [8 empty] | 22.74 |  |  |  |  | 0.00
1989 |  |  |  | 3694.43 |  |  | 6800 |  |  |  | 560 | [10 empty] | 76.95 |  |  |  | 76.95 | [5 empty] | 75.31 |  |  | 77.63 |  |  |  | 1.21 |  | 0.94 | [8 empty] | 22.10 |  |  |  |  | 0.00
1990 |  |  |  | 3198.00 |  |  | 6627 |  |  |  | 560 | [10 empty] | 65.85 |  |  |  | 66.65 | [5 empty] | 65.19 |  |  | 75.65 |  |  |  | 11.05 |  | 8.28 | [8 empty] | 25.07 |  |  |  |  | 0.79
1991 |  |  |  | 3394.00 |  |  | 6631 |  |  |  | 560 | [10 empty] | 63.57 |  |  |  | 63.57 | [5 empty] | 69.19 |  |  | 75.70 |  |  |  | 13.75 |  | 10.14 | [8 empty] | 26.29 |  |  |  |  | 0.00
1992 |  |  |  | 4094.97 |  |  | 7449 |  |  |  | 560 | [10 empty] | 82.82 |  |  |  | 83.06 | [5 empty] | 83.26 |  |  | 84.81 |  |  |  | 0.34 |  | 0.28 | [8 empty] | 16.66 |  |  |  |  | 0.24
1993 |  |  |  | 3914.92 |  |  | 7065 |  |  |  | 560 | [10 empty] | 79.49 |  |  |  | 79.57 | [5 empty] | 79.81 |  |  | 80.65 |  |  |  | 7.18 |  | 6.15 | [8 empty] | 14.28 |  |  |  |  | 0.07
1994 |  |  |  | 3810.67 |  |  | 6977 |  |  |  | 560 | [10 empty] | 78.78 |  |  |  | 78.92 | [5 empty] | 77.68 |  |  | 79.65 |  |  |  | 0.90 |  | 0.71 | [8 empty] | 20.37 |  |  |  |  | 0.14
1995 |  |  |  | 3413.27 |  |  | 6953 |  |  |  | 560 | [10 empty] | 70.70 |  |  |  | 72.28 | [5 empty] | 69.58 |  |  | 79.37 |  |  |  | 9.36 |  | 7.46 | [8 empty] | 20.26 |  |  |  |  | 1.57
1996 |  |  |  | 3722.33 |  |  | 7010 |  |  |  | 560 | [10 empty] | 76.32 |  |  |  | 78.07 | [5 empty] | 75.67 |  |  | 79.80 |  |  |  | 1.72 |  | 1.37 | [8 empty] | 20.57 |  |  |  |  | 1.75
1997 |  |  |  | 3545.80 |  |  | 6596 |  |  |  | 560 | [10 empty] | 72.97 |  |  |  | 74.58 | [5 empty] | 72.28 |  |  | 75.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.42 |  |  |  |  | 1.61
1998 |  |  |  | 2335.33 |  |  | 4385 |  |  |  | 560 | [10 empty] | 47.67 |  |  |  | 49.23 | [5 empty] | 47.61 |  |  | 50.06 |  |  |  | 38.80 |  | 31.21 | [8 empty] | 19.55 |  |  |  |  | 1.56
1999 |  |  |  | 3720.99 |  |  | 6972 |  |  |  | 560 | [10 empty] | 76.18 |  |  |  | 77.96 | [5 empty] | 75.85 |  |  | 79.59 |  |  |  | 4.10 |  | 3.34 | [8 empty] | 18.71 |  |  |  |  | 1.78
2000 |  |  |  | 3565.82 |  |  | 6820 |  |  |  | 560 | [10 empty] | 72.49 |  |  |  | 75.49 | [5 empty] | 72.49 |  |  | 77.64 |  |  |  | 0.31 |  | 0.23 | [8 empty] | 24.27 |  |  |  |  | 3.00
2001 |  |  |  | 3891.10 |  |  | 7214 |  |  |  | 560 | [10 empty] | 79.90 |  |  |  | 80.72 | [5 empty] | 79.32 |  |  | 82.35 |  |  |  | 1.24 |  | 1.01 | [8 empty] | 18.27 |  |  |  |  | 0.82
2002 |  |  |  | 3774.40 |  |  | 7069 |  |  |  | 560 | [10 empty] | 77.30 |  |  |  | 79.34 | [5 empty] | 76.94 |  |  | 80.70 |  |  |  | 2.14 |  | 1.74 | [8 empty] | 18.93 |  |  |  |  | 2.04
2003 |  |  |  | 3693.28 |  |  | 6836 |  |  |  | 560 | [10 empty] | 75.74 |  |  |  | 76.81 | [5 empty] | 75.29 |  |  | 78.04 |  |  |  | 0.91 |  | 0.71 | [8 empty] | 22.48 |  |  |  |  | 1.07
2004 |  |  |  | 3927.64 |  |  | 7185 |  |  |  | 560 | [10 empty] | 80.02 |  |  |  | 80.81 | [5 empty] | 79.85 |  |  | 81.80 |  |  |  | 0.78 |  | 0.64 | [8 empty] | 18.56 |  |  |  |  | 0.78
2005 |  |  |  | 3802.75 |  |  | 6977 |  |  |  | 560 | [10 empty] | 77.76 |  |  |  | 78.77 | [5 empty] | 77.52 |  |  | 79.65 |  |  |  | 0.09 |  | 0.07 | [8 empty] | 21.16 |  |  |  |  | 1.02
2006 |  |  |  | 3844.94 |  |  | 7001 |  |  |  | 560 | [10 empty] | 78.38 |  |  |  | 79.02 | [5 empty] | 78.38 |  |  | 79.92 |  |  |  | 0.36 |  | 0.29 | [8 empty] | 20.69 |  |  |  |  | 0.65
2007 |  |  |  | 3798.42 |  |  | 7089 |  |  |  | 560 | [10 empty] | 77.52 |  |  |  | 77.80 | [5 empty] | 77.43 |  |  | 80.92 |  |  |  | 0.46 |  | 0.36 | [8 empty] | 21.84 |  |  |  |  | 0.28
2008 |  |  |  | 3781.03 |  |  | 6918 |  |  |  | 560 | [10 empty] | 76.85 |  |  |  | 76.95 | [5 empty] | 76.87 |  |  | 78.76 |  |  |  | 0.47 |  | 0.36 | [8 empty] | 22.69 |  |  |  |  | 0.10
2009 |  |  |  | 3736.60 |  |  | 6734 |  |  |  | 560 | [10 empty] | 75.58 |  |  |  | 75.61 | [5 empty] | 76.17 |  |  | 76.87 |  |  |  | 0.49 |  | 0.37 | [8 empty] | 24.01 |  |  |  |  | 0.03
2010 |  |  |  | 3669.75 |  |  | 6541 |  |  |  | 560 | [10 empty] | 73.51 |  |  |  | 73.56 | [5 empty] | 74.81 |  |  | 74.67 |  |  |  | 0.73 |  | 0.54 | [8 empty] | 25.90 |  |  |  |  | 0.05
2011 |  |  |  | 3968.73 |  |  | 7141 |  |  |  | 560 | [10 empty] | 79.17 |  |  |  | 79.17 | [5 empty] | 80.91 |  |  | 81.53 |  |  |  | 0.71 |  | 0.57 | [8 empty] | 20.26 |  |  |  |  | 0.00
2012 |  |  |  | 3975.50 |  |  | 7250 |  |  |  | 560 | [10 empty] | 78.84 |  |  |  | 78.84 | [5 empty] | 80.82 |  |  | 82.54 |  |  |  | 1.62 |  | 2.69 | [8 empty] | 18.47 |  |  |  |  | 0.00
2013 |  |  |  | 3841.06 |  |  | 7398 |  |  |  | 560 | [10 empty] | 77.62 |  |  |  | 77.80 | [5 empty] | 78.30 |  |  | 84.45 |  |  |  | 7.27 |  | 6.10 | [8 empty] | 16.11 |  |  |  |  | 0.18
2014 |  |  |  | 4222.91 |  |  | 7455 |  |  |  | 560 | [10 empty] | 83.77 |  |  |  | 83.77 | [5 empty] | 86.07 |  |  | 85.09 |  |  |  | 0.58 |  | 0.49 | [8 empty] | 15.75 |  |  |  |  | 0.00
2015 |  |  |  | 4220.16 |  |  | 7414 |  |  |  | 560 | [10 empty] | 83.78 |  |  |  | 83.78 | [5 empty] | 86.03 |  |  | 84.63 |  |  |  | 0.39 |  | 0.33 | [8 empty] | 15.89 |  |  |  |  | 0.00
2016 |  |  |  | 4307.17 |  |  | 7517 |  |  |  | 560 | [10 empty] | 84.66 |  |  |  | 84.66 | [5 empty] | 87.56 |  |  | 85.58 |  |  |  | 0.41 |  | 0.35 | [8 empty] | 14.98 |  |  |  |  | 0.00
2017 |  |  |  | 4323.23 |  |  | 7548 |  |  |  | 560 | [10 empty] | 85.36 |  |  |  | 85.36 | [5 empty] | 88.13 |  |  | 86.16 |  |  |  | 0.32 |  | 0.27 | [8 empty] | 14.36 |  |  |  |  | 0.00
2018 |  |  |  | 3809.52 |  |  | 6911 |  |  |  | 560 | [10 empty] | 75.28 |  |  |  | 75.28 | [5 empty] | 77.66 |  |  | 78.89 |  |  |  | 3.23 |  | 3.38 | [8 empty] | 21.34 |  |  |  |  | 0.00
2019 |  |  |  | 4184.26 |  |  | 7453 |  |  |  | 560 | [10 empty] | 82.22 |  |  |  | 82.22 | [5 empty] | 85.30 |  |  | 85.08 |  |  |  | 1.95 |  | 2.15 | [8 empty] | 15.63 |  |  |  |  | 0.00
2020 |  |  |  | 4169.76 |  |  | 7338 |  |  |  | 560 | [10 empty] | 81.60 |  |  |  | 81.60 | [5 empty] | 84.77 |  |  | 83.54 |  |  |  | 1.47 |  | 1.22 | [8 empty] | 17.19 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 71 | [14 empty] | 121
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1443 | [14 empty] | 1269
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 430 |  |  |  | 6
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 1
T. |  | Heat supply (on-site to support next unit or desalination and off-site distribution) | [51 empty] | 0
Subtotal | [22 empty] | 1443 |  |  |  | 71 | [10 empty] | 1699 |  |  |  | 129 | [11 empty] | 3
Total | [22 empty] | 1514 | [14 empty] | 1831
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [19 empty] | 71 | [14 empty] | 2
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 29
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 68
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 71 | [14 empty] | 123
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-December. Additional electricity generation amounted to 151462.267 MWh. The unit was in the intermediate outage from 2020.03.02 to 2020.03.17 and the routine maintenance outage from 2020.08.04 to 2020.09.18 . Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BELOYARSK-4
2020 Operating Experience
RU-116 | [8 empty] | BELOYARSK-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | FBR / BN-800 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2006-07-18
Thermal power | [12 empty] | : |  |  | 2100 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-12-10
Gross electrical power | [12 empty] | : |  |  | 885 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-10-31
Reference unit power (net) | [12 empty] | : |  |  | 820 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 1.65
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 547
| Fuel material | [13 empty] | : |  |  | UO2/PuO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 6 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.56 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 13
| Active core height/length [m] | [13 empty] | : |  |  | 0.88 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 565 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 38 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 16 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | NA | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5934.14 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.45 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.92 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.38 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.64 %
Load Factor (LF) | [18 empty] | : | 82.39 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.06 %
Operating Factor (OF) | [18 empty] | : | 83.94 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1411 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 96.17 | 572.25 |  |  |  | 609.66 |  | 585.82 | [8 empty] | 604.68 |  |  | 569.23 | [6 empty] | 0.00 |  | 529.08 |  |  |  | 587.91 |  |  | 607.59 |  |  | 586.70 | [9 empty] | 585.05 |  |  | 5934.14
EAF [%] |  |  |  |  | 17.17 | 99.41 |  |  |  | 99.08 |  | 98.35 | [8 empty] | 98.25 |  |  | 95.78 | [6 empty] | 0.01 |  | 86.63 |  |  |  | 98.99 |  |  | 98.99 |  |  | 98.52 | [9 empty] | 95.07 |  |  | 81.92
UCF [%] |  |  |  |  | 17.28 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 98.02 | [6 empty] | 0.01 |  | 88.17 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.55 | [9 empty] | 96.00 |  |  | 82.98
LF [%] |  |  |  |  | 15.76 | 100.27 |  |  |  | 99.93 |  | 99.22 | [8 empty] | 99.12 |  |  | 96.41 | [6 empty] | 0.00 |  | 86.72 |  |  |  | 99.58 |  |  | 99.59 |  |  | 99.37 | [9 empty] | 95.90 |  |  | 82.39
OF [%] |  |  |  |  | 20.30 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 0.13 |  | 89.92 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.94
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.45 | [9 empty] | 4.00 |  |  | 0.45
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.45 | [9 empty] | 4.00 |  |  | 0.38
PUF [%] |  |  |  |  | 82.72 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.98 | [6 empty] | 99.99 |  | 11.83 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.64
XUF [%] |  |  |  |  | 0.11 | 0.59 |  |  |  | 0.92 |  | 1.65 | [8 empty] | 1.75 |  |  | 2.25 | [6 empty] | 0.00 |  | 1.54 |  |  |  | 1.01 |  |  | 1.01 |  |  | 1.03 | [9 empty] | 0.93 |  |  | 1.06
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 23909.64 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.41 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.26 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.88 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 72.41 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 23.71 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.45 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.15 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.5 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 3456.96 |  |  | 5453 |  |  |  | 820 | [10 empty] | 81.92 |  |  |  | 81.92 | [5 empty] | 81.96 |  |  | 96.45 |  |  |  | 18.08 |  | 18.08 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 5165.75 |  |  | 6551 |  |  |  | 820 | [10 empty] | 71.81 |  |  |  | 73.11 | [5 empty] | 71.91 |  |  | 74.78 |  |  |  | 1.71 |  | 4.59 | [8 empty] | 22.30 |  |  |  |  | 1.29
2018 |  |  |  | 4408.98 |  |  | 5680 |  |  |  | 820 | [10 empty] | 61.25 |  |  |  | 62.29 | [5 empty] | 61.38 |  |  | 64.84 |  |  |  | 5.45 |  | 3.59 | [8 empty] | 34.12 |  |  |  |  | 1.04
2019 |  |  |  | 4909.25 |  |  | 6196 |  |  |  | 820 | [10 empty] | 68.26 |  |  |  | 69.65 | [5 empty] | 68.34 |  |  | 70.73 |  |  |  | 3.35 |  | 4.61 | [8 empty] | 25.74 |  |  |  |  | 1.39
2020 |  |  |  | 5934.14 |  |  | 7373 |  |  |  | 820 | [10 empty] | 81.92 |  |  |  | 82.98 | [5 empty] | 82.39 |  |  | 83.94 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 16.64 |  |  |  |  | 1.06
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 202
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1411 | [14 empty] | 1947
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 101
Subtotal | [22 empty] | 1411 | [14 empty] | 2048 |  |  |  | 202
Total | [22 empty] | 1411 | [14 empty] | 2250
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2016 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 38
14. |  |  | Safety Systems | [34 empty] | 15
31. |  |  | Turbine and auxiliaries | [34 empty] | 59
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
41. |  |  | Main Generator Systems | [34 empty] | 46
Total | [37 empty] | 168
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the overhoul outage from 2020.01.01 to 2020.01.25 and routine maintenance outage from 2020.07.01 to 2020.08.06. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BILIBINO-2
2020 Operating Experience
RU-142 | [8 empty] | BILIBINO-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / EGP-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-01-01
Thermal power | [12 empty] | : |  |  | 62 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-12-30
Gross electrical power | [12 empty] | : |  |  | 12 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-02-01
Reference unit power (net) | [12 empty] | : |  |  | 11 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 280
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 3000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 273 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 32.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.4 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.4 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.6 %
Load Factor (LF) | [18 empty] | : | 33.55 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 73.19 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2355 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 13.54 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 4.49 | 3.79 |  |  |  | 2.75 |  | 3.50 | [8 empty] | 3.83 |  |  | 3.20 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.76 |  |  | 3.55 |  |  | 2.82 | [9 empty] | 3.72 |  |  | 32.42
EAF [%] |  |  |  |  | 99.69 | 100.00 |  |  |  | 63.48 |  | 85.24 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 4.64 |  | 4.55 |  |  |  | 38.81 |  |  | 100.00 |  |  | 98.85 | [9 empty] | 100.00 |  |  | 74.40
UCF [%] |  |  |  |  | 99.69 | 100.00 |  |  |  | 63.48 |  | 85.24 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 4.64 |  | 4.55 |  |  |  | 38.81 |  |  | 100.00 |  |  | 98.85 | [9 empty] | 100.00 |  |  | 74.40
LF [%] |  |  |  |  | 54.89 | 49.57 |  |  |  | 33.59 |  | 44.23 | [8 empty] | 46.77 |  |  | 40.45 | [6 empty] | 0.04 |  | 0.00 |  |  |  | 9.56 |  |  | 43.37 |  |  | 35.61 | [9 empty] | 45.44 |  |  | 33.55
OF [%] |  |  |  |  | 99.73 | 100.00 |  |  |  | 61.69 |  | 84.58 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 0.13 |  | 0.00 |  |  |  | 35.97 |  |  | 100.00 |  |  | 98.75 | [9 empty] | 100.00 |  |  | 73.19
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.31 | 0.00 |  |  |  | 36.52 |  | 14.76 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 95.36 |  | 95.45 |  |  |  | 61.19 |  |  | 0.00 |  |  | 1.15 | [9 empty] | 0.00 |  |  | 25.60
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 2246.46 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.85 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.68 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.54 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.55 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.92 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 52.28 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 8.87 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.38 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 63.76 |  |  | 7365 |  |  |  | 10 | [10 empty] | 88.97 |  |  |  | 94.67 | [5 empty] | 78.14 |  |  | 90.14 |  |  |  | 1.31 |  | 1.26 | [8 empty] | 4.07 |  |  |  |  | 5.70
1976 |  |  |  | 66.10 |  |  | 7901 |  |  |  | 10 | [10 empty] | 83.67 |  |  |  | 89.44 | [5 empty] | 75.25 |  |  | 89.95 |  |  |  | 1.10 |  | 0.99 | [8 empty] | 9.56 |  |  |  |  | 5.77
1977 |  |  |  | 57.04 |  |  | 7865 |  |  |  | 10 | [10 empty] | 81.34 |  |  |  | 90.50 | [5 empty] | 65.12 |  |  | 89.78 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 9.46 |  |  |  |  | 9.16
1978 |  |  |  | 60.61 |  |  | 7929 |  |  |  | 10 | [10 empty] | 94.81 |  |  |  | 94.81 | [5 empty] | 69.19 |  |  | 90.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.19 |  |  |  |  | 0.00
1979 |  |  |  | 69.85 |  |  | 8170 |  |  |  | 10 | [10 empty] | 88.17 |  |  |  | 92.93 | [5 empty] | 79.74 |  |  | 93.26 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 7.00 |  |  |  |  | 4.76
1980 |  |  |  | 44.05 |  |  | 5666 |  |  |  | 10 | [10 empty] | 59.82 |  |  |  | 62.73 | [5 empty] | 50.15 |  |  | 64.50 |  |  |  | 35.24 |  | 34.13 | [8 empty] | 3.14 |  |  |  |  | 2.91
1981 |  |  |  | 41.36 |  |  | 6520 |  |  |  | 10 | [10 empty] | 70.39 |  |  |  | 73.15 | [5 empty] | 47.21 |  |  | 74.43 |  |  |  | 4.87 |  | 3.74 | [8 empty] | 23.11 |  |  |  |  | 2.76
1982 |  |  |  | 63.92 |  |  | 7028 |  |  |  | 10 | [10 empty] | 79.24 |  |  |  | 79.24 | [5 empty] | 72.97 |  |  | 80.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.76 |  |  |  |  | 0.00
1983 |  |  |  | 73.76 |  |  | 7880 |  |  |  | 10 | [10 empty] | 86.92 |  |  |  | 90.06 | [5 empty] | 84.20 |  |  | 89.95 |  |  |  | 1.96 |  | 1.80 | [8 empty] | 8.14 |  |  |  |  | 3.14
1984 |  |  |  | 77.63 |  |  | 7891 |  |  |  | 10 | [10 empty] | 88.51 |  |  |  | 89.32 | [5 empty] | 88.38 |  |  | 89.83 |  |  |  | 0.29 |  | 0.26 | [8 empty] | 10.41 |  |  |  |  | 0.81
1985 |  |  |  | 78.00 |  |  | 7940 |  |  |  | 10 | [10 empty] | 88.57 |  |  |  | 90.29 | [5 empty] | 89.04 |  |  | 90.64 |  |  |  | 0.46 |  | 0.42 | [8 empty] | 9.29 |  |  |  |  | 1.73
1986 |  |  |  | 76.34 |  |  | 7679 |  |  |  | 10 | [10 empty] | 84.69 |  |  |  | 87.04 | [5 empty] | 87.14 |  |  | 87.66 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 12.93 |  |  |  |  | 2.35
1987 |  |  |  | 88.42 |  |  | 7794 |  |  |  | 12 | [10 empty] | 89.10 |  |  |  | 89.10 | [5 empty] | 84.12 |  |  | 88.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.90 |  |  |  |  | 0.00
1988 |  |  |  | 75.07 |  |  | 7927 |  |  |  | 11 | [10 empty] | 90.84 |  |  |  | 90.84 | [5 empty] | 77.69 |  |  | 90.24 |  |  |  | 0.64 |  | 0.58 | [8 empty] | 8.57 |  |  |  |  | 0.00
1989 |  |  |  | 74.81 |  |  | 7943 |  |  |  | 11 | [10 empty] | 91.38 |  |  |  | 91.38 | [5 empty] | 77.64 |  |  | 90.67 |  |  |  | 0.34 |  | 0.31 | [8 empty] | 8.31 |  |  |  |  | 0.00
1990 |  |  |  | 72.62 |  |  | 7274 |  |  |  | 11 | [10 empty] | 84.57 |  |  |  | 84.57 | [5 empty] | 75.36 |  |  | 83.04 |  |  |  | 3.23 |  | 2.83 | [8 empty] | 12.61 |  |  |  |  | 0.00
1991 |  |  |  | 57.83 |  |  | 4821 |  |  |  | 11 | [10 empty] | 64.92 |  |  |  | 64.92 | [5 empty] | 60.02 |  |  | 55.03 |  |  |  | 20.10 |  | 16.33 | [8 empty] | 18.74 |  |  |  |  | 0.00
1992 |  |  |  | 68.24 |  |  | 7857 |  |  |  | 11 | [10 empty] | 89.91 |  |  |  | 89.91 | [5 empty] | 70.63 |  |  | 89.45 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 9.99 |  |  |  |  | 0.00
1993 |  |  |  | 52.45 |  |  | 7072 |  |  |  | 11 | [10 empty] | 62.17 |  |  |  | 81.86 | [5 empty] | 54.43 |  |  | 80.73 |  |  |  | 1.69 |  | 1.41 | [8 empty] | 16.73 |  |  |  |  | 19.69
1994 |  |  |  | 47.83 |  |  | 6763 |  |  |  | 11 | [10 empty] | 77.31 |  |  |  | 78.74 | [5 empty] | 49.64 |  |  | 77.20 |  |  |  | 2.81 |  | 2.28 | [8 empty] | 18.98 |  |  |  |  | 1.43
1995 |  |  |  | 45.45 |  |  | 8677 |  |  |  | 11 | [10 empty] | 97.19 |  |  |  | 99.19 | [5 empty] | 47.16 |  |  | 99.05 |  |  |  | 0.69 |  | 0.69 | [8 empty] | 0.12 |  |  |  |  | 2.00
1996 |  |  |  | 16.83 |  |  | 2894 |  |  |  | 11 | [10 empty] | 33.47 |  |  |  | 33.47 | [5 empty] | 17.42 |  |  | 32.95 |  |  |  | 2.84 |  | 0.98 | [8 empty] | 65.55 |  |  |  |  | 0.00
1997 |  |  |  | 44.11 |  |  | 8050 |  |  |  | 11 | [10 empty] | 87.71 |  |  |  | 92.70 | [5 empty] | 45.78 |  |  | 91.89 |  |  |  | 0.36 |  | 0.34 | [8 empty] | 6.97 |  |  |  |  | 4.99
1998 |  |  |  | 18.16 |  |  | 3727 |  |  |  | 11 | [10 empty] | 23.30 |  |  |  | 42.91 | [5 empty] | 18.85 |  |  | 42.55 |  |  |  | 0.07 |  | 0.03 | [8 empty] | 57.06 |  |  |  |  | 19.61
1999 |  |  |  | 54.16 |  |  | 7355 |  |  |  | 11 | [10 empty] | 64.09 |  |  |  | 84.73 | [5 empty] | 56.21 |  |  | 83.96 |  |  |  | 0.45 |  | 0.39 | [8 empty] | 14.88 |  |  |  |  | 20.64
2000 |  |  |  | 48.46 |  |  | 6656 |  |  |  | 11 | [10 empty] | 56.35 |  |  |  | 78.15 | [5 empty] | 50.15 |  |  | 75.77 |  |  |  | 0.22 |  | 0.17 | [8 empty] | 21.68 |  |  |  |  | 21.80
2001 |  |  |  | 56.71 |  |  | 7439 |  |  |  | 11 | [10 empty] | 65.81 |  |  |  | 85.23 | [5 empty] | 58.86 |  |  | 84.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.77 |  |  |  |  | 19.42
2002 |  |  |  | 30.02 |  |  | 5744 |  |  |  | 11 | [10 empty] | 38.39 |  |  |  | 66.40 | [5 empty] | 31.16 |  |  | 65.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.60 |  |  |  |  | 28.01
2003 |  |  |  | 33.25 |  |  | 7162 |  |  |  | 11 | [10 empty] | 44.48 |  |  |  | 82.22 | [5 empty] | 34.51 |  |  | 81.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.78 |  |  |  |  | 37.74
2004 |  |  |  | 17.92 |  |  | 5851 |  |  |  | 11 | [10 empty] | 27.23 |  |  |  | 70.29 | [5 empty] | 18.55 |  |  | 66.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.71 |  |  |  |  | 43.05
2005 |  |  |  | 25.33 |  |  | 7351 |  |  |  | 11 | [10 empty] | 38.19 |  |  |  | 84.94 | [5 empty] | 26.29 |  |  | 83.92 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 15.03 |  |  |  |  | 46.76
2006 |  |  |  | 20.34 |  |  | 7248 |  |  |  | 11 | [10 empty] | 32.71 |  |  |  | 84.22 | [5 empty] | 21.11 |  |  | 82.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.78 |  |  |  |  | 51.52
2007 |  |  |  | 26.38 |  |  | 7478 |  |  |  | 11 | [10 empty] | 39.89 |  |  |  | 86.70 | [5 empty] | 27.37 |  |  | 85.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.30 |  |  |  |  | 46.80
2008 |  |  |  | 30.27 |  |  | 6490 |  |  |  | 11 | [10 empty] | 78.78 |  |  |  | 78.78 | [5 empty] | 31.33 |  |  | 73.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.22 |  |  |  |  | 0.00
2009 |  |  |  | 42.44 |  |  | 7388 |  |  |  | 11 | [10 empty] | 86.12 |  |  |  | 86.12 | [5 empty] | 44.04 |  |  | 84.34 |  |  |  | 0.89 |  | 0.78 | [8 empty] | 13.10 |  |  |  |  | 0.00
2010 |  |  |  | 48.08 |  |  | 7627 |  |  |  | 11 | [10 empty] | 88.09 |  |  |  | 88.09 | [5 empty] | 49.89 |  |  | 87.07 |  |  |  | 0.75 |  | 0.66 | [8 empty] | 11.25 |  |  |  |  | 0.00
2011 |  |  |  | 21.71 |  |  | 4977 |  |  |  | 11 | [10 empty] | 84.38 |  |  |  | 84.38 | [5 empty] | 22.53 |  |  | 56.82 |  |  |  | 1.45 |  | 1.24 | [8 empty] | 14.38 |  |  |  |  | 0.00
2012 |  |  |  | 28.27 |  |  | 5461 |  |  |  | 11 | [10 empty] | 72.73 |  |  |  | 72.73 | [5 empty] | 29.26 |  |  | 62.17 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 27.24 |  |  |  |  | 0.00
2013 |  |  |  | 43.12 |  |  | 6904 |  |  |  | 11 | [10 empty] | 85.84 |  |  |  | 85.84 | [5 empty] | 44.75 |  |  | 78.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.16 |  |  |  |  | 0.00
2014 |  |  |  | 40.96 |  |  | 6457 |  |  |  | 11 | [10 empty] | 84.92 |  |  |  | 84.92 | [5 empty] | 42.51 |  |  | 73.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.08 |  |  |  |  | 0.00
2015 |  |  |  | 39.78 |  |  | 6331 |  |  |  | 11 | [10 empty] | 73.73 |  |  |  | 73.73 | [5 empty] | 41.28 |  |  | 72.27 |  |  |  | 0.44 |  | 0.32 | [8 empty] | 25.95 |  |  |  |  | 0.00
2016 |  |  |  | 35.79 |  |  | 6506 |  |  |  | 11 | [10 empty] | 75.88 |  |  |  | 75.88 | [5 empty] | 37.04 |  |  | 74.07 |  |  |  | 0.86 |  | 0.66 | [8 empty] | 23.46 |  |  |  |  | 0.00
2017 |  |  |  | 44.31 |  |  | 7393 |  |  |  | 11 | [10 empty] | 85.12 |  |  |  | 85.12 | [5 empty] | 45.98 |  |  | 84.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.88 |  |  |  |  | 0.00
2018 |  |  |  | 54.16 |  |  | 7383 |  |  |  | 11 | [10 empty] | 84.99 |  |  |  | 84.99 | [5 empty] | 56.20 |  |  | 84.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.01 |  |  |  |  | 0.00
2019 |  |  |  | 57.78 |  |  | 7398 |  |  |  | 11 | [10 empty] | 85.16 |  |  |  | 85.16 | [5 empty] | 59.97 |  |  | 84.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.84 |  |  |  |  | 0.00
2020 |  |  |  | 32.42 |  |  | 6429 |  |  |  | 11 | [10 empty] | 74.40 |  |  |  | 74.40 | [5 empty] | 33.55 |  |  | 73.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.60 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 107
B. |  | Refuelling without maintenance | [20 empty] | 396 | [14 empty] | 9
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1949 | [14 empty] | 1423 |  |  |  | 65
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 104
E. |  | Testing of plant systems or components | [20 empty] | 11 | [14 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 13
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 109
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [35 empty] | 5
Subtotal | [22 empty] | 2356 | [14 empty] | 1548 |  |  |  | 177 | [11 empty] | 122
Total | [22 empty] | 2356 | [14 empty] | 1847
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 55
12. |  |  | Reactor I&C Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 4
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 6
Total | [37 empty] | 108
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the routine maintenance outage from 2020.03.20 to 2020.04.05 and in the in the overhoul outage from 2020.07.01 to 2020.09.20. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BILIBINO-3
2020 Operating Experience
RU-143 | [8 empty] | BILIBINO-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / EGP-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-01-01
Thermal power | [12 empty] | : |  |  | 62 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-12-22
Gross electrical power | [12 empty] | : |  |  | 12 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-02-01
Reference unit power (net) | [12 empty] | : |  |  | 11 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 280
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 3000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 273 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 38 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.21 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.73 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.18 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.73 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.09 %
Load Factor (LF) | [18 empty] | : | 39.33 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 84.02 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1404 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 24.02 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 3.68 | 3.42 |  |  |  | 4.53 |  | 4.58 | [8 empty] | 3.83 |  |  | 3.98 | [6 empty] | 3.61 |  | 3.55 |  |  |  | 2.92 |  |  | 0.00 |  |  | 0.39 | [9 empty] | 3.49 |  |  | 38.00
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.65 |  | 100.00 | [8 empty] | 97.90 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 81.00 |  |  | 4.55 |  |  | 33.94 | [9 empty] | 100.00 |  |  | 84.73
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.65 |  | 100.00 | [8 empty] | 97.90 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 81.00 |  |  | 4.55 |  |  | 33.94 | [9 empty] | 100.00 |  |  | 84.73
LF [%] |  |  |  |  | 44.99 | 44.70 |  |  |  | 55.40 |  | 57.89 | [8 empty] | 46.79 |  |  | 50.25 | [6 empty] | 44.15 |  | 43.37 |  |  |  | 36.87 |  |  | 0.00 |  |  | 4.97 | [9 empty] | 42.64 |  |  | 39.33
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.60 |  | 100.00 | [8 empty] | 97.85 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 80.14 |  |  | 0.00 |  |  | 30.83 | [9 empty] | 100.00 |  |  | 84.02
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.10 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.21
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.10 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.18
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.35 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 19.00 |  |  | 95.45 |  |  | 66.06 | [9 empty] | 0.00 |  |  | 15.09
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 2293.18 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.64 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.05 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.97 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.5 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 54.49 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 8.93 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.29 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | 51.20 |  |  | 6655 |  |  |  | 10 | [10 empty] | 83.33 |  |  |  | 90.55 | [5 empty] | 62.19 |  |  | 77.39 |  |  |  | 2.85 |  | 2.65 | [8 empty] | 6.80 |  |  |  |  | 7.21
1977 |  |  |  | 46.50 |  |  | 7533 |  |  |  | 10 | [10 empty] | 78.21 |  |  |  | 92.83 | [5 empty] | 53.08 |  |  | 85.99 |  |  |  | 0.39 |  | 0.36 | [8 empty] | 6.81 |  |  |  |  | 14.62
1978 |  |  |  | 61.86 |  |  | 7514 |  |  |  | 10 | [10 empty] | 86.25 |  |  |  | 86.25 | [5 empty] | 70.61 |  |  | 85.78 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 13.74 |  |  |  |  | 0.00
1979 |  |  |  | 62.12 |  |  | 7837 |  |  |  | 10 | [10 empty] | 82.45 |  |  |  | 88.94 | [5 empty] | 70.92 |  |  | 89.46 |  |  |  | 0.16 |  | 0.14 | [8 empty] | 10.92 |  |  |  |  | 6.49
1980 |  |  |  | 79.43 |  |  | 8130 |  |  |  | 10 | [10 empty] | 90.99 |  |  |  | 92.18 | [5 empty] | 90.42 |  |  | 92.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.82 |  |  |  |  | 1.20
1981 |  |  |  | 89.78 |  |  | 8480 |  |  |  | 10 | [10 empty] | 96.64 |  |  |  | 96.64 | [5 empty] | 102.49 |  |  | 96.80 |  |  |  | 0.13 |  | 0.12 | [8 empty] | 3.24 |  |  |  |  | 0.00
1982 |  |  |  | 79.34 |  |  | 8323 |  |  |  | 10 | [10 empty] | 94.83 |  |  |  | 94.83 | [5 empty] | 90.57 |  |  | 95.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.17 |  |  |  |  | 0.00
1983 |  |  |  | 72.81 |  |  | 7782 |  |  |  | 10 | [10 empty] | 85.31 |  |  |  | 88.85 | [5 empty] | 83.11 |  |  | 88.84 |  |  |  | 0.34 |  | 0.31 | [8 empty] | 10.85 |  |  |  |  | 3.54
1984 |  |  |  | 76.48 |  |  | 7876 |  |  |  | 10 | [10 empty] | 87.36 |  |  |  | 89.14 | [5 empty] | 87.07 |  |  | 89.66 |  |  |  | 0.48 |  | 0.43 | [8 empty] | 10.42 |  |  |  |  | 1.79
1985 |  |  |  | 69.83 |  |  | 7119 |  |  |  | 10 | [10 empty] | 78.48 |  |  |  | 80.33 | [5 empty] | 79.72 |  |  | 81.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.67 |  |  |  |  | 1.85
1986 |  |  |  | 77.11 |  |  | 8001 |  |  |  | 10 | [10 empty] | 87.71 |  |  |  | 91.02 | [5 empty] | 88.03 |  |  | 91.34 |  |  |  | 0.66 |  | 0.60 | [8 empty] | 8.38 |  |  |  |  | 3.31
1987 |  |  |  | 89.09 |  |  | 7801 |  |  |  | 12 | [10 empty] | 89.09 |  |  |  | 89.09 | [5 empty] | 84.75 |  |  | 89.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.91 |  |  |  |  | 0.00
1988 |  |  |  | 76.71 |  |  | 7815 |  |  |  | 11 | [10 empty] | 89.47 |  |  |  | 89.47 | [5 empty] | 79.39 |  |  | 88.97 |  |  |  | 0.57 |  | 0.51 | [8 empty] | 10.02 |  |  |  |  | 0.00
1989 |  |  |  | 74.26 |  |  | 7756 |  |  |  | 11 | [10 empty] | 89.05 |  |  |  | 89.46 | [5 empty] | 77.06 |  |  | 88.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.54 |  |  |  |  | 0.40
1990 |  |  |  | 73.74 |  |  | 8024 |  |  |  | 11 | [10 empty] | 91.12 |  |  |  | 91.98 | [5 empty] | 76.53 |  |  | 91.60 |  |  |  | 6.83 |  | 6.75 | [8 empty] | 1.28 |  |  |  |  | 0.86
1991 |  |  |  | 66.19 |  |  | 6749 |  |  |  | 11 | [10 empty] | 76.59 |  |  |  | 78.08 | [5 empty] | 68.69 |  |  | 77.04 |  |  |  | 1.34 |  | 1.06 | [8 empty] | 20.86 |  |  |  |  | 1.50
1992 |  |  |  | 70.92 |  |  | 7727 |  |  |  | 11 | [10 empty] | 79.70 |  |  |  | 79.70 | [5 empty] | 73.40 |  |  | 87.97 |  |  |  | 0.40 |  | 0.32 | [8 empty] | 19.98 |  |  |  |  | 0.00
1993 |  |  |  | 52.59 |  |  | 7218 |  |  |  | 11 | [10 empty] | 61.50 |  |  |  | 83.21 | [5 empty] | 54.58 |  |  | 82.40 |  |  |  | 0.16 |  | 0.13 | [8 empty] | 16.66 |  |  |  |  | 21.71
1994 |  |  |  | 44.71 |  |  | 6342 |  |  |  | 11 | [10 empty] | 71.96 |  |  |  | 73.69 | [5 empty] | 46.39 |  |  | 72.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.31 |  |  |  |  | 1.73
1995 |  |  |  | 17.30 |  |  | 3293 |  |  |  | 11 | [10 empty] | 34.90 |  |  |  | 38.15 | [5 empty] | 17.95 |  |  | 37.59 |  |  |  | 9.46 |  | 3.99 | [8 empty] | 57.86 |  |  |  |  | 3.26
1996 |  |  |  | 52.62 |  |  | 7142 |  |  |  | 11 | [10 empty] | 82.27 |  |  |  | 82.27 | [5 empty] | 54.46 |  |  | 81.31 |  |  |  | 6.51 |  | 5.73 | [8 empty] | 12.00 |  |  |  |  | 0.00
1997 |  |  |  | 25.83 |  |  | 3769 |  |  |  | 11 | [10 empty] | 42.86 |  |  |  | 42.86 | [5 empty] | 26.80 |  |  | 43.03 |  |  |  | 0.86 |  | 0.37 | [8 empty] | 56.77 |  |  |  |  | 0.00
1998 |  |  |  | 23.16 |  |  | 4200 |  |  |  | 11 | [10 empty] | 29.11 |  |  |  | 49.13 | [5 empty] | 24.04 |  |  | 47.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 50.87 |  |  |  |  | 20.02
1999 |  |  |  | 51.44 |  |  | 6607 |  |  |  | 11 | [10 empty] | 59.91 |  |  |  | 75.85 | [5 empty] | 53.38 |  |  | 75.42 |  |  |  | 0.12 |  | 0.09 | [8 empty] | 24.06 |  |  |  |  | 15.94
2000 |  |  |  | 45.23 |  |  | 7569 |  |  |  | 11 | [10 empty] | 54.84 |  |  |  | 86.83 | [5 empty] | 46.81 |  |  | 86.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.17 |  |  |  |  | 31.99
2001 |  |  |  | 53.94 |  |  | 7383 |  |  |  | 11 | [10 empty] | 62.96 |  |  |  | 84.88 | [5 empty] | 55.98 |  |  | 84.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.12 |  |  |  |  | 21.91
2002 |  |  |  | 30.73 |  |  | 6250 |  |  |  | 11 | [10 empty] | 39.39 |  |  |  | 71.50 | [5 empty] | 31.90 |  |  | 71.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.50 |  |  |  |  | 32.11
2003 |  |  |  | 35.42 |  |  | 7097 |  |  |  | 11 | [10 empty] | 46.72 |  |  |  | 81.51 | [5 empty] | 36.75 |  |  | 81.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.49 |  |  |  |  | 34.79
2004 |  |  |  | 31.09 |  |  | 7166 |  |  |  | 11 | [10 empty] | 42.00 |  |  |  | 85.77 | [5 empty] | 32.18 |  |  | 81.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.23 |  |  |  |  | 43.77
2005 |  |  |  | 20.37 |  |  | 6102 |  |  |  | 11 | [10 empty] | 30.86 |  |  |  | 71.09 | [5 empty] | 21.14 |  |  | 69.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.91 |  |  |  |  | 40.23
2006 |  |  |  | 26.25 |  |  | 6542 |  |  |  | 11 | [10 empty] | 36.94 |  |  |  | 76.74 | [5 empty] | 27.24 |  |  | 74.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.26 |  |  |  |  | 39.80
2007 |  |  |  | 27.45 |  |  | 7257 |  |  |  | 11 | [10 empty] | 38.64 |  |  |  | 85.73 | [5 empty] | 28.49 |  |  | 82.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.27 |  |  |  |  | 47.09
2008 |  |  |  | 33.28 |  |  | 7335 |  |  |  | 11 | [10 empty] | 85.73 |  |  |  | 85.73 | [5 empty] | 34.44 |  |  | 83.50 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 14.20 |  |  |  |  | 0.00
2009 |  |  |  | 44.57 |  |  | 7972 |  |  |  | 11 | [10 empty] | 91.43 |  |  |  | 91.43 | [5 empty] | 46.25 |  |  | 91.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.57 |  |  |  |  | 0.00
2010 |  |  |  | 33.69 |  |  | 6035 |  |  |  | 11 | [10 empty] | 77.50 |  |  |  | 77.50 | [5 empty] | 34.96 |  |  | 68.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.50 |  |  |  |  | 0.00
2011 |  |  |  | 22.19 |  |  | 4885 |  |  |  | 11 | [10 empty] | 87.96 |  |  |  | 87.96 | [5 empty] | 23.03 |  |  | 55.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.04 |  |  |  |  | 0.00
2012 |  |  |  | 34.63 |  |  | 7253 |  |  |  | 11 | [10 empty] | 86.71 |  |  |  | 86.71 | [5 empty] | 35.84 |  |  | 82.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.29 |  |  |  |  | 0.00
2013 |  |  |  | 43.85 |  |  | 7436 |  |  |  | 11 | [10 empty] | 85.64 |  |  |  | 85.64 | [5 empty] | 45.51 |  |  | 84.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.36 |  |  |  |  | 0.00
2014 |  |  |  | 45.10 |  |  | 6615 |  |  |  | 11 | [10 empty] | 76.67 |  |  |  | 76.67 | [5 empty] | 46.80 |  |  | 75.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.33 |  |  |  |  | 0.00
2015 |  |  |  | 51.64 |  |  | 7337 |  |  |  | 11 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 53.60 |  |  | 83.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.90 |  |  |  |  | 0.00
2016 |  |  |  | 49.20 |  |  | 7410 |  |  |  | 11 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 50.92 |  |  | 84.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.90 |  |  |  |  | 0.00
2017 |  |  |  | 50.50 |  |  | 7377 |  |  |  | 11 | [10 empty] | 84.93 |  |  |  | 84.93 | [5 empty] | 52.41 |  |  | 84.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.07 |  |  |  |  | 0.00
2018 |  |  |  | 48.41 |  |  | 6626 |  |  |  | 11 | [10 empty] | 76.75 |  |  |  | 76.75 | [5 empty] | 50.24 |  |  | 75.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.25 |  |  |  |  | 0.00
2019 |  |  |  | 63.23 |  |  | 7849 |  |  |  | 11 | [10 empty] | 90.08 |  |  |  | 90.08 | [5 empty] | 65.62 |  |  | 89.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.92 |  |  |  |  | 0.00
2020 |  |  |  | 38.00 |  |  | 7380 |  |  |  | 11 | [10 empty] | 84.73 |  |  |  | 84.73 | [5 empty] | 39.33 |  |  | 84.02 |  |  |  | 0.21 |  | 0.18 | [8 empty] | 15.09 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1976 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 17 | [14 empty] | 46
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1386 | [14 empty] | 1308
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 253
E. |  | Testing of plant systems or components | [20 empty] | 3 | [14 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 35
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 98
Z. |  | Other | [35 empty] | 11 |  |  |  | 1
Subtotal | [22 empty] | 1389 |  |  |  | 17 | [10 empty] | 1579 |  |  |  | 47 | [11 empty] | 133
Total | [22 empty] | 1406 | [14 empty] | 1759
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1976 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 13
31. |  |  | Turbine and auxiliaries | [19 empty] | 17 | [14 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 13
Total | [22 empty] | 17 | [14 empty] | 45
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the intermediate outage from 2020.09.25 to 2020.11.21. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BILIBINO-4
2020 Operating Experience
RU-144 | [8 empty] | BILIBINO-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / EGP-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-01-01
Thermal power | [12 empty] | : |  |  | 62 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-12-27
Gross electrical power | [12 empty] | : |  |  | 12 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-01-01
Reference unit power (net) | [12 empty] | : |  |  | 11 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 280
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 3000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 273 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 38.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.72 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.72 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 17.28 %
Load Factor (LF) | [18 empty] | : | 39.39 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 81.9 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1590 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 23.01 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 4.66 | 3.35 |  |  |  | 4.79 |  | 1.39 | [8 empty] | 0.00 |  |  | 2.05 | [6 empty] | 3.03 |  | 3.06 |  |  |  | 4.07 |  |  | 4.42 |  |  | 4.25 | [9 empty] | 2.99 |  |  | 38.06
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 33.37 | [8 empty] | 4.55 |  |  | 56.31 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 98.25 |  |  | 82.72
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 33.37 | [8 empty] | 4.55 |  |  | 56.31 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 98.25 |  |  | 82.72
LF [%] |  |  |  |  | 56.92 | 43.74 |  |  |  | 58.57 |  | 17.59 | [8 empty] | 0.00 |  |  | 25.88 | [6 empty] | 36.97 |  | 37.43 |  |  |  | 51.41 |  |  | 53.98 |  |  | 53.65 | [9 empty] | 36.56 |  |  | 39.39
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 30.14 | [8 empty] | 0.00 |  |  | 54.31 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 98.12 |  |  | 81.90
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 66.63 | [8 empty] | 95.45 |  |  | 43.69 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 1.75 |  |  | 17.28
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 2132.37 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.66 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.59 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.12 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.35 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 52.73 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 8.53 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.97 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 52.65 |  |  | 7392 |  |  |  | 10 | [10 empty] | 82.89 |  |  |  | 93.56 | [5 empty] | 60.10 |  |  | 84.38 |  |  |  | 0.28 |  | 0.27 | [8 empty] | 6.17 |  |  |  |  | 10.67
1978 |  |  |  | 58.30 |  |  | 7827 |  |  |  | 10 | [10 empty] | 91.06 |  |  |  | 91.06 | [5 empty] | 66.55 |  |  | 89.35 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.93 |  |  |  |  | 0.00
1979 |  |  |  | 74.46 |  |  | 7552 |  |  |  | 10 | [10 empty] | 83.88 |  |  |  | 85.52 | [5 empty] | 85.00 |  |  | 86.21 |  |  |  | 0.20 |  | 0.17 | [8 empty] | 14.31 |  |  |  |  | 1.64
1980 |  |  |  | 77.62 |  |  | 8347 |  |  |  | 10 | [10 empty] | 92.91 |  |  |  | 94.77 | [5 empty] | 88.37 |  |  | 95.03 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 5.18 |  |  |  |  | 1.86
1981 |  |  |  | 78.26 |  |  | 7734 |  |  |  | 10 | [10 empty] | 86.61 |  |  |  | 87.69 | [5 empty] | 89.33 |  |  | 88.29 |  |  |  | 0.80 |  | 0.71 | [8 empty] | 11.60 |  |  |  |  | 1.08
1982 |  |  |  | 77.61 |  |  | 7976 |  |  |  | 10 | [10 empty] | 90.71 |  |  |  | 90.71 | [5 empty] | 88.59 |  |  | 91.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.29 |  |  |  |  | 0.00
1983 |  |  |  | 75.53 |  |  | 7923 |  |  |  | 10 | [10 empty] | 86.88 |  |  |  | 89.97 | [5 empty] | 86.23 |  |  | 90.45 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 9.94 |  |  |  |  | 3.09
1984 |  |  |  | 79.01 |  |  | 7744 |  |  |  | 10 | [10 empty] | 86.77 |  |  |  | 87.57 | [5 empty] | 89.95 |  |  | 88.16 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 12.36 |  |  |  |  | 0.80
1985 |  |  |  | 81.23 |  |  | 7919 |  |  |  | 10 | [10 empty] | 89.53 |  |  |  | 90.33 | [5 empty] | 92.73 |  |  | 90.40 |  |  |  | 1.23 |  | 1.13 | [8 empty] | 8.55 |  |  |  |  | 0.79
1986 |  |  |  | 74.54 |  |  | 7083 |  |  |  | 10 | [10 empty] | 79.84 |  |  |  | 79.90 | [5 empty] | 85.09 |  |  | 80.86 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 20.09 |  |  |  |  | 0.06
1987 |  |  |  | 95.55 |  |  | 8154 |  |  |  | 12 | [10 empty] | 93.26 |  |  |  | 93.26 | [5 empty] | 90.89 |  |  | 93.08 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 6.54 |  |  |  |  | 0.00
1988 |  |  |  | 75.85 |  |  | 7617 |  |  |  | 11 | [10 empty] | 87.34 |  |  |  | 87.34 | [5 empty] | 78.50 |  |  | 86.71 |  |  |  | 0.86 |  | 0.76 | [8 empty] | 11.90 |  |  |  |  | 0.00
1989 |  |  |  | 71.37 |  |  | 7853 |  |  |  | 11 | [10 empty] | 93.22 |  |  |  | 93.22 | [5 empty] | 74.06 |  |  | 89.65 |  |  |  | 0.25 |  | 0.24 | [8 empty] | 6.54 |  |  |  |  | 0.00
1990 |  |  |  | 75.29 |  |  | 7588 |  |  |  | 11 | [10 empty] | 86.36 |  |  |  | 87.22 | [5 empty] | 78.13 |  |  | 86.62 |  |  |  | 5.48 |  | 5.06 | [8 empty] | 7.73 |  |  |  |  | 0.86
1991 |  |  |  | 61.32 |  |  | 6139 |  |  |  | 11 | [10 empty] | 69.89 |  |  |  | 71.43 | [5 empty] | 63.64 |  |  | 70.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.57 |  |  |  |  | 1.54
1992 |  |  |  | 69.84 |  |  | 7756 |  |  |  | 11 | [10 empty] | 87.82 |  |  |  | 87.82 | [5 empty] | 72.28 |  |  | 88.30 |  |  |  | 1.22 |  | 1.08 | [8 empty] | 11.10 |  |  |  |  | 0.00
1993 |  |  |  | 56.00 |  |  | 6918 |  |  |  | 11 | [10 empty] | 64.39 |  |  |  | 80.22 | [5 empty] | 58.12 |  |  | 78.97 |  |  |  | 0.82 |  | 0.66 | [8 empty] | 19.11 |  |  |  |  | 15.83
1994 |  |  |  | 38.46 |  |  | 5266 |  |  |  | 11 | [10 empty] | 61.82 |  |  |  | 61.99 | [5 empty] | 39.91 |  |  | 60.11 |  |  |  | 9.18 |  | 6.27 | [8 empty] | 31.75 |  |  |  |  | 0.17
1995 |  |  |  | 29.88 |  |  | 5083 |  |  |  | 11 | [10 empty] | 62.73 |  |  |  | 63.94 | [5 empty] | 31.01 |  |  | 58.03 |  |  |  | 0.53 |  | 0.34 | [8 empty] | 35.72 |  |  |  |  | 1.21
1996 |  |  |  | 35.18 |  |  | 5109 |  |  |  | 11 | [10 empty] | 59.13 |  |  |  | 59.13 | [5 empty] | 36.41 |  |  | 58.16 |  |  |  | 1.36 |  | 0.81 | [8 empty] | 40.06 |  |  |  |  | 0.00
1997 |  |  |  | 15.13 |  |  | 2490 |  |  |  | 11 | [10 empty] | 28.42 |  |  |  | 37.04 | [5 empty] | 15.70 |  |  | 28.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 62.96 |  |  |  |  | 8.61
1998 |  |  |  | 37.29 |  |  | 5510 |  |  |  | 11 | [10 empty] | 44.52 |  |  |  | 63.14 | [5 empty] | 38.70 |  |  | 62.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.86 |  |  |  |  | 18.62
1999 |  |  |  | 28.69 |  |  | 3993 |  |  |  | 11 | [10 empty] | 34.77 |  |  |  | 46.74 | [5 empty] | 29.77 |  |  | 45.58 |  |  |  | 6.39 |  | 3.19 | [8 empty] | 50.07 |  |  |  |  | 11.97
2000 |  |  |  | 55.85 |  |  | 7740 |  |  |  | 11 | [10 empty] | 64.20 |  |  |  | 88.68 | [5 empty] | 57.80 |  |  | 88.11 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 11.29 |  |  |  |  | 24.48
2001 |  |  |  | 35.44 |  |  | 5931 |  |  |  | 11 | [10 empty] | 43.17 |  |  |  | 68.01 | [5 empty] | 36.78 |  |  | 67.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.99 |  |  |  |  | 24.84
2002 |  |  |  | 33.12 |  |  | 6419 |  |  |  | 11 | [10 empty] | 46.34 |  |  |  | 73.76 | [5 empty] | 34.37 |  |  | 73.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.24 |  |  |  |  | 27.42
2003 |  |  |  | 24.52 |  |  | 5849 |  |  |  | 11 | [10 empty] | 34.04 |  |  |  | 67.51 | [5 empty] | 25.45 |  |  | 66.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.49 |  |  |  |  | 33.47
2004 |  |  |  | 26.10 |  |  | 7303 |  |  |  | 11 | [10 empty] | 36.71 |  |  |  | 83.90 | [5 empty] | 27.01 |  |  | 83.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.10 |  |  |  |  | 47.19
2005 |  |  |  | 24.95 |  |  | 7300 |  |  |  | 11 | [10 empty] | 36.29 |  |  |  | 84.32 | [5 empty] | 25.89 |  |  | 83.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.68 |  |  |  |  | 48.03
2006 |  |  |  | 25.22 |  |  | 6626 |  |  |  | 11 | [10 empty] | 36.44 |  |  |  | 76.86 | [5 empty] | 26.18 |  |  | 75.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.14 |  |  |  |  | 40.42
2007 |  |  |  | 19.57 |  |  | 5983 |  |  |  | 11 | [10 empty] | 30.89 |  |  |  | 76.55 | [5 empty] | 20.31 |  |  | 68.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.45 |  |  |  |  | 45.65
2008 |  |  |  | 29.55 |  |  | 7023 |  |  |  | 11 | [10 empty] | 87.66 |  |  |  | 87.66 | [5 empty] | 30.59 |  |  | 79.95 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 12.25 |  |  |  |  | 0.00
2009 |  |  |  | 42.14 |  |  | 7663 |  |  |  | 11 | [10 empty] | 88.40 |  |  |  | 88.40 | [5 empty] | 43.74 |  |  | 87.48 |  |  |  | 0.14 |  | 0.12 | [8 empty] | 11.48 |  |  |  |  | 0.00
2010 |  |  |  | 37.48 |  |  | 7272 |  |  |  | 11 | [10 empty] | 86.93 |  |  |  | 86.93 | [5 empty] | 38.90 |  |  | 83.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.07 |  |  |  |  | 0.00
2011 |  |  |  | 32.79 |  |  | 5944 |  |  |  | 11 | [10 empty] | 77.29 |  |  |  | 77.29 | [5 empty] | 34.03 |  |  | 67.85 |  |  |  | 0.21 |  | 0.16 | [8 empty] | 22.55 |  |  |  |  | 0.00
2012 |  |  |  | 24.50 |  |  | 5886 |  |  |  | 11 | [10 empty] | 86.69 |  |  |  | 86.69 | [5 empty] | 25.36 |  |  | 67.01 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 13.28 |  |  |  |  | 0.00
2013 |  |  |  | 45.48 |  |  | 7472 |  |  |  | 11 | [10 empty] | 87.40 |  |  |  | 87.40 | [5 empty] | 47.19 |  |  | 85.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.60 |  |  |  |  | 0.00
2014 |  |  |  | 45.89 |  |  | 7187 |  |  |  | 11 | [10 empty] | 84.56 |  |  |  | 84.56 | [5 empty] | 47.63 |  |  | 82.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.44 |  |  |  |  | 0.00
2015 |  |  |  | 40.59 |  |  | 6307 |  |  |  | 11 | [10 empty] | 76.02 |  |  |  | 76.02 | [5 empty] | 42.12 |  |  | 72.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.98 |  |  |  |  | 0.00
2016 |  |  |  | 43.53 |  |  | 7163 |  |  |  | 11 | [10 empty] | 83.57 |  |  |  | 83.57 | [5 empty] | 45.05 |  |  | 81.55 |  |  |  | 1.87 |  | 1.59 | [8 empty] | 14.84 |  |  |  |  | 0.00
2017 |  |  |  | 46.22 |  |  | 7395 |  |  |  | 11 | [10 empty] | 85.13 |  |  |  | 85.13 | [5 empty] | 47.97 |  |  | 84.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.87 |  |  |  |  | 0.00
2018 |  |  |  | 54.77 |  |  | 7392 |  |  |  | 11 | [10 empty] | 85.09 |  |  |  | 85.09 | [5 empty] | 56.84 |  |  | 84.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.91 |  |  |  |  | 0.00
2019 |  |  |  | 50.73 |  |  | 6705 |  |  |  | 11 | [10 empty] | 77.60 |  |  |  | 77.60 | [5 empty] | 52.65 |  |  | 76.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.40 |  |  |  |  | 0.00
2020 |  |  |  | 38.06 |  |  | 7194 |  |  |  | 11 | [10 empty] | 82.72 |  |  |  | 82.72 | [5 empty] | 39.39 |  |  | 81.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.28 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1977 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 50
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1576 | [14 empty] | 1448
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 319
E. |  | Testing of plant systems or components | [20 empty] | 14 | [14 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 44
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 106
L. |  | Human factor related | [39 empty] | 0
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 1590 | [14 empty] | 1774 |  |  |  | 51 | [11 empty] | 150
Total | [22 empty] | 1590 | [14 empty] | 1975
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1977 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 13
Total | [37 empty] | 49
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the intermediate outage from 2020.04.10 to 2020.06.14. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-1
2020 Operating Experience
RU-30 | [8 empty] | KALININ-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-338 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-02-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-05-09
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-06-12
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2709.37 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.41 %
Energy Availability Factor (EAF) | [18 empty] | : | 30.56 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.41 %
Unit Capability Factor (UCF) | [18 empty] | : | 30.56 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 68.03 %
Load Factor (LF) | [18 empty] | : | 32.47 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 30.77 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 6081 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 5.54 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 521.73 |  |  | 696.33 |  |  | 726.89 | [9 empty] | 764.42 |  |  | 2709.37
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 73.01 |  |  | 93.41 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 30.56
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 73.01 |  |  | 93.41 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 30.56
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 76.28 |  |  | 98.52 |  |  | 106.27 | [9 empty] | 108.15 |  |  | 32.47
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 75.28 |  |  | 93.68 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 30.77
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 12.44 |  |  | 6.59 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.41
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 10.37 |  |  | 6.59 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.41
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 16.62 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 68.03
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 227893.23 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.76 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.77 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.48 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.94 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.68 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.85 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4487.64 |  |  | 5824 |  |  |  | 950 | [10 empty] | 58.28 |  |  |  | 58.28 | [5 empty] | 57.38 |  |  | 60.38 |  |  |  | 10.99 |  | 7.20 | [8 empty] | 34.52 |  |  |  |  | 0.00
1986 |  |  |  | 5297.73 |  |  | 5946 |  |  |  | 950 | [10 empty] | 62.85 |  |  |  | 62.85 | [5 empty] | 63.66 |  |  | 67.88 |  |  |  | 28.18 |  | 24.65 | [8 empty] | 12.50 |  |  |  |  | 0.00
1987 |  |  |  | 6842.49 |  |  | 6972 |  |  |  | 1000 | [10 empty] | 78.71 |  |  |  | 78.71 | [5 empty] | 78.11 |  |  | 79.59 |  |  |  | 7.76 |  | 6.62 | [8 empty] | 14.67 |  |  |  |  | 0.00
1988 |  |  |  | 5891.61 |  |  | 6187 |  |  |  | 950 | [10 empty] | 70.12 |  |  |  | 70.12 | [5 empty] | 70.60 |  |  | 70.43 |  |  |  | 9.61 |  | 7.45 | [8 empty] | 22.43 |  |  |  |  | 0.00
1989 |  |  |  | 6129.71 |  |  | 6396 |  |  |  | 950 | [10 empty] | 71.91 |  |  |  | 71.94 | [5 empty] | 73.66 |  |  | 73.01 |  |  |  | 10.20 |  | 8.17 | [8 empty] | 19.89 |  |  |  |  | 0.03
1990 |  |  |  | 5192.31 |  |  | 5435 |  |  |  | 950 | [10 empty] | 61.53 |  |  |  | 61.56 | [5 empty] | 62.39 |  |  | 62.04 |  |  |  | 3.54 |  | 2.26 | [8 empty] | 36.18 |  |  |  |  | 0.03
1991 |  |  |  | 6482.72 |  |  | 7161 |  |  |  | 950 | [10 empty] | 77.09 |  |  |  | 78.06 | [5 empty] | 77.90 |  |  | 81.75 |  |  |  | 11.66 |  | 10.30 | [8 empty] | 11.64 |  |  |  |  | 0.97
1992 |  |  |  | 6781.35 |  |  | 7388 |  |  |  | 950 | [10 empty] | 80.33 |  |  |  | 80.36 | [5 empty] | 81.27 |  |  | 84.12 |  |  |  | 12.02 |  | 10.98 | [8 empty] | 8.66 |  |  |  |  | 0.03
1993 |  |  |  | 4927.21 |  |  | 6133 |  |  |  | 950 | [10 empty] | 59.38 |  |  |  | 66.61 | [5 empty] | 59.21 |  |  | 70.01 |  |  |  | 5.55 |  | 3.91 | [8 empty] | 29.48 |  |  |  |  | 7.23
1994 |  |  |  | 4437.58 |  |  | 5440 |  |  |  | 950 | [10 empty] | 54.09 |  |  |  | 54.37 | [5 empty] | 53.32 |  |  | 62.10 |  |  |  | 16.02 |  | 10.37 | [8 empty] | 35.26 |  |  |  |  | 0.29
1995 |  |  |  | 4699.05 |  |  | 6265 |  |  |  | 950 | [10 empty] | 56.75 |  |  |  | 57.00 | [5 empty] | 56.47 |  |  | 71.52 |  |  |  | 26.12 |  | 20.15 | [8 empty] | 22.85 |  |  |  |  | 0.25
1996 |  |  |  | 4431.67 |  |  | 5628 |  |  |  | 950 | [10 empty] | 53.22 |  |  |  | 53.31 | [5 empty] | 53.11 |  |  | 64.07 |  |  |  | 19.08 |  | 12.57 | [8 empty] | 34.11 |  |  |  |  | 0.09
1997 |  |  |  | 5197.08 |  |  | 6195 |  |  |  | 950 | [10 empty] | 63.23 |  |  |  | 65.00 | [5 empty] | 62.45 |  |  | 70.72 |  |  |  | 5.59 |  | 3.85 | [8 empty] | 31.16 |  |  |  |  | 1.77
1998 |  |  |  | 6100.97 |  |  | 6937 |  |  |  | 950 | [10 empty] | 73.04 |  |  |  | 73.33 | [5 empty] | 73.31 |  |  | 79.19 |  |  |  | 6.48 |  | 5.08 | [8 empty] | 21.59 |  |  |  |  | 0.29
1999 |  |  |  | 5775.11 |  |  | 6589 |  |  |  | 950 | [10 empty] | 69.32 |  |  |  | 73.06 | [5 empty] | 69.40 |  |  | 75.22 |  |  |  | 5.65 |  | 4.37 | [8 empty] | 22.56 |  |  |  |  | 3.74
2000 |  |  |  | 6289.72 |  |  | 6784 |  |  |  | 950 | [10 empty] | 75.00 |  |  |  | 76.79 | [5 empty] | 75.37 |  |  | 77.23 |  |  |  | 3.54 |  | 2.82 | [8 empty] | 20.39 |  |  |  |  | 1.79
2001 |  |  |  | 6627.54 |  |  | 7020 |  |  |  | 950 | [10 empty] | 78.18 |  |  |  | 79.37 | [5 empty] | 79.64 |  |  | 80.14 |  |  |  | 5.67 |  | 4.77 | [8 empty] | 15.86 |  |  |  |  | 1.19
2002 |  |  |  | 7248.38 |  |  | 7568 |  |  |  | 950 | [10 empty] | 84.66 |  |  |  | 86.10 | [5 empty] | 87.10 |  |  | 86.39 |  |  |  | 0.27 |  | 0.23 | [8 empty] | 13.66 |  |  |  |  | 1.44
2003 |  |  |  | 7155.92 |  |  | 7408 |  |  |  | 950 | [10 empty] | 83.10 |  |  |  | 83.75 | [5 empty] | 85.99 |  |  | 84.57 |  |  |  | 4.40 |  | 3.85 | [8 empty] | 12.40 |  |  |  |  | 0.65
2004 |  |  |  | 6936.97 |  |  | 7179 |  |  |  | 950 | [10 empty] | 80.69 |  |  |  | 81.55 | [5 empty] | 83.13 |  |  | 81.73 |  |  |  | 2.57 |  | 2.15 | [8 empty] | 16.30 |  |  |  |  | 0.86
2005 |  |  |  | 6836.33 |  |  | 7219 |  |  |  | 950 | [10 empty] | 80.39 |  |  |  | 81.50 | [5 empty] | 82.14 |  |  | 82.40 |  |  |  | 4.45 |  | 4.78 | [8 empty] | 13.72 |  |  |  |  | 1.11
2006 |  |  |  | 6743.58 |  |  | 7112 |  |  |  | 950 | [10 empty] | 79.48 |  |  |  | 80.58 | [5 empty] | 81.03 |  |  | 81.19 |  |  |  | 4.77 |  | 5.16 | [8 empty] | 14.26 |  |  |  |  | 1.10
2007 |  |  |  | 7150.35 |  |  | 7491 |  |  |  | 950 | [10 empty] | 84.04 |  |  |  | 85.24 | [5 empty] | 85.92 |  |  | 85.51 |  |  |  | 2.14 |  | 1.87 | [8 empty] | 12.90 |  |  |  |  | 1.20
2008 |  |  |  | 6953.55 |  |  | 7209 |  |  |  | 950 | [10 empty] | 81.53 |  |  |  | 81.53 | [5 empty] | 83.33 |  |  | 82.07 |  |  |  | 2.44 |  | 2.04 | [8 empty] | 16.43 |  |  |  |  | 0.00
2009 |  |  |  | 7234.70 |  |  | 7669 |  |  |  | 950 | [10 empty] | 87.27 |  |  |  | 87.27 | [5 empty] | 86.93 |  |  | 87.55 |  |  |  | 0.70 |  | 0.62 | [8 empty] | 12.11 |  |  |  |  | 0.00
2010 |  |  |  | 7006.14 |  |  | 7175 |  |  |  | 950 | [10 empty] | 82.65 |  |  |  | 82.74 | [5 empty] | 84.19 |  |  | 81.91 |  |  |  | 6.45 |  | 5.71 | [8 empty] | 11.55 |  |  |  |  | 0.09
2011 |  |  |  | 7516.88 |  |  | 7727 |  |  |  | 950 | [10 empty] | 87.91 |  |  |  | 87.91 | [5 empty] | 90.34 |  |  | 88.22 |  |  |  | 0.22 |  | 0.19 | [8 empty] | 11.89 |  |  |  |  | 0.00
2012 |  |  |  | 6648.33 |  |  | 6833 |  |  |  | 950 | [10 empty] | 77.49 |  |  |  | 77.49 | [5 empty] | 79.67 |  |  | 77.79 |  |  |  | 0.94 |  | 0.74 | [8 empty] | 21.77 |  |  |  |  | 0.00
2013 |  |  |  | 6963.99 |  |  | 6915 |  |  |  | 950 | [10 empty] | 78.67 |  |  |  | 78.67 | [5 empty] | 83.68 |  |  | 78.94 |  |  |  | 6.17 |  | 15.31 | [8 empty] | 6.03 |  |  |  |  | 0.00
2014 |  |  |  | 5892.14 |  |  | 6035 |  |  |  | 950 | [10 empty] | 67.51 |  |  |  | 67.51 | [5 empty] | 70.79 |  |  | 68.88 |  |  |  | 3.79 |  | 2.66 | [8 empty] | 29.83 |  |  |  |  | 0.00
2015 |  |  |  | 8036.64 |  |  | 7931 |  |  |  | 950 | [10 empty] | 90.46 |  |  |  | 90.46 | [5 empty] | 96.57 |  |  | 90.54 |  |  |  | 0.64 |  | 0.58 | [8 empty] | 8.96 |  |  |  |  | 0.00
2016 |  |  |  | 6966.43 |  |  | 6876 |  |  |  | 950 | [10 empty] | 78.17 |  |  |  | 78.17 | [5 empty] | 83.48 |  |  | 78.28 |  |  |  | 8.56 |  | 7.32 | [8 empty] | 14.52 |  |  |  |  | 0.00
2017 |  |  |  | 8025.20 |  |  | 7856 |  |  |  | 950 | [10 empty] | 89.63 |  |  |  | 89.63 | [5 empty] | 96.43 |  |  | 89.68 |  |  |  | 0.00 |  | 0.53 | [8 empty] | 9.84 |  |  |  |  | 0.00
2018 |  |  |  | 8802.94 |  |  | 8643 |  |  |  | 950 | [10 empty] | 98.20 |  |  |  | 98.21 | [5 empty] | 105.78 |  |  | 98.66 |  |  |  | 1.79 |  | 1.79 | [8 empty] | 0.00 |  |  |  |  | 0.01
2019 |  |  |  | 6650.32 |  |  | 6595 |  |  |  | 950 | [10 empty] | 75.05 |  |  |  | 75.10 | [5 empty] | 79.91 |  |  | 75.29 |  |  |  | 6.64 |  | 5.34 | [8 empty] | 19.56 |  |  |  |  | 0.05
2020 |  |  |  | 2709.37 |  |  | 2703 |  |  |  | 950 | [10 empty] | 30.56 |  |  |  | 30.56 | [5 empty] | 32.47 |  |  | 30.77 |  |  |  | 4.41 |  | 1.41 | [8 empty] | 68.03 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 47 | [14 empty] | 280
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 5962 | [14 empty] | 1563 |  |  |  | 30
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 107 |  |  |  | 1
E. |  | Testing of plant systems or components | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [24 empty] | 72 | [14 empty] | 7
Z. |  | Other | [39 empty] | 36
Subtotal | [22 empty] | 5962 |  |  |  | 119 | [10 empty] | 1670 |  |  |  | 355 | [11 empty] | 3
Total | [22 empty] | 6081 | [14 empty] | 2028
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 35
12. |  |  | Reactor I&C Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 38
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 6
31. |  |  | Turbine and auxiliaries | [34 empty] | 25
32. |  |  | Feedwater and Main Steam System | [34 empty] | 21
34. |  |  | Miscellaneous Systems | [34 empty] | 3
35. |  |  | All other I&C Systems | [19 empty] | 47 | [14 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 127
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [22 empty] | 47 | [14 empty] | 289
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in September-Desember. Additional electricity generation amounted to 173244 MWh. The unit was in the overhaul outage from 2019.11.22 to 2020.09.05. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-2
2020 Operating Experience
RU-31 | [8 empty] | KALININ-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-338 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-02-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-12-03
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-03-03
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7987.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.52 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.8 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.48 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.8 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.73 %
Load Factor (LF) | [18 empty] | : | 95.72 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.43 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 753 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 72.92 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 764.04 | 714.10 |  |  |  | 731.86 |  | 659.61 | [8 empty] | 729.28 |  |  | 712.18 | [6 empty] | 752.92 |  | 755.13 |  |  |  | 92.94 |  |  | 600.62 |  |  | 708.46 | [9 empty] | 766.44 |  |  | 7987.59
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 96.99 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 14.01 |  |  | 80.20 |  |  | 97.20 | [9 empty] | 100.00 |  |  | 90.80
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 96.99 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 14.01 |  |  | 80.20 |  |  | 97.20 | [9 empty] | 100.00 |  |  | 90.80
LF [%] |  |  |  |  | 108.10 | 108.00 |  |  |  | 103.55 |  | 96.43 | [8 empty] | 103.18 |  |  | 104.12 | [6 empty] | 106.53 |  | 106.84 |  |  |  | 13.59 |  |  | 84.98 |  |  | 103.58 | [9 empty] | 108.44 |  |  | 95.72
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 15.42 |  |  | 80.65 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.43
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 3.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.80 | [9 empty] | 0.00 |  |  | 0.52
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 3.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.80 | [9 empty] | 0.00 |  |  | 0.48
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 85.99 |  |  | 19.80 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.73
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 225521.58 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.03 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.14 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.22 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.1 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.68 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 79.77 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.95 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.64 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 6494.00 |  |  | 7605 |  |  |  | 1000 | [10 empty] | 86.27 |  |  |  | 86.27 | [5 empty] | 79.18 |  |  | 87.96 |  |  |  | 9.13 |  | 8.67 | [8 empty] | 5.07 |  |  |  |  | 0.00
1988 |  |  |  | 5829.43 |  |  | 6446 |  |  |  | 950 | [10 empty] | 71.67 |  |  |  | 71.67 | [5 empty] | 69.86 |  |  | 73.38 |  |  |  | 9.64 |  | 7.64 | [8 empty] | 20.68 |  |  |  |  | 0.00
1989 |  |  |  | 6580.49 |  |  | 7034 |  |  |  | 950 | [10 empty] | 78.45 |  |  |  | 78.45 | [5 empty] | 79.07 |  |  | 80.30 |  |  |  | 5.86 |  | 4.88 | [8 empty] | 16.67 |  |  |  |  | 0.00
1990 |  |  |  | 6788.16 |  |  | 7083 |  |  |  | 950 | [10 empty] | 79.45 |  |  |  | 79.45 | [5 empty] | 81.57 |  |  | 80.86 |  |  |  | 5.85 |  | 4.94 | [8 empty] | 15.61 |  |  |  |  | 0.00
1991 |  |  |  | 4729.67 |  |  | 5154 |  |  |  | 950 | [10 empty] | 49.79 |  |  |  | 49.79 | [5 empty] | 56.83 |  |  | 58.84 |  |  |  | 30.08 |  | 21.42 | [8 empty] | 28.79 |  |  |  |  | 0.00
1992 |  |  |  | 5496.31 |  |  | 6145 |  |  |  | 950 | [10 empty] | 65.70 |  |  |  | 65.70 | [5 empty] | 65.87 |  |  | 69.96 |  |  |  | 5.58 |  | 3.88 | [8 empty] | 30.42 |  |  |  |  | 0.00
1993 |  |  |  | 5862.30 |  |  | 7078 |  |  |  | 950 | [10 empty] | 51.91 |  |  |  | 56.45 | [5 empty] | 70.44 |  |  | 80.80 |  |  |  | 28.07 |  | 22.03 | [8 empty] | 21.52 |  |  |  |  | 4.54
1994 |  |  |  | 4463.77 |  |  | 6989 |  |  |  | 950 | [10 empty] | 54.87 |  |  |  | 54.87 | [5 empty] | 53.64 |  |  | 79.78 |  |  |  | 31.92 |  | 25.73 | [8 empty] | 19.41 |  |  |  |  | 0.00
1995 |  |  |  | 5769.75 |  |  | 7283 |  |  |  | 950 | [10 empty] | 69.48 |  |  |  | 72.40 | [5 empty] | 69.33 |  |  | 83.14 |  |  |  | 15.96 |  | 13.75 | [8 empty] | 13.85 |  |  |  |  | 2.92
1996 |  |  |  | 4595.17 |  |  | 7501 |  |  |  | 950 | [10 empty] | 56.02 |  |  |  | 78.42 | [5 empty] | 55.07 |  |  | 85.39 |  |  |  | 2.81 |  | 2.26 | [8 empty] | 19.31 |  |  |  |  | 22.40
1997 |  |  |  | 3880.64 |  |  | 6117 |  |  |  | 950 | [10 empty] | 47.25 |  |  |  | 62.67 | [5 empty] | 46.63 |  |  | 69.83 |  |  |  | 2.47 |  | 1.59 | [8 empty] | 35.74 |  |  |  |  | 15.42
1998 |  |  |  | 4946.65 |  |  | 6839 |  |  |  | 950 | [10 empty] | 59.67 |  |  |  | 59.98 | [5 empty] | 59.44 |  |  | 78.07 |  |  |  | 26.91 |  | 22.08 | [8 empty] | 17.93 |  |  |  |  | 0.31
1999 |  |  |  | 6379.25 |  |  | 7155 |  |  |  | 950 | [10 empty] | 76.21 |  |  |  | 80.03 | [5 empty] | 76.66 |  |  | 81.68 |  |  |  | 0.26 |  | 0.21 | [8 empty] | 19.76 |  |  |  |  | 3.82
2000 |  |  |  | 6418.74 |  |  | 7441 |  |  |  | 950 | [10 empty] | 76.26 |  |  |  | 83.57 | [5 empty] | 76.92 |  |  | 84.71 |  |  |  | 0.55 |  | 0.46 | [8 empty] | 15.97 |  |  |  |  | 7.32
2001 |  |  |  | 6708.99 |  |  | 7070 |  |  |  | 950 | [10 empty] | 79.16 |  |  |  | 80.00 | [5 empty] | 80.62 |  |  | 80.71 |  |  |  | 2.26 |  | 1.85 | [8 empty] | 18.15 |  |  |  |  | 0.84
2002 |  |  |  | 7003.43 |  |  | 7554 |  |  |  | 950 | [10 empty] | 82.66 |  |  |  | 85.76 | [5 empty] | 84.16 |  |  | 86.23 |  |  |  | 1.00 |  | 0.86 | [8 empty] | 13.37 |  |  |  |  | 3.10
2003 |  |  |  | 7329.54 |  |  | 7541 |  |  |  | 950 | [10 empty] | 85.33 |  |  |  | 85.89 | [5 empty] | 88.07 |  |  | 86.08 |  |  |  | 0.77 |  | 0.67 | [8 empty] | 13.45 |  |  |  |  | 0.55
2004 |  |  |  | 7398.23 |  |  | 7674 |  |  |  | 950 | [10 empty] | 86.68 |  |  |  | 87.11 | [5 empty] | 88.66 |  |  | 87.36 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 12.79 |  |  |  |  | 0.44
2005 |  |  |  | 6116.27 |  |  | 6476 |  |  |  | 950 | [10 empty] | 72.11 |  |  |  | 73.62 | [5 empty] | 73.49 |  |  | 73.92 |  |  |  | 11.86 |  | 9.90 | [8 empty] | 16.48 |  |  |  |  | 1.51
2006 |  |  |  | 7074.89 |  |  | 7400 |  |  |  | 950 | [10 empty] | 82.73 |  |  |  | 84.26 | [5 empty] | 85.01 |  |  | 84.47 |  |  |  | 3.63 |  | 3.18 | [8 empty] | 12.56 |  |  |  |  | 1.53
2007 |  |  |  | 7231.43 |  |  | 7539 |  |  |  | 950 | [10 empty] | 84.16 |  |  |  | 85.49 | [5 empty] | 86.90 |  |  | 86.06 |  |  |  | 1.16 |  | 1.00 | [8 empty] | 13.51 |  |  |  |  | 1.33
2008 |  |  |  | 7474.79 |  |  | 7756 |  |  |  | 950 | [10 empty] | 88.19 |  |  |  | 88.19 | [5 empty] | 89.57 |  |  | 88.30 |  |  |  | 0.25 |  | 0.22 | [8 empty] | 11.59 |  |  |  |  | 0.00
2009 |  |  |  | 7004.16 |  |  | 7248 |  |  |  | 950 | [10 empty] | 82.51 |  |  |  | 82.51 | [5 empty] | 84.16 |  |  | 82.74 |  |  |  | 1.50 |  | 1.26 | [8 empty] | 16.23 |  |  |  |  | 0.00
2010 |  |  |  | 7423.50 |  |  | 7595 |  |  |  | 950 | [10 empty] | 87.77 |  |  |  | 87.77 | [5 empty] | 89.20 |  |  | 86.70 |  |  |  | 1.51 |  | 1.34 | [8 empty] | 10.89 |  |  |  |  | 0.00
2011 |  |  |  | 7570.61 |  |  | 7675 |  |  |  | 950 | [10 empty] | 86.98 |  |  |  | 86.98 | [5 empty] | 90.98 |  |  | 87.62 |  |  |  | 0.63 |  | 0.55 | [8 empty] | 12.47 |  |  |  |  | 0.00
2012 |  |  |  | 7164.85 |  |  | 7464 |  |  |  | 950 | [10 empty] | 84.47 |  |  |  | 84.47 | [5 empty] | 85.86 |  |  | 84.97 |  |  |  | 0.93 |  | 0.79 | [8 empty] | 14.74 |  |  |  |  | 0.00
2013 |  |  |  | 8635.13 |  |  | 8552 |  |  |  | 950 | [10 empty] | 97.57 |  |  |  | 97.57 | [5 empty] | 103.76 |  |  | 97.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.43 |  |  |  |  | 0.00
2014 |  |  |  | 7030.39 |  |  | 6984 |  |  |  | 950 | [10 empty] | 79.59 |  |  |  | 79.59 | [5 empty] | 84.47 |  |  | 79.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.41 |  |  |  |  | 0.00
2015 |  |  |  | 7883.15 |  |  | 7805 |  |  |  | 950 | [10 empty] | 88.94 |  |  |  | 88.94 | [5 empty] | 94.73 |  |  | 89.10 |  |  |  | 2.10 |  | 1.90 | [8 empty] | 9.16 |  |  |  |  | 0.00
2016 |  |  |  | 6776.88 |  |  | 6664 |  |  |  | 950 | [10 empty] | 75.75 |  |  |  | 75.75 | [5 empty] | 81.21 |  |  | 75.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.25 |  |  |  |  | 0.00
2017 |  |  |  | 7562.08 |  |  | 7439 |  |  |  | 950 | [10 empty] | 84.68 |  |  |  | 84.71 | [5 empty] | 90.87 |  |  | 84.92 |  |  |  | 1.93 |  | 6.54 | [8 empty] | 8.75 |  |  |  |  | 0.03
2018 |  |  |  | 8390.72 |  |  | 8224 |  |  |  | 950 | [10 empty] | 93.84 |  |  |  | 93.86 | [5 empty] | 100.83 |  |  | 93.88 |  |  |  | 6.14 |  | 6.14 | [8 empty] | 0.00 |  |  |  |  | 0.01
2019 |  |  |  | 7769.30 |  |  | 7721 |  |  |  | 950 | [10 empty] | 87.05 |  |  |  | 87.05 | [5 empty] | 93.36 |  |  | 88.14 |  |  |  | 1.94 |  | 1.73 | [8 empty] | 11.23 |  |  |  |  | 0.00
2020 |  |  |  | 7987.59 |  |  | 8031 |  |  |  | 950 | [10 empty] | 90.80 |  |  |  | 90.80 | [5 empty] | 95.72 |  |  | 91.43 |  |  |  | 0.52 |  | 0.48 | [8 empty] | 8.73 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 182
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 753 | [14 empty] | 1234 |  |  |  | 6
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 21 | [14 empty] | 69
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 16
Z. |  | Other | [39 empty] | 3
Subtotal | [22 empty] | 774 | [14 empty] | 1303 |  |  |  | 207 | [11 empty] | 3
Total | [22 empty] | 774 | [14 empty] | 1513
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 19
15. |  |  | Reactor Cooling Systems | [34 empty] | 30
16. |  |  | Steam generation systems | [34 empty] | 4
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 30
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 73
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 189
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-Desember. Additional electricity generation amounted to 510875,3 MWh. The unit was in the overhaul outage from 2020.09.05 to 2020.10.07. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-3
2020 Operating Experience
RU-36 | [8 empty] | KALININ-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | FAEA (Federal Atomic Energy Agency)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-10-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2004-12-16
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2005-11-08
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 16 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8807.69 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 105.55 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 26.56 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 755.78 | 707.27 |  |  |  | 746.96 |  | 717.00 | [8 empty] | 743.28 |  |  | 701.30 | [6 empty] | 742.47 |  | 739.76 |  |  |  | 723.33 |  |  | 747.67 |  |  | 726.73 | [9 empty] | 756.14 |  |  | 8807.69
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 106.93 | 106.97 |  |  |  | 105.68 |  | 104.82 | [8 empty] | 105.16 |  |  | 102.53 | [6 empty] | 105.05 |  | 104.66 |  |  |  | 105.75 |  |  | 105.78 |  |  | 106.25 | [9 empty] | 106.98 |  |  | 105.55
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 111471.88 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.93 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.32 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.82 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.41 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.78 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.92 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.09 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2005 |  |  |  | 4345.70 |  |  | 5686 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.84 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 6287.23 |  |  | 6692 |  |  |  | 950 | [10 empty] | 74.90 |  |  |  | 75.20 | [5 empty] | 75.55 |  |  | 76.39 |  |  |  | 5.71 |  | 6.62 | [8 empty] | 18.18 |  |  |  |  | 0.29
2007 |  |  |  | 7185.22 |  |  | 7505 |  |  |  | 950 | [10 empty] | 84.96 |  |  |  | 85.51 | [5 empty] | 86.34 |  |  | 85.67 |  |  |  | 0.91 |  | 0.81 | [8 empty] | 13.68 |  |  |  |  | 0.55
2008 |  |  |  | 7561.73 |  |  | 7737 |  |  |  | 950 | [10 empty] | 87.74 |  |  |  | 87.78 | [5 empty] | 90.62 |  |  | 88.08 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 12.06 |  |  |  |  | 0.03
2009 |  |  |  | 6806.52 |  |  | 7553 |  |  |  | 950 | [10 empty] | 85.96 |  |  |  | 85.96 | [5 empty] | 81.79 |  |  | 86.22 |  |  |  | 3.61 |  | 3.22 | [8 empty] | 10.82 |  |  |  |  | 0.00
2010 |  |  |  | 6902.21 |  |  | 7248 |  |  |  | 950 | [10 empty] | 82.13 |  |  |  | 82.44 | [5 empty] | 82.94 |  |  | 82.74 |  |  |  | 1.25 |  | 1.04 | [8 empty] | 16.52 |  |  |  |  | 0.31
2011 |  |  |  | 7088.32 |  |  | 7427 |  |  |  | 950 | [10 empty] | 84.82 |  |  |  | 84.85 | [5 empty] | 85.19 |  |  | 84.79 |  |  |  | 0.59 |  | 2.84 | [8 empty] | 12.31 |  |  |  |  | 0.04
2012 |  |  |  | 7765.07 |  |  | 8091 |  |  |  | 950 | [10 empty] | 91.78 |  |  |  | 91.78 | [5 empty] | 93.05 |  |  | 92.11 |  |  |  | 6.68 |  | 6.57 | [8 empty] | 1.65 |  |  |  |  | 0.01
2013 |  |  |  | 6505.71 |  |  | 6698 |  |  |  | 950 | [10 empty] | 76.18 |  |  |  | 76.18 | [5 empty] | 78.17 |  |  | 76.46 |  |  |  | 1.31 |  | 10.15 | [8 empty] | 13.67 |  |  |  |  | 0.00
2014 |  |  |  | 6599.48 |  |  | 6918 |  |  |  | 950 | [10 empty] | 78.27 |  |  |  | 78.27 | [5 empty] | 79.29 |  |  | 78.96 |  |  |  | 5.79 |  | 5.33 | [8 empty] | 16.40 |  |  |  |  | 0.00
2015 |  |  |  | 7665.20 |  |  | 8196 |  |  |  | 950 | [10 empty] | 92.28 |  |  |  | 92.28 | [5 empty] | 92.11 |  |  | 93.56 |  |  |  | 7.67 |  | 7.67 | [8 empty] | 0.05 |  |  |  |  | 0.00
2016 |  |  |  | 5233.15 |  |  | 5612 |  |  |  | 950 | [10 empty] | 62.43 |  |  |  | 62.43 | [5 empty] | 62.71 |  |  | 63.89 |  |  |  | 10.35 |  | 13.02 | [8 empty] | 24.55 |  |  |  |  | 0.00
2017 |  |  |  | 7892.37 |  |  | 7990 |  |  |  | 950 | [10 empty] | 91.11 |  |  |  | 91.11 | [5 empty] | 94.84 |  |  | 91.21 |  |  |  | 8.89 |  | 8.89 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 7504.45 |  |  | 7558 |  |  |  | 950 | [10 empty] | 85.85 |  |  |  | 85.95 | [5 empty] | 90.18 |  |  | 86.28 |  |  |  | 2.29 |  | 2.01 | [8 empty] | 12.04 |  |  |  |  | 0.10
2019 |  |  |  | 7322.22 |  |  | 7362 |  |  |  | 950 | [10 empty] | 83.69 |  |  |  | 83.76 | [5 empty] | 87.99 |  |  | 84.04 |  |  |  | 4.44 |  | 4.74 | [8 empty] | 11.50 |  |  |  |  | 0.07
2020 |  |  |  | 8807.69 |  |  | 8784 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.55 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2005 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 359
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 929 |  |  |  | 12
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 19
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 2
Z. |  | Other | [39 empty] | 13
Subtotal | [37 empty] | 948 |  |  |  | 393 | [11 empty] | 2
Total | [22 empty] | 0 | [14 empty] | 1343
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2005 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 4
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 59
32. |  |  | Feedwater and Main Steam System | [34 empty] | 12
33. |  |  | Circulating Water System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 171
42. |  |  | Electrical Power Supply Systems | [34 empty] | 97
Total | [37 empty] | 376
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-Desember. Additional electricity generation amounted to 498955.5 MWh. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-4
2020 Operating Experience
RU-37 | [8 empty] | KALININ-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1986-08-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2011-11-24
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2012-12-25
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 1.05
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7553.71 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.93 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.69 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.28 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.02 %
Load Factor (LF) | [18 empty] | : | 90.52 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 86.95 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1146 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 23.52 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 755.35 | 701.95 |  |  |  | 733.23 |  | 700.61 | [8 empty] | 728.96 |  |  | 710.47 | [6 empty] | 221.53 |  | 177.63 |  |  |  | 719.69 |  |  | 723.59 |  |  | 729.07 | [9 empty] | 651.63 |  |  | 7553.71
EAF [%] |  |  |  |  | 100.00 | 99.47 |  |  |  | 99.94 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 29.05 |  | 25.45 |  |  |  | 100.00 |  |  | 97.14 |  |  | 100.00 | [9 empty] | 86.99 |  |  | 86.28
UCF [%] |  |  |  |  | 100.00 | 99.47 |  |  |  | 99.94 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 29.05 |  | 25.45 |  |  |  | 100.00 |  |  | 97.14 |  |  | 100.00 | [9 empty] | 86.99 |  |  | 86.28
LF [%] |  |  |  |  | 106.87 | 106.16 |  |  |  | 103.74 |  | 102.43 | [8 empty] | 103.14 |  |  | 103.87 | [6 empty] | 31.34 |  | 25.13 |  |  |  | 105.22 |  |  | 102.37 |  |  | 106.59 | [9 empty] | 92.19 |  |  | 90.52
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 32.39 |  | 26.21 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 87.37 |  |  | 86.95
FLR [%] |  |  |  |  | 0.00 | 0.53 |  |  |  | 0.06 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 12.34 |  |  |  | 0.00 |  |  | 2.86 |  |  | 0.00 | [9 empty] | 13.01 |  |  | 1.93
UCL [%] |  |  |  |  | 0.00 | 0.53 |  |  |  | 0.06 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 3.58 |  |  |  | 0.00 |  |  | 2.86 |  |  | 0.00 | [9 empty] | 13.01 |  |  | 1.69
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 70.95 |  | 70.97 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.02
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 65215.28 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.29 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.55 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.16 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.88 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.82 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2012 |  |  |  | 5166.49 |  |  | 6858 |  |  |  | 950 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 6342.91 |  |  | 6662 |  |  |  | 950 | [10 empty] | 75.72 |  |  |  | 75.73 | [5 empty] | 76.22 |  |  | 76.05 |  |  |  | 6.89 |  | 8.42 | [8 empty] | 15.85 |  |  |  |  | 0.02
2014 |  |  |  | 7249.38 |  |  | 7691 |  |  |  | 950 | [10 empty] | 87.21 |  |  |  | 87.21 | [5 empty] | 87.10 |  |  | 87.79 |  |  |  | 1.23 |  | 1.08 | [8 empty] | 11.71 |  |  |  |  | 0.00
2015 |  |  |  | 8086.65 |  |  | 8346 |  |  |  | 950 | [10 empty] | 95.01 |  |  |  | 95.01 | [5 empty] | 97.17 |  |  | 95.27 |  |  |  | 4.99 |  | 4.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6704.20 |  |  | 7255 |  |  |  | 950 | [10 empty] | 80.15 |  |  |  | 80.15 | [5 empty] | 80.34 |  |  | 82.59 |  |  |  | 9.83 |  | 8.96 | [8 empty] | 10.89 |  |  |  |  | 0.00
2017 |  |  |  | 7535.97 |  |  | 7490 |  |  |  | 950 | [10 empty] | 86.52 |  |  |  | 86.52 | [5 empty] | 90.55 |  |  | 85.50 |  |  |  | 0.92 |  | 2.39 | [8 empty] | 11.09 |  |  |  |  | 0.00
2018 |  |  |  | 8736.46 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.76 |  |  |  | 99.76 | [5 empty] | 104.98 |  |  | 100.00 |  |  |  | 0.24 |  | 0.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7668.87 |  |  | 7745 |  |  |  | 950 | [10 empty] | 87.66 |  |  |  | 87.66 | [5 empty] | 92.15 |  |  | 88.41 |  |  |  | 0.70 |  | 0.61 | [8 empty] | 11.72 |  |  |  |  | 0.00
2020 |  |  |  | 7553.71 |  |  | 7638 |  |  |  | 950 | [10 empty] | 86.28 |  |  |  | 86.28 | [5 empty] | 90.52 |  |  | 86.95 |  |  |  | 1.93 |  | 1.69 | [8 empty] | 12.02 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2012 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 118 | [14 empty] | 254
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1007 | [14 empty] | 786
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 17
L. |  | Human factor related | [39 empty] | 9
Subtotal | [22 empty] | 1007 |  |  |  | 118 | [10 empty] | 803 |  |  |  | 263
Total | [22 empty] | 1125 | [14 empty] | 1066
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2012 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 8
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 84
32. |  |  | Feedwater and Main Steam System | [19 empty] | 94 | [14 empty] | 10
33. |  |  | Circulating Water System | [19 empty] | 25 | [14 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 79
42. |  |  | Electrical Power Supply Systems | [34 empty] | 44
Total | [22 empty] | 119 | [14 empty] | 233
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-Desember. Additional electricity generation amounted to 439698 MWh. The unit was in the overhaul outage from 2020.07.11 to 2020.08.22. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-1
2020 Operating Experience
RU-12 | [8 empty] | KOLA-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-230 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-05-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-06-29
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-12-28
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2327.08 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.07 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.03 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.05 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.03 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.92 %
Load Factor (LF) | [18 empty] | : | 64.46 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 81.89 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1591 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 1.76 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 247.63 | 290.87 |  |  |  | 7.24 |  | 0.00 | [8 empty] | 192.08 |  |  | 271.65 | [6 empty] | 285.65 |  | 283.77 |  |  |  | 131.19 |  |  | 164.87 |  |  | 291.02 | [9 empty] | 161.11 |  |  | 2327.08
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.94 |  | 0.01 | [8 empty] | 66.92 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.33 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.03
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.94 |  | 0.01 | [8 empty] | 66.92 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.33 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.03
LF [%] |  |  |  |  | 80.98 | 101.68 |  |  |  | 2.37 |  | 0.00 | [8 empty] | 62.81 |  |  | 91.80 | [6 empty] | 93.42 |  | 92.80 |  |  |  | 44.33 |  |  | 53.92 |  |  | 98.35 | [9 empty] | 52.69 |  |  | 64.46
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 8.20 |  | 0.00 | [8 empty] | 76.08 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 98.61 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.89
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.67 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.07
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.67 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 58.06 |  | 99.99 | [8 empty] | 33.08 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.92
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 109279.94 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.7 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.19 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.16 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.64 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 64 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 5.24 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.25 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 918.20 |  |  | 4180 |  |  |  | 411 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1974 |  |  |  | 1990.06 |  |  | 8463 |  |  |  | 411 | [10 empty] | 79.22 |  |  |  | 79.22 | [5 empty] | 55.27 |  |  | 96.61 |  |  |  | 0.90 |  | 0.72 | [8 empty] | 20.06 |  |  |  |  | 0.01
1975 |  |  |  | 1015.76 |  |  | 5426 |  |  |  | 411 | [10 empty] | 50.91 |  |  |  | 50.94 | [5 empty] | 28.21 |  |  | 61.94 |  |  |  | 1.27 |  | 0.66 | [8 empty] | 48.40 |  |  |  |  | 0.03
1976 |  |  |  | 2421.71 |  |  | 8247 |  |  |  | 411 | [10 empty] | 74.05 |  |  |  | 74.17 | [5 empty] | 67.08 |  |  | 93.89 |  |  |  | 0.97 |  | 0.73 | [8 empty] | 25.10 |  |  |  |  | 0.12
1977 |  |  |  | 2101.05 |  |  | 7462 |  |  |  | 411 | [10 empty] | 76.38 |  |  |  | 76.40 | [5 empty] | 58.36 |  |  | 85.18 |  |  |  | 6.73 |  | 5.52 | [8 empty] | 18.09 |  |  |  |  | 0.01
1978 |  |  |  | 2978.78 |  |  | 8074 |  |  |  | 411 | [10 empty] | 82.58 |  |  |  | 82.60 | [5 empty] | 82.74 |  |  | 92.17 |  |  |  | 1.55 |  | 1.30 | [8 empty] | 16.10 |  |  |  |  | 0.02
1979 |  |  |  | 2435.60 |  |  | 6232 |  |  |  | 411 | [10 empty] | 64.63 |  |  |  | 64.65 | [5 empty] | 67.65 |  |  | 71.14 |  |  |  | 2.14 |  | 1.41 | [8 empty] | 33.94 |  |  |  |  | 0.02
1980 |  |  |  | 3466.37 |  |  | 8072 |  |  |  | 411 | [10 empty] | 90.90 |  |  |  | 91.05 | [5 empty] | 96.02 |  |  | 91.89 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 8.65 |  |  |  |  | 0.15
1981 |  |  |  | 2870.79 |  |  | 7448 |  |  |  | 411 | [10 empty] | 80.94 |  |  |  | 80.95 | [5 empty] | 79.74 |  |  | 85.02 |  |  |  | 2.81 |  | 2.34 | [8 empty] | 16.71 |  |  |  |  | 0.01
1982 |  |  |  | 2848.07 |  |  | 7875 |  |  |  | 411 | [10 empty] | 85.52 |  |  |  | 85.52 | [5 empty] | 79.11 |  |  | 89.90 |  |  |  | 1.80 |  | 1.56 | [8 empty] | 12.91 |  |  |  |  | 0.01
1983 |  |  |  | 3217.37 |  |  | 7884 |  |  |  | 411 | [10 empty] | 88.25 |  |  |  | 88.27 | [5 empty] | 89.36 |  |  | 90.00 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 11.57 |  |  |  |  | 0.02
1984 |  |  |  | 3112.02 |  |  | 8060 |  |  |  | 411 | [10 empty] | 84.90 |  |  |  | 84.92 | [5 empty] | 86.20 |  |  | 91.76 |  |  |  | 1.41 |  | 1.22 | [8 empty] | 13.87 |  |  |  |  | 0.01
1985 |  |  |  | 2388.76 |  |  | 6001 |  |  |  | 411 | [10 empty] | 67.02 |  |  |  | 67.05 | [5 empty] | 66.35 |  |  | 68.50 |  |  |  | 0.61 |  | 0.41 | [8 empty] | 32.54 |  |  |  |  | 0.03
1986 |  |  |  | 2805.84 |  |  | 8074 |  |  |  | 411 | [10 empty] | 85.08 |  |  |  | 85.08 | [5 empty] | 77.93 |  |  | 92.17 |  |  |  | 5.88 |  | 5.32 | [8 empty] | 9.60 |  |  |  |  | 0.00
1987 |  |  |  | 3268.23 |  |  | 7972 |  |  |  | 440 | [10 empty] | 86.00 |  |  |  | 86.00 | [5 empty] | 84.79 |  |  | 91.00 |  |  |  | 0.96 |  | 0.83 | [8 empty] | 13.17 |  |  |  |  | 0.00
1988 |  |  |  | 2925.01 |  |  | 7482 |  |  |  | 411 | [10 empty] | 82.67 |  |  |  | 82.73 | [5 empty] | 81.02 |  |  | 85.18 |  |  |  | 6.53 |  | 5.78 | [8 empty] | 11.49 |  |  |  |  | 0.06
1989 |  |  |  | 2675.48 |  |  | 6731 |  |  |  | 411 | [10 empty] | 75.44 |  |  |  | 76.23 | [5 empty] | 74.31 |  |  | 76.84 |  |  |  | 1.18 |  | 0.91 | [8 empty] | 22.86 |  |  |  |  | 0.79
1990 |  |  |  | 2735.50 |  |  | 6838 |  |  |  | 411 | [10 empty] | 75.95 |  |  |  | 75.95 | [5 empty] | 75.98 |  |  | 78.06 |  |  |  | 2.00 |  | 1.55 | [8 empty] | 22.50 |  |  |  |  | 0.00
1991 |  |  |  | 2773.12 |  |  | 6965 |  |  |  | 411 | [10 empty] | 77.27 |  |  |  | 77.27 | [5 empty] | 77.02 |  |  | 79.51 |  |  |  | 7.17 |  | 5.97 | [8 empty] | 16.76 |  |  |  |  | 0.00
1992 |  |  |  | 2271.37 |  |  | 6651 |  |  |  | 411 | [10 empty] | 63.44 |  |  |  | 63.70 | [5 empty] | 62.92 |  |  | 75.73 |  |  |  | 17.65 |  | 13.65 | [8 empty] | 22.65 |  |  |  |  | 0.26
1993 |  |  |  | 1992.62 |  |  | 5663 |  |  |  | 411 | [10 empty] | 56.14 |  |  |  | 59.56 | [5 empty] | 55.35 |  |  | 64.65 |  |  |  | 14.77 |  | 10.32 | [8 empty] | 30.11 |  |  |  |  | 3.42
1994 |  |  |  | 1971.62 |  |  | 5359 |  |  |  | 411 | [10 empty] | 56.50 |  |  |  | 58.63 | [5 empty] | 54.76 |  |  | 61.18 |  |  |  | 7.34 |  | 4.65 | [8 empty] | 36.72 |  |  |  |  | 2.13
1995 |  |  |  | 1581.37 |  |  | 5398 |  |  |  | 411 | [10 empty] | 62.24 |  |  |  | 62.24 | [5 empty] | 43.92 |  |  | 61.62 |  |  |  | 5.06 |  | 3.32 | [8 empty] | 34.44 |  |  |  |  | 0.00
1996 |  |  |  | 1409.96 |  |  | 4466 |  |  |  | 411 | [10 empty] | 46.43 |  |  |  | 47.44 | [5 empty] | 39.05 |  |  | 50.84 |  |  |  | 6.51 |  | 3.30 | [8 empty] | 49.26 |  |  |  |  | 1.00
1997 |  |  |  | 2404.12 |  |  | 7942 |  |  |  | 411 | [10 empty] | 88.48 |  |  |  | 88.48 | [5 empty] | 66.77 |  |  | 90.66 |  |  |  | 5.02 |  | 4.68 | [8 empty] | 6.84 |  |  |  |  | 0.00
1998 |  |  |  | 1291.73 |  |  | 5658 |  |  |  | 411 | [10 empty] | 37.66 |  |  |  | 59.27 | [5 empty] | 35.88 |  |  | 64.59 |  |  |  | 12.77 |  | 8.68 | [8 empty] | 32.05 |  |  |  |  | 21.61
1999 |  |  |  | 2028.49 |  |  | 7355 |  |  |  | 411 | [10 empty] | 58.01 |  |  |  | 86.57 | [5 empty] | 56.34 |  |  | 83.96 |  |  |  | 0.97 |  | 0.85 | [8 empty] | 12.58 |  |  |  |  | 28.56
2000 |  |  |  | 1298.85 |  |  | 4643 |  |  |  | 411 | [10 empty] | 37.17 |  |  |  | 84.13 | [5 empty] | 35.98 |  |  | 52.86 |  |  |  | 0.80 |  | 0.68 | [8 empty] | 15.19 |  |  |  |  | 46.96
2001 |  |  |  | 2243.22 |  |  | 7098 |  |  |  | 411 | [10 empty] | 63.27 |  |  |  | 81.60 | [5 empty] | 62.31 |  |  | 81.03 |  |  |  | 0.91 |  | 0.75 | [8 empty] | 17.65 |  |  |  |  | 18.33
2002 |  |  |  | 1841.48 |  |  | 5660 |  |  |  | 411 | [10 empty] | 51.65 |  |  |  | 68.90 | [5 empty] | 51.15 |  |  | 64.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.10 |  |  |  |  | 17.25
2003 |  |  |  | 2164.00 |  |  | 6444 |  |  |  | 411 | [10 empty] | 60.41 |  |  |  | 75.51 | [5 empty] | 60.11 |  |  | 73.56 |  |  |  | 0.73 |  | 0.55 | [8 empty] | 23.94 |  |  |  |  | 15.10
2004 |  |  |  | 2440.48 |  |  | 7326 |  |  |  | 411 | [10 empty] | 68.21 |  |  |  | 83.64 | [5 empty] | 67.60 |  |  | 83.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.36 |  |  |  |  | 15.43
2005 |  |  |  | 2151.67 |  |  | 6901 |  |  |  | 411 | [10 empty] | 60.60 |  |  |  | 90.57 | [5 empty] | 59.76 |  |  | 78.78 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.43 |  |  |  |  | 29.97
2006 |  |  |  | 2338.66 |  |  | 7661 |  |  |  | 411 | [10 empty] | 65.95 |  |  |  | 89.94 | [5 empty] | 64.96 |  |  | 87.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.06 |  |  |  |  | 23.98
2007 |  |  |  | 2658.02 |  |  | 7740 |  |  |  | 411 | [10 empty] | 74.43 |  |  |  | 90.96 | [5 empty] | 73.83 |  |  | 88.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.04 |  |  |  |  | 16.53
2008 |  |  |  | 2705.75 |  |  | 7397 |  |  |  | 411 | [10 empty] | 84.34 |  |  |  | 84.34 | [5 empty] | 74.95 |  |  | 84.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.66 |  |  |  |  | 0.00
2009 |  |  |  | 2277.43 |  |  | 7333 |  |  |  | 411 | [10 empty] | 83.76 |  |  |  | 83.77 | [5 empty] | 63.26 |  |  | 83.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.23 |  |  |  |  | 0.01
2010 |  |  |  | 2467.97 |  |  | 7912 |  |  |  | 411 | [10 empty] | 85.79 |  |  |  | 85.82 | [5 empty] | 68.55 |  |  | 90.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.18 |  |  |  |  | 0.03
2011 |  |  |  | 2465.32 |  |  | 7870 |  |  |  | 411 | [10 empty] | 83.47 |  |  |  | 83.62 | [5 empty] | 68.48 |  |  | 89.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.38 |  |  |  |  | 0.15
2012 |  |  |  | 2205.74 |  |  | 7021 |  |  |  | 411 | [10 empty] | 82.24 |  |  |  | 82.24 | [5 empty] | 61.10 |  |  | 79.93 |  |  |  | 1.67 |  | 1.39 | [8 empty] | 16.37 |  |  |  |  | 0.00
2013 |  |  |  | 2380.88 |  |  | 7811 |  |  |  | 411 | [10 empty] | 83.98 |  |  |  | 83.98 | [5 empty] | 66.13 |  |  | 89.17 |  |  |  | 4.60 |  | 4.05 | [8 empty] | 11.97 |  |  |  |  | 0.00
2014 |  |  |  | 1911.66 |  |  | 7536 |  |  |  | 411 | [10 empty] | 85.18 |  |  |  | 86.19 | [5 empty] | 53.09 |  |  | 86.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.81 |  |  |  |  | 1.01
2015 |  |  |  | 2112.22 |  |  | 7373 |  |  |  | 411 | [10 empty] | 83.10 |  |  |  | 84.00 | [5 empty] | 58.67 |  |  | 84.17 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 15.99 |  |  |  |  | 0.91
2016 |  |  |  | 2097.80 |  |  | 6386 |  |  |  | 411 | [10 empty] | 78.45 |  |  |  | 78.45 | [5 empty] | 58.11 |  |  | 72.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.55 |  |  |  |  | 0.00
2017 |  |  |  | 1982.33 |  |  | 7025 |  |  |  | 411 | [10 empty] | 77.78 |  |  |  | 78.62 | [5 empty] | 55.06 |  |  | 80.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.38 |  |  |  |  | 0.84
2018 |  |  |  | 688.02 |  |  | 2652 |  |  |  | 411 | [10 empty] | 28.92 |  |  |  | 30.25 | [5 empty] | 19.11 |  |  | 30.27 |  |  |  | 5.22 |  | 1.97 | [8 empty] | 67.78 |  |  |  |  | 1.33
2019 |  |  |  | 2796.96 |  |  | 7740 |  |  |  | 411 | [10 empty] | 80.24 |  |  |  | 80.62 | [5 empty] | 77.69 |  |  | 88.36 |  |  |  | 6.14 |  | 7.61 | [8 empty] | 11.77 |  |  |  |  | 0.38
2020 |  |  |  | 2327.08 |  |  | 7193 |  |  |  | 411 | [10 empty] | 84.03 |  |  |  | 84.03 | [5 empty] | 64.46 |  |  | 81.89 |  |  |  | 0.07 |  | 0.05 | [8 empty] | 15.92 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1973 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 10 | [14 empty] | 49
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1330 | [14 empty] | 1492 |  |  |  | 3
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 76
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 56
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 40
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 251 | [19 empty] | 118
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 5
Z. |  | Other | [39 empty] | 8
Subtotal | [22 empty] | 1330 |  |  |  | 10 | [6 empty] | 251 |  |  |  | 1624 |  |  |  | 61 | [11 empty] | 165
Total | [22 empty] | 1591 | [14 empty] | 1850
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1973 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 13
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [19 empty] | 10 | [14 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [22 empty] | 10 | [14 empty] | 49
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-February, May-July, October-Desember. Additional electricity generation amounted to 23553 MWh. The unit was in the overhaul outage from 2020.03.14 to 2020.05.08. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-2
2020 Operating Experience
RU-13 | [8 empty] | KOLA-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-230 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-05-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-12-09
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-02-21
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 1890.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.71 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.71 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.29 %
Load Factor (LF) | [18 empty] | : | 52.37 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.01 %
Operating Factor (OF) | [18 empty] | : | 81.83 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1596 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 1.03 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 187.41 | 78.04 |  |  |  | 273.45 |  | 257.41 | [8 empty] | 211.32 |  |  | 132.01 | [6 empty] | 145.30 |  | 57.19 |  |  |  | 0.00 |  |  | 96.10 |  |  | 285.00 | [9 empty] | 167.45 |  |  | 1890.68
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 46.27 |  |  |  | 0.01 |  |  | 93.55 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.71
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 46.36 |  |  |  | 0.01 |  |  | 93.55 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.71
LF [%] |  |  |  |  | 61.29 | 27.28 |  |  |  | 89.43 |  | 86.99 | [8 empty] | 69.11 |  |  | 44.61 | [6 empty] | 47.52 |  | 18.70 |  |  |  | 0.00 |  |  | 31.43 |  |  | 96.31 | [9 empty] | 54.76 |  |  | 52.37
OF [%] |  |  |  |  | 100.00 | 68.82 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 46.37 |  |  |  | 0.00 |  |  | 65.05 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.83
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 53.64 |  |  |  | 99.99 |  |  | 6.45 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.29
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.09 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 106181.31 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.72 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.77 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.16 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.34 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.5 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 64.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 4.56 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.76 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 1383.07 |  |  | 6449 |  |  |  | 411 | [10 empty] | 88.23 |  |  |  | 88.23 | [5 empty] | 37.48 |  |  | 73.97 |  |  |  | 3.66 |  | 3.35 | [8 empty] | 8.41 |  |  |  |  | 0.00
1976 |  |  |  | 1943.15 |  |  | 7083 |  |  |  | 411 | [10 empty] | 70.82 |  |  |  | 70.82 | [5 empty] | 53.82 |  |  | 80.64 |  |  |  | 0.74 |  | 0.53 | [8 empty] | 28.65 |  |  |  |  | 0.00
1977 |  |  |  | 2627.24 |  |  | 7038 |  |  |  | 411 | [10 empty] | 76.90 |  |  |  | 77.05 | [5 empty] | 72.97 |  |  | 80.34 |  |  |  | 1.10 |  | 0.85 | [8 empty] | 22.09 |  |  |  |  | 0.15
1978 |  |  |  | 2982.47 |  |  | 7576 |  |  |  | 411 | [10 empty] | 82.71 |  |  |  | 82.71 | [5 empty] | 82.84 |  |  | 86.48 |  |  |  | 0.67 |  | 0.56 | [8 empty] | 16.73 |  |  |  |  | 0.00
1979 |  |  |  | 3057.59 |  |  | 7663 |  |  |  | 411 | [10 empty] | 82.40 |  |  |  | 83.51 | [5 empty] | 84.92 |  |  | 87.48 |  |  |  | 3.13 |  | 2.70 | [8 empty] | 13.79 |  |  |  |  | 1.11
1980 |  |  |  | 3266.85 |  |  | 7966 |  |  |  | 411 | [10 empty] | 85.80 |  |  |  | 85.99 | [5 empty] | 90.49 |  |  | 90.69 |  |  |  | 0.71 |  | 0.62 | [8 empty] | 13.40 |  |  |  |  | 0.19
1981 |  |  |  | 3146.68 |  |  | 8225 |  |  |  | 411 | [10 empty] | 87.78 |  |  |  | 87.78 | [5 empty] | 87.40 |  |  | 93.89 |  |  |  | 2.81 |  | 2.54 | [8 empty] | 9.68 |  |  |  |  | 0.00
1982 |  |  |  | 2462.96 |  |  | 6742 |  |  |  | 411 | [10 empty] | 71.24 |  |  |  | 71.24 | [5 empty] | 68.41 |  |  | 76.96 |  |  |  | 3.13 |  | 2.30 | [8 empty] | 26.46 |  |  |  |  | 0.00
1983 |  |  |  | 3072.64 |  |  | 7963 |  |  |  | 411 | [10 empty] | 85.27 |  |  |  | 85.30 | [5 empty] | 85.34 |  |  | 90.90 |  |  |  | 3.18 |  | 2.80 | [8 empty] | 11.90 |  |  |  |  | 0.03
1984 |  |  |  | 3034.45 |  |  | 8079 |  |  |  | 411 | [10 empty] | 86.75 |  |  |  | 86.76 | [5 empty] | 84.05 |  |  | 91.97 |  |  |  | 1.97 |  | 1.74 | [8 empty] | 11.50 |  |  |  |  | 0.00
1985 |  |  |  | 3055.56 |  |  | 7872 |  |  |  | 411 | [10 empty] | 84.90 |  |  |  | 84.94 | [5 empty] | 84.87 |  |  | 89.86 |  |  |  | 3.18 |  | 2.79 | [8 empty] | 12.27 |  |  |  |  | 0.04
1986 |  |  |  | 2844.15 |  |  | 7405 |  |  |  | 411 | [10 empty] | 79.74 |  |  |  | 79.78 | [5 empty] | 79.00 |  |  | 84.53 |  |  |  | 4.19 |  | 3.49 | [8 empty] | 16.73 |  |  |  |  | 0.04
1987 |  |  |  | 3345.38 |  |  | 7900 |  |  |  | 440 | [10 empty] | 89.59 |  |  |  | 89.59 | [5 empty] | 86.79 |  |  | 90.18 |  |  |  | 0.58 |  | 0.52 | [8 empty] | 9.89 |  |  |  |  | 0.00
1988 |  |  |  | 2873.27 |  |  | 7451 |  |  |  | 411 | [10 empty] | 80.46 |  |  |  | 80.49 | [5 empty] | 79.59 |  |  | 84.82 |  |  |  | 5.60 |  | 4.78 | [8 empty] | 14.73 |  |  |  |  | 0.03
1989 |  |  |  | 2707.27 |  |  | 6859 |  |  |  | 411 | [10 empty] | 74.79 |  |  |  | 78.05 | [5 empty] | 75.19 |  |  | 78.30 |  |  |  | 0.67 |  | 0.52 | [8 empty] | 21.43 |  |  |  |  | 3.26
1990 |  |  |  | 2610.91 |  |  | 6751 |  |  |  | 411 | [10 empty] | 72.72 |  |  |  | 72.86 | [5 empty] | 72.52 |  |  | 77.07 |  |  |  | 6.09 |  | 4.73 | [8 empty] | 22.42 |  |  |  |  | 0.14
1991 |  |  |  | 2701.86 |  |  | 6983 |  |  |  | 411 | [10 empty] | 75.33 |  |  |  | 75.41 | [5 empty] | 75.04 |  |  | 79.71 |  |  |  | 11.29 |  | 9.60 | [8 empty] | 14.99 |  |  |  |  | 0.08
1992 |  |  |  | 2133.04 |  |  | 5871 |  |  |  | 411 | [10 empty] | 61.85 |  |  |  | 61.85 | [5 empty] | 59.09 |  |  | 66.85 |  |  |  | 16.94 |  | 12.61 | [8 empty] | 25.54 |  |  |  |  | 0.00
1993 |  |  |  | 2138.83 |  |  | 6377 |  |  |  | 411 | [10 empty] | 60.68 |  |  |  | 65.73 | [5 empty] | 59.41 |  |  | 72.80 |  |  |  | 7.71 |  | 5.49 | [8 empty] | 28.77 |  |  |  |  | 5.05
1994 |  |  |  | 398.60 |  |  | 1466 |  |  |  | 411 | [10 empty] | 16.68 |  |  |  | 16.68 | [5 empty] | 11.07 |  |  | 16.74 |  |  |  | 18.79 |  | 3.86 | [8 empty] | 79.46 |  |  |  |  | 0.00
1995 |  |  |  | 2205.78 |  |  | 6846 |  |  |  | 411 | [10 empty] | 93.58 |  |  |  | 93.58 | [5 empty] | 61.27 |  |  | 78.15 |  |  |  | 2.08 |  | 1.99 | [8 empty] | 4.43 |  |  |  |  | 0.00
1996 |  |  |  | 1946.17 |  |  | 6243 |  |  |  | 411 | [10 empty] | 65.47 |  |  |  | 66.30 | [5 empty] | 53.91 |  |  | 71.07 |  |  |  | 3.53 |  | 2.43 | [8 empty] | 31.27 |  |  |  |  | 0.84
1997 |  |  |  | 1157.94 |  |  | 3955 |  |  |  | 411 | [10 empty] | 40.64 |  |  |  | 53.44 | [5 empty] | 32.16 |  |  | 45.15 |  |  |  | 3.35 |  | 1.85 | [8 empty] | 44.70 |  |  |  |  | 12.80
1998 |  |  |  | 2655.63 |  |  | 8029 |  |  |  | 411 | [10 empty] | 74.46 |  |  |  | 83.64 | [5 empty] | 73.76 |  |  | 91.66 |  |  |  | 8.88 |  | 8.15 | [8 empty] | 8.22 |  |  |  |  | 9.18
1999 |  |  |  | 1272.59 |  |  | 4423 |  |  |  | 411 | [10 empty] | 36.30 |  |  |  | 48.99 | [5 empty] | 35.35 |  |  | 50.49 |  |  |  | 17.19 |  | 10.17 | [8 empty] | 40.84 |  |  |  |  | 12.69
2000 |  |  |  | 2430.51 |  |  | 7626 |  |  |  | 411 | [10 empty] | 68.16 |  |  |  | 83.38 | [5 empty] | 67.32 |  |  | 86.82 |  |  |  | 2.56 |  | 2.19 | [8 empty] | 14.43 |  |  |  |  | 15.22
2001 |  |  |  | 1722.31 |  |  | 6574 |  |  |  | 411 | [10 empty] | 49.08 |  |  |  | 84.74 | [5 empty] | 47.84 |  |  | 75.05 |  |  |  | 1.21 |  | 1.03 | [8 empty] | 14.22 |  |  |  |  | 35.67
2002 |  |  |  | 1738.75 |  |  | 5564 |  |  |  | 411 | [10 empty] | 48.66 |  |  |  | 83.24 | [5 empty] | 48.29 |  |  | 63.52 |  |  |  | 0.30 |  | 0.25 | [8 empty] | 16.51 |  |  |  |  | 34.58
2003 |  |  |  | 1866.10 |  |  | 5459 |  |  |  | 411 | [10 empty] | 52.04 |  |  |  | 66.40 | [5 empty] | 51.83 |  |  | 62.32 |  |  |  | 0.54 |  | 0.36 | [8 empty] | 33.24 |  |  |  |  | 14.37
2004 |  |  |  | 1787.07 |  |  | 5731 |  |  |  | 411 | [10 empty] | 49.92 |  |  |  | 73.84 | [5 empty] | 49.50 |  |  | 65.24 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 26.12 |  |  |  |  | 23.93
2005 |  |  |  | 2889.18 |  |  | 7379 |  |  |  | 411 | [10 empty] | 78.59 |  |  |  | 84.24 | [5 empty] | 80.25 |  |  | 84.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.76 |  |  |  |  | 5.65
2006 |  |  |  | 2640.13 |  |  | 7597 |  |  |  | 411 | [10 empty] | 71.98 |  |  |  | 85.73 | [5 empty] | 73.33 |  |  | 86.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.27 |  |  |  |  | 13.75
2007 |  |  |  | 2508.92 |  |  | 7474 |  |  |  | 411 | [10 empty] | 70.10 |  |  |  | 85.69 | [5 empty] | 69.69 |  |  | 85.32 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 14.14 |  |  |  |  | 15.59
2008 |  |  |  | 2554.70 |  |  | 7762 |  |  |  | 411 | [10 empty] | 89.13 |  |  |  | 89.92 | [5 empty] | 70.76 |  |  | 88.37 |  |  |  | 1.32 |  | 1.20 | [8 empty] | 8.88 |  |  |  |  | 0.79
2009 |  |  |  | 2384.55 |  |  | 6872 |  |  |  | 411 | [10 empty] | 79.44 |  |  |  | 80.28 | [5 empty] | 66.23 |  |  | 78.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.72 |  |  |  |  | 0.84
2010 |  |  |  | 2531.18 |  |  | 7619 |  |  |  | 411 | [10 empty] | 90.18 |  |  |  | 90.41 | [5 empty] | 70.30 |  |  | 86.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.59 |  |  |  |  | 0.24
2011 |  |  |  | 2501.98 |  |  | 7752 |  |  |  | 411 | [10 empty] | 83.07 |  |  |  | 83.63 | [5 empty] | 69.50 |  |  | 88.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.37 |  |  |  |  | 0.56
2012 |  |  |  | 2192.07 |  |  | 7775 |  |  |  | 411 | [10 empty] | 81.85 |  |  |  | 81.85 | [5 empty] | 60.72 |  |  | 88.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.14 |  |  |  |  | 0.00
2013 |  |  |  | 2412.70 |  |  | 7233 |  |  |  | 411 | [10 empty] | 82.80 |  |  |  | 82.80 | [5 empty] | 67.01 |  |  | 82.57 |  |  |  | 1.51 |  | 1.27 | [8 empty] | 15.93 |  |  |  |  | 0.00
2014 |  |  |  | 2596.45 |  |  | 7823 |  |  |  | 411 | [10 empty] | 89.32 |  |  |  | 90.15 | [5 empty] | 72.11 |  |  | 89.29 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 9.82 |  |  |  |  | 0.83
2015 |  |  |  | 1463.78 |  |  | 5450 |  |  |  | 411 | [10 empty] | 85.32 |  |  |  | 85.32 | [5 empty] | 40.66 |  |  | 62.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.68 |  |  |  |  | 0.00
2016 |  |  |  | 2053.14 |  |  | 6416 |  |  |  | 411 | [10 empty] | 79.35 |  |  |  | 79.79 | [5 empty] | 56.87 |  |  | 73.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.21 |  |  |  |  | 0.43
2017 |  |  |  | 1787.16 |  |  | 5615 |  |  |  | 411 | [10 empty] | 83.48 |  |  |  | 83.48 | [5 empty] | 49.64 |  |  | 64.10 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 16.45 |  |  |  |  | 0.00
2018 |  |  |  | 2765.53 |  |  | 7437 |  |  |  | 411 | [10 empty] | 84.10 |  |  |  | 84.42 | [5 empty] | 76.81 |  |  | 84.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.58 |  |  |  |  | 0.32
2019 |  |  |  | 670.53 |  |  | 1904 |  |  |  | 411 | [10 empty] | 20.38 |  |  |  | 21.54 | [5 empty] | 18.62 |  |  | 21.74 |  |  |  | 8.76 |  | 2.07 | [8 empty] | 76.39 |  |  |  |  | 1.17
2020 |  |  |  | 1890.68 |  |  | 7188 |  |  |  | 411 | [10 empty] | 86.71 |  |  |  | 86.71 | [5 empty] | 52.37 |  |  | 81.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.29 |  |  |  |  | 0.01
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 68
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1215 | [14 empty] | 1481
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 54
E. |  | Testing of plant systems or components | [35 empty] | 7
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 107
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 29
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 217 | [19 empty] | 244
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Z. |  | Other | [39 empty] | 0
Subtotal | [22 empty] | 1215 | [10 empty] | 217 |  |  |  | 1649 |  |  |  | 73 | [11 empty] | 275
Total | [22 empty] | 1432 | [14 empty] | 1997
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 39
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 16
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 68
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January, March, May, November. Additional electricity generation amounted to 8667 MWh. The unit was in the intermediate outage from 2020.08.15 to 2020.10.01. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-3
2020 Operating Experience
RU-32 | [8 empty] | KOLA-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-04-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-03-24
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1982-12-03
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2527.89 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.99 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.81 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 17.19 %
Load Factor (LF) | [18 empty] | : | 70.02 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.82 %
Operating Factor (OF) | [18 empty] | : | 81.01 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1668 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 2.06 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 239.78 | 276.68 |  |  |  | 302.87 |  | 232.13 | [8 empty] | 38.21 |  |  | 0.00 | [6 empty] | 58.30 |  | 269.96 |  |  |  | 298.64 |  |  | 291.63 |  |  | 230.84 | [9 empty] | 288.87 |  |  | 2527.89
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 94.87 | [8 empty] | 43.81 |  |  | 0.01 | [6 empty] | 45.33 |  | 99.97 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.93 |  |  | 81.99
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 48.39 |  |  | 0.01 | [6 empty] | 45.37 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.81
LF [%] |  |  |  |  | 78.42 | 96.72 |  |  |  | 99.05 |  | 78.44 | [8 empty] | 12.50 |  |  | 0.00 | [6 empty] | 19.06 |  | 88.29 |  |  |  | 100.92 |  |  | 95.37 |  |  | 78.01 | [9 empty] | 94.47 |  |  | 70.02
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 27.02 |  |  | 0.00 | [6 empty] | 45.56 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.01
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 51.61 |  |  | 99.99 | [6 empty] | 54.63 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 17.19
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 5.13 | [8 empty] | 4.58 |  |  | 0.00 | [6 empty] | 0.04 |  | 0.03 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.07 |  |  | 0.82
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 98492.71 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.38 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.41 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.02 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.36 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.62 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.02 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 5.95 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.3 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1982 |  |  |  | 1891.17 |  |  | 7252 |  |  |  | 411 | [10 empty] | 99.35 |  |  |  | 99.38 | [5 empty] | 98.74 |  |  | 100.00 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 0.54 |  |  |  |  | 0.03
1983 |  |  |  | 2459.86 |  |  | 6818 |  |  |  | 411 | [10 empty] | 71.98 |  |  |  | 71.99 | [5 empty] | 68.32 |  |  | 77.83 |  |  |  | 3.90 |  | 2.92 | [8 empty] | 25.09 |  |  |  |  | 0.01
1984 |  |  |  | 2830.67 |  |  | 7610 |  |  |  | 411 | [10 empty] | 82.71 |  |  |  | 82.71 | [5 empty] | 78.41 |  |  | 86.63 |  |  |  | 1.76 |  | 1.48 | [8 empty] | 15.80 |  |  |  |  | 0.01
1985 |  |  |  | 2972.56 |  |  | 7814 |  |  |  | 411 | [10 empty] | 86.68 |  |  |  | 86.77 | [5 empty] | 82.56 |  |  | 89.20 |  |  |  | 2.25 |  | 2.00 | [8 empty] | 11.23 |  |  |  |  | 0.09
1986 |  |  |  | 2627.25 |  |  | 7244 |  |  |  | 411 | [10 empty] | 74.11 |  |  |  | 74.11 | [5 empty] | 72.97 |  |  | 82.69 |  |  |  | 16.48 |  | 14.62 | [8 empty] | 11.27 |  |  |  |  | 0.00
1987 |  |  |  | 2837.81 |  |  | 7024 |  |  |  | 440 | [10 empty] | 74.79 |  |  |  | 74.79 | [5 empty] | 73.63 |  |  | 80.18 |  |  |  | 6.83 |  | 5.49 | [8 empty] | 19.73 |  |  |  |  | 0.00
1988 |  |  |  | 2933.19 |  |  | 7913 |  |  |  | 411 | [10 empty] | 81.43 |  |  |  | 81.52 | [5 empty] | 81.25 |  |  | 90.08 |  |  |  | 4.73 |  | 4.05 | [8 empty] | 14.44 |  |  |  |  | 0.08
1989 |  |  |  | 3186.68 |  |  | 8047 |  |  |  | 411 | [10 empty] | 87.85 |  |  |  | 90.50 | [5 empty] | 88.51 |  |  | 91.86 |  |  |  | 0.81 |  | 0.74 | [8 empty] | 8.76 |  |  |  |  | 2.65
1990 |  |  |  | 3256.91 |  |  | 8022 |  |  |  | 411 | [10 empty] | 89.72 |  |  |  | 89.77 | [5 empty] | 90.46 |  |  | 91.58 |  |  |  | 0.95 |  | 0.87 | [8 empty] | 9.37 |  |  |  |  | 0.05
1991 |  |  |  | 2935.21 |  |  | 7188 |  |  |  | 411 | [10 empty] | 79.78 |  |  |  | 79.78 | [5 empty] | 81.53 |  |  | 82.05 |  |  |  | 2.74 |  | 2.25 | [8 empty] | 17.97 |  |  |  |  | 0.00
1992 |  |  |  | 2806.37 |  |  | 7396 |  |  |  | 411 | [10 empty] | 87.75 |  |  |  | 87.95 | [5 empty] | 77.74 |  |  | 84.21 |  |  |  | 2.36 |  | 2.13 | [8 empty] | 9.93 |  |  |  |  | 0.20
1993 |  |  |  | 2548.00 |  |  | 6833 |  |  |  | 411 | [10 empty] | 70.46 |  |  |  | 81.91 | [5 empty] | 70.77 |  |  | 78.00 |  |  |  | 1.41 |  | 1.17 | [8 empty] | 16.93 |  |  |  |  | 11.45
1994 |  |  |  | 2466.01 |  |  | 6373 |  |  |  | 411 | [10 empty] | 70.82 |  |  |  | 70.90 | [5 empty] | 68.49 |  |  | 72.75 |  |  |  | 10.76 |  | 8.55 | [8 empty] | 20.55 |  |  |  |  | 0.08
1995 |  |  |  | 2526.12 |  |  | 7083 |  |  |  | 411 | [10 empty] | 80.64 |  |  |  | 81.00 | [5 empty] | 70.16 |  |  | 80.86 |  |  |  | 0.82 |  | 0.67 | [8 empty] | 18.33 |  |  |  |  | 0.36
1996 |  |  |  | 2327.31 |  |  | 6928 |  |  |  | 411 | [10 empty] | 79.77 |  |  |  | 79.77 | [5 empty] | 64.46 |  |  | 78.87 |  |  |  | 5.33 |  | 4.49 | [8 empty] | 15.74 |  |  |  |  | 0.00
1997 |  |  |  | 2340.50 |  |  | 7114 |  |  |  | 411 | [10 empty] | 74.96 |  |  |  | 78.46 | [5 empty] | 65.01 |  |  | 81.21 |  |  |  | 0.56 |  | 0.44 | [8 empty] | 21.11 |  |  |  |  | 3.49
1998 |  |  |  | 2006.34 |  |  | 6705 |  |  |  | 411 | [10 empty] | 56.35 |  |  |  | 86.29 | [5 empty] | 55.73 |  |  | 76.54 |  |  |  | 4.27 |  | 3.85 | [8 empty] | 9.86 |  |  |  |  | 29.94
1999 |  |  |  | 2140.57 |  |  | 7040 |  |  |  | 411 | [10 empty] | 59.90 |  |  |  | 72.59 | [5 empty] | 59.45 |  |  | 80.37 |  |  |  | 9.77 |  | 7.86 | [8 empty] | 19.55 |  |  |  |  | 12.69
2000 |  |  |  | 2244.74 |  |  | 7731 |  |  |  | 411 | [10 empty] | 62.46 |  |  |  | 87.91 | [5 empty] | 62.18 |  |  | 88.01 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 12.02 |  |  |  |  | 25.46
2001 |  |  |  | 2543.29 |  |  | 7057 |  |  |  | 411 | [10 empty] | 70.64 |  |  |  | 85.28 | [5 empty] | 70.64 |  |  | 80.56 |  |  |  | 1.10 |  | 0.95 | [8 empty] | 13.77 |  |  |  |  | 14.64
2002 |  |  |  | 2742.35 |  |  | 7909 |  |  |  | 411 | [10 empty] | 75.89 |  |  |  | 91.39 | [5 empty] | 76.17 |  |  | 90.29 |  |  |  | 0.43 |  | 0.40 | [8 empty] | 8.21 |  |  |  |  | 15.51
2003 |  |  |  | 2740.72 |  |  | 7335 |  |  |  | 411 | [10 empty] | 75.61 |  |  |  | 83.69 | [5 empty] | 76.12 |  |  | 83.73 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 16.26 |  |  |  |  | 8.08
2004 |  |  |  | 2816.85 |  |  | 7688 |  |  |  | 411 | [10 empty] | 77.37 |  |  |  | 88.10 | [5 empty] | 78.02 |  |  | 87.52 |  |  |  | 0.57 |  | 0.51 | [8 empty] | 11.39 |  |  |  |  | 10.73
2005 |  |  |  | 2059.39 |  |  | 7672 |  |  |  | 411 | [10 empty] | 57.64 |  |  |  | 88.49 | [5 empty] | 57.19 |  |  | 87.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.51 |  |  |  |  | 30.85
2006 |  |  |  | 2294.60 |  |  | 7436 |  |  |  | 411 | [10 empty] | 64.00 |  |  |  | 89.99 | [5 empty] | 63.73 |  |  | 84.89 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 9.97 |  |  |  |  | 25.99
2007 |  |  |  | 1815.27 |  |  | 6506 |  |  |  | 411 | [10 empty] | 50.72 |  |  |  | 82.86 | [5 empty] | 50.42 |  |  | 74.27 |  |  |  | 1.49 |  | 1.25 | [8 empty] | 15.89 |  |  |  |  | 32.14
2008 |  |  |  | 1876.73 |  |  | 7405 |  |  |  | 411 | [10 empty] | 83.82 |  |  |  | 83.82 | [5 empty] | 51.98 |  |  | 84.30 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 16.15 |  |  |  |  | 0.00
2009 |  |  |  | 2050.45 |  |  | 7340 |  |  |  | 411 | [10 empty] | 83.13 |  |  |  | 83.85 | [5 empty] | 56.95 |  |  | 83.79 |  |  |  | 0.10 |  | 0.08 | [8 empty] | 16.07 |  |  |  |  | 0.71
2010 |  |  |  | 1979.23 |  |  | 6009 |  |  |  | 411 | [10 empty] | 71.48 |  |  |  | 71.48 | [5 empty] | 54.97 |  |  | 68.60 |  |  |  | 1.03 |  | 0.75 | [8 empty] | 27.78 |  |  |  |  | 0.00
2011 |  |  |  | 2288.62 |  |  | 6405 |  |  |  | 411 | [10 empty] | 71.67 |  |  |  | 71.67 | [5 empty] | 63.57 |  |  | 73.12 |  |  |  | 2.56 |  | 1.89 | [8 empty] | 26.45 |  |  |  |  | 0.00
2012 |  |  |  | 2226.17 |  |  | 6701 |  |  |  | 411 | [10 empty] | 78.13 |  |  |  | 78.13 | [5 empty] | 61.66 |  |  | 76.29 |  |  |  | 1.74 |  | 1.38 | [8 empty] | 20.49 |  |  |  |  | 0.00
2013 |  |  |  | 2264.33 |  |  | 6396 |  |  |  | 411 | [10 empty] | 73.80 |  |  |  | 73.80 | [5 empty] | 62.89 |  |  | 73.01 |  |  |  | 2.75 |  | 2.09 | [8 empty] | 24.11 |  |  |  |  | 0.00
2014 |  |  |  | 2636.67 |  |  | 7712 |  |  |  | 411 | [10 empty] | 87.60 |  |  |  | 87.60 | [5 empty] | 73.23 |  |  | 88.03 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 12.38 |  |  |  |  | 0.00
2015 |  |  |  | 2581.99 |  |  | 7364 |  |  |  | 411 | [10 empty] | 84.12 |  |  |  | 84.12 | [5 empty] | 71.71 |  |  | 84.06 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 15.50 |  |  |  |  | 0.00
2016 |  |  |  | 2583.96 |  |  | 6573 |  |  |  | 411 | [10 empty] | 86.16 |  |  |  | 86.29 | [5 empty] | 71.57 |  |  | 74.83 |  |  |  | 0.41 |  | 0.36 | [8 empty] | 13.36 |  |  |  |  | 0.13
2017 |  |  |  | 2679.44 |  |  | 7494 |  |  |  | 411 | [10 empty] | 84.70 |  |  |  | 84.70 | [5 empty] | 74.42 |  |  | 85.55 |  |  |  | 0.31 |  | 0.27 | [8 empty] | 15.03 |  |  |  |  | 0.00
2018 |  |  |  | 3036.60 |  |  | 7433 |  |  |  | 411 | [10 empty] | 85.34 |  |  |  | 85.34 | [5 empty] | 84.34 |  |  | 84.85 |  |  |  | 2.24 |  | 2.62 | [8 empty] | 12.04 |  |  |  |  | 0.00
2019 |  |  |  | 2759.12 |  |  | 7606 |  |  |  | 411 | [10 empty] | 85.71 |  |  |  | 86.49 | [5 empty] | 76.63 |  |  | 86.83 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 13.47 |  |  |  |  | 0.78
2020 |  |  |  | 2527.89 |  |  | 7116 |  |  |  | 411 | [10 empty] | 81.99 |  |  |  | 82.81 | [5 empty] | 70.02 |  |  | 81.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.19 |  |  |  |  | 0.82
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1982 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 67
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1509 | [14 empty] | 1256
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 64
E. |  | Testing of plant systems or components | [35 empty] | 10 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 51
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 159 | [19 empty] | 107
L. |  | Human factor related | [39 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 3
Subtotal | [22 empty] | 1509 | [10 empty] | 159 |  |  |  | 1330 |  |  |  | 73 | [11 empty] | 159
Total | [22 empty] | 1668 | [14 empty] | 1562
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1982 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 23
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 8
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [37 empty] | 67
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-April, August-December. Additional electricity generation amounted to 36430 MWh. The unit was in the intermediate outage from 2020.05.16 to 2020.07.17. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-4
2020 Operating Experience
RU-33 | [8 empty] | KOLA-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-08-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-10-11
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-12-06
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 1996.91 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.37 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 80.37 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 19.63 %
Load Factor (LF) | [18 empty] | : | 55.31 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 68.21 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2792 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0.43 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 316.21 | 279.35 |  |  |  | 266.65 |  | 133.90 | [8 empty] | 107.80 |  |  | 0.00 | [6 empty] | 0.00 |  | 93.42 |  |  |  | 286.09 |  |  | 265.42 |  |  | 0.00 | [9 empty] | 248.07 |  |  | 1996.91
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 33.34 | [6 empty] | 0.01 |  | 32.71 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.37
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 33.34 | [6 empty] | 0.01 |  | 32.71 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.37
LF [%] |  |  |  |  | 103.41 | 97.65 |  |  |  | 87.20 |  | 45.25 | [8 empty] | 35.25 |  |  | 0.00 | [6 empty] | 0.00 |  | 30.55 |  |  |  | 96.68 |  |  | 86.80 |  |  | 0.00 | [9 empty] | 81.13 |  |  | 55.31
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 76.61 |  |  | 0.00 | [6 empty] | 0.00 |  | 55.11 |  |  |  | 100.00 |  |  | 100.00 |  |  | 1.39 | [9 empty] | 85.22 |  |  | 68.21
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 66.66 | [6 empty] | 99.99 |  | 67.29 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 19.63
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 93758.76 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.65 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.49 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.24 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.32 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.44 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.14 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 5.83 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.69 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 249.38 |  |  | 1605 |  |  |  | 411 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 55.09 |  |  | 98.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 2585.77 |  |  | 7751 |  |  |  | 411 | [10 empty] | 78.18 |  |  |  | 78.19 | [5 empty] | 71.82 |  |  | 88.48 |  |  |  | 3.31 |  | 2.68 | [8 empty] | 19.14 |  |  |  |  | 0.01
1986 |  |  |  | 2690.18 |  |  | 7230 |  |  |  | 411 | [10 empty] | 72.36 |  |  |  | 72.36 | [5 empty] | 74.72 |  |  | 82.53 |  |  |  | 6.11 |  | 4.71 | [8 empty] | 22.93 |  |  |  |  | 0.00
1987 |  |  |  | 3341.17 |  |  | 7861 |  |  |  | 440 | [10 empty] | 85.50 |  |  |  | 85.50 | [5 empty] | 86.68 |  |  | 89.74 |  |  |  | 0.91 |  | 0.79 | [8 empty] | 13.72 |  |  |  |  | 0.00
1988 |  |  |  | 3124.21 |  |  | 7762 |  |  |  | 411 | [10 empty] | 84.95 |  |  |  | 84.96 | [5 empty] | 86.54 |  |  | 88.37 |  |  |  | 4.04 |  | 3.58 | [8 empty] | 11.47 |  |  |  |  | 0.01
1989 |  |  |  | 3111.51 |  |  | 7793 |  |  |  | 411 | [10 empty] | 85.77 |  |  |  | 87.57 | [5 empty] | 86.42 |  |  | 88.96 |  |  |  | 1.33 |  | 1.18 | [8 empty] | 11.25 |  |  |  |  | 1.80
1990 |  |  |  | 2930.40 |  |  | 7142 |  |  |  | 411 | [10 empty] | 80.24 |  |  |  | 80.28 | [5 empty] | 81.39 |  |  | 81.53 |  |  |  | 0.76 |  | 0.62 | [8 empty] | 19.10 |  |  |  |  | 0.05
1991 |  |  |  | 2790.49 |  |  | 7429 |  |  |  | 411 | [10 empty] | 76.70 |  |  |  | 76.70 | [5 empty] | 77.51 |  |  | 84.81 |  |  |  | 8.47 |  | 7.09 | [8 empty] | 16.21 |  |  |  |  | 0.00
1992 |  |  |  | 2764.94 |  |  | 7253 |  |  |  | 411 | [10 empty] | 79.99 |  |  |  | 80.51 | [5 empty] | 76.60 |  |  | 82.58 |  |  |  | 2.77 |  | 2.29 | [8 empty] | 17.19 |  |  |  |  | 0.52
1993 |  |  |  | 2826.99 |  |  | 8247 |  |  |  | 411 | [10 empty] | 79.00 |  |  |  | 92.43 | [5 empty] | 78.52 |  |  | 94.14 |  |  |  | 5.98 |  | 5.88 | [8 empty] | 1.69 |  |  |  |  | 13.43
1994 |  |  |  | 1939.77 |  |  | 5915 |  |  |  | 411 | [10 empty] | 55.77 |  |  |  | 62.72 | [5 empty] | 53.88 |  |  | 67.52 |  |  |  | 20.29 |  | 15.97 | [8 empty] | 21.31 |  |  |  |  | 6.95
1995 |  |  |  | 2288.81 |  |  | 7022 |  |  |  | 411 | [10 empty] | 73.83 |  |  |  | 73.83 | [5 empty] | 63.57 |  |  | 80.16 |  |  |  | 7.04 |  | 5.59 | [8 empty] | 20.57 |  |  |  |  | 0.00
1996 |  |  |  | 2537.72 |  |  | 7792 |  |  |  | 411 | [10 empty] | 84.09 |  |  |  | 84.09 | [5 empty] | 70.29 |  |  | 88.71 |  |  |  | 4.39 |  | 3.86 | [8 empty] | 12.05 |  |  |  |  | 0.00
1997 |  |  |  | 2271.67 |  |  | 6848 |  |  |  | 411 | [10 empty] | 74.56 |  |  |  | 76.16 | [5 empty] | 63.10 |  |  | 78.17 |  |  |  | 6.93 |  | 5.67 | [8 empty] | 18.18 |  |  |  |  | 1.59
1998 |  |  |  | 1927.55 |  |  | 6336 |  |  |  | 411 | [10 empty] | 49.19 |  |  |  | 69.38 | [5 empty] | 53.54 |  |  | 72.33 |  |  |  | 8.64 |  | 6.56 | [8 empty] | 24.05 |  |  |  |  | 20.20
1999 |  |  |  | 2567.48 |  |  | 7193 |  |  |  | 411 | [10 empty] | 71.16 |  |  |  | 82.00 | [5 empty] | 71.31 |  |  | 82.11 |  |  |  | 1.51 |  | 1.26 | [8 empty] | 16.75 |  |  |  |  | 10.84
2000 |  |  |  | 2177.50 |  |  | 7096 |  |  |  | 411 | [10 empty] | 60.44 |  |  |  | 86.31 | [5 empty] | 60.31 |  |  | 80.78 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 13.63 |  |  |  |  | 25.86
2001 |  |  |  | 2447.14 |  |  | 7149 |  |  |  | 411 | [10 empty] | 67.98 |  |  |  | 87.38 | [5 empty] | 67.97 |  |  | 81.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.62 |  |  |  |  | 19.40
2002 |  |  |  | 2601.71 |  |  | 7281 |  |  |  | 411 | [10 empty] | 71.52 |  |  |  | 79.71 | [5 empty] | 72.26 |  |  | 83.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.29 |  |  |  |  | 8.19
2003 |  |  |  | 2480.80 |  |  | 6663 |  |  |  | 411 | [10 empty] | 68.69 |  |  |  | 90.88 | [5 empty] | 68.90 |  |  | 76.06 |  |  |  | 1.45 |  | 1.34 | [8 empty] | 7.78 |  |  |  |  | 22.20
2004 |  |  |  | 2391.59 |  |  | 7863 |  |  |  | 411 | [10 empty] | 66.38 |  |  |  | 86.78 | [5 empty] | 66.24 |  |  | 89.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.22 |  |  |  |  | 20.40
2005 |  |  |  | 2231.75 |  |  | 7879 |  |  |  | 411 | [10 empty] | 62.10 |  |  |  | 90.21 | [5 empty] | 61.98 |  |  | 89.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.79 |  |  |  |  | 28.11
2006 |  |  |  | 2573.11 |  |  | 7217 |  |  |  | 411 | [10 empty] | 71.26 |  |  |  | 84.11 | [5 empty] | 71.47 |  |  | 82.39 |  |  |  | 0.13 |  | 0.11 | [8 empty] | 15.79 |  |  |  |  | 12.85
2007 |  |  |  | 2584.08 |  |  | 7640 |  |  |  | 411 | [10 empty] | 71.52 |  |  |  | 89.77 | [5 empty] | 71.77 |  |  | 87.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.23 |  |  |  |  | 18.25
2008 |  |  |  | 2793.49 |  |  | 7794 |  |  |  | 411 | [10 empty] | 85.15 |  |  |  | 85.20 | [5 empty] | 77.38 |  |  | 88.73 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 14.76 |  |  |  |  | 0.04
2009 |  |  |  | 2468.01 |  |  | 7538 |  |  |  | 411 | [10 empty] | 83.73 |  |  |  | 83.74 | [5 empty] | 68.55 |  |  | 86.05 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 16.25 |  |  |  |  | 0.02
2010 |  |  |  | 2956.73 |  |  | 7332 |  |  |  | 411 | [10 empty] | 84.73 |  |  |  | 84.73 | [5 empty] | 82.12 |  |  | 83.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.27 |  |  |  |  | 0.00
2011 |  |  |  | 2558.01 |  |  | 6803 |  |  |  | 411 | [10 empty] | 79.30 |  |  |  | 79.33 | [5 empty] | 71.06 |  |  | 77.67 |  |  |  | 5.98 |  | 5.05 | [8 empty] | 15.62 |  |  |  |  | 0.03
2012 |  |  |  | 2601.69 |  |  | 7459 |  |  |  | 411 | [10 empty] | 84.75 |  |  |  | 84.75 | [5 empty] | 72.06 |  |  | 84.92 |  |  |  | 0.11 |  | 0.09 | [8 empty] | 15.16 |  |  |  |  | 0.00
2013 |  |  |  | 2572.70 |  |  | 7084 |  |  |  | 411 | [10 empty] | 83.22 |  |  |  | 83.22 | [5 empty] | 71.46 |  |  | 80.87 |  |  |  | 0.26 |  | 0.22 | [8 empty] | 16.56 |  |  |  |  | 0.00
2014 |  |  |  | 2488.19 |  |  | 6241 |  |  |  | 411 | [10 empty] | 70.91 |  |  |  | 70.91 | [5 empty] | 69.10 |  |  | 71.24 |  |  |  | 2.61 |  | 1.90 | [8 empty] | 27.18 |  |  |  |  | 0.00
2015 |  |  |  | 2506.63 |  |  | 6870 |  |  |  | 411 | [10 empty] | 87.25 |  |  |  | 87.25 | [5 empty] | 69.62 |  |  | 78.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.75 |  |  |  |  | 0.00
2016 |  |  |  | 2425.95 |  |  | 6422 |  |  |  | 411 | [10 empty] | 83.44 |  |  |  | 83.44 | [5 empty] | 67.20 |  |  | 73.11 |  |  |  | 0.86 |  | 0.73 | [8 empty] | 15.83 |  |  |  |  | 0.00
2017 |  |  |  | 2994.93 |  |  | 7633 |  |  |  | 411 | [10 empty] | 84.56 |  |  |  | 84.56 | [5 empty] | 83.18 |  |  | 87.13 |  |  |  | 3.60 |  | 3.16 | [8 empty] | 12.28 |  |  |  |  | 0.00
2018 |  |  |  | 3058.96 |  |  | 7464 |  |  |  | 411 | [10 empty] | 84.97 |  |  |  | 84.97 | [5 empty] | 84.96 |  |  | 85.21 |  |  |  | 0.57 |  | 0.49 | [8 empty] | 14.54 |  |  |  |  | 0.00
2019 |  |  |  | 3188.15 |  |  | 7831 |  |  |  | 411 | [10 empty] | 87.41 |  |  |  | 87.48 | [5 empty] | 88.55 |  |  | 89.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.52 |  |  |  |  | 0.07
2020 |  |  |  | 1996.91 |  |  | 5992 |  |  |  | 411 | [10 empty] | 80.37 |  |  |  | 80.37 | [5 empty] | 55.31 |  |  | 68.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.63 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 54
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1558 | [14 empty] | 1149 |  |  |  | 16
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 72
E. |  | Testing of plant systems or components | [35 empty] | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 42
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 1100 | [19 empty] | 167
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
Z. |  | Other | [39 empty] | 0
Subtotal | [22 empty] | 1558 | [10 empty] | 1100 |  |  |  | 1226 |  |  |  | 73 | [11 empty] | 209
Total | [22 empty] | 2658 | [14 empty] | 1508
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 13
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
16. |  |  | Steam generation systems | [34 empty] | 10
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 14
Total | [37 empty] | 58
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-March, August-October, December. Additional electricity generation amounted to 31747 MWh. The unit was in the intermediate outage from 2020.06.11 to 2020.08.14. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-1
2020 Operating Experience
RU-17 | [8 empty] | KURSK-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-06-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-12-19
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-10-12
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1693 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 11.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 138 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5208.97 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2 %
Energy Availability Factor (EAF) | [18 empty] | : | 63.74 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.33 %
Unit Capability Factor (UCF) | [18 empty] | : | 65.06 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 33.61 %
Load Factor (LF) | [18 empty] | : | 64.11 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.32 %
Operating Factor (OF) | [18 empty] | : | 65.81 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3003 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 60.66 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 527.03 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 124.25 |  |  | 528.72 | [6 empty] | 648.22 |  | 655.42 |  |  |  | 649.60 |  |  | 694.74 |  |  | 669.96 | [9 empty] | 711.02 |  |  | 5208.97
EAF [%] |  |  |  |  | 74.61 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.58 |  |  | 80.43 | [6 empty] | 94.25 |  | 95.30 |  |  |  | 97.33 |  |  | 100.00 |  |  | 99.96 | [9 empty] | 100.00 |  |  | 63.74
UCF [%] |  |  |  |  | 74.61 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.71 |  |  | 83.79 | [6 empty] | 99.13 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 65.06
LF [%] |  |  |  |  | 76.58 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.05 |  |  | 79.39 | [6 empty] | 94.19 |  | 95.24 |  |  |  | 97.54 |  |  | 100.95 |  |  | 100.60 | [9 empty] | 103.32 |  |  | 64.11
OF [%] |  |  |  |  | 77.82 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.58 |  |  | 85.83 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 65.81
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 16.21 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 2.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 16.21 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 1.33
PUF [%] |  |  |  |  | 25.39 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 80.29 |  |  | 0.00 | [6 empty] | 0.87 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 33.61
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.13 |  |  | 3.36 | [6 empty] | 4.88 |  | 4.70 |  |  |  | 2.67 |  |  | 0.00 |  |  | 0.03 | [9 empty] | 0.00 |  |  | 1.32
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 225409 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.41 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 63.84 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.51 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 65.53 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 29.96 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 63.83 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.69 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.09 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 3644.87 |  |  | 6899 |  |  |  | 925 | [10 empty] | 79.11 |  |  |  | 79.11 | [5 empty] | 71.43 |  |  | 85.91 |  |  |  | 9.31 |  | 8.12 | [8 empty] | 12.77 |  |  |  |  | 0.00
1978 |  |  |  | 5058.11 |  |  | 7573 |  |  |  | 925 | [10 empty] | 63.00 |  |  |  | 63.00 | [5 empty] | 62.42 |  |  | 86.45 |  |  |  | 17.07 |  | 12.96 | [8 empty] | 24.04 |  |  |  |  | 0.00
1979 |  |  |  | 5930.25 |  |  | 7528 |  |  |  | 925 | [10 empty] | 73.09 |  |  |  | 73.93 | [5 empty] | 73.19 |  |  | 85.94 |  |  |  | 14.94 |  | 12.98 | [8 empty] | 13.08 |  |  |  |  | 0.84
1980 |  |  |  | 6477.67 |  |  | 7669 |  |  |  | 925 | [10 empty] | 79.69 |  |  |  | 79.92 | [5 empty] | 79.72 |  |  | 87.31 |  |  |  | 7.39 |  | 6.38 | [8 empty] | 13.70 |  |  |  |  | 0.23
1981 |  |  |  | 6132.76 |  |  | 7885 |  |  |  | 925 | [10 empty] | 76.36 |  |  |  | 76.36 | [5 empty] | 75.69 |  |  | 90.01 |  |  |  | 12.25 |  | 10.66 | [8 empty] | 12.98 |  |  |  |  | 0.00
1982 |  |  |  | 7010.42 |  |  | 7788 |  |  |  | 925 | [10 empty] | 85.71 |  |  |  | 85.71 | [5 empty] | 86.52 |  |  | 88.90 |  |  |  | 2.73 |  | 2.40 | [8 empty] | 11.89 |  |  |  |  | 0.00
1983 |  |  |  | 6720.27 |  |  | 7456 |  |  |  | 925 | [10 empty] | 82.16 |  |  |  | 82.20 | [5 empty] | 82.94 |  |  | 85.11 |  |  |  | 1.94 |  | 1.63 | [8 empty] | 16.17 |  |  |  |  | 0.04
1984 |  |  |  | 6659.97 |  |  | 7369 |  |  |  | 925 | [10 empty] | 81.37 |  |  |  | 81.37 | [5 empty] | 81.97 |  |  | 83.89 |  |  |  | 2.66 |  | 2.22 | [8 empty] | 16.41 |  |  |  |  | 0.00
1985 |  |  |  | 6346.78 |  |  | 7186 |  |  |  | 925 | [10 empty] | 76.81 |  |  |  | 76.86 | [5 empty] | 78.33 |  |  | 82.03 |  |  |  | 3.99 |  | 3.19 | [8 empty] | 19.95 |  |  |  |  | 0.05
1986 |  |  |  | 5675.79 |  |  | 6598 |  |  |  | 925 | [10 empty] | 69.22 |  |  |  | 69.22 | [5 empty] | 70.05 |  |  | 75.32 |  |  |  | 14.73 |  | 11.96 | [8 empty] | 18.83 |  |  |  |  | 0.00
1987 |  |  |  | 7022.68 |  |  | 7407 |  |  |  | 1000 | [10 empty] | 82.56 |  |  |  | 82.56 | [5 empty] | 80.17 |  |  | 84.55 |  |  |  | 2.48 |  | 2.10 | [8 empty] | 15.34 |  |  |  |  | 0.00
1988 |  |  |  | 6637.98 |  |  | 7350 |  |  |  | 925 | [10 empty] | 81.75 |  |  |  | 81.75 | [5 empty] | 81.70 |  |  | 83.67 |  |  |  | 1.04 |  | 0.86 | [8 empty] | 17.39 |  |  |  |  | 0.00
1989 |  |  |  | 5745.43 |  |  | 6582 |  |  |  | 925 | [10 empty] | 68.25 |  |  |  | 68.29 | [5 empty] | 70.91 |  |  | 75.14 |  |  |  | 8.37 |  | 6.24 | [8 empty] | 25.48 |  |  |  |  | 0.03
1990 |  |  |  | 5090.51 |  |  | 6817 |  |  |  | 925 | [10 empty] | 65.69 |  |  |  | 65.69 | [5 empty] | 62.82 |  |  | 77.82 |  |  |  | 17.24 |  | 13.68 | [8 empty] | 20.63 |  |  |  |  | 0.00
1991 |  |  |  | 4163.08 |  |  | 7038 |  |  |  | 925 | [10 empty] | 52.50 |  |  |  | 53.46 | [5 empty] | 51.38 |  |  | 80.34 |  |  |  | 1.96 |  | 1.07 | [8 empty] | 45.47 |  |  |  |  | 0.96
1992 |  |  |  | 3669.24 |  |  | 6103 |  |  |  | 925 | [10 empty] | 46.25 |  |  |  | 46.25 | [5 empty] | 45.16 |  |  | 69.49 |  |  |  | 4.44 |  | 2.15 | [8 empty] | 51.60 |  |  |  |  | 0.00
1993 |  |  |  | 4809.41 |  |  | 8145 |  |  |  | 925 | [10 empty] | 61.81 |  |  |  | 91.61 | [5 empty] | 59.35 |  |  | 92.98 |  |  |  | 1.35 |  | 1.25 | [8 empty] | 7.13 |  |  |  |  | 29.80
1994 |  |  |  | 1560.59 |  |  | 2686 |  |  |  | 925 | [10 empty] | 19.76 |  |  |  | 20.64 | [5 empty] | 19.26 |  |  | 30.66 |  |  |  | 60.69 |  | 31.88 | [8 empty] | 47.48 |  |  |  |  | 0.88
1995 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1996 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1997 |  |  |  | 27.76 |  |  | 61 |  |  |  | 925 | [10 empty] | 0.54 |  |  |  | 0.54 | [5 empty] | 0.34 |  |  | 0.70 |  |  |  | 39.09 |  | 0.35 | [8 empty] | 99.11 |  |  |  |  | 0.00
1998 |  |  |  | 4508.63 |  |  | 7845 |  |  |  | 925 | [10 empty] | 57.36 |  |  |  | 59.33 | [5 empty] | 55.64 |  |  | 89.55 |  |  |  | 5.73 |  | 3.61 | [8 empty] | 37.07 |  |  |  |  | 1.96
1999 |  |  |  | 4557.04 |  |  | 7464 |  |  |  | 925 | [10 empty] | 57.64 |  |  |  | 58.74 | [5 empty] | 56.24 |  |  | 85.21 |  |  |  | 0.91 |  | 0.54 | [8 empty] | 40.72 |  |  |  |  | 1.11
2000 |  |  |  | 3449.69 |  |  | 5531 |  |  |  | 925 | [10 empty] | 43.56 |  |  |  | 44.33 | [5 empty] | 42.46 |  |  | 62.97 |  |  |  | 6.37 |  | 3.02 | [8 empty] | 52.65 |  |  |  |  | 0.77
2001 |  |  |  | 1296.07 |  |  | 2042 |  |  |  | 925 | [10 empty] | 16.39 |  |  |  | 16.62 | [5 empty] | 15.99 |  |  | 23.31 |  |  |  | 6.51 |  | 1.16 | [8 empty] | 82.22 |  |  |  |  | 0.23
2002 |  |  |  | 2462.70 |  |  | 3439 |  |  |  | 925 | [10 empty] | 30.83 |  |  |  | 32.51 | [5 empty] | 30.39 |  |  | 39.26 |  |  |  | 2.91 |  | 0.97 | [8 empty] | 66.52 |  |  |  |  | 1.68
2003 |  |  |  | 6452.71 |  |  | 7262 |  |  |  | 925 | [10 empty] | 78.90 |  |  |  | 80.17 | [5 empty] | 79.63 |  |  | 82.90 |  |  |  | 6.86 |  | 5.91 | [8 empty] | 13.93 |  |  |  |  | 1.27
2004 |  |  |  | 6601.33 |  |  | 7363 |  |  |  | 925 | [10 empty] | 81.11 |  |  |  | 83.00 | [5 empty] | 81.25 |  |  | 83.82 |  |  |  | 2.85 |  | 2.43 | [8 empty] | 14.57 |  |  |  |  | 1.89
2005 |  |  |  | 6219.96 |  |  | 7651 |  |  |  | 925 | [10 empty] | 76.99 |  |  |  | 82.99 | [5 empty] | 76.75 |  |  | 87.33 |  |  |  | 2.72 |  | 2.53 | [8 empty] | 14.48 |  |  |  |  | 5.99
2006 |  |  |  | 5837.69 |  |  | 7089 |  |  |  | 925 | [10 empty] | 72.19 |  |  |  | 78.44 | [5 empty] | 72.04 |  |  | 80.92 |  |  |  | 3.17 |  | 2.56 | [8 empty] | 18.99 |  |  |  |  | 6.25
2007 |  |  |  | 6736.18 |  |  | 7670 |  |  |  | 925 | [10 empty] | 82.77 |  |  |  | 89.05 | [5 empty] | 83.13 |  |  | 87.56 |  |  |  | 6.05 |  | 5.74 | [8 empty] | 5.21 |  |  |  |  | 6.29
2008 |  |  |  | 6464.58 |  |  | 7596 |  |  |  | 925 | [10 empty] | 81.36 |  |  |  | 84.43 | [5 empty] | 79.56 |  |  | 86.48 |  |  |  | 2.89 |  | 2.51 | [8 empty] | 13.06 |  |  |  |  | 3.08
2009 |  |  |  | 7161.20 |  |  | 8068 |  |  |  | 925 | [10 empty] | 89.95 |  |  |  | 90.26 | [5 empty] | 88.38 |  |  | 92.10 |  |  |  | 4.16 |  | 3.92 | [8 empty] | 5.82 |  |  |  |  | 0.31
2010 |  |  |  | 5640.73 |  |  | 5991 |  |  |  | 925 | [10 empty] | 69.52 |  |  |  | 69.65 | [5 empty] | 69.61 |  |  | 68.39 |  |  |  | 12.86 |  | 10.28 | [8 empty] | 20.06 |  |  |  |  | 0.13
2011 |  |  |  | 7654.80 |  |  | 8620 |  |  |  | 925 | [10 empty] | 90.66 |  |  |  | 90.80 | [5 empty] | 94.48 |  |  | 98.41 |  |  |  | 1.96 |  | 1.82 | [8 empty] | 7.38 |  |  |  |  | 0.15
2012 |  |  |  | 5988.71 |  |  | 6392 |  |  |  | 925 | [10 empty] | 71.19 |  |  |  | 71.72 | [5 empty] | 73.71 |  |  | 72.77 |  |  |  | 0.64 |  | 0.46 | [8 empty] | 27.82 |  |  |  |  | 0.53
2013 |  |  |  | 6759.55 |  |  | 7217 |  |  |  | 925 | [10 empty] | 80.99 |  |  |  | 81.37 | [5 empty] | 83.42 |  |  | 82.39 |  |  |  | 5.16 |  | 4.96 | [8 empty] | 13.67 |  |  |  |  | 0.38
2014 |  |  |  | 6277.53 |  |  | 6846 |  |  |  | 925 | [10 empty] | 75.22 |  |  |  | 75.72 | [5 empty] | 77.46 |  |  | 78.14 |  |  |  | 2.80 |  | 2.18 | [8 empty] | 22.10 |  |  |  |  | 0.49
2015 |  |  |  | 6849.24 |  |  | 7482 |  |  |  | 925 | [10 empty] | 82.74 |  |  |  | 84.12 | [5 empty] | 84.53 |  |  | 85.41 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 15.50 |  |  |  |  | 1.37
2016 |  |  |  | 5293.85 |  |  | 6143 |  |  |  | 925 | [10 empty] | 65.56 |  |  |  | 67.46 | [5 empty] | 65.15 |  |  | 69.93 |  |  |  | 6.10 |  | 4.38 | [8 empty] | 28.16 |  |  |  |  | 1.90
2017 |  |  |  | 6684.29 |  |  | 7504 |  |  |  | 925 | [10 empty] | 81.87 |  |  |  | 82.54 | [5 empty] | 82.49 |  |  | 85.66 |  |  |  | 5.99 |  | 5.26 | [8 empty] | 12.20 |  |  |  |  | 0.68
2018 |  |  |  | 4685.45 |  |  | 5302 |  |  |  | 925 | [10 empty] | 57.65 |  |  |  | 58.92 | [5 empty] | 57.82 |  |  | 60.53 |  |  |  | 5.30 |  | 3.29 | [8 empty] | 37.78 |  |  |  |  | 1.27
2019 |  |  |  | 5300.40 |  |  | 5889 |  |  |  | 925 | [10 empty] | 64.96 |  |  |  | 66.51 | [5 empty] | 65.41 |  |  | 67.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.49 |  |  |  |  | 1.55
2020 |  |  |  | 5208.97 |  |  | 5781 |  |  |  | 925 | [10 empty] | 63.74 |  |  |  | 65.06 | [5 empty] | 64.11 |  |  | 65.81 |  |  |  | 2.00 |  | 1.33 | [8 empty] | 33.61 |  |  |  |  | 1.32
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1977 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 101 | [14 empty] | 122
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2906 | [14 empty] | 911
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 1264
E. |  | Testing of plant systems or components | [35 empty] | 4
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 120
H. |  | Nuclear regulatory requirements | [39 empty] | 9
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 9
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 4
Subtotal | [22 empty] | 2906 |  |  |  | 101 | [10 empty] | 2299 |  |  |  | 140 | [11 empty] | 9
Total | [22 empty] | 3007 | [14 empty] | 2448
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1977 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [19 empty] | 101 | [14 empty] | 35
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 20
16. |  |  | Steam generation systems | [34 empty] | 6
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 12
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
34. |  |  | Miscellaneous Systems | [34 empty] | 16
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 101 | [14 empty] | 123
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January, October-December. Additional electricity generation amounted to 49767.775 MWh. The unit was in the intermediate outage from 2020.01.24 to 2020.05.24. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-2
2020 Operating Experience
RU-22 | [8 empty] | KURSK-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-01-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1979-01-28
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-08-17
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1693 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 11.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 150 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5532.83 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 66.59 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 66.89 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 33.1 %
Load Factor (LF) | [18 empty] | : | 68.09 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.3 %
Operating Factor (OF) | [18 empty] | : | 67.68 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2839 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 81.88 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 712.61 | 670.21 |  |  |  | 717.61 |  | 156.22 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 528.57 |  |  |  | 659.81 |  |  | 703.35 |  |  | 674.04 | [9 empty] | 710.42 |  |  | 5532.83
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 23.74 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 77.42 |  |  |  | 98.72 |  |  | 100.00 |  |  | 99.97 | [9 empty] | 100.00 |  |  | 66.59
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 23.74 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 79.74 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.97 | [9 empty] | 100.00 |  |  | 66.89
LF [%] |  |  |  |  | 103.55 | 104.10 |  |  |  | 104.27 |  | 23.46 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 76.80 |  |  |  | 99.07 |  |  | 102.20 |  |  | 101.21 | [9 empty] | 103.23 |  |  | 68.09
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 27.08 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 85.75 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 67.68
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.03 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.03 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 76.26 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 20.26 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 33.10
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 2.32 |  |  |  | 1.28 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.30
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 217354.41 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.14 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 63.98 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 65.9 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 29.57 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 64.26 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.92 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.37 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 3613.90 |  |  | 6734 |  |  |  | 925 | [10 empty] | 62.36 |  |  |  | 62.36 | [5 empty] | 62.31 |  |  | 80.40 |  |  |  | 27.83 |  | 24.04 | [8 empty] | 13.59 |  |  |  |  | 0.00
1980 |  |  |  | 6404.32 |  |  | 7658 |  |  |  | 925 | [10 empty] | 78.45 |  |  |  | 79.02 | [5 empty] | 78.82 |  |  | 87.18 |  |  |  | 10.04 |  | 8.82 | [8 empty] | 12.15 |  |  |  |  | 0.58
1981 |  |  |  | 6385.88 |  |  | 7874 |  |  |  | 925 | [10 empty] | 78.71 |  |  |  | 78.71 | [5 empty] | 78.81 |  |  | 89.89 |  |  |  | 8.73 |  | 7.53 | [8 empty] | 13.77 |  |  |  |  | 0.00
1982 |  |  |  | 5875.79 |  |  | 6443 |  |  |  | 925 | [10 empty] | 71.11 |  |  |  | 71.11 | [5 empty] | 72.51 |  |  | 73.55 |  |  |  | 6.25 |  | 4.74 | [8 empty] | 24.14 |  |  |  |  | 0.00
1983 |  |  |  | 5707.64 |  |  | 7104 |  |  |  | 925 | [10 empty] | 70.07 |  |  |  | 70.07 | [5 empty] | 70.44 |  |  | 81.10 |  |  |  | 10.00 |  | 7.78 | [8 empty] | 22.15 |  |  |  |  | 0.00
1984 |  |  |  | 6326.50 |  |  | 7219 |  |  |  | 925 | [10 empty] | 77.06 |  |  |  | 77.10 | [5 empty] | 77.86 |  |  | 82.18 |  |  |  | 5.31 |  | 4.33 | [8 empty] | 18.57 |  |  |  |  | 0.05
1985 |  |  |  | 6459.94 |  |  | 7598 |  |  |  | 925 | [10 empty] | 79.41 |  |  |  | 79.41 | [5 empty] | 79.72 |  |  | 86.74 |  |  |  | 6.09 |  | 5.15 | [8 empty] | 15.43 |  |  |  |  | 0.00
1986 |  |  |  | 5617.31 |  |  | 6575 |  |  |  | 925 | [10 empty] | 69.08 |  |  |  | 69.08 | [5 empty] | 69.32 |  |  | 75.06 |  |  |  | 15.66 |  | 12.82 | [8 empty] | 18.10 |  |  |  |  | 0.00
1987 |  |  |  | 7196.69 |  |  | 7539 |  |  |  | 1000 | [10 empty] | 83.29 |  |  |  | 83.29 | [5 empty] | 82.15 |  |  | 86.06 |  |  |  | 3.73 |  | 3.23 | [8 empty] | 13.48 |  |  |  |  | 0.00
1988 |  |  |  | 5725.66 |  |  | 6609 |  |  |  | 925 | [10 empty] | 73.88 |  |  |  | 73.88 | [5 empty] | 70.47 |  |  | 75.24 |  |  |  | 3.50 |  | 2.68 | [8 empty] | 23.44 |  |  |  |  | 0.00
1989 |  |  |  | 6164.20 |  |  | 6797 |  |  |  | 925 | [10 empty] | 74.90 |  |  |  | 74.91 | [5 empty] | 76.07 |  |  | 77.59 |  |  |  | 14.58 |  | 12.79 | [8 empty] | 12.30 |  |  |  |  | 0.02
1990 |  |  |  | 4789.70 |  |  | 6874 |  |  |  | 925 | [10 empty] | 62.20 |  |  |  | 62.20 | [5 empty] | 59.11 |  |  | 78.47 |  |  |  | 26.17 |  | 22.05 | [8 empty] | 15.75 |  |  |  |  | 0.00
1991 |  |  |  | 4375.96 |  |  | 7361 |  |  |  | 925 | [10 empty] | 55.26 |  |  |  | 56.28 | [5 empty] | 54.00 |  |  | 84.03 |  |  |  | 0.70 |  | 0.40 | [8 empty] | 43.32 |  |  |  |  | 1.02
1992 |  |  |  | 2158.37 |  |  | 3552 |  |  |  | 925 | [10 empty] | 27.24 |  |  |  | 27.24 | [5 empty] | 26.57 |  |  | 40.44 |  |  |  | 3.87 |  | 1.10 | [8 empty] | 71.67 |  |  |  |  | 0.00
1993 |  |  |  | 4438.15 |  |  | 7432 |  |  |  | 925 | [10 empty] | 57.09 |  |  |  | 85.00 | [5 empty] | 54.77 |  |  | 84.84 |  |  |  | 2.25 |  | 1.95 | [8 empty] | 13.04 |  |  |  |  | 27.91
1994 |  |  |  | 4212.17 |  |  | 7385 |  |  |  | 925 | [10 empty] | 53.46 |  |  |  | 55.29 | [5 empty] | 51.98 |  |  | 84.30 |  |  |  | 37.66 |  | 33.40 | [8 empty] | 11.31 |  |  |  |  | 1.82
1995 |  |  |  | 4745.36 |  |  | 7708 |  |  |  | 925 | [10 empty] | 59.79 |  |  |  | 90.79 | [5 empty] | 58.56 |  |  | 87.99 |  |  |  | 0.91 |  | 0.83 | [8 empty] | 8.38 |  |  |  |  | 31.00
1996 |  |  |  | 4196.12 |  |  | 7099 |  |  |  | 925 | [10 empty] | 52.69 |  |  |  | 52.84 | [5 empty] | 51.64 |  |  | 80.82 |  |  |  | 7.80 |  | 4.47 | [8 empty] | 42.69 |  |  |  |  | 0.15
1997 |  |  |  | 4354.28 |  |  | 7076 |  |  |  | 925 | [10 empty] | 54.94 |  |  |  | 55.26 | [5 empty] | 53.74 |  |  | 80.78 |  |  |  | 7.36 |  | 4.39 | [8 empty] | 40.36 |  |  |  |  | 0.32
1998 |  |  |  | 1685.05 |  |  | 2805 |  |  |  | 925 | [10 empty] | 21.30 |  |  |  | 21.71 | [5 empty] | 20.80 |  |  | 32.02 |  |  |  | 5.62 |  | 1.29 | [8 empty] | 77.00 |  |  |  |  | 0.41
1999 |  |  |  | 3708.09 |  |  | 6066 |  |  |  | 925 | [10 empty] | 46.84 |  |  |  | 48.03 | [5 empty] | 45.76 |  |  | 69.25 |  |  |  | 4.72 |  | 2.38 | [8 empty] | 49.59 |  |  |  |  | 1.19
2000 |  |  |  | 3668.06 |  |  | 6211 |  |  |  | 925 | [10 empty] | 46.19 |  |  |  | 48.87 | [5 empty] | 45.14 |  |  | 70.71 |  |  |  | 3.97 |  | 2.02 | [8 empty] | 49.11 |  |  |  |  | 2.68
2001 |  |  |  | 4768.15 |  |  | 7667 |  |  |  | 925 | [10 empty] | 60.09 |  |  |  | 61.11 | [5 empty] | 58.84 |  |  | 87.52 |  |  |  | 0.33 |  | 0.20 | [8 empty] | 38.69 |  |  |  |  | 1.02
2002 |  |  |  | 3027.77 |  |  | 4770 |  |  |  | 925 | [10 empty] | 38.07 |  |  |  | 38.25 | [5 empty] | 37.37 |  |  | 54.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 61.75 |  |  |  |  | 0.19
2003 |  |  |  | 3756.24 |  |  | 5834 |  |  |  | 925 | [10 empty] | 46.36 |  |  |  | 47.10 | [5 empty] | 46.36 |  |  | 66.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 52.90 |  |  |  |  | 0.74
2004 |  |  |  | 3692.07 |  |  | 4318 |  |  |  | 925 | [10 empty] | 44.97 |  |  |  | 45.06 | [5 empty] | 45.44 |  |  | 49.16 |  |  |  | 3.87 |  | 1.82 | [8 empty] | 53.13 |  |  |  |  | 0.09
2005 |  |  |  | 6896.62 |  |  | 7782 |  |  |  | 925 | [10 empty] | 84.68 |  |  |  | 87.51 | [5 empty] | 85.10 |  |  | 88.83 |  |  |  | 0.58 |  | 0.51 | [8 empty] | 11.98 |  |  |  |  | 2.83
2006 |  |  |  | 6574.42 |  |  | 7320 |  |  |  | 925 | [10 empty] | 80.34 |  |  |  | 82.92 | [5 empty] | 81.14 |  |  | 83.56 |  |  |  | 1.28 |  | 1.07 | [8 empty] | 16.01 |  |  |  |  | 2.58
2007 |  |  |  | 5728.65 |  |  | 6207 |  |  |  | 925 | [10 empty] | 69.48 |  |  |  | 69.99 | [5 empty] | 70.70 |  |  | 70.86 |  |  |  | 1.70 |  | 1.21 | [8 empty] | 28.80 |  |  |  |  | 0.51
2008 |  |  |  | 6835.74 |  |  | 7351 |  |  |  | 925 | [10 empty] | 82.61 |  |  |  | 82.63 | [5 empty] | 84.13 |  |  | 83.69 |  |  |  | 0.80 |  | 0.66 | [8 empty] | 16.70 |  |  |  |  | 0.03
2009 |  |  |  | 6428.15 |  |  | 6778 |  |  |  | 925 | [10 empty] | 76.64 |  |  |  | 76.67 | [5 empty] | 79.33 |  |  | 77.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.33 |  |  |  |  | 0.03
2010 |  |  |  | 7448.67 |  |  | 8076 |  |  |  | 925 | [10 empty] | 87.81 |  |  |  | 88.09 | [5 empty] | 91.92 |  |  | 92.19 |  |  |  | 1.15 |  | 1.03 | [8 empty] | 10.88 |  |  |  |  | 0.28
2011 |  |  |  | 6368.67 |  |  | 6539 |  |  |  | 925 | [10 empty] | 75.31 |  |  |  | 75.39 | [5 empty] | 78.61 |  |  | 74.65 |  |  |  | 1.56 |  | 1.20 | [8 empty] | 23.41 |  |  |  |  | 0.09
2012 |  |  |  | 7401.98 |  |  | 7802 |  |  |  | 925 | [10 empty] | 87.76 |  |  |  | 88.01 | [5 empty] | 91.10 |  |  | 88.82 |  |  |  | 1.85 |  | 1.66 | [8 empty] | 10.33 |  |  |  |  | 0.25
2013 |  |  |  | 1584.36 |  |  | 1606 |  |  |  | 925 | [10 empty] | 18.25 |  |  |  | 18.25 | [5 empty] | 19.55 |  |  | 18.33 |  |  |  | 0.44 |  | 0.08 | [8 empty] | 81.67 |  |  |  |  | 0.00
2014 |  |  |  | 6299.77 |  |  | 7011 |  |  |  | 925 | [10 empty] | 77.67 |  |  |  | 78.52 | [5 empty] | 77.74 |  |  | 80.03 |  |  |  | 0.54 |  | 0.43 | [8 empty] | 21.05 |  |  |  |  | 0.86
2015 |  |  |  | 6556.20 |  |  | 7160 |  |  |  | 925 | [10 empty] | 79.38 |  |  |  | 80.44 | [5 empty] | 80.91 |  |  | 81.74 |  |  |  | 2.96 |  | 4.25 | [8 empty] | 15.31 |  |  |  |  | 1.06
2016 |  |  |  | 5678.19 |  |  | 6425 |  |  |  | 925 | [10 empty] | 68.85 |  |  |  | 69.57 | [5 empty] | 69.88 |  |  | 73.14 |  |  |  | 3.29 |  | 2.37 | [8 empty] | 28.06 |  |  |  |  | 0.72
2017 |  |  |  | 5437.61 |  |  | 6209 |  |  |  | 925 | [10 empty] | 66.14 |  |  |  | 66.59 | [5 empty] | 67.11 |  |  | 70.88 |  |  |  | 3.75 |  | 7.38 | [8 empty] | 26.03 |  |  |  |  | 0.45
2018 |  |  |  | 4702.96 |  |  | 5689 |  |  |  | 925 | [10 empty] | 56.25 |  |  |  | 56.48 | [5 empty] | 58.04 |  |  | 64.94 |  |  |  | 11.38 |  | 9.58 | [8 empty] | 33.94 |  |  |  |  | 0.22
2019 |  |  |  | 5207.62 |  |  | 5656 |  |  |  | 925 | [10 empty] | 62.03 |  |  |  | 62.17 | [5 empty] | 64.27 |  |  | 64.57 |  |  |  | 2.74 |  | 1.75 | [8 empty] | 36.08 |  |  |  |  | 0.13
2020 |  |  |  | 5532.83 |  |  | 5945 |  |  |  | 925 | [10 empty] | 66.59 |  |  |  | 66.89 | [5 empty] | 68.09 |  |  | 67.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.10 |  |  |  |  | 0.30
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1979 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 110
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2839 | [14 empty] | 1366
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 625
E. |  | Testing of plant systems or components | [35 empty] | 13
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 100
H. |  | Nuclear regulatory requirements | [39 empty] | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 3
Z. |  | Other | [39 empty] | 29
Subtotal | [22 empty] | 2839 | [14 empty] | 2104 |  |  |  | 147 | [11 empty] | 5
Total | [22 empty] | 2839 | [14 empty] | 2256
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1979 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 44
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 17
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 14
41. |  |  | Main Generator Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 110
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-April, September- December. Additional electricity generation amounted to 114745.325 MWh. The unit was in the routine maintenance outage from 2020.04.09 to 2020.08.05. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-3
2020 Operating Experience
RU-38 | [8 empty] | KURSK-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-04-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-10-17
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-03-30
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 170 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6473.17 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.13 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.62 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.32 %
Unit Capability Factor (UCF) | [18 empty] | : | 80.58 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.11 %
Load Factor (LF) | [18 empty] | : | 79.67 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.96 %
Operating Factor (OF) | [18 empty] | : | 84.97 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1320 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 59.39 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 647.20 | 474.54 |  |  |  | 697.95 |  | 686.41 | [8 empty] | 682.72 |  |  | 623.92 | [6 empty] | 624.94 |  | 580.78 |  |  |  | 0.00 |  |  | 106.74 |  |  | 632.42 | [9 empty] | 715.57 |  |  | 6473.17
EAF [%] |  |  |  |  | 90.08 | 71.12 |  |  |  | 97.78 |  | 99.90 | [8 empty] | 99.96 |  |  | 94.40 | [6 empty] | 91.39 |  | 85.37 |  |  |  | 0.16 |  |  | 18.39 |  |  | 93.55 | [9 empty] | 100.00 |  |  | 78.62
UCF [%] |  |  |  |  | 90.08 | 71.12 |  |  |  | 97.78 |  | 99.90 | [8 empty] | 100.00 |  |  | 98.42 | [6 empty] | 99.14 |  | 96.81 |  |  |  | 0.16 |  |  | 18.39 |  |  | 93.55 | [9 empty] | 100.00 |  |  | 80.58
LF [%] |  |  |  |  | 94.04 | 73.71 |  |  |  | 101.42 |  | 103.06 | [8 empty] | 99.20 |  |  | 93.68 | [6 empty] | 90.81 |  | 84.39 |  |  |  | 0.00 |  |  | 15.51 |  |  | 94.96 | [9 empty] | 103.98 |  |  | 79.67
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 0.42 |  |  | 23.92 |  |  | 94.86 | [9 empty] | 100.00 |  |  | 84.97
FLR [%] |  |  |  |  | 0.00 | 28.88 |  |  |  | 2.22 |  | 0.10 | [8 empty] | 0.00 |  |  | 1.45 | [6 empty] | 0.86 |  | 3.19 |  |  |  | 0.00 |  |  | 0.00 |  |  | 6.45 | [9 empty] | 0.00 |  |  | 4.13
UCL [%] |  |  |  |  | 9.92 | 28.88 |  |  |  | 2.22 |  | 0.10 | [8 empty] | 0.00 |  |  | 1.45 | [6 empty] | 0.86 |  | 3.19 |  |  |  | 0.00 |  |  | 0.00 |  |  | 6.45 | [9 empty] | 0.00 |  |  | 4.32
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.13 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 99.84 |  |  | 81.61 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.11
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  | 4.01 | [6 empty] | 7.75 |  | 11.43 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.96
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 222978.59 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.86 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.02 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.41 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.08 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.51 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.13 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.06 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.69 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 5479.24 |  |  | 6830 |  |  |  | 925 | [10 empty] | 72.49 |  |  |  | 72.49 | [5 empty] | 72.15 |  |  | 76.71 |  |  |  | 9.02 |  | 7.18 | [8 empty] | 20.33 |  |  |  |  | 0.00
1985 |  |  |  | 6260.75 |  |  | 7250 |  |  |  | 925 | [10 empty] | 77.59 |  |  |  | 77.93 | [5 empty] | 77.26 |  |  | 82.76 |  |  |  | 7.60 |  | 6.41 | [8 empty] | 15.66 |  |  |  |  | 0.34
1986 |  |  |  | 4810.84 |  |  | 6269 |  |  |  | 925 | [10 empty] | 60.00 |  |  |  | 60.42 | [5 empty] | 59.37 |  |  | 71.56 |  |  |  | 15.08 |  | 10.73 | [8 empty] | 28.85 |  |  |  |  | 0.42
1987 |  |  |  | 5458.95 |  |  | 6185 |  |  |  | 1000 | [10 empty] | 66.40 |  |  |  | 69.01 | [5 empty] | 62.32 |  |  | 70.61 |  |  |  | 5.11 |  | 3.71 | [8 empty] | 27.28 |  |  |  |  | 2.61
1988 |  |  |  | 6693.64 |  |  | 7471 |  |  |  | 925 | [10 empty] | 83.64 |  |  |  | 83.64 | [5 empty] | 82.38 |  |  | 85.05 |  |  |  | 3.44 |  | 2.98 | [8 empty] | 13.38 |  |  |  |  | 0.00
1989 |  |  |  | 5900.50 |  |  | 7200 |  |  |  | 925 | [10 empty] | 74.29 |  |  |  | 74.32 | [5 empty] | 72.82 |  |  | 82.19 |  |  |  | 8.84 |  | 7.21 | [8 empty] | 18.48 |  |  |  |  | 0.03
1990 |  |  |  | 6889.42 |  |  | 8096 |  |  |  | 925 | [10 empty] | 86.52 |  |  |  | 86.52 | [5 empty] | 85.02 |  |  | 92.42 |  |  |  | 7.78 |  | 7.30 | [8 empty] | 6.18 |  |  |  |  | 0.00
1991 |  |  |  | 5138.96 |  |  | 5704 |  |  |  | 925 | [10 empty] | 63.17 |  |  |  | 63.42 | [5 empty] | 63.42 |  |  | 65.11 |  |  |  | 1.30 |  | 0.83 | [8 empty] | 35.74 |  |  |  |  | 0.25
1992 |  |  |  | 6630.50 |  |  | 8126 |  |  |  | 925 | [10 empty] | 82.13 |  |  |  | 82.13 | [5 empty] | 81.61 |  |  | 92.52 |  |  |  | 5.97 |  | 5.22 | [8 empty] | 12.66 |  |  |  |  | 0.00
1993 |  |  |  | 5562.30 |  |  | 6438 |  |  |  | 925 | [10 empty] | 70.34 |  |  |  | 71.22 | [5 empty] | 68.64 |  |  | 73.49 |  |  |  | 8.24 |  | 6.39 | [8 empty] | 22.39 |  |  |  |  | 0.88
1994 |  |  |  | 5077.86 |  |  | 6495 |  |  |  | 925 | [10 empty] | 66.69 |  |  |  | 73.60 | [5 empty] | 62.67 |  |  | 74.14 |  |  |  | 0.74 |  | 0.55 | [8 empty] | 25.84 |  |  |  |  | 6.92
1995 |  |  |  | 5318.13 |  |  | 5974 |  |  |  | 925 | [10 empty] | 65.40 |  |  |  | 65.70 | [5 empty] | 65.63 |  |  | 68.20 |  |  |  | 2.80 |  | 1.90 | [8 empty] | 32.41 |  |  |  |  | 0.30
1996 |  |  |  | 6739.27 |  |  | 7383 |  |  |  | 925 | [10 empty] | 82.67 |  |  |  | 82.89 | [5 empty] | 82.94 |  |  | 84.05 |  |  |  | 2.36 |  | 2.00 | [8 empty] | 15.11 |  |  |  |  | 0.22
1997 |  |  |  | 6548.72 |  |  | 7325 |  |  |  | 925 | [10 empty] | 81.56 |  |  |  | 82.46 | [5 empty] | 80.82 |  |  | 83.62 |  |  |  | 0.21 |  | 0.17 | [8 empty] | 17.37 |  |  |  |  | 0.89
1998 |  |  |  | 4528.32 |  |  | 5405 |  |  |  | 925 | [10 empty] | 56.53 |  |  |  | 60.26 | [5 empty] | 55.88 |  |  | 61.70 |  |  |  | 17.21 |  | 12.53 | [8 empty] | 27.20 |  |  |  |  | 3.74
1999 |  |  |  | 6006.85 |  |  | 6749 |  |  |  | 925 | [10 empty] | 74.33 |  |  |  | 75.32 | [5 empty] | 74.13 |  |  | 77.04 |  |  |  | 4.80 |  | 3.80 | [8 empty] | 20.87 |  |  |  |  | 0.99
2000 |  |  |  | 6382.33 |  |  | 7415 |  |  |  | 925 | [10 empty] | 78.26 |  |  |  | 78.85 | [5 empty] | 78.55 |  |  | 84.41 |  |  |  | 7.98 |  | 6.83 | [8 empty] | 14.32 |  |  |  |  | 0.59
2001 |  |  |  | 3535.20 |  |  | 3948 |  |  |  | 925 | [10 empty] | 43.53 |  |  |  | 44.65 | [5 empty] | 43.63 |  |  | 45.07 |  |  |  | 0.15 |  | 0.07 | [8 empty] | 55.28 |  |  |  |  | 1.12
2002 |  |  |  | 6699.77 |  |  | 7788 |  |  |  | 925 | [10 empty] | 85.07 |  |  |  | 88.23 | [5 empty] | 82.68 |  |  | 88.90 |  |  |  | 0.29 |  | 0.26 | [8 empty] | 11.51 |  |  |  |  | 3.16
2003 |  |  |  | 5100.59 |  |  | 5469 |  |  |  | 925 | [10 empty] | 61.84 |  |  |  | 62.23 | [5 empty] | 62.95 |  |  | 62.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.77 |  |  |  |  | 0.39
2004 |  |  |  | 6894.20 |  |  | 7660 |  |  |  | 925 | [10 empty] | 84.35 |  |  |  | 86.33 | [5 empty] | 84.85 |  |  | 87.20 |  |  |  | 0.82 |  | 0.71 | [8 empty] | 12.96 |  |  |  |  | 1.98
2005 |  |  |  | 4987.10 |  |  | 5598 |  |  |  | 925 | [10 empty] | 61.31 |  |  |  | 63.49 | [5 empty] | 61.55 |  |  | 63.90 |  |  |  | 0.59 |  | 0.37 | [8 empty] | 36.14 |  |  |  |  | 2.17
2006 |  |  |  | 6711.22 |  |  | 7353 |  |  |  | 925 | [10 empty] | 81.93 |  |  |  | 83.37 | [5 empty] | 82.82 |  |  | 83.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.63 |  |  |  |  | 1.44
2007 |  |  |  | 5765.28 |  |  | 6535 |  |  |  | 925 | [10 empty] | 71.07 |  |  |  | 73.75 | [5 empty] | 71.15 |  |  | 74.60 |  |  |  | 1.12 |  | 0.84 | [8 empty] | 25.41 |  |  |  |  | 2.68
2008 |  |  |  | 2117.39 |  |  | 2374 |  |  |  | 925 | [10 empty] | 26.82 |  |  |  | 26.82 | [5 empty] | 26.06 |  |  | 27.03 |  |  |  | 1.30 |  | 0.35 | [8 empty] | 72.83 |  |  |  |  | 0.00
2009 |  |  |  | 7620.95 |  |  | 8216 |  |  |  | 925 | [10 empty] | 93.77 |  |  |  | 93.87 | [5 empty] | 94.05 |  |  | 93.79 |  |  |  | 0.58 |  | 0.55 | [8 empty] | 5.58 |  |  |  |  | 0.10
2010 |  |  |  | 6048.61 |  |  | 6352 |  |  |  | 925 | [10 empty] | 71.67 |  |  |  | 71.78 | [5 empty] | 74.65 |  |  | 72.51 |  |  |  | 1.44 |  | 1.05 | [8 empty] | 27.17 |  |  |  |  | 0.11
2011 |  |  |  | 7574.35 |  |  | 8228 |  |  |  | 925 | [10 empty] | 90.44 |  |  |  | 90.80 | [5 empty] | 93.49 |  |  | 93.94 |  |  |  | 3.77 |  | 3.56 | [8 empty] | 5.64 |  |  |  |  | 0.36
2012 |  |  |  | 6207.22 |  |  | 6900 |  |  |  | 925 | [10 empty] | 74.78 |  |  |  | 75.44 | [5 empty] | 76.39 |  |  | 78.55 |  |  |  | 5.35 |  | 7.58 | [8 empty] | 16.98 |  |  |  |  | 0.66
2013 |  |  |  | 7264.06 |  |  | 8022 |  |  |  | 925 | [10 empty] | 87.02 |  |  |  | 87.23 | [5 empty] | 89.65 |  |  | 91.58 |  |  |  | 5.04 |  | 4.63 | [8 empty] | 8.14 |  |  |  |  | 0.21
2014 |  |  |  | 6969.97 |  |  | 7506 |  |  |  | 925 | [10 empty] | 84.29 |  |  |  | 84.49 | [5 empty] | 86.01 |  |  | 85.68 |  |  |  | 0.85 |  | 4.03 | [8 empty] | 11.48 |  |  |  |  | 0.21
2015 |  |  |  | 7338.33 |  |  | 8075 |  |  |  | 925 | [10 empty] | 89.24 |  |  |  | 89.93 | [5 empty] | 90.56 |  |  | 92.18 |  |  |  | 1.22 |  | 1.11 | [8 empty] | 8.97 |  |  |  |  | 0.68
2016 |  |  |  | 7001.08 |  |  | 7556 |  |  |  | 925 | [10 empty] | 84.05 |  |  |  | 85.12 | [5 empty] | 86.17 |  |  | 86.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.88 |  |  |  |  | 1.07
2017 |  |  |  | 7405.52 |  |  | 8018 |  |  |  | 925 | [10 empty] | 90.09 |  |  |  | 90.92 | [5 empty] | 91.39 |  |  | 91.53 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 9.00 |  |  |  |  | 0.83
2018 |  |  |  | 6346.60 |  |  | 7060 |  |  |  | 925 | [10 empty] | 76.64 |  |  |  | 77.41 | [5 empty] | 78.32 |  |  | 80.59 |  |  |  | 4.10 |  | 8.89 | [8 empty] | 13.70 |  |  |  |  | 0.77
2019 |  |  |  | 4990.43 |  |  | 5623 |  |  |  | 925 | [10 empty] | 60.49 |  |  |  | 61.19 | [5 empty] | 61.59 |  |  | 64.19 |  |  |  | 2.25 |  | 2.92 | [8 empty] | 35.90 |  |  |  |  | 0.70
2020 |  |  |  | 6473.17 |  |  | 7464 |  |  |  | 925 | [10 empty] | 78.62 |  |  |  | 80.58 | [5 empty] | 79.67 |  |  | 84.97 |  |  |  | 4.13 |  | 4.32 | [8 empty] | 15.11 |  |  |  |  | 1.96
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 43 | [14 empty] | 142
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1284 | [14 empty] | 1111
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 695
E. |  | Testing of plant systems or components | [35 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 8
Subtotal | [22 empty] | 1284 |  |  |  | 43 | [10 empty] | 1807 |  |  |  | 142 | [11 empty] | 8
Total | [22 empty] | 1327 | [14 empty] | 1957
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 23
12. |  |  | Reactor I&C Systems | [34 empty] | 16
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [19 empty] | 43 | [14 empty] | 53
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
41. |  |  | Main Generator Systems | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 43 | [14 empty] | 143
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-May, October-Desember. Additional electricity generation amounted to 150914.675 MWh. The unit was in the overhaul outage from 2020.09.01 to 2020.10.24. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-4
2020 Operating Experience
RU-39 | [8 empty] | KURSK-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-05-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-12-02
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-02-05
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 167 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7277.83 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.62 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.64 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.56 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.46 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.98 %
Load Factor (LF) | [18 empty] | : | 89.57 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.81 %
Operating Factor (OF) | [18 empty] | : | 90.97 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 793 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 163.01 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 701.11 | 678.45 |  |  |  | 714.12 |  | 687.54 | [8 empty] | 632.70 |  |  | 630.84 | [6 empty] | 263.54 |  | 259.54 |  |  |  | 656.50 |  |  | 691.57 |  |  | 660.29 | [9 empty] | 701.63 |  |  | 7277.83
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.63 | [8 empty] | 93.71 |  |  | 96.02 | [6 empty] | 39.43 |  | 38.93 |  |  |  | 98.50 |  |  | 99.83 |  |  | 99.68 | [9 empty] | 100.00 |  |  | 88.64
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.63 | [8 empty] | 93.75 |  |  | 99.94 | [6 empty] | 42.10 |  | 40.09 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.46
LF [%] |  |  |  |  | 101.88 | 105.38 |  |  |  | 103.77 |  | 103.23 | [8 empty] | 91.94 |  |  | 94.72 | [6 empty] | 38.29 |  | 37.71 |  |  |  | 98.57 |  |  | 100.49 |  |  | 99.14 | [9 empty] | 101.95 |  |  | 89.57
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 45.56 |  | 47.85 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.97
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.37 | [8 empty] | 6.25 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.62
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.37 | [8 empty] | 6.25 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.56
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.06 | [6 empty] | 57.90 |  | 59.91 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.98
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  | 3.92 | [6 empty] | 2.66 |  | 1.16 |  |  |  | 1.50 |  |  | 0.17 |  |  | 0.32 | [9 empty] | 0.00 |  |  | 0.81
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 222192.96 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.57 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.49 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.09 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.52 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.39 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.61 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 6328.54 |  |  | 7574 |  |  |  | 925 | [10 empty] | 80.35 |  |  |  | 80.81 | [5 empty] | 80.28 |  |  | 88.06 |  |  |  | 12.66 |  | 11.71 | [8 empty] | 7.47 |  |  |  |  | 0.46
1987 |  |  |  | 6167.68 |  |  | 6704 |  |  |  | 1000 | [10 empty] | 72.29 |  |  |  | 72.43 | [5 empty] | 70.41 |  |  | 76.53 |  |  |  | 6.80 |  | 5.28 | [8 empty] | 22.29 |  |  |  |  | 0.14
1988 |  |  |  | 6653.03 |  |  | 7390 |  |  |  | 925 | [10 empty] | 81.73 |  |  |  | 81.73 | [5 empty] | 81.88 |  |  | 84.13 |  |  |  | 5.02 |  | 4.32 | [8 empty] | 13.95 |  |  |  |  | 0.01
1989 |  |  |  | 6131.81 |  |  | 6954 |  |  |  | 925 | [10 empty] | 75.98 |  |  |  | 76.02 | [5 empty] | 75.67 |  |  | 79.38 |  |  |  | 4.04 |  | 3.20 | [8 empty] | 20.78 |  |  |  |  | 0.05
1990 |  |  |  | 6050.02 |  |  | 6922 |  |  |  | 925 | [10 empty] | 73.62 |  |  |  | 73.71 | [5 empty] | 74.66 |  |  | 79.02 |  |  |  | 7.62 |  | 6.08 | [8 empty] | 20.21 |  |  |  |  | 0.09
1991 |  |  |  | 7356.07 |  |  | 8469 |  |  |  | 925 | [10 empty] | 90.30 |  |  |  | 92.54 | [5 empty] | 90.78 |  |  | 96.68 |  |  |  | 4.21 |  | 4.06 | [8 empty] | 3.40 |  |  |  |  | 2.24
1992 |  |  |  | 6117.37 |  |  | 7324 |  |  |  | 925 | [10 empty] | 75.44 |  |  |  | 75.44 | [5 empty] | 75.30 |  |  | 83.39 |  |  |  | 2.41 |  | 1.87 | [8 empty] | 22.69 |  |  |  |  | 0.00
1993 |  |  |  | 5638.27 |  |  | 6439 |  |  |  | 925 | [10 empty] | 70.98 |  |  |  | 71.72 | [5 empty] | 69.58 |  |  | 73.50 |  |  |  | 4.54 |  | 3.41 | [8 empty] | 24.87 |  |  |  |  | 0.74
1994 |  |  |  | 5369.44 |  |  | 6255 |  |  |  | 925 | [10 empty] | 66.98 |  |  |  | 71.55 | [5 empty] | 66.26 |  |  | 71.40 |  |  |  | 1.27 |  | 0.92 | [8 empty] | 27.53 |  |  |  |  | 4.57
1995 |  |  |  | 6207.48 |  |  | 7001 |  |  |  | 925 | [10 empty] | 77.02 |  |  |  | 78.61 | [5 empty] | 76.61 |  |  | 79.92 |  |  |  | 3.36 |  | 2.74 | [8 empty] | 18.66 |  |  |  |  | 1.58
1996 |  |  |  | 6590.19 |  |  | 7373 |  |  |  | 925 | [10 empty] | 80.16 |  |  |  | 81.40 | [5 empty] | 81.11 |  |  | 83.94 |  |  |  | 3.23 |  | 2.71 | [8 empty] | 15.89 |  |  |  |  | 1.23
1997 |  |  |  | 5971.68 |  |  | 6664 |  |  |  | 925 | [10 empty] | 73.05 |  |  |  | 73.87 | [5 empty] | 73.70 |  |  | 76.07 |  |  |  | 2.70 |  | 2.05 | [8 empty] | 24.08 |  |  |  |  | 0.82
1998 |  |  |  | 6641.43 |  |  | 7751 |  |  |  | 925 | [10 empty] | 82.33 |  |  |  | 86.66 | [5 empty] | 81.96 |  |  | 88.48 |  |  |  | 1.46 |  | 1.29 | [8 empty] | 12.05 |  |  |  |  | 4.34
1999 |  |  |  | 5895.38 |  |  | 6595 |  |  |  | 925 | [10 empty] | 72.77 |  |  |  | 74.17 | [5 empty] | 72.76 |  |  | 75.29 |  |  |  | 1.02 |  | 0.77 | [8 empty] | 25.06 |  |  |  |  | 1.40
2000 |  |  |  | 6778.77 |  |  | 7423 |  |  |  | 925 | [10 empty] | 82.81 |  |  |  | 83.47 | [5 empty] | 83.43 |  |  | 84.51 |  |  |  | 0.59 |  | 0.50 | [8 empty] | 16.03 |  |  |  |  | 0.66
2001 |  |  |  | 6671.63 |  |  | 7281 |  |  |  | 925 | [10 empty] | 81.52 |  |  |  | 82.20 | [5 empty] | 82.34 |  |  | 83.12 |  |  |  | 0.81 |  | 0.67 | [8 empty] | 17.13 |  |  |  |  | 0.68
2002 |  |  |  | 5530.98 |  |  | 6094 |  |  |  | 925 | [10 empty] | 67.61 |  |  |  | 68.31 | [5 empty] | 68.26 |  |  | 69.57 |  |  |  | 1.54 |  | 1.07 | [8 empty] | 30.62 |  |  |  |  | 0.71
2003 |  |  |  | 6233.39 |  |  | 6802 |  |  |  | 925 | [10 empty] | 75.84 |  |  |  | 77.26 | [5 empty] | 76.93 |  |  | 77.65 |  |  |  | 0.27 |  | 0.21 | [8 empty] | 22.54 |  |  |  |  | 1.42
2004 |  |  |  | 5422.93 |  |  | 6005 |  |  |  | 925 | [10 empty] | 66.70 |  |  |  | 68.02 | [5 empty] | 66.74 |  |  | 68.36 |  |  |  | 0.27 |  | 0.18 | [8 empty] | 31.80 |  |  |  |  | 1.32
2005 |  |  |  | 7081.14 |  |  | 7858 |  |  |  | 925 | [10 empty] | 87.15 |  |  |  | 89.43 | [5 empty] | 87.38 |  |  | 89.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.57 |  |  |  |  | 2.28
2006 |  |  |  | 3636.44 |  |  | 4115 |  |  |  | 925 | [10 empty] | 44.24 |  |  |  | 44.77 | [5 empty] | 44.88 |  |  | 46.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 55.23 |  |  |  |  | 0.53
2007 |  |  |  | 7426.50 |  |  | 8298 |  |  |  | 925 | [10 empty] | 91.23 |  |  |  | 94.27 | [5 empty] | 91.65 |  |  | 94.73 |  |  |  | 0.19 |  | 0.18 | [8 empty] | 5.54 |  |  |  |  | 3.04
2008 |  |  |  | 6052.40 |  |  | 6580 |  |  |  | 925 | [10 empty] | 73.94 |  |  |  | 74.87 | [5 empty] | 74.49 |  |  | 74.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.13 |  |  |  |  | 0.93
2009 |  |  |  | 4184.28 |  |  | 4786 |  |  |  | 925 | [10 empty] | 52.34 |  |  |  | 52.46 | [5 empty] | 51.64 |  |  | 54.63 |  |  |  | 1.38 |  | 0.73 | [8 empty] | 46.81 |  |  |  |  | 0.12
2010 |  |  |  | 7557.08 |  |  | 8109 |  |  |  | 925 | [10 empty] | 91.31 |  |  |  | 91.65 | [5 empty] | 93.26 |  |  | 92.57 |  |  |  | 2.88 |  | 2.72 | [8 empty] | 5.62 |  |  |  |  | 0.35
2011 |  |  |  | 5500.69 |  |  | 5729 |  |  |  | 925 | [10 empty] | 64.46 |  |  |  | 64.51 | [5 empty] | 67.89 |  |  | 65.41 |  |  |  | 4.61 |  | 3.12 | [8 empty] | 32.37 |  |  |  |  | 0.05
2012 |  |  |  | 7470.41 |  |  | 8144 |  |  |  | 925 | [10 empty] | 89.18 |  |  |  | 89.36 | [5 empty] | 91.94 |  |  | 92.71 |  |  |  | 2.11 |  | 1.93 | [8 empty] | 8.72 |  |  |  |  | 0.18
2013 |  |  |  | 6213.89 |  |  | 6807 |  |  |  | 925 | [10 empty] | 74.33 |  |  |  | 74.78 | [5 empty] | 76.69 |  |  | 77.71 |  |  |  | 1.12 |  | 0.85 | [8 empty] | 24.37 |  |  |  |  | 0.46
2014 |  |  |  | 7517.80 |  |  | 8201 |  |  |  | 925 | [10 empty] | 89.67 |  |  |  | 90.11 | [5 empty] | 92.78 |  |  | 93.62 |  |  |  | 2.44 |  | 2.26 | [8 empty] | 7.64 |  |  |  |  | 0.44
2015 |  |  |  | 6745.34 |  |  | 7348 |  |  |  | 925 | [10 empty] | 81.17 |  |  |  | 82.83 | [5 empty] | 83.24 |  |  | 83.88 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 17.11 |  |  |  |  | 1.67
2016 |  |  |  | 7420.59 |  |  | 8055 |  |  |  | 925 | [10 empty] | 88.67 |  |  |  | 90.08 | [5 empty] | 91.33 |  |  | 91.70 |  |  |  | 0.76 |  | 0.69 | [8 empty] | 9.23 |  |  |  |  | 1.40
2017 |  |  |  | 6940.86 |  |  | 7471 |  |  |  | 925 | [10 empty] | 83.55 |  |  |  | 83.71 | [5 empty] | 85.66 |  |  | 85.29 |  |  |  | 2.08 |  | 1.78 | [8 empty] | 14.52 |  |  |  |  | 0.15
2018 |  |  |  | 7117.30 |  |  | 7645 |  |  |  | 925 | [10 empty] | 85.95 |  |  |  | 86.70 | [5 empty] | 87.84 |  |  | 87.27 |  |  |  | 3.14 |  | 2.81 | [8 empty] | 10.49 |  |  |  |  | 0.75
2019 |  |  |  | 6538.38 |  |  | 7095 |  |  |  | 925 | [10 empty] | 79.38 |  |  |  | 80.03 | [5 empty] | 80.69 |  |  | 80.99 |  |  |  | 2.71 |  | 2.99 | [8 empty] | 16.98 |  |  |  |  | 0.65
2020 |  |  |  | 7277.83 |  |  | 7991 |  |  |  | 925 | [10 empty] | 88.64 |  |  |  | 89.46 | [5 empty] | 89.57 |  |  | 90.97 |  |  |  | 0.62 |  | 0.56 | [8 empty] | 9.98 |  |  |  |  | 0.81
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 71
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 793 | [14 empty] | 1134
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 403
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 78
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 6
Subtotal | [22 empty] | 793 | [14 empty] | 1615 |  |  |  | 82 | [11 empty] | 1
Total | [22 empty] | 793 | [14 empty] | 1698
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 9
12. |  |  | Reactor I&C Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 23
Total | [37 empty] | 71
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-May, September-December. Additional electricity generation amounted to 130641.45 MWh. The unit was in the routine maintenance outage from 2020.07.15 to 2020.08.17. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD 2-1
2020 Operating Experience
RU-163 | [8 empty] | LENINGRAD 2-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-491 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-10-25
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-03-09
Gross electrical power | [12 empty] | : |  |  | 1188 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-10-29
Reference unit power (net) | [12 empty] | : |  |  | 1101 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7530.82 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.18 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.64 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.15 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.44 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.41 %
Load Factor (LF) | [18 empty] | : | 77.87 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.8 %
Operating Factor (OF) | [18 empty] | : | 80.11 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1747 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 811.59 | 754.52 |  |  |  | 811.42 |  | 466.60 | [8 empty] | 476.88 |  |  | 754.05 | [6 empty] | 809.25 |  | 786.08 |  |  |  | 772.57 |  |  | 815.60 |  |  | 272.25 | [9 empty] | 0.00 |  |  | 7530.82
EAF [%] |  |  |  |  | 99.15 | 99.43 |  |  |  | 99.47 |  | 66.19 | [8 empty] | 99.80 |  |  | 96.94 | [6 empty] | 98.77 |  | 98.79 |  |  |  | 99.07 |  |  | 99.09 |  |  | 34.96 | [9 empty] | 0.01 |  |  | 82.64
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 66.43 | [8 empty] | 100.00 |  |  | 98.18 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 36.68 | [9 empty] | 0.01 |  |  | 83.44
LF [%] |  |  |  |  | 99.08 | 98.46 |  |  |  | 99.06 |  | 58.86 | [8 empty] | 58.22 |  |  | 95.12 | [6 empty] | 98.79 |  | 95.96 |  |  |  | 97.46 |  |  | 99.57 |  |  | 34.34 | [9 empty] | 0.00 |  |  | 77.87
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 63.47 | [8 empty] | 61.69 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 36.81 | [9 empty] | 0.00 |  |  | 80.11
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.82 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.18
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.82 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.15
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 33.57 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 63.32 | [9 empty] | 99.99 |  |  | 16.41
XUF [%] |  |  |  |  | 0.85 | 0.57 |  |  |  | 0.53 |  | 0.24 | [8 empty] | 0.20 |  |  | 1.24 | [6 empty] | 1.23 |  | 1.21 |  |  |  | 0.93 |  |  | 0.91 |  |  | 1.73 | [9 empty] | 0.00 |  |  | 0.80
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 17012.85 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.87 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 10.47 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.98 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.71 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.64 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.03 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 2344.91 |  |  | 3078 |  |  |  | 1085 | [10 empty] | 23.75 |  |  |  | 23.75 | [5 empty] | 20.26 |  |  | 25.14 |  |  |  | 76.25 |  | 76.25 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7137.13 |  |  | 6666 |  |  |  | 1101 | [10 empty] | 74.35 |  |  |  | 74.93 | [5 empty] | 74.00 |  |  | 76.10 |  |  |  | 8.67 |  | 9.99 | [8 empty] | 15.09 |  |  |  |  | 0.57
2020 |  |  |  | 7530.82 |  |  | 7037 |  |  |  | 1101 | [10 empty] | 82.64 |  |  |  | 83.44 | [5 empty] | 77.87 |  |  | 80.11 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 16.41 |  |  |  |  | 0.80
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2018 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1021
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1200 | [14 empty] | 1165
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 243 | [14 empty] | 112
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 321 | [19 empty] | 148
Subtotal | [22 empty] | 1443 | [10 empty] | 321 |  |  |  | 1277 |  |  |  | 1021 | [11 empty] | 148
Total | [22 empty] | 1764 | [14 empty] | 2446
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2018 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [34 empty] | 34
31. |  |  | Turbine and auxiliaries | [34 empty] | 206
32. |  |  | Feedwater and Main Steam System | [34 empty] | 159
41. |  |  | Main Generator Systems | [34 empty] | 381
Total | [37 empty] | 780
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in February, April-May. Additional electricity generation amounted to 140 MWh. The unit was in the routine maintenance outage from 2020.04.19 to 2020.04.30 and in the in the overhoul outage from 2020.11.12 to 2021.01.01. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD 2-2
2020 Operating Experience
RU-164 | [6 empty] | LENINGRAD 2-2 | [26 empty] | RUSSIA
Status at end of year | [5 empty] | : | Operational
Operator | [5 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [5 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [5 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [5 empty] | : | AEM (JSC ATOMENERGOMASH)
Reactor Unit Details | [25 empty] | Key Dates
Reactor type and model | [10 empty] | : |  |  | PWR / VVER V-491 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-04-15
Thermal power | [10 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-10-22
Gross electrical power | [10 empty] | : |  |  | 1188 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-03-18
Reference unit power (net) | [10 empty] | : |  |  | 1066 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 0 years
Design Characteristics
| Primary Systems | [26 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [11 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [11 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [11 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [11 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [11 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [11 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [11 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [11 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [11 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [11 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [11 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [11 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [11 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [11 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [11 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [16 empty] | : | 659.54 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [16 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [16 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [16 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [16 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 462 hours
Annual Summary
|  |  | Jan | Oct |  |  |  | Nov |  | Dec | [8 empty] | Feb |  |  | Mar | [6 empty] | Apr |  | May |  |  |  | Jun |  |  | Jul |  |  | Aug | [9 empty] | Sep
GW(e)-h
EAF [%]
UCF [%]
LF [%]
OF [%]
FLR [%]
UCL [%]
PUF [%]
XUF [%]
Historical Summary
Lifetime energy generation | [11 empty] | : |  |  | 659.54 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [11 empty] | : |  |  | 0 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [11 empty] | : |  |  | 0 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0 %
Cumulative Load Factor (LF) | [11 empty] | : |  |  | 0 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [11 empty] | : |  |  | 0 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[21 empty] | 2020 | [14 empty] | 2021 to 2020
Outage Cause | [20 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[21 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
Subtotal
Total | [20 empty] | 0 | [14 empty] | 0
Equipment Related Unplanned Full Outages, Analysis by System
System | [20 empty] | 2020 | [14 empty] | 2021 to 2020
[21 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
Total
Highlights (2020)
Pilot operation

## LENINGRAD 2
2020 Operating Experience
RU-16 | [8 empty] | LENINGRAD-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-06-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-07-11
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-02-11
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 211 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4754.95 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.84 %
Energy Availability Factor (EAF) | [18 empty] | : | 68.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.61 %
Unit Capability Factor (UCF) | [18 empty] | : | 71.67 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 27.73 %
Load Factor (LF) | [18 empty] | : | 67.53 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.38 %
Operating Factor (OF) | [18 empty] | : | 72.92 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2005 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 15.66 GW(e).h
Annual Summary
[5 empty] | Dec | Nov |  |  |  | Jan |  | Feb | [8 empty] | Mar |  |  | Apr | [6 empty] | May |  | Jun |  |  |  | Jul |  |  | Aug |  |  | Sep | [9 empty] | Oct |  |  | Annual
GW(e)-h | [9 empty] | 670.79 |  | 105.08 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 618.70 |  | 639.49 |  |  |  | 624.66 |  |  | 643.32 |  |  | 622.98 | [9 empty] | 647.24 |  |  | 4572.28
EAF [%] | [9 empty] | 98.39 |  | 17.13 | [8 empty] | 0.00 |  |  | 1.73 | [6 empty] | 93.30 |  | 95.87 |  |  |  | 91.07 |  |  | 93.73 |  |  | 93.71 | [9 empty] | 94.18 |  |  | 68.28
UCF [%] | [9 empty] | 100.00 |  | 17.44 | [8 empty] | 0.00 |  |  | 1.73 | [6 empty] | 95.44 |  | 100.00 |  |  |  | 98.11 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 71.67
LF [%] | [9 empty] | 97.47 |  | 16.32 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 89.90 |  | 96.02 |  |  |  | 90.77 |  |  | 93.48 |  |  | 93.54 | [9 empty] | 94.05 |  |  | 67.53
OF [%] | [9 empty] | 100.00 |  | 20.55 | [8 empty] | 0.00 |  |  | 4.86 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 72.92
FLR [%] | [9 empty] | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 4.11 |  | 0.00 |  |  |  | 1.89 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.84
UCL [%] | [9 empty] | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 4.10 |  | 0.00 |  |  |  | 1.89 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.61
PUF [%] | [9 empty] | 0.00 |  | 82.56 | [8 empty] | 100.00 |  |  | 98.27 | [6 empty] | 0.47 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 27.73
XUF [%] | [9 empty] | 1.61 |  | 0.32 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 2.14 |  | 4.13 |  |  |  | 7.05 |  |  | 6.27 |  |  | 6.29 | [9 empty] | 5.82 |  |  | 3.38
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 255713.79 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.21 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 70.12 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.24 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 70.93 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 25.83 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 69.84 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.81 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 75.65 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | 5492.29 |  |  | 7654 |  |  |  | 925 | [10 empty] | 67.86 |  |  |  | 67.92 | [5 empty] | 65.53 |  |  | 85.95 |  |  |  | 18.92 |  | 15.85 | [8 empty] | 16.23 |  |  |  |  | 0.06
1977 |  |  |  | 5413.69 |  |  | 7337 |  |  |  | 925 | [10 empty] | 67.08 |  |  |  | 67.17 | [5 empty] | 66.81 |  |  | 83.76 |  |  |  | 17.69 |  | 14.43 | [8 empty] | 18.40 |  |  |  |  | 0.09
1978 |  |  |  | 6310.80 |  |  | 8008 |  |  |  | 925 | [10 empty] | 78.78 |  |  |  | 78.78 | [5 empty] | 77.88 |  |  | 91.42 |  |  |  | 11.71 |  | 10.44 | [8 empty] | 10.78 |  |  |  |  | 0.00
1979 |  |  |  | 5633.67 |  |  | 6954 |  |  |  | 925 | [10 empty] | 70.08 |  |  |  | 70.08 | [5 empty] | 69.53 |  |  | 79.38 |  |  |  | 11.10 |  | 8.75 | [8 empty] | 21.17 |  |  |  |  | 0.00
1980 |  |  |  | 6351.84 |  |  | 7960 |  |  |  | 925 | [10 empty] | 78.62 |  |  |  | 78.83 | [5 empty] | 78.17 |  |  | 90.62 |  |  |  | 5.91 |  | 4.96 | [8 empty] | 16.22 |  |  |  |  | 0.21
1981 |  |  |  | 5177.19 |  |  | 6057 |  |  |  | 925 | [10 empty] | 61.97 |  |  |  | 61.97 | [5 empty] | 63.89 |  |  | 69.14 |  |  |  | 15.79 |  | 11.62 | [8 empty] | 26.41 |  |  |  |  | 0.00
1982 |  |  |  | 7266.78 |  |  | 8125 |  |  |  | 925 | [10 empty] | 89.86 |  |  |  | 90.38 | [5 empty] | 89.68 |  |  | 92.75 |  |  |  | 2.86 |  | 2.66 | [8 empty] | 6.95 |  |  |  |  | 0.52
1983 |  |  |  | 6790.78 |  |  | 7479 |  |  |  | 925 | [10 empty] | 83.56 |  |  |  | 84.24 | [5 empty] | 83.81 |  |  | 85.38 |  |  |  | 2.47 |  | 2.13 | [8 empty] | 13.63 |  |  |  |  | 0.69
1984 |  |  |  | 7145.90 |  |  | 7881 |  |  |  | 925 | [10 empty] | 87.42 |  |  |  | 87.63 | [5 empty] | 87.95 |  |  | 89.72 |  |  |  | 3.80 |  | 3.47 | [8 empty] | 8.91 |  |  |  |  | 0.21
1985 |  |  |  | 5962.57 |  |  | 6604 |  |  |  | 925 | [10 empty] | 74.32 |  |  |  | 74.36 | [5 empty] | 73.58 |  |  | 75.39 |  |  |  | 5.13 |  | 4.02 | [8 empty] | 21.62 |  |  |  |  | 0.04
1986 |  |  |  | 7152.34 |  |  | 7914 |  |  |  | 925 | [10 empty] | 88.12 |  |  |  | 88.44 | [5 empty] | 88.27 |  |  | 90.34 |  |  |  | 1.57 |  | 1.41 | [8 empty] | 10.15 |  |  |  |  | 0.32
1987 |  |  |  | 7228.20 |  |  | 7513 |  |  |  | 1000 | [10 empty] | 82.95 |  |  |  | 83.71 | [5 empty] | 82.51 |  |  | 85.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.29 |  |  |  |  | 0.75
1988 |  |  |  | 6814.92 |  |  | 7417 |  |  |  | 925 | [10 empty] | 83.59 |  |  |  | 83.59 | [5 empty] | 83.87 |  |  | 84.44 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 16.36 |  |  |  |  | 0.00
1989 |  |  |  | 6111.49 |  |  | 7102 |  |  |  | 925 | [10 empty] | 75.63 |  |  |  | 75.81 | [5 empty] | 75.42 |  |  | 81.07 |  |  |  | 0.98 |  | 0.75 | [8 empty] | 23.44 |  |  |  |  | 0.19
1990 |  |  |  | 5998.30 |  |  | 8125 |  |  |  | 925 | [10 empty] | 75.34 |  |  |  | 75.47 | [5 empty] | 74.03 |  |  | 92.75 |  |  |  | 21.18 |  | 20.28 | [8 empty] | 4.25 |  |  |  |  | 0.13
1991 |  |  |  | 4410.75 |  |  | 7204 |  |  |  | 925 | [10 empty] | 56.34 |  |  |  | 56.37 | [5 empty] | 54.43 |  |  | 82.24 |  |  |  | 1.96 |  | 1.13 | [8 empty] | 42.50 |  |  |  |  | 0.03
1992 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1993 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1994 |  |  |  | 164.10 |  |  | 660 |  |  |  | 925 | [10 empty] | 2.31 |  |  |  | 2.31 | [5 empty] | 2.03 |  |  | 7.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 97.69 |  |  |  |  | 0.00
1995 |  |  |  | 6812.05 |  |  | 8280 |  |  |  | 925 | [10 empty] | 86.18 |  |  |  | 93.38 | [5 empty] | 84.07 |  |  | 94.52 |  |  |  | 2.41 |  | 2.31 | [8 empty] | 4.31 |  |  |  |  | 7.21
1996 |  |  |  | 7244.91 |  |  | 7922 |  |  |  | 925 | [10 empty] | 89.06 |  |  |  | 89.42 | [5 empty] | 89.17 |  |  | 90.19 |  |  |  | 2.42 |  | 2.22 | [8 empty] | 8.36 |  |  |  |  | 0.36
1997 |  |  |  | 6587.14 |  |  | 7342 |  |  |  | 925 | [10 empty] | 82.64 |  |  |  | 83.13 | [5 empty] | 81.29 |  |  | 83.81 |  |  |  | 0.34 |  | 0.29 | [8 empty] | 16.58 |  |  |  |  | 0.50
1998 |  |  |  | 5916.70 |  |  | 6643 |  |  |  | 925 | [10 empty] | 72.45 |  |  |  | 73.43 | [5 empty] | 73.02 |  |  | 75.83 |  |  |  | 5.96 |  | 4.65 | [8 empty] | 21.91 |  |  |  |  | 0.98
1999 |  |  |  | 6557.78 |  |  | 7299 |  |  |  | 925 | [10 empty] | 80.19 |  |  |  | 80.59 | [5 empty] | 80.93 |  |  | 83.32 |  |  |  | 0.55 |  | 0.44 | [8 empty] | 18.96 |  |  |  |  | 0.40
2000 |  |  |  | 7252.55 |  |  | 7972 |  |  |  | 925 | [10 empty] | 88.59 |  |  |  | 90.13 | [5 empty] | 89.26 |  |  | 90.76 |  |  |  | 1.41 |  | 1.29 | [8 empty] | 8.58 |  |  |  |  | 1.53
2001 |  |  |  | 7073.50 |  |  | 7904 |  |  |  | 925 | [10 empty] | 86.60 |  |  |  | 88.46 | [5 empty] | 87.29 |  |  | 90.23 |  |  |  | 3.39 |  | 3.10 | [8 empty] | 8.44 |  |  |  |  | 1.86
2002 |  |  |  | 7024.86 |  |  | 7961 |  |  |  | 925 | [10 empty] | 86.58 |  |  |  | 88.71 | [5 empty] | 86.69 |  |  | 90.88 |  |  |  | 0.97 |  | 0.87 | [8 empty] | 10.42 |  |  |  |  | 2.13
2003 |  |  |  | 7134.43 |  |  | 8298 |  |  |  | 925 | [10 empty] | 87.96 |  |  |  | 90.92 | [5 empty] | 88.05 |  |  | 94.73 |  |  |  | 3.71 |  | 3.50 | [8 empty] | 5.57 |  |  |  |  | 2.96
2004 |  |  |  | 6711.54 |  |  | 7832 |  |  |  | 925 | [10 empty] | 82.87 |  |  |  | 86.40 | [5 empty] | 82.60 |  |  | 89.16 |  |  |  | 2.88 |  | 2.56 | [8 empty] | 11.04 |  |  |  |  | 3.52
2005 |  |  |  | 3763.24 |  |  | 4557 |  |  |  | 925 | [10 empty] | 46.61 |  |  |  | 50.09 | [5 empty] | 46.44 |  |  | 52.02 |  |  |  | 1.61 |  | 0.82 | [8 empty] | 49.10 |  |  |  |  | 3.47
2006 |  |  |  | 1461.44 |  |  | 1760 |  |  |  | 925 | [10 empty] | 18.13 |  |  |  | 18.13 | [5 empty] | 18.04 |  |  | 20.09 |  |  |  | 7.77 |  | 2.17 | [8 empty] | 79.70 |  |  |  |  | 0.00
2007 |  |  |  | 6461.37 |  |  | 7077 |  |  |  | 925 | [10 empty] | 78.97 |  |  |  | 80.12 | [5 empty] | 79.74 |  |  | 80.79 |  |  |  | 1.47 |  | 1.87 | [8 empty] | 18.01 |  |  |  |  | 1.15
2008 |  |  |  | 7017.53 |  |  | 7810 |  |  |  | 925 | [10 empty] | 88.06 |  |  |  | 88.26 | [5 empty] | 86.37 |  |  | 88.91 |  |  |  | 0.53 |  | 0.47 | [8 empty] | 11.27 |  |  |  |  | 0.20
2009 |  |  |  | 7278.61 |  |  | 8310 |  |  |  | 925 | [10 empty] | 93.44 |  |  |  | 93.80 | [5 empty] | 89.83 |  |  | 94.86 |  |  |  | 0.70 |  | 0.66 | [8 empty] | 5.54 |  |  |  |  | 0.36
2010 |  |  |  | 6434.67 |  |  | 7352 |  |  |  | 925 | [10 empty] | 79.65 |  |  |  | 79.98 | [5 empty] | 79.41 |  |  | 83.93 |  |  |  | 1.63 |  | 3.72 | [8 empty] | 16.31 |  |  |  |  | 0.33
2011 |  |  |  | 7751.04 |  |  | 8362 |  |  |  | 925 | [10 empty] | 94.27 |  |  |  | 94.42 | [5 empty] | 95.67 |  |  | 95.47 |  |  |  | 1.46 |  | 1.39 | [8 empty] | 4.18 |  |  |  |  | 0.15
2012 |  |  |  | 5326.19 |  |  | 6317 |  |  |  | 925 | [10 empty] | 65.45 |  |  |  | 65.51 | [5 empty] | 65.55 |  |  | 71.91 |  |  |  | 1.91 |  | 2.20 | [8 empty] | 32.29 |  |  |  |  | 0.05
2013 |  |  |  | 3311.25 |  |  | 5181 |  |  |  | 925 | [10 empty] | 41.63 |  |  |  | 42.40 | [5 empty] | 40.86 |  |  | 59.14 |  |  |  | 0.04 |  | 0.02 | [8 empty] | 57.59 |  |  |  |  | 0.76
2014 |  |  |  | 3213.99 |  |  | 4406 |  |  |  | 925 | [10 empty] | 40.52 |  |  |  | 40.76 | [5 empty] | 39.66 |  |  | 50.29 |  |  |  | 0.74 |  | 1.08 | [8 empty] | 58.16 |  |  |  |  | 0.23
2015 |  |  |  | 6558.58 |  |  | 7316 |  |  |  | 925 | [10 empty] | 81.96 |  |  |  | 82.14 | [5 empty] | 80.94 |  |  | 83.52 |  |  |  | 3.73 |  | 3.18 | [8 empty] | 14.68 |  |  |  |  | 0.18
2016 |  |  |  | 5602.15 |  |  | 6037 |  |  |  | 925 | [10 empty] | 67.74 |  |  |  | 67.85 | [5 empty] | 68.95 |  |  | 68.73 |  |  |  | 0.56 |  | 0.38 | [8 empty] | 31.77 |  |  |  |  | 0.11
2017 |  |  |  | 6331.28 |  |  | 7160 |  |  |  | 925 | [10 empty] | 78.58 |  |  |  | 78.83 | [5 empty] | 78.13 |  |  | 81.74 |  |  |  | 3.67 |  | 3.00 | [8 empty] | 18.16 |  |  |  |  | 0.25
2018 |  |  |  | 5668.25 |  |  | 6265 |  |  |  | 925 | [10 empty] | 69.74 |  |  |  | 70.20 | [5 empty] | 69.95 |  |  | 71.52 |  |  |  | 1.02 |  | 0.73 | [8 empty] | 29.07 |  |  |  |  | 0.46
2019 |  |  |  | 5996.32 |  |  | 6791 |  |  |  | 925 | [10 empty] | 73.94 |  |  |  | 74.94 | [5 empty] | 74.00 |  |  | 77.52 |  |  |  | 1.69 |  | 1.29 | [8 empty] | 23.77 |  |  |  |  | 1.00
2020 |  |  |  | 4754.95 |  |  | 5555 |  |  |  | 925 | [10 empty] | 68.28 |  |  |  | 71.67 | [5 empty] | 67.53 |  |  | 72.92 |  |  |  | 0.84 |  | 0.61 | [8 empty] | 27.73 |  |  |  |  | 3.38
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1976 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 77
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1982 | [14 empty] | 1083
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 715
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 1
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 246
L. |  | Human factor related | [39 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [20 empty] | 24 | [14 empty] | 1
Subtotal | [22 empty] | 2006 | [14 empty] | 2047 |  |  |  | 80 | [11 empty] | 1
Total | [22 empty] | 2006 | [14 empty] | 2128
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1976 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
15. |  |  | Reactor Cooling Systems | [34 empty] | 17
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 6
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 18
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 77
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the intermediate outage from 2020.02.06 to 2020.05.01. Unit shutdown 2020.11.10 for set-up operations for decommissioning. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD 3
2020 Operating Experience
RU-34 | [8 empty] | LENINGRAD-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-12-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1979-12-07
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-06-29
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 211 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5765.23 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 70.51 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.72 %
Unit Capability Factor (UCF) | [18 empty] | : | 70.53 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 28.75 %
Load Factor (LF) | [18 empty] | : | 70.95 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.01 %
Operating Factor (OF) | [18 empty] | : | 71.37 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2515 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 71.42 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 700.37 | 669.31 |  |  |  | 639.27 |  | 683.21 | [8 empty] | 282.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 52.07 |  |  |  | 661.17 |  |  | 696.69 |  |  | 675.80 | [9 empty] | 705.32 |  |  | 5765.23
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 92.35 |  | 100.00 | [8 empty] | 47.05 |  |  | 0.00 | [6 empty] | 0.00 |  | 10.29 |  |  |  | 99.21 |  |  | 99.74 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 70.51
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 92.35 |  | 100.00 | [8 empty] | 47.05 |  |  | 0.00 | [6 empty] | 0.00 |  | 10.29 |  |  |  | 99.34 |  |  | 99.74 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 70.53
LF [%] |  |  |  |  | 101.77 | 103.96 |  |  |  | 92.89 |  | 102.58 | [8 empty] | 40.98 |  |  | 0.00 | [6 empty] | 0.00 |  | 7.57 |  |  |  | 99.27 |  |  | 101.23 |  |  | 101.47 | [9 empty] | 102.49 |  |  | 70.95
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.82 |  | 100.00 | [8 empty] | 48.39 |  |  | 0.00 | [6 empty] | 0.00 |  | 16.53 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 71.37
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 7.65 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.65 |  |  | 0.26 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.02
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 7.65 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.65 |  |  | 0.26 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.72
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 52.95 |  |  | 100.00 | [6 empty] | 100.00 |  | 89.71 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 28.75
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.13 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 240635.95 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.76 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.43 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.95 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.28 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 22.77 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.39 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.85 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.26 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 5345.39 |  |  | 7504 |  |  |  | 925 | [10 empty] | 81.59 |  |  |  | 81.61 | [5 empty] | 80.55 |  |  | 90.94 |  |  |  | 10.86 |  | 9.95 | [8 empty] | 8.45 |  |  |  |  | 0.02
1981 |  |  |  | 6553.56 |  |  | 7528 |  |  |  | 925 | [10 empty] | 81.35 |  |  |  | 81.66 | [5 empty] | 80.88 |  |  | 85.94 |  |  |  | 9.31 |  | 8.38 | [8 empty] | 9.96 |  |  |  |  | 0.32
1982 |  |  |  | 6413.26 |  |  | 7448 |  |  |  | 925 | [10 empty] | 80.27 |  |  |  | 80.80 | [5 empty] | 79.15 |  |  | 85.02 |  |  |  | 7.18 |  | 6.25 | [8 empty] | 12.95 |  |  |  |  | 0.53
1983 |  |  |  | 5708.44 |  |  | 6809 |  |  |  | 925 | [10 empty] | 70.90 |  |  |  | 71.30 | [5 empty] | 70.45 |  |  | 77.73 |  |  |  | 7.88 |  | 6.10 | [8 empty] | 22.61 |  |  |  |  | 0.39
1984 |  |  |  | 7214.95 |  |  | 8060 |  |  |  | 925 | [10 empty] | 89.22 |  |  |  | 89.76 | [5 empty] | 88.80 |  |  | 91.76 |  |  |  | 1.88 |  | 1.72 | [8 empty] | 8.52 |  |  |  |  | 0.55
1985 |  |  |  | 6831.90 |  |  | 7835 |  |  |  | 925 | [10 empty] | 84.94 |  |  |  | 85.42 | [5 empty] | 84.31 |  |  | 89.44 |  |  |  | 5.45 |  | 4.92 | [8 empty] | 9.67 |  |  |  |  | 0.47
1986 |  |  |  | 6890.93 |  |  | 7935 |  |  |  | 925 | [10 empty] | 85.89 |  |  |  | 86.44 | [5 empty] | 85.04 |  |  | 90.58 |  |  |  | 3.36 |  | 3.01 | [8 empty] | 10.55 |  |  |  |  | 0.55
1987 |  |  |  | 6010.31 |  |  | 6362 |  |  |  | 1000 | [10 empty] | 69.36 |  |  |  | 70.37 | [5 empty] | 68.61 |  |  | 72.63 |  |  |  | 1.12 |  | 0.79 | [8 empty] | 28.83 |  |  |  |  | 1.01
1988 |  |  |  | 6951.74 |  |  | 7885 |  |  |  | 925 | [10 empty] | 86.53 |  |  |  | 86.53 | [5 empty] | 85.56 |  |  | 89.77 |  |  |  | 1.44 |  | 1.26 | [8 empty] | 12.21 |  |  |  |  | 0.00
1989 |  |  |  | 6938.14 |  |  | 7455 |  |  |  | 925 | [10 empty] | 85.86 |  |  |  | 86.23 | [5 empty] | 85.62 |  |  | 85.10 |  |  |  | 0.97 |  | 0.84 | [8 empty] | 12.93 |  |  |  |  | 0.37
1990 |  |  |  | 7531.93 |  |  | 8280 |  |  |  | 925 | [10 empty] | 92.35 |  |  |  | 92.96 | [5 empty] | 92.95 |  |  | 94.52 |  |  |  | 1.36 |  | 1.28 | [8 empty] | 5.76 |  |  |  |  | 0.61
1991 |  |  |  | 6506.60 |  |  | 7197 |  |  |  | 925 | [10 empty] | 80.59 |  |  |  | 80.59 | [5 empty] | 80.30 |  |  | 82.16 |  |  |  | 1.25 |  | 1.02 | [8 empty] | 18.39 |  |  |  |  | 0.00
1992 |  |  |  | 5516.63 |  |  | 6122 |  |  |  | 925 | [10 empty] | 68.39 |  |  |  | 68.49 | [5 empty] | 67.90 |  |  | 69.70 |  |  |  | 2.92 |  | 2.06 | [8 empty] | 29.45 |  |  |  |  | 0.09
1993 |  |  |  | 7143.82 |  |  | 7966 |  |  |  | 925 | [10 empty] | 88.90 |  |  |  | 90.14 | [5 empty] | 88.16 |  |  | 90.94 |  |  |  | 0.56 |  | 0.51 | [8 empty] | 9.35 |  |  |  |  | 1.24
1994 |  |  |  | 6631.82 |  |  | 8135 |  |  |  | 925 | [10 empty] | 91.04 |  |  |  | 92.42 | [5 empty] | 81.84 |  |  | 92.87 |  |  |  | 0.26 |  | 0.24 | [8 empty] | 7.34 |  |  |  |  | 1.39
1995 |  |  |  | 3585.96 |  |  | 4332 |  |  |  | 925 | [10 empty] | 46.53 |  |  |  | 49.40 | [5 empty] | 44.25 |  |  | 49.45 |  |  |  | 0.44 |  | 0.22 | [8 empty] | 50.38 |  |  |  |  | 2.87
1996 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1998 |  |  |  | 1386.50 |  |  | 1610 |  |  |  | 925 | [10 empty] | 17.41 |  |  |  | 17.49 | [5 empty] | 17.11 |  |  | 18.38 |  |  |  | 4.00 |  | 0.73 | [8 empty] | 81.78 |  |  |  |  | 0.08
1999 |  |  |  | 7853.14 |  |  | 8701 |  |  |  | 925 | [10 empty] | 97.08 |  |  |  | 99.66 | [5 empty] | 96.92 |  |  | 99.33 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.00 |  |  |  |  | 2.58
2000 |  |  |  | 6352.80 |  |  | 7169 |  |  |  | 925 | [10 empty] | 78.25 |  |  |  | 79.64 | [5 empty] | 78.19 |  |  | 81.61 |  |  |  | 1.83 |  | 1.49 | [8 empty] | 18.87 |  |  |  |  | 1.39
2001 |  |  |  | 6173.49 |  |  | 7007 |  |  |  | 925 | [10 empty] | 76.58 |  |  |  | 78.92 | [5 empty] | 76.19 |  |  | 79.99 |  |  |  | 0.19 |  | 0.15 | [8 empty] | 20.93 |  |  |  |  | 2.34
2002 |  |  |  | 2514.75 |  |  | 3332 |  |  |  | 925 | [10 empty] | 31.88 |  |  |  | 33.60 | [5 empty] | 31.03 |  |  | 38.04 |  |  |  | 17.29 |  | 7.02 | [8 empty] | 59.38 |  |  |  |  | 1.72
2003 |  |  |  | 6729.17 |  |  | 8100 |  |  |  | 925 | [10 empty] | 84.54 |  |  |  | 86.65 | [5 empty] | 83.05 |  |  | 92.47 |  |  |  | 6.00 |  | 5.53 | [8 empty] | 7.82 |  |  |  |  | 2.11
2004 |  |  |  | 6909.08 |  |  | 8426 |  |  |  | 925 | [10 empty] | 86.47 |  |  |  | 90.86 | [5 empty] | 85.03 |  |  | 95.92 |  |  |  | 5.04 |  | 4.82 | [8 empty] | 4.31 |  |  |  |  | 4.40
2005 |  |  |  | 4447.28 |  |  | 5397 |  |  |  | 925 | [10 empty] | 61.10 |  |  |  | 61.46 | [5 empty] | 54.88 |  |  | 61.60 |  |  |  | 2.72 |  | 1.72 | [8 empty] | 36.83 |  |  |  |  | 0.36
2006 |  |  |  | 7332.11 |  |  | 8274 |  |  |  | 925 | [10 empty] | 89.86 |  |  |  | 89.86 | [5 empty] | 90.49 |  |  | 94.45 |  |  |  | 2.22 |  | 4.89 | [8 empty] | 5.25 |  |  |  |  | 0.00
2007 |  |  |  | 3755.96 |  |  | 4820 |  |  |  | 925 | [10 empty] | 47.04 |  |  |  | 54.08 | [5 empty] | 46.35 |  |  | 55.02 |  |  |  | 0.24 |  | 0.13 | [8 empty] | 45.78 |  |  |  |  | 7.04
2008 |  |  |  | 5013.64 |  |  | 5632 |  |  |  | 925 | [10 empty] | 62.68 |  |  |  | 62.71 | [5 empty] | 61.70 |  |  | 64.12 |  |  |  | 1.64 |  | 7.69 | [8 empty] | 29.60 |  |  |  |  | 0.03
2009 |  |  |  | 5336.12 |  |  | 6209 |  |  |  | 925 | [10 empty] | 70.38 |  |  |  | 70.65 | [5 empty] | 65.85 |  |  | 70.88 |  |  |  | 3.40 |  | 22.58 | [8 empty] | 6.78 |  |  |  |  | 0.26
2010 |  |  |  | 7303.22 |  |  | 8261 |  |  |  | 925 | [10 empty] | 92.58 |  |  |  | 92.88 | [5 empty] | 90.13 |  |  | 94.30 |  |  |  | 1.27 |  | 1.19 | [8 empty] | 5.93 |  |  |  |  | 0.29
2011 |  |  |  | 6803.29 |  |  | 7548 |  |  |  | 925 | [10 empty] | 83.65 |  |  |  | 83.81 | [5 empty] | 83.97 |  |  | 86.17 |  |  |  | 0.47 |  | 1.73 | [8 empty] | 14.46 |  |  |  |  | 0.15
2012 |  |  |  | 7401.44 |  |  | 8115 |  |  |  | 925 | [10 empty] | 91.56 |  |  |  | 91.65 | [5 empty] | 91.09 |  |  | 92.38 |  |  |  | 2.66 |  | 2.51 | [8 empty] | 5.84 |  |  |  |  | 0.10
2013 |  |  |  | 6892.27 |  |  | 7446 |  |  |  | 925 | [10 empty] | 83.65 |  |  |  | 83.95 | [5 empty] | 85.06 |  |  | 85.00 |  |  |  | 1.79 |  | 1.55 | [8 empty] | 14.50 |  |  |  |  | 0.30
2014 |  |  |  | 7199.40 |  |  | 8229 |  |  |  | 925 | [10 empty] | 89.69 |  |  |  | 90.10 | [5 empty] | 88.84 |  |  | 93.93 |  |  |  | 1.79 |  | 4.75 | [8 empty] | 5.15 |  |  |  |  | 0.41
2015 |  |  |  | 6817.12 |  |  | 7628 |  |  |  | 925 | [10 empty] | 86.76 |  |  |  | 86.85 | [5 empty] | 84.13 |  |  | 87.08 |  |  |  | 2.01 |  | 1.78 | [8 empty] | 11.37 |  |  |  |  | 0.09
2016 |  |  |  | 7024.91 |  |  | 7879 |  |  |  | 925 | [10 empty] | 87.77 |  |  |  | 87.94 | [5 empty] | 86.46 |  |  | 89.70 |  |  |  | 2.71 |  | 2.45 | [8 empty] | 9.62 |  |  |  |  | 0.16
2017 |  |  |  | 6786.43 |  |  | 7460 |  |  |  | 925 | [10 empty] | 84.94 |  |  |  | 84.96 | [5 empty] | 83.75 |  |  | 85.16 |  |  |  | 1.87 |  | 1.62 | [8 empty] | 13.42 |  |  |  |  | 0.03
2018 |  |  |  | 5801.48 |  |  | 6257 |  |  |  | 925 | [10 empty] | 72.16 |  |  |  | 72.21 | [5 empty] | 71.60 |  |  | 71.43 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 27.77 |  |  |  |  | 0.05
2019 |  |  |  | 6890.81 |  |  | 7642 |  |  |  | 925 | [10 empty] | 84.69 |  |  |  | 84.85 | [5 empty] | 85.04 |  |  | 87.24 |  |  |  | 0.65 |  | 0.56 | [8 empty] | 14.59 |  |  |  |  | 0.16
2020 |  |  |  | 5765.23 |  |  | 6269 |  |  |  | 925 | [10 empty] | 70.51 |  |  |  | 70.53 | [5 empty] | 70.95 |  |  | 71.37 |  |  |  | 1.02 |  | 0.72 | [8 empty] | 28.75 |  |  |  |  | 0.01
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1980 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 67 | [14 empty] | 105
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2490 | [14 empty] | 781
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 942
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 17
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 129
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 79
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 13
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 2490 |  |  |  | 67 | [10 empty] | 1932 |  |  |  | 126 | [11 empty] | 17
Total | [22 empty] | 2557 | [14 empty] | 2075
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1980 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
12. |  |  | Reactor I&C Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 6
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 54
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
33. |  |  | Circulating Water System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 17
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [19 empty] | 67 | [14 empty] | 13
Total | [22 empty] | 67 | [14 empty] | 123
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-May, August-December. Additional electricity generation amounted to 137449 MWh. The unit was in the routine maintenance outage from 2020.05.15 to 2020.0831. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD 4
2020 Operating Experience
RU-35 | [8 empty] | LENINGRAD-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-02-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-02-09
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-08-29
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 211 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6842.29 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.42 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.44 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.35 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.44 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.2 %
Load Factor (LF) | [18 empty] | : | 84.21 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.01 %
Operating Factor (OF) | [18 empty] | : | 85.22 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1298 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 105.76 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 697.67 | 663.63 |  |  |  | 636.99 |  | 654.14 | [8 empty] | 682.67 |  |  | 681.02 | [6 empty] | 389.18 |  | 0.00 |  |  |  | 406.38 |  |  | 707.04 |  |  | 646.24 | [9 empty] | 677.30 |  |  | 6842.29
EAF [%] |  |  |  |  | 100.00 | 99.80 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.81 | [6 empty] | 57.33 |  | 0.00 |  |  |  | 61.95 |  |  | 100.00 |  |  | 97.27 | [9 empty] | 98.74 |  |  | 84.44
UCF [%] |  |  |  |  | 100.00 | 99.80 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.90 | [6 empty] | 57.33 |  | 0.00 |  |  |  | 61.96 |  |  | 100.00 |  |  | 97.27 | [9 empty] | 98.74 |  |  | 84.44
LF [%] |  |  |  |  | 101.38 | 103.08 |  |  |  | 92.56 |  | 98.22 | [8 empty] | 99.20 |  |  | 102.26 | [6 empty] | 56.55 |  | 0.00 |  |  |  | 61.02 |  |  | 102.74 |  |  | 97.03 | [9 empty] | 98.42 |  |  | 84.21
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 60.22 |  | 0.00 |  |  |  | 64.17 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.22
FLR [%] |  |  |  |  | 0.00 | 0.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.10 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.73 | [9 empty] | 1.26 |  |  | 0.42
UCL [%] |  |  |  |  | 0.00 | 0.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.10 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.73 | [9 empty] | 1.26 |  |  | 0.35
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 42.67 |  | 100.00 |  |  |  | 38.04 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.20
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.10 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 231728.76 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.99 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.87 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.03 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.81 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.16 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.05 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.94 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.54 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 3931.27 |  |  | 6151 |  |  |  | 925 | [10 empty] | 76.82 |  |  |  | 76.83 | [5 empty] | 76.06 |  |  | 83.41 |  |  |  | 12.21 |  | 10.69 | [8 empty] | 12.48 |  |  |  |  | 0.01
1982 |  |  |  | 6715.19 |  |  | 7609 |  |  |  | 925 | [10 empty] | 83.59 |  |  |  | 83.72 | [5 empty] | 82.87 |  |  | 86.86 |  |  |  | 4.43 |  | 3.88 | [8 empty] | 12.40 |  |  |  |  | 0.13
1983 |  |  |  | 6844.23 |  |  | 8159 |  |  |  | 925 | [10 empty] | 85.33 |  |  |  | 86.12 | [5 empty] | 84.47 |  |  | 93.14 |  |  |  | 6.80 |  | 6.29 | [8 empty] | 7.59 |  |  |  |  | 0.79
1984 |  |  |  | 6126.32 |  |  | 6803 |  |  |  | 925 | [10 empty] | 74.43 |  |  |  | 74.94 | [5 empty] | 75.40 |  |  | 77.45 |  |  |  | 3.19 |  | 2.47 | [8 empty] | 22.59 |  |  |  |  | 0.52
1985 |  |  |  | 7335.31 |  |  | 8309 |  |  |  | 925 | [10 empty] | 90.92 |  |  |  | 91.18 | [5 empty] | 90.53 |  |  | 94.85 |  |  |  | 3.29 |  | 3.10 | [8 empty] | 5.72 |  |  |  |  | 0.26
1986 |  |  |  | 7060.95 |  |  | 7826 |  |  |  | 925 | [10 empty] | 87.65 |  |  |  | 88.69 | [5 empty] | 87.14 |  |  | 89.34 |  |  |  | 0.49 |  | 0.44 | [8 empty] | 10.87 |  |  |  |  | 1.04
1987 |  |  |  | 7319.23 |  |  | 7530 |  |  |  | 1000 | [10 empty] | 84.15 |  |  |  | 85.01 | [5 empty] | 83.55 |  |  | 85.96 |  |  |  | 2.18 |  | 1.90 | [8 empty] | 13.09 |  |  |  |  | 0.86
1988 |  |  |  | 6050.44 |  |  | 6667 |  |  |  | 925 | [10 empty] | 74.82 |  |  |  | 74.82 | [5 empty] | 74.47 |  |  | 75.90 |  |  |  | 0.72 |  | 0.54 | [8 empty] | 24.64 |  |  |  |  | 0.00
1989 |  |  |  | 7409.69 |  |  | 8185 |  |  |  | 925 | [10 empty] | 91.46 |  |  |  | 91.89 | [5 empty] | 91.44 |  |  | 93.44 |  |  |  | 2.23 |  | 2.10 | [8 empty] | 6.01 |  |  |  |  | 0.43
1990 |  |  |  | 7762.56 |  |  | 8588 |  |  |  | 925 | [10 empty] | 95.38 |  |  |  | 96.06 | [5 empty] | 95.80 |  |  | 98.04 |  |  |  | 2.33 |  | 2.29 | [8 empty] | 1.65 |  |  |  |  | 0.68
1991 |  |  |  | 6130.70 |  |  | 6870 |  |  |  | 925 | [10 empty] | 76.14 |  |  |  | 76.77 | [5 empty] | 75.66 |  |  | 78.42 |  |  |  | 1.77 |  | 1.38 | [8 empty] | 21.85 |  |  |  |  | 0.62
1992 |  |  |  | 5618.11 |  |  | 6617 |  |  |  | 925 | [10 empty] | 70.29 |  |  |  | 70.79 | [5 empty] | 69.15 |  |  | 75.34 |  |  |  | 4.30 |  | 3.18 | [8 empty] | 26.02 |  |  |  |  | 0.51
1993 |  |  |  | 6735.70 |  |  | 7762 |  |  |  | 925 | [10 empty] | 85.27 |  |  |  | 87.61 | [5 empty] | 83.13 |  |  | 88.61 |  |  |  | 1.54 |  | 1.37 | [8 empty] | 11.02 |  |  |  |  | 2.34
1994 |  |  |  | 6167.07 |  |  | 7340 |  |  |  | 925 | [10 empty] | 82.08 |  |  |  | 83.16 | [5 empty] | 76.11 |  |  | 83.79 |  |  |  | 1.33 |  | 1.12 | [8 empty] | 15.72 |  |  |  |  | 1.07
1995 |  |  |  | 6140.97 |  |  | 7270 |  |  |  | 925 | [10 empty] | 82.96 |  |  |  | 86.06 | [5 empty] | 75.79 |  |  | 82.99 |  |  |  | 0.29 |  | 0.25 | [8 empty] | 13.69 |  |  |  |  | 3.11
1996 |  |  |  | 7079.69 |  |  | 8048 |  |  |  | 925 | [10 empty] | 88.30 |  |  |  | 88.78 | [5 empty] | 87.13 |  |  | 91.62 |  |  |  | 4.63 |  | 4.31 | [8 empty] | 6.91 |  |  |  |  | 0.47
1997 |  |  |  | 7644.68 |  |  | 8760 |  |  |  | 925 | [10 empty] | 95.95 |  |  |  | 98.19 | [5 empty] | 94.34 |  |  | 100.00 |  |  |  | 1.81 |  | 1.81 | [8 empty] | 0.00 |  |  |  |  | 2.24
1998 |  |  |  | 3681.98 |  |  | 4341 |  |  |  | 925 | [10 empty] | 45.98 |  |  |  | 47.31 | [5 empty] | 45.44 |  |  | 49.55 |  |  |  | 2.11 |  | 1.02 | [8 empty] | 51.68 |  |  |  |  | 1.32
1999 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2000 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2001 |  |  |  | 3585.73 |  |  | 4387 |  |  |  | 925 | [10 empty] | 44.56 |  |  |  | 45.54 | [5 empty] | 44.25 |  |  | 50.08 |  |  |  | 23.52 |  | 14.00 | [8 empty] | 40.46 |  |  |  |  | 0.98
2002 |  |  |  | 7528.53 |  |  | 8760 |  |  |  | 925 | [10 empty] | 93.93 |  |  |  | 97.55 | [5 empty] | 92.91 |  |  | 100.00 |  |  |  | 2.45 |  | 2.45 | [8 empty] | 0.00 |  |  |  |  | 3.62
2003 |  |  |  | 1957.16 |  |  | 2399 |  |  |  | 925 | [10 empty] | 24.69 |  |  |  | 26.03 | [5 empty] | 24.15 |  |  | 27.39 |  |  |  | 2.58 |  | 0.69 | [8 empty] | 73.28 |  |  |  |  | 1.35
2004 |  |  |  | 7232.18 |  |  | 8243 |  |  |  | 925 | [10 empty] | 89.58 |  |  |  | 92.27 | [5 empty] | 89.01 |  |  | 93.84 |  |  |  | 3.43 |  | 3.28 | [8 empty] | 4.45 |  |  |  |  | 2.70
2005 |  |  |  | 6730.12 |  |  | 7838 |  |  |  | 925 | [10 empty] | 83.76 |  |  |  | 89.33 | [5 empty] | 83.05 |  |  | 89.46 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 10.57 |  |  |  |  | 5.57
2006 |  |  |  | 5611.94 |  |  | 6197 |  |  |  | 925 | [10 empty] | 69.36 |  |  |  | 69.36 | [5 empty] | 69.26 |  |  | 70.74 |  |  |  | 0.80 |  | 1.36 | [8 empty] | 29.29 |  |  |  |  | 0.00
2007 |  |  |  | 4827.43 |  |  | 5713 |  |  |  | 925 | [10 empty] | 59.73 |  |  |  | 64.85 | [5 empty] | 59.58 |  |  | 65.22 |  |  |  | 3.84 |  | 18.24 | [8 empty] | 16.91 |  |  |  |  | 5.11
2008 |  |  |  | 7526.25 |  |  | 8714 |  |  |  | 925 | [10 empty] | 94.69 |  |  |  | 94.90 | [5 empty] | 92.63 |  |  | 99.20 |  |  |  | 2.93 |  | 2.86 | [8 empty] | 2.24 |  |  |  |  | 0.22
2009 |  |  |  | 4052.83 |  |  | 4695 |  |  |  | 925 | [10 empty] | 53.23 |  |  |  | 53.37 | [5 empty] | 50.02 |  |  | 53.60 |  |  |  | 4.90 |  | 2.75 | [8 empty] | 43.88 |  |  |  |  | 0.14
2010 |  |  |  | 5222.37 |  |  | 5798 |  |  |  | 925 | [10 empty] | 64.04 |  |  |  | 64.18 | [5 empty] | 64.45 |  |  | 66.19 |  |  |  | 3.64 |  | 9.60 | [8 empty] | 26.21 |  |  |  |  | 0.14
2011 |  |  |  | 6589.79 |  |  | 7177 |  |  |  | 925 | [10 empty] | 80.76 |  |  |  | 81.01 | [5 empty] | 81.33 |  |  | 81.94 |  |  |  | 3.53 |  | 4.93 | [8 empty] | 14.06 |  |  |  |  | 0.25
2012 |  |  |  | 7559.92 |  |  | 8254 |  |  |  | 925 | [10 empty] | 92.28 |  |  |  | 92.30 | [5 empty] | 93.04 |  |  | 93.97 |  |  |  | 0.23 |  | 0.52 | [8 empty] | 7.18 |  |  |  |  | 0.02
2013 |  |  |  | 6992.92 |  |  | 7739 |  |  |  | 925 | [10 empty] | 85.84 |  |  |  | 85.93 | [5 empty] | 86.30 |  |  | 88.34 |  |  |  | 2.97 |  | 2.63 | [8 empty] | 11.43 |  |  |  |  | 0.09
2014 |  |  |  | 6942.49 |  |  | 7665 |  |  |  | 925 | [10 empty] | 85.92 |  |  |  | 86.00 | [5 empty] | 85.67 |  |  | 87.49 |  |  |  | 2.03 |  | 2.77 | [8 empty] | 11.23 |  |  |  |  | 0.08
2015 |  |  |  | 6617.16 |  |  | 7414 |  |  |  | 925 | [10 empty] | 85.58 |  |  |  | 85.60 | [5 empty] | 81.66 |  |  | 84.63 |  |  |  | 2.97 |  | 2.62 | [8 empty] | 11.78 |  |  |  |  | 0.02
2016 |  |  |  | 6912.04 |  |  | 7660 |  |  |  | 925 | [10 empty] | 85.43 |  |  |  | 85.45 | [5 empty] | 85.07 |  |  | 87.20 |  |  |  | 0.85 |  | 0.73 | [8 empty] | 13.82 |  |  |  |  | 0.01
2017 |  |  |  | 6846.75 |  |  | 7873 |  |  |  | 925 | [10 empty] | 85.57 |  |  |  | 85.58 | [5 empty] | 84.50 |  |  | 89.87 |  |  |  | 4.04 |  | 4.04 | [8 empty] | 10.39 |  |  |  |  | 0.01
2018 |  |  |  | 6951.25 |  |  | 7499 |  |  |  | 925 | [10 empty] | 84.68 |  |  |  | 84.83 | [5 empty] | 85.79 |  |  | 85.61 |  |  |  | 4.62 |  | 4.11 | [8 empty] | 11.06 |  |  |  |  | 0.15
2019 |  |  |  | 6265.79 |  |  | 6730 |  |  |  | 925 | [10 empty] | 75.83 |  |  |  | 75.83 | [5 empty] | 77.33 |  |  | 76.83 |  |  |  | 0.31 |  | 0.24 | [8 empty] | 23.94 |  |  |  |  | 0.00
2020 |  |  |  | 6842.29 |  |  | 7486 |  |  |  | 925 | [10 empty] | 84.44 |  |  |  | 84.44 | [5 empty] | 84.21 |  |  | 85.22 |  |  |  | 0.42 |  | 0.35 | [8 empty] | 15.20 |  |  |  |  | 0.01
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 85
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1298 | [14 empty] | 1317
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 214
E. |  | Testing of plant systems or components | [39 empty] | 0
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 162
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 102 |  |  |  | 35
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 0
Z. |  | Other | [39 empty] | 19 | [11 empty] | 1
Subtotal | [22 empty] | 1298 | [14 empty] | 1795 |  |  |  | 140 | [11 empty] | 13
Total | [22 empty] | 1298 | [14 empty] | 1948
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [34 empty] | 19
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 19
16. |  |  | Steam generation systems | [34 empty] | 11
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
33. |  |  | Circulating Water System | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 9
Total | [37 empty] | 85
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-July, Septenber-December. Additional electricity generation amounted to 143974 MWh. The unit was in the routine maintenance outage from 2020.07.19 to 2020.09.15. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH 2-1
2020 Operating Experience
RU-161 | [8 empty] | NOVOVORONEZH 2-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-392M | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-06-24
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-08-05
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2017-02-27
Reference unit power (net) | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7602.46 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.44 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.29 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.32 %
Unit Capability Factor (UCF) | [18 empty] | : | 82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.67 %
Load Factor (LF) | [18 empty] | : | 78.68 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.71 %
Operating Factor (OF) | [18 empty] | : | 84.98 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1319 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 766.28 | 766.53 |  |  |  | 759.53 |  | 748.29 | [8 empty] | 633.18 |  |  | 196.96 | [6 empty] | 0.00 |  | 626.72 |  |  |  | 777.45 |  |  | 812.91 |  |  | 704.55 | [9 empty] | 810.05 |  |  | 7602.46
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 98.82 |  | 96.00 | [8 empty] | 78.12 |  |  | 26.67 | [6 empty] | 0.21 |  | 72.72 |  |  |  | 96.48 |  |  | 97.66 |  |  | 97.93 | [9 empty] | 100.00 |  |  | 80.29
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 80.51 |  |  | 28.23 | [6 empty] | 0.21 |  | 76.26 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.00
LF [%] |  |  |  |  | 93.63 | 100.12 |  |  |  | 92.81 |  | 94.48 | [8 empty] | 77.37 |  |  | 24.87 | [6 empty] | 0.00 |  | 76.58 |  |  |  | 98.16 |  |  | 99.33 |  |  | 88.96 | [9 empty] | 98.98 |  |  | 78.68
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 43.89 | [6 empty] | 0.00 |  | 77.02 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.98
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.49 |  |  | 35.29 | [6 empty] | 0.00 |  | 0.20 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.44
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.49 |  |  | 15.39 | [6 empty] | 0.00 |  | 16.65 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.32
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 56.38 | [6 empty] | 99.79 |  | 7.09 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.67
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.18 |  | 4.00 | [8 empty] | 2.39 |  |  | 1.56 | [6 empty] | 0.00 |  | 3.54 |  |  |  | 3.52 |  |  | 2.34 |  |  | 2.07 | [9 empty] | 0.00 |  |  | 1.71
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 29029.46 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.94 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.7 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.66 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.19 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.89 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.96 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.96 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2017 |  |  |  | 5620.47 |  |  | 6226 |  |  |  | 1114 | [10 empty] | 62.35 |  |  |  | 65.08 | [5 empty] | 60.87 |  |  | 75.08 |  |  |  | 19.08 |  | 15.34 | [8 empty] | 19.58 |  |  |  |  | 2.73
2018 |  |  |  | 7746.87 |  |  | 7378 |  |  |  | 1114 | [10 empty] | 81.34 |  |  |  | 83.60 | [5 empty] | 79.38 |  |  | 84.22 |  |  |  | 5.56 |  | 4.92 | [8 empty] | 11.47 |  |  |  |  | 2.27
2019 |  |  |  | 7186.30 |  |  | 6885 |  |  |  | 1100 | [10 empty] | 76.74 |  |  |  | 77.97 | [5 empty] | 74.58 |  |  | 78.60 |  |  |  | 1.81 |  | 1.44 | [8 empty] | 20.59 |  |  |  |  | 1.22
2020 |  |  |  | 7602.46 |  |  | 7465 |  |  |  | 1100 | [10 empty] | 80.29 |  |  |  | 82.00 | [5 empty] | 78.68 |  |  | 84.98 |  |  |  | 3.44 |  | 4.32 | [8 empty] | 13.67 |  |  |  |  | 1.71
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2017 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 136 | [14 empty] | 289
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1197 | [14 empty] | 1416
Subtotal | [22 empty] | 1197 |  |  |  | 136 | [10 empty] | 1416 |  |  |  | 289
Total | [22 empty] | 1333 | [14 empty] | 1705
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2017 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
14. |  |  | Safety Systems | [19 empty] | 123 | [14 empty] | 31
31. |  |  | Turbine and auxiliaries | [34 empty] | 67
32. |  |  | Feedwater and Main Steam System | [34 empty] | 66
33. |  |  | Circulating Water System | [19 empty] | 13 | [14 empty] | 54
41. |  |  | Main Generator Systems | [34 empty] | 59
Total | [22 empty] | 136 | [14 empty] | 277
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-February, December. Additional electricity generation amounted to 2261 MWh. The unit was in the intermediate outage from 2020.06.14 to 2020.08.03. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH 2-2
2020 Operating Experience
RU-162 | [8 empty] | NOVOVORONEZH 2-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-392M | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-07-12
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-05-01
Gross electrical power | [12 empty] | : |  |  | 1181 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2019-10-31
Reference unit power (net) | [12 empty] | : |  |  | 1101 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7602.61 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.46 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.5 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.68 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.32 %
Load Factor (LF) | [18 empty] | : | 78.61 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.18 %
Operating Factor (OF) | [18 empty] | : | 83.87 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1417 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 773.16 | 772.26 |  |  |  | 777.20 |  | 0.00 | [8 empty] | 112.52 |  |  | 640.23 | [6 empty] | 772.27 |  | 786.96 |  |  |  | 763.65 |  |  | 791.34 |  |  | 655.47 | [9 empty] | 757.57 |  |  | 7602.61
EAF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 98.59 |  | 0.50 | [8 empty] | 17.97 |  |  | 85.89 | [6 empty] | 94.21 |  | 95.69 |  |  |  | 95.93 |  |  | 97.52 |  |  | 91.21 | [9 empty] | 100.00 |  |  | 81.50
UCF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 100.00 |  | 0.50 | [8 empty] | 19.03 |  |  | 91.09 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 92.95 | [9 empty] | 100.00 |  |  | 83.68
LF [%] |  |  |  |  | 94.39 | 100.78 |  |  |  | 94.88 |  | 0.00 | [8 empty] | 13.74 |  |  | 80.76 | [6 empty] | 94.28 |  | 96.07 |  |  |  | 96.33 |  |  | 96.61 |  |  | 82.69 | [9 empty] | 92.48 |  |  | 78.61
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 0.56 | [8 empty] | 19.35 |  |  | 92.78 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 93.19 | [9 empty] | 100.00 |  |  | 83.87
FLR [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 51.21 |  |  | 8.91 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 7.05 | [9 empty] | 0.00 |  |  | 3.46
UCL [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.98 |  |  | 8.91 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 7.05 | [9 empty] | 0.00 |  |  | 3.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 99.50 | [8 empty] | 60.99 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.32
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.41 |  | 0.00 | [8 empty] | 1.06 |  |  | 5.20 | [6 empty] | 5.79 |  | 4.31 |  |  |  | 4.07 |  |  | 2.48 |  |  | 1.73 | [9 empty] | 0.00 |  |  | 2.18
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 11159.61 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.08 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.07 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.49 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.93 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.58 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 79.31 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.87 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.49 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2019 |  |  |  | 3557.06 |  |  | 4222 |  |  |  | 1101 | [10 empty] | 85.48 |  |  |  | 85.48 | [5 empty] | 83.47 |  |  | 88.25 |  |  |  | 13.57 |  | 13.43 | [8 empty] | 1.09 |  |  |  |  | 0.00
2020 |  |  |  | 7602.61 |  |  | 7367 |  |  |  | 1101 | [10 empty] | 81.50 |  |  |  | 83.68 | [5 empty] | 78.61 |  |  | 83.87 |  |  |  | 3.46 |  | 3.00 | [8 empty] | 13.32 |  |  |  |  | 2.18
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2019 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 228 | [14 empty] | 345
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1170 | [14 empty] | 1003
L. |  | Human factor related | [24 empty] | 21 | [14 empty] | 18
Subtotal | [22 empty] | 1170 |  |  |  | 249 | [10 empty] | 1003 |  |  |  | 363
Total | [22 empty] | 1419 | [14 empty] | 1366
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2019 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [19 empty] | 21 | [14 empty] | 12
31. |  |  | Turbine and auxiliaries | [19 empty] | 33 | [14 empty] | 20
32. |  |  | Feedwater and Main Steam System | [19 empty] | 146 | [14 empty] | 185
33. |  |  | Circulating Water System | [19 empty] | 49 | [14 empty] | 30
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [22 empty] | 249 | [14 empty] | 254
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in Januare. Additional electricity generation amounted to 345 MWh. The unit was in the intermediate outage from 2020.04.01 to 2020.05.19. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH-4
2020 Operating Experience
RU-11 | [8 empty] | NOVOVORONEZH-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-179 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-07-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1972-12-28
Gross electrical power | [12 empty] | : |  |  | 417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-03-24
Reference unit power (net) | [12 empty] | : |  |  | 385 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 295.8
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2945.24 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.27 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.4 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.6 %
Load Factor (LF) | [18 empty] | : | 87.09 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.13 %
Operating Factor (OF) | [18 empty] | : | 90.57 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 828 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 85.13 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 282.33 | 283.69 |  |  |  | 299.31 |  | 287.80 | [8 empty] | 280.89 |  |  | 266.17 | [6 empty] | 282.97 |  | 247.90 |  |  |  | 132.40 |  |  | 65.94 |  |  | 259.84 | [9 empty] | 256.01 |  |  | 2945.24
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.10 | [6 empty] | 99.13 |  | 96.56 |  |  |  | 51.95 |  |  | 25.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.27
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 60.37 |  |  | 25.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.40
LF [%] |  |  |  |  | 98.57 | 105.87 |  |  |  | 104.49 |  | 103.82 | [8 empty] | 98.06 |  |  | 96.02 | [6 empty] | 98.79 |  | 86.54 |  |  |  | 47.76 |  |  | 23.02 |  |  | 93.74 | [9 empty] | 89.38 |  |  | 87.09
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 60.56 |  |  | 26.88 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.57
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 39.63 |  |  | 75.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.60
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.90 | [6 empty] | 0.87 |  | 3.44 |  |  |  | 8.43 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.13
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 126123.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.47 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.96 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.79 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.92 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.82 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.34 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.71 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 2570.51 |  |  | 8072 |  |  |  | 385 | [10 empty] | 84.20 |  |  |  | 84.20 | [5 empty] | 84.95 |  |  | 93.15 |  |  |  | 14.82 |  | 14.65 | [8 empty] | 1.15 |  |  |  |  | 0.00
1974 |  |  |  | 2411.84 |  |  | 7159 |  |  |  | 385 | [10 empty] | 71.28 |  |  |  | 71.28 | [5 empty] | 71.51 |  |  | 81.72 |  |  |  | 15.90 |  | 13.48 | [8 empty] | 15.24 |  |  |  |  | 0.00
1975 |  |  |  | 2644.87 |  |  | 7950 |  |  |  | 385 | [10 empty] | 75.64 |  |  |  | 75.64 | [5 empty] | 78.42 |  |  | 90.75 |  |  |  | 9.17 |  | 7.63 | [8 empty] | 16.73 |  |  |  |  | 0.00
1976 |  |  |  | 2924.13 |  |  | 7963 |  |  |  | 385 | [10 empty] | 84.48 |  |  |  | 84.48 | [5 empty] | 86.47 |  |  | 90.65 |  |  |  | 4.63 |  | 4.10 | [8 empty] | 11.42 |  |  |  |  | 0.00
1977 |  |  |  | 2822.95 |  |  | 7637 |  |  |  | 385 | [10 empty] | 81.34 |  |  |  | 81.34 | [5 empty] | 83.70 |  |  | 87.18 |  |  |  | 4.88 |  | 4.17 | [8 empty] | 14.49 |  |  |  |  | 0.00
1978 |  |  |  | 2658.54 |  |  | 7388 |  |  |  | 385 | [10 empty] | 78.18 |  |  |  | 78.18 | [5 empty] | 78.83 |  |  | 84.34 |  |  |  | 3.70 |  | 3.00 | [8 empty] | 18.82 |  |  |  |  | 0.00
1979 |  |  |  | 2442.24 |  |  | 6888 |  |  |  | 385 | [10 empty] | 72.44 |  |  |  | 72.44 | [5 empty] | 72.41 |  |  | 78.63 |  |  |  | 8.70 |  | 6.90 | [8 empty] | 20.66 |  |  |  |  | 0.00
1980 |  |  |  | 2842.93 |  |  | 7690 |  |  |  | 385 | [10 empty] | 84.08 |  |  |  | 84.08 | [5 empty] | 84.06 |  |  | 87.55 |  |  |  | 3.15 |  | 2.74 | [8 empty] | 13.18 |  |  |  |  | 0.00
1981 |  |  |  | 3019.87 |  |  | 8278 |  |  |  | 385 | [10 empty] | 90.03 |  |  |  | 90.03 | [5 empty] | 89.55 |  |  | 94.51 |  |  |  | 4.32 |  | 4.06 | [8 empty] | 5.91 |  |  |  |  | 0.00
1982 |  |  |  | 2797.51 |  |  | 8278 |  |  |  | 385 | [10 empty] | 83.88 |  |  |  | 83.88 | [5 empty] | 82.95 |  |  | 94.50 |  |  |  | 9.47 |  | 8.78 | [8 empty] | 7.35 |  |  |  |  | 0.00
1983 |  |  |  | 2950.30 |  |  | 8216 |  |  |  | 385 | [10 empty] | 89.15 |  |  |  | 89.15 | [5 empty] | 87.48 |  |  | 93.79 |  |  |  | 3.80 |  | 3.52 | [8 empty] | 7.33 |  |  |  |  | 0.00
1984 |  |  |  | 2974.10 |  |  | 7982 |  |  |  | 385 | [10 empty] | 87.89 |  |  |  | 87.89 | [5 empty] | 87.94 |  |  | 90.87 |  |  |  | 3.16 |  | 2.87 | [8 empty] | 9.24 |  |  |  |  | 0.00
1985 |  |  |  | 3097.87 |  |  | 8250 |  |  |  | 385 | [10 empty] | 91.30 |  |  |  | 91.30 | [5 empty] | 91.85 |  |  | 94.18 |  |  |  | 2.71 |  | 2.54 | [8 empty] | 6.16 |  |  |  |  | 0.00
1986 |  |  |  | 2792.21 |  |  | 7688 |  |  |  | 385 | [10 empty] | 82.62 |  |  |  | 82.62 | [5 empty] | 82.79 |  |  | 87.76 |  |  |  | 5.57 |  | 4.88 | [8 empty] | 12.51 |  |  |  |  | 0.00
1987 |  |  |  | 3262.68 |  |  | 8252 |  |  |  | 417 | [10 empty] | 91.72 |  |  |  | 91.72 | [5 empty] | 89.32 |  |  | 94.20 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 8.14 |  |  |  |  | 0.00
1988 |  |  |  | 2529.37 |  |  | 7152 |  |  |  | 385 | [10 empty] | 79.97 |  |  |  | 79.97 | [5 empty] | 74.79 |  |  | 81.42 |  |  |  | 1.21 |  | 0.98 | [8 empty] | 19.05 |  |  |  |  | 0.00
1989 |  |  |  | 2710.26 |  |  | 8357 |  |  |  | 385 | [10 empty] | 90.16 |  |  |  | 90.19 | [5 empty] | 80.36 |  |  | 95.40 |  |  |  | 5.71 |  | 5.46 | [8 empty] | 4.35 |  |  |  |  | 0.04
1990 |  |  |  | 2244.69 |  |  | 6622 |  |  |  | 385 | [10 empty] | 69.63 |  |  |  | 70.55 | [5 empty] | 66.56 |  |  | 75.59 |  |  |  | 11.28 |  | 8.97 | [8 empty] | 20.48 |  |  |  |  | 0.92
1991 |  |  |  | 1827.62 |  |  | 5540 |  |  |  | 385 | [10 empty] | 57.96 |  |  |  | 58.24 | [5 empty] | 54.19 |  |  | 63.24 |  |  |  | 9.28 |  | 5.96 | [8 empty] | 35.80 |  |  |  |  | 0.28
1992 |  |  |  | 2853.44 |  |  | 8163 |  |  |  | 385 | [10 empty] | 82.38 |  |  |  | 87.35 | [5 empty] | 84.38 |  |  | 92.94 |  |  |  | 6.01 |  | 5.58 | [8 empty] | 7.07 |  |  |  |  | 4.97
1993 |  |  |  | 2613.71 |  |  | 7204 |  |  |  | 385 | [10 empty] | 76.60 |  |  |  | 79.73 | [5 empty] | 77.50 |  |  | 82.24 |  |  |  | 2.64 |  | 2.16 | [8 empty] | 18.11 |  |  |  |  | 3.13
1994 |  |  |  | 1954.27 |  |  | 6033 |  |  |  | 385 | [10 empty] | 56.65 |  |  |  | 66.91 | [5 empty] | 57.95 |  |  | 68.87 |  |  |  | 2.79 |  | 1.92 | [8 empty] | 31.17 |  |  |  |  | 10.26
1995 |  |  |  | 2119.99 |  |  | 5818 |  |  |  | 385 | [10 empty] | 62.15 |  |  |  | 65.50 | [5 empty] | 62.86 |  |  | 66.42 |  |  |  | 0.64 |  | 0.42 | [8 empty] | 34.08 |  |  |  |  | 3.35
1996 |  |  |  | 3080.28 |  |  | 8362 |  |  |  | 385 | [10 empty] | 90.38 |  |  |  | 93.78 | [5 empty] | 91.08 |  |  | 95.20 |  |  |  | 1.08 |  | 1.02 | [8 empty] | 5.20 |  |  |  |  | 3.40
1997 |  |  |  | 2235.48 |  |  | 6690 |  |  |  | 385 | [10 empty] | 66.98 |  |  |  | 70.29 | [5 empty] | 66.28 |  |  | 76.37 |  |  |  | 0.76 |  | 0.54 | [8 empty] | 29.17 |  |  |  |  | 3.30
1998 |  |  |  | 2714.87 |  |  | 7366 |  |  |  | 385 | [10 empty] | 80.18 |  |  |  | 83.16 | [5 empty] | 80.50 |  |  | 84.09 |  |  |  | 0.98 |  | 0.82 | [8 empty] | 16.02 |  |  |  |  | 2.98
1999 |  |  |  | 1791.48 |  |  | 4927 |  |  |  | 385 | [10 empty] | 53.21 |  |  |  | 54.93 | [5 empty] | 53.12 |  |  | 56.24 |  |  |  | 17.55 |  | 11.69 | [8 empty] | 33.38 |  |  |  |  | 1.72
2000 |  |  |  | 2474.25 |  |  | 6784 |  |  |  | 385 | [10 empty] | 73.08 |  |  |  | 74.64 | [5 empty] | 73.16 |  |  | 77.23 |  |  |  | 3.12 |  | 2.40 | [8 empty] | 22.96 |  |  |  |  | 1.56
2001 |  |  |  | 2655.95 |  |  | 7173 |  |  |  | 385 | [10 empty] | 79.22 |  |  |  | 80.72 | [5 empty] | 78.75 |  |  | 81.88 |  |  |  | 1.24 |  | 1.01 | [8 empty] | 18.26 |  |  |  |  | 1.51
2002 |  |  |  | 2184.85 |  |  | 5857 |  |  |  | 385 | [10 empty] | 64.21 |  |  |  | 65.37 | [5 empty] | 64.78 |  |  | 66.86 |  |  |  | 4.51 |  | 3.09 | [8 empty] | 31.55 |  |  |  |  | 1.15
2003 |  |  |  | 2583.05 |  |  | 6950 |  |  |  | 385 | [10 empty] | 76.75 |  |  |  | 78.78 | [5 empty] | 76.59 |  |  | 79.34 |  |  |  | 1.32 |  | 1.05 | [8 empty] | 20.17 |  |  |  |  | 2.02
2004 |  |  |  | 2714.01 |  |  | 7685 |  |  |  | 385 | [10 empty] | 80.75 |  |  |  | 83.75 | [5 empty] | 80.25 |  |  | 87.49 |  |  |  | 4.90 |  | 4.32 | [8 empty] | 11.94 |  |  |  |  | 2.99
2005 |  |  |  | 2433.38 |  |  | 7228 |  |  |  | 385 | [10 empty] | 73.09 |  |  |  | 75.27 | [5 empty] | 72.15 |  |  | 82.51 |  |  |  | 12.96 |  | 11.20 | [8 empty] | 13.53 |  |  |  |  | 2.18
2006 |  |  |  | 2575.08 |  |  | 7636 |  |  |  | 385 | [10 empty] | 76.49 |  |  |  | 81.29 | [5 empty] | 76.35 |  |  | 87.17 |  |  |  | 8.30 |  | 7.36 | [8 empty] | 11.36 |  |  |  |  | 4.79
2007 |  |  |  | 2290.27 |  |  | 6488 |  |  |  | 385 | [10 empty] | 67.88 |  |  |  | 69.12 | [5 empty] | 67.91 |  |  | 74.06 |  |  |  | 8.19 |  | 9.08 | [8 empty] | 21.80 |  |  |  |  | 1.24
2008 |  |  |  | 2876.30 |  |  | 7464 |  |  |  | 385 | [10 empty] | 83.37 |  |  |  | 84.02 | [5 empty] | 85.05 |  |  | 84.97 |  |  |  | 3.95 |  | 3.45 | [8 empty] | 12.53 |  |  |  |  | 0.65
2009 |  |  |  | 2931.78 |  |  | 7580 |  |  |  | 385 | [10 empty] | 85.23 |  |  |  | 86.31 | [5 empty] | 86.93 |  |  | 86.53 |  |  |  | 0.01 |  | 0.78 | [8 empty] | 12.91 |  |  |  |  | 1.08
2010 |  |  |  | 2928.70 |  |  | 7727 |  |  |  | 385 | [10 empty] | 85.82 |  |  |  | 87.48 | [5 empty] | 86.84 |  |  | 88.21 |  |  |  | 3.36 |  | 3.04 | [8 empty] | 9.48 |  |  |  |  | 1.66
2011 |  |  |  | 2707.55 |  |  | 7263 |  |  |  | 385 | [10 empty] | 80.64 |  |  |  | 82.08 | [5 empty] | 80.29 |  |  | 82.92 |  |  |  | 1.69 |  | 1.41 | [8 empty] | 16.51 |  |  |  |  | 1.44
2012 |  |  |  | 2944.86 |  |  | 7707 |  |  |  | 385 | [10 empty] | 87.14 |  |  |  | 87.87 | [5 empty] | 87.08 |  |  | 87.74 |  |  |  | 1.22 |  | 1.09 | [8 empty] | 11.04 |  |  |  |  | 0.73
2013 |  |  |  | 3038.98 |  |  | 7929 |  |  |  | 385 | [10 empty] | 89.36 |  |  |  | 90.36 | [5 empty] | 90.11 |  |  | 90.51 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.63 |  |  |  |  | 1.00
2014 |  |  |  | 3061.07 |  |  | 7932 |  |  |  | 385 | [10 empty] | 89.26 |  |  |  | 90.33 | [5 empty] | 90.75 |  |  | 90.54 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 9.56 |  |  |  |  | 1.07
2015 |  |  |  | 2704.38 |  |  | 7085 |  |  |  | 385 | [10 empty] | 79.59 |  |  |  | 80.43 | [5 empty] | 80.19 |  |  | 80.88 |  |  |  | 0.45 |  | 0.36 | [8 empty] | 19.21 |  |  |  |  | 0.83
2016 |  |  |  | 2959.49 |  |  | 7783 |  |  |  | 385 | [10 empty] | 87.26 |  |  |  | 88.31 | [5 empty] | 87.51 |  |  | 88.60 |  |  |  | 2.91 |  | 2.65 | [8 empty] | 9.04 |  |  |  |  | 1.05
2017 |  |  |  | 3148.86 |  |  | 8259 |  |  |  | 385 | [10 empty] | 92.54 |  |  |  | 93.92 | [5 empty] | 93.37 |  |  | 94.28 |  |  |  | 0.37 |  | 0.35 | [8 empty] | 5.73 |  |  |  |  | 1.38
2018 |  |  |  | 8.92 |  |  | 73 |  |  |  | 385 | [10 empty] | 0.43 |  |  |  | 0.43 | [5 empty] | 0.26 |  |  | 0.83 |  |  |  | 47.79 |  | 0.39 | [8 empty] | 99.18 |  |  |  |  | 0.00
2019 |  |  |  | 2994.94 |  |  | 7654 |  |  |  | 385 | [10 empty] | 86.23 |  |  |  | 86.33 | [5 empty] | 88.80 |  |  | 87.37 |  |  |  | 3.00 |  | 2.67 | [8 empty] | 11.01 |  |  |  |  | 0.09
2020 |  |  |  | 2945.24 |  |  | 7956 |  |  |  | 385 | [10 empty] | 89.27 |  |  |  | 90.40 | [5 empty] | 87.09 |  |  | 90.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.60 |  |  |  |  | 1.13
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1973 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 69
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 826 | [14 empty] | 1236
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 93
E. |  | Testing of plant systems or components | [35 empty] | 12
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 57
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 9
L. |  | Human factor related | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 9
Z. |  | Other | [35 empty] | 2 |  |  |  | 14
Subtotal | [22 empty] | 826 | [14 empty] | 1400 |  |  |  | 94 | [11 empty] | 9
Total | [22 empty] | 826 | [14 empty] | 1503
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1973 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [34 empty] | 14
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
16. |  |  | Steam generation systems | [34 empty] | 32
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 0
Total | [37 empty] | 70
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-May, October-December. Additional electricity generation amounted to 70689 MWh. The unit was in the intermediate outage from 2020.09.19 to 2020.10.23. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH-5
2020 Operating Experience
RU-20 | [8 empty] | NOVOVORONEZH-5 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-187 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-03-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-05-31
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-02-20
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 324
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.5
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 109 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6787.87 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.96 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.89 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.84 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.6 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.56 %
Load Factor (LF) | [18 empty] | : | 81.34 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.71 %
Operating Factor (OF) | [18 empty] | : | 85.19 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1301 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 4.77 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 546.51 | 669.94 |  |  |  | 715.57 |  | 689.00 | [8 empty] | 683.50 |  |  | 660.93 | [6 empty] | 678.07 |  | 134.79 |  |  |  | 137.19 |  |  | 666.66 |  |  | 542.86 | [9 empty] | 662.85 |  |  | 6787.87
EAF [%] |  |  |  |  | 79.75 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.93 |  |  | 97.72 | [6 empty] | 96.68 |  | 22.20 |  |  |  | 22.62 |  |  | 98.51 |  |  | 89.51 | [9 empty] | 100.00 |  |  | 83.89
UCF [%] |  |  |  |  | 79.75 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 22.96 |  |  |  | 23.16 |  |  | 99.97 |  |  | 89.51 | [9 empty] | 100.00 |  |  | 84.60
LF [%] |  |  |  |  | 77.32 | 101.32 |  |  |  | 101.24 |  | 100.73 | [8 empty] | 96.70 |  |  | 96.63 | [6 empty] | 95.94 |  | 19.07 |  |  |  | 20.06 |  |  | 94.32 |  |  | 79.37 | [9 empty] | 93.78 |  |  | 81.34
OF [%] |  |  |  |  | 80.65 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 23.25 |  |  |  | 26.94 |  |  | 100.00 |  |  | 91.67 | [9 empty] | 100.00 |  |  | 85.19
FLR [%] |  |  |  |  | 20.25 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.83 |  |  | 0.03 |  |  | 10.36 | [9 empty] | 0.00 |  |  | 2.96
UCL [%] |  |  |  |  | 20.25 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 3.37 |  |  | 0.03 |  |  | 10.35 | [9 empty] | 0.00 |  |  | 2.84
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 77.04 |  |  |  | 73.47 |  |  | 0.00 |  |  | 0.14 | [9 empty] | 0.00 |  |  | 12.56
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.07 |  |  | 2.28 | [6 empty] | 3.32 |  | 0.76 |  |  |  | 0.53 |  |  | 1.46 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.71
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 214583.17 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 12.08 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 66.47 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.28 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 67.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 66.26 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.82 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 4639.79 |  |  | 6929 |  |  |  | 950 | [10 empty] | 56.62 |  |  |  | 56.62 | [5 empty] | 56.10 |  |  | 77.77 |  |  |  | 28.48 |  | 22.54 | [8 empty] | 20.83 |  |  |  |  | 0.00
1982 |  |  |  | 5042.84 |  |  | 6631 |  |  |  | 950 | [10 empty] | 60.89 |  |  |  | 60.89 | [5 empty] | 60.60 |  |  | 75.70 |  |  |  | 25.30 |  | 20.62 | [8 empty] | 18.49 |  |  |  |  | 0.00
1983 |  |  |  | 6607.53 |  |  | 7716 |  |  |  | 950 | [10 empty] | 79.53 |  |  |  | 79.53 | [5 empty] | 79.40 |  |  | 88.08 |  |  |  | 7.92 |  | 6.84 | [8 empty] | 13.64 |  |  |  |  | 0.00
1984 |  |  |  | 6979.64 |  |  | 7742 |  |  |  | 950 | [10 empty] | 83.42 |  |  |  | 83.42 | [5 empty] | 83.64 |  |  | 88.14 |  |  |  | 5.18 |  | 4.56 | [8 empty] | 12.02 |  |  |  |  | 0.00
1985 |  |  |  | 6894.29 |  |  | 7979 |  |  |  | 950 | [10 empty] | 83.12 |  |  |  | 83.12 | [5 empty] | 82.84 |  |  | 91.08 |  |  |  | 8.96 |  | 8.18 | [8 empty] | 8.69 |  |  |  |  | 0.00
1986 |  |  |  | 5523.75 |  |  | 6806 |  |  |  | 950 | [10 empty] | 65.91 |  |  |  | 65.96 | [5 empty] | 66.38 |  |  | 77.69 |  |  |  | 17.36 |  | 13.86 | [8 empty] | 20.18 |  |  |  |  | 0.04
1987 |  |  |  | 7052.70 |  |  | 7399 |  |  |  | 1000 | [10 empty] | 81.79 |  |  |  | 81.79 | [5 empty] | 80.51 |  |  | 84.46 |  |  |  | 2.68 |  | 2.26 | [8 empty] | 15.96 |  |  |  |  | 0.00
1988 |  |  |  | 3017.85 |  |  | 3439 |  |  |  | 950 | [10 empty] | 36.51 |  |  |  | 36.51 | [5 empty] | 36.16 |  |  | 39.15 |  |  |  | 59.88 |  | 54.50 | [8 empty] | 8.98 |  |  |  |  | 0.00
1989 |  |  |  | 3308.95 |  |  | 3778 |  |  |  | 950 | [10 empty] | 40.88 |  |  |  | 40.88 | [5 empty] | 39.76 |  |  | 43.13 |  |  |  | 25.41 |  | 13.93 | [8 empty] | 45.19 |  |  |  |  | 0.00
1990 |  |  |  | 3913.28 |  |  | 4715 |  |  |  | 950 | [10 empty] | 47.63 |  |  |  | 47.72 | [5 empty] | 47.02 |  |  | 53.82 |  |  |  | 15.35 |  | 8.66 | [8 empty] | 43.62 |  |  |  |  | 0.09
1991 |  |  |  | 5878.22 |  |  | 6996 |  |  |  | 950 | [10 empty] | 71.54 |  |  |  | 71.54 | [5 empty] | 70.63 |  |  | 79.86 |  |  |  | 19.86 |  | 17.72 | [8 empty] | 10.74 |  |  |  |  | 0.00
1992 |  |  |  | 3752.83 |  |  | 5244 |  |  |  | 950 | [10 empty] | 45.70 |  |  |  | 45.89 | [5 empty] | 44.98 |  |  | 59.71 |  |  |  | 8.71 |  | 4.38 | [8 empty] | 49.73 |  |  |  |  | 0.20
1993 |  |  |  | 5935.41 |  |  | 7448 |  |  |  | 950 | [10 empty] | 72.55 |  |  |  | 73.79 | [5 empty] | 71.32 |  |  | 85.02 |  |  |  | 10.42 |  | 8.59 | [8 empty] | 17.62 |  |  |  |  | 1.24
1994 |  |  |  | 2281.89 |  |  | 4288 |  |  |  | 950 | [10 empty] | 28.94 |  |  |  | 33.19 | [5 empty] | 27.42 |  |  | 48.95 |  |  |  | 50.98 |  | 34.51 | [8 empty] | 32.29 |  |  |  |  | 4.26
1995 |  |  |  | 4753.72 |  |  | 6670 |  |  |  | 950 | [10 empty] | 57.46 |  |  |  | 63.87 | [5 empty] | 57.12 |  |  | 76.14 |  |  |  | 14.52 |  | 10.85 | [8 empty] | 25.28 |  |  |  |  | 6.41
1996 |  |  |  | 3861.84 |  |  | 4759 |  |  |  | 950 | [10 empty] | 46.71 |  |  |  | 46.71 | [5 empty] | 46.28 |  |  | 54.18 |  |  |  | 15.10 |  | 8.31 | [8 empty] | 44.98 |  |  |  |  | 0.00
1997 |  |  |  | 5949.25 |  |  | 6854 |  |  |  | 950 | [10 empty] | 71.37 |  |  |  | 71.69 | [5 empty] | 71.49 |  |  | 78.24 |  |  |  | 7.84 |  | 6.10 | [8 empty] | 22.21 |  |  |  |  | 0.33
1998 |  |  |  | 3771.78 |  |  | 4457 |  |  |  | 950 | [10 empty] | 44.89 |  |  |  | 45.48 | [5 empty] | 45.32 |  |  | 50.88 |  |  |  | 28.35 |  | 17.99 | [8 empty] | 36.52 |  |  |  |  | 0.60
1999 |  |  |  | 4845.42 |  |  | 6062 |  |  |  | 950 | [10 empty] | 58.73 |  |  |  | 61.16 | [5 empty] | 58.22 |  |  | 69.20 |  |  |  | 17.37 |  | 12.86 | [8 empty] | 25.99 |  |  |  |  | 2.43
2000 |  |  |  | 5278.64 |  |  | 6479 |  |  |  | 950 | [10 empty] | 63.54 |  |  |  | 65.56 | [5 empty] | 63.26 |  |  | 73.76 |  |  |  | 7.30 |  | 5.17 | [8 empty] | 29.27 |  |  |  |  | 2.02
2001 |  |  |  | 5984.59 |  |  | 7508 |  |  |  | 950 | [10 empty] | 72.26 |  |  |  | 73.22 | [5 empty] | 71.91 |  |  | 85.71 |  |  |  | 6.60 |  | 5.17 | [8 empty] | 21.61 |  |  |  |  | 0.96
2002 |  |  |  | 6762.21 |  |  | 7430 |  |  |  | 950 | [10 empty] | 80.68 |  |  |  | 83.14 | [5 empty] | 81.26 |  |  | 84.82 |  |  |  | 1.95 |  | 1.65 | [8 empty] | 15.21 |  |  |  |  | 2.45
2003 |  |  |  | 6951.21 |  |  | 7507 |  |  |  | 950 | [10 empty] | 83.05 |  |  |  | 84.51 | [5 empty] | 83.53 |  |  | 85.70 |  |  |  | 0.93 |  | 0.79 | [8 empty] | 14.70 |  |  |  |  | 1.46
2004 |  |  |  | 3610.61 |  |  | 4032 |  |  |  | 950 | [10 empty] | 43.13 |  |  |  | 43.61 | [5 empty] | 43.27 |  |  | 45.90 |  |  |  | 44.15 |  | 34.48 | [8 empty] | 21.91 |  |  |  |  | 0.48
2005 |  |  |  | 2544.26 |  |  | 2861 |  |  |  | 950 | [10 empty] | 30.60 |  |  |  | 31.42 | [5 empty] | 30.57 |  |  | 32.66 |  |  |  | 0.00 |  | 68.58 | [8 empty] | 0.00 |  |  |  |  | 0.82
2006 |  |  |  | 7264.41 |  |  | 7762 |  |  |  | 950 | [10 empty] | 86.70 |  |  |  | 87.75 | [5 empty] | 87.29 |  |  | 88.61 |  |  |  | 0.61 |  | 0.54 | [8 empty] | 11.71 |  |  |  |  | 1.05
2007 |  |  |  | 6556.27 |  |  | 7140 |  |  |  | 950 | [10 empty] | 78.48 |  |  |  | 79.84 | [5 empty] | 78.78 |  |  | 81.51 |  |  |  | 7.10 |  | 7.85 | [8 empty] | 12.31 |  |  |  |  | 1.36
2008 |  |  |  | 7285.18 |  |  | 7718 |  |  |  | 950 | [10 empty] | 86.89 |  |  |  | 87.00 | [5 empty] | 87.30 |  |  | 87.86 |  |  |  | 0.51 |  | 0.44 | [8 empty] | 12.56 |  |  |  |  | 0.11
2009 |  |  |  | 6518.11 |  |  | 6865 |  |  |  | 950 | [10 empty] | 77.59 |  |  |  | 77.86 | [5 empty] | 78.32 |  |  | 78.37 |  |  |  | 4.04 |  | 3.28 | [8 empty] | 18.86 |  |  |  |  | 0.27
2010 |  |  |  | 5585.30 |  |  | 6404 |  |  |  | 950 | [10 empty] | 66.98 |  |  |  | 69.12 | [5 empty] | 67.11 |  |  | 73.11 |  |  |  | 5.83 |  | 4.28 | [8 empty] | 26.61 |  |  |  |  | 2.13
2011 |  |  |  | 2085.77 |  |  | 2422 |  |  |  | 950 | [10 empty] | 25.11 |  |  |  | 25.11 | [5 empty] | 25.07 |  |  | 27.65 |  |  |  | 7.01 |  | 7.99 | [8 empty] | 66.90 |  |  |  |  | 0.00
2012 |  |  |  | 7014.58 |  |  | 7457 |  |  |  | 950 | [10 empty] | 83.60 |  |  |  | 83.72 | [5 empty] | 84.06 |  |  | 84.89 |  |  |  | 1.80 |  | 2.89 | [8 empty] | 13.38 |  |  |  |  | 0.13
2013 |  |  |  | 7205.36 |  |  | 7773 |  |  |  | 950 | [10 empty] | 85.97 |  |  |  | 86.24 | [5 empty] | 86.58 |  |  | 88.73 |  |  |  | 1.20 |  | 1.23 | [8 empty] | 12.54 |  |  |  |  | 0.27
2014 |  |  |  | 6193.58 |  |  | 7712 |  |  |  | 950 | [10 empty] | 74.39 |  |  |  | 74.40 | [5 empty] | 74.42 |  |  | 88.03 |  |  |  | 11.44 |  | 9.61 | [8 empty] | 15.99 |  |  |  |  | 0.01
2015 |  |  |  | 6209.76 |  |  | 7120 |  |  |  | 950 | [10 empty] | 74.34 |  |  |  | 74.50 | [5 empty] | 74.62 |  |  | 81.28 |  |  |  | 8.43 |  | 7.73 | [8 empty] | 17.77 |  |  |  |  | 0.16
2016 |  |  |  | 7191.83 |  |  | 7777 |  |  |  | 950 | [10 empty] | 85.94 |  |  |  | 86.18 | [5 empty] | 86.18 |  |  | 88.54 |  |  |  | 1.73 |  | 1.85 | [8 empty] | 11.97 |  |  |  |  | 0.24
2017 |  |  |  | 6560.03 |  |  | 7811 |  |  |  | 950 | [10 empty] | 78.87 |  |  |  | 79.36 | [5 empty] | 78.83 |  |  | 89.17 |  |  |  | 0.60 |  | 0.48 | [8 empty] | 20.16 |  |  |  |  | 0.49
2018 |  |  |  | 7134.80 |  |  | 7766 |  |  |  | 950 | [10 empty] | 86.22 |  |  |  | 87.70 | [5 empty] | 85.73 |  |  | 88.65 |  |  |  | 0.99 |  | 2.46 | [8 empty] | 9.84 |  |  |  |  | 1.48
2019 |  |  |  | 6092.49 |  |  | 6806 |  |  |  | 950 | [10 empty] | 74.19 |  |  |  | 74.67 | [5 empty] | 73.21 |  |  | 77.69 |  |  |  | 8.33 |  | 6.79 | [8 empty] | 18.54 |  |  |  |  | 0.49
2020 |  |  |  | 6787.87 |  |  | 7483 |  |  |  | 950 | [10 empty] | 83.89 |  |  |  | 84.60 | [5 empty] | 81.34 |  |  | 85.19 |  |  |  | 2.96 |  | 2.84 | [8 empty] | 12.56 |  |  |  |  | 0.71
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 204 | [14 empty] | 626
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1057 | [14 empty] | 1447
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 309
L. |  | Human factor related | [39 empty] | 2
Z. |  | Other | [39 empty] | 11
Subtotal | [22 empty] | 1057 |  |  |  | 204 | [10 empty] | 1756 |  |  |  | 639
Total | [22 empty] | 1261 | [14 empty] | 2395
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 241
12. |  |  | Reactor I&C Systems | [34 empty] | 19
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 52
16. |  |  | Steam generation systems | [19 empty] | 144 | [14 empty] | 218
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 13
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 6
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 50
42. |  |  | Electrical Power Supply Systems | [19 empty] | 60 | [14 empty] | 4
Total | [22 empty] | 204 | [14 empty] | 624
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-April, November-December. Additional electricity generation amounted to 41203 MWh. The unit was in the intermediate outage from 2020.08.08 to 2020.09.22. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-1
2020 Operating Experience
RU-59 | [8 empty] | ROSTOV-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-09-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2001-03-30
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2001-12-25
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 19 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7443.25 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.96 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.6 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.85 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.29 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.86 %
Load Factor (LF) | [18 empty] | : | 89.2 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.68 %
Operating Factor (OF) | [18 empty] | : | 87.53 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1095 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 746.64 | 641.86 |  |  |  | 127.37 |  | 239.35 | [8 empty] | 671.05 |  |  | 672.92 | [6 empty] | 732.34 |  | 731.77 |  |  |  | 716.86 |  |  | 743.88 |  |  | 666.89 | [9 empty] | 752.33 |  |  | 7443.25
EAF [%] |  |  |  |  | 100.00 | 95.60 |  |  |  | 18.79 |  | 35.25 | [8 empty] | 99.27 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.22 |  |  | 91.02 | [9 empty] | 100.00 |  |  | 86.60
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 22.75 |  | 35.25 | [8 empty] | 99.27 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.22 |  |  | 91.02 | [9 empty] | 100.00 |  |  | 87.29
LF [%] |  |  |  |  | 105.64 | 97.07 |  |  |  | 18.02 |  | 34.99 | [8 empty] | 94.94 |  |  | 98.38 | [6 empty] | 103.61 |  | 103.53 |  |  |  | 104.80 |  |  | 105.25 |  |  | 97.50 | [9 empty] | 106.44 |  |  | 89.20
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 23.12 |  | 36.11 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 91.25 | [9 empty] | 100.00 |  |  | 87.53
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.73 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.61 |  |  | 8.98 | [9 empty] | 0.00 |  |  | 0.96
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.73 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.61 |  |  | 8.98 | [9 empty] | 0.00 |  |  | 0.85
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 77.25 |  | 64.75 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.17 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 11.86
XUF [%] |  |  |  |  | 0.00 | 4.40 |  |  |  | 3.96 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.68
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 148500.84 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.19 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.05 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.37 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.3 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.34 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.32 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.68 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2001 |  |  |  | Data not provided
2002 |  |  |  | 7176.18 |  |  | 7543 |  |  |  | 950 | [10 empty] | 84.06 |  |  |  | 85.51 | [5 empty] | 86.23 |  |  | 86.11 |  |  |  | 1.33 |  | 1.16 | [8 empty] | 13.33 |  |  |  |  | 1.45
2003 |  |  |  | 6973.93 |  |  | 7154 |  |  |  | 950 | [10 empty] | 81.33 |  |  |  | 82.56 | [5 empty] | 83.80 |  |  | 81.67 |  |  |  | 2.81 |  | 2.39 | [8 empty] | 15.05 |  |  |  |  | 1.23
2004 |  |  |  | 7439.31 |  |  | 7766 |  |  |  | 950 | [10 empty] | 87.75 |  |  |  | 87.96 | [5 empty] | 89.15 |  |  | 88.41 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 11.87 |  |  |  |  | 0.21
2005 |  |  |  | 7232.86 |  |  | 7628 |  |  |  | 950 | [10 empty] | 85.85 |  |  |  | 86.87 | [5 empty] | 86.90 |  |  | 87.07 |  |  |  | 0.60 |  | 0.52 | [8 empty] | 12.60 |  |  |  |  | 1.02
2006 |  |  |  | 7216.42 |  |  | 7386 |  |  |  | 950 | [10 empty] | 83.82 |  |  |  | 84.19 | [5 empty] | 86.71 |  |  | 84.32 |  |  |  | 0.29 |  | 3.46 | [8 empty] | 12.35 |  |  |  |  | 0.38
2007 |  |  |  | 7309.44 |  |  | 7536 |  |  |  | 950 | [10 empty] | 85.28 |  |  |  | 85.48 | [5 empty] | 87.83 |  |  | 86.03 |  |  |  | 0.55 |  | 0.47 | [8 empty] | 14.04 |  |  |  |  | 0.20
2008 |  |  |  | 7745.73 |  |  | 7799 |  |  |  | 950 | [10 empty] | 88.53 |  |  |  | 88.56 | [5 empty] | 92.82 |  |  | 88.79 |  |  |  | 1.00 |  | 0.89 | [8 empty] | 10.54 |  |  |  |  | 0.03
2009 |  |  |  | 7927.02 |  |  | 7916 |  |  |  | 950 | [10 empty] | 90.27 |  |  |  | 90.29 | [5 empty] | 95.25 |  |  | 90.37 |  |  |  | 0.52 |  | 0.47 | [8 empty] | 9.25 |  |  |  |  | 0.01
2010 |  |  |  | 7398.47 |  |  | 7828 |  |  |  | 950 | [10 empty] | 88.60 |  |  |  | 88.91 | [5 empty] | 88.90 |  |  | 89.36 |  |  |  | 2.23 |  | 2.02 | [8 empty] | 9.06 |  |  |  |  | 0.32
2011 |  |  |  | 7695.35 |  |  | 7736 |  |  |  | 950 | [10 empty] | 88.24 |  |  |  | 88.24 | [5 empty] | 92.48 |  |  | 88.32 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 11.68 |  |  |  |  | 0.00
2012 |  |  |  | 7569.03 |  |  | 7614 |  |  |  | 950 | [10 empty] | 86.42 |  |  |  | 86.51 | [5 empty] | 90.70 |  |  | 86.68 |  |  |  | 0.10 |  | 1.40 | [8 empty] | 12.09 |  |  |  |  | 0.09
2013 |  |  |  | 8557.12 |  |  | 8618 |  |  |  | 950 | [10 empty] | 98.15 |  |  |  | 98.15 | [5 empty] | 102.83 |  |  | 98.38 |  |  |  | 1.85 |  | 1.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 7227.67 |  |  | 7498 |  |  |  | 950 | [10 empty] | 85.13 |  |  |  | 85.37 | [5 empty] | 86.84 |  |  | 85.58 |  |  |  | 1.82 |  | 1.58 | [8 empty] | 13.05 |  |  |  |  | 0.25
2015 |  |  |  | 6713.50 |  |  | 6980 |  |  |  | 950 | [10 empty] | 76.83 |  |  |  | 76.83 | [5 empty] | 80.67 |  |  | 79.68 |  |  |  | 7.21 |  | 5.97 | [8 empty] | 17.21 |  |  |  |  | 0.00
2016 |  |  |  | 8833.60 |  |  | 8753 |  |  |  | 950 | [10 empty] | 99.63 |  |  |  | 99.63 | [5 empty] | 105.86 |  |  | 99.65 |  |  |  | 0.37 |  | 0.37 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7840.38 |  |  | 7825 |  |  |  | 950 | [10 empty] | 89.24 |  |  |  | 89.24 | [5 empty] | 94.21 |  |  | 89.33 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 10.76 |  |  |  |  | 0.00
2018 |  |  |  | 7609.90 |  |  | 7719 |  |  |  | 950 | [10 empty] | 87.71 |  |  |  | 87.98 | [5 empty] | 91.44 |  |  | 88.12 |  |  |  | 0.74 |  | 1.07 | [8 empty] | 10.95 |  |  |  |  | 0.27
2019 |  |  |  | 8620.25 |  |  | 8723 |  |  |  | 950 | [10 empty] | 99.49 |  |  |  | 99.52 | [5 empty] | 103.58 |  |  | 99.58 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.00 |  |  |  |  | 0.03
2020 |  |  |  | 7443.25 |  |  | 7689 |  |  |  | 950 | [10 empty] | 86.60 |  |  |  | 87.29 | [5 empty] | 89.20 |  |  | 87.53 |  |  |  | 0.96 |  | 0.85 | [8 empty] | 11.86 |  |  |  |  | 0.68
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2001 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 63 | [14 empty] | 90
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1032 | [14 empty] | 884
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 7
E. |  | Testing of plant systems or components | [39 empty] | 2
L. |  | Human factor related | [39 empty] | 3
Subtotal | [22 empty] | 1032 |  |  |  | 63 | [10 empty] | 891 |  |  |  | 95
Total | [22 empty] | 1095 | [14 empty] | 986
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2001 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 2
16. |  |  | Steam generation systems | [34 empty] | 36
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
33. |  |  | Circulating Water System | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 32
42. |  |  | Electrical Power Supply Systems | [19 empty] | 63 | [14 empty] | 16
Total | [22 empty] | 63 | [14 empty] | 95
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-February, April-Desember. Additional electricity generation amounted to 309074.9 MWh. The unit was in the overhaul outage from 2020.03.08 to 2020.05.01. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-2
2020 Operating Experience
RU-62 | [8 empty] | ROSTOV-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | FAEA (Federal Atomic Energy Agency)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1983-05-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2010-03-18
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2010-12-10
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 10 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 0.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7864.15 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.61 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.79 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.21 %
Load Factor (LF) | [18 empty] | : | 94.24 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.18 %
Operating Factor (OF) | [18 empty] | : | 90.87 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 802 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 728.64 | 0.00 |  |  |  | 641.24 |  | 709.91 | [8 empty] | 680.97 |  |  | 662.57 | [6 empty] | 730.99 |  | 732.66 |  |  |  | 720.27 |  |  | 752.34 |  |  | 741.81 | [9 empty] | 762.74 |  |  | 7864.15
EAF [%] |  |  |  |  | 100.00 | 0.21 |  |  |  | 84.59 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 97.87 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.61
UCF [%] |  |  |  |  | 100.00 | 0.21 |  |  |  | 84.59 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.79
LF [%] |  |  |  |  | 103.09 | 0.00 |  |  |  | 90.72 |  | 103.79 | [8 empty] | 96.35 |  |  | 96.87 | [6 empty] | 103.42 |  | 103.66 |  |  |  | 105.30 |  |  | 106.44 |  |  | 108.45 | [9 empty] | 107.91 |  |  | 94.24
OF [%] |  |  |  |  | 100.00 | 0.57 |  |  |  | 85.22 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.87
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.07 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.06 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
PUF [%] |  |  |  |  | 0.00 | 99.79 |  |  |  | 15.35 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.21
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 2.13 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.18
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 81022.05 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.1 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.87 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.58 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 92.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.29 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2010 |  |  |  | 4303.76 |  |  | 6133 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.93 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 7368.43 |  |  | 7944 |  |  |  | 950 | [10 empty] | 89.41 |  |  |  | 90.23 | [5 empty] | 88.55 |  |  | 90.70 |  |  |  | 0.63 |  | 0.58 | [8 empty] | 9.19 |  |  |  |  | 0.82
2012 |  |  |  | 7433.18 |  |  | 7781 |  |  |  | 950 | [10 empty] | 87.61 |  |  |  | 87.79 | [5 empty] | 89.08 |  |  | 88.58 |  |  |  | 1.30 |  | 1.16 | [8 empty] | 11.05 |  |  |  |  | 0.18
2013 |  |  |  | 7832.67 |  |  | 8151 |  |  |  | 950 | [10 empty] | 92.80 |  |  |  | 92.80 | [5 empty] | 94.12 |  |  | 93.05 |  |  |  | 0.55 |  | 0.51 | [8 empty] | 6.69 |  |  |  |  | 0.00
2014 |  |  |  | 7741.45 |  |  | 8018 |  |  |  | 950 | [10 empty] | 91.20 |  |  |  | 91.29 | [5 empty] | 93.01 |  |  | 91.52 |  |  |  | 0.26 |  | 0.24 | [8 empty] | 8.47 |  |  |  |  | 0.09
2015 |  |  |  | 7525.83 |  |  | 7610 |  |  |  | 950 | [10 empty] | 86.39 |  |  |  | 86.41 | [5 empty] | 90.43 |  |  | 86.87 |  |  |  | 1.26 |  | 1.11 | [8 empty] | 12.48 |  |  |  |  | 0.03
2016 |  |  |  | 7890.03 |  |  | 7974 |  |  |  | 950 | [10 empty] | 90.15 |  |  |  | 90.69 | [5 empty] | 94.55 |  |  | 90.78 |  |  |  | 1.44 |  | 1.33 | [8 empty] | 7.98 |  |  |  |  | 0.54
2017 |  |  |  | 7734.15 |  |  | 7755 |  |  |  | 950 | [10 empty] | 88.29 |  |  |  | 88.31 | [5 empty] | 92.94 |  |  | 88.53 |  |  |  | 11.64 |  | 11.63 | [8 empty] | 0.06 |  |  |  |  | 0.01
2018 |  |  |  | 6666.68 |  |  | 6845 |  |  |  | 950 | [10 empty] | 76.80 |  |  |  | 77.90 | [5 empty] | 80.11 |  |  | 78.14 |  |  |  | 12.50 |  | 11.13 | [8 empty] | 10.98 |  |  |  |  | 1.09
2019 |  |  |  | 8662.06 |  |  | 8650 |  |  |  | 950 | [10 empty] | 98.71 |  |  |  | 98.72 | [5 empty] | 104.09 |  |  | 98.74 |  |  |  | 1.28 |  | 1.28 | [8 empty] | 0.00 |  |  |  |  | 0.01
2020 |  |  |  | 7864.15 |  |  | 7982 |  |  |  | 950 | [10 empty] | 90.61 |  |  |  | 90.79 | [5 empty] | 94.24 |  |  | 90.87 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.21 |  |  |  |  | 0.18
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2010 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 235
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 803 | [14 empty] | 593
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 57
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
Subtotal | [22 empty] | 803 | [14 empty] | 650 |  |  |  | 235 | [11 empty] | 1
Total | [22 empty] | 803 | [14 empty] | 886
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2010 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 45
41. |  |  | Main Generator Systems | [34 empty] | 101
42. |  |  | Electrical Power Supply Systems | [34 empty] | 53
Total | [37 empty] | 219
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January, March-December. Additional electricity generation amounted to 370403.9 MWh. The unit was in the intermediate outage from 2020.02.01 to 2020.03.05. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-3
2020 Operating Experience
RU-63 | [8 empty] | ROSTOV-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-09-15
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-12-27
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-09-17
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 6 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7651.88 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.38 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.89 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.26 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.36 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.38 %
Load Factor (LF) | [18 empty] | : | 91.7 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.47 %
Operating Factor (OF) | [18 empty] | : | 92 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 703 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 149.39 | 705.82 |  |  |  | 671.20 |  | 638.29 | [8 empty] | 680.97 |  |  | 635.03 | [6 empty] | 691.68 |  | 717.51 |  |  |  | 702.18 |  |  | 737.65 |  |  | 568.10 | [9 empty] | 754.06 |  |  | 7651.88
EAF [%] |  |  |  |  | 21.22 | 100.00 |  |  |  | 91.61 |  | 93.28 | [8 empty] | 99.09 |  |  | 98.09 | [6 empty] | 97.68 |  | 99.79 |  |  |  | 99.75 |  |  | 100.00 |  |  | 79.16 | [9 empty] | 100.00 |  |  | 89.89
UCF [%] |  |  |  |  | 21.22 | 100.00 |  |  |  | 91.61 |  | 93.28 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 79.16 | [9 empty] | 100.00 |  |  | 90.36
LF [%] |  |  |  |  | 21.14 | 106.75 |  |  |  | 94.96 |  | 93.32 | [8 empty] | 96.35 |  |  | 92.84 | [6 empty] | 97.86 |  | 101.52 |  |  |  | 102.66 |  |  | 104.36 |  |  | 83.06 | [9 empty] | 106.69 |  |  | 91.70
OF [%] |  |  |  |  | 21.51 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 83.47 | [9 empty] | 100.00 |  |  | 92.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 8.39 |  | 6.72 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.38
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 8.39 |  | 6.72 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.26
PUF [%] |  |  |  |  | 78.78 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 20.84 | [9 empty] | 0.00 |  |  | 8.38
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.91 |  |  | 1.91 | [6 empty] | 2.32 |  | 0.21 |  |  |  | 0.25 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.47
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 40386.58 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.99 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.98 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.64 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.19 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.17 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.59 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.21 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.23 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 5132.22 |  |  | 7040 |  |  |  | 950 | [10 empty] | 99.65 |  |  |  | 99.65 | [5 empty] | 104.56 |  |  | 100.00 |  |  |  | 0.35 |  | 0.35 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6110.00 |  |  | 6728 |  |  |  | 950 | [10 empty] | 71.98 |  |  |  | 73.43 | [5 empty] | 73.22 |  |  | 76.59 |  |  |  | 5.40 |  | 14.24 | [8 empty] | 12.33 |  |  |  |  | 1.45
2017 |  |  |  | 6422.53 |  |  | 6888 |  |  |  | 950 | [10 empty] | 76.35 |  |  |  | 77.80 | [5 empty] | 77.18 |  |  | 78.63 |  |  |  | 3.24 |  | 2.60 | [8 empty] | 19.60 |  |  |  |  | 1.45
2018 |  |  |  | 7709.57 |  |  | 7962 |  |  |  | 950 | [10 empty] | 90.24 |  |  |  | 90.77 | [5 empty] | 92.64 |  |  | 90.89 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 8.95 |  |  |  |  | 0.53
2019 |  |  |  | 7360.63 |  |  | 7848 |  |  |  | 950 | [10 empty] | 87.53 |  |  |  | 89.97 | [5 empty] | 88.45 |  |  | 89.59 |  |  |  | 0.71 |  | 0.64 | [8 empty] | 9.39 |  |  |  |  | 2.44
2020 |  |  |  | 7651.88 |  |  | 8081 |  |  |  | 950 | [10 empty] | 89.89 |  |  |  | 90.36 | [5 empty] | 91.70 |  |  | 92.00 |  |  |  | 1.38 |  | 1.26 | [8 empty] | 8.38 |  |  |  |  | 0.47
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2015 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 238
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 726 | [14 empty] | 628
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 19
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 318
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 13
Subtotal | [22 empty] | 726 | [14 empty] | 965 |  |  |  | 238 | [11 empty] | 13
Total | [22 empty] | 726 | [14 empty] | 1216
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2015 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 33
16. |  |  | Steam generation systems | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 17
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
33. |  |  | Circulating Water System | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 150
Total | [37 empty] | 208
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January - December. Additional electricity generation amounted to 313085.6 MWh. The unit was in the routine maintenance outage from 2020.11.09 to 2020.11.15 and in the in the overhoul outage from 2020.01.01 to 2020.01.25. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-4
2020 Operating Experience
RU-64 | [8 empty] | ROSTOV-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-06-16
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-02-02
Gross electrical power | [12 empty] | : |  |  | 1030 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-09-28
Reference unit power (net) | [12 empty] | : |  |  | 979 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8066.5 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.5 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.86 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.5 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.45 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.05 %
Load Factor (LF) | [18 empty] | : | 93.8 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.58 %
Operating Factor (OF) | [18 empty] | : | 97.6 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 211 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 728.84 | 682.53 |  |  |  | 725.17 |  | 680.30 | [8 empty] | 657.15 |  |  | 617.47 | [6 empty] | 664.51 |  | 691.54 |  |  |  | 553.26 |  |  | 602.73 |  |  | 706.70 | [9 empty] | 756.29 |  |  | 8066.50
EAF [%] |  |  |  |  | 99.83 | 99.14 |  |  |  | 99.76 |  | 99.69 | [8 empty] | 95.73 |  |  | 91.98 | [6 empty] | 92.55 |  | 96.05 |  |  |  | 80.06 |  |  | 84.13 |  |  | 99.44 | [9 empty] | 100.00 |  |  | 94.86
UCF [%] |  |  |  |  | 100.00 | 99.32 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 83.54 |  |  | 86.44 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.45
LF [%] |  |  |  |  | 100.06 | 100.17 |  |  |  | 99.56 |  | 96.51 | [8 empty] | 90.22 |  |  | 87.60 | [6 empty] | 91.23 |  | 94.94 |  |  |  | 78.49 |  |  | 82.75 |  |  | 100.26 | [9 empty] | 103.83 |  |  | 93.80
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 83.75 |  |  | 87.37 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.60
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 16.46 |  |  | 13.56 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.50
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 16.46 |  |  | 13.56 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.50
PUF [%] |  |  |  |  | 0.00 | 0.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
XUF [%] |  |  |  |  | 0.17 | 0.17 |  |  |  | 0.24 |  | 0.31 | [8 empty] | 4.27 |  |  | 8.02 | [6 empty] | 7.45 |  | 3.95 |  |  |  | 3.48 |  |  | 2.31 |  |  | 0.56 | [9 empty] | 0.00 |  |  | 2.58
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 21112.2 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.34 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.27 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 5.08 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.7 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.72 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 93.82 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 5681.92 |  |  | 6556 |  |  |  | 950 | [10 empty] | 99.97 |  |  |  | 99.99 | [5 empty] | 103.76 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.00 |  |  |  |  | 0.01
2019 |  |  |  | 7430.57 |  |  | 7751 |  |  |  | 979 | [10 empty] | 87.01 |  |  |  | 88.29 | [5 empty] | 86.64 |  |  | 88.48 |  |  |  | 0.40 |  | 0.35 | [8 empty] | 11.36 |  |  |  |  | 1.28
2020 |  |  |  | 8066.50 |  |  | 8573 |  |  |  | 979 | [10 empty] | 94.86 |  |  |  | 97.45 | [5 empty] | 93.80 |  |  | 97.60 |  |  |  | 2.50 |  | 2.50 | [8 empty] | 0.05 |  |  |  |  | 2.58
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2018 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 216 | [14 empty] | 108
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 501
L. |  | Human factor related | [39 empty] | 4
Subtotal | [26 empty] | 216 | [10 empty] | 501 |  |  |  | 112
Total | [22 empty] | 216 | [14 empty] | 613
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2018 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [19 empty] | 28 | [14 empty] | 14
32. |  |  | Feedwater and Main Steam System | [19 empty] | 188 | [14 empty] | 94
33. |  |  | Circulating Water System | [34 empty] | 4
Total | [22 empty] | 216 | [14 empty] | 112
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January - April, November- December. Additional electricity generation amounted to 73199 MWh. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## SMOLENSK-1
2020 Operating Experience
RU-23 | [8 empty] | SMOLENSK-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-10-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-12-09
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-09-30
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 175 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | PH / DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6155 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.51 %
Energy Availability Factor (EAF) | [18 empty] | : | 73.88 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.38 %
Unit Capability Factor (UCF) | [18 empty] | : | 73.96 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.66 %
Load Factor (LF) | [18 empty] | : | 75.75 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.08 %
Operating Factor (OF) | [18 empty] | : | 78.89 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1854 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 62.87 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 706.65 | 688.52 |  |  |  | 589.35 |  | 403.98 | [8 empty] | 713.11 |  |  | 670.94 | [6 empty] | 60.86 |  | 0.00 |  |  |  | 265.39 |  |  | 636.81 |  |  | 697.66 | [9 empty] | 721.72 |  |  | 6155.00
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 83.14 |  | 62.73 | [8 empty] | 100.00 |  |  | 99.20 | [6 empty] | 10.74 |  | 0.00 |  |  |  | 42.16 |  |  | 90.50 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 73.88
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 83.14 |  | 62.73 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 10.94 |  | 0.00 |  |  |  | 42.16 |  |  | 90.50 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 73.96
LF [%] |  |  |  |  | 102.68 | 106.95 |  |  |  | 85.64 |  | 60.66 | [8 empty] | 103.62 |  |  | 100.74 | [6 empty] | 8.84 |  | 0.00 |  |  |  | 39.85 |  |  | 92.53 |  |  | 104.75 | [9 empty] | 104.87 |  |  | 75.75
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 84.14 |  | 66.67 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 13.17 |  | 0.00 |  |  |  | 85.28 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.89
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 3.37 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 2.55 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.51
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 2.19 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 2.37 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.38
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 16.86 |  | 35.08 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 89.06 |  | 100.00 |  |  |  | 57.84 |  |  | 7.13 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 25.66
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.80 | [6 empty] | 0.20 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.08
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 227572.27 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.41 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.87 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.63 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 22.37 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.43 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.76 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.13 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 4744.20 |  |  | 7223 |  |  |  | 925 | [10 empty] | 99.64 |  |  |  | 99.64 | [5 empty] | 100.76 |  |  | 99.86 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 6921.35 |  |  | 7830 |  |  |  | 925 | [10 empty] | 84.23 |  |  |  | 84.23 | [5 empty] | 85.18 |  |  | 89.14 |  |  |  | 2.64 |  | 2.28 | [8 empty] | 13.49 |  |  |  |  | 0.00
1985 |  |  |  | 5850.24 |  |  | 6806 |  |  |  | 925 | [10 empty] | 72.40 |  |  |  | 74.87 | [5 empty] | 72.20 |  |  | 77.69 |  |  |  | 1.52 |  | 1.15 | [8 empty] | 23.97 |  |  |  |  | 2.47
1986 |  |  |  | 3039.75 |  |  | 3472 |  |  |  | 925 | [10 empty] | 37.79 |  |  |  | 37.79 | [5 empty] | 37.51 |  |  | 39.63 |  |  |  | 0.05 |  | 0.02 | [8 empty] | 62.20 |  |  |  |  | 0.00
1987 |  |  |  | 7445.76 |  |  | 7620 |  |  |  | 1000 | [10 empty] | 86.72 |  |  |  | 86.72 | [5 empty] | 85.00 |  |  | 86.99 |  |  |  | 2.08 |  | 1.84 | [8 empty] | 11.44 |  |  |  |  | 0.00
1988 |  |  |  | 6695.59 |  |  | 7288 |  |  |  | 925 | [10 empty] | 81.89 |  |  |  | 81.89 | [5 empty] | 82.41 |  |  | 82.97 |  |  |  | 0.44 |  | 0.36 | [8 empty] | 17.75 |  |  |  |  | 0.00
1989 |  |  |  | 6506.46 |  |  | 7177 |  |  |  | 925 | [10 empty] | 79.32 |  |  |  | 79.70 | [5 empty] | 80.30 |  |  | 81.93 |  |  |  | 6.44 |  | 5.49 | [8 empty] | 14.82 |  |  |  |  | 0.38
1990 |  |  |  | 6227.84 |  |  | 6851 |  |  |  | 925 | [10 empty] | 76.14 |  |  |  | 76.59 | [5 empty] | 76.86 |  |  | 78.21 |  |  |  | 3.90 |  | 3.11 | [8 empty] | 20.30 |  |  |  |  | 0.45
1991 |  |  |  | 6693.92 |  |  | 7252 |  |  |  | 925 | [10 empty] | 81.29 |  |  |  | 81.29 | [5 empty] | 82.61 |  |  | 82.79 |  |  |  | 3.68 |  | 3.11 | [8 empty] | 15.60 |  |  |  |  | 0.00
1992 |  |  |  | 6849.38 |  |  | 7563 |  |  |  | 925 | [10 empty] | 83.69 |  |  |  | 83.69 | [5 empty] | 84.31 |  |  | 86.11 |  |  |  | 2.55 |  | 2.19 | [8 empty] | 14.12 |  |  |  |  | 0.00
1993 |  |  |  | 6290.56 |  |  | 6993 |  |  |  | 925 | [10 empty] | 78.01 |  |  |  | 78.41 | [5 empty] | 77.63 |  |  | 79.83 |  |  |  | 0.38 |  | 0.30 | [8 empty] | 21.29 |  |  |  |  | 0.40
1994 |  |  |  | 4217.84 |  |  | 6286 |  |  |  | 925 | [10 empty] | 57.81 |  |  |  | 71.04 | [5 empty] | 52.05 |  |  | 71.76 |  |  |  | 0.20 |  | 0.14 | [8 empty] | 28.82 |  |  |  |  | 13.23
1995 |  |  |  | 5002.47 |  |  | 6390 |  |  |  | 925 | [10 empty] | 62.97 |  |  |  | 77.35 | [5 empty] | 61.74 |  |  | 72.95 |  |  |  | 1.91 |  | 1.50 | [8 empty] | 21.15 |  |  |  |  | 14.38
1996 |  |  |  | 5666.43 |  |  | 6604 |  |  |  | 925 | [10 empty] | 71.56 |  |  |  | 71.73 | [5 empty] | 69.74 |  |  | 75.18 |  |  |  | 1.05 |  | 0.76 | [8 empty] | 27.51 |  |  |  |  | 0.17
1997 |  |  |  | 4674.51 |  |  | 5366 |  |  |  | 925 | [10 empty] | 57.82 |  |  |  | 59.14 | [5 empty] | 57.69 |  |  | 61.26 |  |  |  | 2.88 |  | 1.75 | [8 empty] | 39.11 |  |  |  |  | 1.32
1998 |  |  |  | 3554.08 |  |  | 5411 |  |  |  | 925 | [10 empty] | 45.04 |  |  |  | 58.85 | [5 empty] | 43.86 |  |  | 61.77 |  |  |  | 3.49 |  | 2.13 | [8 empty] | 39.02 |  |  |  |  | 13.81
1999 |  |  |  | 6478.89 |  |  | 7417 |  |  |  | 925 | [10 empty] | 80.06 |  |  |  | 83.51 | [5 empty] | 79.96 |  |  | 84.67 |  |  |  | 3.29 |  | 2.84 | [8 empty] | 13.65 |  |  |  |  | 3.45
2000 |  |  |  | 5228.48 |  |  | 5738 |  |  |  | 925 | [10 empty] | 63.83 |  |  |  | 64.36 | [5 empty] | 64.35 |  |  | 65.32 |  |  |  | 0.06 |  | 0.04 | [8 empty] | 35.60 |  |  |  |  | 0.53
2001 |  |  |  | 5165.12 |  |  | 5940 |  |  |  | 925 | [10 empty] | 63.24 |  |  |  | 67.43 | [5 empty] | 63.74 |  |  | 67.81 |  |  |  | 2.61 |  | 1.81 | [8 empty] | 30.76 |  |  |  |  | 4.19
2002 |  |  |  | 6866.73 |  |  | 7587 |  |  |  | 925 | [10 empty] | 83.69 |  |  |  | 85.10 | [5 empty] | 84.74 |  |  | 86.61 |  |  |  | 2.59 |  | 2.26 | [8 empty] | 12.64 |  |  |  |  | 1.41
2003 |  |  |  | 6711.76 |  |  | 7533 |  |  |  | 925 | [10 empty] | 82.90 |  |  |  | 84.38 | [5 empty] | 82.83 |  |  | 85.99 |  |  |  | 3.18 |  | 2.77 | [8 empty] | 12.85 |  |  |  |  | 1.48
2004 |  |  |  | 2337.12 |  |  | 2592 |  |  |  | 925 | [10 empty] | 28.50 |  |  |  | 29.09 | [5 empty] | 28.76 |  |  | 29.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 70.91 |  |  |  |  | 0.59
2005 |  |  |  | 7354.10 |  |  | 8414 |  |  |  | 925 | [10 empty] | 90.63 |  |  |  | 94.66 | [5 empty] | 90.75 |  |  | 96.04 |  |  |  | 0.80 |  | 0.76 | [8 empty] | 4.58 |  |  |  |  | 4.03
2006 |  |  |  | 5417.08 |  |  | 6021 |  |  |  | 925 | [10 empty] | 67.09 |  |  |  | 67.09 | [5 empty] | 66.85 |  |  | 68.73 |  |  |  | 1.33 |  | 3.79 | [8 empty] | 29.12 |  |  |  |  | 0.00
2007 |  |  |  | 6569.65 |  |  | 7138 |  |  |  | 925 | [10 empty] | 80.25 |  |  |  | 80.82 | [5 empty] | 81.08 |  |  | 81.48 |  |  |  | 0.20 |  | 0.16 | [8 empty] | 19.02 |  |  |  |  | 0.57
2008 |  |  |  | 7794.93 |  |  | 8430 |  |  |  | 925 | [10 empty] | 94.94 |  |  |  | 95.19 | [5 empty] | 95.94 |  |  | 95.97 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 4.79 |  |  |  |  | 0.25
2009 |  |  |  | 6122.29 |  |  | 6974 |  |  |  | 925 | [10 empty] | 77.32 |  |  |  | 77.60 | [5 empty] | 75.56 |  |  | 79.61 |  |  |  | 12.28 |  | 10.86 | [8 empty] | 11.54 |  |  |  |  | 0.28
2010 |  |  |  | 4896.26 |  |  | 5424 |  |  |  | 925 | [10 empty] | 61.10 |  |  |  | 61.75 | [5 empty] | 60.43 |  |  | 61.92 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 38.24 |  |  |  |  | 0.65
2011 |  |  |  | 5444.54 |  |  | 5899 |  |  |  | 925 | [10 empty] | 65.97 |  |  |  | 66.24 | [5 empty] | 67.20 |  |  | 67.35 |  |  |  | 0.05 |  | 0.03 | [8 empty] | 33.73 |  |  |  |  | 0.27
2012 |  |  |  | 6306.76 |  |  | 6741 |  |  |  | 925 | [10 empty] | 75.88 |  |  |  | 76.32 | [5 empty] | 77.62 |  |  | 76.74 |  |  |  | 1.76 |  | 1.37 | [8 empty] | 22.31 |  |  |  |  | 0.45
2013 |  |  |  | 7775.27 |  |  | 8267 |  |  |  | 925 | [10 empty] | 93.47 |  |  |  | 93.80 | [5 empty] | 95.96 |  |  | 94.37 |  |  |  | 3.63 |  | 3.53 | [8 empty] | 2.67 |  |  |  |  | 0.34
2014 |  |  |  | 7330.99 |  |  | 7691 |  |  |  | 925 | [10 empty] | 87.06 |  |  |  | 87.27 | [5 empty] | 90.46 |  |  | 87.79 |  |  |  | 0.92 |  | 0.83 | [8 empty] | 11.89 |  |  |  |  | 0.21
2015 |  |  |  | 7050.99 |  |  | 7394 |  |  |  | 925 | [10 empty] | 83.24 |  |  |  | 83.37 | [5 empty] | 87.02 |  |  | 84.41 |  |  |  | 2.18 |  | 1.86 | [8 empty] | 14.77 |  |  |  |  | 0.14
2016 |  |  |  | 6746.07 |  |  | 7003 |  |  |  | 925 | [10 empty] | 79.38 |  |  |  | 79.45 | [5 empty] | 83.03 |  |  | 79.72 |  |  |  | 0.15 |  | 0.12 | [8 empty] | 20.42 |  |  |  |  | 0.07
2017 |  |  |  | 6710.68 |  |  | 7720 |  |  |  | 925 | [10 empty] | 80.35 |  |  |  | 80.44 | [5 empty] | 82.82 |  |  | 88.13 |  |  |  | 9.47 |  | 8.41 | [8 empty] | 11.15 |  |  |  |  | 0.08
2018 |  |  |  | 6788.06 |  |  | 7256 |  |  |  | 925 | [10 empty] | 80.82 |  |  |  | 80.92 | [5 empty] | 83.77 |  |  | 82.83 |  |  |  | 4.80 |  | 4.08 | [8 empty] | 15.00 |  |  |  |  | 0.10
2019 |  |  |  | 6373.86 |  |  | 6673 |  |  |  | 925 | [10 empty] | 75.51 |  |  |  | 75.51 | [5 empty] | 78.66 |  |  | 76.18 |  |  |  | 0.54 |  | 2.32 | [8 empty] | 22.17 |  |  |  |  | 0.00
2020 |  |  |  | 6155.00 |  |  | 6930 |  |  |  | 925 | [10 empty] | 73.88 |  |  |  | 73.96 | [5 empty] | 75.75 |  |  | 78.89 |  |  |  | 0.51 |  | 0.38 | [8 empty] | 25.66 |  |  |  |  | 0.08
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 99
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1854 | [14 empty] | 1182
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 286
E. |  | Testing of plant systems or components | [35 empty] | 20
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 276
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 12
Subtotal | [22 empty] | 1854 | [14 empty] | 1764 |  |  |  | 100 | [11 empty] | 17
Total | [22 empty] | 1854 | [14 empty] | 1881
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 21
12. |  |  | Reactor I&C Systems | [34 empty] | 14
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [34 empty] | 23
16. |  |  | Steam generation systems | [34 empty] | 0
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 0
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [37 empty] | 98
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-June, October-December. Additional electricity generation amounted to 218181.6 MWh. The unit was in the routine maintenance outage from 2020.03.27 to 2020.04.17 and in the in the intermediate outage from 2020.07.05 to 2020.09.05. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## SMOLENSK-2
2020 Operating Experience
RU-24 | [8 empty] | SMOLENSK-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-06-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-05-31
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-07-02
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 175 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | PH / DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7313.92 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.86 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.74 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.76 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.86 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.38 %
Load Factor (LF) | [18 empty] | : | 90.02 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.11 %
Operating Factor (OF) | [18 empty] | : | 89.23 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 946 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 98.65 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 704.07 | 682.66 |  |  |  | 718.81 |  | 682.29 | [8 empty] | 426.85 |  |  | 0.00 | [6 empty] | 660.32 |  | 683.34 |  |  |  | 674.04 |  |  | 665.65 |  |  | 696.14 | [9 empty] | 719.74 |  |  | 7313.92
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 62.84 |  |  | 0.63 | [6 empty] | 95.40 |  | 99.11 |  |  |  | 99.90 |  |  | 94.19 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.74
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 62.84 |  |  | 0.63 | [6 empty] | 95.76 |  | 100.00 |  |  |  | 100.00 |  |  | 94.19 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.86
LF [%] |  |  |  |  | 102.31 | 106.04 |  |  |  | 104.45 |  | 102.45 | [8 empty] | 62.02 |  |  | 0.00 | [6 empty] | 95.95 |  | 99.29 |  |  |  | 101.21 |  |  | 96.72 |  |  | 104.52 | [9 empty] | 104.58 |  |  | 90.02
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 68.01 |  |  | 1.67 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.23
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.86 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 5.81 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.86
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.21 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 5.81 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.76
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.95 |  |  | 99.37 | [6 empty] | 4.24 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 11.38
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.36 |  | 0.89 |  |  |  | 0.10 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.11
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 219978.3 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.88 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.74 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.61 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.06 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.23 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.87 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 3623.94 |  |  | 4593 |  |  |  | 925 | [10 empty] | 81.32 |  |  |  | 90.61 | [5 empty] | 80.97 |  |  | 91.89 |  |  |  | 6.31 |  | 6.10 | [8 empty] | 3.29 |  |  |  |  | 9.28
1986 |  |  |  | 6667.30 |  |  | 7442 |  |  |  | 925 | [10 empty] | 82.57 |  |  |  | 82.57 | [5 empty] | 82.28 |  |  | 84.95 |  |  |  | 1.56 |  | 1.31 | [8 empty] | 16.12 |  |  |  |  | 0.00
1987 |  |  |  | 6364.93 |  |  | 6707 |  |  |  | 1000 | [10 empty] | 74.52 |  |  |  | 74.52 | [5 empty] | 72.66 |  |  | 76.56 |  |  |  | 4.46 |  | 3.48 | [8 empty] | 22.01 |  |  |  |  | 0.00
1988 |  |  |  | 6757.16 |  |  | 7594 |  |  |  | 925 | [10 empty] | 83.49 |  |  |  | 83.55 | [5 empty] | 83.16 |  |  | 86.45 |  |  |  | 1.83 |  | 1.56 | [8 empty] | 14.89 |  |  |  |  | 0.06
1989 |  |  |  | 6627.33 |  |  | 7336 |  |  |  | 925 | [10 empty] | 81.50 |  |  |  | 81.85 | [5 empty] | 81.79 |  |  | 83.74 |  |  |  | 2.69 |  | 2.26 | [8 empty] | 15.88 |  |  |  |  | 0.36
1990 |  |  |  | 6710.59 |  |  | 7453 |  |  |  | 925 | [10 empty] | 82.52 |  |  |  | 82.97 | [5 empty] | 82.82 |  |  | 85.08 |  |  |  | 5.48 |  | 4.81 | [8 empty] | 12.22 |  |  |  |  | 0.45
1991 |  |  |  | 5796.72 |  |  | 6495 |  |  |  | 925 | [10 empty] | 71.36 |  |  |  | 71.36 | [5 empty] | 71.54 |  |  | 74.14 |  |  |  | 3.36 |  | 2.48 | [8 empty] | 26.16 |  |  |  |  | 0.00
1992 |  |  |  | 6731.61 |  |  | 7472 |  |  |  | 925 | [10 empty] | 82.63 |  |  |  | 83.90 | [5 empty] | 82.86 |  |  | 85.07 |  |  |  | 1.14 |  | 0.96 | [8 empty] | 15.13 |  |  |  |  | 1.28
1993 |  |  |  | 6634.11 |  |  | 7492 |  |  |  | 925 | [10 empty] | 82.69 |  |  |  | 84.90 | [5 empty] | 81.87 |  |  | 85.53 |  |  |  | 0.29 |  | 0.25 | [8 empty] | 14.86 |  |  |  |  | 2.21
1994 |  |  |  | 5259.83 |  |  | 7044 |  |  |  | 925 | [10 empty] | 66.56 |  |  |  | 80.25 | [5 empty] | 64.91 |  |  | 80.41 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 19.73 |  |  |  |  | 13.69
1995 |  |  |  | 5337.40 |  |  | 6738 |  |  |  | 925 | [10 empty] | 66.84 |  |  |  | 80.32 | [5 empty] | 65.87 |  |  | 76.92 |  |  |  | 0.26 |  | 0.21 | [8 empty] | 19.47 |  |  |  |  | 13.49
1996 |  |  |  | 6127.71 |  |  | 7010 |  |  |  | 925 | [10 empty] | 77.82 |  |  |  | 79.09 | [5 empty] | 75.42 |  |  | 79.80 |  |  |  | 0.89 |  | 0.71 | [8 empty] | 20.20 |  |  |  |  | 1.27
1997 |  |  |  | 4991.02 |  |  | 5642 |  |  |  | 925 | [10 empty] | 61.57 |  |  |  | 61.70 | [5 empty] | 61.59 |  |  | 64.41 |  |  |  | 4.41 |  | 2.84 | [8 empty] | 35.46 |  |  |  |  | 0.13
1998 |  |  |  | 5297.02 |  |  | 6576 |  |  |  | 925 | [10 empty] | 65.58 |  |  |  | 73.88 | [5 empty] | 65.37 |  |  | 75.07 |  |  |  | 1.37 |  | 1.03 | [8 empty] | 25.09 |  |  |  |  | 8.30
1999 |  |  |  | 5362.50 |  |  | 6090 |  |  |  | 925 | [10 empty] | 66.03 |  |  |  | 69.14 | [5 empty] | 66.18 |  |  | 69.52 |  |  |  | 0.12 |  | 0.09 | [8 empty] | 30.78 |  |  |  |  | 3.11
2000 |  |  |  | 6566.15 |  |  | 7108 |  |  |  | 925 | [10 empty] | 80.10 |  |  |  | 80.54 | [5 empty] | 80.81 |  |  | 80.92 |  |  |  | 3.91 |  | 3.28 | [8 empty] | 16.19 |  |  |  |  | 0.44
2001 |  |  |  | 6457.64 |  |  | 7537 |  |  |  | 925 | [10 empty] | 78.96 |  |  |  | 81.02 | [5 empty] | 79.69 |  |  | 86.04 |  |  |  | 6.08 |  | 5.25 | [8 empty] | 13.73 |  |  |  |  | 2.06
2002 |  |  |  | 3431.09 |  |  | 3890 |  |  |  | 925 | [10 empty] | 41.69 |  |  |  | 43.60 | [5 empty] | 42.34 |  |  | 44.41 |  |  |  | 1.66 |  | 0.74 | [8 empty] | 55.66 |  |  |  |  | 1.91
2003 |  |  |  | 6438.59 |  |  | 7734 |  |  |  | 925 | [10 empty] | 79.13 |  |  |  | 81.42 | [5 empty] | 79.46 |  |  | 88.29 |  |  |  | 8.45 |  | 7.52 | [8 empty] | 11.06 |  |  |  |  | 2.29
2004 |  |  |  | 7480.14 |  |  | 8312 |  |  |  | 925 | [10 empty] | 90.85 |  |  |  | 93.66 | [5 empty] | 92.06 |  |  | 94.63 |  |  |  | 0.62 |  | 0.59 | [8 empty] | 5.75 |  |  |  |  | 2.80
2005 |  |  |  | 3053.40 |  |  | 3734 |  |  |  | 925 | [10 empty] | 37.72 |  |  |  | 41.71 | [5 empty] | 37.68 |  |  | 42.63 |  |  |  | 0.42 |  | 0.17 | [8 empty] | 58.11 |  |  |  |  | 4.00
2006 |  |  |  | 7623.87 |  |  | 8306 |  |  |  | 925 | [10 empty] | 93.15 |  |  |  | 93.15 | [5 empty] | 94.09 |  |  | 94.82 |  |  |  | 0.16 |  | 1.27 | [8 empty] | 5.58 |  |  |  |  | 0.00
2007 |  |  |  | 4096.43 |  |  | 4878 |  |  |  | 925 | [10 empty] | 49.68 |  |  |  | 50.76 | [5 empty] | 50.55 |  |  | 55.68 |  |  |  | 2.50 |  | 1.30 | [8 empty] | 47.94 |  |  |  |  | 1.08
2008 |  |  |  | 6718.76 |  |  | 7823 |  |  |  | 925 | [10 empty] | 83.20 |  |  |  | 83.66 | [5 empty] | 82.69 |  |  | 89.06 |  |  |  | 1.71 |  | 1.46 | [8 empty] | 14.89 |  |  |  |  | 0.46
2009 |  |  |  | 7668.41 |  |  | 8279 |  |  |  | 925 | [10 empty] | 93.84 |  |  |  | 94.10 | [5 empty] | 94.64 |  |  | 94.51 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 5.82 |  |  |  |  | 0.26
2010 |  |  |  | 6651.23 |  |  | 7626 |  |  |  | 925 | [10 empty] | 82.04 |  |  |  | 82.31 | [5 empty] | 82.08 |  |  | 87.05 |  |  |  | 0.56 |  | 0.46 | [8 empty] | 17.23 |  |  |  |  | 0.27
2011 |  |  |  | 7328.17 |  |  | 8314 |  |  |  | 925 | [10 empty] | 89.65 |  |  |  | 90.28 | [5 empty] | 90.45 |  |  | 94.92 |  |  |  | 3.58 |  | 3.36 | [8 empty] | 6.36 |  |  |  |  | 0.63
2012 |  |  |  | 6802.21 |  |  | 7767 |  |  |  | 925 | [10 empty] | 85.94 |  |  |  | 86.34 | [5 empty] | 83.72 |  |  | 88.42 |  |  |  | 3.24 |  | 2.89 | [8 empty] | 10.76 |  |  |  |  | 0.41
2013 |  |  |  | 2630.28 |  |  | 3045 |  |  |  | 925 | [10 empty] | 32.61 |  |  |  | 32.62 | [5 empty] | 32.46 |  |  | 34.76 |  |  |  | 5.82 |  | 2.02 | [8 empty] | 65.36 |  |  |  |  | 0.01
2014 |  |  |  | 7821.17 |  |  | 8524 |  |  |  | 925 | [10 empty] | 94.28 |  |  |  | 94.57 | [5 empty] | 96.51 |  |  | 97.29 |  |  |  | 1.89 |  | 1.82 | [8 empty] | 3.61 |  |  |  |  | 0.29
2015 |  |  |  | 7404.36 |  |  | 7809 |  |  |  | 925 | [10 empty] | 87.61 |  |  |  | 87.79 | [5 empty] | 91.38 |  |  | 89.14 |  |  |  | 1.26 |  | 1.12 | [8 empty] | 11.09 |  |  |  |  | 0.17
2016 |  |  |  | 6910.57 |  |  | 7360 |  |  |  | 925 | [10 empty] | 82.20 |  |  |  | 82.32 | [5 empty] | 85.05 |  |  | 83.79 |  |  |  | 11.12 |  | 10.30 | [8 empty] | 7.39 |  |  |  |  | 0.12
2017 |  |  |  | 6307.00 |  |  | 6734 |  |  |  | 925 | [10 empty] | 74.22 |  |  |  | 74.29 | [5 empty] | 77.84 |  |  | 76.87 |  |  |  | 5.42 |  | 4.26 | [8 empty] | 21.45 |  |  |  |  | 0.07
2018 |  |  |  | 7352.87 |  |  | 7772 |  |  |  | 925 | [10 empty] | 87.37 |  |  |  | 87.42 | [5 empty] | 90.74 |  |  | 88.72 |  |  |  | 3.77 |  | 3.43 | [8 empty] | 9.16 |  |  |  |  | 0.05
2019 |  |  |  | 5918.57 |  |  | 6573 |  |  |  | 925 | [10 empty] | 70.29 |  |  |  | 70.31 | [5 empty] | 73.04 |  |  | 75.03 |  |  |  | 7.33 |  | 5.56 | [8 empty] | 24.13 |  |  |  |  | 0.03
2020 |  |  |  | 7313.92 |  |  | 7838 |  |  |  | 925 | [10 empty] | 87.74 |  |  |  | 87.86 | [5 empty] | 90.02 |  |  | 89.23 |  |  |  | 0.86 |  | 0.76 | [8 empty] | 11.38 |  |  |  |  | 0.11
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 86
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 979 | [14 empty] | 1012
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 271
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 136
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 248
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 10
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 979 | [14 empty] | 1667 |  |  |  | 90 | [11 empty] | 21
Total | [22 empty] | 979 | [14 empty] | 1778
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 24
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 5
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 14
Total | [37 empty] | 89
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-May, Jule-December. Additional electricity generation amounted to 192032.775 MWh. The unit was in the intermediate outage from 2020.05.22 to 2020.07.05. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## SMOLENSK-3
2020 Operating Experience
RU-67 | [8 empty] | SMOLENSK-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (JSC ATOMENERGOMASH)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-05-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-01-17
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-10-12
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 175 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | PH / DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6927.47 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.35 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.21 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.29 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.22 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.49 %
Load Factor (LF) | [18 empty] | : | 85.26 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 86.79 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1160 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 59.98 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 86.73 | 57.22 |  |  |  | 506.14 |  | 661.52 | [8 empty] | 710.73 |  |  | 676.26 | [6 empty] | 699.43 |  | 702.71 |  |  |  | 686.33 |  |  | 715.53 |  |  | 702.13 | [9 empty] | 722.74 |  |  | 6927.47
EAF [%] |  |  |  |  | 13.76 | 11.82 |  |  |  | 73.91 |  | 96.80 | [8 empty] | 100.00 |  |  | 99.74 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.21
UCF [%] |  |  |  |  | 13.76 | 11.82 |  |  |  | 73.91 |  | 96.80 | [8 empty] | 100.00 |  |  | 99.74 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.22
LF [%] |  |  |  |  | 12.60 | 8.89 |  |  |  | 73.55 |  | 99.33 | [8 empty] | 103.27 |  |  | 101.54 | [6 empty] | 101.63 |  | 102.11 |  |  |  | 103.05 |  |  | 103.97 |  |  | 105.42 | [9 empty] | 105.02 |  |  | 85.26
OF [%] |  |  |  |  | 16.26 | 22.84 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.79
FLR [%] |  |  |  |  | 12.48 | 0.00 |  |  |  | 0.00 |  | 1.28 | [8 empty] | 0.00 |  |  | 0.26 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.35
UCL [%] |  |  |  |  | 1.96 | 0.00 |  |  |  | 0.00 |  | 1.25 | [8 empty] | 0.00 |  |  | 0.26 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.29
PUF [%] |  |  |  |  | 84.27 | 88.18 |  |  |  | 26.09 |  | 1.95 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.49
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 199177.39 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.04 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.75 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.54 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.71 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.07 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.61 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.27 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 4570.76 |  |  | 6767 |  |  |  | 925 | [10 empty] | 99.06 |  |  |  | 99.06 | [5 empty] | 101.20 |  |  | 100.00 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.32 |  |  |  |  | 0.00
1991 |  |  |  | 6561.74 |  |  | 7338 |  |  |  | 925 | [10 empty] | 80.87 |  |  |  | 80.87 | [5 empty] | 80.98 |  |  | 83.77 |  |  |  | 3.91 |  | 3.29 | [8 empty] | 15.84 |  |  |  |  | 0.00
1992 |  |  |  | 6866.56 |  |  | 7515 |  |  |  | 925 | [10 empty] | 83.90 |  |  |  | 83.92 | [5 empty] | 84.52 |  |  | 85.56 |  |  |  | 6.83 |  | 6.15 | [8 empty] | 9.93 |  |  |  |  | 0.03
1993 |  |  |  | 6595.99 |  |  | 7419 |  |  |  | 925 | [10 empty] | 81.42 |  |  |  | 82.61 | [5 empty] | 81.40 |  |  | 84.69 |  |  |  | 1.76 |  | 1.48 | [8 empty] | 15.91 |  |  |  |  | 1.19
1994 |  |  |  | 5513.66 |  |  | 6701 |  |  |  | 925 | [10 empty] | 72.50 |  |  |  | 82.28 | [5 empty] | 68.04 |  |  | 76.50 |  |  |  | 0.43 |  | 0.35 | [8 empty] | 17.37 |  |  |  |  | 9.78
1995 |  |  |  | 5090.97 |  |  | 5844 |  |  |  | 925 | [10 empty] | 63.17 |  |  |  | 78.19 | [5 empty] | 62.83 |  |  | 66.71 |  |  |  | 1.13 |  | 0.89 | [8 empty] | 20.92 |  |  |  |  | 15.02
1996 |  |  |  | 6496.64 |  |  | 7268 |  |  |  | 925 | [10 empty] | 80.83 |  |  |  | 82.16 | [5 empty] | 79.96 |  |  | 82.74 |  |  |  | 7.42 |  | 6.58 | [8 empty] | 11.25 |  |  |  |  | 1.34
1997 |  |  |  | 5559.27 |  |  | 6469 |  |  |  | 925 | [10 empty] | 69.32 |  |  |  | 69.32 | [5 empty] | 68.61 |  |  | 73.85 |  |  |  | 6.03 |  | 4.45 | [8 empty] | 26.23 |  |  |  |  | 0.00
1998 |  |  |  | 4575.89 |  |  | 6162 |  |  |  | 925 | [10 empty] | 57.53 |  |  |  | 68.95 | [5 empty] | 56.47 |  |  | 70.34 |  |  |  | 3.48 |  | 2.49 | [8 empty] | 28.56 |  |  |  |  | 11.42
1999 |  |  |  | 6410.98 |  |  | 7063 |  |  |  | 925 | [10 empty] | 78.19 |  |  |  | 79.31 | [5 empty] | 79.12 |  |  | 80.63 |  |  |  | 0.39 |  | 0.31 | [8 empty] | 20.38 |  |  |  |  | 1.12
2000 |  |  |  | 6970.48 |  |  | 7542 |  |  |  | 925 | [10 empty] | 84.58 |  |  |  | 84.70 | [5 empty] | 85.79 |  |  | 85.86 |  |  |  | 2.37 |  | 2.06 | [8 empty] | 13.24 |  |  |  |  | 0.12
2001 |  |  |  | 6951.72 |  |  | 7823 |  |  |  | 925 | [10 empty] | 85.39 |  |  |  | 87.30 | [5 empty] | 85.79 |  |  | 89.30 |  |  |  | 0.15 |  | 0.13 | [8 empty] | 12.57 |  |  |  |  | 1.91
2002 |  |  |  | 7204.90 |  |  | 7831 |  |  |  | 925 | [10 empty] | 87.67 |  |  |  | 88.71 | [5 empty] | 88.92 |  |  | 89.39 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 11.02 |  |  |  |  | 1.03
2003 |  |  |  | 7038.23 |  |  | 7697 |  |  |  | 925 | [10 empty] | 86.26 |  |  |  | 87.09 | [5 empty] | 86.86 |  |  | 87.87 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 12.73 |  |  |  |  | 0.82
2004 |  |  |  | 7085.74 |  |  | 7765 |  |  |  | 925 | [10 empty] | 86.88 |  |  |  | 87.86 | [5 empty] | 87.21 |  |  | 88.40 |  |  |  | 0.00 |  | 0.08 | [8 empty] | 12.05 |  |  |  |  | 0.99
2005 |  |  |  | 7303.68 |  |  | 8192 |  |  |  | 925 | [10 empty] | 90.36 |  |  |  | 93.06 | [5 empty] | 90.14 |  |  | 93.52 |  |  |  | 1.07 |  | 1.01 | [8 empty] | 5.93 |  |  |  |  | 2.70
2006 |  |  |  | 4942.96 |  |  | 5631 |  |  |  | 925 | [10 empty] | 60.71 |  |  |  | 60.71 | [5 empty] | 61.00 |  |  | 64.28 |  |  |  | 4.39 |  | 3.15 | [8 empty] | 36.14 |  |  |  |  | 0.00
2007 |  |  |  | 7566.25 |  |  | 8247 |  |  |  | 925 | [10 empty] | 92.46 |  |  |  | 93.15 | [5 empty] | 93.38 |  |  | 94.14 |  |  |  | 1.48 |  | 1.40 | [8 empty] | 5.44 |  |  |  |  | 0.70
2008 |  |  |  | 5093.44 |  |  | 5396 |  |  |  | 925 | [10 empty] | 61.23 |  |  |  | 61.29 | [5 empty] | 62.69 |  |  | 61.43 |  |  |  | 0.07 |  | 0.04 | [8 empty] | 38.67 |  |  |  |  | 0.06
2009 |  |  |  | 6082.98 |  |  | 6706 |  |  |  | 925 | [10 empty] | 74.30 |  |  |  | 74.31 | [5 empty] | 75.07 |  |  | 76.55 |  |  |  | 1.66 |  | 1.26 | [8 empty] | 24.44 |  |  |  |  | 0.00
2010 |  |  |  | 7738.82 |  |  | 8233 |  |  |  | 925 | [10 empty] | 93.55 |  |  |  | 93.71 | [5 empty] | 95.51 |  |  | 93.98 |  |  |  | 0.12 |  | 0.38 | [8 empty] | 5.91 |  |  |  |  | 0.16
2011 |  |  |  | 6241.79 |  |  | 6579 |  |  |  | 925 | [10 empty] | 73.98 |  |  |  | 74.01 | [5 empty] | 77.04 |  |  | 75.11 |  |  |  | 0.15 |  | 0.11 | [8 empty] | 25.88 |  |  |  |  | 0.03
2012 |  |  |  | 5845.23 |  |  | 6279 |  |  |  | 925 | [10 empty] | 70.62 |  |  |  | 70.62 | [5 empty] | 71.94 |  |  | 71.48 |  |  |  | 7.04 |  | 5.35 | [8 empty] | 24.03 |  |  |  |  | 0.00
2013 |  |  |  | 7942.17 |  |  | 8471 |  |  |  | 925 | [10 empty] | 95.12 |  |  |  | 95.19 | [5 empty] | 98.02 |  |  | 96.70 |  |  |  | 2.12 |  | 2.06 | [8 empty] | 2.75 |  |  |  |  | 0.07
2014 |  |  |  | 6894.49 |  |  | 7219 |  |  |  | 925 | [10 empty] | 81.72 |  |  |  | 81.82 | [5 empty] | 85.08 |  |  | 82.40 |  |  |  | 0.30 |  | 0.24 | [8 empty] | 17.94 |  |  |  |  | 0.10
2015 |  |  |  | 8079.91 |  |  | 8364 |  |  |  | 925 | [10 empty] | 95.01 |  |  |  | 95.01 | [5 empty] | 99.71 |  |  | 95.48 |  |  |  | 0.33 |  | 0.31 | [8 empty] | 4.67 |  |  |  |  | 0.00
2016 |  |  |  | 7116.59 |  |  | 7352 |  |  |  | 925 | [10 empty] | 83.34 |  |  |  | 83.35 | [5 empty] | 87.59 |  |  | 83.70 |  |  |  | 2.89 |  | 2.48 | [8 empty] | 14.17 |  |  |  |  | 0.02
2017 |  |  |  | 7946.26 |  |  | 8266 |  |  |  | 925 | [10 empty] | 93.42 |  |  |  | 93.49 | [5 empty] | 98.07 |  |  | 94.36 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 6.40 |  |  |  |  | 0.06
2018 |  |  |  | 3494.62 |  |  | 3601 |  |  |  | 925 | [10 empty] | 40.84 |  |  |  | 40.84 | [5 empty] | 43.13 |  |  | 41.11 |  |  |  | 0.66 |  | 1.09 | [8 empty] | 58.07 |  |  |  |  | 0.00
2019 |  |  |  | 6207.98 |  |  | 6723 |  |  |  | 925 | [10 empty] | 74.43 |  |  |  | 74.46 | [5 empty] | 76.61 |  |  | 76.75 |  |  |  | 5.25 |  | 4.90 | [8 empty] | 20.64 |  |  |  |  | 0.03
2020 |  |  |  | 6927.47 |  |  | 7624 |  |  |  | 925 | [10 empty] | 83.21 |  |  |  | 83.22 | [5 empty] | 85.26 |  |  | 86.79 |  |  |  | 0.35 |  | 0.29 | [8 empty] | 16.49 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1990 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 72
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1160 | [14 empty] | 1005
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 261
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 178
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 103
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 53
Z. |  | Other | [39 empty] | 18
Subtotal | [22 empty] | 1160 | [14 empty] | 1547 |  |  |  | 92 | [11 empty] | 54
Total | [22 empty] | 1160 | [14 empty] | 1693
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1990 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 14
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 9
16. |  |  | Steam generation systems | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 8
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 4
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 73
Highlights (2020)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January, March-December. Additional electricity generation amounted to 228664.625 MWh. The unit was in the routine maintenance outage from 2020.01.06 to 2020.02.23. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.