## ATUCHA-1
2020 Operating Experience
AR-1 | [8 empty] | ATUCHA-1 | [26 empty] | ARGENTINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Owner | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Reactor Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Turbine Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / PHWR KWU | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-06-01
Thermal power | [12 empty] | : |  |  | 1179 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-03-19
Gross electrical power | [12 empty] | : |  |  | 362 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-06-24
Reference unit power (net) | [12 empty] | : |  |  | 340 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 11.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 303.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.28
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.85 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 11140 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.51 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.26
| Active core height/length [m] | [13 empty] | : |  |  | 5.3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 21
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 250 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 23.22 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2680.41 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.8 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.75 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.84 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.75 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.41 %
Load Factor (LF) | [18 empty] | : | 89.75 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.84 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 717 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 219.61 | 229.57 |  |  |  | 245.52 |  | 241.76 | [8 empty] | 251.69 |  |  | 240.33 | [6 empty] | 145.52 |  | 126.44 |  |  |  | 243.77 |  |  | 249.18 |  |  | 240.19 | [9 empty] | 246.83 |  |  | 2680.41
EAF [%] |  |  |  |  | 86.82 | 97.01 |  |  |  | 97.06 |  | 98.76 | [8 empty] | 99.50 |  |  | 98.18 | [6 empty] | 57.53 |  | 49.98 |  |  |  | 99.58 |  |  | 98.50 |  |  | 98.12 | [9 empty] | 97.58 |  |  | 89.75
UCF [%] |  |  |  |  | 86.82 | 97.01 |  |  |  | 97.06 |  | 98.76 | [8 empty] | 99.50 |  |  | 98.18 | [6 empty] | 57.53 |  | 49.98 |  |  |  | 99.58 |  |  | 98.50 |  |  | 98.12 | [9 empty] | 97.58 |  |  | 89.75
LF [%] |  |  |  |  | 86.82 | 97.01 |  |  |  | 97.06 |  | 98.76 | [8 empty] | 99.50 |  |  | 98.18 | [6 empty] | 57.53 |  | 49.98 |  |  |  | 99.58 |  |  | 98.50 |  |  | 98.12 | [9 empty] | 97.58 |  |  | 89.75
OF [%] |  |  |  |  | 91.53 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 57.53 |  | 54.57 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.84
FLR [%] |  |  |  |  | 13.18 | 2.99 |  |  |  | 2.94 |  | 1.24 | [8 empty] | 0.50 |  |  | 1.82 | [6 empty] | 0.93 |  | 20.42 |  |  |  | 0.42 |  |  | 1.50 |  |  | 1.88 | [9 empty] | 2.42 |  |  | 3.80
UCL [%] |  |  |  |  | 13.18 | 2.99 |  |  |  | 2.94 |  | 1.24 | [8 empty] | 0.50 |  |  | 1.82 | [6 empty] | 0.54 |  | 16.25 |  |  |  | 0.42 |  |  | 1.50 |  |  | 1.88 | [9 empty] | 2.42 |  |  | 3.84
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 41.94 |  | 33.77 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.41
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 99169.81 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.54 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.5 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.07 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.46 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.46 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.49 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.96 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.83 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 947.50 |  |  | 4458 |  |  |  | 321 | [10 empty] | 50.27 |  |  |  | 51.01 | [5 empty] | 50.29 |  |  | 65.96 |  |  |  | 16.06 |  | 9.76 | [8 empty] | 39.23 |  |  |  |  | 0.73
1975 |  |  |  | 2357.80 |  |  | 7730 |  |  |  | 319 | [10 empty] | 85.63 |  |  |  | 85.63 | [5 empty] | 84.37 |  |  | 88.24 |  |  |  | 5.33 |  | 4.82 | [8 empty] | 9.55 |  |  |  |  | 0.00
1976 |  |  |  | 2408.60 |  |  | 7808 |  |  |  | 319 | [10 empty] | 86.89 |  |  |  | 86.89 | [5 empty] | 85.96 |  |  | 88.89 |  |  |  | 10.93 |  | 10.66 | [8 empty] | 2.45 |  |  |  |  | 0.00
1977 |  |  |  | 1537.00 |  |  | 4650 |  |  |  | 336 | [10 empty] | 52.99 |  |  |  | 52.99 | [5 empty] | 52.15 |  |  | 53.08 |  |  |  | 24.01 |  | 16.75 | [8 empty] | 30.26 |  |  |  |  | 0.00
1978 |  |  |  | 2711.81 |  |  | 8026 |  |  |  | 345 | [10 empty] | 90.89 |  |  |  | 90.89 | [5 empty] | 89.73 |  |  | 91.62 |  |  |  | 8.88 |  | 8.85 | [8 empty] | 0.26 |  |  |  |  | 0.00
1979 |  |  |  | 2503.70 |  |  | 7551 |  |  |  | 335 | [10 empty] | 84.14 |  |  |  | 84.14 | [5 empty] | 85.32 |  |  | 86.20 |  |  |  | 15.72 |  | 15.70 | [8 empty] | 0.16 |  |  |  |  | 0.00
1980 |  |  |  | 2180.50 |  |  | 6947 |  |  |  | 335 | [10 empty] | 73.51 |  |  |  | 73.51 | [5 empty] | 74.10 |  |  | 79.09 |  |  |  | 8.40 |  | 6.74 | [8 empty] | 19.74 |  |  |  |  | 0.00
1981 |  |  |  | 2647.60 |  |  | 8120 |  |  |  | 335 | [10 empty] | 89.66 |  |  |  | 89.66 | [5 empty] | 90.22 |  |  | 92.69 |  |  |  | 8.38 |  | 8.20 | [8 empty] | 2.13 |  |  |  |  | 0.00
1982 |  |  |  | 1753.60 |  |  | 5600 |  |  |  | 335 | [10 empty] | 59.17 |  |  |  | 59.17 | [5 empty] | 59.76 |  |  | 63.93 |  |  |  | 13.18 |  | 8.98 | [8 empty] | 31.85 |  |  |  |  | 0.00
1983 |  |  |  | 2356.00 |  |  | 8101 |  |  |  | 335 | [10 empty] | 78.36 |  |  |  | 78.36 | [5 empty] | 80.28 |  |  | 92.48 |  |  |  | 11.09 |  | 9.77 | [8 empty] | 11.87 |  |  |  |  | 0.00
1984 |  |  |  | 1706.12 |  |  | 8678 |  |  |  | 335 | [10 empty] | 98.74 |  |  |  | 98.74 | [5 empty] | 57.98 |  |  | 98.79 |  |  |  | 1.26 |  | 1.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 1470.45 |  |  | 7159 |  |  |  | 335 | [10 empty] | 91.58 |  |  |  | 91.58 | [5 empty] | 50.11 |  |  | 81.72 |  |  |  | 8.42 |  | 8.42 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 2204.96 |  |  | 7532 |  |  |  | 335 | [10 empty] | 75.83 |  |  |  | 75.83 | [5 empty] | 75.14 |  |  | 85.98 |  |  |  | 10.36 |  | 8.76 | [8 empty] | 15.40 |  |  |  |  | 0.00
1987 |  |  |  | 1405.80 |  |  | 4391 |  |  |  | 335 | [10 empty] | 49.18 |  |  |  | 49.24 | [5 empty] | 47.90 |  |  | 50.13 |  |  |  | 29.90 |  | 21.01 | [8 empty] | 29.75 |  |  |  |  | 0.06
1988 |  |  |  | 808.10 |  |  | 2515 |  |  |  | 335 | [10 empty] | 27.07 |  |  |  | 27.07 | [5 empty] | 27.46 |  |  | 28.63 |  |  |  | 72.93 |  | 72.93 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 0.00 |  |  | 0 |  |  |  | 335 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1990 |  |  |  | 1722.59 |  |  | 7201 |  |  |  | 335 | [10 empty] | 58.70 |  |  |  | 84.89 | [5 empty] | 58.70 |  |  | 82.20 |  |  |  | 6.76 |  | 6.15 | [8 empty] | 8.96 |  |  |  |  | 26.19
1991 |  |  |  | 2721.89 |  |  | 8390 |  |  |  | 335 | [10 empty] | 92.58 |  |  |  | 92.58 | [5 empty] | 92.75 |  |  | 95.78 |  |  |  | 7.35 |  | 7.34 | [8 empty] | 0.08 |  |  |  |  | 0.00
1992 |  |  |  | 2230.24 |  |  | 7089 |  |  |  | 335 | [10 empty] | 76.33 |  |  |  | 76.33 | [5 empty] | 75.79 |  |  | 80.70 |  |  |  | 7.71 |  | 6.38 | [8 empty] | 17.29 |  |  |  |  | 0.00
1993 |  |  |  | 2403.66 |  |  | 7287 |  |  |  | 335 | [10 empty] | 82.16 |  |  |  | 82.16 | [5 empty] | 81.91 |  |  | 83.18 |  |  |  | 6.54 |  | 5.75 | [8 empty] | 12.09 |  |  |  |  | 0.00
1994 |  |  |  | 2651.86 |  |  | 7916 |  |  |  | 335 | [10 empty] | 90.37 |  |  |  | 90.37 | [5 empty] | 90.37 |  |  | 90.37 |  |  |  | 1.19 |  | 1.08 | [8 empty] | 8.55 |  |  |  |  | 0.00
1995 |  |  |  | 2671.71 |  |  | 8376 |  |  |  | 335 | [10 empty] | 92.28 |  |  |  | 92.28 | [5 empty] | 91.04 |  |  | 95.62 |  |  |  | 7.58 |  | 7.57 | [8 empty] | 0.15 |  |  |  |  | 0.00
1996 |  |  |  | 2038.80 |  |  | 6990 |  |  |  | 335 | [10 empty] | 70.62 |  |  |  | 70.62 | [5 empty] | 69.28 |  |  | 79.58 |  |  |  | 6.80 |  | 5.15 | [8 empty] | 24.23 |  |  |  |  | 0.00
1997 |  |  |  | 2720.14 |  |  | 8329 |  |  |  | 335 | [10 empty] | 93.36 |  |  |  | 93.36 | [5 empty] | 92.69 |  |  | 95.08 |  |  |  | 6.64 |  | 6.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 2374.36 |  |  | 7242 |  |  |  | 335 | [10 empty] | 81.32 |  |  |  | 81.40 | [5 empty] | 80.91 |  |  | 82.67 |  |  |  | 6.76 |  | 5.90 | [8 empty] | 12.69 |  |  |  |  | 0.08
1999 |  |  |  | 1395.50 |  |  | 4364 |  |  |  | 335 | [10 empty] | 47.81 |  |  |  | 47.81 | [5 empty] | 47.55 |  |  | 49.82 |  |  |  | 25.70 |  | 16.54 | [8 empty] | 35.66 |  |  |  |  | 0.00
2000 |  |  |  | 1677.85 |  |  | 5038 |  |  |  | 335 | [10 empty] | 56.85 |  |  |  | 72.76 | [5 empty] | 57.02 |  |  | 57.35 |  |  |  | 27.24 |  | 27.24 | [8 empty] | 0.00 |  |  |  |  | 15.92
2001 |  |  |  | 1425.96 |  |  | 4407 |  |  |  | 335 | [10 empty] | 48.74 |  |  |  | 48.74 | [5 empty] | 48.59 |  |  | 50.31 |  |  |  | 28.98 |  | 19.89 | [8 empty] | 31.38 |  |  |  |  | 0.00
2002 |  |  |  | 1011.50 |  |  | 3030 |  |  |  | 335 | [10 empty] | 34.58 |  |  |  | 34.58 | [5 empty] | 34.47 |  |  | 34.59 |  |  |  | 16.39 |  | 6.78 | [8 empty] | 58.64 |  |  |  |  | 0.00
2003 |  |  |  | 2020.60 |  |  | 6094 |  |  |  | 335 | [10 empty] | 68.76 |  |  |  | 68.76 | [5 empty] | 68.85 |  |  | 69.57 |  |  |  | 9.42 |  | 7.15 | [8 empty] | 24.09 |  |  |  |  | 0.00
2004 |  |  |  | 2725.01 |  |  | 8250 |  |  |  | 335 | [10 empty] | 92.17 |  |  |  | 92.17 | [5 empty] | 92.60 |  |  | 93.92 |  |  |  | 7.83 |  | 7.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 1997.96 |  |  | 7004 |  |  |  | 335 | [10 empty] | 68.50 |  |  |  | 68.50 | [5 empty] | 68.08 |  |  | 79.95 |  |  |  | 6.44 |  | 4.72 | [8 empty] | 26.79 |  |  |  |  | 0.00
2006 |  |  |  | 2100.55 |  |  | 6403 |  |  |  | 335 | [10 empty] | 72.10 |  |  |  | 72.10 | [5 empty] | 71.58 |  |  | 73.09 |  |  |  | 14.45 |  | 12.18 | [8 empty] | 15.72 |  |  |  |  | 0.00
2007 |  |  |  | 2718.74 |  |  | 8300 |  |  |  | 335 | [10 empty] | 93.83 |  |  |  | 93.95 | [5 empty] | 92.64 |  |  | 94.75 |  |  |  | 6.05 |  | 6.05 | [8 empty] | 0.00 |  |  |  |  | 0.12
2008 |  |  |  | 2481.26 |  |  | 7562 |  |  |  | 335 | [10 empty] | 85.27 |  |  |  | 85.27 | [5 empty] | 84.32 |  |  | 86.09 |  |  |  | 2.49 |  | 2.18 | [8 empty] | 12.55 |  |  |  |  | 0.00
2009 |  |  |  | 2397.18 |  |  | 7296 |  |  |  | 335 | [10 empty] | 82.88 |  |  |  | 82.88 | [5 empty] | 81.69 |  |  | 83.29 |  |  |  | 0.38 |  | 0.32 | [8 empty] | 16.80 |  |  |  |  | 0.00
2010 |  |  |  | 2782.75 |  |  | 8560 |  |  |  | 335 | [10 empty] | 95.52 |  |  |  | 95.52 | [5 empty] | 94.83 |  |  | 97.72 |  |  |  | 4.48 |  | 4.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 2334.46 |  |  | 7289 |  |  |  | 335 | [10 empty] | 79.63 |  |  |  | 80.28 | [5 empty] | 79.55 |  |  | 83.21 |  |  |  | 4.07 |  | 5.45 | [8 empty] | 14.27 |  |  |  |  | 0.65
2012 |  |  |  | 2477.36 |  |  | 7521 |  |  |  | 335 | [10 empty] | 84.15 |  |  |  | 84.15 | [5 empty] | 84.19 |  |  | 85.62 |  |  |  | 5.20 |  | 4.61 | [8 empty] | 11.24 |  |  |  |  | 0.00
2013 |  |  |  | 2449.53 |  |  | 7310 |  |  |  | 340 | [10 empty] | 82.55 |  |  |  | 83.29 | [5 empty] | 82.75 |  |  | 83.45 |  |  |  | 2.94 |  | 3.49 | [8 empty] | 13.22 |  |  |  |  | 0.73
2014 |  |  |  | 2631.71 |  |  | 7875 |  |  |  | 340 | [10 empty] | 88.78 |  |  |  | 89.28 | [5 empty] | 88.36 |  |  | 89.90 |  |  |  | 0.00 |  | 1.89 | [8 empty] | 8.83 |  |  |  |  | 0.50
2015 |  |  |  | 1951.35 |  |  | 6109 |  |  |  | 340 | [10 empty] | 66.00 |  |  |  | 66.03 | [5 empty] | 65.52 |  |  | 69.74 |  |  |  | 6.26 |  | 6.69 | [8 empty] | 27.28 |  |  |  |  | 0.03
2016 |  |  |  | 2476.82 |  |  | 7700 |  |  |  | 340 | [10 empty] | 83.27 |  |  |  | 83.27 | [5 empty] | 82.93 |  |  | 87.66 |  |  |  | 4.66 |  | 4.40 | [8 empty] | 12.33 |  |  |  |  | 0.00
2017 |  |  |  | 2359.66 |  |  | 7832 |  |  |  | 340 | [10 empty] | 79.70 |  |  |  | 79.70 | [5 empty] | 79.23 |  |  | 89.41 |  |  |  | 5.87 |  | 4.97 | [8 empty] | 15.33 |  |  |  |  | 0.00
2018 |  |  |  | 2274.09 |  |  | 7393 |  |  |  | 340 | [10 empty] | 76.27 |  |  |  | 76.27 | [5 empty] | 76.35 |  |  | 84.39 |  |  |  | 7.72 |  | 7.01 | [8 empty] | 16.73 |  |  |  |  | 0.00
2019 |  |  |  | 2392.40 |  |  | 7341 |  |  |  | 340 | [10 empty] | 80.33 |  |  |  | 80.33 | [5 empty] | 80.33 |  |  | 83.80 |  |  |  | 5.48 |  | 4.66 | [8 empty] | 15.01 |  |  |  |  | 0.00
2020 |  |  |  | 2680.41 |  |  | 8067 |  |  |  | 340 | [10 empty] | 89.75 |  |  |  | 89.75 | [5 empty] | 89.75 |  |  | 91.84 |  |  |  | 3.80 |  | 3.84 | [8 empty] | 6.41 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 169 | [14 empty] | 642
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 29
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 548 | [14 empty] | 1121 |  |  |  | 12
E. |  | Testing of plant systems or components | [35 empty] | 9
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 31
H. |  | Nuclear regulatory requirements | [39 empty] | 64
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 16
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 21
L. |  | Human factor related | [39 empty] | 9
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 2
Subtotal | [22 empty] | 548 |  |  |  | 169 | [10 empty] | 1190 |  |  |  | 727 | [11 empty] | 39
Total | [22 empty] | 717 | [14 empty] | 1956
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 97
12. |  |  | Reactor I&C Systems | [34 empty] | 46
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 25 | [14 empty] | 131
14. |  |  | Safety Systems | [19 empty] | 63 | [14 empty] | 36
15. |  |  | Reactor Cooling Systems | [19 empty] | 80 | [14 empty] | 152
16. |  |  | Steam generation systems | [34 empty] | 48
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 9
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 16
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 22
33. |  |  | Circulating Water System | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 7
42. |  |  | Electrical Power Supply Systems | [34 empty] | 57
Total | [22 empty] | 168 | [14 empty] | 642
Highlights (2020)
2020.01.01 12:00 am to 2020.01.06 03:46 am – Normal operation. Loss of energy due to plant performance, due to various factors (fouling of condenser tubes, performance of equipment, etc.) the theorical generation was not reached. 2020.01.06 03:46 am to 2020.01.06 04:05 – Power ramp down. 2020.01.06 04:05 to 2020.01.08 07:08 pm – Manual shutdown for intervention of TB11S03. 08/01/2020 07:08 pm to 2020.01.10 11:00 am – Power rump-up. 10/01/2020 11:00 am to 2020.06.02 11:50 am –Normal operation. Loss of energy due to plant performance, due to various factors (fouling of condenser tubes, performance of equipment, etc.) the theorical generation was not reached. 2020.06.02 11:50 am to 2020.06.02 06:00 pm – Power ramp down. 2020.06.02 06:00 pm to 2020.06.04 01:00 am – Power reduction for intervention of SD11W011. 2020.06.04 01:00 am to 2020.06.04 06:30 pm – Power ramp-up. 2020.06.04 06:30 pm to 2020.07.18 08:16 pm - Normal operation. Normal operation. Loss of energy due to plant performance, due to various factors (fouling of condenser tubes, performance of equipment, etc.) the theorical generation was not reached. 2020.07.18 08:16 pm to 2020.07.19 12:00 am – Automatic scram due to low rotational speed of a main pump (QF02D01). 2020.07.19 12:00 am to 2020.08.10 08:16 pm – Planned outage. 2020.08.10 08:16 pm to 2020.08.11 09:43 pm – Unplanned extension of planned outage. 2020.08.11 09:43 pm to 2020.08.13 05:16 am – Power ramp-up. 2020.08.13 05:16 am to 2020.08.16 09:51 am – Manualshutdown for intervention of QD01S01. 2020.08.16 09:51 am to 2020.08.18 07:40 am – Power rump-up 2020.08.18 07:40 am to 2020.09.07 08:04 am – Normal operation. Normal operation. Loss of energy due to plant performance, due to various factors (fouling of condenser tubes, performance of equipment, etc.) the theorical generation was not reached. 2020.09.07 08:04 am to 2020.09.08 03:50 am – Power reduction for intervention of RM02D001. 2020.09.08 03:50 am to 2020.10.17 02:06 pm - Normal operation. Normal operation. Loss of energy due to plant performance, due to various factors (fouling of condenser tubes, performance of equipment, etc.) the theorical generation was not reached. 2020.10.17 02:06 pm to 2020.10.17 11:35 pm – Power reduction due to YX04X001 anomaly. 2020.10.17 11:35 pm to 2021.01.01 12:00 am - Normal operation. Normal operation. Loss of energy due to plant performance, due to various factors (fouling of condenser tubes, performance of equipment, etc.) the theorical generation was not reached.

## ATUCHA-2
2020 Operating Experience
AR-3 | [8 empty] | ATUCHA-2 | [26 empty] | ARGENTINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Owner | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Reactor Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / PHWR KWU | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-07-14
Thermal power | [12 empty] | : |  |  | 2160 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-06-25
Gross electrical power | [12 empty] | : |  |  | 745 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-05-26
Reference unit power (net) | [12 empty] | : |  |  | 693 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 6 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 312.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.48
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7800 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.59
| Active core height/length [m] | [13 empty] | : |  |  | 5.3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 21
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 451 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 23.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 18 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2421.87 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 47.24 %
Energy Availability Factor (EAF) | [18 empty] | : | 39.79 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 40.55 %
Unit Capability Factor (UCF) | [18 empty] | : | 39.79 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 19.67 %
Load Factor (LF) | [18 empty] | : | 39.79 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 70.07 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2629 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 241.93 | 246.48 |  |  |  | 306.35 |  | 298.65 | [8 empty] | 309.49 |  |  | 247.55 | [6 empty] | 176.84 |  | 310.82 |  |  |  | 268.65 |  |  | 15.12 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2421.87
EAF [%] |  |  |  |  | 46.92 | 51.10 |  |  |  | 59.42 |  | 59.86 | [8 empty] | 60.03 |  |  | 49.61 | [6 empty] | 34.30 |  | 60.28 |  |  |  | 53.84 |  |  | 2.93 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 39.79
UCF [%] |  |  |  |  | 46.92 | 51.10 |  |  |  | 59.42 |  | 59.86 | [8 empty] | 60.03 |  |  | 49.61 | [6 empty] | 34.30 |  | 60.28 |  |  |  | 53.84 |  |  | 2.93 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 39.79
LF [%] |  |  |  |  | 46.92 | 51.10 |  |  |  | 59.42 |  | 59.86 | [8 empty] | 60.03 |  |  | 49.61 | [6 empty] | 34.30 |  | 60.28 |  |  |  | 53.84 |  |  | 2.93 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 39.79
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 81.81 | [6 empty] | 54.44 |  | 100.00 |  |  |  | 100.00 |  |  | 6.59 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 70.07
FLR [%] |  |  |  |  | 53.08 | 48.90 |  |  |  | 40.58 |  | 40.14 | [8 empty] | 39.97 |  |  | 50.39 | [6 empty] | 65.70 |  | 39.72 |  |  |  | 46.16 |  |  | 55.03 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 47.24
UCL [%] |  |  |  |  | 53.08 | 48.90 |  |  |  | 40.58 |  | 40.14 | [8 empty] | 39.97 |  |  | 50.39 | [6 empty] | 65.70 |  | 39.72 |  |  |  | 46.16 |  |  | 3.59 |  |  | 0.00 | [9 empty] | 58.06 |  |  | 40.55
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 93.48 |  |  | 100.00 | [9 empty] | 41.94 |  |  | 19.67
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 21925.26 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 34.99 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 53.05 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 34.77 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 53.05 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.18 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 52.71 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.96 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 5200.54 |  |  | 8063 |  |  |  | 692 | [10 empty] | 84.64 |  |  |  | 84.64 | [5 empty] | 83.75 |  |  | 89.49 |  |  |  | 15.36 |  | 15.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 3356.61 |  |  | 5130 |  |  |  | 693 | [10 empty] | 56.27 |  |  |  | 56.27 | [5 empty] | 55.29 |  |  | 58.56 |  |  |  | 7.12 |  | 27.04 | [8 empty] | 16.68 |  |  |  |  | 0.00
2018 |  |  |  | 4178.88 |  |  | 6448 |  |  |  | 693 | [10 empty] | 68.84 |  |  |  | 68.84 | [5 empty] | 68.84 |  |  | 73.61 |  |  |  | 20.72 |  | 17.99 | [8 empty] | 13.17 |  |  |  |  | 0.00
2019 |  |  |  | 1748.39 |  |  | 7001 |  |  |  | 693 | [10 empty] | 28.85 |  |  |  | 28.85 | [5 empty] | 28.80 |  |  | 79.92 |  |  |  | 68.93 |  | 64.83 | [8 empty] | 6.32 |  |  |  |  | 0.00
2020 |  |  |  | 2421.87 |  |  | 6155 |  |  |  | 693 | [10 empty] | 39.79 |  |  |  | 39.79 | [5 empty] | 39.79 |  |  | 70.07 |  |  |  | 47.24 |  | 40.55 | [8 empty] | 19.67 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 902 | [14 empty] | 1410
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 1728 | [14 empty] | 1000
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
Subtotal | [22 empty] | 1728 |  |  |  | 902 | [10 empty] | 1000 |  |  |  | 1410 | [11 empty] | 1
Total | [22 empty] | 2630 | [14 empty] | 2411
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2016 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 470 | [14 empty] | 502
12. |  |  | Reactor I&C Systems | [19 empty] | 432 | [14 empty] | 86
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 53
14. |  |  | Safety Systems | [34 empty] | 83
15. |  |  | Reactor Cooling Systems | [34 empty] | 499
16. |  |  | Steam generation systems | [34 empty] | 15
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 27
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
42. |  |  | Electrical Power Supply Systems | [34 empty] | 10
Total | [22 empty] | 902 | [14 empty] | 1291
Highlights (2020)
2020.01.01 12:00 am to 2020.02.19 09:50 pm - Operation at low power (60%). Debris removal strategy from the reactor cooling system. 2020.02.19 09:50 pm to 2020.05.20 11:15 pm - Operation at low power (70%). Debris removal strategy from the reactor cooling system. 2020.05.20 11:15 pm to 2020.05.21 08:47 am – Power ramp down. 2020.05.21 08:47 am to 2020.05.23 07:16 am – Operation at low power due to high sodium concentration in the SG blowdown. 2020.05.23 07:16 am to 2020.05.23 08:38 am – Power ramp-up. 2020.05.23 08:38 am to 2020.06.25 12:43 pm - Operation at low power (70%). Debris removal strategy from the reactor cooling system. 2020.06.25 12:43 pm to 2020.07.15 02:30 am - Manual shutdown to repair a moderator pump (JFB30AP001). 2020.07.15 02:30 am to 2020.07.15 09:05 am - Power ramp-up. 2020.07.15 09:05 am to 2020.08.20 08:00 am - Operation at low power (70%). Debris removal strategy from the reactor cooling system. 2020.08.20 08:00 am to 2020.09.23 06:23 pm – Operation at low power (65%) due to preliminary work for the planned outage. 2020.09.23 06:23 pm to 2020.09.26 01:38 am – Power ramp down. 2020.09.26 01:38 am to 2020.10.03 12:30 am - Operation at low power (55%) due to preliminary work for the planned outage. 2020.10.03 12:30 am to 2020.12.14 12:00 am– Planned outage. 2020.12.14 12:00 am to 2021.01.01 12:00 am – Unplanned extension of planned outage. Reactor Internal Inspection

## EMBALSE
2020 Operating Experience
AR-2 | [8 empty] | EMBALSE | [26 empty] | ARGENTINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Owner | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Reactor Supplier | [7 empty] | : | AECL (ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | AMN (ANSALDO/Asgen)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-04-01
Thermal power | [12 empty] | : |  |  | 2064 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-04-25
Gross electrical power | [12 empty] | : |  |  | 656 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-01-20
Reference unit power (net) | [12 empty] | : |  |  | 608 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 312
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.125
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7190 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 6.28 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.62
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.75 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4910.14 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 6.33 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.88 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 6.22 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.93 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 1.85 %
Load Factor (LF) | [18 empty] | : | 91.94 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.05 %
Operating Factor (OF) | [18 empty] | : | 96.16 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 337 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 331.67 | 328.79 |  |  |  | 375.73 |  | 434.95 | [8 empty] | 452.62 |  |  | 438.83 | [6 empty] | 413.90 |  | 453.95 |  |  |  | 367.57 |  |  | 426.52 |  |  | 438.05 | [9 empty] | 447.57 |  |  | 4910.14
EAF [%] |  |  |  |  | 73.32 | 77.70 |  |  |  | 83.06 |  | 99.36 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 91.50 |  | 100.00 |  |  |  | 83.97 |  |  | 94.29 |  |  | 100.00 | [9 empty] | 98.94 |  |  | 91.88
UCF [%] |  |  |  |  | 73.32 | 77.70 |  |  |  | 83.06 |  | 99.36 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 91.50 |  | 100.00 |  |  |  | 83.97 |  |  | 94.29 |  |  | 100.00 | [9 empty] | 99.58 |  |  | 91.93
LF [%] |  |  |  |  | 73.32 | 77.70 |  |  |  | 83.06 |  | 99.36 | [8 empty] | 100.06 |  |  | 100.25 | [6 empty] | 91.50 |  | 100.35 |  |  |  | 83.97 |  |  | 94.29 |  |  | 100.07 | [9 empty] | 98.94 |  |  | 91.94
OF [%] |  |  |  |  | 100.00 | 91.67 |  |  |  | 91.67 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 91.80 |  | 100.00 |  |  |  | 83.89 |  |  | 94.62 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 96.16
FLR [%] |  |  |  |  | 26.45 | 22.22 |  |  |  | 16.92 |  | 0.44 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 8.50 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.42 |  |  | 6.33
UCL [%] |  |  |  |  | 26.37 | 22.20 |  |  |  | 16.92 |  | 0.44 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 8.50 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.42 |  |  | 6.22
PUF [%] |  |  |  |  | 0.31 | 0.11 |  |  |  | 0.02 |  | 0.21 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 16.03 |  |  | 5.71 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.85
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.64 |  |  | 0.05
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 142321.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.01 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.58 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.47 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.65 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.46 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.29 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 2527.07 |  |  | 6355 |  |  |  | 600 | [10 empty] | 68.74 |  |  |  | 68.74 | [5 empty] | 44.29 |  |  | 70.56 |  |  |  | 5.92 |  | 4.32 | [8 empty] | 26.93 |  |  |  |  | 0.00
1985 |  |  |  | 3778.57 |  |  | 8170 |  |  |  | 600 | [10 empty] | 93.44 |  |  |  | 93.44 | [5 empty] | 71.89 |  |  | 93.26 |  |  |  | 6.15 |  | 6.13 | [8 empty] | 0.43 |  |  |  |  | 0.00
1986 |  |  |  | 3061.67 |  |  | 5847 |  |  |  | 600 | [10 empty] | 66.34 |  |  |  | 67.12 | [5 empty] | 58.25 |  |  | 66.75 |  |  |  | 1.85 |  | 1.27 | [8 empty] | 31.62 |  |  |  |  | 0.78
1987 |  |  |  | 4577.05 |  |  | 7951 |  |  |  | 600 | [10 empty] | 87.92 |  |  |  | 87.92 | [5 empty] | 87.08 |  |  | 90.76 |  |  |  | 5.89 |  | 5.50 | [8 empty] | 6.58 |  |  |  |  | 0.00
1988 |  |  |  | 4560.58 |  |  | 7798 |  |  |  | 600 | [10 empty] | 88.78 |  |  |  | 88.79 | [5 empty] | 86.53 |  |  | 88.78 |  |  |  | 11.21 |  | 11.21 | [8 empty] | 0.00 |  |  |  |  | 0.01
1989 |  |  |  | 4658.98 |  |  | 7804 |  |  |  | 600 | [10 empty] | 89.11 |  |  |  | 90.09 | [5 empty] | 88.64 |  |  | 89.09 |  |  |  | 1.00 |  | 0.91 | [8 empty] | 9.00 |  |  |  |  | 0.98
1990 |  |  |  | 5000.74 |  |  | 8404 |  |  |  | 600 | [10 empty] | 95.10 |  |  |  | 96.49 | [5 empty] | 95.14 |  |  | 95.94 |  |  |  | 1.87 |  | 1.84 | [8 empty] | 1.67 |  |  |  |  | 1.38
1991 |  |  |  | 4498.81 |  |  | 7855 |  |  |  | 600 | [10 empty] | 85.76 |  |  |  | 89.68 | [5 empty] | 85.59 |  |  | 89.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.32 |  |  |  |  | 3.92
1992 |  |  |  | 4353.98 |  |  | 7440 |  |  |  | 600 | [10 empty] | 81.59 |  |  |  | 83.42 | [5 empty] | 82.61 |  |  | 84.70 |  |  |  | 1.12 |  | 0.95 | [8 empty] | 15.64 |  |  |  |  | 1.83
1993 |  |  |  | 4773.27 |  |  | 7956 |  |  |  | 600 | [10 empty] | 90.60 |  |  |  | 90.68 | [5 empty] | 90.82 |  |  | 90.82 |  |  |  | 0.73 |  | 0.67 | [8 empty] | 8.65 |  |  |  |  | 0.08
1994 |  |  |  | 5157.89 |  |  | 8575 |  |  |  | 600 | [10 empty] | 97.78 |  |  |  | 98.27 | [5 empty] | 98.13 |  |  | 97.89 |  |  |  | 1.69 |  | 1.69 | [8 empty] | 0.03 |  |  |  |  | 0.49
1995 |  |  |  | 3897.91 |  |  | 6541 |  |  |  | 600 | [10 empty] | 74.34 |  |  |  | 74.34 | [5 empty] | 74.16 |  |  | 74.67 |  |  |  | 5.54 |  | 4.36 | [8 empty] | 21.30 |  |  |  |  | 0.00
1996 |  |  |  | 4891.97 |  |  | 8176 |  |  |  | 600 | [10 empty] | 92.77 |  |  |  | 92.77 | [5 empty] | 92.82 |  |  | 93.08 |  |  |  | 1.38 |  | 1.30 | [8 empty] | 5.94 |  |  |  |  | 0.00
1997 |  |  |  | 4737.03 |  |  | 7821 |  |  |  | 600 | [10 empty] | 89.27 |  |  |  | 89.27 | [5 empty] | 90.13 |  |  | 89.28 |  |  |  | 0.54 |  | 0.48 | [8 empty] | 10.25 |  |  |  |  | 0.00
1998 |  |  |  | 4555.43 |  |  | 7629 |  |  |  | 600 | [10 empty] | 86.87 |  |  |  | 86.88 | [5 empty] | 86.67 |  |  | 87.09 |  |  |  | 4.13 |  | 3.75 | [8 empty] | 9.38 |  |  |  |  | 0.01
1999 |  |  |  | 5201.79 |  |  | 8700 |  |  |  | 598 | [10 empty] | 99.14 |  |  |  | 99.14 | [5 empty] | 99.30 |  |  | 99.32 |  |  |  | 0.73 |  | 0.73 | [8 empty] | 0.14 |  |  |  |  | 0.00
2000 |  |  |  | 4064.48 |  |  | 6837 |  |  |  | 643 | [10 empty] | 78.08 |  |  |  | 78.19 | [5 empty] | 71.96 |  |  | 77.83 |  |  |  | 8.13 |  | 6.92 | [8 empty] | 14.89 |  |  |  |  | 0.10
2001 |  |  |  | 5128.11 |  |  | 8564 |  |  |  | 600 | [10 empty] | 97.45 |  |  |  | 97.47 | [5 empty] | 97.57 |  |  | 97.76 |  |  |  | 2.29 |  | 2.28 | [8 empty] | 0.25 |  |  |  |  | 0.02
2002 |  |  |  | 4385.52 |  |  | 7401 |  |  |  | 600 | [10 empty] | 83.40 |  |  |  | 84.00 | [5 empty] | 83.44 |  |  | 84.49 |  |  |  | 0.86 |  | 0.72 | [8 empty] | 15.28 |  |  |  |  | 0.59
2003 |  |  |  | 5004.14 |  |  | 8367 |  |  |  | 600 | [10 empty] | 95.07 |  |  |  | 95.13 | [5 empty] | 95.21 |  |  | 95.51 |  |  |  | 4.58 |  | 4.57 | [8 empty] | 0.30 |  |  |  |  | 0.05
2004 |  |  |  | 4589.57 |  |  | 7704 |  |  |  | 600 | [10 empty] | 87.51 |  |  |  | 87.54 | [5 empty] | 87.08 |  |  | 87.70 |  |  |  | 1.27 |  | 1.12 | [8 empty] | 11.33 |  |  |  |  | 0.03
2005 |  |  |  | 4372.48 |  |  | 7341 |  |  |  | 600 | [10 empty] | 83.32 |  |  |  | 83.32 | [5 empty] | 83.19 |  |  | 83.80 |  |  |  | 0.00 |  | 0.43 | [8 empty] | 16.25 |  |  |  |  | 0.00
2006 |  |  |  | 5052.10 |  |  | 8455 |  |  |  | 600 | [10 empty] | 96.23 |  |  |  | 96.23 | [5 empty] | 96.12 |  |  | 96.52 |  |  |  | 3.66 |  | 3.66 | [8 empty] | 0.11 |  |  |  |  | 0.00
2007 |  |  |  | 4003.72 |  |  | 6771 |  |  |  | 600 | [10 empty] | 76.51 |  |  |  | 76.51 | [5 empty] | 76.17 |  |  | 77.29 |  |  |  | 6.19 |  | 5.53 | [8 empty] | 17.96 |  |  |  |  | 0.00
2008 |  |  |  | 4368.61 |  |  | 7382 |  |  |  | 600 | [10 empty] | 82.89 |  |  |  | 82.89 | [5 empty] | 82.89 |  |  | 84.04 |  |  |  | 5.24 |  | 4.65 | [8 empty] | 12.46 |  |  |  |  | 0.00
2009 |  |  |  | 5192.43 |  |  | 8705 |  |  |  | 600 | [10 empty] | 98.79 |  |  |  | 98.79 | [5 empty] | 98.78 |  |  | 99.36 |  |  |  | 0.78 |  | 0.78 | [8 empty] | 0.44 |  |  |  |  | 0.00
2010 |  |  |  | 3908.69 |  |  | 6701 |  |  |  | 600 | [10 empty] | 74.37 |  |  |  | 74.86 | [5 empty] | 74.37 |  |  | 76.50 |  |  |  | 6.11 |  | 4.87 | [8 empty] | 20.26 |  |  |  |  | 0.50
2011 |  |  |  | 3559.35 |  |  | 7405 |  |  |  | 600 | [10 empty] | 67.72 |  |  |  | 67.72 | [5 empty] | 67.72 |  |  | 84.53 |  |  |  | 0.69 |  | 0.47 | [8 empty] | 31.81 |  |  |  |  | 0.00
2012 |  |  |  | 3425.53 |  |  | 7214 |  |  |  | 600 | [10 empty] | 65.07 |  |  |  | 65.07 | [5 empty] | 65.00 |  |  | 82.13 |  |  |  | 0.11 |  | 0.07 | [8 empty] | 34.86 |  |  |  |  | 0.00
2013 |  |  |  | 3285.69 |  |  | 6841 |  |  |  | 600 | [10 empty] | 69.65 |  |  |  | 69.65 | [5 empty] | 62.51 |  |  | 78.09 |  |  |  | 1.31 |  | 0.92 | [8 empty] | 29.43 |  |  |  |  | 0.00
2014 |  |  |  | 1533.11 |  |  | 3678 |  |  |  | 600 | [10 empty] | 99.79 |  |  |  | 99.79 | [5 empty] | 29.17 |  |  | 41.99 |  |  |  | 0.14 |  | 0.14 | [8 empty] | 0.07 |  |  |  |  | 0.00
2015 |  |  |  | 641.36 |  |  | 1564 |  |  |  | 600 | [10 empty] | 99.78 |  |  |  | 99.78 | [5 empty] | 12.20 |  |  | 17.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.22 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 600 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 600 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 600 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 3786.17 |  |  | 7051 |  |  |  | 608 | [10 empty] | 71.76 |  |  |  | 71.76 | [5 empty] | 71.09 |  |  | 80.49 |  |  |  | 3.80 |  | 2.83 | [8 empty] | 25.41 |  |  |  |  | 0.00
2020 |  |  |  | 4910.14 |  |  | 8447 |  |  |  | 608 | [10 empty] | 91.88 |  |  |  | 91.93 | [5 empty] | 91.94 |  |  | 96.16 |  |  |  | 6.33 |  | 6.22 | [8 empty] | 1.85 |  |  |  |  | 0.05
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 180 | [14 empty] | 216
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 95
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 157 | [14 empty] | 663
E. |  | Testing of plant systems or components | [35 empty] | 39 |  |  |  | 1
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 742
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 16
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 17
L. |  | Human factor related | [39 empty] | 1
M. |  | Governmental requirements or court decisions | [51 empty] | 332
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 157 |  |  |  | 180 | [10 empty] | 1539 |  |  |  | 221 | [11 empty] | 366
Total | [22 empty] | 337 | [14 empty] | 2126
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 62 | [14 empty] | 8
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 32
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 63
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 25
32. |  |  | Feedwater and Main Steam System | [19 empty] | 118 | [14 empty] | 22
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 38
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [22 empty] | 180 | [14 empty] | 221
Highlights (2020)
2020.01.01 12:00 am to 2020.01.05 08:37 am – Power reduction due to limitations of the Reactor Regulating System. 2020.01.01 12:00 am to 2020.02.08 01:00 am - Loss of energy due to condenser vacuum reduction. 2020.02.08 12:00 am to 2020.02.08 01:00 am – Power ramp down. 2020.02.08 01:00 am to 2020.02.10 10:48 am - Loss of water in steam generator feedwater header. 2020.02.10 10:48 am to 2020.02.10 09:28 pm – Power ramp-up. 2020.02.10 09:28 pm to 2020.03.13 02:15 pm - Loss of energy due to condenser vacuum reduction. 2020.03.13 02:22 pm to 2020.03.13 03:16 pm – Power ramp down. 2020.03.13 03:16 pm to 2020.03.16 05:16 am – Manual shutdown due to a blocked shield plug. 2020.03.16 05:16 am to 2020.02.16 09:30 am – Power ramp-up. 2020.03.16 09:30 am to 2020.03.21 02:00 pm – Power reduction due to failure of sea water. 2020.03.21 02:00 pm to 2020.04:30 12:00 am - Loss of energy due to condenser vacuum reduction. 2020.07.26 03:00 pm to 2020.07.29 03:19 am - Automatic scram due to failure of a feedwater valve. 2020.07.29 03:19 am to 2020.07.30 06:00 am – Power ramp-up. 2020.09.26 01.05 am to 2020.09.26 04:44 am - Power ramp down. 2020.09.26 04:44 am am to 2020.10.02 05:15 pm – Planned outage. 2020.10.02 05:15 pm to 2020.10.03 01:57 pm – Power ramp-up. 2020.12.01 12:00 am to 2020.12.31 11:59 pm - Loss of performance due to variation of cooling water temperature. 2020.12.21 05:55 pm to 2020.12.22 12:33 pm – Power reduction to carry out testing of the turbine emergency valves.