## CEFR
2020 Operating Experience
CN-901 | [6 empty] | CEFR | [26 empty] | CHINA
Status at end of year | [5 empty] | : | Operational
Operator | [5 empty] | : | CIAE (CHINA INSTITUTE OF ATOMIC ENERGY)
Owner | [5 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Reactor Supplier | [5 empty] | : | IZ (Izhorskiye Zavody)
Turbine Supplier | [5 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [25 empty] | Key Dates
Reactor type and model | [10 empty] | : |  |  | FBR / BN-20 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2000-05-10
Thermal power | [10 empty] | : |  |  | 65 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2011-07-21
Gross electrical power | [10 empty] | : |  |  | 25 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | :
Reference unit power (net) | [10 empty] | : |  |  | 20 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [26 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [11 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [11 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [11 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [11 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [11 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [11 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [11 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [11 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [11 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [11 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [11 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [11 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [11 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [11 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [11 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [16 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [16 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [16 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [16 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [16 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | hours
Annual Summary
|  |  | Jan | Oct |  |  |  | Nov |  | Dec | [8 empty] | Feb |  |  | Mar | [6 empty] | Apr |  | May |  |  |  | Jun |  |  | Jul |  |  | Aug | [9 empty] | Sep
GW(e)-h
EAF [%]
UCF [%]
LF [%]
OF [%]
FLR [%]
UCL [%]
PUF [%]
XUF [%]
Historical Summary
Lifetime energy generation | [11 empty] | : |  |  | 0 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [11 empty] | : |  |  | 0 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [11 empty] | : |  |  | 0 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0 %
Cumulative Load Factor (LF) | [11 empty] | : |  |  | 0 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [11 empty] | : |  |  | 0 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[21 empty] | 2020 | [14 empty] | 1 to 2020
Outage Cause | [20 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[21 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
Subtotal
Total | [20 empty] | 0 | [14 empty] | 0
Equipment Related Unplanned Full Outages, Analysis by System
System | [20 empty] | 2020 | [14 empty] | 1 to 2020
[21 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
Total

## CHANGJIANG-1
2020 Operating Experience
CN-36 | [8 empty] | CHANGJIANG-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | HNPC (Hainan Nuclear Power Company)
Owner | [7 empty] | : | HNPC (Hainan Nuclear Power Company)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-04-25
Thermal power | [12 empty] | : |  |  | 1930 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-11-07
Gross electrical power | [12 empty] | : |  |  | 650 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-12-25
Reference unit power (net) | [12 empty] | : |  |  | 601 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.35
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.53 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 29.75 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 2.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.09 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4519.05 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.48 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.48 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.52 %
Load Factor (LF) | [18 empty] | : | 85.86 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.31 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 851 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 437.01 | 155.83 |  |  |  | 119.53 |  | 373.72 | [8 empty] | 433.11 |  |  | 421.64 | [6 empty] | 436.81 |  | 437.45 |  |  |  | 423.76 |  |  | 414.04 |  |  | 436.83 | [9 empty] | 429.32 |  |  | 4519.05
EAF [%] |  |  |  |  | 100.00 | 62.07 |  |  |  | 34.52 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.48
UCF [%] |  |  |  |  | 100.00 | 62.07 |  |  |  | 34.52 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.48
LF [%] |  |  |  |  | 99.56 | 37.95 |  |  |  | 26.73 |  | 86.36 | [8 empty] | 96.86 |  |  | 97.44 | [6 empty] | 97.69 |  | 97.83 |  |  |  | 97.93 |  |  | 92.60 |  |  | 100.95 | [9 empty] | 96.01 |  |  | 85.86
OF [%] |  |  |  |  | 100.00 | 42.39 |  |  |  | 39.52 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.31
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 37.93 |  |  |  | 65.48 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.52
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 19847.05 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.27 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.08 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.24 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.08 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.68 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.19 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.98 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 43.73 |  |  | 1006 |  |  |  | 610 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 3617.23 |  |  | 8185 |  |  |  | 601 | [10 empty] | 93.96 |  |  |  | 93.96 | [5 empty] | 68.52 |  |  | 93.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.04 |  |  |  |  | 0.00
2017 |  |  |  | 3405.19 |  |  | 7006 |  |  |  | 601 | [10 empty] | 79.95 |  |  |  | 79.95 | [5 empty] | 64.68 |  |  | 79.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.05 |  |  |  |  | 0.00
2018 |  |  |  | 3909.29 |  |  | 7711 |  |  |  | 601 | [10 empty] | 87.53 |  |  |  | 87.53 | [5 empty] | 74.25 |  |  | 88.03 |  |  |  | 1.36 |  | 1.21 | [8 empty] | 11.26 |  |  |  |  | 0.00
2019 |  |  |  | 4352.30 |  |  | 7741 |  |  |  | 601 | [10 empty] | 87.46 |  |  |  | 87.46 | [5 empty] | 82.67 |  |  | 88.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.54 |  |  |  |  | 0.00
2020 |  |  |  | 4519.05 |  |  | 7933 |  |  |  | 601 | [10 empty] | 91.48 |  |  |  | 91.48 | [5 empty] | 85.86 |  |  | 90.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.52 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2015 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 6
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 714 | [14 empty] | 851
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 123
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 137 | [19 empty] | 74
Subtotal | [22 empty] | 714 | [10 empty] | 137 |  |  |  | 974 |  |  |  | 6 | [11 empty] | 74
Total | [22 empty] | 851 | [14 empty] | 1054
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2015 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [19 empty] | 137 | [14 empty] | 27
Total | [22 empty] | 137 | [14 empty] | 33

## CHANGJIANG-2
2020 Operating Experience
CN-37 | [8 empty] | CHANGJIANG-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | HNPC (Hainan Nuclear Power Company)
Owner | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-11-21
Thermal power | [12 empty] | : |  |  | 1930 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-06-20
Gross electrical power | [12 empty] | : |  |  | 650 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-08-12
Reference unit power (net) | [12 empty] | : |  |  | 601 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.35
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.53 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 29.75 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 2.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.09 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4328.28 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.11 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.11 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.89 %
Load Factor (LF) | [18 empty] | : | 81.99 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 87.53 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1095 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 223.60 |  |  |  | 402.52 |  | 339.19 | [8 empty] | 379.44 |  |  | 411.14 | [6 empty] | 432.85 |  | 435.01 |  |  |  | 422.64 |  |  | 417.29 |  |  | 434.63 | [9 empty] | 429.97 |  |  | 4328.28
EAF [%] |  |  |  |  | 16.13 | 90.06 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.11
UCF [%] |  |  |  |  | 16.13 | 90.06 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.11
LF [%] |  |  |  |  | 0.00 | 53.45 |  |  |  | 90.02 |  | 78.39 | [8 empty] | 84.86 |  |  | 95.01 | [6 empty] | 96.80 |  | 97.29 |  |  |  | 97.67 |  |  | 93.32 |  |  | 100.44 | [9 empty] | 96.16 |  |  | 81.99
OF [%] |  |  |  |  | 0.00 | 61.21 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 89.11 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.53
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 83.87 | 9.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.89
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 17457.13 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.67 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.53 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.83 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.53 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.64 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.04 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.12 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 1831.25 |  |  | 4180 |  |  |  | 601 | [10 empty] | 95.30 |  |  |  | 95.30 | [5 empty] | 72.98 |  |  | 95.89 |  |  |  | 3.07 |  | 3.02 | [8 empty] | 1.68 |  |  |  |  | 0.00
2017 |  |  |  | 3417.22 |  |  | 7524 |  |  |  | 601 | [10 empty] | 88.44 |  |  |  | 88.44 | [5 empty] | 64.91 |  |  | 85.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.56 |  |  |  |  | 0.00
2018 |  |  |  | 3239.86 |  |  | 6531 |  |  |  | 601 | [10 empty] | 74.48 |  |  |  | 74.48 | [5 empty] | 61.54 |  |  | 74.55 |  |  |  | 1.82 |  | 2.40 | [8 empty] | 23.12 |  |  |  |  | 0.00
2019 |  |  |  | 4641.87 |  |  | 8483 |  |  |  | 601 | [10 empty] | 96.23 |  |  |  | 96.23 | [5 empty] | 88.17 |  |  | 96.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.77 |  |  |  |  | 0.00
2020 |  |  |  | 4328.28 |  |  | 7689 |  |  |  | 601 | [10 empty] | 92.11 |  |  |  | 92.11 | [5 empty] | 81.99 |  |  | 87.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.89 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 67
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 624 | [14 empty] | 889
E. |  | Testing of plant systems or components | [35 empty] | 73
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 471 | [19 empty] | 179
Subtotal | [22 empty] | 624 | [10 empty] | 471 |  |  |  | 962 |  |  |  | 67 | [11 empty] | 179
Total | [22 empty] | 1095 | [14 empty] | 1208
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2016 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 20
16. |  |  | Steam generation systems | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [19 empty] | 81 | [14 empty] | 18
33. |  |  | Circulating Water System | [34 empty] | 31
34. |  |  | Miscellaneous Systems | [19 empty] | 390 | [14 empty] | 85
Total | [22 empty] | 471 | [14 empty] | 169

## DAYA BAY-1
2020 Operating Experience
CN-2 | [8 empty] | DAYA BAY-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | GNPJVC (GUANDONG NUCLEAR POWER JOINT VENTURE COMPANY LIMITED)
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M310 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1987-08-07
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-08-31
Gross electrical power | [12 empty] | : |  |  | 984 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-02-01
Reference unit power (net) | [12 empty] | : |  |  | 944 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 46 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 26
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8398.23 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.99 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.99 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 101.28 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 706.99 | 670.50 |  |  |  | 716.76 |  | 693.70 | [8 empty] | 712.59 |  |  | 686.44 | [6 empty] | 709.76 |  | 707.16 |  |  |  | 684.06 |  |  | 709.53 |  |  | 684.82 | [9 empty] | 715.90 |  |  | 8398.23
EAF [%] |  |  |  |  | 99.98 | 100.00 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 99.97 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.91 |  |  | 99.99
UCF [%] |  |  |  |  | 99.98 | 100.00 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 99.97 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.91 |  |  | 99.99
LF [%] |  |  |  |  | 100.66 | 102.05 |  |  |  | 102.05 |  | 102.06 | [8 empty] | 101.46 |  |  | 100.99 | [6 empty] | 101.06 |  | 100.69 |  |  |  | 100.65 |  |  | 101.02 |  |  | 100.76 | [9 empty] | 101.93 |  |  | 101.28
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.03 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.09 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 192462.14 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.28 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.31 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.82 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.73 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.42 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 5917.39 |  |  | 6539 |  |  |  | 944 | [10 empty] | 76.26 |  |  |  | 77.44 | [5 empty] | 76.76 |  |  | 79.65 |  |  |  | 18.87 |  | 18.01 | [8 empty] | 4.55 |  |  |  |  | 1.18
1995 |  |  |  | 3723.63 |  |  | 4088 |  |  |  | 944 | [10 empty] | 46.21 |  |  |  | 84.61 | [5 empty] | 45.03 |  |  | 46.67 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 15.00 |  |  |  |  | 38.40
1996 |  |  |  | 6252.67 |  |  | 6847 |  |  |  | 944 | [10 empty] | 76.01 |  |  |  | 76.77 | [5 empty] | 75.41 |  |  | 77.95 |  |  |  | 5.09 |  | 4.12 | [8 empty] | 19.11 |  |  |  |  | 0.75
1997 |  |  |  | 6491.23 |  |  | 7272 |  |  |  | 944 | [10 empty] | 74.61 |  |  |  | 82.05 | [5 empty] | 78.50 |  |  | 83.01 |  |  |  | 0.26 |  | 0.21 | [8 empty] | 17.74 |  |  |  |  | 7.44
1998 |  |  |  | 6040.47 |  |  | 7344 |  |  |  | 944 | [10 empty] | 71.99 |  |  |  | 79.64 | [5 empty] | 73.05 |  |  | 83.84 |  |  |  | 5.64 |  | 4.76 | [8 empty] | 15.60 |  |  |  |  | 7.65
1999 |  |  |  | 6723.65 |  |  | 7680 |  |  |  | 944 | [10 empty] | 82.71 |  |  |  | 87.65 | [5 empty] | 81.30 |  |  | 87.66 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 12.33 |  |  |  |  | 4.94
2000 |  |  |  | 6986.58 |  |  | 7641 |  |  |  | 944 | [10 empty] | 85.18 |  |  |  | 85.44 | [5 empty] | 84.26 |  |  | 86.99 |  |  |  | 2.85 |  | 2.50 | [8 empty] | 12.06 |  |  |  |  | 0.26
2001 |  |  |  | 7009.34 |  |  | 7619 |  |  |  | 944 | [10 empty] | 84.81 |  |  |  | 87.49 | [5 empty] | 84.76 |  |  | 86.97 |  |  |  | 0.36 |  | 0.32 | [8 empty] | 12.19 |  |  |  |  | 2.68
2002 |  |  |  | 7387.25 |  |  | 7924 |  |  |  | 944 | [10 empty] | 89.52 |  |  |  | 89.62 | [5 empty] | 89.33 |  |  | 90.46 |  |  |  | 0.27 |  | 0.24 | [8 empty] | 10.13 |  |  |  |  | 0.10
2003 |  |  |  | 7400.76 |  |  | 7958 |  |  |  | 944 | [10 empty] | 90.42 |  |  |  | 90.95 | [5 empty] | 89.50 |  |  | 90.84 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 8.99 |  |  |  |  | 0.53
2004 |  |  |  | 7540.90 |  |  | 7789 |  |  |  | 944 | [10 empty] | 88.21 |  |  |  | 88.45 | [5 empty] | 90.94 |  |  | 88.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.55 |  |  |  |  | 0.24
2005 |  |  |  | 8260.49 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 99.89 |  |  | 100.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.01 |  |  |  |  | 0.00
2006 |  |  |  | 6635.15 |  |  | 7133 |  |  |  | 944 | [10 empty] | 79.86 |  |  |  | 79.86 | [5 empty] | 80.24 |  |  | 81.43 |  |  |  | 1.10 |  | 0.89 | [8 empty] | 19.26 |  |  |  |  | 0.00
2007 |  |  |  | 7542.13 |  |  | 8074 |  |  |  | 944 | [10 empty] | 91.20 |  |  |  | 91.20 | [5 empty] | 91.20 |  |  | 92.17 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 8.59 |  |  |  |  | 0.00
2008 |  |  |  | 8255.49 |  |  | 8774 |  |  |  | 944 | [10 empty] | 99.84 |  |  |  | 99.97 | [5 empty] | 99.56 |  |  | 99.89 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.02 |  |  |  |  | 0.13
2009 |  |  |  | 7439.13 |  |  | 8055 |  |  |  | 944 | [10 empty] | 90.81 |  |  |  | 90.86 | [5 empty] | 89.96 |  |  | 91.95 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 9.12 |  |  |  |  | 0.05
2010 |  |  |  | 7328.51 |  |  | 7876 |  |  |  | 944 | [10 empty] | 88.95 |  |  |  | 88.95 | [5 empty] | 88.62 |  |  | 89.91 |  |  |  | 0.00 |  | 1.61 | [8 empty] | 9.44 |  |  |  |  | 0.00
2011 |  |  |  | 8222.61 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 99.43 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
2012 |  |  |  | 6952.17 |  |  | 7452 |  |  |  | 944 | [10 empty] | 83.56 |  |  |  | 83.90 | [5 empty] | 83.84 |  |  | 84.84 |  |  |  | 0.14 |  | 1.36 | [8 empty] | 14.74 |  |  |  |  | 0.35
2013 |  |  |  | 7150.01 |  |  | 7682 |  |  |  | 944 | [10 empty] | 86.41 |  |  |  | 86.68 | [5 empty] | 86.46 |  |  | 87.69 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 13.31 |  |  |  |  | 0.26
2014 |  |  |  | 8247.51 |  |  | 8735 |  |  |  | 944 | [10 empty] | 99.33 |  |  |  | 99.53 | [5 empty] | 99.73 |  |  | 99.71 |  |  |  | 0.31 |  | 0.31 | [8 empty] | 0.15 |  |  |  |  | 0.20
2015 |  |  |  | 6581.67 |  |  | 6954 |  |  |  | 944 | [10 empty] | 78.84 |  |  |  | 78.84 | [5 empty] | 79.59 |  |  | 79.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.16 |  |  |  |  | 0.00
2016 |  |  |  | 7235.87 |  |  | 7671 |  |  |  | 944 | [10 empty] | 86.58 |  |  |  | 86.58 | [5 empty] | 87.26 |  |  | 87.33 |  |  |  | 0.04 |  | 1.24 | [8 empty] | 12.18 |  |  |  |  | 0.00
2017 |  |  |  | 8343.32 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 100.89 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2018 |  |  |  | 7444.51 |  |  | 7871 |  |  |  | 944 | [10 empty] | 89.18 |  |  |  | 89.25 | [5 empty] | 90.02 |  |  | 89.85 |  |  |  | 0.42 |  | 0.38 | [8 empty] | 10.37 |  |  |  |  | 0.07
2019 |  |  |  | 7771.68 |  |  | 8186 |  |  |  | 944 | [10 empty] | 92.94 |  |  |  | 92.94 | [5 empty] | 93.98 |  |  | 93.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.06 |  |  |  |  | 0.00
2020 |  |  |  | 8398.23 |  |  | 8784 |  |  |  | 944 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 101.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1994 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 93
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 810
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 11
E. |  | Testing of plant systems or components | [39 empty] | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 11
Z. |  | Other | [51 empty] | 114
Subtotal | [37 empty] | 821 |  |  |  | 93 | [11 empty] | 125
Total | [22 empty] | 0 | [14 empty] | 1039
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1994 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 12
33. |  |  | Circulating Water System | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 36
42. |  |  | Electrical Power Supply Systems | [34 empty] | 21
Total | [37 empty] | 94

## DAYA BAY-2
2020 Operating Experience
CN-3 | [8 empty] | DAYA BAY-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | GNPJVC (GUANDONG NUCLEAR POWER JOINT VENTURE COMPANY LIMITED)
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M310 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1988-04-07
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1994-02-07
Gross electrical power | [12 empty] | : |  |  | 984 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-05-06
Reference unit power (net) | [12 empty] | : |  |  | 944 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 26 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 46 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 26
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7475.32 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.13 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.21 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.12 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.21 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.67 %
Load Factor (LF) | [18 empty] | : | 90.15 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 89.81 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 895 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 707.31 | 670.39 |  |  |  | 716.69 |  | 692.62 | [8 empty] | 709.66 |  |  | 684.53 | [6 empty] | 707.36 |  | 702.76 |  |  |  | 680.93 |  |  | 226.50 |  |  | 261.21 | [9 empty] | 715.38 |  |  | 7475.32
EAF [%] |  |  |  |  | 100.00 | 99.97 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.98 | [6 empty] | 100.00 |  | 99.91 |  |  |  | 100.00 |  |  | 32.36 |  |  | 38.40 | [9 empty] | 99.98 |  |  | 89.21
UCF [%] |  |  |  |  | 100.00 | 99.97 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.98 | [6 empty] | 100.00 |  | 99.91 |  |  |  | 100.00 |  |  | 32.36 |  |  | 38.40 | [9 empty] | 99.98 |  |  | 89.21
LF [%] |  |  |  |  | 100.71 | 102.03 |  |  |  | 102.04 |  | 101.90 | [8 empty] | 101.04 |  |  | 100.71 | [6 empty] | 100.71 |  | 100.06 |  |  |  | 100.18 |  |  | 32.25 |  |  | 38.43 | [9 empty] | 101.86 |  |  | 90.15
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 32.66 |  |  | 45.28 | [9 empty] | 100.00 |  |  | 89.81
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 3.66 | [9 empty] | 0.00 |  |  | 0.13
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 1.46 | [9 empty] | 0.00 |  |  | 0.12
PUF [%] |  |  |  |  | 0.00 | 0.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.09 |  |  |  | 0.00 |  |  | 67.64 |  |  | 60.14 | [9 empty] | 0.02 |  |  | 10.67
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 189748.09 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.57 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.21 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.56 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.13 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.63 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 5741.21 |  |  | 6889 |  |  |  | 944 | [10 empty] | 92.32 |  |  |  | 99.39 | [5 empty] | 90.33 |  |  | 97.98 |  |  |  | 0.60 |  | 0.60 | [8 empty] | 0.01 |  |  |  |  | 7.07
1995 |  |  |  | 6343.33 |  |  | 7146 |  |  |  | 944 | [10 empty] | 77.48 |  |  |  | 81.09 | [5 empty] | 76.71 |  |  | 81.58 |  |  |  | 1.35 |  | 1.11 | [8 empty] | 17.80 |  |  |  |  | 3.60
1996 |  |  |  | 5276.90 |  |  | 5740 |  |  |  | 944 | [10 empty] | 63.92 |  |  |  | 67.43 | [5 empty] | 63.64 |  |  | 65.35 |  |  |  | 13.49 |  | 10.51 | [8 empty] | 22.05 |  |  |  |  | 3.51
1997 |  |  |  | 5914.84 |  |  | 6194 |  |  |  | 944 | [10 empty] | 67.41 |  |  |  | 70.10 | [5 empty] | 71.53 |  |  | 70.71 |  |  |  | 2.15 |  | 1.54 | [8 empty] | 28.37 |  |  |  |  | 2.69
1998 |  |  |  | 6259.05 |  |  | 7302 |  |  |  | 944 | [10 empty] | 74.71 |  |  |  | 82.90 | [5 empty] | 75.69 |  |  | 83.36 |  |  |  | 2.15 |  | 1.82 | [8 empty] | 15.27 |  |  |  |  | 8.19
1999 |  |  |  | 6789.46 |  |  | 7594 |  |  |  | 944 | [10 empty] | 83.32 |  |  |  | 86.18 | [5 empty] | 82.10 |  |  | 86.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.82 |  |  |  |  | 2.87
2000 |  |  |  | 6995.52 |  |  | 7840 |  |  |  | 944 | [10 empty] | 88.39 |  |  |  | 89.13 | [5 empty] | 84.36 |  |  | 89.25 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 10.83 |  |  |  |  | 0.73
2001 |  |  |  | 7355.47 |  |  | 7986 |  |  |  | 944 | [10 empty] | 89.46 |  |  |  | 91.12 | [5 empty] | 88.95 |  |  | 91.16 |  |  |  | 0.19 |  | 0.18 | [8 empty] | 8.70 |  |  |  |  | 1.66
2002 |  |  |  | 6728.92 |  |  | 7224 |  |  |  | 944 | [10 empty] | 81.62 |  |  |  | 82.22 | [5 empty] | 81.37 |  |  | 82.47 |  |  |  | 15.12 |  | 14.64 | [8 empty] | 3.14 |  |  |  |  | 0.60
2003 |  |  |  | 6983.05 |  |  | 7503 |  |  |  | 944 | [10 empty] | 84.53 |  |  |  | 84.62 | [5 empty] | 84.44 |  |  | 85.65 |  |  |  | 0.53 |  | 1.17 | [8 empty] | 14.21 |  |  |  |  | 0.09
2004 |  |  |  | 6358.88 |  |  | 6580 |  |  |  | 944 | [10 empty] | 74.23 |  |  |  | 74.39 | [5 empty] | 76.69 |  |  | 74.91 |  |  |  | 0.10 |  | 16.74 | [8 empty] | 8.87 |  |  |  |  | 0.17
2005 |  |  |  | 6586.98 |  |  | 7075 |  |  |  | 944 | [10 empty] | 79.62 |  |  |  | 79.62 | [5 empty] | 79.65 |  |  | 80.76 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 20.36 |  |  |  |  | 0.00
2006 |  |  |  | 8222.79 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.89 |  |  |  | 99.89 | [5 empty] | 99.44 |  |  | 100.00 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.07 |  |  |  |  | 0.00
2007 |  |  |  | 7344.17 |  |  | 7858 |  |  |  | 944 | [10 empty] | 88.81 |  |  |  | 88.81 | [5 empty] | 88.81 |  |  | 89.70 |  |  |  | 0.90 |  | 2.27 | [8 empty] | 8.92 |  |  |  |  | 0.00
2008 |  |  |  | 7174.36 |  |  | 7667 |  |  |  | 944 | [10 empty] | 86.25 |  |  |  | 86.25 | [5 empty] | 86.52 |  |  | 87.28 |  |  |  | 5.20 |  | 4.73 | [8 empty] | 9.02 |  |  |  |  | 0.00
2009 |  |  |  | 8222.61 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.98 |  |  |  | 99.99 | [5 empty] | 99.43 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.01
2010 |  |  |  | 7685.64 |  |  | 8197 |  |  |  | 944 | [10 empty] | 92.50 |  |  |  | 92.50 | [5 empty] | 92.94 |  |  | 93.57 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 7.49 |  |  |  |  | 0.00
2011 |  |  |  | 7113.12 |  |  | 7649 |  |  |  | 944 | [10 empty] | 86.23 |  |  |  | 86.34 | [5 empty] | 86.02 |  |  | 87.32 |  |  |  | 0.00 |  | 2.65 | [8 empty] | 11.00 |  |  |  |  | 0.11
2012 |  |  |  | 8304.98 |  |  | 8784 |  |  |  | 944 | [10 empty] | 99.66 |  |  |  | 99.97 | [5 empty] | 100.16 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.31
2013 |  |  |  | 7091.41 |  |  | 7605 |  |  |  | 944 | [10 empty] | 85.58 |  |  |  | 85.81 | [5 empty] | 85.75 |  |  | 86.82 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 14.17 |  |  |  |  | 0.23
2014 |  |  |  | 6249.97 |  |  | 6629 |  |  |  | 944 | [10 empty] | 75.23 |  |  |  | 75.57 | [5 empty] | 75.58 |  |  | 75.67 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 24.41 |  |  |  |  | 0.34
2015 |  |  |  | 8193.18 |  |  | 8700 |  |  |  | 944 | [10 empty] | 98.65 |  |  |  | 98.65 | [5 empty] | 99.08 |  |  | 99.32 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 1.34 |  |  |  |  | 0.01
2016 |  |  |  | 7290.17 |  |  | 7750 |  |  |  | 944 | [10 empty] | 87.39 |  |  |  | 87.39 | [5 empty] | 87.92 |  |  | 88.23 |  |  |  | 0.30 |  | 0.30 | [8 empty] | 12.32 |  |  |  |  | 0.00
2017 |  |  |  | 7376.85 |  |  | 7819 |  |  |  | 944 | [10 empty] | 88.63 |  |  |  | 88.74 | [5 empty] | 89.21 |  |  | 89.26 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 11.25 |  |  |  |  | 0.11
2018 |  |  |  | 8306.97 |  |  | 8739 |  |  |  | 944 | [10 empty] | 99.65 |  |  |  | 99.72 | [5 empty] | 100.45 |  |  | 99.76 |  |  |  | 0.27 |  | 0.27 | [8 empty] | 0.01 |  |  |  |  | 0.06
2019 |  |  |  | 7704.07 |  |  | 8143 |  |  |  | 944 | [10 empty] | 92.35 |  |  |  | 92.35 | [5 empty] | 93.16 |  |  | 92.96 |  |  |  | 0.04 |  | 0.24 | [8 empty] | 7.40 |  |  |  |  | 0.00
2020 |  |  |  | 7475.32 |  |  | 7889 |  |  |  | 944 | [10 empty] | 89.21 |  |  |  | 89.21 | [5 empty] | 90.15 |  |  | 89.81 |  |  |  | 0.13 |  | 0.12 | [8 empty] | 10.67 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1994 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 104
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 895 | [14 empty] | 852 |  |  |  | 8
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 10
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 12
L. |  | Human factor related | [39 empty] | 16
Subtotal | [22 empty] | 895 | [14 empty] | 862 |  |  |  | 128 | [11 empty] | 12
Total | [22 empty] | 895 | [14 empty] | 1002
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1994 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 40
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 48
42. |  |  | Electrical Power Supply Systems | [34 empty] | 17
Total | [37 empty] | 117

## FANGCHENGGANG-1
2020 Operating Experience
CN-38 | [8 empty] | FANGCHENGGANG-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | GFNPC (Guangxi Fangchenggang Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | GFNPC (Guangxi Fangchenggang Nuclear Power Company, Ltd.)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-07-30
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-10-25
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-01-01
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7919.2 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.72 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.43 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.66 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.43 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.91 %
Load Factor (LF) | [18 empty] | : | 90.15 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.67 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 644 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 738.50 | 626.69 |  |  |  | 555.43 |  | 223.51 | [8 empty] | 724.07 |  |  | 667.16 | [6 empty] | 742.45 |  | 745.23 |  |  |  | 662.33 |  |  | 732.12 |  |  | 736.03 | [9 empty] | 765.68 |  |  | 7919.20
EAF [%] |  |  |  |  | 99.87 | 99.99 |  |  |  | 73.94 |  | 30.68 | [8 empty] | 96.89 |  |  | 95.09 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.98 |  |  | 99.98 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.43
UCF [%] |  |  |  |  | 99.87 | 99.99 |  |  |  | 73.94 |  | 30.68 | [8 empty] | 96.89 |  |  | 95.09 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.98 |  |  | 99.98 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.43
LF [%] |  |  |  |  | 99.26 | 90.04 |  |  |  | 74.65 |  | 31.04 | [8 empty] | 97.32 |  |  | 92.66 | [6 empty] | 99.79 |  | 100.17 |  |  |  | 91.99 |  |  | 98.40 |  |  | 102.23 | [9 empty] | 102.91 |  |  | 90.15
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 74.60 |  | 36.81 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.67
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.10 |  |  | 4.87 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.72
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.10 |  |  | 4.86 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.66
PUF [%] |  |  |  |  | 0.13 | 0.01 |  |  |  | 26.06 |  | 69.32 | [8 empty] | 0.00 |  |  | 0.05 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.91
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 36901.2 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.23 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.54 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.39 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.61 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.65 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.07 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.78 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 7141.83 |  |  | 7761 |  |  |  | 1000 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 81.30 |  |  | 88.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.01
2017 |  |  |  | 5212.98 |  |  | 5794 |  |  |  | 1000 | [10 empty] | 76.66 |  |  |  | 76.82 | [5 empty] | 59.51 |  |  | 66.14 |  |  |  | 0.00 |  | 0.91 | [8 empty] | 22.27 |  |  |  |  | 0.16
2018 |  |  |  | 7425.87 |  |  | 7622 |  |  |  | 1000 | [10 empty] | 90.01 |  |  |  | 90.19 | [5 empty] | 84.77 |  |  | 87.01 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.80 |  |  |  |  | 0.18
2019 |  |  |  | 8540.31 |  |  | 8736 |  |  |  | 1000 | [10 empty] | 99.62 |  |  |  | 99.62 | [5 empty] | 97.49 |  |  | 99.73 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.02 |  |  |  |  | 0.00
2020 |  |  |  | 7919.20 |  |  | 8140 |  |  |  | 1000 | [10 empty] | 91.43 |  |  |  | 91.43 | [5 empty] | 90.15 |  |  | 92.67 |  |  |  | 0.72 |  | 0.66 | [8 empty] | 7.91 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 21
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 644 | [14 empty] | 668
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 471
Subtotal | [22 empty] | 644 | [14 empty] | 668 |  |  |  | 21 | [11 empty] | 471
Total | [22 empty] | 644 | [14 empty] | 1160
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2016 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
14. |  |  | Safety Systems | [34 empty] | 16
31. |  |  | Turbine and auxiliaries | [34 empty] | 5
Total | [37 empty] | 21
Highlights (2020)
1.CN38 was basically operated in base-load mode. There was no scram in 2020. 2.According to the requirements of grid, CN38 deloaded for some holidays,weekends and other reasons. 3.CN38 was bearing its third refuelling outage from Mar 24 to Apr 19, lasting 26.54 days.

## FANGCHENGGANG-2
2020 Operating Experience
CN-39 | [8 empty] | FANGCHENGGANG-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | GFNPC (Guangxi Fangchenggang Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | GFNPC (Guangxi Fangchenggang Nuclear Power Company, Ltd.)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-12-23
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-07-15
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-10-01
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7901 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.98 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.02 %
Load Factor (LF) | [18 empty] | : | 89.95 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.06 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 873 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 557.05 | 616.66 |  |  |  | 768.02 |  | 739.64 | [8 empty] | 753.43 |  |  | 709.99 | [6 empty] | 744.65 |  | 747.72 |  |  |  | 639.82 |  |  | 101.73 |  |  | 747.02 | [9 empty] | 775.27 |  |  | 7901.00
EAF [%] |  |  |  |  | 99.98 | 99.99 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 99.95 |  |  | 99.98 | [6 empty] | 100.00 |  | 99.93 |  |  |  | 89.98 |  |  | 15.19 |  |  | 100.00 | [9 empty] | 99.93 |  |  | 91.98
UCF [%] |  |  |  |  | 99.98 | 99.99 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 99.95 |  |  | 99.98 | [6 empty] | 100.00 |  | 99.93 |  |  |  | 89.98 |  |  | 15.19 |  |  | 100.00 | [9 empty] | 99.93 |  |  | 91.98
LF [%] |  |  |  |  | 74.87 | 88.60 |  |  |  | 103.23 |  | 102.73 | [8 empty] | 101.27 |  |  | 98.61 | [6 empty] | 100.09 |  | 100.50 |  |  |  | 88.86 |  |  | 13.67 |  |  | 103.75 | [9 empty] | 104.20 |  |  | 89.95
OF [%] |  |  |  |  | 73.66 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 90.42 |  |  | 18.28 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.06
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.02 | 0.01 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.03 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.07 |  |  |  | 10.02 |  |  | 84.81 |  |  | 0.00 | [9 empty] | 0.07 |  |  | 8.02
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 32258 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.36 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.58 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.02 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.1 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.07 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.2 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 2648.30 |  |  | 3297 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 91.13 |  |  | 88.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6569.07 |  |  | 6827 |  |  |  | 1000 | [10 empty] | 80.27 |  |  |  | 80.38 | [5 empty] | 74.99 |  |  | 77.93 |  |  |  | 1.63 |  | 1.33 | [8 empty] | 18.29 |  |  |  |  | 0.12
2018 |  |  |  | 7655.73 |  |  | 7816 |  |  |  | 1000 | [10 empty] | 99.81 |  |  |  | 99.98 | [5 empty] | 87.39 |  |  | 89.22 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.01 |  |  |  |  | 0.18
2019 |  |  |  | 7579.32 |  |  | 7625 |  |  |  | 1000 | [10 empty] | 92.14 |  |  |  | 92.14 | [5 empty] | 86.52 |  |  | 87.04 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 7.78 |  |  |  |  | 0.00
2020 |  |  |  | 7901.00 |  |  | 7911 |  |  |  | 1000 | [10 empty] | 91.98 |  |  |  | 91.98 | [5 empty] | 89.95 |  |  | 90.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.02 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 28
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 668 | [14 empty] | 669
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 205 | [19 empty] | 513
Subtotal | [22 empty] | 668 | [10 empty] | 205 |  |  |  | 669 |  |  |  | 28 | [11 empty] | 513
Total | [22 empty] | 873 | [14 empty] | 1210
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2016 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 27
34. |  |  | Miscellaneous Systems | [19 empty] | 205 | [14 empty] | 152
Total | [22 empty] | 205 | [14 empty] | 179
Highlights (2020)
1.CN39 was basically operated in base-load mode. There was no scram in 2020. 2.According to the requirements of grid, CN39 deloaded for some holidays,weekends and other reasons. 3.CN39 was bearing its third refuelling outage from Sep 28 to Oct 26, lasting 27.29 days.

## FANGJIASHAN-1
2020 Operating Experience
CN-24 | [8 empty] | FANGJIASHAN-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | QNPC (QINSHAN NUCLEAR POWER COMPANY)
Owner | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-12-26
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-11-04
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2014-12-15
Reference unit power (net) | [12 empty] | : |  |  | 1012 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 6 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7214.92 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.3 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.77 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.23 %
Load Factor (LF) | [18 empty] | : | 81.16 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.46 %
Operating Factor (OF) | [18 empty] | : | 82.17 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1566 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 490.21 | 200.60 |  |  |  | 764.54 |  | 739.49 | [8 empty] | 757.61 |  |  | 727.21 | [6 empty] | 747.81 |  | 735.08 |  |  |  | 717.54 |  |  | 207.69 |  |  | 362.89 | [9 empty] | 764.25 |  |  | 7214.92
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.80 | [6 empty] | 99.32 |  | 97.63 |  |  |  | 98.48 |  |  | 27.58 |  |  | 49.19 | [9 empty] | 100.00 |  |  | 89.30
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.94 |  |  |  | 100.00 |  |  | 28.40 |  |  | 49.19 | [9 empty] | 100.00 |  |  | 89.77
LF [%] |  |  |  |  | 65.11 | 28.48 |  |  |  | 101.54 |  | 101.49 | [8 empty] | 100.62 |  |  | 99.80 | [6 empty] | 99.32 |  | 97.63 |  |  |  | 98.48 |  |  | 27.58 |  |  | 49.80 | [9 empty] | 101.50 |  |  | 81.16
OF [%] |  |  |  |  | 65.32 | 32.61 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 29.17 |  |  | 56.67 | [9 empty] | 100.00 |  |  | 82.17
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.06 |  |  |  | 0.00 |  |  | 71.60 |  |  | 50.81 | [9 empty] | 0.00 |  |  | 10.23
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.20 | [6 empty] | 0.68 |  | 2.31 |  |  |  | 1.52 |  |  | 0.82 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.46
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 46605.12 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.09 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.62 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.08 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.09 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.83 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.33 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.47 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 7180.23 |  |  | 7289 |  |  |  | 1012 | [10 empty] | 84.47 |  |  |  | 84.47 | [5 empty] | 80.99 |  |  | 83.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.53 |  |  |  |  | 0.00
2016 |  |  |  | 7827.38 |  |  | 7910 |  |  |  | 1012 | [10 empty] | 91.68 |  |  |  | 91.68 | [5 empty] | 88.05 |  |  | 90.05 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 8.28 |  |  |  |  | 0.00
2017 |  |  |  | 7628.57 |  |  | 7676 |  |  |  | 1012 | [10 empty] | 88.54 |  |  |  | 89.14 | [5 empty] | 86.05 |  |  | 87.63 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 10.79 |  |  |  |  | 0.60
2018 |  |  |  | 8761.17 |  |  | 8732 |  |  |  | 1012 | [10 empty] | 99.06 |  |  |  | 99.61 | [5 empty] | 98.83 |  |  | 99.68 |  |  |  | 0.39 |  | 0.39 | [8 empty] | 0.00 |  |  |  |  | 0.55
2019 |  |  |  | 7992.84 |  |  | 8048 |  |  |  | 1012 | [10 empty] | 89.85 |  |  |  | 91.12 | [5 empty] | 90.16 |  |  | 91.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.88 |  |  |  |  | 1.28
2020 |  |  |  | 7214.92 |  |  | 7218 |  |  |  | 1012 | [10 empty] | 89.30 |  |  |  | 89.77 | [5 empty] | 81.16 |  |  | 82.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.23 |  |  |  |  | 0.46
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2014 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 839 | [14 empty] | 748
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 727 | [19 empty] | 203
L. |  | Human factor related | [39 empty] | 5
Subtotal | [22 empty] | 839 | [10 empty] | 727 |  |  |  | 748 |  |  |  | 5 | [11 empty] | 203
Total | [22 empty] | 1566 | [14 empty] | 956
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2014 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [19 empty] | 727 | [14 empty] | 121
Total | [22 empty] | 727 | [14 empty] | 121

## FANGJIASHAN-2
2020 Operating Experience
CN-25 | [8 empty] | FANGJIASHAN-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | QNPC (QINSHAN NUCLEAR POWER COMPANY)
Owner | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-07-17
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-01-12
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-02-12
Reference unit power (net) | [12 empty] | : |  |  | 1012 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8418.73 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.04 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.62 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.04 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.93 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.03 %
Load Factor (LF) | [18 empty] | : | 94.71 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.31 %
Operating Factor (OF) | [18 empty] | : | 95.36 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 408 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 719.52 | 540.61 |  |  |  | 757.60 |  | 733.54 | [8 empty] | 747.49 |  |  | 727.62 | [6 empty] | 748.81 |  | 736.13 |  |  |  | 594.61 |  |  | 615.83 |  |  | 734.53 | [9 empty] | 762.45 |  |  | 8418.73
EAF [%] |  |  |  |  | 99.91 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.86 | [6 empty] | 99.45 |  | 97.77 |  |  |  | 99.25 |  |  | 99.54 |  |  | 100.00 | [9 empty] | 99.69 |  |  | 99.62
UCF [%] |  |  |  |  | 99.91 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.89 |  |  |  | 99.77 |  |  | 99.54 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.93
LF [%] |  |  |  |  | 95.56 | 76.75 |  |  |  | 100.62 |  | 100.67 | [8 empty] | 99.28 |  |  | 99.86 | [6 empty] | 99.45 |  | 97.77 |  |  |  | 81.61 |  |  | 81.79 |  |  | 100.81 | [9 empty] | 101.26 |  |  | 94.71
OF [%] |  |  |  |  | 100.00 | 80.46 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 83.33 |  |  | 79.57 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.36
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.46 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.04
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.46 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.04
PUF [%] |  |  |  |  | 0.09 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.11 |  |  |  | 0.23 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.14 | [6 empty] | 0.55 |  | 2.12 |  |  |  | 0.52 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.31 |  |  | 0.31
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 47104.1 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.1 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.27 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.09 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.61 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.3 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.55 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.34 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.32 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 7400.55 |  |  | 7747 |  |  |  | 1012 | [10 empty] | 93.22 |  |  |  | 93.22 | [5 empty] | 89.98 |  |  | 92.90 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 6.76 |  |  |  |  | 0.00
2016 |  |  |  | 7324.84 |  |  | 7529 |  |  |  | 1012 | [10 empty] | 87.29 |  |  |  | 87.29 | [5 empty] | 82.40 |  |  | 85.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.71 |  |  |  |  | 0.00
2017 |  |  |  | 7521.75 |  |  | 7563 |  |  |  | 1012 | [10 empty] | 84.95 |  |  |  | 85.72 | [5 empty] | 84.85 |  |  | 86.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.28 |  |  |  |  | 0.77
2018 |  |  |  | 8472.42 |  |  | 8483 |  |  |  | 1012 | [10 empty] | 97.62 |  |  |  | 98.08 | [5 empty] | 95.57 |  |  | 96.84 |  |  |  | 0.48 |  | 0.47 | [8 empty] | 1.45 |  |  |  |  | 0.46
2019 |  |  |  | 7965.85 |  |  | 7963 |  |  |  | 1012 | [10 empty] | 90.97 |  |  |  | 91.45 | [5 empty] | 89.86 |  |  | 90.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.55 |  |  |  |  | 0.48
2020 |  |  |  | 8418.73 |  |  | 8376 |  |  |  | 1012 | [10 empty] | 99.62 |  |  |  | 99.93 | [5 empty] | 94.71 |  |  | 95.36 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.03 |  |  |  |  | 0.31
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2015 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 3 | [14 empty] | 5
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 615
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 381 | [19 empty] | 132
Subtotal | [26 empty] | 3 | [6 empty] | 381 |  |  |  | 615 |  |  |  | 5 | [11 empty] | 132
Total | [22 empty] | 384 | [14 empty] | 752
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2015 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [19 empty] | 3 | [14 empty] | 1
34. |  |  | Miscellaneous Systems | [19 empty] | 381 | [14 empty] | 63
Total | [22 empty] | 384 | [14 empty] | 68
Highlights (2020)

## FUQING-1
2020 Operating Experience
CN-20 | [8 empty] | FUQING-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-11-21
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-08-20
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2014-11-22
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 6 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8222.85 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.58 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.3 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.7 %
Load Factor (LF) | [18 empty] | : | 93.61 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.72 %
Operating Factor (OF) | [18 empty] | : | 99.11 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 78 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 661.69 | 601.21 |  |  |  | 693.52 |  | 584.85 | [8 empty] | 696.58 |  |  | 705.97 | [6 empty] | 725.52 |  | 725.22 |  |  |  | 704.83 |  |  | 663.59 |  |  | 717.05 | [9 empty] | 742.83 |  |  | 8222.85
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 98.14 |  |  | 99.14 | [6 empty] | 98.53 |  | 98.53 |  |  |  | 98.53 |  |  | 90.30 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.58
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.92 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 91.77 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.30
LF [%] |  |  |  |  | 88.94 | 86.38 |  |  |  | 93.22 |  | 81.23 | [8 empty] | 93.63 |  |  | 98.05 | [6 empty] | 97.52 |  | 97.48 |  |  |  | 97.89 |  |  | 89.19 |  |  | 99.59 | [9 empty] | 99.84 |  |  | 93.61
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 89.17 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.11
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.08 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.08 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 8.23 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.70
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.86 |  |  | 0.78 | [6 empty] | 1.47 |  | 1.47 |  |  |  | 1.47 |  |  | 1.47 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.72
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 43301.49 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.31 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.66 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.65 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.47 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.75 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.21 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.56 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2014 |  |  |  | 1033.07 |  |  | 949 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 109.00 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6032.38 |  |  | 6514 |  |  |  | 1000 | [10 empty] | 74.11 |  |  |  | 74.11 | [5 empty] | 68.86 |  |  | 74.36 |  |  |  | 1.98 |  | 3.77 | [8 empty] | 22.12 |  |  |  |  | 0.00
2016 |  |  |  | 6662.04 |  |  | 7511 |  |  |  | 1000 | [10 empty] | 99.31 |  |  |  | 99.31 | [5 empty] | 75.84 |  |  | 85.51 |  |  |  | 0.20 |  | 0.20 | [8 empty] | 0.50 |  |  |  |  | 0.00
2017 |  |  |  | 7535.41 |  |  | 7930 |  |  |  | 1000 | [10 empty] | 89.81 |  |  |  | 89.81 | [5 empty] | 86.02 |  |  | 90.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.19 |  |  |  |  | 0.00
2018 |  |  |  | 7398.98 |  |  | 7702 |  |  |  | 1000 | [10 empty] | 86.59 |  |  |  | 86.78 | [5 empty] | 84.46 |  |  | 87.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.22 |  |  |  |  | 0.19
2019 |  |  |  | 6417.64 |  |  | 7072 |  |  |  | 1000 | [10 empty] | 88.64 |  |  |  | 89.03 | [5 empty] | 73.26 |  |  | 80.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.97 |  |  |  |  | 0.39
2020 |  |  |  | 8222.85 |  |  | 8706 |  |  |  | 1000 | [10 empty] | 98.58 |  |  |  | 99.30 | [5 empty] | 93.61 |  |  | 99.11 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.70 |  |  |  |  | 0.72
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2014 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 54
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 783
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 78 | [19 empty] | 357
Subtotal | [33 empty] | 78 |  |  |  | 783 |  |  |  | 54 | [11 empty] | 357
Total | [22 empty] | 78 | [14 empty] | 1194
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2014 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 10
34. |  |  | Miscellaneous Systems | [19 empty] | 78 | [14 empty] | 13
42. |  |  | Electrical Power Supply Systems | [34 empty] | 33
Total | [22 empty] | 78 | [14 empty] | 67

## FUQING-2
2020 Operating Experience
CN-21 | [8 empty] | FUQING-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-06-17
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-08-06
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-10-16
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7726.34 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.54 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.02 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.98 %
Load Factor (LF) | [18 empty] | : | 87.96 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.49 %
Operating Factor (OF) | [18 empty] | : | 92.63 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 647 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 680.11 | 600.70 |  |  |  | 639.29 |  | 690.20 | [8 empty] | 361.10 |  |  | 390.70 | [6 empty] | 728.66 |  | 729.05 |  |  |  | 708.13 |  |  | 731.73 |  |  | 720.92 | [9 empty] | 745.73 |  |  | 7726.34
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 48.63 |  |  | 55.10 | [6 empty] | 98.71 |  | 98.71 |  |  |  | 98.71 |  |  | 98.71 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.54
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 48.63 |  |  | 55.79 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.02
LF [%] |  |  |  |  | 91.41 | 86.31 |  |  |  | 85.93 |  | 95.86 | [8 empty] | 48.53 |  |  | 54.26 | [6 empty] | 97.94 |  | 97.99 |  |  |  | 98.35 |  |  | 98.35 |  |  | 100.13 | [9 empty] | 100.23 |  |  | 87.96
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 49.46 |  |  | 62.36 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.63
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 51.37 |  |  | 44.21 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.98
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.69 | [6 empty] | 1.29 |  | 1.29 |  |  |  | 1.29 |  |  | 1.29 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.49
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 38372.34 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.02 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.22 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.24 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.09 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.21 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.02 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 2017.22 |  |  | 3487 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 87.75 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6070.84 |  |  | 6807 |  |  |  | 1000 | [10 empty] | 81.46 |  |  |  | 81.46 | [5 empty] | 69.11 |  |  | 77.49 |  |  |  | 0.34 |  | 0.27 | [8 empty] | 18.26 |  |  |  |  | 0.00
2017 |  |  |  | 7416.83 |  |  | 7659 |  |  |  | 1000 | [10 empty] | 86.58 |  |  |  | 86.58 | [5 empty] | 84.67 |  |  | 87.43 |  |  |  | 3.03 |  | 2.71 | [8 empty] | 10.71 |  |  |  |  | 0.00
2018 |  |  |  | 7255.87 |  |  | 7587 |  |  |  | 1000 | [10 empty] | 84.82 |  |  |  | 84.97 | [5 empty] | 82.83 |  |  | 86.61 |  |  |  | 3.06 |  | 2.68 | [8 empty] | 12.34 |  |  |  |  | 0.16
2019 |  |  |  | 7893.35 |  |  | 8685 |  |  |  | 1000 | [10 empty] | 98.89 |  |  |  | 99.35 | [5 empty] | 90.11 |  |  | 99.14 |  |  |  | 0.65 |  | 0.65 | [8 empty] | 0.00 |  |  |  |  | 0.46
2020 |  |  |  | 7726.34 |  |  | 8137 |  |  |  | 1000 | [10 empty] | 91.54 |  |  |  | 92.02 | [5 empty] | 87.96 |  |  | 92.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.98 |  |  |  |  | 0.49
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2015 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 93
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 647 | [14 empty] | 775
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 99
Subtotal | [22 empty] | 647 | [14 empty] | 775 |  |  |  | 93 | [11 empty] | 99
Total | [22 empty] | 647 | [14 empty] | 967
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2015 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
33. |  |  | Circulating Water System | [34 empty] | 72
41. |  |  | Main Generator Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 11
Total | [37 empty] | 89

## FUQING-3
2020 Operating Experience
CN-42 | [8 empty] | FUQING-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-12-31
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-09-07
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-10-24
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7265.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.22 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.61 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.2 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.24 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.56 %
Load Factor (LF) | [18 empty] | : | 82.71 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.63 %
Operating Factor (OF) | [18 empty] | : | 87.93 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1060 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 288.11 | 172.93 |  |  |  | 674.64 |  | 468.04 | [8 empty] | 678.80 |  |  | 654.63 | [6 empty] | 731.70 |  | 731.70 |  |  |  | 708.10 |  |  | 702.27 |  |  | 720.00 | [9 empty] | 734.49 |  |  | 7265.42
EAF [%] |  |  |  |  | 44.45 | 26.06 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 98.88 |  |  | 97.88 | [6 empty] | 98.35 |  | 98.35 |  |  |  | 98.35 |  |  | 98.35 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.61
UCF [%] |  |  |  |  | 44.45 | 26.06 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 98.88 |  |  | 98.76 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.24
LF [%] |  |  |  |  | 38.73 | 24.85 |  |  |  | 90.68 |  | 65.01 | [8 empty] | 91.24 |  |  | 90.92 | [6 empty] | 98.35 |  | 98.35 |  |  |  | 98.35 |  |  | 94.39 |  |  | 100.00 | [9 empty] | 98.72 |  |  | 82.71
OF [%] |  |  |  |  | 45.30 | 36.06 |  |  |  | 100.00 |  | 71.11 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.93
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.12 |  |  | 1.24 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.22
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.12 |  |  | 1.24 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.20
PUF [%] |  |  |  |  | 55.55 | 73.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.56
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.88 | [6 empty] | 1.65 |  | 1.65 |  |  |  | 1.65 |  |  | 1.65 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.63
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 27943.42 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.05 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.05 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.45 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.51 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.01 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.33 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.53 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 1628.31 |  |  | 1648 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.60 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6110.93 |  |  | 6592 |  |  |  | 1000 | [10 empty] | 82.12 |  |  |  | 82.12 | [5 empty] | 69.76 |  |  | 75.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.88 |  |  |  |  | 0.00
2018 |  |  |  | 7013.40 |  |  | 7357 |  |  |  | 1000 | [10 empty] | 88.67 |  |  |  | 88.88 | [5 empty] | 80.06 |  |  | 83.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.12 |  |  |  |  | 0.21
2019 |  |  |  | 7390.94 |  |  | 8107 |  |  |  | 1000 | [10 empty] | 95.23 |  |  |  | 95.78 | [5 empty] | 84.37 |  |  | 92.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.22 |  |  |  |  | 0.55
2020 |  |  |  | 7265.42 |  |  | 7724 |  |  |  | 1000 | [10 empty] | 88.61 |  |  |  | 89.24 | [5 empty] | 82.71 |  |  | 87.93 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 10.56 |  |  |  |  | 0.63
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 852 | [14 empty] | 862
H. |  | Nuclear regulatory requirements | [51 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 208 | [19 empty] | 404
Subtotal | [22 empty] | 852 | [10 empty] | 208 |  |  |  | 862 | [15 empty] | 406
Total | [22 empty] | 1060 | [14 empty] | 1268
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2016 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [19 empty] | 208 | [14 empty] | 48
Total | [22 empty] | 208 | [14 empty] | 48

## FUQING-4
2020 Operating Experience
CN-43 | [8 empty] | FUQING-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2012-11-17
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2017-07-29
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2017-09-17
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6587.82 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.01 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.47 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.53 %
Load Factor (LF) | [18 empty] | : | 75 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.45 %
Operating Factor (OF) | [18 empty] | : | 79.16 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1831 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 419.92 | 78.99 |  |  |  | 295.24 |  | 677.72 | [8 empty] | 722.20 |  |  | 683.91 | [6 empty] | 726.86 |  | 727.24 |  |  |  | 518.07 |  |  | 268.97 |  |  | 721.41 | [9 empty] | 747.28 |  |  | 6587.82
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.36 | [6 empty] | 98.81 |  | 98.81 |  |  |  | 72.35 |  |  | 35.45 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.01
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 73.55 |  |  | 36.65 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.47
LF [%] |  |  |  |  | 56.44 | 11.35 |  |  |  | 39.68 |  | 94.13 | [8 empty] | 97.07 |  |  | 94.99 | [6 empty] | 97.70 |  | 97.75 |  |  |  | 71.95 |  |  | 36.15 |  |  | 100.20 | [9 empty] | 100.44 |  |  | 75.00
OF [%] |  |  |  |  | 61.29 | 16.38 |  |  |  | 49.06 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 74.31 |  |  | 46.64 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 79.16
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 26.45 |  |  | 63.35 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.53
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.64 | [6 empty] | 1.19 |  | 1.19 |  |  |  | 1.19 |  |  | 1.19 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.45
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 22409.6 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.27 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.05 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.24 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.34 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.43 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.29 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.6 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2017 |  |  |  | 2540.07 |  |  | 2544 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.00 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 6682.09 |  |  | 6890 |  |  |  | 1000 | [10 empty] | 77.79 |  |  |  | 77.91 | [5 empty] | 76.28 |  |  | 78.65 |  |  |  | 0.98 |  | 0.77 | [8 empty] | 21.32 |  |  |  |  | 0.12
2019 |  |  |  | 6599.78 |  |  | 7215 |  |  |  | 1000 | [10 empty] | 91.31 |  |  |  | 91.68 | [5 empty] | 75.34 |  |  | 82.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.32 |  |  |  |  | 0.36
2020 |  |  |  | 6587.82 |  |  | 6953 |  |  |  | 1000 | [10 empty] | 92.01 |  |  |  | 92.47 | [5 empty] | 75.00 |  |  | 79.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.53 |  |  |  |  | 0.45
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2017 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 17
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 606 | [14 empty] | 1029
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 1249 | [19 empty] | 708
Subtotal | [22 empty] | 606 | [10 empty] | 1249 |  |  |  | 1029 |  |  |  | 17 | [11 empty] | 708
Total | [22 empty] | 1855 | [14 empty] | 1754
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2017 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 17
34. |  |  | Miscellaneous Systems | [19 empty] | 1249 | [14 empty] | 416
Total | [22 empty] | 1249 | [14 empty] | 433

## FUQING-5
2020 Operating Experience
CN-51 | [7 empty] | FUQING-5 | [26 empty] | CHINA
Status at end of year | [6 empty] | : | Operational
Operator | [6 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [6 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [6 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [6 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [26 empty] | Key Dates
Reactor type and model | [11 empty] | : |  |  | PWR / HPR1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2015-05-07
Thermal power | [11 empty] | : |  |  | 3060 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-11-27
Gross electrical power | [11 empty] | : |  |  | 1150 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-01-29
Reference unit power (net) | [11 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 0 years
Design Characteristics
| Primary Systems | [27 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [12 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.5
| Fuel material | [12 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [12 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [12 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [12 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [12 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [12 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [12 empty] | : |  |  | 46410 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [12 empty] | : |  |  | 3.228 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.5
| Active core height/length [m] | [12 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [12 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [12 empty] | : |  |  | 17.38 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [12 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [12 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [12 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [17 empty] | : | 91.72 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [17 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [17 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [17 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [17 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 528 hours
Annual Summary
|  |  |  | Jan | Oct |  |  |  | Nov |  | Dec | [8 empty] | Feb |  |  | Mar | [6 empty] | Apr |  | May |  |  |  | Jun |  |  | Jul |  |  | Aug | [9 empty] | Sep
GW(e)-h
EAF [%]
UCF [%]
LF [%]
OF [%]
FLR [%]
UCL [%]
PUF [%]
XUF [%]
Historical Summary
Lifetime energy generation | [12 empty] | : |  |  | 91.72 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [12 empty] | : |  |  | 0 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [12 empty] | : |  |  | 0 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0 %
Cumulative Load Factor (LF) | [12 empty] | : |  |  | 0 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [12 empty] | : |  |  | 0 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[22 empty] | 2020 | [14 empty] | 2021 to 2020
Outage Cause | [21 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[22 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
E. |  | Testing of plant systems or components | [19 empty] | 527
Subtotal | [21 empty] | 527
Total | [21 empty] | 527 | [14 empty] | 0
Equipment Related Unplanned Full Outages, Analysis by System
System | [21 empty] | 2020 | [14 empty] | 2021 to 2020
[22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
Total

## HAIYANG-1
2020 Operating Experience
CN-30 | [8 empty] | HAIYANG-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SDNPC (Shandong Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | CPIC (China Power Investment Corporation)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / AP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-09-24
Thermal power | [12 empty] | : |  |  | 3415 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-08-17
Gross electrical power | [12 empty] | : |  |  | 1250 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-10-22
Reference unit power (net) | [12 empty] | : |  |  | 1170 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.513
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321.11
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.407
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.7239 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.76 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 4.2672 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.76 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 69 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8762.3 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.31 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.68 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.27 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.31 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.42 %
Load Factor (LF) | [18 empty] | : | 85.26 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.63 %
Operating Factor (OF) | [18 empty] | : | 87.67 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1083 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 396.16 | 4.13 |  |  |  | 773.28 |  | 842.35 | [8 empty] | 840.14 |  |  | 814.24 | [6 empty] | 853.22 |  | 847.19 |  |  |  | 825.71 |  |  | 856.86 |  |  | 834.81 | [9 empty] | 874.21 |  |  | 8762.30
EAF [%] |  |  |  |  | 45.07 | 0.51 |  |  |  | 88.80 |  | 100.00 | [8 empty] | 100.00 |  |  | 96.71 | [6 empty] | 98.18 |  | 97.32 |  |  |  | 98.02 |  |  | 99.71 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.68
UCF [%] |  |  |  |  | 45.07 | 0.51 |  |  |  | 88.80 |  | 100.00 | [8 empty] | 100.00 |  |  | 97.52 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.99 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.31
LF [%] |  |  |  |  | 45.51 | 0.51 |  |  |  | 88.83 |  | 99.99 | [8 empty] | 96.51 |  |  | 96.66 | [6 empty] | 98.02 |  | 97.32 |  |  |  | 98.02 |  |  | 98.44 |  |  | 99.10 | [9 empty] | 100.43 |  |  | 85.26
OF [%] |  |  |  |  | 45.43 | 4.02 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 98.75 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.67
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.84 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.48 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.31
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.75 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.48 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.27
PUF [%] |  |  |  |  | 54.93 | 99.49 |  |  |  | 10.45 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.42
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.81 | [6 empty] | 1.82 |  | 2.68 |  |  |  | 1.97 |  |  | 0.29 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.63
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 20965.05 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.21 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.02 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.78 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.72 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.1 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 2746.03 |  |  | 2870 |  |  |  | 1170 | [10 empty] | 94.20 |  |  |  | 94.20 | [5 empty] | 93.91 |  |  | 95.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.80 |  |  |  |  | 0.00
2019 |  |  |  | 9456.75 |  |  | 8221 |  |  |  | 1170 | [10 empty] | 96.46 |  |  |  | 97.39 | [5 empty] | 92.27 |  |  | 93.85 |  |  |  | 0.16 |  | 0.16 | [8 empty] | 2.45 |  |  |  |  | 0.93
2020 |  |  |  | 8762.30 |  |  | 7701 |  |  |  | 1170 | [10 empty] | 85.68 |  |  |  | 86.31 | [5 empty] | 85.26 |  |  | 87.67 |  |  |  | 0.31 |  | 0.27 | [8 empty] | 13.42 |  |  |  |  | 0.63
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2018 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1074 | [14 empty] | 495
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 280
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 153
L. |  | Human factor related | [39 empty] | 3
Subtotal | [22 empty] | 1074 | [14 empty] | 775 |  |  |  | 3 | [11 empty] | 153
Total | [22 empty] | 1074 | [14 empty] | 931
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2018 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
41. |  |  | Main Generator Systems | [34 empty] | 3
Total | [37 empty] | 3
Highlights (2020)
From Jan.14 to Mar.8,HY1 started the First Refueling Outage. During this year, HY1 has external load 11 times and internal load 10 times.There has an unplanned turbine trip at Jun.24 without shutdown. On Mar.3,the unit unplanned reduced power due to deal with the defects of main feedwater pump. On Sept.10,the unit unplanned reduced power to clean the temporary filter which is on the inlet of drain pump from MSR B shell-side. During May to October, the unit reduced power due to the seawater temperature.

## HAIYANG-2
2020 Operating Experience
CN-31 | [8 empty] | HAIYANG-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SDNPC (Shandong Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | CPIC (China Power Investment Corporation)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / AP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-06-20
Thermal power | [12 empty] | : |  |  | 3415 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-10-13
Gross electrical power | [12 empty] | : |  |  | 1250 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2019-01-09
Reference unit power (net) | [12 empty] | : |  |  | 1170 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.513
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321.11
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.407
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.7239 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.76 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 4.2672 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.76 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 69 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9066.38 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.44 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.33 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.4 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.91 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.69 %
Load Factor (LF) | [18 empty] | : | 88.22 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.58 %
Operating Factor (OF) | [18 empty] | : | 90.88 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 801 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 820.60 | 796.49 |  |  |  | 159.94 |  | 522.08 | [8 empty] | 873.28 |  |  | 835.19 | [6 empty] | 824.28 |  | 846.76 |  |  |  | 821.61 |  |  | 857.28 |  |  | 836.60 | [9 empty] | 872.27 |  |  | 9066.38
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 18.29 |  | 66.14 | [8 empty] | 100.00 |  |  | 99.16 | [6 empty] | 94.69 |  | 97.28 |  |  |  | 97.53 |  |  | 99.79 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.33
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 18.29 |  | 66.14 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 96.38 |  | 99.91 |  |  |  | 99.04 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.91
LF [%] |  |  |  |  | 94.27 | 97.81 |  |  |  | 18.37 |  | 61.98 | [8 empty] | 100.32 |  |  | 99.14 | [6 empty] | 94.69 |  | 97.28 |  |  |  | 97.53 |  |  | 98.48 |  |  | 99.31 | [9 empty] | 100.21 |  |  | 88.22
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 18.28 |  | 75.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 98.25 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.88
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.13 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 3.62 |  | 0.09 |  |  |  | 0.96 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.44
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.09 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 3.62 |  | 0.09 |  |  |  | 0.96 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.40
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 81.71 |  | 33.77 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.69
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.84 | [6 empty] | 1.69 |  | 2.63 |  |  |  | 1.51 |  |  | 0.21 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.58
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 19802.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.87 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 93.35 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.82 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 94.16 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 5.01 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 92.57 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.81 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 95.16 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2019 |  |  |  | 9935.22 |  |  | 8711 |  |  |  | 1170 | [10 empty] | 97.38 |  |  |  | 98.43 | [5 empty] | 96.94 |  |  | 99.44 |  |  |  | 1.25 |  | 1.25 | [8 empty] | 0.32 |  |  |  |  | 1.05
2020 |  |  |  | 9066.38 |  |  | 7983 |  |  |  | 1170 | [10 empty] | 89.33 |  |  |  | 89.91 | [5 empty] | 88.22 |  |  | 90.88 |  |  |  | 0.44 |  | 0.40 | [8 empty] | 9.69 |  |  |  |  | 0.58
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2019 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 13 | [14 empty] | 31
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 788 | [14 empty] | 394
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 195
E. |  | Testing of plant systems or components | [35 empty] | 47
L. |  | Human factor related | [39 empty] | 164
Subtotal | [22 empty] | 788 |  |  |  | 13 | [10 empty] | 636 |  |  |  | 195
Total | [22 empty] | 801 | [14 empty] | 831
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2019 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 16
31. |  |  | Turbine and auxiliaries | [34 empty] | 5
32. |  |  | Feedwater and Main Steam System | [19 empty] | 13 | [14 empty] | 151
Total | [22 empty] | 13 | [14 empty] | 172
Highlights (2020)
From May.6 to Apr.15,HY2 started the First Refueling Outage. During this year, HY2 has external load 11 times and internal load 10 times.There has an unplanned shutdown event at May.6. To deal with the defects, the unit unplanned reduced power for 3 times and shutdown 1 time. On Apr.11,the unit reduced power because there is an abnormality by the chlorine ion in sewage discharge of SG. During May to October, the unit reduced power due to the seawater temperature.

## HONGYANHE-1
2020 Operating Experience
CN-16 | [8 empty] | HONGYANHE-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Owner | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-08-18
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2013-02-17
Gross electrical power | [12 empty] | : |  |  | 1119 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2013-06-06
Reference unit power (net) | [12 empty] | : |  |  | 1061 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.11
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7903.95 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.65 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.1 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.9 %
Load Factor (LF) | [18 empty] | : | 84.81 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.44 %
Operating Factor (OF) | [18 empty] | : | 91.45 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 751 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 714.30 | 550.37 |  |  |  | 745.86 |  | 742.64 | [8 empty] | 749.95 |  |  | 745.63 | [6 empty] | 755.01 |  | 741.80 |  |  |  | 688.24 |  |  | 530.52 |  |  | 153.65 | [9 empty] | 785.97 |  |  | 7903.95
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 97.60 | [6 empty] | 95.64 |  | 94.49 |  |  |  | 94.95 |  |  | 69.50 |  |  | 22.93 | [9 empty] | 100.00 |  |  | 89.65
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.98 |  |  |  | 100.00 |  |  | 69.50 |  |  | 22.93 | [9 empty] | 100.00 |  |  | 91.10
LF [%] |  |  |  |  | 90.49 | 74.53 |  |  |  | 94.49 |  | 97.21 | [8 empty] | 95.00 |  |  | 97.61 | [6 empty] | 95.65 |  | 93.97 |  |  |  | 90.09 |  |  | 67.21 |  |  | 20.11 | [9 empty] | 99.57 |  |  | 84.81
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 69.89 |  |  | 26.81 | [9 empty] | 100.00 |  |  | 91.45
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.02 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.02 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 30.50 |  |  | 77.07 | [9 empty] | 0.00 |  |  | 8.90
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.40 | [6 empty] | 4.36 |  | 5.49 |  |  |  | 5.05 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.44
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 57389.57 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.43 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.69 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.32 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.62 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.06 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.06 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.93 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.62 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2013 |  |  |  | 5683.38 |  |  | 7632 |  |  |  | 1061 | [10 empty] | 98.62 |  |  |  | 99.55 | [5 empty] | 102.41 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.44 |  |  |  |  | 0.94
2014 |  |  |  | 6093.20 |  |  | 6218 |  |  |  | 1061 | [10 empty] | 68.38 |  |  |  | 69.32 | [5 empty] | 65.56 |  |  | 70.98 |  |  |  | 9.71 |  | 7.65 | [8 empty] | 23.03 |  |  |  |  | 0.95
2015 |  |  |  | 7369.75 |  |  | 7756 |  |  |  | 1061 | [10 empty] | 87.80 |  |  |  | 87.80 | [5 empty] | 79.29 |  |  | 88.54 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 12.19 |  |  |  |  | 0.00
2016 |  |  |  | 6066.04 |  |  | 6694 |  |  |  | 1061 | [10 empty] | 86.62 |  |  |  | 86.62 | [5 empty] | 65.09 |  |  | 76.21 |  |  |  | 2.14 |  | 1.93 | [8 empty] | 11.45 |  |  |  |  | 0.00
2017 |  |  |  | 7304.12 |  |  | 7720 |  |  |  | 1061 | [10 empty] | 87.92 |  |  |  | 88.92 | [5 empty] | 78.59 |  |  | 88.13 |  |  |  | 0.43 |  | 0.38 | [8 empty] | 10.69 |  |  |  |  | 1.01
2018 |  |  |  | 8797.86 |  |  | 8760 |  |  |  | 1061 | [10 empty] | 98.55 |  |  |  | 99.98 | [5 empty] | 94.66 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 1.43
2019 |  |  |  | 8077.71 |  |  | 7954 |  |  |  | 1061 | [10 empty] | 88.51 |  |  |  | 90.20 | [5 empty] | 86.91 |  |  | 90.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.80 |  |  |  |  | 1.68
2020 |  |  |  | 7903.95 |  |  | 8033 |  |  |  | 1061 | [10 empty] | 89.65 |  |  |  | 91.10 | [5 empty] | 84.81 |  |  | 91.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.90 |  |  |  |  | 1.44
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2013 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 85
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 751 | [14 empty] | 829
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 173
Subtotal | [22 empty] | 751 | [14 empty] | 829 |  |  |  | 85 | [11 empty] | 173
Total | [22 empty] | 751 | [14 empty] | 1087
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2013 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 0
33. |  |  | Circulating Water System | [34 empty] | 16
41. |  |  | Main Generator Systems | [34 empty] | 63
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [37 empty] | 81

## HONGYANHE-2
2020 Operating Experience
CN-17 | [8 empty] | HONGYANHE-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Owner | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-03-28
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2013-11-23
Gross electrical power | [12 empty] | : |  |  | 1119 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2014-05-13
Reference unit power (net) | [12 empty] | : |  |  | 1061 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | NA
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7767.35 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.29 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.7 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.88 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.42 %
Load Factor (LF) | [18 empty] | : | 83.34 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.59 %
Operating Factor (OF) | [18 empty] | : | 91.28 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 766 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 716.38 | 567.75 |  |  |  | 775.36 |  | 505.75 | [8 empty] | 172.35 |  |  | 743.61 | [6 empty] | 757.74 |  | 745.00 |  |  |  | 673.05 |  |  | 715.76 |  |  | 639.15 | [9 empty] | 755.46 |  |  | 7767.35
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 66.96 | [8 empty] | 24.29 |  |  | 97.77 | [6 empty] | 95.98 |  | 94.88 |  |  |  | 95.26 |  |  | 97.13 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.29
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 66.96 | [8 empty] | 24.29 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.88
LF [%] |  |  |  |  | 90.75 | 76.88 |  |  |  | 98.22 |  | 66.20 | [8 empty] | 21.83 |  |  | 97.34 | [6 empty] | 95.99 |  | 94.38 |  |  |  | 88.11 |  |  | 90.67 |  |  | 83.67 | [9 empty] | 95.70 |  |  | 83.34
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 67.36 | [8 empty] | 28.63 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.28
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.23 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.70
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 33.04 | [8 empty] | 67.48 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.42
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.23 | [6 empty] | 4.02 |  | 5.12 |  |  |  | 4.74 |  |  | 2.87 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.59
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 43200.72 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.9 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.64 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.21 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 68.77 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.08 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 75.58 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2014 |  |  |  | 4963.31 |  |  | 5053 |  |  |  | 1061 | [10 empty] | 81.06 |  |  |  | 81.06 | [5 empty] | 72.46 |  |  | 79.81 |  |  |  | 8.62 |  | 7.64 | [8 empty] | 11.29 |  |  |  |  | 0.00
2015 |  |  |  | 3496.01 |  |  | 3925 |  |  |  | 1061 | [10 empty] | 65.63 |  |  |  | 65.63 | [5 empty] | 37.61 |  |  | 44.81 |  |  |  | 0.16 |  | 0.34 | [8 empty] | 34.03 |  |  |  |  | 0.00
2016 |  |  |  | 5288.78 |  |  | 5542 |  |  |  | 1061 | [10 empty] | 87.53 |  |  |  | 87.53 | [5 empty] | 56.75 |  |  | 63.09 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 12.47 |  |  |  |  | 0.00
2017 |  |  |  | 5790.37 |  |  | 6250 |  |  |  | 1061 | [10 empty] | 95.98 |  |  |  | 98.08 | [5 empty] | 62.30 |  |  | 71.35 |  |  |  | 0.00 |  | 1.53 | [8 empty] | 0.40 |  |  |  |  | 2.10
2018 |  |  |  | 7737.78 |  |  | 7723 |  |  |  | 1061 | [10 empty] | 88.18 |  |  |  | 89.80 | [5 empty] | 83.25 |  |  | 88.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.20 |  |  |  |  | 1.63
2019 |  |  |  | 8077.34 |  |  | 8056 |  |  |  | 1061 | [10 empty] | 89.72 |  |  |  | 91.62 | [5 empty] | 86.91 |  |  | 91.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.38 |  |  |  |  | 1.89
2020 |  |  |  | 7767.35 |  |  | 8018 |  |  |  | 1061 | [10 empty] | 89.29 |  |  |  | 90.88 | [5 empty] | 83.34 |  |  | 91.28 |  |  |  | 0.00 |  | 0.70 | [8 empty] | 8.42 |  |  |  |  | 1.59
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2014 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 61 | [14 empty] | 96
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 705 | [14 empty] | 1030
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1001
Subtotal | [22 empty] | 705 |  |  |  | 61 | [10 empty] | 1030 |  |  |  | 96 | [11 empty] | 1001
Total | [22 empty] | 766 | [14 empty] | 2127
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2014 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 61 | [14 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 19
31. |  |  | Turbine and auxiliaries | [34 empty] | 26
33. |  |  | Circulating Water System | [34 empty] | 37
Total | [22 empty] | 61 | [14 empty] | 91

## HONGYANHE-3
2020 Operating Experience
CN-26 | [8 empty] | HONGYANHE-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Owner | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-03-07
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-03-23
Gross electrical power | [12 empty] | : |  |  | 1119 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-08-16
Reference unit power (net) | [12 empty] | : |  |  | 1061 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.11
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6938.56 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.09 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.05 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.09 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.73 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.18 %
Load Factor (LF) | [18 empty] | : | 74.45 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.69 %
Operating Factor (OF) | [18 empty] | : | 81.01 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1668 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 493.49 | 0.00 |  |  |  | 25.31 |  | 697.19 | [8 empty] | 712.08 |  |  | 740.79 | [6 empty] | 747.90 |  | 738.46 |  |  |  | 674.53 |  |  | 719.46 |  |  | 630.39 | [9 empty] | 758.96 |  |  | 6938.56
EAF [%] |  |  |  |  | 97.87 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 97.54 | [6 empty] | 94.75 |  | 94.12 |  |  |  | 95.13 |  |  | 97.30 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.05
UCF [%] |  |  |  |  | 97.87 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.34 |  | 99.65 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.73
LF [%] |  |  |  |  | 62.52 | 0.00 |  |  |  | 3.21 |  | 91.27 | [8 empty] | 90.21 |  |  | 96.97 | [6 empty] | 94.75 |  | 93.55 |  |  |  | 88.30 |  |  | 91.14 |  |  | 82.52 | [9 empty] | 96.15 |  |  | 74.45
OF [%] |  |  |  |  | 64.65 | 0.00 |  |  |  | 4.70 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.01
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.66 |  | 0.35 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.09
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.66 |  | 0.35 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.09
PUF [%] |  |  |  |  | 2.13 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.18
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.46 | [6 empty] | 4.59 |  | 5.53 |  |  |  | 4.87 |  |  | 2.70 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.69
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 34386.39 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.9 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.32 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.22 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.46 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.35 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.32 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.62 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 2322.53 |  |  | 2835 |  |  |  | 1061 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 43.20 |  |  | 47.98 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.01 |  |  |  |  | 0.00
2016 |  |  |  | 5483.99 |  |  | 5764 |  |  |  | 1061 | [10 empty] | 94.69 |  |  |  | 94.69 | [5 empty] | 58.84 |  |  | 65.62 |  |  |  | 0.55 |  | 0.52 | [8 empty] | 4.79 |  |  |  |  | 0.00
2017 |  |  |  | 5631.50 |  |  | 5975 |  |  |  | 1061 | [10 empty] | 80.94 |  |  |  | 82.61 | [5 empty] | 60.59 |  |  | 68.21 |  |  |  | 0.67 |  | 0.56 | [8 empty] | 16.83 |  |  |  |  | 1.67
2018 |  |  |  | 6535.98 |  |  | 6697 |  |  |  | 1061 | [10 empty] | 89.74 |  |  |  | 91.17 | [5 empty] | 70.32 |  |  | 76.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.82 |  |  |  |  | 1.44
2019 |  |  |  | 7491.34 |  |  | 7481 |  |  |  | 1061 | [10 empty] | 82.68 |  |  |  | 84.95 | [5 empty] | 80.60 |  |  | 85.40 |  |  |  | 0.60 |  | 0.51 | [8 empty] | 14.53 |  |  |  |  | 2.27
2020 |  |  |  | 6938.56 |  |  | 7116 |  |  |  | 1061 | [10 empty] | 98.05 |  |  |  | 99.73 | [5 empty] | 74.45 |  |  | 81.01 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 0.18 |  |  |  |  | 1.69
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2015 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 16
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 718
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 1668 | [19 empty] | 1581
Subtotal | [33 empty] | 1668 |  |  |  | 718 |  |  |  | 16 | [11 empty] | 1581
Total | [22 empty] | 1668 | [14 empty] | 2315
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2015 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 1668 | [14 empty] | 286
12. |  |  | Reactor I&C Systems | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 7
Total | [22 empty] | 1668 | [14 empty] | 301

## HONGYANHE-4
2020 Operating Experience
CN-27 | [8 empty] | HONGYANHE-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Owner | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-08-15
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-04-01
Gross electrical power | [12 empty] | : |  |  | 1119 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-06-08
Reference unit power (net) | [12 empty] | : |  |  | 1061 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.657 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | NA
| Active core height/length [m] | [13 empty] | : |  |  | NA | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7755.39 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.37 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.35 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.78 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.87 %
Load Factor (LF) | [18 empty] | : | 83.21 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.5 %
Operating Factor (OF) | [18 empty] | : | 93.16 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 601 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 714.47 | 589.09 |  |  |  | 770.42 |  | 732.87 | [8 empty] | 775.05 |  |  | 297.71 | [6 empty] | 549.43 |  | 743.97 |  |  |  | 465.31 |  |  | 721.00 |  |  | 639.03 | [9 empty] | 757.03 |  |  | 7755.39
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 98.18 |  |  | 38.97 | [6 empty] | 69.61 |  | 94.79 |  |  |  | 95.54 |  |  | 97.83 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.28
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 39.66 | [6 empty] | 73.13 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.78
LF [%] |  |  |  |  | 90.51 | 79.77 |  |  |  | 97.60 |  | 95.94 | [8 empty] | 98.18 |  |  | 38.97 | [6 empty] | 69.60 |  | 94.25 |  |  |  | 60.91 |  |  | 91.34 |  |  | 83.65 | [9 empty] | 95.90 |  |  | 83.21
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 40.00 | [6 empty] | 77.28 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.16
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 5.33 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.37
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 4.12 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.35
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 60.34 | [6 empty] | 22.75 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.87
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.82 |  |  | 0.69 | [6 empty] | 3.52 |  | 5.21 |  |  |  | 4.46 |  |  | 2.17 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.50
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 24985.76 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.17 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.21 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.16 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.37 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.47 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 57.81 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.16 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 63.23 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 1130.44 |  |  | 1200 |  |  |  | 1000 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 22.01 |  |  | 23.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2017 |  |  |  | 3276.06 |  |  | 3638 |  |  |  | 1061 | [10 empty] | 85.13 |  |  |  | 85.76 | [5 empty] | 35.25 |  |  | 41.53 |  |  |  | 0.17 |  | 0.15 | [8 empty] | 14.10 |  |  |  |  | 0.63
2018 |  |  |  | 5198.53 |  |  | 5361 |  |  |  | 1061 | [10 empty] | 84.08 |  |  |  | 85.16 | [5 empty] | 55.93 |  |  | 61.20 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 14.82 |  |  |  |  | 1.08
2019 |  |  |  | 7117.14 |  |  | 7035 |  |  |  | 1061 | [10 empty] | 90.39 |  |  |  | 92.47 | [5 empty] | 76.57 |  |  | 80.31 |  |  |  | 0.21 |  | 0.20 | [8 empty] | 7.33 |  |  |  |  | 2.09
2020 |  |  |  | 7755.39 |  |  | 8183 |  |  |  | 1061 | [10 empty] | 91.28 |  |  |  | 92.78 | [5 empty] | 83.21 |  |  | 93.16 |  |  |  | 0.37 |  | 0.35 | [8 empty] | 6.87 |  |  |  |  | 1.50
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 31 | [14 empty] | 10
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 570 | [14 empty] | 804
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1833
Subtotal | [22 empty] | 570 |  |  |  | 31 | [10 empty] | 804 |  |  |  | 10 | [11 empty] | 1833
Total | [22 empty] | 601 | [14 empty] | 2647
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2016 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
33. |  |  | Circulating Water System | [19 empty] | 31 | [14 empty] | 6
Total | [22 empty] | 31 | [14 empty] | 10

## LING AO-1
2020 Operating Experience
CN-6 | [8 empty] | LING AO-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | LANPC (LINGAO NUCLEAR POWER COMPANY LTD.)
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M310 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1997-05-15
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-02-26
Gross electrical power | [12 empty] | : |  |  | 990 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-05-28
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 18 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 26
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7556.54 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.99 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.99 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 90.55 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 455.80 | 218.86 |  |  |  | 626.41 |  | 687.94 | [8 empty] | 705.09 |  |  | 681.58 | [6 empty] | 704.44 |  | 700.21 |  |  |  | 677.17 |  |  | 703.11 |  |  | 685.27 | [9 empty] | 710.65 |  |  | 7556.54
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.96 |  | 99.98 |  |  |  | 100.00 |  |  | 99.98 |  |  | 100.00 | [9 empty] | 99.96 |  |  | 99.99
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.96 |  | 99.98 |  |  |  | 100.00 |  |  | 99.98 |  |  | 100.00 | [9 empty] | 99.96 |  |  | 99.99
LF [%] |  |  |  |  | 64.49 | 33.10 |  |  |  | 88.63 |  | 100.58 | [8 empty] | 99.76 |  |  | 99.65 | [6 empty] | 99.67 |  | 99.07 |  |  |  | 99.00 |  |  | 99.48 |  |  | 100.19 | [9 empty] | 100.54 |  |  | 90.55
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.02 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.04 |  |  | 0.01
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.02 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.04 |  |  | 0.01
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.04 |  | 0.00 |  |  |  | 0.00 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 136045.33 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.44 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.87 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.99 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.24 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.77 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.22 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.37 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.7 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 4583.85 |  |  | 5184 |  |  |  | 938 | [10 empty] | 95.06 |  |  |  | 95.06 | [5 empty] | 93.54 |  |  | 99.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.94 |  |  |  |  | 0.00
2003 |  |  |  | 6375.05 |  |  | 7215 |  |  |  | 938 | [10 empty] | 80.36 |  |  |  | 82.30 | [5 empty] | 77.58 |  |  | 82.36 |  |  |  | 6.17 |  | 5.41 | [8 empty] | 12.30 |  |  |  |  | 1.93
2004 |  |  |  | 7331.36 |  |  | 7884 |  |  |  | 938 | [10 empty] | 88.69 |  |  |  | 88.95 | [5 empty] | 88.98 |  |  | 89.75 |  |  |  | 0.51 |  | 0.91 | [8 empty] | 10.13 |  |  |  |  | 0.26
2005 |  |  |  | 6906.43 |  |  | 7424 |  |  |  | 938 | [10 empty] | 84.27 |  |  |  | 84.27 | [5 empty] | 84.05 |  |  | 84.75 |  |  |  | 0.46 |  | 0.39 | [8 empty] | 15.34 |  |  |  |  | 0.00
2006 |  |  |  | 7401.01 |  |  | 7964 |  |  |  | 938 | [10 empty] | 90.12 |  |  |  | 90.12 | [5 empty] | 90.07 |  |  | 90.91 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.87 |  |  |  |  | 0.00
2007 |  |  |  | 6835.04 |  |  | 7345 |  |  |  | 938 | [10 empty] | 83.18 |  |  |  | 83.18 | [5 empty] | 83.18 |  |  | 83.85 |  |  |  | 0.00 |  | 6.58 | [8 empty] | 10.24 |  |  |  |  | 0.00
2008 |  |  |  | 7542.85 |  |  | 8163 |  |  |  | 938 | [10 empty] | 91.20 |  |  |  | 92.11 | [5 empty] | 91.55 |  |  | 92.93 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 7.81 |  |  |  |  | 0.91
2009 |  |  |  | 7002.52 |  |  | 7997 |  |  |  | 938 | [10 empty] | 90.35 |  |  |  | 90.39 | [5 empty] | 85.22 |  |  | 91.29 |  |  |  | 0.69 |  | 0.63 | [8 empty] | 8.99 |  |  |  |  | 0.04
2010 |  |  |  | 7714.57 |  |  | 8288 |  |  |  | 938 | [10 empty] | 93.60 |  |  |  | 93.66 | [5 empty] | 93.89 |  |  | 94.61 |  |  |  | 0.18 |  | 0.17 | [8 empty] | 6.18 |  |  |  |  | 0.05
2011 |  |  |  | 7571.37 |  |  | 8072 |  |  |  | 938 | [10 empty] | 91.16 |  |  |  | 91.16 | [5 empty] | 92.14 |  |  | 92.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.84 |  |  |  |  | 0.00
2012 |  |  |  | 7657.29 |  |  | 8286 |  |  |  | 938 | [10 empty] | 93.35 |  |  |  | 93.47 | [5 empty] | 92.94 |  |  | 94.33 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 6.52 |  |  |  |  | 0.12
2013 |  |  |  | 6841.69 |  |  | 7340 |  |  |  | 950 | [10 empty] | 82.46 |  |  |  | 82.80 | [5 empty] | 82.30 |  |  | 83.79 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 17.18 |  |  |  |  | 0.34
2014 |  |  |  | 7361.90 |  |  | 7899 |  |  |  | 950 | [10 empty] | 89.37 |  |  |  | 90.44 | [5 empty] | 88.46 |  |  | 90.17 |  |  |  | 0.03 |  | 2.71 | [8 empty] | 6.86 |  |  |  |  | 1.06
2015 |  |  |  | 7180.10 |  |  | 7656 |  |  |  | 950 | [10 empty] | 86.80 |  |  |  | 86.80 | [5 empty] | 86.28 |  |  | 87.40 |  |  |  | 0.07 |  | 0.34 | [8 empty] | 12.86 |  |  |  |  | 0.00
2016 |  |  |  | 8253.13 |  |  | 8784 |  |  |  | 950 | [10 empty] | 99.66 |  |  |  | 99.98 | [5 empty] | 98.90 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.02 |  |  |  |  | 0.31
2017 |  |  |  | 7020.49 |  |  | 7538 |  |  |  | 950 | [10 empty] | 88.57 |  |  |  | 89.15 | [5 empty] | 84.36 |  |  | 86.05 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 10.84 |  |  |  |  | 0.58
2018 |  |  |  | 6990.81 |  |  | 7667 |  |  |  | 950 | [10 empty] | 86.52 |  |  |  | 87.40 | [5 empty] | 84.00 |  |  | 87.52 |  |  |  | 0.28 |  | 1.27 | [8 empty] | 11.33 |  |  |  |  | 0.88
2019 |  |  |  | 7518.48 |  |  | 8363 |  |  |  | 950 | [10 empty] | 94.72 |  |  |  | 95.04 | [5 empty] | 90.34 |  |  | 95.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.96 |  |  |  |  | 0.33
2020 |  |  |  | 7556.54 |  |  | 8784 |  |  |  | 950 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 90.55 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.01 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2002 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 71
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 732 |  |  |  | 13
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 21
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
Subtotal | [37 empty] | 732 |  |  |  | 84 | [11 empty] | 25
Total | [22 empty] | 0 | [14 empty] | 841
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2002 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 32
16. |  |  | Steam generation systems | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 33
Total | [37 empty] | 72

## LING AO-2
2020 Operating Experience
CN-7 | [8 empty] | LING AO-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | LANPC (LINGAO NUCLEAR POWER COMPANY LTD.)
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M310 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1997-11-28
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-09-14
Gross electrical power | [12 empty] | : |  |  | 990 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2003-01-08
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 18 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 26
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7007.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.17 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.17 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.83 %
Load Factor (LF) | [18 empty] | : | 83.97 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.02 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 877 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 637.02 | 404.68 |  |  |  | 663.03 |  | 673.36 | [8 empty] | 700.41 |  |  | 671.88 | [6 empty] | 704.33 |  | 693.60 |  |  |  | 631.92 |  |  | 0.00 |  |  | 532.16 | [9 empty] | 694.88 |  |  | 7007.26
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 93.42 |  |  | 0.00 |  |  | 77.81 | [9 empty] | 99.99 |  |  | 89.17
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 93.42 |  |  | 0.00 |  |  | 77.81 | [9 empty] | 99.99 |  |  | 89.17
LF [%] |  |  |  |  | 90.13 | 61.20 |  |  |  | 93.81 |  | 98.44 | [8 empty] | 99.10 |  |  | 98.23 | [6 empty] | 99.65 |  | 98.13 |  |  |  | 92.39 |  |  | 0.00 |  |  | 77.80 | [9 empty] | 98.31 |  |  | 83.97
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 93.75 |  |  | 0.00 |  |  | 87.78 | [9 empty] | 100.00 |  |  | 90.02
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 6.58 |  |  | 100.00 |  |  | 22.19 | [9 empty] | 0.01 |  |  | 10.83
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 131709.66 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.45 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.08 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.45 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.33 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.22 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.44 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.25 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.32 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2003 |  |  |  | 6934.88 |  |  | 7494 |  |  |  | 938 | [10 empty] | 89.94 |  |  |  | 90.58 | [5 empty] | 84.40 |  |  | 85.55 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 9.35 |  |  |  |  | 0.64
2004 |  |  |  | 6669.41 |  |  | 7109 |  |  |  | 938 | [10 empty] | 79.80 |  |  |  | 79.85 | [5 empty] | 80.95 |  |  | 80.93 |  |  |  | 2.01 |  | 2.33 | [8 empty] | 17.82 |  |  |  |  | 0.05
2005 |  |  |  | 7530.93 |  |  | 8075 |  |  |  | 938 | [10 empty] | 91.25 |  |  |  | 91.55 | [5 empty] | 91.65 |  |  | 92.18 |  |  |  | 0.70 |  | 0.64 | [8 empty] | 7.81 |  |  |  |  | 0.30
2006 |  |  |  | 7660.99 |  |  | 8164 |  |  |  | 938 | [10 empty] | 92.08 |  |  |  | 92.08 | [5 empty] | 93.23 |  |  | 93.20 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 7.90 |  |  |  |  | 0.00
2007 |  |  |  | 7215.07 |  |  | 7796 |  |  |  | 938 | [10 empty] | 87.81 |  |  |  | 87.81 | [5 empty] | 87.81 |  |  | 89.00 |  |  |  | 3.81 |  | 3.47 | [8 empty] | 8.72 |  |  |  |  | 0.00
2008 |  |  |  | 7077.15 |  |  | 7577 |  |  |  | 938 | [10 empty] | 85.24 |  |  |  | 85.24 | [5 empty] | 85.89 |  |  | 86.26 |  |  |  | 0.20 |  | 0.17 | [8 empty] | 14.59 |  |  |  |  | 0.00
2009 |  |  |  | 7433.81 |  |  | 8052 |  |  |  | 938 | [10 empty] | 90.89 |  |  |  | 90.89 | [5 empty] | 90.47 |  |  | 91.92 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.09 |  |  |  |  | 0.00
2010 |  |  |  | 7505.55 |  |  | 8112 |  |  |  | 938 | [10 empty] | 90.84 |  |  |  | 90.84 | [5 empty] | 91.34 |  |  | 92.60 |  |  |  | 0.58 |  | 0.53 | [8 empty] | 8.63 |  |  |  |  | 0.00
2011 |  |  |  | 7734.34 |  |  | 8284 |  |  |  | 938 | [10 empty] | 93.74 |  |  |  | 93.74 | [5 empty] | 94.13 |  |  | 94.57 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 6.24 |  |  |  |  | 0.00
2012 |  |  |  | 7474.47 |  |  | 8113 |  |  |  | 938 | [10 empty] | 90.95 |  |  |  | 91.09 | [5 empty] | 90.72 |  |  | 92.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.91 |  |  |  |  | 0.15
2013 |  |  |  | 7261.33 |  |  | 7804 |  |  |  | 950 | [10 empty] | 87.91 |  |  |  | 88.62 | [5 empty] | 87.25 |  |  | 89.09 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 11.36 |  |  |  |  | 0.71
2014 |  |  |  | 7773.26 |  |  | 8363 |  |  |  | 950 | [10 empty] | 94.31 |  |  |  | 94.47 | [5 empty] | 93.41 |  |  | 95.47 |  |  |  | 0.21 |  | 0.20 | [8 empty] | 5.33 |  |  |  |  | 0.16
2015 |  |  |  | 7548.19 |  |  | 8114 |  |  |  | 950 | [10 empty] | 93.63 |  |  |  | 93.68 | [5 empty] | 90.70 |  |  | 92.63 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 6.29 |  |  |  |  | 0.05
2016 |  |  |  | 6969.06 |  |  | 7514 |  |  |  | 950 | [10 empty] | 88.13 |  |  |  | 88.66 | [5 empty] | 83.51 |  |  | 85.54 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 11.28 |  |  |  |  | 0.53
2017 |  |  |  | 7720.79 |  |  | 8404 |  |  |  | 950 | [10 empty] | 95.50 |  |  |  | 96.32 | [5 empty] | 92.78 |  |  | 95.94 |  |  |  | 0.48 |  | 0.46 | [8 empty] | 3.21 |  |  |  |  | 0.82
2018 |  |  |  | 7269.80 |  |  | 8108 |  |  |  | 950 | [10 empty] | 91.53 |  |  |  | 92.09 | [5 empty] | 87.36 |  |  | 92.56 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 7.90 |  |  |  |  | 0.57
2019 |  |  |  | 6863.24 |  |  | 7531 |  |  |  | 950 | [10 empty] | 88.63 |  |  |  | 89.17 | [5 empty] | 82.47 |  |  | 85.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.83 |  |  |  |  | 0.54
2020 |  |  |  | 7007.26 |  |  | 7907 |  |  |  | 950 | [10 empty] | 89.17 |  |  |  | 89.17 | [5 empty] | 83.97 |  |  | 90.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.83 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2003 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 23
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 877 | [14 empty] | 734
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 15
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 49
L. |  | Human factor related | [39 empty] | 0
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Subtotal | [22 empty] | 877 | [14 empty] | 749 |  |  |  | 23 | [11 empty] | 51
Total | [22 empty] | 877 | [14 empty] | 823
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2003 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 0
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
33. |  |  | Circulating Water System | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 18
Total | [37 empty] | 26

## LING AO-3
2020 Operating Experience
CN-12 | [8 empty] | LING AO-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | LDNPC (Lingdong Nuclear Power Company Ltd.)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2005-12-15
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2010-07-15
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2010-09-15
Reference unit power (net) | [12 empty] | : |  |  | 1007 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 10 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7539.38 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.56 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.98 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.51 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.51 %
Load Factor (LF) | [18 empty] | : | 85.23 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.93 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 797 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 346.94 | 259.21 |  |  |  | 625.76 |  | 724.10 | [8 empty] | 739.27 |  |  | 662.72 | [6 empty] | 749.86 |  | 723.26 |  |  |  | 652.61 |  |  | 647.32 |  |  | 659.74 | [9 empty] | 748.59 |  |  | 7539.38
EAF [%] |  |  |  |  | 45.33 | 38.48 |  |  |  | 99.99 |  | 99.97 | [8 empty] | 100.00 |  |  | 94.32 | [6 empty] | 99.46 |  | 99.99 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 99.99 |  |  | 89.98
UCF [%] |  |  |  |  | 45.33 | 38.48 |  |  |  | 99.99 |  | 99.97 | [8 empty] | 100.00 |  |  | 94.32 | [6 empty] | 99.46 |  | 99.99 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 99.99 |  |  | 89.98
LF [%] |  |  |  |  | 46.31 | 36.98 |  |  |  | 83.52 |  | 99.87 | [8 empty] | 98.67 |  |  | 91.40 | [6 empty] | 100.09 |  | 96.54 |  |  |  | 90.01 |  |  | 86.40 |  |  | 90.99 | [9 empty] | 99.92 |  |  | 85.23
OF [%] |  |  |  |  | 45.70 | 43.53 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.93
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 5.67 | [6 empty] | 0.54 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.56
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 5.67 | [6 empty] | 0.54 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.51
PUF [%] |  |  |  |  | 54.67 | 61.52 |  |  |  | 0.01 |  | 0.03 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.01 |  | 0.01 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.01 |  |  | 9.51
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 78713.39 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.93 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.1 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.11 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.35 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.47 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.25 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.18 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2010 |  |  |  | 2164.44 |  |  | 2642 |  |  |  | 1007 | [10 empty] | 77.65 |  |  |  | 77.65 | [5 empty] | 62.01 |  |  | 64.34 |  |  |  | 1.39 |  | 1.09 | [8 empty] | 21.26 |  |  |  |  | 0.00
2011 |  |  |  | 6333.19 |  |  | 6866 |  |  |  | 1007 | [10 empty] | 71.31 |  |  |  | 71.31 | [5 empty] | 71.79 |  |  | 78.38 |  |  |  | 7.44 |  | 7.39 | [8 empty] | 21.30 |  |  |  |  | 0.00
2012 |  |  |  | 7720.90 |  |  | 7877 |  |  |  | 1020 | [10 empty] | 88.02 |  |  |  | 88.26 | [5 empty] | 86.82 |  |  | 89.67 |  |  |  | 1.18 |  | 1.06 | [8 empty] | 10.69 |  |  |  |  | 0.24
2013 |  |  |  | 7942.05 |  |  | 8017 |  |  |  | 1007 | [10 empty] | 89.63 |  |  |  | 90.10 | [5 empty] | 90.03 |  |  | 91.52 |  |  |  | 0.71 |  | 0.64 | [8 empty] | 9.26 |  |  |  |  | 0.48
2014 |  |  |  | 7854.08 |  |  | 7901 |  |  |  | 1007 | [10 empty] | 88.91 |  |  |  | 89.37 | [5 empty] | 89.04 |  |  | 90.19 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 10.58 |  |  |  |  | 0.46
2015 |  |  |  | 7958.52 |  |  | 7969 |  |  |  | 1007 | [10 empty] | 90.10 |  |  |  | 90.10 | [5 empty] | 90.22 |  |  | 90.97 |  |  |  | 0.23 |  | 0.35 | [8 empty] | 9.55 |  |  |  |  | 0.00
2016 |  |  |  | 7999.24 |  |  | 8004 |  |  |  | 1007 | [10 empty] | 91.09 |  |  |  | 91.63 | [5 empty] | 90.43 |  |  | 91.12 |  |  |  | 0.01 |  | 1.03 | [8 empty] | 7.34 |  |  |  |  | 0.53
2017 |  |  |  | 7519.94 |  |  | 7668 |  |  |  | 1007 | [10 empty] | 86.12 |  |  |  | 86.99 | [5 empty] | 85.25 |  |  | 87.53 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 12.99 |  |  |  |  | 0.86
2018 |  |  |  | 7903.44 |  |  | 7865 |  |  |  | 1007 | [10 empty] | 89.32 |  |  |  | 89.32 | [5 empty] | 89.59 |  |  | 89.78 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 10.67 |  |  |  |  | 0.00
2019 |  |  |  | 8329.82 |  |  | 8760 |  |  |  | 1007 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 94.43 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
2020 |  |  |  | 7539.38 |  |  | 7987 |  |  |  | 1007 | [10 empty] | 89.98 |  |  |  | 89.98 | [5 empty] | 85.23 |  |  | 90.93 |  |  |  | 0.56 |  | 0.51 | [8 empty] | 9.51 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2010 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 31
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 797 | [14 empty] | 803
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 95
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 9
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Subtotal | [22 empty] | 797 | [14 empty] | 898 |  |  |  | 31 | [11 empty] | 11
Total | [22 empty] | 797 | [14 empty] | 940
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2010 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 14
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 1
Total | [37 empty] | 31

## LING AO-4
2020 Operating Experience
CN-13 | [8 empty] | LING AO-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | LDNPC (Lingdong Nuclear Power Company Ltd.)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2006-06-15
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2011-05-03
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2011-08-07
Reference unit power (net) | [12 empty] | : |  |  | 1007 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7333.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.77 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.77 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.23 %
Load Factor (LF) | [18 empty] | : | 82.91 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.18 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 599 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 698.89 | 449.79 |  |  |  | 765.55 |  | 716.21 | [8 empty] | 132.49 |  |  | 705.95 | [6 empty] | 747.23 |  | 699.74 |  |  |  | 639.20 |  |  | 410.52 |  |  | 618.64 | [9 empty] | 749.38 |  |  | 7333.58
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.98 |  | 96.82 | [8 empty] | 17.77 |  |  | 99.99 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 99.99 |  |  | 92.77
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.98 |  | 96.82 | [8 empty] | 17.77 |  |  | 99.99 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 99.99 |  |  | 92.77
LF [%] |  |  |  |  | 93.28 | 64.18 |  |  |  | 102.18 |  | 98.78 | [8 empty] | 17.68 |  |  | 97.37 | [6 empty] | 99.74 |  | 93.40 |  |  |  | 88.16 |  |  | 54.79 |  |  | 85.33 | [9 empty] | 100.02 |  |  | 82.91
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 97.08 | [8 empty] | 22.85 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.44 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.18
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.02 |  | 3.18 | [8 empty] | 82.23 |  |  | 0.01 | [6 empty] | 0.02 |  | 0.00 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.01 |  |  | 7.23
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 71823.95 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.26 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.07 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.56 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.06 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.3 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.44 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2011 |  |  |  | 3914.72 |  |  | 5268 |  |  |  | 1007 | [10 empty] | 99.60 |  |  |  | 99.60 | [5 empty] | 96.00 |  |  | 100.00 |  |  |  | 0.35 |  | 0.35 | [8 empty] | 0.05 |  |  |  |  | 0.00
2012 |  |  |  | 7009.72 |  |  | 7156 |  |  |  | 1020 | [10 empty] | 80.10 |  |  |  | 80.55 | [5 empty] | 78.24 |  |  | 81.47 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 19.44 |  |  |  |  | 0.45
2013 |  |  |  | 7870.25 |  |  | 7880 |  |  |  | 1007 | [10 empty] | 88.42 |  |  |  | 88.99 | [5 empty] | 89.22 |  |  | 89.95 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 10.84 |  |  |  |  | 0.58
2014 |  |  |  | 7895.97 |  |  | 7972 |  |  |  | 1007 | [10 empty] | 89.82 |  |  |  | 90.25 | [5 empty] | 89.51 |  |  | 91.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.75 |  |  |  |  | 0.43
2015 |  |  |  | 7916.59 |  |  | 7963 |  |  |  | 1007 | [10 empty] | 90.29 |  |  |  | 90.29 | [5 empty] | 89.74 |  |  | 90.90 |  |  |  | 0.00 |  | 0.88 | [8 empty] | 8.83 |  |  |  |  | 0.00
2016 |  |  |  | 7211.42 |  |  | 7329 |  |  |  | 1007 | [10 empty] | 87.55 |  |  |  | 87.85 | [5 empty] | 81.53 |  |  | 83.44 |  |  |  | 0.18 |  | 2.39 | [8 empty] | 9.76 |  |  |  |  | 0.30
2017 |  |  |  | 7677.26 |  |  | 7668 |  |  |  | 1007 | [10 empty] | 91.24 |  |  |  | 91.33 | [5 empty] | 87.03 |  |  | 87.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.67 |  |  |  |  | 0.09
2018 |  |  |  | 8207.81 |  |  | 8447 |  |  |  | 1007 | [10 empty] | 97.86 |  |  |  | 98.34 | [5 empty] | 93.05 |  |  | 96.43 |  |  |  | 1.65 |  | 1.65 | [8 empty] | 0.01 |  |  |  |  | 0.48
2019 |  |  |  | 7157.30 |  |  | 7588 |  |  |  | 1007 | [10 empty] | 88.75 |  |  |  | 89.29 | [5 empty] | 81.14 |  |  | 86.62 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 10.65 |  |  |  |  | 0.55
2020 |  |  |  | 7333.57 |  |  | 8185 |  |  |  | 1007 | [10 empty] | 92.77 |  |  |  | 92.77 | [5 empty] | 82.91 |  |  | 93.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.23 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2011 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 21
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 595 | [14 empty] | 747
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 138
L. |  | Human factor related | [39 empty] | 21
Subtotal | [22 empty] | 595 | [14 empty] | 747 |  |  |  | 42 | [11 empty] | 138
Total | [22 empty] | 595 | [14 empty] | 927
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2011 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [34 empty] | 9
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 30
Total | [37 empty] | 50

## NINGDE-1
2020 Operating Experience
CN-18 | [8 empty] | NINGDE-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-02-18
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2012-12-28
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2013-04-15
Reference unit power (net) | [12 empty] | : |  |  | 1018 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8119.41 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.33 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.8 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.3 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.8 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.9 %
Load Factor (LF) | [18 empty] | : | 90.8 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.15 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 777 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 757.35 | 708.52 |  |  |  | 757.34 |  | 732.78 | [8 empty] | 708.80 |  |  | 0.17 | [6 empty] | 743.48 |  | 730.51 |  |  |  | 732.96 |  |  | 757.31 |  |  | 732.83 | [9 empty] | 757.36 |  |  | 8119.41
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 99.99 | [8 empty] | 93.58 |  |  | 0.02 | [6 empty] | 98.16 |  | 96.45 |  |  |  | 100.00 |  |  | 99.99 |  |  | 99.98 | [9 empty] | 100.00 |  |  | 90.80
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 99.99 | [8 empty] | 93.58 |  |  | 0.02 | [6 empty] | 98.16 |  | 96.45 |  |  |  | 100.00 |  |  | 99.99 |  |  | 99.98 | [9 empty] | 100.00 |  |  | 90.80
LF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 99.98 | [8 empty] | 93.58 |  |  | 0.02 | [6 empty] | 98.16 |  | 96.45 |  |  |  | 100.00 |  |  | 99.99 |  |  | 99.98 | [9 empty] | 100.00 |  |  | 90.80
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 94.09 |  |  | 0.00 | [6 empty] | 98.25 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.15
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 3.54 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.33
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 3.54 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.30
PUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 6.42 |  |  | 99.98 | [6 empty] | 1.84 |  | 0.01 |  |  |  | 0.00 |  |  | 0.01 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 8.90
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 58398.41 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.52 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.32 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.82 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.42 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.77 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.74 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.1 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.61 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2013 |  |  |  | 6947.98 |  |  | 7369 |  |  |  | 1018 | [10 empty] | 99.94 |  |  |  | 99.94 | [5 empty] | 96.64 |  |  | 99.33 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.04 |  |  |  |  | 0.00
2014 |  |  |  | 5047.23 |  |  | 5119 |  |  |  | 1018 | [10 empty] | 56.73 |  |  |  | 56.73 | [5 empty] | 56.60 |  |  | 58.44 |  |  |  | 23.57 |  | 21.32 | [8 empty] | 21.96 |  |  |  |  | 0.00
2015 |  |  |  | 7583.95 |  |  | 7798 |  |  |  | 1018 | [10 empty] | 88.02 |  |  |  | 88.02 | [5 empty] | 85.04 |  |  | 89.02 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 11.80 |  |  |  |  | 0.00
2016 |  |  |  | 6764.98 |  |  | 7207 |  |  |  | 1018 | [10 empty] | 97.33 |  |  |  | 98.07 | [5 empty] | 75.65 |  |  | 82.05 |  |  |  | 1.93 |  | 1.93 | [8 empty] | 0.00 |  |  |  |  | 0.74
2017 |  |  |  | 7210.58 |  |  | 7177 |  |  |  | 1018 | [10 empty] | 83.79 |  |  |  | 83.79 | [5 empty] | 80.86 |  |  | 81.93 |  |  |  | 4.26 |  | 4.80 | [8 empty] | 11.40 |  |  |  |  | 0.00
2018 |  |  |  | 8116.45 |  |  | 7756 |  |  |  | 1018 | [10 empty] | 88.50 |  |  |  | 88.50 | [5 empty] | 91.02 |  |  | 88.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.50 |  |  |  |  | 0.00
2019 |  |  |  | 8608.23 |  |  | 8567 |  |  |  | 1018 | [10 empty] | 96.53 |  |  |  | 96.53 | [5 empty] | 96.53 |  |  | 97.80 |  |  |  | 1.09 |  | 1.07 | [8 empty] | 2.40 |  |  |  |  | 0.00
2020 |  |  |  | 8119.41 |  |  | 8007 |  |  |  | 1018 | [10 empty] | 90.80 |  |  |  | 90.80 | [5 empty] | 90.80 |  |  | 91.15 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 8.90 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2013 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 268
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 777 | [14 empty] | 730
H. |  | Nuclear regulatory requirements | [39 empty] | 40
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 211
M. |  | Governmental requirements or court decisions | [51 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 12
Subtotal | [22 empty] | 777 | [14 empty] | 730 |  |  |  | 320 | [11 empty] | 212
Total | [22 empty] | 777 | [14 empty] | 1262
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2013 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [34 empty] | 187
32. |  |  | Feedwater and Main Steam System | [34 empty] | 20
41. |  |  | Main Generator Systems | [34 empty] | 13
42. |  |  | Electrical Power Supply Systems | [34 empty] | 32
Total | [37 empty] | 260

## NINGDE-2
2020 Operating Experience
CN-19 | [7 empty] | NINGDE-2 | [26 empty] | CHINA
Status at end of year | [6 empty] | : | Operational
Operator | [6 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Owner | [6 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Reactor Supplier | [6 empty] | : | SHE (Shanghai Electric)
Turbine Supplier | [6 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [26 empty] | Key Dates
Reactor type and model | [11 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-11-12
Thermal power | [11 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-01-04
Gross electrical power | [11 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2014-05-04
Reference unit power (net) | [11 empty] | : |  |  | 1018 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 6 years
Design Characteristics
| Primary Systems | [27 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [12 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [12 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [12 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [12 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [12 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [12 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [12 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [12 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [12 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [12 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [12 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [12 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [12 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [12 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [12 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [17 empty] | : | 8940.5 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [17 empty] | : | 99.98 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [17 empty] | : | 99.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [17 empty] | : | 99.98 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [17 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
|  |  |  | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  | 757.34 | 708.53 |  |  |  | 757.34 |  | 732.69 | [8 empty] | 757.34 |  |  | 732.87 | [6 empty] | 757.32 |  | 757.33 |  |  |  | 732.46 |  |  | 757.05 |  |  | 732.92 | [9 empty] | 757.33 |  |  | 8940.50
EAF [%] |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 99.99 | [8 empty] | 99.99 |  |  | 99.99 | [6 empty] | 99.99 |  | 99.99 |  |  |  | 99.93 |  |  | 99.95 |  |  | 99.99 | [9 empty] | 99.99 |  |  | 99.98
UCF [%] |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 99.99 | [8 empty] | 99.99 |  |  | 99.99 | [6 empty] | 99.99 |  | 99.99 |  |  |  | 99.93 |  |  | 99.95 |  |  | 99.99 | [9 empty] | 99.99 |  |  | 99.98
LF [%] |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 99.96 | [8 empty] | 99.99 |  |  | 99.99 | [6 empty] | 99.99 |  | 99.99 |  |  |  | 99.93 |  |  | 99.95 |  |  | 99.99 | [9 empty] | 99.99 |  |  | 99.98
OF [%] |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  | 0.01 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.01 | [6 empty] | 0.01 |  | 0.01 |  |  |  | 0.07 |  |  | 0.05 |  |  | 0.01 | [9 empty] | 0.01 |  |  | 0.01
XUF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [12 empty] | : |  |  | 52037.5 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.35 %
Cumulative Energy Availability Factor (EAF) | [12 empty] | : |  |  | 91.76 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.52 %
Cumulative Unit Capability Factor (UCF) | [12 empty] | : |  |  | 91.79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.69 %
Cumulative Load Factor (LF) | [12 empty] | : |  |  | 86.17 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [12 empty] | : |  |  | 89.65 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2014 |  |  | 6568.05 |  |  | 7044 |  |  |  | 1018 | [10 empty] | 99.85 |  |  |  | 99.85 | [5 empty] | 97.55 |  |  | 100.00 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 0.14 |  |  |  |  | 0.00
2015 |  |  | 6528.23 |  |  | 7145 |  |  |  | 1018 | [10 empty] | 80.58 |  |  |  | 80.58 | [5 empty] | 73.21 |  |  | 81.56 |  |  |  | 0.22 |  | 0.18 | [8 empty] | 19.24 |  |  |  |  | 0.00
2016 |  |  | 5714.85 |  |  | 6290 |  |  |  | 1018 | [10 empty] | 86.24 |  |  |  | 86.39 | [5 empty] | 63.91 |  |  | 71.61 |  |  |  | 0.32 |  | 1.62 | [8 empty] | 12.00 |  |  |  |  | 0.14
2017 |  |  | 8252.86 |  |  | 8371 |  |  |  | 1018 | [10 empty] | 98.72 |  |  |  | 98.72 | [5 empty] | 92.54 |  |  | 95.56 |  |  |  | 1.26 |  | 1.26 | [8 empty] | 0.02 |  |  |  |  | 0.00
2018 |  |  | 7953.87 |  |  | 7938 |  |  |  | 1018 | [10 empty] | 89.03 |  |  |  | 89.03 | [5 empty] | 89.19 |  |  | 90.62 |  |  |  | 0.44 |  | 0.40 | [8 empty] | 10.57 |  |  |  |  | 0.00
2019 |  |  | 8079.09 |  |  | 8026 |  |  |  | 1018 | [10 empty] | 90.60 |  |  |  | 90.60 | [5 empty] | 90.60 |  |  | 91.62 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 9.40 |  |  |  |  | 0.00
2020 |  |  | 8940.50 |  |  | 8784 |  |  |  | 1018 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 99.98 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[22 empty] | 2020 | [14 empty] | 2014 to 2020
Outage Cause | [21 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[22 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [34 empty] | 627
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [50 empty] | 263
Z. |  | Other | [38 empty] | 18
Subtotal | [36 empty] | 627 |  |  |  | 18 | [11 empty] | 263
Total | [21 empty] | 0 | [14 empty] | 908
Equipment Related Unplanned Full Outages, Analysis by System
System | [21 empty] | 2020 | [14 empty] | 2014 to 2020
[22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
Total

## NINGDE-3
2020 Operating Experience
CN-34 | [8 empty] | NINGDE-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-01-08
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-03-21
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-06-10
Reference unit power (net) | [12 empty] | : |  |  | 1018 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8650.7 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.74 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.74 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 3.26 %
Load Factor (LF) | [18 empty] | : | 96.74 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 96.78 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 283 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 757.39 | 708.53 |  |  |  | 757.38 |  | 732.72 | [8 empty] | 757.33 |  |  | 732.94 | [6 empty] | 757.34 |  | 757.34 |  |  |  | 732.89 |  |  | 757.37 |  |  | 732.90 | [9 empty] | 466.58 |  |  | 8650.70
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.99 |  | 99.99 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 61.60 |  |  | 96.74
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.99 |  | 99.99 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 61.60 |  |  | 96.74
LF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.97 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.99 |  | 99.99 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 61.60 |  |  | 96.74
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 61.96 |  |  | 96.78
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.01 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 38.40 |  |  | 3.26
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 43171.7 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.05 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.51 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.97 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.52 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.51 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.97 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.04 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 4638.75 |  |  | 5586 |  |  |  | 1018 | [10 empty] | 91.25 |  |  |  | 91.25 | [5 empty] | 80.88 |  |  | 92.85 |  |  |  | 8.74 |  | 8.74 | [8 empty] | 0.01 |  |  |  |  | 0.00
2016 |  |  |  | 6086.41 |  |  | 6514 |  |  |  | 1018 | [10 empty] | 81.37 |  |  |  | 81.37 | [5 empty] | 68.06 |  |  | 74.16 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 18.62 |  |  |  |  | 0.00
2017 |  |  |  | 7971.03 |  |  | 8107 |  |  |  | 1018 | [10 empty] | 95.64 |  |  |  | 95.64 | [5 empty] | 89.38 |  |  | 92.55 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 4.35 |  |  |  |  | 0.00
2018 |  |  |  | 8264.16 |  |  | 8141 |  |  |  | 1018 | [10 empty] | 92.40 |  |  |  | 92.44 | [5 empty] | 92.67 |  |  | 92.93 |  |  |  | 0.28 |  | 0.26 | [8 empty] | 7.29 |  |  |  |  | 0.05
2019 |  |  |  | 8167.27 |  |  | 8075 |  |  |  | 1018 | [10 empty] | 91.59 |  |  |  | 91.59 | [5 empty] | 91.59 |  |  | 92.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.41 |  |  |  |  | 0.00
2020 |  |  |  | 8650.70 |  |  | 8501 |  |  |  | 1018 | [10 empty] | 96.74 |  |  |  | 96.74 | [5 empty] | 96.74 |  |  | 96.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.26 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2015 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 26
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 282 | [14 empty] | 635
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 168
L. |  | Human factor related | [39 empty] | 50
Subtotal | [22 empty] | 282 | [14 empty] | 635 |  |  |  | 76 | [11 empty] | 168
Total | [22 empty] | 282 | [14 empty] | 879
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2015 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 48
31. |  |  | Turbine and auxiliaries | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 16
Total | [37 empty] | 72

## NINGDE-4
2020 Operating Experience
CN-35 | [7 empty] | NINGDE-4 | [26 empty] | CHINA
Status at end of year | [6 empty] | : | Operational
Operator | [6 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Owner | [6 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Reactor Supplier | [6 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [6 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [26 empty] | Key Dates
Reactor type and model | [11 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-09-29
Thermal power | [11 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-03-29
Gross electrical power | [11 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-07-21
Reference unit power (net) | [11 empty] | : |  |  | 1018 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [27 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [12 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [12 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [12 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [12 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [12 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [12 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [12 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [12 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [12 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [12 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [12 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [12 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [12 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [12 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [12 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [17 empty] | : | 7998.17 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [17 empty] | : | 89.45 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [17 empty] | : | 89.45 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.55 %
Load Factor (LF) | [17 empty] | : | 89.44 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [17 empty] | : | 91.45 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 751 hours
Annual Summary
|  |  |  | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  | 582.40 | 708.52 |  |  |  | 757.39 |  | 732.74 | [8 empty] | 757.38 |  |  | 732.88 | [6 empty] | 757.27 |  | 757.37 |  |  |  | 684.98 |  |  | 37.28 |  |  | 732.58 | [9 empty] | 757.38 |  |  | 7998.17
EAF [%] |  |  |  | 76.89 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 93.45 |  |  | 4.92 |  |  | 99.95 | [9 empty] | 100.00 |  |  | 89.45
UCF [%] |  |  |  | 76.89 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 93.45 |  |  | 4.92 |  |  | 99.95 | [9 empty] | 100.00 |  |  | 89.45
LF [%] |  |  |  | 76.89 | 100.00 |  |  |  | 100.00 |  | 99.97 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 93.45 |  |  | 4.92 |  |  | 99.95 | [9 empty] | 100.00 |  |  | 89.44
OF [%] |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 93.89 |  |  | 4.97 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.45
FLR [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  | 23.11 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.02 |  | 0.00 |  |  |  | 6.55 |  |  | 95.08 |  |  | 0.05 | [9 empty] | 0.00 |  |  | 10.55
XUF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [12 empty] | : |  |  | 33988.17 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.04 %
Cumulative Energy Availability Factor (EAF) | [12 empty] | : |  |  | 91.91 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.03 %
Cumulative Unit Capability Factor (UCF) | [12 empty] | : |  |  | 91.91 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.05 %
Cumulative Load Factor (LF) | [12 empty] | : |  |  | 85.53 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [12 empty] | : |  |  | 87.89 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  | 3694.87 |  |  | 3786 |  |  |  | 1018 | [10 empty] | 99.87 |  |  |  | 99.87 | [5 empty] | 91.83 |  |  | 95.92 |  |  |  | 0.12 |  | 0.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  | 5303.77 |  |  | 5739 |  |  |  | 1018 | [10 empty] | 84.33 |  |  |  | 84.33 | [5 empty] | 59.47 |  |  | 65.51 |  |  |  | 0.12 |  | 0.10 | [8 empty] | 15.57 |  |  |  |  | 0.00
2018 |  |  | 8917.08 |  |  | 8760 |  |  |  | 1018 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 99.99 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2019 |  |  | 8074.33 |  |  | 7992 |  |  |  | 1018 | [10 empty] | 90.54 |  |  |  | 90.54 | [5 empty] | 90.54 |  |  | 91.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.46 |  |  |  |  | 0.00
2020 |  |  | 7998.17 |  |  | 8033 |  |  |  | 1018 | [10 empty] | 89.45 |  |  |  | 89.45 | [5 empty] | 89.44 |  |  | 91.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.55 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[22 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [21 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[22 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [19 empty] | 751 | [14 empty] | 639
J. |  | Grid limitation, failure or grid unavailability | [50 empty] | 237
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [50 empty] | 186
Subtotal | [21 empty] | 751 | [14 empty] | 639 | [15 empty] | 423
Total | [21 empty] | 751 | [14 empty] | 1062
Equipment Related Unplanned Full Outages, Analysis by System
System | [21 empty] | 2020 | [14 empty] | 2016 to 2020
[22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
Total

## QINSHAN 2-1
2020 Operating Experience
CN-4 | [8 empty] | QINSHAN 2-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Owner | [7 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1996-06-02
Thermal power | [12 empty] | : |  |  | 1930 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-02-06
Gross electrical power | [12 empty] | : |  |  | 650 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-04-15
Reference unit power (net) | [12 empty] | : |  |  | 610 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 18 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.2
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.45
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.25 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 2.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.6576 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.09 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5228.19 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.88 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.95 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.05 %
Load Factor (LF) | [18 empty] | : | 97.57 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.07 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 351.37 | 337.47 |  |  |  | 465.24 |  | 449.04 | [8 empty] | 460.61 |  |  | 445.64 | [6 empty] | 460.85 |  | 449.27 |  |  |  | 437.54 |  |  | 449.39 |  |  | 452.29 | [9 empty] | 469.47 |  |  | 5228.19
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.29 |  |  |  | 99.58 |  |  | 100.00 |  |  | 99.73 | [9 empty] | 100.00 |  |  | 99.88
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.71 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.73 | [9 empty] | 100.00 |  |  | 99.95
LF [%] |  |  |  |  | 77.42 | 79.49 |  |  |  | 102.51 |  | 102.24 | [8 empty] | 101.49 |  |  | 101.47 | [6 empty] | 101.54 |  | 98.99 |  |  |  | 99.62 |  |  | 99.02 |  |  | 102.98 | [9 empty] | 103.45 |  |  | 97.57
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.29 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.27 | [9 empty] | 0.00 |  |  | 0.05
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.42 |  |  |  | 0.42 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.07
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 84998.69 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.11 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.01 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.93 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.04 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.03 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.96 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 2965.29 |  |  | 4631 |  |  |  | 610 | [10 empty] | 81.56 |  |  |  | 81.56 | [5 empty] | 73.64 |  |  | 70.16 |  |  |  | 18.44 |  | 18.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 4327.30 |  |  | 7123 |  |  |  | 610 | [10 empty] | 80.90 |  |  |  | 80.95 | [5 empty] | 80.98 |  |  | 81.31 |  |  |  | 2.61 |  | 2.17 | [8 empty] | 16.88 |  |  |  |  | 0.05
2004 |  |  |  | 4395.68 |  |  | 7117 |  |  |  | 610 | [10 empty] | 80.13 |  |  |  | 80.13 | [5 empty] | 82.04 |  |  | 81.02 |  |  |  | 3.25 |  | 2.69 | [8 empty] | 17.17 |  |  |  |  | 0.00
2005 |  |  |  | 4944.77 |  |  | 7982 |  |  |  | 610 | [10 empty] | 90.61 |  |  |  | 90.61 | [5 empty] | 92.54 |  |  | 91.12 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.37 |  |  |  |  | 0.00
2006 |  |  |  | 2938.16 |  |  | 4890 |  |  |  | 610 | [10 empty] | 55.23 |  |  |  | 55.23 | [5 empty] | 54.98 |  |  | 55.82 |  |  |  | 15.49 |  | 10.12 | [8 empty] | 34.65 |  |  |  |  | 0.00
2007 |  |  |  | 3503.00 |  |  | 5681 |  |  |  | 610 | [10 empty] | 64.12 |  |  |  | 64.12 | [5 empty] | 65.56 |  |  | 64.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 35.88 |  |  |  |  | 0.00
2008 |  |  |  | 4677.61 |  |  | 7554 |  |  |  | 610 | [10 empty] | 85.25 |  |  |  | 85.35 | [5 empty] | 87.30 |  |  | 86.00 |  |  |  | 0.18 |  | 0.48 | [8 empty] | 14.17 |  |  |  |  | 0.10
2009 |  |  |  | 4500.99 |  |  | 7256 |  |  |  | 610 | [10 empty] | 82.66 |  |  |  | 82.66 | [5 empty] | 84.23 |  |  | 82.83 |  |  |  | 0.74 |  | 0.62 | [8 empty] | 16.72 |  |  |  |  | 0.00
2010 |  |  |  | 4985.39 |  |  | 8095 |  |  |  | 610 | [10 empty] | 91.70 |  |  |  | 91.70 | [5 empty] | 93.30 |  |  | 92.41 |  |  |  | 0.21 |  | 0.19 | [8 empty] | 8.11 |  |  |  |  | 0.00
2011 |  |  |  | 4029.39 |  |  | 6521 |  |  |  | 610 | [10 empty] | 73.66 |  |  |  | 73.66 | [5 empty] | 75.41 |  |  | 74.44 |  |  |  | 2.90 |  | 3.97 | [8 empty] | 22.37 |  |  |  |  | 0.00
2012 |  |  |  | 4545.92 |  |  | 7543 |  |  |  | 610 | [10 empty] | 85.20 |  |  |  | 85.20 | [5 empty] | 84.84 |  |  | 85.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.80 |  |  |  |  | 0.00
2013 |  |  |  | 4680.90 |  |  | 7561 |  |  |  | 610 | [10 empty] | 85.75 |  |  |  | 85.75 | [5 empty] | 87.60 |  |  | 86.31 |  |  |  | 0.87 |  | 0.75 | [8 empty] | 13.50 |  |  |  |  | 0.00
2014 |  |  |  | 4579.16 |  |  | 7412 |  |  |  | 610 | [10 empty] | 83.68 |  |  |  | 83.68 | [5 empty] | 85.69 |  |  | 84.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.32 |  |  |  |  | 0.00
2015 |  |  |  | 4775.88 |  |  | 7859 |  |  |  | 610 | [10 empty] | 89.35 |  |  |  | 89.35 | [5 empty] | 89.38 |  |  | 89.71 |  |  |  | 0.84 |  | 0.76 | [8 empty] | 9.90 |  |  |  |  | 0.00
2016 |  |  |  | 4732.19 |  |  | 7825 |  |  |  | 610 | [10 empty] | 91.28 |  |  |  | 91.28 | [5 empty] | 88.32 |  |  | 89.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.72 |  |  |  |  | 0.00
2017 |  |  |  | 5385.37 |  |  | 8732 |  |  |  | 610 | [10 empty] | 99.32 |  |  |  | 99.52 | [5 empty] | 100.78 |  |  | 99.68 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.13 |  |  |  |  | 0.20
2018 |  |  |  | 4725.63 |  |  | 7682 |  |  |  | 610 | [10 empty] | 87.19 |  |  |  | 87.19 | [5 empty] | 88.44 |  |  | 87.69 |  |  |  | 0.16 |  | 0.14 | [8 empty] | 12.67 |  |  |  |  | 0.00
2019 |  |  |  | 4796.97 |  |  | 7781 |  |  |  | 610 | [10 empty] | 88.15 |  |  |  | 88.20 | [5 empty] | 89.77 |  |  | 88.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.80 |  |  |  |  | 0.06
2020 |  |  |  | 5228.19 |  |  | 8784 |  |  |  | 610 | [10 empty] | 99.88 |  |  |  | 99.95 | [5 empty] | 97.57 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  |  |  | 0.07
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2002 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 90
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1008
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 25
E. |  | Testing of plant systems or components | [39 empty] | 1
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 219
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
Z. |  | Other | [39 empty] | 8
Subtotal | [37 empty] | 1252 |  |  |  | 99 | [11 empty] | 11
Total | [22 empty] | 0 | [14 empty] | 1362
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2002 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 2
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 40
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 17
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 28
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [37 empty] | 94

## QINSHAN 2-2
2020 Operating Experience
CN-5 | [8 empty] | QINSHAN 2-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Owner | [7 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1997-04-01
Thermal power | [12 empty] | : |  |  | 1930 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2004-03-11
Gross electrical power | [12 empty] | : |  |  | 650 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2004-05-03
Reference unit power (net) | [12 empty] | : |  |  | 610 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 16 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.2
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.450
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.25 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 2.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.6576 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.09 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4758.46 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.79 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.31 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.69 %
Load Factor (LF) | [18 empty] | : | 88.81 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.52 %
Operating Factor (OF) | [18 empty] | : | 92.85 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 628 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 435.15 | 234.75 |  |  |  | 467.87 |  | 445.96 | [8 empty] | 455.19 |  |  | 443.25 | [6 empty] | 460.89 |  | 408.19 |  |  |  | 29.49 |  |  | 458.58 |  |  | 451.45 | [9 empty] | 467.68 |  |  | 4758.46
EAF [%] |  |  |  |  | 99.58 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 82.07 |  |  |  | 6.73 |  |  | 99.90 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.79
UCF [%] |  |  |  |  | 99.58 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 6.73 |  |  | 99.90 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.31
LF [%] |  |  |  |  | 95.88 | 55.29 |  |  |  | 103.09 |  | 101.54 | [8 empty] | 100.30 |  |  | 100.92 | [6 empty] | 101.55 |  | 89.94 |  |  |  | 6.71 |  |  | 101.05 |  |  | 102.79 | [9 empty] | 103.05 |  |  | 88.81
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 12.78 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.85
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.42 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 93.27 |  |  | 0.10 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.69
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 17.93 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.52
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 79774.2 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.5 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.27 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.34 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.39 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.26 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.21 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.12 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.73 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2004 |  |  |  | 3764.39 |  |  | 6381 |  |  |  | 610 | [10 empty] | 96.24 |  |  |  | 96.24 | [5 empty] | 97.96 |  |  | 96.62 |  |  |  | 0.90 |  | 0.87 | [8 empty] | 2.88 |  |  |  |  | 0.00
2005 |  |  |  | 4521.51 |  |  | 7331 |  |  |  | 610 | [10 empty] | 82.69 |  |  |  | 82.77 | [5 empty] | 84.62 |  |  | 83.69 |  |  |  | 1.65 |  | 1.39 | [8 empty] | 15.84 |  |  |  |  | 0.08
2006 |  |  |  | 4790.44 |  |  | 7822 |  |  |  | 610 | [10 empty] | 88.78 |  |  |  | 88.78 | [5 empty] | 89.65 |  |  | 89.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.21 |  |  |  |  | 0.00
2007 |  |  |  | 4817.01 |  |  | 7792 |  |  |  | 610 | [10 empty] | 88.30 |  |  |  | 88.30 | [5 empty] | 90.15 |  |  | 88.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.70 |  |  |  |  | 0.00
2008 |  |  |  | 4635.51 |  |  | 7545 |  |  |  | 610 | [10 empty] | 84.89 |  |  |  | 85.21 | [5 empty] | 86.51 |  |  | 85.89 |  |  |  | 0.36 |  | 0.31 | [8 empty] | 14.48 |  |  |  |  | 0.32
2009 |  |  |  | 4787.80 |  |  | 7821 |  |  |  | 610 | [10 empty] | 88.22 |  |  |  | 88.22 | [5 empty] | 89.60 |  |  | 89.28 |  |  |  | 0.62 |  | 0.55 | [8 empty] | 11.24 |  |  |  |  | 0.00
2010 |  |  |  | 4715.04 |  |  | 7645 |  |  |  | 610 | [10 empty] | 86.64 |  |  |  | 86.64 | [5 empty] | 88.24 |  |  | 87.27 |  |  |  | 0.43 |  | 0.37 | [8 empty] | 12.98 |  |  |  |  | 0.00
2011 |  |  |  | 4960.23 |  |  | 8014 |  |  |  | 610 | [10 empty] | 90.91 |  |  |  | 90.91 | [5 empty] | 92.83 |  |  | 91.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.09 |  |  |  |  | 0.00
2012 |  |  |  | 4335.54 |  |  | 7072 |  |  |  | 610 | [10 empty] | 79.63 |  |  |  | 79.63 | [5 empty] | 80.91 |  |  | 80.51 |  |  |  | 10.13 |  | 8.98 | [8 empty] | 11.39 |  |  |  |  | 0.00
2013 |  |  |  | 4818.51 |  |  | 7826 |  |  |  | 610 | [10 empty] | 88.70 |  |  |  | 88.70 | [5 empty] | 90.17 |  |  | 89.34 |  |  |  | 1.23 |  | 1.11 | [8 empty] | 10.19 |  |  |  |  | 0.00
2014 |  |  |  | 4626.25 |  |  | 7514 |  |  |  | 610 | [10 empty] | 85.00 |  |  |  | 85.00 | [5 empty] | 86.58 |  |  | 85.78 |  |  |  | 2.26 |  | 1.96 | [8 empty] | 13.04 |  |  |  |  | 0.00
2015 |  |  |  | 4872.99 |  |  | 7990 |  |  |  | 610 | [10 empty] | 95.14 |  |  |  | 95.14 | [5 empty] | 91.19 |  |  | 91.21 |  |  |  | 4.84 |  | 4.83 | [8 empty] | 0.03 |  |  |  |  | 0.00
2016 |  |  |  | 4525.57 |  |  | 7377 |  |  |  | 610 | [10 empty] | 83.79 |  |  |  | 83.79 | [5 empty] | 84.46 |  |  | 83.98 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 16.20 |  |  |  |  | 0.00
2017 |  |  |  | 4803.39 |  |  | 7830 |  |  |  | 610 | [10 empty] | 88.83 |  |  |  | 88.83 | [5 empty] | 89.89 |  |  | 89.38 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 11.16 |  |  |  |  | 0.00
2018 |  |  |  | 5306.28 |  |  | 8574 |  |  |  | 610 | [10 empty] | 97.65 |  |  |  | 97.65 | [5 empty] | 99.30 |  |  | 97.88 |  |  |  | 2.30 |  | 2.29 | [8 empty] | 0.05 |  |  |  |  | 0.00
2019 |  |  |  | 4735.26 |  |  | 7680 |  |  |  | 610 | [10 empty] | 87.10 |  |  |  | 87.16 | [5 empty] | 88.62 |  |  | 87.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.84 |  |  |  |  | 0.06
2020 |  |  |  | 4758.46 |  |  | 8156 |  |  |  | 610 | [10 empty] | 90.79 |  |  |  | 92.31 | [5 empty] | 88.81 |  |  | 92.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.69 |  |  |  |  | 1.52
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2004 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 108
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 627 | [14 empty] | 845
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 23
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 5
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 24
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Subtotal | [22 empty] | 627 | [14 empty] | 873 |  |  |  | 108 | [11 empty] | 25
Total | [22 empty] | 627 | [14 empty] | 1006
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2004 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 86
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [37 empty] | 109

## QINSHAN 2-3
2020 Operating Experience
CN-14 | [8 empty] | QINSHAN 2-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Owner | [7 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2006-04-28
Thermal power | [12 empty] | : |  |  | 1930 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2010-08-01
Gross electrical power | [12 empty] | : |  |  | 660 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2010-10-05
Reference unit power (net) | [12 empty] | : |  |  | 619 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 10 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.2
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.45
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.25 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 2.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.6576 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.09 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4753.88 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.05 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.36 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.64 %
Load Factor (LF) | [18 empty] | : | 87.43 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.31 %
Operating Factor (OF) | [18 empty] | : | 89.59 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 914 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 377.35 | 341.46 |  |  |  | 463.35 |  | 447.53 | [8 empty] | 165.01 |  |  | 230.80 | [6 empty] | 460.75 |  | 454.84 |  |  |  | 444.62 |  |  | 445.72 |  |  | 453.51 | [9 empty] | 468.94 |  |  | 4753.88
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 35.17 |  |  | 49.36 | [6 empty] | 98.76 |  | 98.76 |  |  |  | 98.76 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.05
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 35.17 |  |  | 49.36 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.36
LF [%] |  |  |  |  | 81.94 | 79.26 |  |  |  | 100.61 |  | 100.42 | [8 empty] | 35.83 |  |  | 51.79 | [6 empty] | 100.05 |  | 98.76 |  |  |  | 99.76 |  |  | 96.78 |  |  | 101.76 | [9 empty] | 101.82 |  |  | 87.43
OF [%] |  |  |  |  | 83.20 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 35.35 |  |  | 57.22 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.59
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 64.83 |  |  | 50.64 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.64
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.24 |  | 1.24 |  |  |  | 1.24 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.31
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 50161.11 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.17 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.88 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.07 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.97 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.96 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 90.28 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.08 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.97 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2010 |  |  |  | 1465.17 |  |  | 2685 |  |  |  | 610 | [10 empty] | 94.75 |  |  |  | 94.75 | [5 empty] | 96.66 |  |  | 97.55 |  |  |  | 5.22 |  | 5.21 | [8 empty] | 0.04 |  |  |  |  | 0.00
2011 |  |  |  | 4434.13 |  |  | 7226 |  |  |  | 610 | [10 empty] | 81.55 |  |  |  | 81.56 | [5 empty] | 82.98 |  |  | 82.49 |  |  |  | 0.21 |  | 0.17 | [8 empty] | 18.27 |  |  |  |  | 0.01
2012 |  |  |  | 4846.78 |  |  | 7977 |  |  |  | 610 | [10 empty] | 90.05 |  |  |  | 90.05 | [5 empty] | 90.45 |  |  | 90.81 |  |  |  | 0.50 |  | 0.45 | [8 empty] | 9.49 |  |  |  |  | 0.00
2013 |  |  |  | 5076.15 |  |  | 8243 |  |  |  | 610 | [10 empty] | 93.46 |  |  |  | 93.46 | [5 empty] | 94.99 |  |  | 94.10 |  |  |  | 0.17 |  | 0.16 | [8 empty] | 6.38 |  |  |  |  | 0.00
2014 |  |  |  | 4929.31 |  |  | 8078 |  |  |  | 619 | [10 empty] | 91.99 |  |  |  | 92.07 | [5 empty] | 90.91 |  |  | 92.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.93 |  |  |  |  | 0.08
2015 |  |  |  | 4519.98 |  |  | 7410 |  |  |  | 619 | [10 empty] | 86.17 |  |  |  | 86.17 | [5 empty] | 83.36 |  |  | 84.59 |  |  |  | 6.43 |  | 5.93 | [8 empty] | 7.91 |  |  |  |  | 0.00
2016 |  |  |  | 5259.45 |  |  | 8584 |  |  |  | 619 | [10 empty] | 99.80 |  |  |  | 99.80 | [5 empty] | 96.73 |  |  | 97.72 |  |  |  | 0.12 |  | 0.12 | [8 empty] | 0.09 |  |  |  |  | 0.00
2017 |  |  |  | 4768.41 |  |  | 7804 |  |  |  | 619 | [10 empty] | 87.96 |  |  |  | 88.41 | [5 empty] | 87.94 |  |  | 89.09 |  |  |  | 0.38 |  | 0.34 | [8 empty] | 11.25 |  |  |  |  | 0.45
2018 |  |  |  | 4767.33 |  |  | 7756 |  |  |  | 619 | [10 empty] | 87.93 |  |  |  | 87.93 | [5 empty] | 87.92 |  |  | 88.54 |  |  |  | 1.57 |  | 1.41 | [8 empty] | 10.67 |  |  |  |  | 0.00
2019 |  |  |  | 5341.24 |  |  | 8664 |  |  |  | 619 | [10 empty] | 98.82 |  |  |  | 98.82 | [5 empty] | 98.50 |  |  | 98.90 |  |  |  | 1.11 |  | 1.11 | [8 empty] | 0.07 |  |  |  |  | 0.00
2020 |  |  |  | 4753.88 |  |  | 7870 |  |  |  | 619 | [10 empty] | 90.05 |  |  |  | 90.36 | [5 empty] | 87.43 |  |  | 89.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.64 |  |  |  |  | 0.31
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2010 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 82
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 789 | [14 empty] | 679
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 125 | [19 empty] | 47
L. |  | Human factor related | [39 empty] | 0
Subtotal | [22 empty] | 789 | [10 empty] | 125 |  |  |  | 679 |  |  |  | 82 | [11 empty] | 47
Total | [22 empty] | 914 | [14 empty] | 808
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2010 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
16. |  |  | Steam generation systems | [34 empty] | 11
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 51
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [19 empty] | 125 | [14 empty] | 12
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 125 | [14 empty] | 92

## QINSHAN 2-4
2020 Operating Experience
CN-15 | [8 empty] | QINSHAN 2-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Owner | [7 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-01-28
Thermal power | [12 empty] | : |  |  | 1930 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2011-11-25
Gross electrical power | [12 empty] | : |  |  | 660 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2011-12-30
Reference unit power (net) | [12 empty] | : |  |  | 619 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.2
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.45
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.25 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 2.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.6576 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.09 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5276.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.97 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.97 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.03 %
Load Factor (LF) | [18 empty] | : | 97.05 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 439.43 | 341.44 |  |  |  | 463.74 |  | 447.66 | [8 empty] | 454.10 |  |  | 442.14 | [6 empty] | 463.10 |  | 460.54 |  |  |  | 447.62 |  |  | 395.70 |  |  | 452.88 | [9 empty] | 468.35 |  |  | 5276.68
EAF [%] |  |  |  |  | 99.69 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.90 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.97
UCF [%] |  |  |  |  | 99.69 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.90 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.97
LF [%] |  |  |  |  | 95.42 | 79.25 |  |  |  | 100.70 |  | 100.45 | [8 empty] | 98.60 |  |  | 99.21 | [6 empty] | 100.56 |  | 100.00 |  |  |  | 100.43 |  |  | 85.92 |  |  | 101.61 | [9 empty] | 101.70 |  |  | 97.05
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.10 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.10 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
PUF [%] |  |  |  |  | 0.31 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 44484.66 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.17 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.35 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.49 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.36 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.28 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.14 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.55 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2011 |  |  |  | 257.02 |  |  | 614 |  |  |  | 610 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 5195.81 |  |  | 8438 |  |  |  | 610 | [10 empty] | 95.79 |  |  |  | 95.79 | [5 empty] | 96.97 |  |  | 96.06 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 4.17 |  |  |  |  | 0.00
2013 |  |  |  | 4591.39 |  |  | 7428 |  |  |  | 610 | [10 empty] | 84.25 |  |  |  | 84.25 | [5 empty] | 85.92 |  |  | 84.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.75 |  |  |  |  | 0.00
2014 |  |  |  | 4844.49 |  |  | 7905 |  |  |  | 610 | [10 empty] | 88.86 |  |  |  | 89.62 | [5 empty] | 90.66 |  |  | 90.24 |  |  |  | 1.32 |  | 1.20 | [8 empty] | 9.19 |  |  |  |  | 0.75
2015 |  |  |  | 4837.34 |  |  | 7994 |  |  |  | 610 | [10 empty] | 91.06 |  |  |  | 91.06 | [5 empty] | 90.53 |  |  | 91.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.94 |  |  |  |  | 0.00
2016 |  |  |  | 4983.82 |  |  | 8130 |  |  |  | 610 | [10 empty] | 91.93 |  |  |  | 91.93 | [5 empty] | 93.01 |  |  | 92.55 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 8.00 |  |  |  |  | 0.00
2017 |  |  |  | 4899.45 |  |  | 7993 |  |  |  | 619 | [10 empty] | 90.14 |  |  |  | 90.61 | [5 empty] | 90.35 |  |  | 91.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.39 |  |  |  |  | 0.48
2018 |  |  |  | 4786.77 |  |  | 7760 |  |  |  | 619 | [10 empty] | 88.16 |  |  |  | 88.16 | [5 empty] | 88.28 |  |  | 88.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.84 |  |  |  |  | 0.00
2019 |  |  |  | 4812.21 |  |  | 7815 |  |  |  | 619 | [10 empty] | 91.91 |  |  |  | 91.91 | [5 empty] | 88.75 |  |  | 89.21 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 8.00 |  |  |  |  | 0.00
2020 |  |  |  | 5276.68 |  |  | 8784 |  |  |  | 619 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 97.05 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.03 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2011 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 662
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 29
E. |  | Testing of plant systems or components | [35 empty] | 9
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 30
Subtotal | [37 empty] | 700 |  |  |  | 1 | [11 empty] | 30
Total | [22 empty] | 0 | [14 empty] | 731
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2011 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
35. |  |  | All other I&C Systems | [34 empty] | 1
Total | [37 empty] | 1

## QINSHAN 3-1
2020 Operating Experience
CN-8 | [8 empty] | QINSHAN 3-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TQNPC (The Third Qinshan Joint Venture Company, LTD.)
Owner | [7 empty] | : | TQNPC (The Third Qinshan Joint Venture Company, LTD.)
Reactor Supplier | [7 empty] | : | AECL (ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | Hit (Japan Hitachi Company.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1998-06-08
Thermal power | [12 empty] | : |  |  | 2064 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-11-19
Gross electrical power | [12 empty] | : |  |  | 728 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-12-31
Reference unit power (net) | [12 empty] | : |  |  | 677 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 18 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.89
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.124
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.71 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 60 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7186 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 6.28 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 25.35 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5714.7 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.07 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.95 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.07 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.92 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 96.1 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.97 %
Operating Factor (OF) | [18 empty] | : | 99.03 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 85 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 483.60 | 384.54 |  |  |  | 501.87 |  | 477.74 | [8 empty] | 493.20 |  |  | 418.03 | [6 empty] | 503.60 |  | 503.60 |  |  |  | 485.67 |  |  | 478.02 |  |  | 483.19 | [9 empty] | 501.64 |  |  | 5714.70
EAF [%] |  |  |  |  | 99.98 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 88.14 | [6 empty] | 99.98 |  | 99.98 |  |  |  | 99.98 |  |  | 99.28 |  |  | 99.99 | [9 empty] | 99.93 |  |  | 98.95
UCF [%] |  |  |  |  | 99.98 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.98 |  | 99.98 |  |  |  | 99.98 |  |  | 99.28 |  |  | 99.99 | [9 empty] | 99.93 |  |  | 99.92
LF [%] |  |  |  |  | 96.01 | 81.61 |  |  |  | 99.64 |  | 98.01 | [8 empty] | 97.92 |  |  | 85.76 | [6 empty] | 99.98 |  | 99.98 |  |  |  | 99.64 |  |  | 94.90 |  |  | 99.13 | [9 empty] | 99.59 |  |  | 96.10
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 88.19 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.03
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.72 |  |  | 0.00 | [9 empty] | 0.06 |  |  | 0.07
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.72 |  |  | 0.00 | [9 empty] | 0.06 |  |  | 0.07
PUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.02 |  | 0.02 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.01 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 11.86 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.97
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 94198.51 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.64 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.75 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.21 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.29 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 90.28 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.46 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.47 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | Data not provided
2003 |  |  |  | 5174.75 |  |  | 7977 |  |  |  | 650 | [10 empty] | 86.59 |  |  |  | 89.65 | [5 empty] | 90.88 |  |  | 91.06 |  |  |  | 10.35 |  | 10.35 | [8 empty] | 0.00 |  |  |  |  | 3.06
2004 |  |  |  | 4405.52 |  |  | 6745 |  |  |  | 650 | [10 empty] | 75.60 |  |  |  | 75.61 | [5 empty] | 77.16 |  |  | 76.79 |  |  |  | 2.31 |  | 1.78 | [8 empty] | 22.61 |  |  |  |  | 0.01
2005 |  |  |  | 4781.60 |  |  | 7249 |  |  |  | 650 | [10 empty] | 82.43 |  |  |  | 82.50 | [5 empty] | 83.98 |  |  | 82.75 |  |  |  | 2.18 |  | 1.84 | [8 empty] | 15.66 |  |  |  |  | 0.07
2006 |  |  |  | 5577.79 |  |  | 8484 |  |  |  | 650 | [10 empty] | 96.34 |  |  |  | 96.34 | [5 empty] | 97.96 |  |  | 96.85 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 3.60 |  |  |  |  | 0.00
2007 |  |  |  | 5020.40 |  |  | 7597 |  |  |  | 650 | [10 empty] | 86.41 |  |  |  | 86.41 | [5 empty] | 88.17 |  |  | 86.72 |  |  |  | 0.95 |  | 0.82 | [8 empty] | 12.76 |  |  |  |  | 0.00
2008 |  |  |  | 5328.57 |  |  | 8051 |  |  |  | 650 | [10 empty] | 91.11 |  |  |  | 91.21 | [5 empty] | 93.33 |  |  | 91.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.79 |  |  |  |  | 0.10
2009 |  |  |  | 5326.22 |  |  | 8076 |  |  |  | 650 | [10 empty] | 91.91 |  |  |  | 91.91 | [5 empty] | 93.54 |  |  | 92.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.09 |  |  |  |  | 0.00
2010 |  |  |  | 5216.34 |  |  | 7884 |  |  |  | 650 | [10 empty] | 89.71 |  |  |  | 89.71 | [5 empty] | 91.61 |  |  | 90.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 10.27 |  |  |  |  | 0.00
2011 |  |  |  | 5388.51 |  |  | 8131 |  |  |  | 650 | [10 empty] | 92.55 |  |  |  | 92.55 | [5 empty] | 94.63 |  |  | 92.82 |  |  |  | 1.96 |  | 1.85 | [8 empty] | 5.60 |  |  |  |  | 0.00
2012 |  |  |  | 5544.58 |  |  | 8462 |  |  |  | 650 | [10 empty] | 96.25 |  |  |  | 96.25 | [5 empty] | 97.11 |  |  | 96.33 |  |  |  | 0.34 |  | 0.33 | [8 empty] | 3.41 |  |  |  |  | 0.00
2013 |  |  |  | 5237.40 |  |  | 7949 |  |  |  | 650 | [10 empty] | 89.89 |  |  |  | 89.89 | [5 empty] | 91.98 |  |  | 90.74 |  |  |  | 1.22 |  | 1.11 | [8 empty] | 9.00 |  |  |  |  | 0.00
2014 |  |  |  | 5594.85 |  |  | 8451 |  |  |  | 650 | [10 empty] | 96.13 |  |  |  | 96.13 | [5 empty] | 98.26 |  |  | 96.47 |  |  |  | 3.83 |  | 3.83 | [8 empty] | 0.04 |  |  |  |  | 0.00
2015 |  |  |  | 4758.34 |  |  | 7292 |  |  |  | 677 | [10 empty] | 83.19 |  |  |  | 83.19 | [5 empty] | 80.23 |  |  | 83.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.81 |  |  |  |  | 0.00
2016 |  |  |  | 5476.06 |  |  | 8351 |  |  |  | 677 | [10 empty] | 94.90 |  |  |  | 94.90 | [5 empty] | 92.08 |  |  | 95.07 |  |  |  | 5.08 |  | 5.08 | [8 empty] | 0.02 |  |  |  |  | 0.00
2017 |  |  |  | 4542.77 |  |  | 7000 |  |  |  | 677 | [10 empty] | 78.63 |  |  |  | 79.83 | [5 empty] | 76.60 |  |  | 79.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.17 |  |  |  |  | 1.20
2018 |  |  |  | 5729.05 |  |  | 8657 |  |  |  | 677 | [10 empty] | 98.76 |  |  |  | 99.96 | [5 empty] | 96.60 |  |  | 98.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  |  |  | 1.20
2019 |  |  |  | 5061.34 |  |  | 7709 |  |  |  | 677 | [10 empty] | 86.01 |  |  |  | 87.63 | [5 empty] | 85.34 |  |  | 88.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 12.34 |  |  |  |  | 1.62
2020 |  |  |  | 5714.70 |  |  | 8699 |  |  |  | 677 | [10 empty] | 98.95 |  |  |  | 99.92 | [5 empty] | 96.10 |  |  | 99.03 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 0.01 |  |  |  |  | 0.97
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2002 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 114
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 709
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 6
Z. |  | Other | [31 empty] | 85 | [19 empty] | 5
Subtotal | [33 empty] | 85 |  |  |  | 709 |  |  |  | 114 | [11 empty] | 11
Total | [22 empty] | 85 | [14 empty] | 834
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2002 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 4
12. |  |  | Reactor I&C Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 39
16. |  |  | Steam generation systems | [34 empty] | 10
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [19 empty] | 85 | [14 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 41
Total | [22 empty] | 85 | [14 empty] | 119
Highlights (2020)

## QINSHAN 3-2
2020 Operating Experience
CN-9 | [8 empty] | QINSHAN 3-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TQNPC (The Third Qinshan Joint Venture Company, LTD.)
Owner | [7 empty] | : | TQNPC (The Third Qinshan Joint Venture Company, LTD.)
Reactor Supplier | [7 empty] | : | AECL (ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | Hit (Japan Hitachi Company.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1998-09-25
Thermal power | [12 empty] | : |  |  | 2064 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2003-06-12
Gross electrical power | [12 empty] | : |  |  | 728 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2003-07-24
Reference unit power (net) | [12 empty] | : |  |  | 677 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 17 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.89
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.124
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.71 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 60 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7186 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 6.28 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.51
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 25.35 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5261.05 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.04 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.04 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.96 %
Load Factor (LF) | [18 empty] | : | 88.47 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.23 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 770 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 482.14 | 382.49 |  |  |  | 500.78 |  | 475.73 | [8 empty] | 0.06 |  |  | 450.23 | [6 empty] | 503.69 |  | 503.69 |  |  |  | 487.44 |  |  | 491.93 |  |  | 482.64 | [9 empty] | 500.23 |  |  | 5261.05
EAF [%] |  |  |  |  | 99.98 | 100.00 |  |  |  | 99.99 |  | 99.75 | [8 empty] | 0.09 |  |  | 94.25 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.04
UCF [%] |  |  |  |  | 99.98 | 100.00 |  |  |  | 99.99 |  | 99.75 | [8 empty] | 0.09 |  |  | 94.25 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.04
LF [%] |  |  |  |  | 95.72 | 81.18 |  |  |  | 99.42 |  | 97.60 | [8 empty] | 0.01 |  |  | 92.37 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 97.66 |  |  | 99.02 | [9 empty] | 99.31 |  |  | 88.47
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.13 |  |  | 96.25 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.23
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.01 |  | 0.25 | [8 empty] | 99.91 |  |  | 5.75 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.96
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 91675.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.61 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.01 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.56 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.37 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.06 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 90.86 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.36 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.43 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2003 |  |  |  | Data not provided
2004 |  |  |  | 5358.59 |  |  | 8236 |  |  |  | 665 | [10 empty] | 92.43 |  |  |  | 93.00 | [5 empty] | 91.74 |  |  | 93.76 |  |  |  | 2.84 |  | 2.72 | [8 empty] | 4.28 |  |  |  |  | 0.57
2005 |  |  |  | 4604.65 |  |  | 7014 |  |  |  | 665 | [10 empty] | 80.14 |  |  |  | 80.24 | [5 empty] | 79.04 |  |  | 80.07 |  |  |  | 0.90 |  | 0.73 | [8 empty] | 19.03 |  |  |  |  | 0.11
2006 |  |  |  | 5038.17 |  |  | 7721 |  |  |  | 650 | [10 empty] | 86.72 |  |  |  | 86.72 | [5 empty] | 88.48 |  |  | 88.14 |  |  |  | 0.25 |  | 0.22 | [8 empty] | 13.06 |  |  |  |  | 0.00
2007 |  |  |  | 5675.70 |  |  | 8559 |  |  |  | 650 | [10 empty] | 97.55 |  |  |  | 97.55 | [5 empty] | 99.68 |  |  | 97.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.45 |  |  |  |  | 0.00
2008 |  |  |  | 5083.41 |  |  | 7697 |  |  |  | 650 | [10 empty] | 87.21 |  |  |  | 87.32 | [5 empty] | 89.03 |  |  | 87.63 |  |  |  | 0.55 |  | 0.48 | [8 empty] | 12.20 |  |  |  |  | 0.11
2009 |  |  |  | 5523.74 |  |  | 8359 |  |  |  | 650 | [10 empty] | 95.36 |  |  |  | 95.36 | [5 empty] | 97.01 |  |  | 95.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.64 |  |  |  |  | 0.00
2010 |  |  |  | 5341.46 |  |  | 8099 |  |  |  | 650 | [10 empty] | 92.06 |  |  |  | 92.06 | [5 empty] | 93.81 |  |  | 92.45 |  |  |  | 1.93 |  | 1.82 | [8 empty] | 6.13 |  |  |  |  | 0.00
2011 |  |  |  | 5261.09 |  |  | 7951 |  |  |  | 650 | [10 empty] | 90.34 |  |  |  | 91.00 | [5 empty] | 92.40 |  |  | 90.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.00 |  |  |  |  | 0.66
2012 |  |  |  | 5210.75 |  |  | 7980 |  |  |  | 650 | [10 empty] | 90.44 |  |  |  | 90.44 | [5 empty] | 91.26 |  |  | 90.85 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 9.53 |  |  |  |  | 0.00
2013 |  |  |  | 5794.09 |  |  | 8760 |  |  |  | 650 | [10 empty] | 99.85 |  |  |  | 99.85 | [5 empty] | 101.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.15 |  |  |  |  | 0.00
2014 |  |  |  | 5223.32 |  |  | 7892 |  |  |  | 650 | [10 empty] | 89.99 |  |  |  | 89.99 | [5 empty] | 91.73 |  |  | 90.09 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 9.98 |  |  |  |  | 0.00
2015 |  |  |  | 5623.82 |  |  | 8553 |  |  |  | 677 | [10 empty] | 97.30 |  |  |  | 97.30 | [5 empty] | 94.83 |  |  | 97.64 |  |  |  | 2.69 |  | 2.69 | [8 empty] | 0.02 |  |  |  |  | 0.00
2016 |  |  |  | 4555.03 |  |  | 6979 |  |  |  | 677 | [10 empty] | 79.27 |  |  |  | 79.27 | [5 empty] | 76.60 |  |  | 79.45 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 20.71 |  |  |  |  | 0.00
2017 |  |  |  | 5598.62 |  |  | 8580 |  |  |  | 677 | [10 empty] | 98.19 |  |  |  | 99.96 | [5 empty] | 94.40 |  |  | 97.95 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.01 |  |  |  |  | 1.76
2018 |  |  |  | 4685.15 |  |  | 7183 |  |  |  | 677 | [10 empty] | 81.58 |  |  |  | 82.62 | [5 empty] | 79.00 |  |  | 82.00 |  |  |  | 0.94 |  | 0.78 | [8 empty] | 16.60 |  |  |  |  | 1.03
2019 |  |  |  | 5716.87 |  |  | 8686 |  |  |  | 677 | [10 empty] | 98.02 |  |  |  | 99.85 | [5 empty] | 96.40 |  |  | 99.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.15 |  |  |  |  | 1.83
2020 |  |  |  | 5261.05 |  |  | 8014 |  |  |  | 677 | [10 empty] | 91.04 |  |  |  | 91.04 | [5 empty] | 88.47 |  |  | 91.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.96 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2003 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 37
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 106
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 770 | [14 empty] | 573
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 21
L. |  | Human factor related | [39 empty] | 6
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 6
Subtotal | [22 empty] | 770 | [14 empty] | 679 |  |  |  | 43 | [11 empty] | 27
Total | [22 empty] | 770 | [14 empty] | 749
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2003 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 12
12. |  |  | Reactor I&C Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 10
16. |  |  | Steam generation systems | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [37 empty] | 46
Highlights (2020)
Unit was shutdown for 10th planned outage from April 30 to June 4.

## QINSHAN-1
2020 Operating Experience
CN-1 | [9 empty] | QINSHAN-1 | [28 empty] | CHINA
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | CNNO (CNNC Nuclear Operation Management Company Limited)
Owner | [8 empty] | : | QNPC (QINSHAN NUCLEAR POWER COMPANY)
Reactor Supplier | [8 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [8 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PWR / CNP-300 | [12 empty] | Construction Date | [16 empty] | : |  |  | 1985-03-20
Thermal power | [14 empty] | : |  |  | 966 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 1991-12-15
Gross electrical power | [14 empty] | : |  |  | 330 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 1994-04-01
Reference unit power (net) | [14 empty] | : |  |  | 308 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 29 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Vertical | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 308.5
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 2
| Refuelling type | [15 empty] | : |  |  | OFF-line | [12 empty] | Containment type | [16 empty] | : |  |  | Single
| Moderator material | [15 empty] | : |  |  | H2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 2.65
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | 3.4 | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | 12 | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 1
| Part of the core refuelled [%] | [15 empty] | : |  |  | 33.33 | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | 33000 | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | 2
| Active core diameter [m] | [15 empty] | : |  |  | 2.486 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 5.45
| Active core height/length [m] | [15 empty] | : |  |  | 2.9 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | 18
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 121 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 13.5 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | 3
| Number of control rod assemblies | [15 empty] | : |  |  | 37 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | 2
| Number of external reactor coolant loops | [15 empty] | : |  |  | 2 | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | 3
| Coolant type | [15 empty] | : |  |  | H2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [20 empty] | : | 2496.95 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 5.67 %
Energy Availability Factor (EAF) | [20 empty] | : | 92.28 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 5.54 %
Unit Capability Factor (UCF) | [20 empty] | : | 92.28 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 2.18 %
Load Factor (LF) | [20 empty] | : | 92.29 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0 %
Operating Factor (OF) | [20 empty] | : | 92.58 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 652 hours
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 232.06 |  | 137.88 |  |  |  |  | 243.41 |  | 232.19 | [8 empty] | 237.81 |  |  |  | 226.21 | [6 empty] | 234.27 |  | 79.74 |  |  |  |  | 226.50 |  |  | 229.57 |  |  | 235.08 | [9 empty] | 182.23 |  |  | 2496.95
EAF [%] |  |  |  |  | 99.69 |  | 100.00 |  |  |  |  | 99.95 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 34.61 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 74.60 |  |  | 92.28
UCF [%] |  |  |  |  | 99.69 |  | 100.00 |  |  |  |  | 99.95 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 34.61 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 74.60 |  |  | 92.28
LF [%] |  |  |  |  | 101.27 |  | 64.32 |  |  |  |  | 106.22 |  | 104.70 | [8 empty] | 103.78 |  |  |  | 102.01 | [6 empty] | 102.23 |  | 34.80 |  |  |  |  | 102.14 |  |  | 100.18 |  |  | 106.01 | [9 empty] | 79.52 |  |  | 92.29
OF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 36.69 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 75.67 |  |  | 92.58
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.05 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 65.39 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.67
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.05 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 65.39 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.54
PUF [%] |  |  |  |  | 0.31 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 25.40 |  |  | 2.18
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 59202.75 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 3.99 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 81.99 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 3.78 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 82.97 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 13.26 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 83.26 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.98 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 83.66 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 1648.58 |  |  |  | 6439 |  |  |  |  | 279 | [10 empty] | 62.02 |  |  |  |  | 67.45 | [5 empty] | 62.67 |  |  | 70.06 |  |  |  |  | 3.98 |  | 2.80 | [8 empty] | 29.75 |  |  |  |  | 5.44
1995 |  |  |  | 2063.90 |  |  |  | 7886 |  |  |  |  | 300 | [10 empty] | 82.32 |  |  |  |  | 86.80 | [5 empty] | 78.53 |  |  | 90.02 |  |  |  |  | 2.25 |  | 2.00 | [8 empty] | 11.20 |  |  |  |  | 4.49
1996 |  |  |  | 2073.72 |  |  |  | 7479 |  |  |  |  | 279 | [10 empty] | 81.19 |  |  |  |  | 81.19 | [5 empty] | 84.62 |  |  | 85.14 |  |  |  |  | 1.17 |  | 0.96 | [8 empty] | 17.85 |  |  |  |  | 0.00
1997 |  |  |  | 2011.67 |  |  |  | 7185 |  |  |  |  | 300 | [10 empty] | 76.11 |  |  |  |  | 81.78 | [5 empty] | 76.55 |  |  | 82.02 |  |  |  |  | 2.87 |  | 2.42 | [8 empty] | 15.80 |  |  |  |  | 5.67
1998 |  |  |  | 1149.49 |  |  |  | 4331 |  |  |  |  | 279 | [10 empty] | 42.59 |  |  |  |  | 48.78 | [5 empty] | 47.03 |  |  | 49.44 |  |  |  |  | 0.98 |  | 0.48 | [8 empty] | 50.74 |  |  |  |  | 6.19
1999 |  |  |  | 680.88 |  |  |  | 2519 |  |  |  |  | 279 | [10 empty] | 27.76 |  |  |  |  | 27.76 | [5 empty] | 27.86 |  |  | 28.76 |  |  |  |  | 71.97 |  | 71.28 | [8 empty] | 0.96 |  |  |  |  | 0.00
2000 |  |  |  | 2035.48 |  |  |  | 6840 |  |  |  |  | 300 | [10 empty] | 77.61 |  |  |  |  | 77.61 | [5 empty] | 77.24 |  |  | 77.87 |  |  |  |  | 2.79 |  | 2.23 | [8 empty] | 20.16 |  |  |  |  | 0.00
2001 |  |  |  | 2319.37 |  |  |  | 8370 |  |  |  |  | 279 | [10 empty] | 92.82 |  |  |  |  | 93.47 | [5 empty] | 94.90 |  |  | 95.55 |  |  |  |  | 0.51 |  | 0.48 | [8 empty] | 6.05 |  |  |  |  | 0.64
2002 |  |  |  | 1783.25 |  |  |  | 5989 |  |  |  |  | 279 | [10 empty] | 66.31 |  |  |  |  | 69.21 | [5 empty] | 72.96 |  |  | 68.37 |  |  |  |  | 1.40 |  | 0.98 | [8 empty] | 29.81 |  |  |  |  | 2.90
2003 |  |  |  | 2256.57 |  |  |  | 7798 |  |  |  |  | 288 | [10 empty] | 88.44 |  |  |  |  | 88.46 | [5 empty] | 89.44 |  |  | 89.02 |  |  |  |  | 0.24 |  | 0.21 | [8 empty] | 11.33 |  |  |  |  | 0.01
2004 |  |  |  | 2565.24 |  |  |  | 8784 |  |  |  |  | 288 | [10 empty] | 99.08 |  |  |  |  | 99.79 | [5 empty] | 101.40 |  |  | 100.00 |  |  |  |  | 0.11 |  | 0.11 | [8 empty] | 0.10 |  |  |  |  | 0.71
2005 |  |  |  | 2194.56 |  |  |  | 7693 |  |  |  |  | 288 | [10 empty] | 86.83 |  |  |  |  | 87.02 | [5 empty] | 86.99 |  |  | 87.82 |  |  |  |  | 0.53 |  | 0.46 | [8 empty] | 12.52 |  |  |  |  | 0.19
2006 |  |  |  | 2310.41 |  |  |  | 8086 |  |  |  |  | 288 | [10 empty] | 91.81 |  |  |  |  | 91.81 | [5 empty] | 91.58 |  |  | 92.31 |  |  |  |  | 0.05 |  | 0.29 | [8 empty] | 7.89 |  |  |  |  | 0.00
2007 |  |  |  | 2061.43 |  |  |  | 7218 |  |  |  |  | 288 | [10 empty] | 81.99 |  |  |  |  | 82.22 | [5 empty] | 81.71 |  |  | 82.40 |  |  |  |  | 0.10 |  | 0.08 | [8 empty] | 17.70 |  |  |  |  | 0.23
2008 |  |  |  | 2430.72 |  |  |  | 8434 |  |  |  |  | 288 | [10 empty] | 95.38 |  |  |  |  | 95.54 | [5 empty] | 96.08 |  |  | 96.02 |  |  |  |  | 1.02 |  | 2.99 | [8 empty] | 1.47 |  |  |  |  | 0.16
2009 |  |  |  | 2195.44 |  |  |  | 7704 |  |  |  |  | 288 | [10 empty] | 87.33 |  |  |  |  | 87.41 | [5 empty] | 87.02 |  |  | 87.95 |  |  |  |  | 2.20 |  | 1.96 | [8 empty] | 10.62 |  |  |  |  | 0.08
2010 |  |  |  | 2169.32 |  |  |  | 7398 |  |  |  |  | 298 | [10 empty] | 83.24 |  |  |  |  | 83.33 | [5 empty] | 84.27 |  |  | 84.45 |  |  |  |  | 0.47 |  | 6.03 | [8 empty] | 10.64 |  |  |  |  | 0.09
2011 |  |  |  | 2332.64 |  |  |  | 7762 |  |  |  |  | 298 | [10 empty] | 87.88 |  |  |  |  | 88.06 | [5 empty] | 89.36 |  |  | 88.61 |  |  |  |  | 0.41 |  | 1.20 | [8 empty] | 10.75 |  |  |  |  | 0.18
2012 |  |  |  | 2659.07 |  |  |  | 8784 |  |  |  |  | 298 | [10 empty] | 99.80 |  |  |  |  | 99.94 | [5 empty] | 101.58 |  |  | 100.00 |  |  |  |  | 0.02 |  | 0.02 | [8 empty] | 0.05 |  |  |  |  | 0.14
2013 |  |  |  | 2158.84 |  |  |  | 7199 |  |  |  |  | 298 | [10 empty] | 80.86 |  |  |  |  | 80.98 | [5 empty] | 82.70 |  |  | 82.18 |  |  |  |  | 0.02 |  | 0.02 | [8 empty] | 19.00 |  |  |  |  | 0.12
2014 |  |  |  | 2461.14 |  |  |  | 8221 |  |  |  |  | 298 | [10 empty] | 92.93 |  |  |  |  | 92.93 | [5 empty] | 94.28 |  |  | 93.85 |  |  |  |  | 2.07 |  | 1.97 | [8 empty] | 5.10 |  |  |  |  | 0.00
2015 |  |  |  | 2413.17 |  |  |  | 8003 |  |  |  |  | 298 | [10 empty] | 91.14 |  |  |  |  | 91.14 | [5 empty] | 92.44 |  |  | 91.36 |  |  |  |  | 0.11 |  | 0.10 | [8 empty] | 8.76 |  |  |  |  | 0.00
2016 |  |  |  | 2418.29 |  |  |  | 8084 |  |  |  |  | 298 | [10 empty] | 91.75 |  |  |  |  | 91.75 | [5 empty] | 92.38 |  |  | 92.03 |  |  |  |  | 0.02 |  | 0.02 | [8 empty] | 8.23 |  |  |  |  | 0.00
2017 |  |  |  | 2615.97 |  |  |  | 8760 |  |  |  |  | 298 | [10 empty] | 99.37 |  |  |  |  | 99.96 | [5 empty] | 100.21 |  |  | 100.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  |  |  | 0.60
2018 |  |  |  | 1509.11 |  |  |  | 5147 |  |  |  |  | 298 | [10 empty] | 55.80 |  |  |  |  | 55.80 | [5 empty] | 57.81 |  |  | 58.76 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 44.20 |  |  |  |  | 0.00
2019 |  |  |  | 2447.78 |  |  |  | 7782 |  |  |  |  | 298 | [10 empty] | 88.27 |  |  |  |  | 88.27 | [5 empty] | 93.77 |  |  | 88.84 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.73 |  |  |  |  | 0.00
2020 |  |  |  | 2496.95 |  |  |  | 8132 |  |  |  |  | 308 | [10 empty] | 92.28 |  |  |  |  | 92.28 | [5 empty] | 92.29 |  |  | 92.58 |  |  |  |  | 5.67 |  | 5.54 | [8 empty] | 2.18 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2020 | [16 empty] | 1994 to 2020
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [27 empty] | 471 | [15 empty] | 77
C. |  | Inspection, maintenance or repair combined with refuelling | [22 empty] | 180 | [16 empty] | 1058
D. |  | Inspection, maintenance or repair without refuelling | [39 empty] | 47
E. |  | Testing of plant systems or components | [22 empty] | 2 | [16 empty] | 0 |  |  |  | 2
L. |  | Human factor related | [43 empty] | 14
Z. |  | Other | [43 empty] | 232 | [11 empty] | 2
Subtotal | [24 empty] | 182 |  |  |  |  | 471 | [11 empty] | 1105 |  |  |  | 325 | [11 empty] | 2
Total | [24 empty] | 653 | [16 empty] | 1432
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2020 | [16 empty] | 1994 to 2020
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [38 empty] | 17
12. |  |  | Reactor I&C Systems | [38 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [38 empty] | 3
15. |  |  | Reactor Cooling Systems | [38 empty] | 7
16. |  |  | Steam generation systems | [38 empty] | 0
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [38 empty] | 1
31. |  |  | Turbine and auxiliaries | [38 empty] | 5
32. |  |  | Feedwater and Main Steam System | [38 empty] | 10
33. |  |  | Circulating Water System | [38 empty] | 3
34. |  |  | Miscellaneous Systems | [38 empty] | 2
35. |  |  | All other I&C Systems | [38 empty] | 1
41. |  |  | Main Generator Systems | [21 empty] | 471 | [16 empty] | 18
Total | [24 empty] | 471 | [16 empty] | 79
RUP revision during the year (2020) due to power uprate
RUP at the end of previous year : 298 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
January | [5 empty] | 308 |  |  |  |  | Extended power uprate (>7%) | [14 empty] | Balance of plant | [13 empty] | power Uprate

## SANMEN-1
2020 Operating Experience
CN-28 | [8 empty] | SANMEN-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SMNPC (SANMEN NUCLEAR POWER CO., LTD.)
Owner | [7 empty] | : | SMNPC (SANMEN NUCLEAR POWER CO., LTD.)
Reactor Supplier | [7 empty] | : | WH/MHI (WESTINGHOUSE ELECTRIC CORPORATION / MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / AP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-04-19
Thermal power | [12 empty] | : |  |  | 3400 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-06-30
Gross electrical power | [12 empty] | : |  |  | 1251 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-09-21
Reference unit power (net) | [12 empty] | : |  |  | 1157 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.407
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.7239 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.8 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50558 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.77 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 69 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8757.82 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 6.47 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.29 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 6.09 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.13 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.78 %
Load Factor (LF) | [18 empty] | : | 86.17 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.84 %
Operating Factor (OF) | [18 empty] | : | 89.16 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 952 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 263.41 | 714.42 |  |  |  | 860.81 |  | 829.46 | [8 empty] | 232.46 |  |  | 820.03 | [6 empty] | 837.41 |  | 833.22 |  |  |  | 814.78 |  |  | 858.09 |  |  | 833.00 | [9 empty] | 860.73 |  |  | 8757.82
EAF [%] |  |  |  |  | 31.84 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 27.98 |  |  | 98.44 | [6 empty] | 97.28 |  | 96.80 |  |  |  | 97.81 |  |  | 99.68 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 87.29
UCF [%] |  |  |  |  | 31.84 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 28.05 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 88.13
LF [%] |  |  |  |  | 30.60 | 88.72 |  |  |  | 100.00 |  | 99.57 | [8 empty] | 27.00 |  |  | 98.44 | [6 empty] | 97.28 |  | 96.80 |  |  |  | 97.81 |  |  | 99.68 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 86.17
OF [%] |  |  |  |  | 42.20 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 29.84 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.16
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 71.95 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.47
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 71.95 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.09
PUF [%] |  |  |  |  | 68.16 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 5.78
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.07 |  |  | 1.56 | [6 empty] | 2.71 |  | 3.20 |  |  |  | 2.19 |  |  | 0.31 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.84
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 21075.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.88 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.4 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.71 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.76 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.89 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 3330.63 |  |  | 3840 |  |  |  | 1157 | [10 empty] | 99.85 |  |  |  | 99.98 | [5 empty] | 99.39 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.13
2019 |  |  |  | 8987.29 |  |  | 7909 |  |  |  | 1157 | [10 empty] | 91.14 |  |  |  | 92.26 | [5 empty] | 88.67 |  |  | 90.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.74 |  |  |  |  | 1.12
2020 |  |  |  | 8757.82 |  |  | 7832 |  |  |  | 1157 | [10 empty] | 87.29 |  |  |  | 88.13 | [5 empty] | 86.17 |  |  | 89.16 |  |  |  | 6.47 |  | 6.09 | [8 empty] | 5.78 |  |  |  |  | 0.84
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2018 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 522 | [14 empty] | 232
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 429 | [14 empty] | 491
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 126
E. |  | Testing of plant systems or components | [35 empty] | 138
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 77
Subtotal | [22 empty] | 429 |  |  |  | 522 | [10 empty] | 755 |  |  |  | 232 | [11 empty] | 77
Total | [22 empty] | 951 | [14 empty] | 1064
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2018 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [19 empty] | 522 | [14 empty] | 202
Total | [22 empty] | 522 | [14 empty] | 202

## SANMEN-2
2020 Operating Experience
CN-29 | [8 empty] | SANMEN-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SMNPC (SANMEN NUCLEAR POWER CO., LTD.)
Owner | [7 empty] | : | SMNPC (SANMEN NUCLEAR POWER CO., LTD.)
Reactor Supplier | [7 empty] | : | WH/MHI (WESTINGHOUSE ELECTRIC CORPORATION / MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / AP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-12-15
Thermal power | [12 empty] | : |  |  | 3400 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-08-24
Gross electrical power | [12 empty] | : |  |  | 1251 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-11-05
Reference unit power (net) | [12 empty] | : |  |  | 1157 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.407
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.7239 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.8 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50558 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.77 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 69 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8786.18 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.25 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.99 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 86.45 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.74 %
Operating Factor (OF) | [18 empty] | : | 89.61 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 913 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 575.52 | 63.32 |  |  |  | 860.81 |  | 829.48 | [8 empty] | 849.90 |  |  | 819.76 | [6 empty] | 837.03 |  | 832.50 |  |  |  | 814.20 |  |  | 801.71 |  |  | 703.77 | [9 empty] | 798.18 |  |  | 8786.18
EAF [%] |  |  |  |  | 99.88 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.98 |  |  | 98.41 | [6 empty] | 97.24 |  | 96.71 |  |  |  | 97.74 |  |  | 99.71 |  |  | 84.48 | [9 empty] | 92.72 |  |  | 97.25
UCF [%] |  |  |  |  | 99.88 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.98 |  |  | 100.00 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 99.99
LF [%] |  |  |  |  | 66.86 | 7.86 |  |  |  | 100.00 |  | 99.57 | [8 empty] | 98.73 |  |  | 98.41 | [6 empty] | 97.24 |  | 96.71 |  |  |  | 97.74 |  |  | 93.14 |  |  | 84.48 | [9 empty] | 92.72 |  |  | 86.45
OF [%] |  |  |  |  | 68.01 | 9.77 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 93.68 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.61
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.12 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.59 | [6 empty] | 2.75 |  | 3.29 |  |  |  | 2.26 |  |  | 0.29 |  |  | 15.51 | [9 empty] | 7.27 |  |  | 2.74
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 11944.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 43 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 55.62 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 42.92 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 56.88 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0.2 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 50.68 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.27 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 52.27 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 2252.77 |  |  | 2381 |  |  |  | 1157 | [10 empty] | 85.14 |  |  |  | 85.14 | [5 empty] | 85.84 |  |  | 85.18 |  |  |  | 14.85 |  | 14.84 | [8 empty] | 0.02 |  |  |  |  | 0.00
2019 |  |  |  | 905.96 |  |  | 817 |  |  |  | 1157 | [10 empty] | 8.94 |  |  |  | 8.94 | [5 empty] | 8.94 |  |  | 9.33 |  |  |  | 91.02 |  | 90.64 | [8 empty] | 0.42 |  |  |  |  | 0.00
2020 |  |  |  | 8786.18 |  |  | 7871 |  |  |  | 1157 | [10 empty] | 97.25 |  |  |  | 99.99 | [5 empty] | 86.45 |  |  | 89.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 2.74
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2018 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 3765
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 145
E. |  | Testing of plant systems or components | [35 empty] | 89
O. |  | Load dispatching, prioritization | [31 empty] | 913 | [19 empty] | 421
Subtotal | [33 empty] | 913 |  |  |  | 234 |  |  |  | 3765 | [11 empty] | 421
Total | [22 empty] | 913 | [14 empty] | 4420
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2018 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 3376
Total | [37 empty] | 3376

## TAISHAN-1
2020 Operating Experience
CN-32 | [8 empty] | TAISHAN-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TNPJVC (Taishan Nuclear Power Joint Venture Company Limited)
Owner | [7 empty] | : | TNPJVC (Taishan Nuclear Power Joint Venture Company Limited)
Reactor Supplier | [7 empty] | : | ORANO (ORANO)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / EPR-1750 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-11-18
Thermal power | [12 empty] | : |  |  | 4590 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-06-29
Gross electrical power | [12 empty] | : |  |  | 1750 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-12-13
Reference unit power (net) | [12 empty] | : |  |  | 1660 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.55
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.98 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 29.88 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 59000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.657 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | NA
| Active core height/length [m] | [13 empty] | : |  |  | 4.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 6
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9169.83 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.53 %
Energy Availability Factor (EAF) | [18 empty] | : | 70.53 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.49 %
Unit Capability Factor (UCF) | [18 empty] | : | 71.56 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.95 %
Load Factor (LF) | [18 empty] | : | 62.89 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.03 %
Operating Factor (OF) | [18 empty] | : | 72.6 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2407 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 742.41 | 620.98 |  |  |  | 1089.20 |  | 1158.14 | [8 empty] | 1185.79 |  |  | 1035.69 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 80.54 |  |  | 930.59 |  |  | 1096.94 | [9 empty] | 1229.57 |  |  | 9169.83
EAF [%] |  |  |  |  | 84.40 | 96.98 |  |  |  | 99.09 |  | 99.13 | [8 empty] | 98.18 |  |  | 86.65 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 6.74 |  |  | 83.59 |  |  | 93.91 | [9 empty] | 99.56 |  |  | 70.53
UCF [%] |  |  |  |  | 84.41 | 96.98 |  |  |  | 99.09 |  | 99.99 | [8 empty] | 99.93 |  |  | 93.70 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 7.44 |  |  | 84.87 |  |  | 94.67 | [9 empty] | 99.56 |  |  | 71.56
LF [%] |  |  |  |  | 60.11 | 53.75 |  |  |  | 88.19 |  | 96.90 | [8 empty] | 96.01 |  |  | 86.65 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 6.74 |  |  | 75.35 |  |  | 91.78 | [9 empty] | 99.56 |  |  | 62.89
OF [%] |  |  |  |  | 74.19 | 84.34 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 94.03 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 20.14 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 72.60
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.91 |  | 0.00 | [8 empty] | 0.06 |  |  | 0.04 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 3.49 |  |  | 0.46 | [9 empty] | 0.00 |  |  | 0.53
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.91 |  | 0.00 | [8 empty] | 0.06 |  |  | 0.03 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 25.78 |  |  | 3.07 |  |  | 0.44 | [9 empty] | 0.00 |  |  | 2.49
PUF [%] |  |  |  |  | 15.59 | 3.02 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 6.27 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 66.79 |  |  | 12.06 |  |  | 4.89 | [9 empty] | 0.44 |  |  | 25.95
XUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.87 | [8 empty] | 1.75 |  |  | 7.05 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.70 |  |  | 1.28 |  |  | 0.76 | [9 empty] | 0.00 |  |  | 1.03
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 24178.65 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.62 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.79 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.28 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.98 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.49 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.79 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 3056.09 |  |  | 3958 |  |  |  | 1660 | [10 empty] | 84.52 |  |  |  | 84.52 | [5 empty] | 83.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.48 |  |  |  |  | 0.00
2019 |  |  |  | 11952.73 |  |  | 7836 |  |  |  | 1660 | [10 empty] | 90.77 |  |  |  | 90.77 | [5 empty] | 82.20 |  |  | 89.45 |  |  |  | 0.73 |  | 2.26 | [8 empty] | 6.97 |  |  |  |  | 0.00
2020 |  |  |  | 9169.83 |  |  | 6377 |  |  |  | 1660 | [10 empty] | 70.53 |  |  |  | 71.56 | [5 empty] | 62.89 |  |  | 72.60 |  |  |  | 0.53 |  | 2.49 | [8 empty] | 25.95 |  |  |  |  | 1.03
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2018 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 107
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1920 | [14 empty] | 922
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 137 | [14 empty] | 335
E. |  | Testing of plant systems or components | [35 empty] | 15
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 164 | [19 empty] | 159
L. |  | Human factor related | [39 empty] | 206
Z. |  | Other | [24 empty] | 186 | [14 empty] | 89
Subtotal | [22 empty] | 2057 |  |  |  | 186 | [6 empty] | 164 |  |  |  | 1272 |  |  |  | 402 | [11 empty] | 159
Total | [22 empty] | 2407 | [14 empty] | 1833
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2018 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 30
16. |  |  | Steam generation systems | [34 empty] | 31
31. |  |  | Turbine and auxiliaries | [34 empty] | 32
32. |  |  | Feedwater and Main Steam System | [34 empty] | 120
33. |  |  | Circulating Water System | [34 empty] | 36
34. |  |  | Miscellaneous Systems | [19 empty] | 349 | [14 empty] | 135
Total | [22 empty] | 349 | [14 empty] | 386
Highlights (2020)
There was no unplanned shutdown and scram in CN32 in 2020, and CN32 shutdown for T101 outage from June to Spetember. CN32 reduced power daily and during holiday according to the requirement of the Grid.

## TAISHAN-2
2020 Operating Experience
CN-33 | [8 empty] | TAISHAN-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TNPJVC (Taishan Nuclear Power Joint Venture Company Limited)
Owner | [7 empty] | : | TNPJVC (Taishan Nuclear Power Joint Venture Company Limited)
Reactor Supplier | [7 empty] | : | ORANO (ORANO)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / EPR-1750 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-04-15
Thermal power | [12 empty] | : |  |  | 4590 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-06-23
Gross electrical power | [12 empty] | : |  |  | 1750 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | :
Reference unit power (net) | [12 empty] | : |  |  | 1660 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.55
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.98 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 29.8755 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 59000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.657 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | NA
| Active core height/length [m] | [13 empty] | : |  |  | 4.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 6
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 12454.8 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 117 hours
Annual Summary
[5 empty] | Jan | Oct |  |  |  | Nov |  | Dec | [8 empty] | Feb |  |  | Mar | [6 empty] | Apr |  | May |  |  |  | Jun |  |  | Jul |  |  | Aug | [9 empty] | Sep
GW(e)-h
EAF [%]
UCF [%]
LF [%]
OF [%]
FLR [%]
UCL [%]
PUF [%]
XUF [%]
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 17810.94 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 0 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 63
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 54
Subtotal | [22 empty] | 63 | [10 empty] | 54
Total | [22 empty] | 117 | [14 empty] | 0
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [19 empty] | 54 | [14 empty] | 79
Total | [22 empty] | 54 | [14 empty] | 79
Highlights (2020)
There was no unplanned shutdown and scram in CN33 in 2020, and CN33 shutdown according to the requirement of the Grid during National holiday. CN33 reduced power dailiy and during holiday according to the requirement of the Grid.

## TIANWAN-1
2020 Operating Experience
CN-10 | [8 empty] | TIANWAN-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | IZ (Izhorskiye Zavody)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-428 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1999-10-20
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2006-05-12
Gross electrical power | [12 empty] | : |  |  | 1060 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2007-05-17
Reference unit power (net) | [12 empty] | : |  |  | 990 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 14 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 4
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.78
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 103 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7424.97 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.31 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.31 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.69 %
Load Factor (LF) | [18 empty] | : | 85.38 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 89.41 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 930 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 700.11 | 586.01 |  |  |  | 735.87 |  | 696.78 | [8 empty] | 0.00 |  |  | 557.68 | [6 empty] | 729.03 |  | 727.06 |  |  |  | 707.89 |  |  | 726.32 |  |  | 543.07 | [9 empty] | 715.18 |  |  | 7424.97
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 97.59 | [8 empty] | 0.00 |  |  | 75.27 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.31
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 97.59 | [8 empty] | 0.00 |  |  | 75.27 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.31
LF [%] |  |  |  |  | 95.05 | 85.05 |  |  |  | 99.91 |  | 97.75 | [8 empty] | 0.00 |  |  | 78.24 | [6 empty] | 98.98 |  | 98.71 |  |  |  | 99.31 |  |  | 98.61 |  |  | 76.19 | [9 empty] | 97.10 |  |  | 85.38
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 98.89 | [8 empty] | 0.00 |  |  | 75.28 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.41
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 2.41 | [8 empty] | 100.00 |  |  | 24.71 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.69
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 102764.97 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.64 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.67 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.76 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.57 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.33 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.13 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2007 |  |  |  | 5311.00 |  |  | 5688 |  |  |  | 933 | [10 empty] | 82.44 |  |  |  | 82.44 | [5 empty] | 84.77 |  |  | 82.71 |  |  |  | 0.44 |  | 0.36 | [8 empty] | 17.20 |  |  |  |  | 0.00
2008 |  |  |  | 6116.16 |  |  | 6270 |  |  |  | 933 | [10 empty] | 70.97 |  |  |  | 70.97 | [5 empty] | 74.63 |  |  | 71.38 |  |  |  | 3.60 |  | 2.65 | [8 empty] | 26.38 |  |  |  |  | 0.00
2009 |  |  |  | 6337.71 |  |  | 6553 |  |  |  | 933 | [10 empty] | 74.12 |  |  |  | 74.12 | [5 empty] | 77.54 |  |  | 74.81 |  |  |  | 0.97 |  | 0.73 | [8 empty] | 25.16 |  |  |  |  | 0.00
2010 |  |  |  | 7539.59 |  |  | 7643 |  |  |  | 933 | [10 empty] | 87.02 |  |  |  | 87.02 | [5 empty] | 92.25 |  |  | 87.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.98 |  |  |  |  | 0.00
2011 |  |  |  | 7470.08 |  |  | 7606 |  |  |  | 990 | [10 empty] | 86.55 |  |  |  | 86.55 | [5 empty] | 86.14 |  |  | 86.83 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 13.39 |  |  |  |  | 0.00
2012 |  |  |  | 7550.16 |  |  | 7635 |  |  |  | 990 | [10 empty] | 86.78 |  |  |  | 86.78 | [5 empty] | 86.82 |  |  | 86.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.22 |  |  |  |  | 0.00
2013 |  |  |  | 7869.05 |  |  | 7959 |  |  |  | 990 | [10 empty] | 90.71 |  |  |  | 90.71 | [5 empty] | 90.74 |  |  | 90.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.29 |  |  |  |  | 0.00
2014 |  |  |  | 7766.80 |  |  | 7888 |  |  |  | 990 | [10 empty] | 89.83 |  |  |  | 89.83 | [5 empty] | 89.56 |  |  | 90.05 |  |  |  | 0.09 |  | 0.44 | [8 empty] | 9.73 |  |  |  |  | 0.00
2015 |  |  |  | 7894.21 |  |  | 7996 |  |  |  | 990 | [10 empty] | 91.07 |  |  |  | 91.07 | [5 empty] | 91.03 |  |  | 91.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.92 |  |  |  |  | 0.00
2016 |  |  |  | 7027.54 |  |  | 7295 |  |  |  | 990 | [10 empty] | 81.71 |  |  |  | 81.71 | [5 empty] | 80.81 |  |  | 83.05 |  |  |  | 0.90 |  | 0.74 | [8 empty] | 17.54 |  |  |  |  | 0.00
2017 |  |  |  | 7869.01 |  |  | 8081 |  |  |  | 990 | [10 empty] | 91.25 |  |  |  | 92.05 | [5 empty] | 90.74 |  |  | 92.25 |  |  |  | 0.40 |  | 0.37 | [8 empty] | 7.58 |  |  |  |  | 0.80
2018 |  |  |  | 7074.55 |  |  | 7450 |  |  |  | 990 | [10 empty] | 89.28 |  |  |  | 89.91 | [5 empty] | 81.58 |  |  | 85.05 |  |  |  | 3.66 |  | 3.42 | [8 empty] | 6.67 |  |  |  |  | 0.64
2019 |  |  |  | 8254.54 |  |  | 8501 |  |  |  | 990 | [10 empty] | 98.43 |  |  |  | 98.68 | [5 empty] | 95.18 |  |  | 97.04 |  |  |  | 0.52 |  | 0.52 | [8 empty] | 0.80 |  |  |  |  | 0.25
2020 |  |  |  | 7424.97 |  |  | 7854 |  |  |  | 990 | [10 empty] | 89.31 |  |  |  | 89.31 | [5 empty] | 85.38 |  |  | 89.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.69 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2007 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 0 | [14 empty] | 49
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 934 | [14 empty] | 990
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 102
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 45
L. |  | Human factor related | [39 empty] | 2
Subtotal | [22 empty] | 934 |  |  |  | 0 | [10 empty] | 1092 |  |  |  | 51 | [11 empty] | 45
Total | [22 empty] | 934 | [14 empty] | 1188
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2007 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 4
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [19 empty] | 0 | [14 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 21
42. |  |  | Electrical Power Supply Systems | [34 empty] | 18
Total | [22 empty] | 0 | [14 empty] | 47
Highlights (2020)
This year, Unit 1 experienced the 12th refueling outage, cooperated with the power grid to reduce power for many times, and other time maintained power operation. The details are as follows: at 12:00 on April 30, 2020, the unit shut down and began refueling outage. At 00:50 on June 7, 2020, the unit was connected to the grid and the outage ended smoothly.

## TIANWAN-2
2020 Operating Experience
CN-11 | [8 empty] | TIANWAN-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | IZ (Izhorskiye Zavody)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-428 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2000-09-20
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2007-05-14
Gross electrical power | [12 empty] | : |  |  | 1060 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2007-08-16
Reference unit power (net) | [12 empty] | : |  |  | 990 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 13 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.49 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 4
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.78
| Active core height/length [m] | [13 empty] | : |  |  | 3.68 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 103 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7991.08 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.25 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.32 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.25 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.32 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 1.43 %
Load Factor (LF) | [18 empty] | : | 91.89 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 98.85 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 101 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 736.36 | 334.47 |  |  |  | 732.84 |  | 688.23 | [8 empty] | 718.25 |  |  | 695.97 | [6 empty] | 607.76 |  | 736.56 |  |  |  | 705.30 |  |  | 723.88 |  |  | 711.39 | [9 empty] | 600.07 |  |  | 7991.08
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 97.09 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 83.09 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.32
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 97.09 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 83.09 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.32
LF [%] |  |  |  |  | 99.97 | 48.54 |  |  |  | 99.49 |  | 96.55 | [8 empty] | 97.51 |  |  | 97.64 | [6 empty] | 82.51 |  | 100.00 |  |  |  | 98.95 |  |  | 98.28 |  |  | 99.80 | [9 empty] | 81.47 |  |  | 91.89
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 86.42 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.85
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 2.91 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.25
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 2.91 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.25
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 16.91 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.43
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 102371.08 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.15 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.2 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.13 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.33 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.78 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.13 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2007 |  |  |  | 3974.00 |  |  | 4471 |  |  |  | 958 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.13 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 7003.03 |  |  | 7193 |  |  |  | 933 | [10 empty] | 81.20 |  |  |  | 81.20 | [5 empty] | 85.45 |  |  | 81.89 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 18.77 |  |  |  |  | 0.00
2009 |  |  |  | 6943.40 |  |  | 7054 |  |  |  | 933 | [10 empty] | 80.69 |  |  |  | 80.69 | [5 empty] | 84.95 |  |  | 80.53 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 19.29 |  |  |  |  | 0.00
2010 |  |  |  | 7131.13 |  |  | 7260 |  |  |  | 933 | [10 empty] | 82.28 |  |  |  | 82.28 | [5 empty] | 87.25 |  |  | 82.88 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 17.65 |  |  |  |  | 0.00
2011 |  |  |  | 7546.20 |  |  | 7658 |  |  |  | 990 | [10 empty] | 87.05 |  |  |  | 87.05 | [5 empty] | 87.01 |  |  | 87.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.95 |  |  |  |  | 0.00
2012 |  |  |  | 7640.12 |  |  | 7722 |  |  |  | 990 | [10 empty] | 87.77 |  |  |  | 87.77 | [5 empty] | 87.86 |  |  | 87.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.23 |  |  |  |  | 0.00
2013 |  |  |  | 7741.45 |  |  | 7837 |  |  |  | 990 | [10 empty] | 89.14 |  |  |  | 89.14 | [5 empty] | 89.27 |  |  | 89.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.86 |  |  |  |  | 0.00
2014 |  |  |  | 7901.45 |  |  | 7950 |  |  |  | 990 | [10 empty] | 91.10 |  |  |  | 91.10 | [5 empty] | 91.11 |  |  | 90.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.90 |  |  |  |  | 0.00
2015 |  |  |  | 7666.57 |  |  | 7790 |  |  |  | 990 | [10 empty] | 88.22 |  |  |  | 88.22 | [5 empty] | 88.40 |  |  | 88.93 |  |  |  | 0.87 |  | 0.77 | [8 empty] | 11.01 |  |  |  |  | 0.00
2016 |  |  |  | 7326.45 |  |  | 7705 |  |  |  | 990 | [10 empty] | 87.36 |  |  |  | 87.36 | [5 empty] | 84.25 |  |  | 87.72 |  |  |  | 0.50 |  | 0.44 | [8 empty] | 12.20 |  |  |  |  | 0.00
2017 |  |  |  | 8201.96 |  |  | 8430 |  |  |  | 990 | [10 empty] | 98.97 |  |  |  | 99.90 | [5 empty] | 94.58 |  |  | 96.23 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.07 |  |  |  |  | 0.93
2018 |  |  |  | 7661.18 |  |  | 8007 |  |  |  | 990 | [10 empty] | 91.64 |  |  |  | 92.22 | [5 empty] | 88.34 |  |  | 91.40 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 7.72 |  |  |  |  | 0.58
2019 |  |  |  | 7644.10 |  |  | 7833 |  |  |  | 990 | [10 empty] | 91.13 |  |  |  | 91.30 | [5 empty] | 88.14 |  |  | 89.42 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 8.62 |  |  |  |  | 0.17
2020 |  |  |  | 7991.08 |  |  | 8683 |  |  |  | 990 | [10 empty] | 98.32 |  |  |  | 98.32 | [5 empty] | 91.89 |  |  | 98.85 |  |  |  | 0.25 |  | 0.25 | [8 empty] | 1.43 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2007 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 22 | [14 empty] | 4
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 801
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 116 | [14 empty] | 129
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 49
L. |  | Human factor related | [39 empty] | 3
Subtotal | [22 empty] | 116 |  |  |  | 22 | [10 empty] | 930 |  |  |  | 7 | [11 empty] | 49
Total | [22 empty] | 138 | [14 empty] | 986
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2007 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [19 empty] | 22 | [14 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 2
Total | [22 empty] | 22 | [14 empty] | 7
Highlights (2020)
In this year, unit 2 experienced a minor repair event of manual disconnection with the power grid, cooperated with the power grid to reduce power for many times, and other units kept power operation. The details are as follows: at 20:00 on July 13, 2020, the unit shut down and started minor repair. At 16:27 on July 18, 2020, the unit was connected to the grid and the minor repair was successfully completed.

## TIANWAN-3
2020 Operating Experience
CN-45 | [8 empty] | TIANWAN-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | IZ (Izhorskiye Zavody)
Turbine Supplier | [7 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-428M | [11 empty] | Construction Date | [15 empty] | : |  |  | 2012-12-27
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2017-12-30
Gross electrical power | [12 empty] | : |  |  | 1126 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-02-14
Reference unit power (net) | [12 empty] | : |  |  | 1045 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.49
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | NA | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.88
| Active core height/length [m] | [13 empty] | : |  |  | NA | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | NA | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 103 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6896.21 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.7 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.29 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.71 %
Load Factor (LF) | [18 empty] | : | 75.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.58 %
Operating Factor (OF) | [18 empty] | : | 86.65 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1173 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 734.67 | 349.45 |  |  |  | 474.13 |  | 243.35 | [8 empty] | 754.21 |  |  | 738.95 | [6 empty] | 754.16 |  | 776.78 |  |  |  | 264.05 |  |  | 441.77 |  |  | 639.48 | [9 empty] | 725.19 |  |  | 6896.21
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 62.55 |  | 32.88 | [8 empty] | 100.00 |  |  | 97.94 | [6 empty] | 99.92 |  | 96.79 |  |  |  | 98.16 |  |  | 99.75 |  |  | 99.94 | [9 empty] | 100.00 |  |  | 90.70
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 62.55 |  | 32.88 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.92 |  | 99.91 |  |  |  | 100.00 |  |  | 99.75 |  |  | 99.94 | [9 empty] | 100.00 |  |  | 91.29
LF [%] |  |  |  |  | 94.49 | 48.05 |  |  |  | 60.98 |  | 32.34 | [8 empty] | 97.01 |  |  | 98.21 | [6 empty] | 97.00 |  | 99.91 |  |  |  | 35.09 |  |  | 56.82 |  |  | 84.99 | [9 empty] | 93.27 |  |  | 75.13
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 63.17 |  | 37.92 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 37.22 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.65
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 37.45 |  | 67.12 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.08 |  | 0.09 |  |  |  | 0.00 |  |  | 0.25 |  |  | 0.06 | [9 empty] | 0.00 |  |  | 8.71
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.06 | [6 empty] | 0.00 |  | 3.12 |  |  |  | 1.84 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.58
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 20970.21 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.5 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.5 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.25 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.92 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.83 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.31 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.42 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.61 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 6922.47 |  |  | 7704 |  |  |  | 1045 | [10 empty] | 90.85 |  |  |  | 91.48 | [5 empty] | 78.83 |  |  | 86.83 |  |  |  | 7.27 |  | 7.18 | [8 empty] | 1.34 |  |  |  |  | 0.63
2019 |  |  |  | 7149.36 |  |  | 7055 |  |  |  | 1045 | [10 empty] | 81.24 |  |  |  | 81.29 | [5 empty] | 78.10 |  |  | 80.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.71 |  |  |  |  | 0.05
2020 |  |  |  | 6896.21 |  |  | 7611 |  |  |  | 1045 | [10 empty] | 90.70 |  |  |  | 91.29 | [5 empty] | 75.13 |  |  | 86.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.71 |  |  |  |  | 0.58
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2018 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 171
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 722 | [14 empty] | 803
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 464 | [19 empty] | 371
Subtotal | [22 empty] | 722 | [10 empty] | 464 |  |  |  | 803 |  |  |  | 171 | [11 empty] | 371
Total | [22 empty] | 1186 | [14 empty] | 1345
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2018 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 122
16. |  |  | Steam generation systems | [34 empty] | 44
34. |  |  | Miscellaneous Systems | [19 empty] | 464 | [14 empty] | 155
Total | [22 empty] | 464 | [14 empty] | 321
Highlights (2020)
Unit 3 has undergone the second refuelling outage in this year, and according to the Jiangsu Province ,the unit reduced the power for many times. The details are as follows: At 11:40 on March 20, 2020, the unit was shut down and started the first refuelling outage; at 13:16 on April 19, 2020, the unit was successfully connected to the grid.

## TIANWAN-4
2020 Operating Experience
CN-46 | [8 empty] | TIANWAN-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | IZ (Izhorskiye Zavody)
Turbine Supplier | [7 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-428M | [11 empty] | Construction Date | [15 empty] | : |  |  | 2013-09-27
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-10-27
Gross electrical power | [12 empty] | : |  |  | 1126 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-12-22
Reference unit power (net) | [12 empty] | : |  |  | 1045 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.49
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | NA | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.88
| Active core height/length [m] | [13 empty] | : |  |  | NA | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | NA | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 103 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7033.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.17 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.17 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.8 %
Load Factor (LF) | [18 empty] | : | 76.63 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 79.72 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1781 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 538.09 | 273.09 |  |  |  | 10.97 |  | 752.40 | [8 empty] | 704.87 |  |  | 719.06 | [6 empty] | 753.12 |  | 777.37 |  |  |  | 645.59 |  |  | 731.24 |  |  | 757.05 | [9 empty] | 370.83 |  |  | 7033.68
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 95.56 | [8 empty] | 99.86 |  |  | 99.84 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 100.00 |  |  | 99.93 |  |  | 100.00 | [9 empty] | 47.70 |  |  | 95.17
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 95.56 | [8 empty] | 99.86 |  |  | 99.84 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 100.00 |  |  | 99.93 |  |  | 100.00 | [9 empty] | 47.70 |  |  | 95.17
LF [%] |  |  |  |  | 69.21 | 37.55 |  |  |  | 1.41 |  | 100.00 | [8 empty] | 90.66 |  |  | 95.57 | [6 empty] | 96.87 |  | 99.99 |  |  |  | 85.80 |  |  | 94.05 |  |  | 100.62 | [9 empty] | 47.70 |  |  | 76.63
OF [%] |  |  |  |  | 71.91 | 39.37 |  |  |  | 1.34 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 95.83 |  |  | 100.00 | [9 empty] | 48.25 |  |  | 79.72
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.14 |  |  | 0.16 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.14 |  |  | 0.16 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 4.44 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.00 |  |  | 0.07 |  |  | 0.00 | [9 empty] | 52.30 |  |  | 4.80
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 15285.68 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.1 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.91 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.09 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.95 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.96 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 79.38 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.45 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 732.62 |  |  | 1035 |  |  |  | 1045 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7519.47 |  |  | 7462 |  |  |  | 1045 | [10 empty] | 84.63 |  |  |  | 84.71 | [5 empty] | 82.14 |  |  | 85.18 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 15.13 |  |  |  |  | 0.09
2020 |  |  |  | 7033.68 |  |  | 7003 |  |  |  | 1045 | [10 empty] | 95.17 |  |  |  | 95.17 | [5 empty] | 76.63 |  |  | 79.72 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 4.80 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2018 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 2
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 385 | [14 empty] | 839
E. |  | Testing of plant systems or components | [35 empty] | 265
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 1396 | [19 empty] | 698
Subtotal | [22 empty] | 385 | [10 empty] | 1396 |  |  |  | 1104 |  |  |  | 2 | [11 empty] | 698
Total | [22 empty] | 1781 | [14 empty] | 1804
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2018 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [19 empty] | 1396 | [14 empty] | 620
Total | [22 empty] | 1396 | [14 empty] | 621
Highlights (2020)
In this year, unit 4 experienced the second refuelling outage, and cooperated with the grid for power reduction for many times. Other time kept power operation, and no manual scram occurred. The details are as follows: At 22:02 on November 15, 2020, the unit was shut down and started the second refueling outage; At 22:42 January,9 2021, the unit was reconnected to the grid .

## TIANWAN-5
2020 Operating Experience
CN-53 | [8 empty] | TIANWAN-5 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | SHE (Shanghai Electric)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2015-12-27
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-08-08
Gross electrical power | [12 empty] | : |  |  | 1118 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2020-09-08
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 0 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.8
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 3.2 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2901.91 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.34 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.34 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.66 %
Load Factor (LF) | [18 empty] | : | 91.31 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 95.87 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 121 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | Aug |  |  | May | [6 empty] | Jun |  | Jul |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [36 empty] | 507.39 |  |  | 702.30 |  |  | 720.00 | [9 empty] | 744.00 |  |  | 2673.69
EAF [%] | [36 empty] | 72.92 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.34
UCF [%] | [36 empty] | 72.92 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.34
LF [%] | [36 empty] | 70.47 |  |  | 94.39 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.31
OF [%] | [36 empty] | 92.78 |  |  | 90.73 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.87
FLR [%] | [36 empty] | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] | [36 empty] | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] | [36 empty] | 27.08 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.66
XUF [%] | [36 empty] | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 2901.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 93.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.34 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.66 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.31 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 95.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2020 |  |  |  | 2901.91 |  |  | 3383 |  |  |  | 1000 | [10 empty] | 93.34 |  |  |  | 93.34 | [5 empty] | 91.31 |  |  | 95.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.66 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2020 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 121 | [19 empty] | 363
Subtotal | [33 empty] | 121 | [19 empty] | 363
Total | [22 empty] | 121 | [14 empty] | 363
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2020 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [19 empty] | 121 | [14 empty] | 290
Total | [22 empty] | 121 | [14 empty] | 290
Highlights (2020)
During this year, unit 5 was loaded and tested many times. It was connected to the grid on August 8 and was ready for commercial operation on September 8.

## YANGJIANG-1
2020 Operating Experience
CN-22 | [8 empty] | YANGJIANG-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-12-16
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2013-12-31
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2014-03-25
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8122.92 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.49 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.42 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.49 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.51 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 92.47 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.09 %
Operating Factor (OF) | [18 empty] | : | 98.65 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 119 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 697.61 | 565.69 |  |  |  | 537.99 |  | 681.94 | [8 empty] | 714.25 |  |  | 715.24 | [6 empty] | 718.77 |  | 738.94 |  |  |  | 719.14 |  |  | 650.33 |  |  | 630.24 | [9 empty] | 752.78 |  |  | 8122.92
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 82.71 |  | 99.69 | [8 empty] | 100.00 |  |  | 99.75 | [6 empty] | 100.00 |  | 99.14 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.42
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 82.71 |  | 99.69 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.51
LF [%] |  |  |  |  | 93.76 | 81.28 |  |  |  | 72.31 |  | 94.71 | [8 empty] | 96.00 |  |  | 99.34 | [6 empty] | 96.61 |  | 99.32 |  |  |  | 99.88 |  |  | 87.41 |  |  | 87.53 | [9 empty] | 101.18 |  |  | 92.47
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 84.01 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.65
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 17.29 |  | 0.30 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.49
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 17.29 |  | 0.30 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.49
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.25 | [6 empty] | 0.00 |  | 0.86 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.09
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 53874.92 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.62 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.31 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.68 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.01 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.96 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.06 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.53 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2014 |  |  |  | 6793.37 |  |  | 6753 |  |  |  | 1000 | [10 empty] | 99.93 |  |  |  | 99.93 | [5 empty] | 100.54 |  |  | 100.00 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 0.02 |  |  |  |  | 0.00
2015 |  |  |  | 7025.37 |  |  | 7021 |  |  |  | 1000 | [10 empty] | 79.73 |  |  |  | 79.73 | [5 empty] | 80.20 |  |  | 80.15 |  |  |  | 0.74 |  | 0.59 | [8 empty] | 19.68 |  |  |  |  | 0.00
2016 |  |  |  | 7077.81 |  |  | 6989 |  |  |  | 1000 | [10 empty] | 81.52 |  |  |  | 81.56 | [5 empty] | 80.58 |  |  | 79.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.44 |  |  |  |  | 0.04
2017 |  |  |  | 8699.83 |  |  | 8677 |  |  |  | 1000 | [10 empty] | 99.75 |  |  |  | 99.99 | [5 empty] | 99.31 |  |  | 99.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.24
2018 |  |  |  | 7715.76 |  |  | 7789 |  |  |  | 1000 | [10 empty] | 88.20 |  |  |  | 88.24 | [5 empty] | 88.08 |  |  | 88.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.76 |  |  |  |  | 0.03
2019 |  |  |  | 7988.46 |  |  | 7861 |  |  |  | 1000 | [10 empty] | 89.09 |  |  |  | 89.09 | [5 empty] | 91.19 |  |  | 89.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.91 |  |  |  |  | 0.00
2020 |  |  |  | 8122.92 |  |  | 8665 |  |  |  | 1000 | [10 empty] | 98.42 |  |  |  | 98.51 | [5 empty] | 92.47 |  |  | 98.65 |  |  |  | 1.49 |  | 1.49 | [8 empty] | 0.00 |  |  |  |  | 0.09
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2014 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 119 | [14 empty] | 28
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 855
E. |  | Testing of plant systems or components | [35 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 50
Subtotal | [26 empty] | 119 | [10 empty] | 855 |  |  |  | 28 | [11 empty] | 50
Total | [22 empty] | 119 | [14 empty] | 933
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2014 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 9
33. |  |  | Circulating Water System | [19 empty] | 119 | [14 empty] | 20
Total | [22 empty] | 119 | [14 empty] | 29
Highlights (2020)
On March 25, 2020, the reactor was shut down manually as large shoals of acetes flooded into the water intake. On March 30, Unit 1 was resynchronized to the grid. It ran at reduced power in response to grid peak load regulation during holidays, and ran at full power during the rest time of the year.

## YANGJIANG-2
2020 Operating Experience
CN-23 | [8 empty] | YANGJIANG-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-06-04
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-03-10
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-06-05
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6539.67 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.84 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.49 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.59 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.49 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.92 %
Load Factor (LF) | [18 empty] | : | 74.45 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 78.03 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1930 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 432.38 | 50.08 |  |  |  | 596.09 |  | 539.92 | [8 empty] | 724.02 |  |  | 712.88 | [6 empty] | 755.46 |  | 751.50 |  |  |  | 605.02 |  |  | 80.80 |  |  | 627.67 | [9 empty] | 663.85 |  |  | 6539.67
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 79.36 |  | 89.78 | [8 empty] | 100.00 |  |  | 99.95 | [6 empty] | 100.00 |  | 99.94 |  |  |  | 83.27 |  |  | 10.93 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 88.49
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 79.36 |  | 89.78 | [8 empty] | 100.00 |  |  | 99.95 | [6 empty] | 100.00 |  | 99.94 |  |  |  | 83.27 |  |  | 10.93 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 88.49
LF [%] |  |  |  |  | 58.12 | 7.20 |  |  |  | 80.12 |  | 74.99 | [8 empty] | 97.31 |  |  | 99.01 | [6 empty] | 101.54 |  | 101.01 |  |  |  | 84.03 |  |  | 10.86 |  |  | 87.18 | [9 empty] | 89.23 |  |  | 74.45
OF [%] |  |  |  |  | 67.61 | 9.20 |  |  |  | 79.70 |  | 75.83 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 83.75 |  |  | 17.34 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.03
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 20.63 |  | 10.22 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.06 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.84
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 20.63 |  | 10.22 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.06 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.59
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.05 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 16.73 |  |  | 89.07 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 8.92
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 43020.67 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.63 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.94 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.57 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.02 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.41 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.94 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.08 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 5683.72 |  |  | 6017 |  |  |  | 1000 | [10 empty] | 99.79 |  |  |  | 99.79 | [5 empty] | 102.21 |  |  | 100.00 |  |  |  | 0.20 |  | 0.20 | [8 empty] | 0.01 |  |  |  |  | 0.00
2016 |  |  |  | 6911.71 |  |  | 6874 |  |  |  | 1000 | [10 empty] | 77.59 |  |  |  | 77.69 | [5 empty] | 78.69 |  |  | 78.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.31 |  |  |  |  | 0.10
2017 |  |  |  | 7497.38 |  |  | 7476 |  |  |  | 1000 | [10 empty] | 87.99 |  |  |  | 87.99 | [5 empty] | 85.59 |  |  | 85.34 |  |  |  | 0.52 |  | 0.46 | [8 empty] | 11.55 |  |  |  |  | 0.00
2018 |  |  |  | 8910.12 |  |  | 8760 |  |  |  | 1000 | [10 empty] | 99.95 |  |  |  | 99.98 | [5 empty] | 101.71 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.04
2019 |  |  |  | 7478.07 |  |  | 7943 |  |  |  | 1000 | [10 empty] | 89.97 |  |  |  | 90.27 | [5 empty] | 85.37 |  |  | 90.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.73 |  |  |  |  | 0.30
2020 |  |  |  | 6539.67 |  |  | 6854 |  |  |  | 1000 | [10 empty] | 88.49 |  |  |  | 88.49 | [5 empty] | 74.45 |  |  | 78.03 |  |  |  | 2.84 |  | 2.59 | [8 empty] | 8.92 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2015 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 7
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 720 | [14 empty] | 783
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 4
I. |  | Grid capacity limitation | [31 empty] | 976 | [19 empty] | 175
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 52
Z. |  | Other | [20 empty] | 12 |  |  |  | 222 | [10 empty] | 2 |  |  |  | 40
Subtotal | [22 empty] | 732 |  |  |  | 222 | [6 empty] | 976 |  |  |  | 789 |  |  |  | 47 | [11 empty] | 227
Total | [22 empty] | 1930 | [14 empty] | 1063
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2015 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [19 empty] | 222 | [14 empty] | 38
42. |  |  | Electrical Power Supply Systems | [19 empty] | 976 | [14 empty] | 167
Total | [22 empty] | 1198 | [14 empty] | 212
Highlights (2020)
On March 25, 2020, the reactor was shut down automatically as large shoals of acetes flooded into the water intake. On April 8, Unit 2 was resynchronized to the grid. Unit 2 was disconnected for Y204 outage (the 4th outage of Unit 2) on September 26, 2020, and resynchronized, after an outage of 30.49 days, to the grid on October 26. It ran at reduced power in response to grid peak load regulation during holidays, including shutdown once for standby in response to grid requirements, and ran at full power during the rest time of the year.

## YANGJIANG-3
2020 Operating Experience
CN-40 | [8 empty] | YANGJIANG-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-11-15
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-10-18
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-01-01
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6600.21 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.7 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.76 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.41 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.91 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.68 %
Load Factor (LF) | [18 empty] | : | 75.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.15 %
Operating Factor (OF) | [18 empty] | : | 80.13 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1745 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 411.29 | 97.46 |  |  |  | 517.47 |  | 626.89 | [8 empty] | 725.28 |  |  | 563.94 | [6 empty] | 619.14 |  | 741.70 |  |  |  | 692.11 |  |  | 369.10 |  |  | 558.01 | [9 empty] | 677.82 |  |  | 6600.21
EAF [%] |  |  |  |  | 54.01 | 14.46 |  |  |  | 79.59 |  | 91.64 | [8 empty] | 100.00 |  |  | 98.98 | [6 empty] | 100.00 |  | 99.20 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.76
UCF [%] |  |  |  |  | 54.01 | 14.46 |  |  |  | 79.59 |  | 91.64 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.91
LF [%] |  |  |  |  | 55.28 | 14.00 |  |  |  | 69.55 |  | 87.07 | [8 empty] | 97.48 |  |  | 78.33 | [6 empty] | 83.22 |  | 99.69 |  |  |  | 96.13 |  |  | 49.61 |  |  | 77.50 | [9 empty] | 91.10 |  |  | 75.14
OF [%] |  |  |  |  | 55.11 | 19.25 |  |  |  | 79.57 |  | 92.08 | [8 empty] | 100.00 |  |  | 80.42 | [6 empty] | 82.80 |  | 100.00 |  |  |  | 100.00 |  |  | 61.69 |  |  | 88.06 | [9 empty] | 100.00 |  |  | 80.13
FLR [%] |  |  |  |  | 0.00 | 0.07 |  |  |  | 20.41 |  | 8.34 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.70
UCL [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 20.41 |  | 8.34 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.41
PUF [%] |  |  |  |  | 45.99 | 85.53 |  |  |  | 0.00 |  | 0.02 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.68
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.02 | [6 empty] | 0.00 |  | 0.80 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.15
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 38617.14 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.57 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.01 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.52 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.3 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.17 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.98 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.29 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.54 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 7593.85 |  |  | 7559 |  |  |  | 1000 | [10 empty] | 91.12 |  |  |  | 91.24 | [5 empty] | 86.45 |  |  | 86.05 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.75 |  |  |  |  | 0.12
2017 |  |  |  | 7396.07 |  |  | 7435 |  |  |  | 1000 | [10 empty] | 86.14 |  |  |  | 86.87 | [5 empty] | 84.43 |  |  | 84.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.13 |  |  |  |  | 0.72
2018 |  |  |  | 7926.66 |  |  | 8028 |  |  |  | 1000 | [10 empty] | 91.09 |  |  |  | 91.51 | [5 empty] | 90.49 |  |  | 91.64 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 8.30 |  |  |  |  | 0.41
2019 |  |  |  | 8621.67 |  |  | 8760 |  |  |  | 1000 | [10 empty] | 99.96 |  |  |  | 99.99 | [5 empty] | 98.42 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.04
2020 |  |  |  | 6600.21 |  |  | 7039 |  |  |  | 1000 | [10 empty] | 86.76 |  |  |  | 86.91 | [5 empty] | 75.14 |  |  | 80.13 |  |  |  | 2.70 |  | 2.41 | [8 empty] | 10.68 |  |  |  |  | 0.15
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 3
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 892 | [14 empty] | 689
I. |  | Grid capacity limitation | [31 empty] | 643 | [19 empty] | 129
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 136
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 6
Z. |  | Other | [24 empty] | 209 | [14 empty] | 42
Subtotal | [22 empty] | 892 |  |  |  | 209 | [6 empty] | 643 |  |  |  | 689 |  |  |  | 45 | [11 empty] | 271
Total | [22 empty] | 1744 | [14 empty] | 1005
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2016 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
33. |  |  | Circulating Water System | [19 empty] | 209 | [14 empty] | 42
42. |  |  | Electrical Power Supply Systems | [19 empty] | 643 | [14 empty] | 129
Total | [22 empty] | 852 | [14 empty] | 174
Highlights (2020)
Unit 3 was disconnected for Y303 outage (the 3rd outage of Unit 3) on January 18, 2020, and resynchronized, after an outage of 37.15 days, to grid on February 24. On March 25, 2020, the reactor was shut down automatically as large shoals of acetes flooded into the water intake. On April 3, Unit 3 was resynchronized to the grid. It ran at reduced power in response to grid peak load regulation during holidays, including shutdown twice for standby in response to grid requirements, and ran at full power during the rest time of the year.

## YANGJIANG-4
2020 Operating Experience
CN-41 | [8 empty] | YANGJIANG-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2012-11-17
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2017-01-08
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2017-03-15
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7954.62 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.88 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.02 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.88 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.11 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 90.56 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.09 %
Operating Factor (OF) | [18 empty] | : | 93.53 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 568 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 687.56 | 588.04 |  |  |  | 591.96 |  | 494.25 | [8 empty] | 696.71 |  |  | 700.22 | [6 empty] | 743.69 |  | 739.42 |  |  |  | 691.10 |  |  | 605.16 |  |  | 682.12 | [9 empty] | 734.39 |  |  | 7954.62
EAF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 76.85 |  | 88.73 | [8 empty] | 100.00 |  |  | 99.73 | [6 empty] | 100.00 |  | 99.14 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 97.02
UCF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 76.85 |  | 88.73 | [8 empty] | 100.00 |  |  | 99.98 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 97.11
LF [%] |  |  |  |  | 92.41 | 84.49 |  |  |  | 79.56 |  | 68.65 | [8 empty] | 93.64 |  |  | 97.25 | [6 empty] | 99.96 |  | 99.38 |  |  |  | 95.99 |  |  | 81.34 |  |  | 94.74 | [9 empty] | 98.71 |  |  | 90.56
OF [%] |  |  |  |  | 95.97 | 100.00 |  |  |  | 77.15 |  | 72.50 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 97.22 |  |  | 79.84 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.53
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 23.15 |  | 11.27 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.88
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 23.15 |  | 11.27 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.88
PUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.25 | [6 empty] | 0.00 |  | 0.85 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.09
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 28222.17 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.9 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.75 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.72 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.86 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.11 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.49 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2017 |  |  |  | 6759.71 |  |  | 6353 |  |  |  | 1000 | [10 empty] | 90.72 |  |  |  | 91.02 | [5 empty] | 90.26 |  |  | 86.51 |  |  |  | 8.98 |  | 8.98 | [8 empty] | 0.01 |  |  |  |  | 0.30
2018 |  |  |  | 6591.93 |  |  | 6695 |  |  |  | 1000 | [10 empty] | 83.35 |  |  |  | 83.43 | [5 empty] | 75.25 |  |  | 76.43 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 16.57 |  |  |  |  | 0.07
2019 |  |  |  | 6915.91 |  |  | 7164 |  |  |  | 1000 | [10 empty] | 91.88 |  |  |  | 91.88 | [5 empty] | 78.95 |  |  | 81.78 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.11 |  |  |  |  | 0.00
2020 |  |  |  | 7954.62 |  |  | 8216 |  |  |  | 1000 | [10 empty] | 97.02 |  |  |  | 97.11 | [5 empty] | 90.56 |  |  | 93.53 |  |  |  | 2.88 |  | 2.88 | [8 empty] | 0.00 |  |  |  |  | 0.09
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2017 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 171
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 543
I. |  | Grid capacity limitation | [31 empty] | 320 | [19 empty] | 83
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 411
Z. |  | Other | [24 empty] | 249 | [14 empty] | 65
Subtotal | [26 empty] | 249 | [6 empty] | 320 |  |  |  | 543 |  |  |  | 236 | [11 empty] | 494
Total | [22 empty] | 569 | [14 empty] | 1273
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2017 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
33. |  |  | Circulating Water System | [19 empty] | 249 | [14 empty] | 62
42. |  |  | Electrical Power Supply Systems | [19 empty] | 320 | [14 empty] | 244
Total | [22 empty] | 569 | [14 empty] | 306
Highlights (2020)
On March 24 and 25, 2020, the reactor was shut down automatically as large shoals of acetes flooded into the water intake. On April 9, Unit 4 was resynchronized to the grid. It ran at reduced power in response to grid peak load regulation during holidays, including shutdown twice for standby in response to grid requirements, and ran at full power during the rest time of the year.

## YANGJIANG-5
2020 Operating Experience
CN-47 | [8 empty] | YANGJIANG-5 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / ACPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2013-09-18
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-05-23
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-07-12
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7318.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.83 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.64 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.76 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.79 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.45 %
Load Factor (LF) | [18 empty] | : | 83.32 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.15 %
Operating Factor (OF) | [18 empty] | : | 87.73 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1078 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 473.24 | 583.72 |  |  |  | 500.89 |  | 467.75 | [8 empty] | 657.62 |  |  | 687.06 | [6 empty] | 717.97 |  | 736.67 |  |  |  | 685.59 |  |  | 522.54 |  |  | 740.46 | [9 empty] | 545.17 |  |  | 7318.68
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 79.18 |  | 87.88 | [8 empty] | 100.00 |  |  | 99.01 | [6 empty] | 99.97 |  | 99.19 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 71.07 |  |  | 94.64
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 79.18 |  | 87.88 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.97 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 71.07 |  |  | 94.79
LF [%] |  |  |  |  | 63.61 | 83.87 |  |  |  | 67.32 |  | 64.97 | [8 empty] | 88.39 |  |  | 95.42 | [6 empty] | 96.50 |  | 99.01 |  |  |  | 95.22 |  |  | 70.23 |  |  | 102.84 | [9 empty] | 73.28 |  |  | 83.32
OF [%] |  |  |  |  | 75.13 | 100.00 |  |  |  | 79.70 |  | 65.83 | [8 empty] | 92.20 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 69.62 |  |  | 100.00 | [9 empty] | 71.51 |  |  | 87.73
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 20.82 |  | 12.12 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.83
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 20.82 |  | 12.12 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.76
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 28.93 |  |  | 2.45
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.99 | [6 empty] | 0.00 |  | 0.81 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.15
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 18383.45 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.45 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.64 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.34 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.79 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.81 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.23 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 4365.35 |  |  | 4847 |  |  |  | 1000 | [10 empty] | 99.11 |  |  |  | 99.94 | [5 empty] | 94.36 |  |  | 97.26 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 0.00 |  |  |  |  | 0.83
2019 |  |  |  | 6699.42 |  |  | 6927 |  |  |  | 1000 | [10 empty] | 82.36 |  |  |  | 82.36 | [5 empty] | 76.48 |  |  | 79.08 |  |  |  | 0.68 |  | 0.56 | [8 empty] | 17.08 |  |  |  |  | 0.00
2020 |  |  |  | 7318.68 |  |  | 7706 |  |  |  | 1000 | [10 empty] | 94.64 |  |  |  | 94.79 | [5 empty] | 83.32 |  |  | 87.73 |  |  |  | 2.83 |  | 2.76 | [8 empty] | 2.45 |  |  |  |  | 0.15
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2018 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 18
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 212 | [14 empty] | 664
I. |  | Grid capacity limitation | [31 empty] | 631 | [19 empty] | 252
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 135
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 12
Z. |  | Other | [24 empty] | 235 | [14 empty] | 94
Subtotal | [22 empty] | 212 |  |  |  | 235 | [6 empty] | 631 |  |  |  | 664 |  |  |  | 112 | [11 empty] | 399
Total | [22 empty] | 1078 | [14 empty] | 1175
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2018 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
14. |  |  | Safety Systems | [34 empty] | 17
33. |  |  | Circulating Water System | [19 empty] | 235 | [14 empty] | 88
42. |  |  | Electrical Power Supply Systems | [19 empty] | 631 | [14 empty] | 236
Total | [22 empty] | 866 | [14 empty] | 341
Highlights (2020)
On March 25, 2020, the reactor was shut down manually as large shoals of acetes flooded into the water intake. On April 11, Unit 5 was resynchronized to the grid. On December 23, 2020, Unit 5 was disconnected for Y502 outage (the 2nd outage of Unit 5). By December 31, the outage had not been completed yet. It ran at reduced power in response to grid peak load regulation during holidays, including shutdown three times for standby in response to grid requirements, and ran at full power during the rest time of the year.

## YANGJIANG-6
2020 Operating Experience
CN-48 | [8 empty] | YANGJIANG-6 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / ACPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2013-12-23
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-06-29
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2019-07-24
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5896.66 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.15 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.41 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.57 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.41 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 14.02 %
Load Factor (LF) | [18 empty] | : | 67.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 74.29 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2258 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 656.75 | 130.71 |  |  |  | 588.09 |  | 669.26 | [8 empty] | 756.22 |  |  | 729.09 | [6 empty] | 388.56 |  | 0.00 |  |  |  | 538.42 |  |  | 546.93 |  |  | 373.03 | [9 empty] | 519.60 |  |  | 5896.66
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 79.36 |  | 90.45 | [8 empty] | 100.00 |  |  | 99.97 | [6 empty] | 51.65 |  | 0.00 |  |  |  | 82.37 |  |  | 100.00 |  |  | 93.75 | [9 empty] | 93.73 |  |  | 82.41
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 79.36 |  | 90.45 | [8 empty] | 100.00 |  |  | 99.97 | [6 empty] | 51.65 |  | 0.00 |  |  |  | 82.37 |  |  | 100.00 |  |  | 93.75 | [9 empty] | 93.73 |  |  | 82.41
LF [%] |  |  |  |  | 88.27 | 18.78 |  |  |  | 79.04 |  | 92.95 | [8 empty] | 101.64 |  |  | 101.26 | [6 empty] | 52.23 |  | 0.00 |  |  |  | 74.78 |  |  | 73.51 |  |  | 51.81 | [9 empty] | 69.84 |  |  | 67.13
OF [%] |  |  |  |  | 98.79 | 22.99 |  |  |  | 79.57 |  | 90.97 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 52.02 |  | 0.00 |  |  |  | 87.08 |  |  | 87.50 |  |  | 70.97 | [9 empty] | 100.00 |  |  | 74.29
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 20.63 |  | 9.55 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 6.20 | [9 empty] | 6.27 |  |  | 4.15
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 20.63 |  | 9.55 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 6.20 | [9 empty] | 6.27 |  |  | 3.57
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.03 | [6 empty] | 48.35 |  | 100.00 |  |  |  | 17.63 |  |  | 0.00 |  |  | 0.05 | [9 empty] | 0.00 |  |  | 14.02
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 9830.84 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.79 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.6 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.52 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.6 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.89 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.7 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.88 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2019 |  |  |  | 3934.18 |  |  | 3915 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 92.83 |  |  | 93.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 5896.66 |  |  | 6526 |  |  |  | 1000 | [10 empty] | 82.41 |  |  |  | 82.41 | [5 empty] | 67.13 |  |  | 74.29 |  |  |  | 4.15 |  | 3.57 | [8 empty] | 14.02 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2019 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1193 | [14 empty] | 842
I. |  | Grid capacity limitation | [31 empty] | 852 | [19 empty] | 602
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 175
Z. |  | Other | [24 empty] | 217 | [14 empty] | 153
Subtotal | [22 empty] | 1193 |  |  |  | 217 | [6 empty] | 852 |  |  |  | 842 |  |  |  | 153 | [11 empty] | 777
Total | [22 empty] | 2262 | [14 empty] | 1772
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2019 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
33. |  |  | Circulating Water System | [19 empty] | 217 | [14 empty] | 137
42. |  |  | Electrical Power Supply Systems | [19 empty] | 852 | [14 empty] | 538
Total | [22 empty] | 1069 | [14 empty] | 675
Highlights (2020)
On March 25, 2020, the reactor was shut down automatically as large shoals of acetes flooded into the water intake. On April 3, Unit 6 was resynchronized to the grid. Unit 6 was disconnected for Y601 outage (the 1st outage of Unit 6) on July 17, 2020, and resynchronized, after an outage of 49.73 days, to the grid on September 4. On November 23-27 and December 1-5, 2020, Unit 6 was shut down for Y6CRF001PO (No.1 pump of circulating water system of Unit 6 of Yangjiang Nuclear Power Plant) maintenance. It ran at reduced power in response to grid peak load regulation during holidays, including shutdown twice for standby in response to grid requirements, and ran at full power during the rest time of the year.