## BOHUNICE-3
2020 Operating Experience
SK-13 | [8 empty] | BOHUNICE-3 | [26 empty] | SLOVAKIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SE (SLOVENSKÉ ELEKTRÁRNE , AS.)
Owner | [7 empty] | : | SE (SLOVENSKÉ ELEKTRÁRNE , AS.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-12-01
Thermal power | [12 empty] | : |  |  | 1471 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-08-20
Gross electrical power | [12 empty] | : |  |  | 500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-02-14
Reference unit power (net) | [12 empty] | : |  |  | 466 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.0
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 295
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.245
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.25 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 23 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 55000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.32
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3683.59 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.09 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.64 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.08 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.78 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.14 %
Load Factor (LF) | [18 empty] | : | 89.11 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.14 %
Operating Factor (OF) | [18 empty] | : | 93.76 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 548 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 56.31 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 337.42 | 314.30 |  |  |  | 336.92 |  | 323.87 | [8 empty] | 325.38 |  |  | 187.59 | [6 empty] | 198.48 |  | 328.13 |  |  |  | 323.64 |  |  | 338.20 |  |  | 328.47 | [9 empty] | 341.19 |  |  | 3683.59
EAF [%] |  |  |  |  | 96.64 | 96.29 |  |  |  | 97.50 |  | 96.38 | [8 empty] | 93.51 |  |  | 56.21 | [6 empty] | 57.50 |  | 94.32 |  |  |  | 95.88 |  |  | 96.69 |  |  | 97.25 | [9 empty] | 97.60 |  |  | 89.64
UCF [%] |  |  |  |  | 99.96 | 99.49 |  |  |  | 100.00 |  | 99.57 | [8 empty] | 96.39 |  |  | 59.00 | [6 empty] | 59.99 |  | 99.83 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.62 | [9 empty] | 99.61 |  |  | 92.78
LF [%] |  |  |  |  | 96.29 | 95.88 |  |  |  | 96.28 |  | 95.50 | [8 empty] | 92.85 |  |  | 55.32 | [6 empty] | 56.64 |  | 93.64 |  |  |  | 95.43 |  |  | 96.38 |  |  | 96.86 | [9 empty] | 98.41 |  |  | 89.11
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 63.75 | [6 empty] | 61.42 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.76
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.43 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.17 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.39 |  |  | 0.09
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.43 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.17 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.39 |  |  | 0.08
PUF [%] |  |  |  |  | 0.04 | 0.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.61 |  |  | 41.00 | [6 empty] | 40.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.38 | [9 empty] | 0.00 |  |  | 7.14
XUF [%] |  |  |  |  | 3.32 | 3.20 |  |  |  | 2.50 |  | 3.19 | [8 empty] | 2.88 |  |  | 2.80 | [6 empty] | 2.49 |  | 5.51 |  |  |  | 4.12 |  |  | 3.31 |  |  | 2.36 | [9 empty] | 2.01 |  |  | 3.14
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 109127.57 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.17 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.41 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.13 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.66 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.21 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 79.91 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.24 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.53 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 2721.56 |  |  | 7057 |  |  |  | 408 | [10 empty] | 76.82 |  |  |  | 76.82 | [5 empty] | 74.45 |  |  | 78.87 |  |  |  | 1.66 |  | 1.30 | [8 empty] | 21.89 |  |  |  |  | 0.00
1986 |  |  |  | 2674.14 |  |  | 7089 |  |  |  | 408 | [10 empty] | 75.40 |  |  |  | 75.43 | [5 empty] | 74.82 |  |  | 80.92 |  |  |  | 7.77 |  | 6.35 | [8 empty] | 18.22 |  |  |  |  | 0.03
1987 |  |  |  | 1997.38 |  |  | 5181 |  |  |  | 408 | [10 empty] | 53.70 |  |  |  | 55.54 | [5 empty] | 55.89 |  |  | 59.14 |  |  |  | 2.29 |  | 1.30 | [8 empty] | 43.16 |  |  |  |  | 1.83
1988 |  |  |  | 2866.88 |  |  | 7329 |  |  |  | 408 | [10 empty] | 79.89 |  |  |  | 80.24 | [5 empty] | 79.99 |  |  | 83.44 |  |  |  | 0.42 |  | 0.34 | [8 empty] | 19.43 |  |  |  |  | 0.35
1989 |  |  |  | 2992.32 |  |  | 7633 |  |  |  | 408 | [10 empty] | 84.14 |  |  |  | 85.01 | [5 empty] | 83.72 |  |  | 87.13 |  |  |  | 0.57 |  | 0.49 | [8 empty] | 14.50 |  |  |  |  | 0.88
1990 |  |  |  | 2829.10 |  |  | 7376 |  |  |  | 408 | [10 empty] | 79.25 |  |  |  | 80.49 | [5 empty] | 79.16 |  |  | 84.20 |  |  |  | 5.39 |  | 4.59 | [8 empty] | 14.93 |  |  |  |  | 1.24
1991 |  |  |  | 2585.64 |  |  | 6717 |  |  |  | 408 | [10 empty] | 71.95 |  |  |  | 74.16 | [5 empty] | 72.34 |  |  | 76.68 |  |  |  | 1.36 |  | 1.03 | [8 empty] | 24.81 |  |  |  |  | 2.21
1992 |  |  |  | 3140.69 |  |  | 7528 |  |  |  | 408 | [10 empty] | 82.77 |  |  |  | 83.89 | [5 empty] | 87.63 |  |  | 85.70 |  |  |  | 0.75 |  | 0.63 | [8 empty] | 15.48 |  |  |  |  | 1.12
1993 |  |  |  | 2973.14 |  |  | 7721 |  |  |  | 408 | [10 empty] | 83.19 |  |  |  | 86.52 | [5 empty] | 83.19 |  |  | 88.14 |  |  |  | 1.24 |  | 1.09 | [8 empty] | 12.39 |  |  |  |  | 3.34
1994 |  |  |  | 2806.83 |  |  | 7423 |  |  |  | 405 | [10 empty] | 79.05 |  |  |  | 84.03 | [5 empty] | 79.11 |  |  | 84.74 |  |  |  | 0.73 |  | 0.62 | [8 empty] | 15.36 |  |  |  |  | 4.97
1995 |  |  |  | 2536.71 |  |  | 6440 |  |  |  | 408 | [10 empty] | 70.14 |  |  |  | 78.13 | [5 empty] | 70.98 |  |  | 73.52 |  |  |  | 1.74 |  | 1.39 | [8 empty] | 20.48 |  |  |  |  | 8.00
1996 |  |  |  | 3045.91 |  |  | 7504 |  |  |  | 436 | [10 empty] | 82.50 |  |  |  | 85.56 | [5 empty] | 79.53 |  |  | 85.43 |  |  |  | 1.45 |  | 1.26 | [8 empty] | 13.18 |  |  |  |  | 3.06
1997 |  |  |  | 3096.42 |  |  | 7711 |  |  |  | 440 | [10 empty] | 84.04 |  |  |  | 87.73 | [5 empty] | 80.33 |  |  | 88.03 |  |  |  | 0.49 |  | 0.43 | [8 empty] | 11.84 |  |  |  |  | 3.69
1998 |  |  |  | 2804.63 |  |  | 7571 |  |  |  | 408 | [10 empty] | 81.80 |  |  |  | 85.32 | [5 empty] | 78.47 |  |  | 86.43 |  |  |  | 2.30 |  | 2.00 | [8 empty] | 12.68 |  |  |  |  | 3.52
1999 |  |  |  | 2468.54 |  |  | 6620 |  |  |  | 408 | [10 empty] | 69.65 |  |  |  | 76.46 | [5 empty] | 69.07 |  |  | 75.57 |  |  |  | 3.81 |  | 3.03 | [8 empty] | 20.51 |  |  |  |  | 6.81
2000 |  |  |  | 2806.72 |  |  | 7776 |  |  |  | 408 | [10 empty] | 79.82 |  |  |  | 87.92 | [5 empty] | 78.32 |  |  | 88.52 |  |  |  | 1.07 |  | 0.95 | [8 empty] | 11.13 |  |  |  |  | 8.10
2001 |  |  |  | 2686.99 |  |  | 7680 |  |  |  | 408 | [10 empty] | 76.48 |  |  |  | 86.60 | [5 empty] | 75.18 |  |  | 87.67 |  |  |  | 1.03 |  | 0.90 | [8 empty] | 12.50 |  |  |  |  | 10.12
2002 |  |  |  | 2690.74 |  |  | 7711 |  |  |  | 408 | [10 empty] | 83.86 |  |  |  | 87.38 | [5 empty] | 75.28 |  |  | 88.03 |  |  |  | 0.22 |  | 0.19 | [8 empty] | 12.43 |  |  |  |  | 3.52
2003 |  |  |  | 2484.97 |  |  | 6908 |  |  |  | 408 | [10 empty] | 75.46 |  |  |  | 78.28 | [5 empty] | 69.53 |  |  | 78.86 |  |  |  | 0.16 |  | 0.13 | [8 empty] | 21.59 |  |  |  |  | 2.82
2004 |  |  |  | 2564.55 |  |  | 7228 |  |  |  | 408 | [10 empty] | 79.03 |  |  |  | 81.97 | [5 empty] | 71.56 |  |  | 82.29 |  |  |  | 0.39 |  | 0.32 | [8 empty] | 17.72 |  |  |  |  | 2.93
2005 |  |  |  | 2587.73 |  |  | 7034 |  |  |  | 408 | [10 empty] | 76.69 |  |  |  | 79.44 | [5 empty] | 72.40 |  |  | 80.30 |  |  |  | 0.91 |  | 0.73 | [8 empty] | 19.83 |  |  |  |  | 2.74
2006 |  |  |  | 2582.58 |  |  | 7106 |  |  |  | 408 | [10 empty] | 78.36 |  |  |  | 80.73 | [5 empty] | 72.26 |  |  | 81.12 |  |  |  | 0.29 |  | 0.24 | [8 empty] | 19.03 |  |  |  |  | 2.37
2007 |  |  |  | 2432.56 |  |  | 6687 |  |  |  | 408 | [10 empty] | 71.57 |  |  |  | 73.84 | [5 empty] | 68.06 |  |  | 76.34 |  |  |  | 7.18 |  | 5.71 | [8 empty] | 20.45 |  |  |  |  | 2.27
2008 |  |  |  | 3038.40 |  |  | 7680 |  |  |  | 429 | [10 empty] | 85.82 |  |  |  | 86.69 | [5 empty] | 83.70 |  |  | 87.43 |  |  |  | 0.56 |  | 0.49 | [8 empty] | 12.82 |  |  |  |  | 0.87
2009 |  |  |  | 3309.67 |  |  | 8176 |  |  |  | 442 | [10 empty] | 87.18 |  |  |  | 89.33 | [5 empty] | 87.40 |  |  | 93.33 |  |  |  | 0.12 |  | 0.10 | [8 empty] | 10.56 |  |  |  |  | 2.15
2010 |  |  |  | 3385.92 |  |  | 8194 |  |  |  | 472 | [10 empty] | 84.80 |  |  |  | 87.97 | [5 empty] | 85.98 |  |  | 93.54 |  |  |  | 0.26 |  | 0.23 | [8 empty] | 11.80 |  |  |  |  | 3.17
2011 |  |  |  | 3586.04 |  |  | 7890 |  |  |  | 472 | [10 empty] | 87.25 |  |  |  | 89.94 | [5 empty] | 86.73 |  |  | 90.07 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 10.03 |  |  |  |  | 2.69
2012 |  |  |  | 3761.71 |  |  | 8295 |  |  |  | 472 | [10 empty] | 91.28 |  |  |  | 94.17 | [5 empty] | 90.73 |  |  | 94.43 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 5.81 |  |  |  |  | 2.90
2013 |  |  |  | 3726.97 |  |  | 8245 |  |  |  | 472 | [10 empty] | 90.67 |  |  |  | 93.71 | [5 empty] | 90.14 |  |  | 94.12 |  |  |  | 0.38 |  | 0.36 | [8 empty] | 5.93 |  |  |  |  | 3.04
2014 |  |  |  | 3730.20 |  |  | 8235 |  |  |  | 471 | [10 empty] | 90.60 |  |  |  | 93.90 | [5 empty] | 90.41 |  |  | 94.01 |  |  |  | 0.01 |  | 0.58 | [8 empty] | 5.53 |  |  |  |  | 3.30
2015 |  |  |  | 3388.98 |  |  | 7635 |  |  |  | 471 | [10 empty] | 83.58 |  |  |  | 86.81 | [5 empty] | 82.14 |  |  | 87.16 |  |  |  | 0.40 |  | 0.73 | [8 empty] | 12.46 |  |  |  |  | 3.23
2016 |  |  |  | 3425.51 |  |  | 7738 |  |  |  | 471 | [10 empty] | 84.12 |  |  |  | 87.53 | [5 empty] | 82.80 |  |  | 88.09 |  |  |  | 0.45 |  | 2.46 | [8 empty] | 10.00 |  |  |  |  | 3.42
2017 |  |  |  | 3615.51 |  |  | 8231 |  |  |  | 471 | [10 empty] | 89.61 |  |  |  | 93.73 | [5 empty] | 87.63 |  |  | 93.96 |  |  |  | 0.05 |  | 0.89 | [8 empty] | 5.38 |  |  |  |  | 4.12
2018 |  |  |  | 3609.99 |  |  | 8288 |  |  |  | 471 | [10 empty] | 89.51 |  |  |  | 94.39 | [5 empty] | 87.49 |  |  | 94.61 |  |  |  | 0.00 |  | 0.12 | [8 empty] | 5.49 |  |  |  |  | 4.88
2019 |  |  |  | 3625.03 |  |  | 8135 |  |  |  | 471 | [10 empty] | 88.72 |  |  |  | 92.26 | [5 empty] | 87.86 |  |  | 92.87 |  |  |  | 0.33 |  | 0.59 | [8 empty] | 7.14 |  |  |  |  | 3.55
2020 |  |  |  | 3683.59 |  |  | 8236 |  |  |  | 466 | [10 empty] | 89.64 |  |  |  | 92.78 | [5 empty] | 89.11 |  |  | 93.76 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 7.14 |  |  |  |  | 3.14
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 80
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 548 | [14 empty] | 1086
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 92
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 0
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Subtotal | [22 empty] | 548 | [14 empty] | 1178 |  |  |  | 80 | [11 empty] | 7
Total | [22 empty] | 548 | [14 empty] | 1265
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 25
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 0
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 19
Total | [37 empty] | 82
Highlights (2020)
16.02.2020 ordered power reduction - reactor power decreasing to 82,2 % due to main condenser TG32 tubes leakage repair. Steam extraction for district heating exchanger. From 09.03. 2020 to 27.03.2020 ancillary services actuation - secondary frequency control. 18.04.2020 ordered power reduction - reactor power decreasing to 80,4 % due to main condenser TG32 tubes leakage repair and ordered power reduction "–20 MW" reduced energy demand on market. From 29.05.2020 to 03.06.2020 reactor power decreasing to 56 % due to circulating water circuit isolation valves repair (valves in front of main condenser and cooling towers) - approved power reduction. 17.06. - 19.06.2020 coast-down operation. From 20.06.2020 annual maintenance and refuelling, start-up operation, scheduled measuring and testing. 26.08. - 27.08.2020 TG31 shutdown by means of push-button „danger“ after condensate pumps shutdown due to signal „ condensate demineralizer (BUK) TG31 impassibility“. Reactor power decreasing to 58 %. 14.11.2020 ordered power reduction - reactor power decreasing to 79,5 % due to main condenser TG32 tubes leakage repair. 26.12.2020 ordered power reduction - reactor power decreasing to 79,6 % due to main condenser TG31 tubes leakage repair. From 09.2020 steam extraction for district heating exchanger.

## BOHUNICE-4
2020 Operating Experience
SK-14 | [8 empty] | BOHUNICE-4 | [26 empty] | SLOVAKIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SE (SLOVENSKÉ ELEKTRÁRNE , AS.)
Owner | [7 empty] | : | SE (SLOVENSKÉ ELEKTRÁRNE , AS.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-12-01
Thermal power | [12 empty] | : |  |  | 1471 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-08-09
Gross electrical power | [12 empty] | : |  |  | 500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-12-18
Reference unit power (net) | [12 empty] | : |  |  | 466 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.0
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 295
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.245
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 1.25 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 22 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 54000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.32
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.49 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3730.79 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.19 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.23 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.71 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.06 %
Load Factor (LF) | [18 empty] | : | 90.26 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.52 %
Operating Factor (OF) | [18 empty] | : | 92.93 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 621 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 43.83 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 347.70 | 324.23 |  |  |  | 341.46 |  | 333.30 | [8 empty] | 164.21 |  |  | 210.38 | [6 empty] | 335.49 |  | 334.64 |  |  |  | 327.30 |  |  | 341.62 |  |  | 329.41 | [9 empty] | 341.04 |  |  | 3730.79
EAF [%] |  |  |  |  | 98.48 | 98.63 |  |  |  | 97.47 |  | 98.24 | [8 empty] | 47.47 |  |  | 62.80 | [6 empty] | 95.95 |  | 95.54 |  |  |  | 96.59 |  |  | 97.40 |  |  | 97.06 | [9 empty] | 97.06 |  |  | 90.19
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.53 |  | 100.00 | [8 empty] | 48.52 |  |  | 65.12 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.65 | [9 empty] | 100.00 |  |  | 92.71
LF [%] |  |  |  |  | 99.22 | 98.91 |  |  |  | 97.57 |  | 98.28 | [8 empty] | 46.86 |  |  | 62.04 | [6 empty] | 95.74 |  | 95.50 |  |  |  | 96.52 |  |  | 97.36 |  |  | 97.14 | [9 empty] | 98.37 |  |  | 90.26
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 48.79 |  |  | 66.67 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.93
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.82 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.23
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.47 |  | 0.00 | [8 empty] | 51.48 |  |  | 32.06 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.35 | [9 empty] | 0.00 |  |  | 7.06
XUF [%] |  |  |  |  | 1.52 | 1.37 |  |  |  | 2.07 |  | 1.76 | [8 empty] | 1.05 |  |  | 2.32 | [6 empty] | 4.05 |  | 4.46 |  |  |  | 3.41 |  |  | 2.60 |  |  | 2.58 | [9 empty] | 2.94 |  |  | 2.52
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 108107 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.2 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.54 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.17 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.07 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.1 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.43 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 1083.50 |  |  | 3177 |  |  |  | 408 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 2887.85 |  |  | 7294 |  |  |  | 408 | [10 empty] | 80.98 |  |  |  | 80.98 | [5 empty] | 80.80 |  |  | 83.26 |  |  |  | 3.11 |  | 2.60 | [8 empty] | 16.42 |  |  |  |  | 0.00
1987 |  |  |  | 3084.68 |  |  | 7783 |  |  |  | 408 | [10 empty] | 86.11 |  |  |  | 86.60 | [5 empty] | 86.31 |  |  | 88.85 |  |  |  | 0.89 |  | 0.78 | [8 empty] | 12.63 |  |  |  |  | 0.49
1988 |  |  |  | 2786.46 |  |  | 7248 |  |  |  | 408 | [10 empty] | 77.76 |  |  |  | 78.01 | [5 empty] | 77.75 |  |  | 82.51 |  |  |  | 1.22 |  | 0.96 | [8 empty] | 21.02 |  |  |  |  | 0.25
1989 |  |  |  | 2827.66 |  |  | 7548 |  |  |  | 408 | [10 empty] | 79.20 |  |  |  | 79.98 | [5 empty] | 79.12 |  |  | 86.16 |  |  |  | 5.84 |  | 4.96 | [8 empty] | 15.06 |  |  |  |  | 0.78
1990 |  |  |  | 2873.81 |  |  | 7427 |  |  |  | 408 | [10 empty] | 80.71 |  |  |  | 81.99 | [5 empty] | 80.41 |  |  | 84.78 |  |  |  | 1.42 |  | 1.18 | [8 empty] | 16.83 |  |  |  |  | 1.29
1991 |  |  |  | 2850.52 |  |  | 7438 |  |  |  | 408 | [10 empty] | 80.36 |  |  |  | 82.88 | [5 empty] | 79.76 |  |  | 84.91 |  |  |  | 0.54 |  | 0.45 | [8 empty] | 16.66 |  |  |  |  | 2.52
1992 |  |  |  | 2711.90 |  |  | 6714 |  |  |  | 408 | [10 empty] | 70.43 |  |  |  | 73.33 | [5 empty] | 75.67 |  |  | 76.43 |  |  |  | 2.61 |  | 1.96 | [8 empty] | 24.71 |  |  |  |  | 2.89
1993 |  |  |  | 2847.62 |  |  | 7341 |  |  |  | 408 | [10 empty] | 79.68 |  |  |  | 82.63 | [5 empty] | 79.67 |  |  | 83.80 |  |  |  | 5.40 |  | 4.72 | [8 empty] | 12.65 |  |  |  |  | 2.95
1994 |  |  |  | 2791.41 |  |  | 7389 |  |  |  | 405 | [10 empty] | 78.68 |  |  |  | 83.87 | [5 empty] | 78.68 |  |  | 84.35 |  |  |  | 0.30 |  | 0.25 | [8 empty] | 15.88 |  |  |  |  | 5.19
1995 |  |  |  | 2823.67 |  |  | 7211 |  |  |  | 408 | [10 empty] | 79.29 |  |  |  | 88.47 | [5 empty] | 79.00 |  |  | 82.32 |  |  |  | 0.96 |  | 0.86 | [8 empty] | 10.67 |  |  |  |  | 9.18
1996 |  |  |  | 2834.89 |  |  | 6953 |  |  |  | 436 | [10 empty] | 76.13 |  |  |  | 79.21 | [5 empty] | 74.02 |  |  | 79.16 |  |  |  | 0.18 |  | 0.14 | [8 empty] | 20.65 |  |  |  |  | 3.08
1997 |  |  |  | 2953.49 |  |  | 7469 |  |  |  | 440 | [10 empty] | 80.22 |  |  |  | 84.66 | [5 empty] | 76.63 |  |  | 85.26 |  |  |  | 2.41 |  | 2.09 | [8 empty] | 13.25 |  |  |  |  | 4.43
1998 |  |  |  | 2822.41 |  |  | 7525 |  |  |  | 408 | [10 empty] | 82.45 |  |  |  | 85.68 | [5 empty] | 78.97 |  |  | 85.90 |  |  |  | 1.62 |  | 1.41 | [8 empty] | 12.92 |  |  |  |  | 3.23
1999 |  |  |  | 2656.54 |  |  | 7283 |  |  |  | 408 | [10 empty] | 75.13 |  |  |  | 81.68 | [5 empty] | 74.33 |  |  | 83.14 |  |  |  | 2.00 |  | 1.66 | [8 empty] | 16.66 |  |  |  |  | 6.54
2000 |  |  |  | 2431.85 |  |  | 6791 |  |  |  | 408 | [10 empty] | 68.88 |  |  |  | 76.32 | [5 empty] | 67.86 |  |  | 77.31 |  |  |  | 1.40 |  | 1.08 | [8 empty] | 22.60 |  |  |  |  | 7.44
2001 |  |  |  | 2793.27 |  |  | 7721 |  |  |  | 408 | [10 empty] | 79.25 |  |  |  | 86.73 | [5 empty] | 78.15 |  |  | 88.14 |  |  |  | 1.29 |  | 1.13 | [8 empty] | 12.14 |  |  |  |  | 7.48
2002 |  |  |  | 2823.23 |  |  | 7742 |  |  |  | 408 | [10 empty] | 84.99 |  |  |  | 87.88 | [5 empty] | 78.99 |  |  | 88.38 |  |  |  | 0.36 |  | 0.32 | [8 empty] | 11.81 |  |  |  |  | 2.89
2003 |  |  |  | 2814.89 |  |  | 7737 |  |  |  | 408 | [10 empty] | 84.35 |  |  |  | 87.76 | [5 empty] | 78.76 |  |  | 88.32 |  |  |  | 0.42 |  | 0.37 | [8 empty] | 11.87 |  |  |  |  | 3.41
2004 |  |  |  | 2390.94 |  |  | 6786 |  |  |  | 408 | [10 empty] | 74.44 |  |  |  | 76.95 | [5 empty] | 66.71 |  |  | 77.25 |  |  |  | 0.24 |  | 0.18 | [8 empty] | 22.86 |  |  |  |  | 2.51
2005 |  |  |  | 2840.98 |  |  | 7671 |  |  |  | 408 | [10 empty] | 84.31 |  |  |  | 87.29 | [5 empty] | 79.49 |  |  | 87.57 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 12.66 |  |  |  |  | 2.98
2006 |  |  |  | 2489.28 |  |  | 7035 |  |  |  | 408 | [10 empty] | 77.03 |  |  |  | 79.27 | [5 empty] | 69.65 |  |  | 80.31 |  |  |  | 1.06 |  | 0.85 | [8 empty] | 19.89 |  |  |  |  | 2.24
2007 |  |  |  | 2648.45 |  |  | 7053 |  |  |  | 408 | [10 empty] | 77.97 |  |  |  | 79.87 | [5 empty] | 74.10 |  |  | 80.51 |  |  |  | 2.90 |  | 2.39 | [8 empty] | 17.74 |  |  |  |  | 1.90
2008 |  |  |  | 2739.03 |  |  | 7254 |  |  |  | 410 | [10 empty] | 78.82 |  |  |  | 79.65 | [5 empty] | 76.27 |  |  | 82.58 |  |  |  | 2.90 |  | 2.38 | [8 empty] | 17.98 |  |  |  |  | 0.83
2009 |  |  |  | 3239.57 |  |  | 8118 |  |  |  | 448 | [10 empty] | 86.87 |  |  |  | 88.92 | [5 empty] | 87.05 |  |  | 92.67 |  |  |  | 0.67 |  | 0.60 | [8 empty] | 10.48 |  |  |  |  | 2.06
2010 |  |  |  | 3513.14 |  |  | 8214 |  |  |  | 472 | [10 empty] | 87.73 |  |  |  | 90.33 | [5 empty] | 87.55 |  |  | 93.77 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 9.62 |  |  |  |  | 2.60
2011 |  |  |  | 3732.88 |  |  | 8225 |  |  |  | 472 | [10 empty] | 90.80 |  |  |  | 93.43 | [5 empty] | 90.28 |  |  | 93.89 |  |  |  | 0.27 |  | 0.25 | [8 empty] | 6.32 |  |  |  |  | 2.62
2012 |  |  |  | 3640.36 |  |  | 7952 |  |  |  | 472 | [10 empty] | 87.88 |  |  |  | 90.12 | [5 empty] | 87.80 |  |  | 90.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.88 |  |  |  |  | 2.23
2013 |  |  |  | 3788.68 |  |  | 8313 |  |  |  | 471 | [10 empty] | 91.81 |  |  |  | 94.54 | [5 empty] | 91.83 |  |  | 94.90 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 5.40 |  |  |  |  | 2.72
2014 |  |  |  | 3767.52 |  |  | 8314 |  |  |  | 471 | [10 empty] | 91.44 |  |  |  | 94.56 | [5 empty] | 91.31 |  |  | 94.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.44 |  |  |  |  | 3.12
2015 |  |  |  | 3697.16 |  |  | 8285 |  |  |  | 471 | [10 empty] | 91.11 |  |  |  | 94.40 | [5 empty] | 89.61 |  |  | 94.58 |  |  |  | 0.05 |  | 0.54 | [8 empty] | 5.06 |  |  |  |  | 3.28
2016 |  |  |  | 3293.87 |  |  | 7371 |  |  |  | 471 | [10 empty] | 80.22 |  |  |  | 83.23 | [5 empty] | 79.61 |  |  | 83.91 |  |  |  | 0.63 |  | 4.05 | [8 empty] | 12.72 |  |  |  |  | 3.01
2017 |  |  |  | 3648.54 |  |  | 8115 |  |  |  | 471 | [10 empty] | 88.85 |  |  |  | 92.33 | [5 empty] | 88.43 |  |  | 92.64 |  |  |  | 0.12 |  | 2.03 | [8 empty] | 5.64 |  |  |  |  | 3.49
2018 |  |  |  | 3367.93 |  |  | 7553 |  |  |  | 471 | [10 empty] | 82.13 |  |  |  | 85.75 | [5 empty] | 81.63 |  |  | 86.22 |  |  |  | 3.42 |  | 3.57 | [8 empty] | 10.68 |  |  |  |  | 3.62
2019 |  |  |  | 3711.18 |  |  | 8157 |  |  |  | 471 | [10 empty] | 90.02 |  |  |  | 92.85 | [5 empty] | 89.95 |  |  | 93.12 |  |  |  | 0.01 |  | 1.28 | [8 empty] | 5.87 |  |  |  |  | 2.82
2020 |  |  |  | 3730.79 |  |  | 8163 |  |  |  | 466 | [10 empty] | 90.19 |  |  |  | 92.71 | [5 empty] | 90.26 |  |  | 92.93 |  |  |  | 0.00 |  | 0.23 | [8 empty] | 7.06 |  |  |  |  | 2.52
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 20 | [14 empty] | 54
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 600 | [14 empty] | 1045
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 44
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 0
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 16
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 9
Subtotal | [22 empty] | 600 |  |  |  | 20 | [10 empty] | 1106 |  |  |  | 63 | [11 empty] | 0
Total | [22 empty] | 620 | [14 empty] | 1169
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 5
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 28
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [19 empty] | 20 | [14 empty] | 5
33. |  |  | Circulating Water System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 20 | [14 empty] | 63
Highlights (2020)
I.-IV.2020 operation at full power in base load mode. Steam extraction for district heating exchanger. 20.03.2020 reactor power decreasing to 75 % due to main condenser TG42 tubes leakage location and blinding (approved power reduction). 13.04.2020 ordered power reduction – reactor power decreasing to 95,8 % ( reduced energy demand on market). V.-VI.2020 annual maintenance and refuelling, annual maintenance unplanned extension, start-up operation, scheduled measuring and testing. 24.06.2020 ancillary services certification (secondary frequency control). 28.11.2020 reactor power decreasing to 77,7 % due to main condenser TG41 tubes leakage location and blinding (approved power reduction - planned). IX.-XII.2020 steam extraction for district heating exchanger. Operation without any failures.

## MOCHOVCE-1
2020 Operating Experience
SK-6 | [8 empty] | MOCHOVCE-1 | [26 empty] | SLOVAKIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SE (SLOVENSKÉ ELEKTRÁRNE , AS.)
Owner | [7 empty] | : | SE (SLOVENSKÉ ELEKTRÁRNE , AS.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1983-10-13
Thermal power | [12 empty] | : |  |  | 1471 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1998-07-04
Gross electrical power | [12 empty] | : |  |  | 470 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1998-10-29
Reference unit power (net) | [12 empty] | : |  |  | 436 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 22 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.0
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 295
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.245
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.25 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 22 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 54000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.32
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.49 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3610.02 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.82 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.07 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.52 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.42 %
Load Factor (LF) | [18 empty] | : | 94.27 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.69 %
Operating Factor (OF) | [18 empty] | : | 94.75 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 461 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 331.77 | 308.53 |  |  |  | 275.49 |  | 143.31 | [8 empty] | 318.81 |  |  | 305.88 | [6 empty] | 315.87 |  | 315.99 |  |  |  | 315.41 |  |  | 329.96 |  |  | 318.44 | [9 empty] | 330.55 |  |  | 3610.01
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 84.79 |  | 46.51 | [8 empty] | 99.76 |  |  | 98.51 | [6 empty] | 97.87 |  | 98.08 |  |  |  | 99.77 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.82
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 87.25 |  | 46.57 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.72 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.52
LF [%] |  |  |  |  | 102.28 | 101.67 |  |  |  | 85.04 |  | 45.65 | [8 empty] | 98.28 |  |  | 97.44 | [6 empty] | 97.38 |  | 97.41 |  |  |  | 100.47 |  |  | 101.72 |  |  | 101.44 | [9 empty] | 101.90 |  |  | 94.27
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 87.62 |  | 48.75 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.75
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.21 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.59 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.21 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.07
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 12.75 |  | 52.84 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.07 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.42
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 2.46 |  | 0.06 | [8 empty] | 0.24 |  |  | 1.49 | [6 empty] | 2.13 |  | 1.64 |  |  |  | 0.23 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.69
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 70941.75 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.97 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.9 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.01 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.51 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.48 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.04 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.61 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.4 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1998 |  |  |  | 936.28 |  |  | 3343 |  |  |  | 408 | [10 empty] | 94.96 |  |  |  | 96.83 | [5 empty] | 93.54 |  |  | 98.98 |  |  |  | 3.17 |  | 3.17 | [8 empty] | 0.00 |  |  |  |  | 1.87
1999 |  |  |  | 2376.14 |  |  | 6397 |  |  |  | 404 | [10 empty] | 65.82 |  |  |  | 70.37 | [5 empty] | 67.14 |  |  | 73.03 |  |  |  | 3.19 |  | 2.32 | [8 empty] | 27.30 |  |  |  |  | 4.55
2000 |  |  |  | 2816.90 |  |  | 8311 |  |  |  | 404 | [10 empty] | 79.38 |  |  |  | 89.96 | [5 empty] | 79.38 |  |  | 94.62 |  |  |  | 2.46 |  | 2.27 | [8 empty] | 7.77 |  |  |  |  | 10.58
2001 |  |  |  | 2423.59 |  |  | 6648 |  |  |  | 404 | [10 empty] | 68.15 |  |  |  | 74.98 | [5 empty] | 68.48 |  |  | 75.89 |  |  |  | 2.49 |  | 1.92 | [8 empty] | 23.10 |  |  |  |  | 6.83
2002 |  |  |  | 2914.76 |  |  | 7628 |  |  |  | 405 | [10 empty] | 83.31 |  |  |  | 86.32 | [5 empty] | 82.16 |  |  | 87.08 |  |  |  | 0.24 |  | 0.21 | [8 empty] | 13.47 |  |  |  |  | 3.02
2003 |  |  |  | 2796.62 |  |  | 7324 |  |  |  | 405 | [10 empty] | 82.28 |  |  |  | 82.97 | [5 empty] | 78.83 |  |  | 83.61 |  |  |  | 5.91 |  | 5.21 | [8 empty] | 11.82 |  |  |  |  | 0.69
2004 |  |  |  | 2995.97 |  |  | 7801 |  |  |  | 405 | [10 empty] | 88.10 |  |  |  | 88.58 | [5 empty] | 84.22 |  |  | 88.81 |  |  |  | 0.15 |  | 0.13 | [8 empty] | 11.28 |  |  |  |  | 0.48
2005 |  |  |  | 2712.57 |  |  | 7128 |  |  |  | 405 | [10 empty] | 80.33 |  |  |  | 80.76 | [5 empty] | 76.46 |  |  | 81.37 |  |  |  | 0.10 |  | 0.08 | [8 empty] | 19.16 |  |  |  |  | 0.43
2006 |  |  |  | 3059.75 |  |  | 7977 |  |  |  | 405 | [10 empty] | 90.01 |  |  |  | 90.72 | [5 empty] | 86.23 |  |  | 91.05 |  |  |  | 0.43 |  | 0.39 | [8 empty] | 8.88 |  |  |  |  | 0.71
2007 |  |  |  | 3142.72 |  |  | 7954 |  |  |  | 405 | [10 empty] | 89.21 |  |  |  | 90.03 | [5 empty] | 88.58 |  |  | 90.80 |  |  |  | 0.28 |  | 1.79 | [8 empty] | 8.18 |  |  |  |  | 0.82
2008 |  |  |  | 3329.40 |  |  | 8064 |  |  |  | 436 | [10 empty] | 90.62 |  |  |  | 91.05 | [5 empty] | 89.58 |  |  | 91.80 |  |  |  | 0.21 |  | 0.76 | [8 empty] | 8.19 |  |  |  |  | 0.43
2009 |  |  |  | 3111.64 |  |  | 7466 |  |  |  | 436 | [10 empty] | 82.05 |  |  |  | 82.37 | [5 empty] | 81.47 |  |  | 85.23 |  |  |  | 1.27 |  | 1.06 | [8 empty] | 16.57 |  |  |  |  | 0.32
2010 |  |  |  | 3446.79 |  |  | 8074 |  |  |  | 436 | [10 empty] | 91.02 |  |  |  | 91.51 | [5 empty] | 90.25 |  |  | 92.17 |  |  |  | 1.92 |  | 1.79 | [8 empty] | 6.70 |  |  |  |  | 0.49
2011 |  |  |  | 3542.88 |  |  | 8235 |  |  |  | 436 | [10 empty] | 92.92 |  |  |  | 93.27 | [5 empty] | 92.76 |  |  | 94.01 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 6.69 |  |  |  |  | 0.35
2012 |  |  |  | 3532.61 |  |  | 8188 |  |  |  | 436 | [10 empty] | 92.14 |  |  |  | 92.63 | [5 empty] | 92.24 |  |  | 93.21 |  |  |  | 0.81 |  | 0.82 | [8 empty] | 6.55 |  |  |  |  | 0.49
2013 |  |  |  | 3526.15 |  |  | 8195 |  |  |  | 436 | [10 empty] | 92.29 |  |  |  | 93.33 | [5 empty] | 92.32 |  |  | 93.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.67 |  |  |  |  | 1.04
2014 |  |  |  | 3530.12 |  |  | 8259 |  |  |  | 436 | [10 empty] | 92.38 |  |  |  | 92.55 | [5 empty] | 92.43 |  |  | 94.28 |  |  |  | 0.13 |  | 0.55 | [8 empty] | 6.90 |  |  |  |  | 0.18
2015 |  |  |  | 3436.31 |  |  | 8067 |  |  |  | 436 | [10 empty] | 90.98 |  |  |  | 91.59 | [5 empty] | 89.97 |  |  | 92.09 |  |  |  | 0.76 |  | 0.71 | [8 empty] | 7.71 |  |  |  |  | 0.61
2016 |  |  |  | 3478.22 |  |  | 8185 |  |  |  | 436 | [10 empty] | 91.64 |  |  |  | 92.67 | [5 empty] | 90.82 |  |  | 93.18 |  |  |  | 0.42 |  | 0.73 | [8 empty] | 6.60 |  |  |  |  | 1.03
2017 |  |  |  | 3208.45 |  |  | 7542 |  |  |  | 436 | [10 empty] | 84.20 |  |  |  | 84.97 | [5 empty] | 84.00 |  |  | 86.10 |  |  |  | 1.05 |  | 1.07 | [8 empty] | 13.96 |  |  |  |  | 0.77
2018 |  |  |  | 3539.85 |  |  | 8299 |  |  |  | 436 | [10 empty] | 93.39 |  |  |  | 94.37 | [5 empty] | 92.68 |  |  | 94.74 |  |  |  | 0.27 |  | 0.25 | [8 empty] | 5.38 |  |  |  |  | 0.98
2019 |  |  |  | 3547.11 |  |  | 8225 |  |  |  | 436 | [10 empty] | 92.50 |  |  |  | 93.44 | [5 empty] | 92.87 |  |  | 93.89 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 6.47 |  |  |  |  | 0.94
2020 |  |  |  | 3610.01 |  |  | 8322 |  |  |  | 436 | [10 empty] | 93.82 |  |  |  | 94.52 | [5 empty] | 94.27 |  |  | 94.75 |  |  |  | 0.02 |  | 0.07 | [8 empty] | 5.42 |  |  |  |  | 0.69
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1998 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 4 | [14 empty] | 49
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 456 | [14 empty] | 832
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 31
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 8
Z. |  | Other | [39 empty] | 3
Subtotal | [22 empty] | 456 |  |  |  | 4 | [10 empty] | 863 |  |  |  | 60 | [11 empty] | 3
Total | [22 empty] | 460 | [14 empty] | 926
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1998 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [19 empty] | 4 | [14 empty] | 1
16. |  |  | Steam generation systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [22 empty] | 4 | [14 empty] | 52
Highlights (2020)
MOCHOVCE 1 unit was operated at full power in base load mode in 2020. Unit provided grid supporting services for load following - frequency and secondary power control for grid adjustment and tertiary power control. Load-following losses for a period were 13.6 GWh . Over the reporting period there was only one forced unplanned event - Reactor power reduction to 73% due to inadvertent actuation of the reactor coolant pump power relay, occurred in August, with losses of 0.7 GWh. Throughout the year there was no automatic reactor scram and no unplanned full outage. Planned energy loses of 223.6 GWh were caused by general overhaul with refueling in April and supporting services recertifications. Other factors affecting energy generation were limitations due to coast-down operation and environmental conditions.

## MOCHOVCE-2
2020 Operating Experience
SK-7 | [9 empty] | MOCHOVCE-2 | [28 empty] | SLOVAKIA
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | SE (SLOVENSKÉ ELEKTRÁRNE , AS.)
Owner | [8 empty] | : | SE (SLOVENSKÉ ELEKTRÁRNE , AS.)
Reactor Supplier | [8 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [8 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PWR / VVER V-213 | [12 empty] | Construction Date | [16 empty] | : |  |  | 1983-10-13
Thermal power | [14 empty] | : |  |  | 1471 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 1999-12-20
Gross electrical power | [14 empty] | : |  |  | 501 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 2000-04-11
Reference unit power (net) | [14 empty] | : |  |  | 469 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 21 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 12.0
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Vertical | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 295
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 6
| Refuelling type | [15 empty] | : |  |  | OFF-line | [12 empty] | Containment type | [16 empty] | : |  |  | Confinement
| Moderator material | [15 empty] | : |  |  | H2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 0.245
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | 4.25 | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | 12 | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 2
| Part of the core refuelled [%] | [15 empty] | : |  |  | 22 | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | 44000 | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | 2
| Active core diameter [m] | [15 empty] | : |  |  | 2.88 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 4.32
| Active core height/length [m] | [15 empty] | : |  |  | 2.5 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 349 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 13.49 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | 6
| Number of control rod assemblies | [15 empty] | : |  |  | 37 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | 4
| Number of external reactor coolant loops | [15 empty] | : |  |  | 6 | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | 3
| Coolant type | [15 empty] | : |  |  | H2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [20 empty] | : | 3332.8 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 0.11 %
Energy Availability Factor (EAF) | [20 empty] | : | 85.26 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 0.79 %
Unit Capability Factor (UCF) | [20 empty] | : | 85.77 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 13.44 %
Load Factor (LF) | [20 empty] | : | 86.47 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0.5 %
Operating Factor (OF) | [20 empty] | : | 92.35 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 672 hours
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 332.79 |  | 310.22 |  |  |  |  | 328.05 |  | 315.40 | [8 empty] | 322.63 |  |  |  | 309.10 | [6 empty] | 318.26 |  | 233.86 |  |  |  |  | 56.10 |  |  | 122.98 |  |  | 332.75 | [9 empty] | 350.66 |  |  | 3332.80
EAF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 99.94 |  | 99.87 | [8 empty] | 99.61 |  |  |  | 98.18 | [6 empty] | 97.87 |  | 72.46 |  |  |  |  | 18.46 |  |  | 37.17 |  |  | 98.62 | [9 empty] | 99.94 |  |  | 85.26
UCF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 99.99 | [6 empty] | 100.00 |  | 73.87 |  |  |  |  | 18.46 |  |  | 37.24 |  |  | 98.62 | [9 empty] | 100.00 |  |  | 85.77
LF [%] |  |  |  |  | 102.59 |  | 102.23 |  |  |  |  | 101.13 |  | 100.47 | [8 empty] | 99.46 |  |  |  | 98.47 | [6 empty] | 98.11 |  | 72.09 |  |  |  |  | 17.87 |  |  | 37.91 |  |  | 106.00 | [9 empty] | 100.49 |  |  | 86.47
OF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  |  | 37.08 |  |  | 70.70 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.35
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 2.92 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.11
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 9.40 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.79
PUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 26.13 |  |  |  |  | 81.54 |  |  | 53.36 |  |  | 1.38 | [9 empty] | 0.00 |  |  | 13.44
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.06 |  | 0.13 | [8 empty] | 0.39 |  |  |  | 1.82 | [6 empty] | 2.13 |  | 1.42 |  |  |  |  | 0.00 |  |  | 0.07 |  |  | 0.00 | [9 empty] | 0.06 |  |  | 0.50
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 65945.34 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 0.77 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 87.06 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 1.12 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 88.41 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 10.47 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 85.12 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 1.35 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 89.25 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2000 |  |  |  | 2641.42 |  |  |  | 7513 |  |  |  |  | 404 | [10 empty] | 87.87 |  |  |  |  | 91.55 | [5 empty] | 83.34 |  |  | 89.56 |  |  |  |  | 1.67 |  | 1.56 | [8 empty] | 6.89 |  |  |  |  | 3.68
2001 |  |  |  | 2540.88 |  |  |  | 6967 |  |  |  |  | 404 | [10 empty] | 72.10 |  |  |  |  | 78.17 | [5 empty] | 71.80 |  |  | 79.53 |  |  |  |  | 6.46 |  | 5.40 | [8 empty] | 16.43 |  |  |  |  | 6.07
2002 |  |  |  | 2498.36 |  |  |  | 6862 |  |  |  |  | 405 | [10 empty] | 71.67 |  |  |  |  | 76.02 | [5 empty] | 70.42 |  |  | 78.33 |  |  |  |  | 2.28 |  | 1.78 | [8 empty] | 22.20 |  |  |  |  | 4.36
2003 |  |  |  | 2964.87 |  |  |  | 7729 |  |  |  |  | 405 | [10 empty] | 87.37 |  |  |  |  | 87.81 | [5 empty] | 83.57 |  |  | 88.23 |  |  |  |  | 0.52 |  | 0.46 | [8 empty] | 11.73 |  |  |  |  | 0.43
2004 |  |  |  | 2034.50 |  |  |  | 7210 |  |  |  |  | 405 | [10 empty] | 81.41 |  |  |  |  | 81.61 | [5 empty] | 57.19 |  |  | 82.08 |  |  |  |  | 0.43 |  | 1.11 | [8 empty] | 17.28 |  |  |  |  | 0.20
2005 |  |  |  | 3050.88 |  |  |  | 7900 |  |  |  |  | 405 | [10 empty] | 88.52 |  |  |  |  | 89.45 | [5 empty] | 85.99 |  |  | 90.18 |  |  |  |  | 0.51 |  | 0.45 | [8 empty] | 10.09 |  |  |  |  | 0.93
2006 |  |  |  | 2787.17 |  |  |  | 7254 |  |  |  |  | 405 | [10 empty] | 81.05 |  |  |  |  | 82.07 | [5 empty] | 78.56 |  |  | 82.81 |  |  |  |  | 0.59 |  | 0.60 | [8 empty] | 17.33 |  |  |  |  | 1.02
2007 |  |  |  | 3191.35 |  |  |  | 8082 |  |  |  |  | 405 | [10 empty] | 90.85 |  |  |  |  | 91.26 | [5 empty] | 89.95 |  |  | 92.26 |  |  |  |  | 1.11 |  | 1.39 | [8 empty] | 7.36 |  |  |  |  | 0.41
2008 |  |  |  | 3070.50 |  |  |  | 7797 |  |  |  |  | 436 | [10 empty] | 87.85 |  |  |  |  | 88.31 | [5 empty] | 85.22 |  |  | 88.76 |  |  |  |  | 0.31 |  | 0.28 | [8 empty] | 11.41 |  |  |  |  | 0.46
2009 |  |  |  | 3414.88 |  |  |  | 8128 |  |  |  |  | 436 | [10 empty] | 90.86 |  |  |  |  | 91.54 | [5 empty] | 89.41 |  |  | 92.79 |  |  |  |  | 0.50 |  | 0.56 | [8 empty] | 7.90 |  |  |  |  | 0.68
2010 |  |  |  | 3189.95 |  |  |  | 7574 |  |  |  |  | 436 | [10 empty] | 84.38 |  |  |  |  | 85.22 | [5 empty] | 83.52 |  |  | 86.46 |  |  |  |  | 0.83 |  | 0.72 | [8 empty] | 14.07 |  |  |  |  | 0.84
2011 |  |  |  | 3480.32 |  |  |  | 8195 |  |  |  |  | 436 | [10 empty] | 91.55 |  |  |  |  | 92.49 | [5 empty] | 91.12 |  |  | 93.55 |  |  |  |  | 0.33 |  | 0.31 | [8 empty] | 7.21 |  |  |  |  | 0.93
2012 |  |  |  | 3476.42 |  |  |  | 8121 |  |  |  |  | 436 | [10 empty] | 90.40 |  |  |  |  | 91.96 | [5 empty] | 90.77 |  |  | 92.45 |  |  |  |  | 0.35 |  | 1.10 | [8 empty] | 6.94 |  |  |  |  | 1.56
2013 |  |  |  | 3581.83 |  |  |  | 8274 |  |  |  |  | 436 | [10 empty] | 93.27 |  |  |  |  | 94.22 | [5 empty] | 93.78 |  |  | 94.45 |  |  |  |  | 0.11 |  | 0.10 | [8 empty] | 5.68 |  |  |  |  | 0.95
2014 |  |  |  | 3392.49 |  |  |  | 7842 |  |  |  |  | 436 | [10 empty] | 88.41 |  |  |  |  | 89.18 | [5 empty] | 88.82 |  |  | 89.52 |  |  |  |  | 0.16 |  | 1.86 | [8 empty] | 8.96 |  |  |  |  | 0.76
2015 |  |  |  | 3561.23 |  |  |  | 8296 |  |  |  |  | 436 | [10 empty] | 93.39 |  |  |  |  | 94.40 | [5 empty] | 93.24 |  |  | 94.70 |  |  |  |  | 0.01 |  | 0.10 | [8 empty] | 5.50 |  |  |  |  | 1.02
2016 |  |  |  | 3535.75 |  |  |  | 8268 |  |  |  |  | 436 | [10 empty] | 92.59 |  |  |  |  | 93.67 | [5 empty] | 92.32 |  |  | 94.13 |  |  |  |  | 0.50 |  | 1.15 | [8 empty] | 5.18 |  |  |  |  | 1.08
2017 |  |  |  | 3543.32 |  |  |  | 8280 |  |  |  |  | 436 | [10 empty] | 93.20 |  |  |  |  | 94.16 | [5 empty] | 92.77 |  |  | 94.52 |  |  |  |  | 0.15 |  | 0.41 | [8 empty] | 5.43 |  |  |  |  | 0.95
2018 |  |  |  | 3271.12 |  |  |  | 7642 |  |  |  |  | 436 | [10 empty] | 85.31 |  |  |  |  | 86.66 | [5 empty] | 85.65 |  |  | 87.24 |  |  |  |  | 0.38 |  | 0.48 | [8 empty] | 12.86 |  |  |  |  | 1.35
2019 |  |  |  | 3398.93 |  |  |  | 7922 |  |  |  |  | 436 | [10 empty] | 88.65 |  |  |  |  | 89.77 | [5 empty] | 88.99 |  |  | 90.43 |  |  |  |  | 0.18 |  | 3.26 | [8 empty] | 6.97 |  |  |  |  | 1.12
2020 |  |  |  | 3332.80 |  |  |  | 8112 |  |  |  |  | 469 | [10 empty] | 85.26 |  |  |  |  | 85.77 | [5 empty] | 86.47 |  |  | 92.35 |  |  |  |  | 0.11 |  | 0.79 | [8 empty] | 13.44 |  |  |  |  | 0.50
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2020 | [16 empty] | 2000 to 2020
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [27 empty] | 70 | [15 empty] | 63
C. |  | Inspection, maintenance or repair combined with refuelling | [22 empty] | 600 | [16 empty] | 788
D. |  | Inspection, maintenance or repair without refuelling | [39 empty] | 76
L. |  | Human factor related | [43 empty] | 5
Subtotal | [24 empty] | 600 |  |  |  |  | 70 | [11 empty] | 864 |  |  |  | 68
Total | [24 empty] | 670 | [16 empty] | 932
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2020 | [16 empty] | 2000 to 2020
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [38 empty] | 3
12. |  |  | Reactor I&C Systems | [38 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [38 empty] | 3
14. |  |  | Safety Systems | [38 empty] | 7
15. |  |  | Reactor Cooling Systems | [21 empty] | 62 | [16 empty] | 28
16. |  |  | Steam generation systems | [38 empty] | 9
21. |  |  | Fuel Handling and Storage Facilities | [38 empty] | 2
31. |  |  | Turbine and auxiliaries | [21 empty] | 8 | [16 empty] | 2
33. |  |  | Circulating Water System | [38 empty] | 1
41. |  |  | Main Generator Systems | [38 empty] | 3
42. |  |  | Electrical Power Supply Systems | [38 empty] | 3
Total | [24 empty] | 70 | [16 empty] | 62
RUP revision during the year (2020) due to power uprate
RUP at the end of previous year : 436 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
December | [5 empty] | 469 |  |  |  |  | Extended power uprate (>7%) | [14 empty] | Balance of plant | [13 empty] | The RUPnet was increased from 436 to 468.8 MWe after the completion of the modernization project in order to increase the efficiency of the unit. During this projekt, the important equipment of secondary circuit was replaced, such as the high-pressur
Highlights (2020)
MOCHOVCE 2 unit was largely operated at full power in base load mode in 2020. Unit provided grid supporting services for load following - frequency and secondary power control for grid adjustment and tertiary power control. Load-following losses for a period were 4.6 GWh . Throughout the year there was no automatic reactor scram. Unplanned outages caused forced losses of 32.9 GWh. The most of them 29.0 GWh were caused by the extension of the general overhaul. Planned energy loses of 558.5 GWh were caused by general overhaul with refueling and by operation with one turbogenerator before and after the general overhaul. During these planned outages the major balance-of-plant equipment was replaced and modified in order to increase the efficiency of the unit. The result of this project was the increase of gross electrical power from 470 MW to 500 MW.