## ALMARAZ-1
2020 Operating Experience
ES-6 | [8 empty] | ALMARAZ-1 | [26 empty] | SPAIN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CNAT (CENTRALES NUCLEARES ALMARAZ-TRILLO (ID/UFG/ENDESA/HC/NUCLENOR))
Owner | [7 empty] | : | ID/EN/GN (Iberdrola, Endesa, Gas Natural)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-07-03
Thermal power | [12 empty] | : |  |  | 2947 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-05-01
Gross electrical power | [12 empty] | : |  |  | 1049 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-09-01
Reference unit power (net) | [12 empty] | : |  |  | 1011 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 3.5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.60 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 58000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.9
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6913.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.66 %
Energy Availability Factor (EAF) | [18 empty] | : | 77.54 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.34 %
Unit Capability Factor (UCF) | [18 empty] | : | 79.58 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 19.08 %
Load Factor (LF) | [18 empty] | : | 77.85 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.04 %
Operating Factor (OF) | [18 empty] | : | 80.43 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1719 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 750.38 | 690.98 |  |  |  | 724.15 |  | 286.34 | [8 empty] | 0.00 |  |  | 76.27 | [6 empty] | 732.64 |  | 719.38 |  |  |  | 713.13 |  |  | 745.17 |  |  | 722.58 | [9 empty] | 752.11 |  |  | 6913.13
EAF [%] |  |  |  |  | 99.76 | 99.33 |  |  |  | 97.91 |  | 39.34 | [8 empty] | 0.00 |  |  | 10.48 | [6 empty] | 97.40 |  | 95.64 |  |  |  | 97.97 |  |  | 98.93 |  |  | 92.89 | [9 empty] | 99.99 |  |  | 77.54
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 45.42 | [8 empty] | 0.00 |  |  | 10.48 | [6 empty] | 100.00 |  | 98.38 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.98 | [9 empty] | 100.00 |  |  | 79.58
LF [%] |  |  |  |  | 99.76 | 98.20 |  |  |  | 96.40 |  | 39.34 | [8 empty] | 0.00 |  |  | 10.48 | [6 empty] | 97.40 |  | 95.64 |  |  |  | 97.97 |  |  | 98.93 |  |  | 99.27 | [9 empty] | 99.99 |  |  | 77.85
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 46.11 | [8 empty] | 0.00 |  |  | 18.47 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.43
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 58.42 | [6 empty] | 0.00 |  | 1.62 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.66
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 14.72 | [6 empty] | 0.00 |  | 1.62 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.34
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 54.58 | [8 empty] | 100.00 |  |  | 74.80 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 19.08
XUF [%] |  |  |  |  | 0.24 | 0.67 |  |  |  | 2.09 |  | 6.09 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 2.60 |  | 2.74 |  |  |  | 2.03 |  |  | 1.07 |  |  | 7.09 | [9 empty] | 0.01 |  |  | 2.04
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 271512.12 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.42 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.95 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.21 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.79 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.01 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.05 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.51 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 3713.90 |  |  | 5925 |  |  |  | 930 | [10 empty] | 78.42 |  |  |  | 78.42 | [5 empty] | 78.40 |  |  | 88.67 |  |  |  | 1.07 |  | 0.85 | [8 empty] | 20.73 |  |  |  |  | 0.00
1984 |  |  |  | 4820.50 |  |  | 6062 |  |  |  | 893 | [10 empty] | 65.03 |  |  |  | 65.03 | [5 empty] | 61.45 |  |  | 69.01 |  |  |  | 6.16 |  | 4.27 | [8 empty] | 30.71 |  |  |  |  | 0.00
1985 |  |  |  | 4825.17 |  |  | 5705 |  |  |  | 900 | [10 empty] | 61.63 |  |  |  | 61.63 | [5 empty] | 61.20 |  |  | 65.13 |  |  |  | 7.22 |  | 4.80 | [8 empty] | 33.57 |  |  |  |  | 0.00
1986 |  |  |  | 5425.02 |  |  | 6418 |  |  |  | 900 | [10 empty] | 69.29 |  |  |  | 69.29 | [5 empty] | 68.81 |  |  | 73.26 |  |  |  | 10.45 |  | 8.08 | [8 empty] | 22.63 |  |  |  |  | 0.00
1987 |  |  |  | 7193.69 |  |  | 8346 |  |  |  | 900 | [10 empty] | 92.54 |  |  |  | 92.54 | [5 empty] | 91.24 |  |  | 95.27 |  |  |  | 2.97 |  | 2.83 | [8 empty] | 4.63 |  |  |  |  | 0.00
1988 |  |  |  | 5879.59 |  |  | 6899 |  |  |  | 900 | [10 empty] | 74.60 |  |  |  | 74.60 | [5 empty] | 74.37 |  |  | 78.54 |  |  |  | 15.76 |  | 13.96 | [8 empty] | 11.45 |  |  |  |  | 0.00
1989 |  |  |  | 6562.18 |  |  | 7640 |  |  |  | 895 | [10 empty] | 83.20 |  |  |  | 83.20 | [5 empty] | 83.70 |  |  | 87.21 |  |  |  | 1.90 |  | 1.61 | [8 empty] | 15.19 |  |  |  |  | 0.00
1990 |  |  |  | 6460.66 |  |  | 7451 |  |  |  | 895 | [10 empty] | 82.22 |  |  |  | 82.22 | [5 empty] | 82.40 |  |  | 85.06 |  |  |  | 1.63 |  | 1.36 | [8 empty] | 16.42 |  |  |  |  | 0.00
1991 |  |  |  | 7481.71 |  |  | 8589 |  |  |  | 895 | [10 empty] | 96.20 |  |  |  | 96.20 | [5 empty] | 95.43 |  |  | 98.05 |  |  |  | 2.72 |  | 2.69 | [8 empty] | 1.11 |  |  |  |  | 0.00
1992 |  |  |  | 6379.06 |  |  | 7387 |  |  |  | 895 | [10 empty] | 80.76 |  |  |  | 80.76 | [5 empty] | 81.14 |  |  | 84.10 |  |  |  | 1.88 |  | 1.55 | [8 empty] | 17.68 |  |  |  |  | 0.00
1993 |  |  |  | 6530.85 |  |  | 7663 |  |  |  | 895 | [10 empty] | 83.19 |  |  |  | 85.05 | [5 empty] | 83.30 |  |  | 87.48 |  |  |  | 4.26 |  | 3.78 | [8 empty] | 11.17 |  |  |  |  | 1.86
1994 |  |  |  | 7448.60 |  |  | 8495 |  |  |  | 895 | [10 empty] | 95.05 |  |  |  | 95.92 | [5 empty] | 95.01 |  |  | 96.97 |  |  |  | 3.38 |  | 3.36 | [8 empty] | 0.73 |  |  |  |  | 0.86
1995 |  |  |  | 6588.46 |  |  | 7709 |  |  |  | 895 | [10 empty] | 83.74 |  |  |  | 86.23 | [5 empty] | 84.03 |  |  | 88.00 |  |  |  | 3.41 |  | 3.05 | [8 empty] | 10.73 |  |  |  |  | 2.49
1996 |  |  |  | 5904.30 |  |  | 6789 |  |  |  | 895 | [10 empty] | 72.53 |  |  |  | 73.77 | [5 empty] | 75.10 |  |  | 77.29 |  |  |  | 2.81 |  | 2.13 | [8 empty] | 24.09 |  |  |  |  | 1.24
1997 |  |  |  | 6642.83 |  |  | 7371 |  |  |  | 895 | [10 empty] | 79.57 |  |  |  | 82.95 | [5 empty] | 84.73 |  |  | 84.14 |  |  |  | 3.20 |  | 2.75 | [8 empty] | 14.30 |  |  |  |  | 3.38
1998 |  |  |  | 8032.46 |  |  | 8760 |  |  |  | 944 | [10 empty] | 97.12 |  |  |  | 98.81 | [5 empty] | 97.13 |  |  | 100.00 |  |  |  | 1.19 |  | 1.19 | [8 empty] | 0.00 |  |  |  |  | 1.69
1999 |  |  |  | 6988.63 |  |  | 7613 |  |  |  | 927 | [10 empty] | 84.68 |  |  |  | 85.40 | [5 empty] | 86.06 |  |  | 86.91 |  |  |  | 2.93 |  | 2.58 | [8 empty] | 12.01 |  |  |  |  | 0.73
2000 |  |  |  | 7471.57 |  |  | 8014 |  |  |  | 927 | [10 empty] | 90.32 |  |  |  | 91.08 | [5 empty] | 91.76 |  |  | 91.23 |  |  |  | 1.08 |  | 0.99 | [8 empty] | 7.93 |  |  |  |  | 0.76
2001 |  |  |  | 8151.39 |  |  | 8749 |  |  |  | 927 | [10 empty] | 99.02 |  |  |  | 99.59 | [5 empty] | 100.38 |  |  | 99.87 |  |  |  | 0.41 |  | 0.41 | [8 empty] | 0.00 |  |  |  |  | 0.56
2002 |  |  |  | 7427.99 |  |  | 8100 |  |  |  | 944 | [10 empty] | 90.38 |  |  |  | 92.21 | [5 empty] | 89.82 |  |  | 92.47 |  |  |  | 0.66 |  | 0.61 | [8 empty] | 7.17 |  |  |  |  | 1.83
2003 |  |  |  | 7499.11 |  |  | 8233 |  |  |  | 944 | [10 empty] | 91.59 |  |  |  | 93.76 | [5 empty] | 90.68 |  |  | 93.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.24 |  |  |  |  | 2.17
2004 |  |  |  | 8185.69 |  |  | 8784 |  |  |  | 944 | [10 empty] | 99.23 |  |  |  | 99.90 | [5 empty] | 98.72 |  |  | 100.00 |  |  |  | 0.10 |  | 0.10 | [8 empty] | 0.01 |  |  |  |  | 0.67
2005 |  |  |  | 7519.43 |  |  | 8180 |  |  |  | 944 | [10 empty] | 91.45 |  |  |  | 93.06 | [5 empty] | 90.93 |  |  | 93.38 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 6.92 |  |  |  |  | 1.61
2006 |  |  |  | 7152.42 |  |  | 7831 |  |  |  | 944 | [10 empty] | 86.54 |  |  |  | 88.07 | [5 empty] | 86.49 |  |  | 89.39 |  |  |  | 1.96 |  | 1.76 | [8 empty] | 10.17 |  |  |  |  | 1.54
2007 |  |  |  | 8189.80 |  |  | 8760 |  |  |  | 944 | [10 empty] | 98.98 |  |  |  | 99.93 | [5 empty] | 99.04 |  |  | 100.00 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 0.00 |  |  |  |  | 0.95
2008 |  |  |  | 7190.76 |  |  | 7725 |  |  |  | 944 | [10 empty] | 86.61 |  |  |  | 87.16 | [5 empty] | 86.72 |  |  | 87.94 |  |  |  | 0.10 |  | 2.08 | [8 empty] | 10.77 |  |  |  |  | 0.55
2009 |  |  |  | 6880.10 |  |  | 7336 |  |  |  | 944 | [10 empty] | 82.85 |  |  |  | 83.73 | [5 empty] | 83.20 |  |  | 83.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.27 |  |  |  |  | 0.88
2010 |  |  |  | 7884.25 |  |  | 8147 |  |  |  | 1008 | [10 empty] | 89.67 |  |  |  | 90.50 | [5 empty] | 89.70 |  |  | 93.00 |  |  |  | 3.31 |  | 3.10 | [8 empty] | 6.40 |  |  |  |  | 0.82
2011 |  |  |  | 7519.49 |  |  | 7814 |  |  |  | 1011 | [10 empty] | 84.91 |  |  |  | 86.77 | [5 empty] | 84.90 |  |  | 89.20 |  |  |  | 0.94 |  | 0.82 | [8 empty] | 12.41 |  |  |  |  | 1.86
2012 |  |  |  | 7346.07 |  |  | 7405 |  |  |  | 1004 | [10 empty] | 85.00 |  |  |  | 85.90 | [5 empty] | 83.30 |  |  | 84.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.10 |  |  |  |  | 0.90
2013 |  |  |  | 7695.84 |  |  | 7882 |  |  |  | 1011 | [10 empty] | 87.08 |  |  |  | 88.34 | [5 empty] | 86.90 |  |  | 89.98 |  |  |  | 8.65 |  | 8.36 | [8 empty] | 3.30 |  |  |  |  | 1.26
2014 |  |  |  | 7252.45 |  |  | 7351 |  |  |  | 1011 | [10 empty] | 81.86 |  |  |  | 82.70 | [5 empty] | 81.89 |  |  | 83.92 |  |  |  | 0.56 |  | 0.47 | [8 empty] | 16.83 |  |  |  |  | 0.84
2015 |  |  |  | 8438.61 |  |  | 8613 |  |  |  | 1011 | [10 empty] | 95.28 |  |  |  | 96.61 | [5 empty] | 95.28 |  |  | 98.32 |  |  |  | 1.43 |  | 1.41 | [8 empty] | 1.98 |  |  |  |  | 1.33
2016 |  |  |  | 7447.79 |  |  | 7622 |  |  |  | 1011 | [10 empty] | 84.08 |  |  |  | 86.06 | [5 empty] | 83.87 |  |  | 86.77 |  |  |  | 0.43 |  | 0.37 | [8 empty] | 13.57 |  |  |  |  | 1.98
2017 |  |  |  | 7753.93 |  |  | 7885 |  |  |  | 1011 | [10 empty] | 87.55 |  |  |  | 88.77 | [5 empty] | 87.55 |  |  | 90.01 |  |  |  | 1.44 |  | 1.29 | [8 empty] | 9.94 |  |  |  |  | 1.22
2018 |  |  |  | 7844.02 |  |  | 7934 |  |  |  | 1011 | [10 empty] | 88.69 |  |  |  | 89.96 | [5 empty] | 88.57 |  |  | 90.57 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 10.01 |  |  |  |  | 1.27
2019 |  |  |  | 8662.82 |  |  | 8760 |  |  |  | 1011 | [10 empty] | 98.05 |  |  |  | 99.42 | [5 empty] | 97.81 |  |  | 100.00 |  |  |  | 0.57 |  | 0.57 | [8 empty] | 0.01 |  |  |  |  | 1.37
2020 |  |  |  | 6913.13 |  |  | 7065 |  |  |  | 1011 | [10 empty] | 77.54 |  |  |  | 79.58 | [5 empty] | 77.85 |  |  | 80.43 |  |  |  | 1.66 |  | 1.34 | [8 empty] | 19.08 |  |  |  |  | 2.04
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 108 | [14 empty] | 125
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1624 | [14 empty] | 810
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 159
E. |  | Testing of plant systems or components | [35 empty] | 45 |  |  |  | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 3
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 1624 |  |  |  | 108 | [10 empty] | 1014 |  |  |  | 129 | [11 empty] | 4
Total | [22 empty] | 1732 | [14 empty] | 1147
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 28
15. |  |  | Reactor Cooling Systems | [34 empty] | 10
16. |  |  | Steam generation systems | [34 empty] | 4
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 18
33. |  |  | Circulating Water System | [34 empty] | 1
41. |  |  | Main Generator Systems | [19 empty] | 108 | [14 empty] | 25
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [22 empty] | 108 | [14 empty] | 123
Highlights (2020)
Twenty-seventh refueling.

## ALMARAZ-2
2020 Operating Experience
ES-7 | [8 empty] | ALMARAZ-2 | [26 empty] | SPAIN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CNAT (CENTRALES NUCLEARES ALMARAZ-TRILLO (ID/UFG/ENDESA/HC/NUCLENOR))
Owner | [7 empty] | : | ID/EN/GN (Iberdrola, Endesa, Gas Natural)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-07-03
Thermal power | [12 empty] | : |  |  | 2947 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-10-08
Gross electrical power | [12 empty] | : |  |  | 1044 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-07-01
Reference unit power (net) | [12 empty] | : |  |  | 1006 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 3.5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.60 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 58000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.9
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8366.41 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.77 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.82 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.77 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.22 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 94.68 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.4 %
Operating Factor (OF) | [18 empty] | : | 99.51 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 43 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 748.38 | 687.30 |  |  |  | 727.47 |  | 607.66 | [8 empty] | 606.68 |  |  | 655.79 | [6 empty] | 717.55 |  | 717.02 |  |  |  | 698.33 |  |  | 736.95 |  |  | 716.42 | [9 empty] | 746.85 |  |  | 8366.41
EAF [%] |  |  |  |  | 99.99 | 99.46 |  |  |  | 99.52 |  | 99.42 | [8 empty] | 99.72 |  |  | 90.54 | [6 empty] | 95.87 |  | 95.80 |  |  |  | 96.41 |  |  | 98.33 |  |  | 98.91 | [9 empty] | 99.78 |  |  | 97.82
UCF [%] |  |  |  |  | 100.00 | 99.98 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 91.41 | [6 empty] | 99.52 |  | 99.96 |  |  |  | 99.63 |  |  | 100.00 |  |  | 99.97 | [9 empty] | 100.00 |  |  | 99.22
LF [%] |  |  |  |  | 99.99 | 98.16 |  |  |  | 97.33 |  | 83.89 | [8 empty] | 81.06 |  |  | 90.54 | [6 empty] | 95.87 |  | 95.80 |  |  |  | 96.41 |  |  | 98.33 |  |  | 98.91 | [9 empty] | 99.78 |  |  | 94.68
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 94.03 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.51
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 8.59 | [6 empty] | 0.48 |  | 0.00 |  |  |  | 0.37 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.77
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 8.59 | [6 empty] | 0.48 |  | 0.00 |  |  |  | 0.37 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.77
PUF [%] |  |  |  |  | 0.00 | 0.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.04 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.03 | [9 empty] | 0.00 |  |  | 0.01
XUF [%] |  |  |  |  | 0.01 | 0.51 |  |  |  | 0.48 |  | 0.58 | [8 empty] | 0.28 |  |  | 0.87 | [6 empty] | 3.65 |  | 4.16 |  |  |  | 3.22 |  |  | 1.67 |  |  | 1.06 | [9 empty] | 0.22 |  |  | 1.40
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 268975.41 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.26 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.68 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.81 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.75 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.11 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.28 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 6012.94 |  |  | 7502 |  |  |  | 893 | [10 empty] | 86.01 |  |  |  | 86.01 | [5 empty] | 81.25 |  |  | 90.31 |  |  |  | 6.46 |  | 5.94 | [8 empty] | 8.05 |  |  |  |  | 0.00
1985 |  |  |  | 6236.07 |  |  | 7297 |  |  |  | 900 | [10 empty] | 79.84 |  |  |  | 79.84 | [5 empty] | 79.10 |  |  | 83.30 |  |  |  | 2.74 |  | 2.25 | [8 empty] | 17.91 |  |  |  |  | 0.00
1986 |  |  |  | 5825.18 |  |  | 7136 |  |  |  | 900 | [10 empty] | 75.23 |  |  |  | 75.23 | [5 empty] | 73.89 |  |  | 81.46 |  |  |  | 4.46 |  | 3.51 | [8 empty] | 21.26 |  |  |  |  | 0.00
1987 |  |  |  | 6402.53 |  |  | 7351 |  |  |  | 900 | [10 empty] | 81.78 |  |  |  | 81.78 | [5 empty] | 81.21 |  |  | 83.92 |  |  |  | 2.13 |  | 1.78 | [8 empty] | 16.45 |  |  |  |  | 0.00
1988 |  |  |  | 6809.37 |  |  | 7838 |  |  |  | 900 | [10 empty] | 86.26 |  |  |  | 86.26 | [5 empty] | 86.13 |  |  | 89.23 |  |  |  | 2.06 |  | 1.81 | [8 empty] | 11.93 |  |  |  |  | 0.00
1989 |  |  |  | 6545.67 |  |  | 7638 |  |  |  | 895 | [10 empty] | 82.83 |  |  |  | 82.83 | [5 empty] | 83.49 |  |  | 87.19 |  |  |  | 5.23 |  | 4.57 | [8 empty] | 12.60 |  |  |  |  | 0.00
1990 |  |  |  | 7649.30 |  |  | 8652 |  |  |  | 895 | [10 empty] | 97.39 |  |  |  | 97.39 | [5 empty] | 97.57 |  |  | 98.77 |  |  |  | 1.08 |  | 1.06 | [8 empty] | 1.54 |  |  |  |  | 0.00
1991 |  |  |  | 6812.87 |  |  | 7712 |  |  |  | 895 | [10 empty] | 85.35 |  |  |  | 85.35 | [5 empty] | 86.90 |  |  | 88.04 |  |  |  | 2.01 |  | 1.75 | [8 empty] | 12.90 |  |  |  |  | 0.00
1992 |  |  |  | 6892.72 |  |  | 7997 |  |  |  | 895 | [10 empty] | 87.33 |  |  |  | 87.33 | [5 empty] | 87.67 |  |  | 91.04 |  |  |  | 0.66 |  | 0.58 | [8 empty] | 12.09 |  |  |  |  | 0.00
1993 |  |  |  | 7710.14 |  |  | 8760 |  |  |  | 895 | [10 empty] | 98.54 |  |  |  | 98.99 | [5 empty] | 98.34 |  |  | 100.00 |  |  |  | 0.94 |  | 0.94 | [8 empty] | 0.07 |  |  |  |  | 0.45
1994 |  |  |  | 6384.58 |  |  | 7562 |  |  |  | 895 | [10 empty] | 80.89 |  |  |  | 84.25 | [5 empty] | 81.43 |  |  | 86.32 |  |  |  | 1.56 |  | 1.34 | [8 empty] | 14.42 |  |  |  |  | 3.35
1995 |  |  |  | 6814.74 |  |  | 7952 |  |  |  | 895 | [10 empty] | 86.18 |  |  |  | 89.05 | [5 empty] | 86.92 |  |  | 90.78 |  |  |  | 1.22 |  | 1.10 | [8 empty] | 9.85 |  |  |  |  | 2.87
1996 |  |  |  | 7273.32 |  |  | 8108 |  |  |  | 895 | [10 empty] | 91.50 |  |  |  | 91.64 | [5 empty] | 92.52 |  |  | 92.30 |  |  |  | 8.16 |  | 8.15 | [8 empty] | 0.22 |  |  |  |  | 0.13
1997 |  |  |  | 6042.50 |  |  | 6811 |  |  |  | 895 | [10 empty] | 72.56 |  |  |  | 76.60 | [5 empty] | 77.07 |  |  | 77.75 |  |  |  | 3.68 |  | 2.93 | [8 empty] | 20.47 |  |  |  |  | 4.04
1998 |  |  |  | 5892.43 |  |  | 6810 |  |  |  | 953 | [10 empty] | 70.16 |  |  |  | 75.90 | [5 empty] | 70.58 |  |  | 77.74 |  |  |  | 13.09 |  | 11.43 | [8 empty] | 12.67 |  |  |  |  | 5.75
1999 |  |  |  | 8126.64 |  |  | 8743 |  |  |  | 936 | [10 empty] | 97.41 |  |  |  | 98.04 | [5 empty] | 99.11 |  |  | 99.81 |  |  |  | 1.96 |  | 1.96 | [8 empty] | 0.00 |  |  |  |  | 0.63
2000 |  |  |  | 7401.83 |  |  | 8160 |  |  |  | 936 | [10 empty] | 88.45 |  |  |  | 90.58 | [5 empty] | 90.03 |  |  | 92.90 |  |  |  | 1.69 |  | 1.56 | [8 empty] | 7.86 |  |  |  |  | 2.13
2001 |  |  |  | 7601.46 |  |  | 8189 |  |  |  | 936 | [10 empty] | 91.33 |  |  |  | 92.08 | [5 empty] | 92.71 |  |  | 93.48 |  |  |  | 1.56 |  | 1.46 | [8 empty] | 6.45 |  |  |  |  | 0.75
2002 |  |  |  | 8154.94 |  |  | 8760 |  |  |  | 953 | [10 empty] | 98.10 |  |  |  | 98.84 | [5 empty] | 97.68 |  |  | 100.00 |  |  |  | 1.14 |  | 1.14 | [8 empty] | 0.01 |  |  |  |  | 0.75
2003 |  |  |  | 6627.94 |  |  | 7391 |  |  |  | 953 | [10 empty] | 79.90 |  |  |  | 81.88 | [5 empty] | 79.39 |  |  | 84.37 |  |  |  | 4.75 |  | 10.80 | [8 empty] | 7.32 |  |  |  |  | 1.97
2004 |  |  |  | 7563.17 |  |  | 8083 |  |  |  | 953 | [10 empty] | 90.93 |  |  |  | 91.63 | [5 empty] | 90.35 |  |  | 92.02 |  |  |  | 1.00 |  | 0.92 | [8 empty] | 7.45 |  |  |  |  | 0.69
2005 |  |  |  | 8253.32 |  |  | 8760 |  |  |  | 956 | [10 empty] | 99.24 |  |  |  | 99.96 | [5 empty] | 98.55 |  |  | 100.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.00 |  |  |  |  | 0.73
2006 |  |  |  | 7250.11 |  |  | 7747 |  |  |  | 956 | [10 empty] | 86.78 |  |  |  | 87.71 | [5 empty] | 86.56 |  |  | 88.43 |  |  |  | 5.41 |  | 5.02 | [8 empty] | 7.27 |  |  |  |  | 0.93
2007 |  |  |  | 7191.67 |  |  | 7668 |  |  |  | 956 | [10 empty] | 86.04 |  |  |  | 87.11 | [5 empty] | 85.88 |  |  | 87.53 |  |  |  | 0.00 |  | 1.38 | [8 empty] | 11.51 |  |  |  |  | 1.07
2008 |  |  |  | 8331.69 |  |  | 8784 |  |  |  | 956 | [10 empty] | 99.22 |  |  |  | 99.98 | [5 empty] | 99.22 |  |  | 100.00 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 0.00 |  |  |  |  | 0.76
2009 |  |  |  | 6864.58 |  |  | 7367 |  |  |  | 956 | [10 empty] | 82.01 |  |  |  | 82.91 | [5 empty] | 81.97 |  |  | 84.10 |  |  |  | 2.19 |  | 4.60 | [8 empty] | 12.49 |  |  |  |  | 0.90
2010 |  |  |  | 7007.03 |  |  | 7572 |  |  |  | 956 | [10 empty] | 83.79 |  |  |  | 85.50 | [5 empty] | 83.67 |  |  | 86.44 |  |  |  | 3.74 |  | 3.32 | [8 empty] | 11.18 |  |  |  |  | 1.71
2011 |  |  |  | 7737.28 |  |  | 7991 |  |  |  | 1006 | [10 empty] | 88.07 |  |  |  | 88.58 | [5 empty] | 88.17 |  |  | 91.22 |  |  |  | 2.84 |  | 2.59 | [8 empty] | 8.83 |  |  |  |  | 0.51
2012 |  |  |  | 7698.78 |  |  | 7730 |  |  |  | 1006 | [10 empty] | 87.55 |  |  |  | 88.16 | [5 empty] | 87.12 |  |  | 88.00 |  |  |  | 0.00 |  | 0.22 | [8 empty] | 11.63 |  |  |  |  | 0.61
2013 |  |  |  | 7412.90 |  |  | 7557 |  |  |  | 1006 | [10 empty] | 84.00 |  |  |  | 85.90 | [5 empty] | 84.12 |  |  | 86.27 |  |  |  | 3.94 |  | 3.52 | [8 empty] | 10.58 |  |  |  |  | 1.90
2014 |  |  |  | 7949.00 |  |  | 8054 |  |  |  | 1006 | [10 empty] | 90.18 |  |  |  | 91.06 | [5 empty] | 90.20 |  |  | 91.94 |  |  |  | 1.78 |  | 1.65 | [8 empty] | 7.29 |  |  |  |  | 0.88
2015 |  |  |  | 7635.93 |  |  | 7709 |  |  |  | 1006 | [10 empty] | 86.58 |  |  |  | 87.06 | [5 empty] | 86.65 |  |  | 88.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.94 |  |  |  |  | 0.47
2016 |  |  |  | 7726.48 |  |  | 7827 |  |  |  | 1006 | [10 empty] | 87.88 |  |  |  | 88.56 | [5 empty] | 87.44 |  |  | 89.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.44 |  |  |  |  | 0.68
2017 |  |  |  | 8593.49 |  |  | 8656 |  |  |  | 1006 | [10 empty] | 97.36 |  |  |  | 98.47 | [5 empty] | 97.51 |  |  | 98.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.53 |  |  |  |  | 1.11
2018 |  |  |  | 7854.88 |  |  | 7969 |  |  |  | 1006 | [10 empty] | 88.97 |  |  |  | 90.40 | [5 empty] | 89.13 |  |  | 90.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.60 |  |  |  |  | 1.43
2019 |  |  |  | 7662.81 |  |  | 7824 |  |  |  | 1006 | [10 empty] | 86.95 |  |  |  | 88.66 | [5 empty] | 86.95 |  |  | 89.32 |  |  |  | 0.00 |  | 1.36 | [8 empty] | 9.98 |  |  |  |  | 1.70
2020 |  |  |  | 8366.41 |  |  | 8741 |  |  |  | 1006 | [10 empty] | 97.82 |  |  |  | 99.22 | [5 empty] | 94.68 |  |  | 99.51 |  |  |  | 0.77 |  | 0.77 | [8 empty] | 0.01 |  |  |  |  | 1.40
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 93 | [14 empty] | 129
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 689 |  |  |  | 5
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 17
E. |  | Testing of plant systems or components | [35 empty] | 29
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 7
Z. |  | Other | [39 empty] | 8
Subtotal | [26 empty] | 93 | [10 empty] | 735 |  |  |  | 149 | [11 empty] | 2
Total | [22 empty] | 93 | [14 empty] | 886
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 93 | [14 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 16
16. |  |  | Steam generation systems | [34 empty] | 22
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 23
32. |  |  | Feedwater and Main Steam System | [34 empty] | 22
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 16
42. |  |  | Electrical Power Supply Systems | [34 empty] | 24
Total | [22 empty] | 93 | [14 empty] | 142

## ASCO-1
2020 Operating Experience
ES-8 | [8 empty] | ASCO-1 | [26 empty] | SPAIN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ANAV (ASOCIACIÓN NUCLEAR ASCÓ-VANDELLÓS A.I.E. (ENDESA/ID))
Owner | [7 empty] | : | ENDESA (ENDESA, S.A.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-05-16
Thermal power | [12 empty] | : |  |  | 2941 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-08-13
Gross electrical power | [12 empty] | : |  |  | 1033 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-12-10
Reference unit power (net) | [12 empty] | : |  |  | 995 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.72
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 3.86
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 28 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.6
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.92 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7669.03 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.84 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.75 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.47 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.92 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.61 %
Load Factor (LF) | [18 empty] | : | 87.75 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.18 %
Operating Factor (OF) | [18 empty] | : | 89.52 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 921 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 739.31 | 691.61 |  |  |  | 726.67 |  | 558.03 | [8 empty] | 0.00 |  |  | 642.19 | [6 empty] | 737.48 |  | 733.00 |  |  |  | 645.66 |  |  | 740.30 |  |  | 715.46 | [9 empty] | 739.31 |  |  | 7669.03
EAF [%] |  |  |  |  | 99.87 | 99.87 |  |  |  | 98.29 |  | 77.89 | [8 empty] | 0.00 |  |  | 89.64 | [6 empty] | 99.62 |  | 99.02 |  |  |  | 90.13 |  |  | 99.87 |  |  | 99.87 | [9 empty] | 99.87 |  |  | 87.75
UCF [%] |  |  |  |  | 99.87 | 99.87 |  |  |  | 99.87 |  | 88.91 | [8 empty] | 0.00 |  |  | 89.64 | [6 empty] | 99.87 |  | 99.87 |  |  |  | 90.71 |  |  | 99.87 |  |  | 99.87 | [9 empty] | 99.87 |  |  | 88.92
LF [%] |  |  |  |  | 99.87 | 99.87 |  |  |  | 98.29 |  | 77.89 | [8 empty] | 0.00 |  |  | 89.64 | [6 empty] | 99.62 |  | 99.02 |  |  |  | 90.13 |  |  | 99.87 |  |  | 99.87 | [9 empty] | 99.87 |  |  | 87.75
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 90.00 | [8 empty] | 0.00 |  |  | 94.58 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 90.83 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.52
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 9.18 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.84
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.23 |  |  | 5.42 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 9.17 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.47
PUF [%] |  |  |  |  | 0.13 | 0.13 |  |  |  | 0.13 |  | 11.09 | [8 empty] | 96.77 |  |  | 4.94 | [6 empty] | 0.13 |  | 0.13 |  |  |  | 0.12 |  |  | 0.13 |  |  | 0.13 | [9 empty] | 0.13 |  |  | 9.61
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.58 |  | 11.02 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.25 |  | 0.85 |  |  |  | 0.59 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.18
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 262735.03 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.55 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.57 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.22 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.24 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.96 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.67 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 4038.42 |  |  | 5771 |  |  |  | 887 | [10 empty] | 20.02 |  |  |  | 20.02 | [5 empty] | 15.76 |  |  | 21.64 |  |  |  | 67.19 |  | 41.00 | [8 empty] | 38.98 |  |  |  |  | 0.00
1985 |  |  |  | 4429.40 |  |  | 5342 |  |  |  | 898 | [10 empty] | 60.32 |  |  |  | 60.32 | [5 empty] | 56.31 |  |  | 60.98 |  |  |  | 6.75 |  | 4.37 | [8 empty] | 35.31 |  |  |  |  | 0.00
1986 |  |  |  | 5129.00 |  |  | 6208 |  |  |  | 898 | [10 empty] | 68.16 |  |  |  | 68.16 | [5 empty] | 65.20 |  |  | 70.87 |  |  |  | 2.29 |  | 1.60 | [8 empty] | 30.24 |  |  |  |  | 0.00
1987 |  |  |  | 6392.00 |  |  | 7569 |  |  |  | 898 | [10 empty] | 83.70 |  |  |  | 84.27 | [5 empty] | 81.26 |  |  | 86.40 |  |  |  | 2.22 |  | 1.91 | [8 empty] | 13.82 |  |  |  |  | 0.57
1988 |  |  |  | 6669.00 |  |  | 7599 |  |  |  | 898 | [10 empty] | 84.11 |  |  |  | 84.11 | [5 empty] | 84.55 |  |  | 86.51 |  |  |  | 6.85 |  | 6.19 | [8 empty] | 9.70 |  |  |  |  | 0.00
1989 |  |  |  | 6750.00 |  |  | 7771 |  |  |  | 930 | [10 empty] | 86.03 |  |  |  | 86.05 | [5 empty] | 82.85 |  |  | 88.71 |  |  |  | 2.79 |  | 2.47 | [8 empty] | 11.48 |  |  |  |  | 0.03
1990 |  |  |  | 6642.00 |  |  | 7699 |  |  |  | 930 | [10 empty] | 84.54 |  |  |  | 84.54 | [5 empty] | 81.53 |  |  | 87.89 |  |  |  | 2.21 |  | 1.91 | [8 empty] | 13.55 |  |  |  |  | 0.00
1991 |  |  |  | 6836.00 |  |  | 7810 |  |  |  | 930 | [10 empty] | 87.03 |  |  |  | 87.16 | [5 empty] | 83.91 |  |  | 89.16 |  |  |  | 1.58 |  | 1.40 | [8 empty] | 11.44 |  |  |  |  | 0.13
1992 |  |  |  | 6875.00 |  |  | 7898 |  |  |  | 887 | [10 empty] | 86.51 |  |  |  | 86.51 | [5 empty] | 88.24 |  |  | 89.91 |  |  |  | 1.66 |  | 1.46 | [8 empty] | 12.03 |  |  |  |  | 0.00
1993 |  |  |  | 6599.00 |  |  | 7401 |  |  |  | 930 | [10 empty] | 83.19 |  |  |  | 83.33 | [5 empty] | 81.00 |  |  | 84.49 |  |  |  | 5.59 |  | 4.94 | [8 empty] | 11.73 |  |  |  |  | 0.14
1994 |  |  |  | 6868.00 |  |  | 7758 |  |  |  | 930 | [10 empty] | 86.85 |  |  |  | 87.13 | [5 empty] | 84.30 |  |  | 88.56 |  |  |  | 1.43 |  | 1.26 | [8 empty] | 11.60 |  |  |  |  | 0.29
1995 |  |  |  | 5708.00 |  |  | 6387 |  |  |  | 900 | [10 empty] | 70.37 |  |  |  | 70.75 | [5 empty] | 72.40 |  |  | 72.91 |  |  |  | 1.90 |  | 1.37 | [8 empty] | 27.88 |  |  |  |  | 0.38
1996 |  |  |  | 7972.00 |  |  | 8755 |  |  |  | 947 | [10 empty] | 99.04 |  |  |  | 99.04 | [5 empty] | 95.84 |  |  | 99.67 |  |  |  | 0.86 |  | 0.85 | [8 empty] | 0.10 |  |  |  |  | 0.00
1997 |  |  |  | 6411.00 |  |  | 7198 |  |  |  | 915 | [10 empty] | 77.58 |  |  |  | 80.50 | [5 empty] | 79.98 |  |  | 82.17 |  |  |  | 9.99 |  | 8.93 | [8 empty] | 10.57 |  |  |  |  | 2.92
1998 |  |  |  | 7349.00 |  |  | 7943 |  |  |  | 949 | [10 empty] | 89.13 |  |  |  | 89.28 | [5 empty] | 88.40 |  |  | 90.67 |  |  |  | 3.21 |  | 2.96 | [8 empty] | 7.75 |  |  |  |  | 0.16
1999 |  |  |  | 8147.00 |  |  | 8741 |  |  |  | 945 | [10 empty] | 98.74 |  |  |  | 98.96 | [5 empty] | 98.42 |  |  | 99.78 |  |  |  | 1.00 |  | 1.00 | [8 empty] | 0.03 |  |  |  |  | 0.23
2000 |  |  |  | 7681.00 |  |  | 8008 |  |  |  | 991 | [10 empty] | 89.50 |  |  |  | 89.81 | [5 empty] | 89.27 |  |  | 91.17 |  |  |  | 1.23 |  | 1.12 | [8 empty] | 9.07 |  |  |  |  | 0.31
2001 |  |  |  | 7798.00 |  |  | 8056 |  |  |  | 991 | [10 empty] | 89.81 |  |  |  | 90.30 | [5 empty] | 89.83 |  |  | 91.96 |  |  |  | 0.58 |  | 0.52 | [8 empty] | 9.18 |  |  |  |  | 0.48
2002 |  |  |  | 8397.00 |  |  | 8737 |  |  |  | 998 | [10 empty] | 97.60 |  |  |  | 98.24 | [5 empty] | 96.05 |  |  | 99.74 |  |  |  | 0.43 |  | 0.43 | [8 empty] | 1.33 |  |  |  |  | 0.64
2003 |  |  |  | 7581.11 |  |  | 7900 |  |  |  | 995 | [10 empty] | 87.32 |  |  |  | 88.04 | [5 empty] | 86.89 |  |  | 90.18 |  |  |  | 0.12 |  | 0.10 | [8 empty] | 11.85 |  |  |  |  | 0.73
2004 |  |  |  | 7734.27 |  |  | 7949 |  |  |  | 995 | [10 empty] | 88.62 |  |  |  | 89.16 | [5 empty] | 88.49 |  |  | 90.49 |  |  |  | 0.36 |  | 0.78 | [8 empty] | 10.05 |  |  |  |  | 0.55
2005 |  |  |  | 7640.50 |  |  | 8548 |  |  |  | 995 | [10 empty] | 88.24 |  |  |  | 88.99 | [5 empty] | 87.66 |  |  | 97.58 |  |  |  | 2.98 |  | 2.73 | [8 empty] | 8.28 |  |  |  |  | 0.76
2006 |  |  |  | 7418.37 |  |  | 7971 |  |  |  | 995 | [10 empty] | 85.38 |  |  |  | 87.09 | [5 empty] | 85.10 |  |  | 90.98 |  |  |  | 0.32 |  | 0.52 | [8 empty] | 12.39 |  |  |  |  | 1.71
2007 |  |  |  | 7574.76 |  |  | 7876 |  |  |  | 995 | [10 empty] | 87.36 |  |  |  | 88.63 | [5 empty] | 86.90 |  |  | 89.91 |  |  |  | 0.73 |  | 1.72 | [8 empty] | 9.65 |  |  |  |  | 1.27
2008 |  |  |  | 7436.29 |  |  | 7768 |  |  |  | 995 | [10 empty] | 85.23 |  |  |  | 86.34 | [5 empty] | 85.08 |  |  | 88.43 |  |  |  | 0.61 |  | 7.65 | [8 empty] | 6.00 |  |  |  |  | 1.12
2009 |  |  |  | 5499.76 |  |  | 5758 |  |  |  | 995 | [10 empty] | 63.10 |  |  |  | 64.43 | [5 empty] | 63.10 |  |  | 65.73 |  |  |  | 22.82 |  | 23.92 | [8 empty] | 11.65 |  |  |  |  | 1.33
2010 |  |  |  | 7996.12 |  |  | 8231 |  |  |  | 995 | [10 empty] | 91.74 |  |  |  | 93.31 | [5 empty] | 91.74 |  |  | 93.96 |  |  |  | 6.45 |  | 6.43 | [8 empty] | 0.25 |  |  |  |  | 1.58
2011 |  |  |  | 6674.51 |  |  | 6946 |  |  |  | 995 | [10 empty] | 76.58 |  |  |  | 77.45 | [5 empty] | 76.58 |  |  | 79.29 |  |  |  | 0.43 |  | 9.31 | [8 empty] | 13.24 |  |  |  |  | 0.88
2012 |  |  |  | 7388.22 |  |  | 7666 |  |  |  | 995 | [10 empty] | 84.51 |  |  |  | 85.97 | [5 empty] | 84.53 |  |  | 87.27 |  |  |  | 0.41 |  | 0.35 | [8 empty] | 13.67 |  |  |  |  | 1.46
2013 |  |  |  | 8687.39 |  |  | 8760 |  |  |  | 995 | [10 empty] | 99.33 |  |  |  | 99.87 | [5 empty] | 99.67 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.13 |  |  |  |  | 0.54
2014 |  |  |  | 7096.39 |  |  | 7226 |  |  |  | 995 | [10 empty] | 80.98 |  |  |  | 81.69 | [5 empty] | 81.42 |  |  | 82.49 |  |  |  | 0.00 |  | 4.48 | [8 empty] | 13.82 |  |  |  |  | 0.72
2015 |  |  |  | 7397.93 |  |  | 7725 |  |  |  | 995 | [10 empty] | 84.36 |  |  |  | 84.82 | [5 empty] | 84.88 |  |  | 88.18 |  |  |  | 2.13 |  | 3.24 | [8 empty] | 11.93 |  |  |  |  | 0.46
2016 |  |  |  | 8439.80 |  |  | 8560 |  |  |  | 995 | [10 empty] | 95.91 |  |  |  | 96.83 | [5 empty] | 96.56 |  |  | 97.45 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 3.12 |  |  |  |  | 0.91
2017 |  |  |  | 7522.94 |  |  | 7689 |  |  |  | 995 | [10 empty] | 85.67 |  |  |  | 86.95 | [5 empty] | 86.31 |  |  | 87.77 |  |  |  | 1.05 |  | 2.92 | [8 empty] | 10.13 |  |  |  |  | 1.27
2018 |  |  |  | 7592.83 |  |  | 7718 |  |  |  | 995 | [10 empty] | 86.76 |  |  |  | 87.18 | [5 empty] | 87.11 |  |  | 88.11 |  |  |  | 0.00 |  | 2.44 | [8 empty] | 10.38 |  |  |  |  | 0.42
2019 |  |  |  | 8630.08 |  |  | 8760 |  |  |  | 995 | [10 empty] | 99.25 |  |  |  | 99.87 | [5 empty] | 99.01 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.13 |  |  |  |  | 0.62
2020 |  |  |  | 7669.03 |  |  | 7863 |  |  |  | 995 | [10 empty] | 87.75 |  |  |  | 88.92 | [5 empty] | 87.75 |  |  | 89.52 |  |  |  | 0.84 |  | 1.47 | [8 empty] | 9.61 |  |  |  |  | 1.18
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 66 | [14 empty] | 253
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 792 |  |  |  | 24 | [10 empty] | 791 |  |  |  | 39
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 33
E. |  | Testing of plant systems or components | [24 empty] | 39 | [10 empty] | 47 |  |  |  | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 4
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 6
Z. |  | Other | [39 empty] | 7
Subtotal | [22 empty] | 792 |  |  |  | 129 | [10 empty] | 871 |  |  |  | 308 | [11 empty] | 12
Total | [22 empty] | 921 | [14 empty] | 1191
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 3
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [19 empty] | 66 | [14 empty] | 10
16. |  |  | Steam generation systems | [34 empty] | 14
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [19 empty] | 63 | [14 empty] | 47
31. |  |  | Turbine and auxiliaries | [34 empty] | 51
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
33. |  |  | Circulating Water System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 75
42. |  |  | Electrical Power Supply Systems | [34 empty] | 70
Total | [22 empty] | 129 | [14 empty] | 297

## ASCO-2
2020 Operating Experience
ES-9 | [8 empty] | ASCO-2 | [26 empty] | SPAIN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ANAV (ASOCIACIÓN NUCLEAR ASCÓ-VANDELLÓS A.I.E. (ENDESA/ID))
Owner | [7 empty] | : | EN/ID (ENDESA, IBERDROLA)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-03-07
Thermal power | [12 empty] | : |  |  | 2941 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-10-23
Gross electrical power | [12 empty] | : |  |  | 1027 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-03-31
Reference unit power (net) | [12 empty] | : |  |  | 997 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.72
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 3.86
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.6
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.92 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7368.41 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.64 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.97 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.18 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.25 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.57 %
Load Factor (LF) | [18 empty] | : | 84.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.28 %
Operating Factor (OF) | [18 empty] | : | 86.07 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1224 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 740.81 | 686.51 |  |  |  | 728.16 |  | 688.16 | [8 empty] | 715.17 |  |  | 590.45 | [6 empty] | 738.01 |  | 733.80 |  |  |  | 704.80 |  |  | 28.40 |  |  | 273.34 | [9 empty] | 740.80 |  |  | 7368.41
EAF [%] |  |  |  |  | 99.87 | 99.87 |  |  |  | 99.87 |  | 99.87 | [8 empty] | 99.87 |  |  | 82.25 | [6 empty] | 99.49 |  | 98.93 |  |  |  | 98.18 |  |  | 3.82 |  |  | 38.08 | [9 empty] | 99.87 |  |  | 84.97
UCF [%] |  |  |  |  | 99.87 | 99.87 |  |  |  | 99.87 |  | 99.87 | [8 empty] | 99.87 |  |  | 82.53 | [6 empty] | 99.87 |  | 99.87 |  |  |  | 99.82 |  |  | 4.00 |  |  | 38.08 | [9 empty] | 99.87 |  |  | 85.25
LF [%] |  |  |  |  | 99.87 | 98.93 |  |  |  | 98.30 |  | 95.87 | [8 empty] | 96.41 |  |  | 82.25 | [6 empty] | 99.49 |  | 98.93 |  |  |  | 98.18 |  |  | 3.82 |  |  | 38.08 | [9 empty] | 99.87 |  |  | 84.14
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 82.64 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 6.44 |  |  | 44.17 | [9 empty] | 100.00 |  |  | 86.07
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 17.38 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.64
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 17.36 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 45.83 | [9 empty] | 0.00 |  |  | 5.18
PUF [%] |  |  |  |  | 0.13 | 0.13 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 0.13 |  |  | 0.11 | [6 empty] | 0.13 |  | 0.13 |  |  |  | 0.18 |  |  | 96.00 |  |  | 16.09 | [9 empty] | 0.13 |  |  | 9.57
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.28 | [6 empty] | 0.38 |  | 0.95 |  |  |  | 1.64 |  |  | 0.17 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.28
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 255810.41 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.7 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.27 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.21 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.56 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.46 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.96 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.62 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 5368.00 |  |  | 6639 |  |  |  | 898 | [10 empty] | 77.72 |  |  |  | 77.72 | [5 empty] | 74.11 |  |  | 78.65 |  |  |  | 21.50 |  | 21.28 | [8 empty] | 1.00 |  |  |  |  | 0.00
1987 |  |  |  | 5954.00 |  |  | 7035 |  |  |  | 898 | [10 empty] | 77.27 |  |  |  | 78.13 | [5 empty] | 75.69 |  |  | 80.31 |  |  |  | 3.63 |  | 2.94 | [8 empty] | 18.93 |  |  |  |  | 0.86
1988 |  |  |  | 6865.00 |  |  | 7874 |  |  |  | 898 | [10 empty] | 86.76 |  |  |  | 88.23 | [5 empty] | 87.03 |  |  | 89.64 |  |  |  | 1.86 |  | 1.67 | [8 empty] | 10.10 |  |  |  |  | 1.47
1989 |  |  |  | 6732.00 |  |  | 7729 |  |  |  | 930 | [10 empty] | 85.70 |  |  |  | 86.30 | [5 empty] | 82.63 |  |  | 88.23 |  |  |  | 1.79 |  | 1.57 | [8 empty] | 12.13 |  |  |  |  | 0.60
1990 |  |  |  | 6933.00 |  |  | 7916 |  |  |  | 930 | [10 empty] | 90.42 |  |  |  | 90.42 | [5 empty] | 85.10 |  |  | 90.37 |  |  |  | 0.73 |  | 0.66 | [8 empty] | 8.92 |  |  |  |  | 0.00
1991 |  |  |  | 6820.00 |  |  | 7799 |  |  |  | 930 | [10 empty] | 86.49 |  |  |  | 86.69 | [5 empty] | 83.71 |  |  | 89.03 |  |  |  | 0.76 |  | 0.67 | [8 empty] | 12.64 |  |  |  |  | 0.20
1992 |  |  |  | 7077.00 |  |  | 8042 |  |  |  | 953 | [10 empty] | 89.92 |  |  |  | 89.92 | [5 empty] | 84.54 |  |  | 91.55 |  |  |  | 0.99 |  | 0.90 | [8 empty] | 9.17 |  |  |  |  | 0.00
1993 |  |  |  | 7052.00 |  |  | 7897 |  |  |  | 930 | [10 empty] | 88.61 |  |  |  | 90.02 | [5 empty] | 86.56 |  |  | 90.15 |  |  |  | 1.20 |  | 1.09 | [8 empty] | 8.89 |  |  |  |  | 1.41
1994 |  |  |  | 7085.00 |  |  | 7962 |  |  |  | 930 | [10 empty] | 89.47 |  |  |  | 89.77 | [5 empty] | 86.97 |  |  | 90.89 |  |  |  | 1.56 |  | 1.43 | [8 empty] | 8.81 |  |  |  |  | 0.29
1995 |  |  |  | 6977.00 |  |  | 7674 |  |  |  | 900 | [10 empty] | 86.25 |  |  |  | 86.39 | [5 empty] | 88.50 |  |  | 87.60 |  |  |  | 1.04 |  | 0.91 | [8 empty] | 12.70 |  |  |  |  | 0.13
1996 |  |  |  | 6011.00 |  |  | 6825 |  |  |  | 963 | [10 empty] | 75.14 |  |  |  | 75.61 | [5 empty] | 71.06 |  |  | 77.70 |  |  |  | 3.95 |  | 3.11 | [8 empty] | 21.28 |  |  |  |  | 0.47
1997 |  |  |  | 7916.00 |  |  | 8725 |  |  |  | 900 | [10 empty] | 96.18 |  |  |  | 98.17 | [5 empty] | 100.42 |  |  | 99.61 |  |  |  | 1.24 |  | 1.23 | [8 empty] | 0.60 |  |  |  |  | 1.99
1998 |  |  |  | 7399.00 |  |  | 8050 |  |  |  | 946 | [10 empty] | 89.88 |  |  |  | 90.57 | [5 empty] | 89.28 |  |  | 91.89 |  |  |  | 1.27 |  | 1.16 | [8 empty] | 8.26 |  |  |  |  | 0.69
1999 |  |  |  | 7215.00 |  |  | 7854 |  |  |  | 946 | [10 empty] | 86.42 |  |  |  | 87.17 | [5 empty] | 87.06 |  |  | 89.66 |  |  |  | 3.04 |  | 2.73 | [8 empty] | 10.10 |  |  |  |  | 0.75
2000 |  |  |  | 8451.00 |  |  | 8734 |  |  |  | 983 | [10 empty] | 98.63 |  |  |  | 98.63 | [5 empty] | 97.87 |  |  | 99.43 |  |  |  | 0.59 |  | 0.59 | [8 empty] | 0.78 |  |  |  |  | 0.00
2001 |  |  |  | 7829.00 |  |  | 8102 |  |  |  | 983 | [10 empty] | 90.55 |  |  |  | 90.97 | [5 empty] | 90.92 |  |  | 92.49 |  |  |  | 0.48 |  | 0.44 | [8 empty] | 8.59 |  |  |  |  | 0.42
2002 |  |  |  | 7780.00 |  |  | 8127 |  |  |  | 997 | [10 empty] | 89.40 |  |  |  | 90.78 | [5 empty] | 89.08 |  |  | 92.77 |  |  |  | 0.50 |  | 0.45 | [8 empty] | 8.77 |  |  |  |  | 1.38
2003 |  |  |  | 8521.20 |  |  | 8738 |  |  |  | 997 | [10 empty] | 98.73 |  |  |  | 99.59 | [5 empty] | 97.57 |  |  | 99.75 |  |  |  | 0.27 |  | 0.27 | [8 empty] | 0.14 |  |  |  |  | 0.86
2004 |  |  |  | 6909.28 |  |  | 7287 |  |  |  | 997 | [10 empty] | 79.62 |  |  |  | 80.24 | [5 empty] | 78.89 |  |  | 82.96 |  |  |  | 10.36 |  | 9.83 | [8 empty] | 9.93 |  |  |  |  | 0.62
2005 |  |  |  | 7418.88 |  |  | 7779 |  |  |  | 997 | [10 empty] | 86.10 |  |  |  | 86.75 | [5 empty] | 84.95 |  |  | 88.80 |  |  |  | 2.29 |  | 3.03 | [8 empty] | 10.22 |  |  |  |  | 0.65
2006 |  |  |  | 7968.75 |  |  | 8335 |  |  |  | 997 | [10 empty] | 92.42 |  |  |  | 94.34 | [5 empty] | 91.24 |  |  | 95.15 |  |  |  | 5.52 |  | 5.51 | [8 empty] | 0.16 |  |  |  |  | 1.92
2007 |  |  |  | 7091.43 |  |  | 7532 |  |  |  | 997 | [10 empty] | 81.94 |  |  |  | 83.58 | [5 empty] | 81.20 |  |  | 85.98 |  |  |  | 5.19 |  | 6.77 | [8 empty] | 9.64 |  |  |  |  | 1.65
2008 |  |  |  | 7123.62 |  |  | 7413 |  |  |  | 997 | [10 empty] | 81.98 |  |  |  | 83.28 | [5 empty] | 81.34 |  |  | 84.39 |  |  |  | 0.03 |  | 6.84 | [8 empty] | 9.88 |  |  |  |  | 1.30
2009 |  |  |  | 7818.32 |  |  | 8082 |  |  |  | 997 | [10 empty] | 89.52 |  |  |  | 91.34 | [5 empty] | 89.52 |  |  | 92.26 |  |  |  | 6.95 |  | 6.82 | [8 empty] | 1.84 |  |  |  |  | 1.82
2010 |  |  |  | 7309.13 |  |  | 7583 |  |  |  | 997 | [10 empty] | 83.69 |  |  |  | 85.62 | [5 empty] | 83.69 |  |  | 86.56 |  |  |  | 0.03 |  | 1.68 | [8 empty] | 12.70 |  |  |  |  | 1.93
2011 |  |  |  | 7142.24 |  |  | 7560 |  |  |  | 997 | [10 empty] | 81.78 |  |  |  | 84.19 | [5 empty] | 81.78 |  |  | 86.30 |  |  |  | 1.55 |  | 4.57 | [8 empty] | 11.25 |  |  |  |  | 2.41
2012 |  |  |  | 7831.53 |  |  | 8327 |  |  |  | 997 | [10 empty] | 89.43 |  |  |  | 92.80 | [5 empty] | 89.43 |  |  | 94.80 |  |  |  | 1.14 |  | 4.47 | [8 empty] | 2.73 |  |  |  |  | 3.37
2013 |  |  |  | 7274.22 |  |  | 7499 |  |  |  | 997 | [10 empty] | 83.27 |  |  |  | 84.30 | [5 empty] | 83.29 |  |  | 85.61 |  |  |  | 2.16 |  | 2.16 | [8 empty] | 13.55 |  |  |  |  | 1.02
2014 |  |  |  | 6837.37 |  |  | 7010 |  |  |  | 997 | [10 empty] | 78.03 |  |  |  | 78.37 | [5 empty] | 78.29 |  |  | 80.02 |  |  |  | 9.18 |  | 8.43 | [8 empty] | 13.20 |  |  |  |  | 0.33
2015 |  |  |  | 8442.11 |  |  | 8656 |  |  |  | 997 | [10 empty] | 96.27 |  |  |  | 96.47 | [5 empty] | 96.66 |  |  | 98.81 |  |  |  | 2.62 |  | 2.59 | [8 empty] | 0.94 |  |  |  |  | 0.20
2016 |  |  |  | 7646.24 |  |  | 7852 |  |  |  | 997 | [10 empty] | 87.14 |  |  |  | 88.26 | [5 empty] | 87.31 |  |  | 89.39 |  |  |  | 0.00 |  | 0.23 | [8 empty] | 11.51 |  |  |  |  | 1.13
2017 |  |  |  | 7716.07 |  |  | 7917 |  |  |  | 997 | [10 empty] | 87.78 |  |  |  | 89.52 | [5 empty] | 88.35 |  |  | 90.38 |  |  |  | 0.00 |  | 0.31 | [8 empty] | 10.18 |  |  |  |  | 1.74
2018 |  |  |  | 8514.79 |  |  | 8582 |  |  |  | 997 | [10 empty] | 97.30 |  |  |  | 97.73 | [5 empty] | 97.49 |  |  | 97.97 |  |  |  | 2.15 |  | 2.14 | [8 empty] | 0.13 |  |  |  |  | 0.43
2019 |  |  |  | 7537.35 |  |  | 7783 |  |  |  | 997 | [10 empty] | 86.54 |  |  |  | 87.35 | [5 empty] | 86.30 |  |  | 88.85 |  |  |  | 1.31 |  | 2.90 | [8 empty] | 9.74 |  |  |  |  | 0.82
2020 |  |  |  | 7368.41 |  |  | 7560 |  |  |  | 997 | [10 empty] | 84.97 |  |  |  | 85.25 | [5 empty] | 84.14 |  |  | 86.07 |  |  |  | 1.64 |  | 5.18 | [8 empty] | 9.57 |  |  |  |  | 0.28
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 455 | [14 empty] | 196
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 769 | [14 empty] | 658 |  |  |  | 42
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 30
E. |  | Testing of plant systems or components | [35 empty] | 15 |  |  |  | 7
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 14
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 7
Z. |  | Other | [35 empty] | 3 |  |  |  | 7
Subtotal | [22 empty] | 769 |  |  |  | 455 | [10 empty] | 727 |  |  |  | 255 | [11 empty] | 7
Total | [22 empty] | 1224 | [14 empty] | 989
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 125 | [14 empty] | 23
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [19 empty] | 330 | [14 empty] | 17
16. |  |  | Steam generation systems | [34 empty] | 12
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 53
31. |  |  | Turbine and auxiliaries | [34 empty] | 13
32. |  |  | Feedwater and Main Steam System | [34 empty] | 56
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 7
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 7
42. |  |  | Electrical Power Supply Systems | [34 empty] | 51
Total | [22 empty] | 455 | [14 empty] | 255

## COFRENTES
2020 Operating Experience
ES-10 | [8 empty] | COFRENTES | [26 empty] | SPAIN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ID (IBERDROLA, S.A.)
Owner | [7 empty] | : | ID (IBERDROLA, S.A.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-6 (Mark 3) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-09-09
Thermal power | [12 empty] | : |  |  | 3237 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-10-14
Gross electrical power | [12 empty] | : |  |  | 1102 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-03-11
Reference unit power (net) | [12 empty] | : |  |  | 1064 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.26
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 288
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.103
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 41 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 4.29 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.115
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 624 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.03 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 145 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8902.95 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.34 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.83 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.34 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.38 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.28 %
Load Factor (LF) | [18 empty] | : | 95.26 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.55 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 788.55 | 716.20 |  |  |  | 759.69 |  | 617.75 | [8 empty] | 641.59 |  |  | 756.73 | [6 empty] | 766.33 |  | 783.23 |  |  |  | 759.93 |  |  | 774.87 |  |  | 762.83 | [9 empty] | 775.24 |  |  | 8902.95
EAF [%] |  |  |  |  | 99.62 | 97.64 |  |  |  | 99.65 |  | 99.76 | [8 empty] | 99.32 |  |  | 98.79 | [6 empty] | 96.81 |  | 98.95 |  |  |  | 99.20 |  |  | 98.65 |  |  | 99.58 | [9 empty] | 97.94 |  |  | 98.83
UCF [%] |  |  |  |  | 99.93 | 97.98 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.68 |  |  | 99.63 | [6 empty] | 97.89 |  | 100.00 |  |  |  | 100.00 |  |  | 99.15 |  |  | 100.00 | [9 empty] | 98.27 |  |  | 99.38
LF [%] |  |  |  |  | 99.61 | 96.71 |  |  |  | 96.10 |  | 80.64 | [8 empty] | 81.05 |  |  | 98.78 | [6 empty] | 96.81 |  | 98.94 |  |  |  | 99.20 |  |  | 97.75 |  |  | 99.58 | [9 empty] | 97.93 |  |  | 95.26
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.07 | 0.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.32 |  |  | 0.37 | [6 empty] | 0.81 |  | 0.00 |  |  |  | 0.00 |  |  | 0.04 |  |  | 0.00 | [9 empty] | 1.73 |  |  | 0.34
UCL [%] |  |  |  |  | 0.07 | 0.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.32 |  |  | 0.37 | [6 empty] | 0.80 |  | 0.00 |  |  |  | 0.00 |  |  | 0.04 |  |  | 0.00 | [9 empty] | 1.73 |  |  | 0.34
PUF [%] |  |  |  |  | 0.00 | 1.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.31 |  | 0.00 |  |  |  | 0.00 |  |  | 0.81 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.28
XUF [%] |  |  |  |  | 0.31 | 0.35 |  |  |  | 0.35 |  | 0.24 | [8 empty] | 0.36 |  |  | 0.85 | [6 empty] | 1.08 |  | 1.05 |  |  |  | 0.80 |  |  | 0.50 |  |  | 0.42 | [9 empty] | 0.33 |  |  | 0.55
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 278659.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.83 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.42 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.05 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.39 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.57 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.33 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.97 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.23 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 6142.48 |  |  | 7300 |  |  |  | 939 | [10 empty] | 81.41 |  |  |  | 81.41 | [5 empty] | 81.39 |  |  | 87.75 |  |  |  | 12.12 |  | 11.23 | [8 empty] | 7.35 |  |  |  |  | 0.00
1986 |  |  |  | 6668.30 |  |  | 7487 |  |  |  | 939 | [10 empty] | 81.07 |  |  |  | 81.96 | [5 empty] | 81.07 |  |  | 85.47 |  |  |  | 2.10 |  | 1.75 | [8 empty] | 16.29 |  |  |  |  | 0.89
1987 |  |  |  | 6883.08 |  |  | 7615 |  |  |  | 930 | [10 empty] | 83.40 |  |  |  | 83.42 | [5 empty] | 84.49 |  |  | 86.93 |  |  |  | 5.00 |  | 4.39 | [8 empty] | 12.19 |  |  |  |  | 0.02
1988 |  |  |  | 7142.15 |  |  | 7850 |  |  |  | 930 | [10 empty] | 85.51 |  |  |  | 85.74 | [5 empty] | 87.43 |  |  | 89.37 |  |  |  | 2.18 |  | 1.91 | [8 empty] | 12.35 |  |  |  |  | 0.23
1989 |  |  |  | 7052.24 |  |  | 7732 |  |  |  | 939 | [10 empty] | 83.90 |  |  |  | 83.90 | [5 empty] | 85.73 |  |  | 88.26 |  |  |  | 4.54 |  | 3.99 | [8 empty] | 12.11 |  |  |  |  | 0.00
1990 |  |  |  | 7070.30 |  |  | 7560 |  |  |  | 939 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 85.95 |  |  | 86.30 |  |  |  | 4.12 |  | 3.66 | [8 empty] | 11.24 |  |  |  |  | 0.00
1991 |  |  |  | 6999.63 |  |  | 7660 |  |  |  | 953 | [10 empty] | 83.70 |  |  |  | 83.70 | [5 empty] | 83.85 |  |  | 87.44 |  |  |  | 3.62 |  | 3.15 | [8 empty] | 13.15 |  |  |  |  | 0.00
1992 |  |  |  | 7712.12 |  |  | 8376 |  |  |  | 939 | [10 empty] | 91.87 |  |  |  | 91.87 | [5 empty] | 93.50 |  |  | 95.36 |  |  |  | 3.17 |  | 3.01 | [8 empty] | 5.12 |  |  |  |  | 0.00
1993 |  |  |  | 7016.23 |  |  | 7579 |  |  |  | 953 | [10 empty] | 83.57 |  |  |  | 84.76 | [5 empty] | 84.04 |  |  | 86.52 |  |  |  | 3.31 |  | 2.90 | [8 empty] | 12.34 |  |  |  |  | 1.18
1994 |  |  |  | 6990.86 |  |  | 7553 |  |  |  | 953 | [10 empty] | 83.55 |  |  |  | 85.06 | [5 empty] | 83.74 |  |  | 86.22 |  |  |  | 1.05 |  | 0.90 | [8 empty] | 14.04 |  |  |  |  | 1.51
1995 |  |  |  | 8186.97 |  |  | 8683 |  |  |  | 953 | [10 empty] | 97.54 |  |  |  | 97.78 | [5 empty] | 98.07 |  |  | 99.12 |  |  |  | 1.60 |  | 1.59 | [8 empty] | 0.63 |  |  |  |  | 0.24
1996 |  |  |  | 7687.49 |  |  | 8215 |  |  |  | 953 | [10 empty] | 90.88 |  |  |  | 91.90 | [5 empty] | 91.83 |  |  | 93.52 |  |  |  | 1.09 |  | 1.01 | [8 empty] | 7.08 |  |  |  |  | 1.02
1997 |  |  |  | 6893.65 |  |  | 7668 |  |  |  | 953 | [10 empty] | 83.73 |  |  |  | 86.15 | [5 empty] | 82.59 |  |  | 87.54 |  |  |  | 3.25 |  | 2.90 | [8 empty] | 10.95 |  |  |  |  | 2.43
1998 |  |  |  | 8174.10 |  |  | 8546 |  |  |  | 993 | [10 empty] | 96.56 |  |  |  | 96.56 | [5 empty] | 93.97 |  |  | 97.56 |  |  |  | 2.86 |  | 2.85 | [8 empty] | 0.59 |  |  |  |  | 0.00
1999 |  |  |  | 7491.64 |  |  | 8004 |  |  |  | 989 | [10 empty] | 86.43 |  |  |  | 89.83 | [5 empty] | 86.47 |  |  | 91.37 |  |  |  | 2.06 |  | 1.89 | [8 empty] | 8.28 |  |  |  |  | 3.39
2000 |  |  |  | 7348.14 |  |  | 7808 |  |  |  | 989 | [10 empty] | 84.59 |  |  |  | 86.87 | [5 empty] | 84.58 |  |  | 88.89 |  |  |  | 1.76 |  | 1.56 | [8 empty] | 11.57 |  |  |  |  | 2.28
2001 |  |  |  | 8278.15 |  |  | 8424 |  |  |  | 989 | [10 empty] | 95.54 |  |  |  | 95.54 | [5 empty] | 95.55 |  |  | 96.16 |  |  |  | 4.17 |  | 4.16 | [8 empty] | 0.30 |  |  |  |  | 0.00
2002 |  |  |  | 7918.10 |  |  | 7875 |  |  |  | 1043 | [10 empty] | 88.24 |  |  |  | 89.20 | [5 empty] | 86.66 |  |  | 89.90 |  |  |  | 1.73 |  | 1.57 | [8 empty] | 9.23 |  |  |  |  | 0.97
2003 |  |  |  | 8002.51 |  |  | 7742 |  |  |  | 1062 | [10 empty] | 88.17 |  |  |  | 88.17 | [5 empty] | 86.45 |  |  | 88.38 |  |  |  | 2.80 |  | 4.42 | [8 empty] | 7.41 |  |  |  |  | 0.00
2004 |  |  |  | 8813.91 |  |  | 8457 |  |  |  | 1064 | [10 empty] | 94.29 |  |  |  | 94.94 | [5 empty] | 94.32 |  |  | 96.28 |  |  |  | 2.00 |  | 1.97 | [8 empty] | 3.09 |  |  |  |  | 0.65
2005 |  |  |  | 6765.14 |  |  | 6768 |  |  |  | 1064 | [10 empty] | 72.84 |  |  |  | 75.92 | [5 empty] | 72.58 |  |  | 77.26 |  |  |  | 1.10 |  | 1.56 | [8 empty] | 22.53 |  |  |  |  | 3.07
2006 |  |  |  | 8872.52 |  |  | 8492 |  |  |  | 1064 | [10 empty] | 95.32 |  |  |  | 95.64 | [5 empty] | 95.19 |  |  | 96.94 |  |  |  | 1.57 |  | 1.53 | [8 empty] | 2.83 |  |  |  |  | 0.32
2007 |  |  |  | 6008.35 |  |  | 5898 |  |  |  | 1064 | [10 empty] | 64.47 |  |  |  | 66.05 | [5 empty] | 64.46 |  |  | 67.33 |  |  |  | 10.93 |  | 10.84 | [8 empty] | 23.11 |  |  |  |  | 1.59
2008 |  |  |  | 7856.29 |  |  | 7643 |  |  |  | 1064 | [10 empty] | 84.10 |  |  |  | 84.40 | [5 empty] | 84.06 |  |  | 87.01 |  |  |  | 15.51 |  | 15.49 | [8 empty] | 0.11 |  |  |  |  | 0.30
2009 |  |  |  | 7747.00 |  |  | 7618 |  |  |  | 1064 | [10 empty] | 83.12 |  |  |  | 85.54 | [5 empty] | 83.12 |  |  | 86.96 |  |  |  | 1.27 |  | 1.10 | [8 empty] | 13.36 |  |  |  |  | 2.42
2010 |  |  |  | 9201.90 |  |  | 8760 |  |  |  | 1064 | [10 empty] | 98.73 |  |  |  | 98.99 | [5 empty] | 98.73 |  |  | 100.00 |  |  |  | 0.57 |  | 0.56 | [8 empty] | 0.45 |  |  |  |  | 0.26
2011 |  |  |  | 7599.08 |  |  | 7564 |  |  |  | 1064 | [10 empty] | 81.54 |  |  |  | 84.40 | [5 empty] | 81.53 |  |  | 86.35 |  |  |  | 1.14 |  | 0.98 | [8 empty] | 14.62 |  |  |  |  | 2.87
2012 |  |  |  | 9064.14 |  |  | 8686 |  |  |  | 1064 | [10 empty] | 97.00 |  |  |  | 97.21 | [5 empty] | 96.98 |  |  | 98.88 |  |  |  | 0.36 |  | 0.35 | [8 empty] | 2.43 |  |  |  |  | 0.22
2013 |  |  |  | 8012.79 |  |  | 7800 |  |  |  | 1064 | [10 empty] | 86.31 |  |  |  | 87.99 | [5 empty] | 85.97 |  |  | 89.04 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 11.89 |  |  |  |  | 1.68
2014 |  |  |  | 9114.79 |  |  | 8760 |  |  |  | 1064 | [10 empty] | 97.93 |  |  |  | 98.13 | [5 empty] | 97.79 |  |  | 100.00 |  |  |  | 0.97 |  | 0.96 | [8 empty] | 0.91 |  |  |  |  | 0.20
2015 |  |  |  | 7438.67 |  |  | 7325 |  |  |  | 1064 | [10 empty] | 79.81 |  |  |  | 81.51 | [5 empty] | 79.81 |  |  | 83.62 |  |  |  | 0.21 |  | 0.17 | [8 empty] | 18.31 |  |  |  |  | 1.70
2016 |  |  |  | 9187.25 |  |  | 8784 |  |  |  | 1064 | [10 empty] | 98.31 |  |  |  | 98.52 | [5 empty] | 98.30 |  |  | 100.00 |  |  |  | 0.37 |  | 0.37 | [8 empty] | 1.11 |  |  |  |  | 0.22
2017 |  |  |  | 7060.25 |  |  | 7030 |  |  |  | 1064 | [10 empty] | 75.75 |  |  |  | 78.08 | [5 empty] | 75.75 |  |  | 80.25 |  |  |  | 0.55 |  | 11.16 | [8 empty] | 10.76 |  |  |  |  | 2.33
2018 |  |  |  | 8816.13 |  |  | 8436 |  |  |  | 1064 | [10 empty] | 94.59 |  |  |  | 94.94 | [5 empty] | 94.59 |  |  | 96.30 |  |  |  | 4.63 |  | 4.61 | [8 empty] | 0.45 |  |  |  |  | 0.35
2019 |  |  |  | 8074.05 |  |  | 7854 |  |  |  | 1064 | [10 empty] | 86.78 |  |  |  | 88.15 | [5 empty] | 86.63 |  |  | 89.66 |  |  |  | 0.20 |  | 0.17 | [8 empty] | 11.68 |  |  |  |  | 1.36
2020 |  |  |  | 8902.95 |  |  | 8784 |  |  |  | 1064 | [10 empty] | 98.83 |  |  |  | 99.38 | [5 empty] | 95.26 |  |  | 100.00 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.28 |  |  |  |  | 0.55
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 213
B. |  | Refuelling without maintenance | [35 empty] | 6
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 591 |  |  |  | 2
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 16
E. |  | Testing of plant systems or components | [35 empty] | 15
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 5
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
P. |  | Fire | [39 empty] | 16
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 7
Z. |  | Other | [39 empty] | 9
Subtotal | [37 empty] | 635 |  |  |  | 245 | [11 empty] | 4
Total | [22 empty] | 0 | [14 empty] | 884
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 50
12. |  |  | Reactor I&C Systems | [34 empty] | 43
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 54
32. |  |  | Feedwater and Main Steam System | [34 empty] | 29
34. |  |  | Miscellaneous Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 21
42. |  |  | Electrical Power Supply Systems | [34 empty] | 24
Total | [37 empty] | 234

## TRILLO-1
2020 Operating Experience
ES-11 | [8 empty] | TRILLO-1 | [26 empty] | SPAIN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CNAT (CENTRALES NUCLEARES ALMARAZ-TRILLO (ID/UFG/ENDESA/HC/NUCLENOR))
Owner | [7 empty] | : | ID/GN/HC (Iberdrola, Gas Natural, Hidroeléctrica del Cantábrico, Nuclenor)
Reactor Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / PWR 3 loops | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-08-17
Thermal power | [12 empty] | : |  |  | 3010 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-05-23
Gross electrical power | [12 empty] | : |  |  | 1066 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-08-06
Reference unit power (net) | [12 empty] | : |  |  | 1003 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.538
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.20 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 22.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.44 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.261
| Active core height/length [m] | [13 empty] | : |  |  | 3.4 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.71 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 52 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7729.61 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.29 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.12 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.26 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.39 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.35 %
Load Factor (LF) | [18 empty] | : | 87.73 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.26 %
Operating Factor (OF) | [18 empty] | : | 90.86 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 803 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 736.45 | 680.07 |  |  |  | 722.38 |  | 613.80 | [8 empty] | 387.98 |  |  | 233.37 | [6 empty] | 729.82 |  | 730.82 |  |  |  | 709.69 |  |  | 736.46 |  |  | 712.47 | [9 empty] | 736.28 |  |  | 7729.61
EAF [%] |  |  |  |  | 98.69 | 98.69 |  |  |  | 98.71 |  | 98.89 | [8 empty] | 51.99 |  |  | 32.32 | [6 empty] | 97.80 |  | 97.93 |  |  |  | 98.27 |  |  | 98.56 |  |  | 98.66 | [9 empty] | 98.67 |  |  | 89.12
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 52.02 |  |  | 32.42 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.94 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.95 |  |  | 90.39
LF [%] |  |  |  |  | 98.69 | 97.42 |  |  |  | 96.93 |  | 85.00 | [8 empty] | 51.99 |  |  | 32.32 | [6 empty] | 97.80 |  | 97.93 |  |  |  | 98.27 |  |  | 98.56 |  |  | 98.66 | [9 empty] | 98.67 |  |  | 87.73
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 55.11 |  |  | 34.86 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.86
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.61 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.29
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.09 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.26
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 44.89 |  |  | 67.58 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.06 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.05 |  |  | 9.35
XUF [%] |  |  |  |  | 1.31 | 1.31 |  |  |  | 1.29 |  | 1.11 | [8 empty] | 0.03 |  |  | 0.10 | [6 empty] | 2.20 |  | 2.07 |  |  |  | 1.66 |  |  | 1.44 |  |  | 1.34 | [9 empty] | 1.28 |  |  | 1.26
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 247166.63 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.42 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.6 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.82 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.58 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.88 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.49 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 2896.23 |  |  | 3511 |  |  |  | 997 | [10 empty] | 72.66 |  |  |  | 72.66 | [5 empty] | 66.29 |  |  | 72.11 |  |  |  | 16.08 |  | 13.93 | [8 empty] | 13.41 |  |  |  |  | 0.00
1989 |  |  |  | 7147.79 |  |  | 7665 |  |  |  | 974 | [10 empty] | 83.77 |  |  |  | 83.79 | [5 empty] | 83.77 |  |  | 87.50 |  |  |  | 1.38 |  | 1.17 | [8 empty] | 15.04 |  |  |  |  | 0.02
1990 |  |  |  | 6372.44 |  |  | 7170 |  |  |  | 974 | [10 empty] | 74.69 |  |  |  | 74.69 | [5 empty] | 74.69 |  |  | 81.85 |  |  |  | 10.14 |  | 8.42 | [8 empty] | 16.89 |  |  |  |  | 0.00
1991 |  |  |  | 6481.54 |  |  | 6891 |  |  |  | 974 | [10 empty] | 75.97 |  |  |  | 75.97 | [5 empty] | 75.97 |  |  | 78.66 |  |  |  | 5.72 |  | 4.61 | [8 empty] | 19.43 |  |  |  |  | 0.00
1992 |  |  |  | 7938.46 |  |  | 8028 |  |  |  | 1000 | [10 empty] | 90.37 |  |  |  | 90.37 | [5 empty] | 90.37 |  |  | 91.39 |  |  |  | 2.05 |  | 1.89 | [8 empty] | 7.74 |  |  |  |  | 0.00
1993 |  |  |  | 7395.86 |  |  | 7512 |  |  |  | 1000 | [10 empty] | 84.43 |  |  |  | 84.43 | [5 empty] | 84.43 |  |  | 85.75 |  |  |  | 3.95 |  | 3.47 | [8 empty] | 12.10 |  |  |  |  | 0.00
1994 |  |  |  | 7927.69 |  |  | 8009 |  |  |  | 1000 | [10 empty] | 90.99 |  |  |  | 90.99 | [5 empty] | 90.50 |  |  | 91.43 |  |  |  | 0.29 |  | 0.27 | [8 empty] | 8.74 |  |  |  |  | 0.00
1995 |  |  |  | 7472.62 |  |  | 7597 |  |  |  | 1000 | [10 empty] | 85.78 |  |  |  | 86.43 | [5 empty] | 85.30 |  |  | 86.72 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 13.51 |  |  |  |  | 0.64
1996 |  |  |  | 7626.31 |  |  | 7713 |  |  |  | 1000 | [10 empty] | 87.34 |  |  |  | 87.37 | [5 empty] | 86.82 |  |  | 87.81 |  |  |  | 1.25 |  | 1.11 | [8 empty] | 11.52 |  |  |  |  | 0.03
1997 |  |  |  | 7765.45 |  |  | 8066 |  |  |  | 1000 | [10 empty] | 89.30 |  |  |  | 91.85 | [5 empty] | 88.65 |  |  | 92.08 |  |  |  | 0.17 |  | 0.15 | [8 empty] | 7.99 |  |  |  |  | 2.55
1998 |  |  |  | 6589.73 |  |  | 6686 |  |  |  | 1000 | [10 empty] | 75.77 |  |  |  | 76.10 | [5 empty] | 75.23 |  |  | 76.32 |  |  |  | 23.89 |  | 23.88 | [8 empty] | 0.02 |  |  |  |  | 0.33
1999 |  |  |  | 6828.82 |  |  | 6876 |  |  |  | 1000 | [10 empty] | 78.01 |  |  |  | 78.03 | [5 empty] | 77.95 |  |  | 78.48 |  |  |  | 3.34 |  | 2.69 | [8 empty] | 19.28 |  |  |  |  | 0.02
2000 |  |  |  | 8206.49 |  |  | 8251 |  |  |  | 1000 | [10 empty] | 93.62 |  |  |  | 93.68 | [5 empty] | 93.41 |  |  | 93.92 |  |  |  | 0.32 |  | 0.30 | [8 empty] | 6.02 |  |  |  |  | 0.06
2001 |  |  |  | 7907.41 |  |  | 7966 |  |  |  | 1000 | [10 empty] | 90.63 |  |  |  | 90.66 | [5 empty] | 90.27 |  |  | 90.94 |  |  |  | 2.42 |  | 2.25 | [8 empty] | 7.09 |  |  |  |  | 0.03
2002 |  |  |  | 7827.00 |  |  | 7876 |  |  |  | 1000 | [10 empty] | 89.61 |  |  |  | 89.65 | [5 empty] | 89.34 |  |  | 89.90 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 10.34 |  |  |  |  | 0.04
2003 |  |  |  | 8114.66 |  |  | 8210 |  |  |  | 1003 | [10 empty] | 93.10 |  |  |  | 93.10 | [5 empty] | 92.46 |  |  | 93.71 |  |  |  | 1.36 |  | 1.84 | [8 empty] | 5.07 |  |  |  |  | 0.00
2004 |  |  |  | 7980.12 |  |  | 8121 |  |  |  | 1003 | [10 empty] | 91.50 |  |  |  | 91.50 | [5 empty] | 90.57 |  |  | 92.44 |  |  |  | 2.04 |  | 2.82 | [8 empty] | 5.68 |  |  |  |  | 0.00
2005 |  |  |  | 8080.62 |  |  | 8175 |  |  |  | 1003 | [10 empty] | 92.94 |  |  |  | 92.94 | [5 empty] | 91.97 |  |  | 93.32 |  |  |  | 0.28 |  | 1.74 | [8 empty] | 5.32 |  |  |  |  | 0.00
2006 |  |  |  | 7687.80 |  |  | 7788 |  |  |  | 1003 | [10 empty] | 88.45 |  |  |  | 88.59 | [5 empty] | 87.50 |  |  | 88.90 |  |  |  | 1.53 |  | 4.92 | [8 empty] | 6.50 |  |  |  |  | 0.14
2007 |  |  |  | 7948.88 |  |  | 8039 |  |  |  | 1003 | [10 empty] | 91.44 |  |  |  | 91.50 | [5 empty] | 90.47 |  |  | 91.77 |  |  |  | 0.33 |  | 1.86 | [8 empty] | 6.64 |  |  |  |  | 0.05
2008 |  |  |  | 7743.95 |  |  | 7820 |  |  |  | 1003 | [10 empty] | 88.53 |  |  |  | 88.66 | [5 empty] | 87.90 |  |  | 89.03 |  |  |  | 0.36 |  | 0.32 | [8 empty] | 11.02 |  |  |  |  | 0.13
2009 |  |  |  | 7197.10 |  |  | 7438 |  |  |  | 1003 | [10 empty] | 82.38 |  |  |  | 82.48 | [5 empty] | 81.91 |  |  | 84.91 |  |  |  | 3.56 |  | 3.05 | [8 empty] | 14.47 |  |  |  |  | 0.09
2010 |  |  |  | 7695.50 |  |  | 7969 |  |  |  | 1003 | [10 empty] | 87.85 |  |  |  | 88.54 | [5 empty] | 87.59 |  |  | 90.97 |  |  |  | 0.92 |  | 1.01 | [8 empty] | 10.44 |  |  |  |  | 0.70
2011 |  |  |  | 7835.70 |  |  | 7940 |  |  |  | 1003 | [10 empty] | 89.14 |  |  |  | 90.38 | [5 empty] | 89.18 |  |  | 90.64 |  |  |  | 1.50 |  | 1.52 | [8 empty] | 8.10 |  |  |  |  | 1.24
2012 |  |  |  | 7948.78 |  |  | 8066 |  |  |  | 1003 | [10 empty] | 90.26 |  |  |  | 91.33 | [5 empty] | 90.22 |  |  | 91.83 |  |  |  | 0.14 |  | 0.68 | [8 empty] | 7.99 |  |  |  |  | 1.07
2013 |  |  |  | 7487.11 |  |  | 7656 |  |  |  | 1003 | [10 empty] | 85.43 |  |  |  | 86.56 | [5 empty] | 85.21 |  |  | 87.40 |  |  |  | 3.47 |  | 4.81 | [8 empty] | 8.63 |  |  |  |  | 1.12
2014 |  |  |  | 7785.49 |  |  | 7901 |  |  |  | 1003 | [10 empty] | 88.65 |  |  |  | 89.96 | [5 empty] | 88.61 |  |  | 90.19 |  |  |  | 0.00 |  | 2.13 | [8 empty] | 7.90 |  |  |  |  | 1.31
2015 |  |  |  | 7926.99 |  |  | 8009 |  |  |  | 1003 | [10 empty] | 90.24 |  |  |  | 91.21 | [5 empty] | 90.22 |  |  | 91.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.79 |  |  |  |  | 0.97
2016 |  |  |  | 8004.55 |  |  | 8111 |  |  |  | 1003 | [10 empty] | 91.44 |  |  |  | 92.23 | [5 empty] | 90.85 |  |  | 92.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.77 |  |  |  |  | 0.80
2017 |  |  |  | 7983.09 |  |  | 8067 |  |  |  | 1003 | [10 empty] | 90.86 |  |  |  | 91.90 | [5 empty] | 90.86 |  |  | 92.09 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 8.02 |  |  |  |  | 1.04
2018 |  |  |  | 7732.00 |  |  | 7841 |  |  |  | 1003 | [10 empty] | 88.12 |  |  |  | 88.79 | [5 empty] | 88.00 |  |  | 89.51 |  |  |  | 0.65 |  | 0.65 | [8 empty] | 10.56 |  |  |  |  | 0.67
2019 |  |  |  | 7905.28 |  |  | 8049 |  |  |  | 1003 | [10 empty] | 90.23 |  |  |  | 91.61 | [5 empty] | 89.97 |  |  | 91.88 |  |  |  | 0.01 |  | 0.59 | [8 empty] | 7.80 |  |  |  |  | 1.38
2020 |  |  |  | 7729.61 |  |  | 7981 |  |  |  | 1003 | [10 empty] | 89.12 |  |  |  | 90.39 | [5 empty] | 87.73 |  |  | 90.86 |  |  |  | 0.29 |  | 0.26 | [8 empty] | 9.35 |  |  |  |  | 1.26
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 118
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 803 | [14 empty] | 790 |  |  |  | 6
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 3
Subtotal | [22 empty] | 803 | [14 empty] | 793 |  |  |  | 124
Total | [22 empty] | 803 | [14 empty] | 917
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 4
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 30
16. |  |  | Steam generation systems | [34 empty] | 9
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 32
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
34. |  |  | Miscellaneous Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 8
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 119
Highlights (2020)
Operation at 100% power, except during periods reported in outages

## VANDELLOS-2
2020 Operating Experience
ES-16 | [8 empty] | VANDELLOS-2 | [26 empty] | SPAIN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ANAV (ASOCIACIÓN NUCLEAR ASCÓ-VANDELLÓS A.I.E. (ENDESA/ID))
Owner | [7 empty] | : | EN/ID (ENDESA, IBERDROLA)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-12-29
Thermal power | [12 empty] | : |  |  | 2941 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-12-12
Gross electrical power | [12 empty] | : |  |  | 1087 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-03-08
Reference unit power (net) | [12 empty] | : |  |  | 1045 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.38
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.6 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 21
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.92 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8875.72 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.12 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.53 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.12 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.73 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.15 %
Load Factor (LF) | [18 empty] | : | 96.69 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.21 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 770.15 | 719.54 |  |  |  | 762.25 |  | 716.63 | [8 empty] | 741.77 |  |  | 705.27 | [6 empty] | 751.14 |  | 749.81 |  |  |  | 673.74 |  |  | 770.01 |  |  | 745.20 | [9 empty] | 770.21 |  |  | 8875.72
EAF [%] |  |  |  |  | 99.06 | 99.75 |  |  |  | 99.73 |  | 99.60 | [8 empty] | 98.71 |  |  | 93.74 | [6 empty] | 96.61 |  | 96.44 |  |  |  | 89.55 |  |  | 98.91 |  |  | 99.04 | [9 empty] | 99.06 |  |  | 97.53
UCF [%] |  |  |  |  | 99.36 | 99.87 |  |  |  | 99.86 |  | 99.86 | [8 empty] | 99.86 |  |  | 95.34 | [6 empty] | 99.46 |  | 99.77 |  |  |  | 92.29 |  |  | 99.87 |  |  | 99.76 | [9 empty] | 99.33 |  |  | 98.73
LF [%] |  |  |  |  | 99.06 | 98.93 |  |  |  | 98.17 |  | 95.25 | [8 empty] | 95.41 |  |  | 93.74 | [6 empty] | 96.61 |  | 96.44 |  |  |  | 89.55 |  |  | 98.91 |  |  | 99.04 | [9 empty] | 99.06 |  |  | 96.69
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.45 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 4.52 | [6 empty] | 0.39 |  | 0.06 |  |  |  | 7.57 |  |  | 0.00 |  |  | 0.09 | [9 empty] | 0.54 |  |  | 1.12
UCL [%] |  |  |  |  | 0.45 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 4.51 | [6 empty] | 0.39 |  | 0.06 |  |  |  | 7.56 |  |  | 0.00 |  |  | 0.09 | [9 empty] | 0.54 |  |  | 1.12
PUF [%] |  |  |  |  | 0.19 | 0.13 |  |  |  | 0.14 |  | 0.14 | [8 empty] | 0.14 |  |  | 0.15 | [6 empty] | 0.14 |  | 0.17 |  |  |  | 0.15 |  |  | 0.13 |  |  | 0.16 | [9 empty] | 0.13 |  |  | 0.15
XUF [%] |  |  |  |  | 0.30 | 0.12 |  |  |  | 0.12 |  | 0.25 | [8 empty] | 1.15 |  |  | 1.61 | [6 empty] | 2.85 |  | 3.33 |  |  |  | 2.74 |  |  | 0.96 |  |  | 0.72 | [9 empty] | 0.26 |  |  | 1.21
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 240003.42 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.05 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.32 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.14 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.28 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.57 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.97 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.55 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 5101.90 |  |  | 6262 |  |  |  | 930 | [10 empty] | 67.36 |  |  |  | 68.34 | [5 empty] | 67.51 |  |  | 70.53 |  |  |  | 26.77 |  | 24.98 | [8 empty] | 6.68 |  |  |  |  | 0.99
1989 |  |  |  | 5868.79 |  |  | 6357 |  |  |  | 943 | [10 empty] | 70.58 |  |  |  | 70.62 | [5 empty] | 71.04 |  |  | 72.57 |  |  |  | 22.13 |  | 20.07 | [8 empty] | 9.31 |  |  |  |  | 0.04
1990 |  |  |  | 7334.29 |  |  | 7925 |  |  |  | 943 | [10 empty] | 87.80 |  |  |  | 87.80 | [5 empty] | 88.79 |  |  | 90.47 |  |  |  | 2.90 |  | 2.62 | [8 empty] | 9.58 |  |  |  |  | 0.00
1991 |  |  |  | 7214.92 |  |  | 7825 |  |  |  | 953 | [10 empty] | 86.31 |  |  |  | 88.49 | [5 empty] | 86.42 |  |  | 89.33 |  |  |  | 2.06 |  | 1.86 | [8 empty] | 9.65 |  |  |  |  | 2.18
1992 |  |  |  | 6718.20 |  |  | 7249 |  |  |  | 953 | [10 empty] | 79.63 |  |  |  | 79.63 | [5 empty] | 80.25 |  |  | 82.53 |  |  |  | 5.74 |  | 4.84 | [8 empty] | 15.52 |  |  |  |  | 0.00
1993 |  |  |  | 6910.40 |  |  | 7377 |  |  |  | 961 | [10 empty] | 82.41 |  |  |  | 84.33 | [5 empty] | 82.09 |  |  | 84.21 |  |  |  | 7.95 |  | 7.28 | [8 empty] | 8.39 |  |  |  |  | 1.92
1994 |  |  |  | 7208.44 |  |  | 7676 |  |  |  | 961 | [10 empty] | 85.60 |  |  |  | 85.60 | [5 empty] | 85.63 |  |  | 87.63 |  |  |  | 2.56 |  | 2.25 | [8 empty] | 12.15 |  |  |  |  | 0.00
1995 |  |  |  | 7571.28 |  |  | 7957 |  |  |  | 961 | [10 empty] | 89.48 |  |  |  | 89.48 | [5 empty] | 89.94 |  |  | 90.83 |  |  |  | 0.59 |  | 0.53 | [8 empty] | 9.98 |  |  |  |  | 0.00
1996 |  |  |  | 7511.43 |  |  | 7942 |  |  |  | 961 | [10 empty] | 88.97 |  |  |  | 89.08 | [5 empty] | 88.98 |  |  | 90.41 |  |  |  | 1.63 |  | 1.48 | [8 empty] | 9.45 |  |  |  |  | 0.11
1997 |  |  |  | 7243.11 |  |  | 7961 |  |  |  | 961 | [10 empty] | 85.51 |  |  |  | 88.66 | [5 empty] | 86.05 |  |  | 90.89 |  |  |  | 1.25 |  | 1.12 | [8 empty] | 10.22 |  |  |  |  | 3.16
1998 |  |  |  | 8359.01 |  |  | 8760 |  |  |  | 966 | [10 empty] | 99.05 |  |  |  | 99.26 | [5 empty] | 98.78 |  |  | 100.00 |  |  |  | 0.56 |  | 0.56 | [8 empty] | 0.18 |  |  |  |  | 0.21
1999 |  |  |  | 7224.37 |  |  | 7430 |  |  |  | 1024 | [10 empty] | 82.51 |  |  |  | 83.41 | [5 empty] | 80.50 |  |  | 84.82 |  |  |  | 4.54 |  | 3.97 | [8 empty] | 12.62 |  |  |  |  | 0.89
2000 |  |  |  | 7976.91 |  |  | 7852 |  |  |  | 1043 | [10 empty] | 87.64 |  |  |  | 87.89 | [5 empty] | 87.07 |  |  | 89.39 |  |  |  | 2.77 |  | 2.51 | [8 empty] | 9.60 |  |  |  |  | 0.25
2001 |  |  |  | 9010.35 |  |  | 8727 |  |  |  | 1043 | [10 empty] | 99.43 |  |  |  | 99.43 | [5 empty] | 98.62 |  |  | 99.62 |  |  |  | 0.51 |  | 0.51 | [8 empty] | 0.06 |  |  |  |  | 0.00
2002 |  |  |  | 8010.07 |  |  | 7881 |  |  |  | 1040 | [10 empty] | 88.07 |  |  |  | 89.25 | [5 empty] | 87.92 |  |  | 89.97 |  |  |  | 0.47 |  | 0.42 | [8 empty] | 10.33 |  |  |  |  | 1.18
2003 |  |  |  | 8219.25 |  |  | 8067 |  |  |  | 1040 | [10 empty] | 89.47 |  |  |  | 90.89 | [5 empty] | 90.22 |  |  | 92.09 |  |  |  | 0.23 |  | 0.21 | [8 empty] | 8.90 |  |  |  |  | 1.43
2004 |  |  |  | 8677.05 |  |  | 8429 |  |  |  | 1045 | [10 empty] | 94.49 |  |  |  | 95.79 | [5 empty] | 94.53 |  |  | 95.96 |  |  |  | 4.21 |  | 4.21 | [8 empty] | 0.00 |  |  |  |  | 1.31
2005 |  |  |  | 4698.40 |  |  | 4657 |  |  |  | 1045 | [10 empty] | 51.31 |  |  |  | 51.67 | [5 empty] | 51.33 |  |  | 53.16 |  |  |  | 0.04 |  | 34.82 | [8 empty] | 13.50 |  |  |  |  | 0.36
2006 |  |  |  | 7022.75 |  |  | 6882 |  |  |  | 1045 | [10 empty] | 76.20 |  |  |  | 77.98 | [5 empty] | 76.72 |  |  | 78.56 |  |  |  | 14.22 |  | 12.92 | [8 empty] | 9.10 |  |  |  |  | 1.78
2007 |  |  |  | 5387.75 |  |  | 5313 |  |  |  | 1045 | [10 empty] | 59.15 |  |  |  | 59.43 | [5 empty] | 58.86 |  |  | 60.65 |  |  |  | 28.65 |  | 26.16 | [8 empty] | 14.41 |  |  |  |  | 0.29
2008 |  |  |  | 6926.03 |  |  | 6922 |  |  |  | 1045 | [10 empty] | 75.39 |  |  |  | 76.31 | [5 empty] | 75.45 |  |  | 78.80 |  |  |  | 22.68 |  | 22.39 | [8 empty] | 1.30 |  |  |  |  | 0.92
2009 |  |  |  | 5164.06 |  |  | 5241 |  |  |  | 1045 | [10 empty] | 56.42 |  |  |  | 57.45 | [5 empty] | 56.42 |  |  | 59.84 |  |  |  | 4.36 |  | 2.62 | [8 empty] | 39.93 |  |  |  |  | 1.03
2010 |  |  |  | 8498.80 |  |  | 8293 |  |  |  | 1045 | [10 empty] | 92.79 |  |  |  | 94.10 | [5 empty] | 92.84 |  |  | 94.67 |  |  |  | 5.74 |  | 5.73 | [8 empty] | 0.17 |  |  |  |  | 1.31
2011 |  |  |  | 7034.35 |  |  | 6894 |  |  |  | 1045 | [10 empty] | 77.30 |  |  |  | 78.59 | [5 empty] | 76.85 |  |  | 78.71 |  |  |  | 2.52 |  | 7.79 | [8 empty] | 13.62 |  |  |  |  | 1.29
2012 |  |  |  | 7718.56 |  |  | 7549 |  |  |  | 1045 | [10 empty] | 84.26 |  |  |  | 85.27 | [5 empty] | 84.09 |  |  | 85.94 |  |  |  | 0.76 |  | 1.83 | [8 empty] | 12.90 |  |  |  |  | 1.01
2013 |  |  |  | 7742.95 |  |  | 7676 |  |  |  | 1045 | [10 empty] | 84.75 |  |  |  | 85.81 | [5 empty] | 84.58 |  |  | 87.63 |  |  |  | 1.63 |  | 3.30 | [8 empty] | 10.89 |  |  |  |  | 1.05
2014 |  |  |  | 8824.89 |  |  | 8663 |  |  |  | 1045 | [10 empty] | 96.41 |  |  |  | 98.26 | [5 empty] | 96.40 |  |  | 98.89 |  |  |  | 1.59 |  | 1.59 | [8 empty] | 0.16 |  |  |  |  | 1.85
2015 |  |  |  | 7478.53 |  |  | 7353 |  |  |  | 1045 | [10 empty] | 81.70 |  |  |  | 83.06 | [5 empty] | 81.70 |  |  | 83.94 |  |  |  | 0.69 |  | 3.88 | [8 empty] | 13.06 |  |  |  |  | 1.36
2016 |  |  |  | 7650.33 |  |  | 7568 |  |  |  | 1045 | [10 empty] | 83.88 |  |  |  | 85.24 | [5 empty] | 83.34 |  |  | 86.16 |  |  |  | 0.03 |  | 2.90 | [8 empty] | 11.86 |  |  |  |  | 1.36
2017 |  |  |  | 8997.98 |  |  | 8760 |  |  |  | 1045 | [10 empty] | 98.29 |  |  |  | 99.61 | [5 empty] | 98.29 |  |  | 100.00 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 0.30 |  |  |  |  | 1.32
2018 |  |  |  | 5009.18 |  |  | 4947 |  |  |  | 1045 | [10 empty] | 54.72 |  |  |  | 55.61 | [5 empty] | 54.72 |  |  | 56.47 |  |  |  | 28.07 |  | 24.26 | [8 empty] | 20.13 |  |  |  |  | 0.89
2019 |  |  |  | 7383.68 |  |  | 7293 |  |  |  | 1045 | [10 empty] | 80.66 |  |  |  | 81.76 | [5 empty] | 80.66 |  |  | 83.25 |  |  |  | 5.94 |  | 7.15 | [8 empty] | 11.09 |  |  |  |  | 1.10
2020 |  |  |  | 8875.72 |  |  | 8784 |  |  |  | 1045 | [10 empty] | 97.53 |  |  |  | 98.73 | [5 empty] | 96.69 |  |  | 100.00 |  |  |  | 1.12 |  | 1.12 | [8 empty] | 0.15 |  |  |  |  | 1.21
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 445
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 699 |  |  |  | 16
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 47
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [39 empty] | 55
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 9
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 11
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 4
Subtotal | [37 empty] | 749 |  |  |  | 528 | [11 empty] | 14
Total | [22 empty] | 0 | [14 empty] | 1291
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 18
12. |  |  | Reactor I&C Systems | [34 empty] | 57
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 96
15. |  |  | Reactor Cooling Systems | [34 empty] | 99
16. |  |  | Steam generation systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 15
32. |  |  | Feedwater and Main Steam System | [34 empty] | 64
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 57
42. |  |  | Electrical Power Supply Systems | [34 empty] | 89
Total | [37 empty] | 508
Highlights (2020)
In 2020, Vandellos II NPP produced 9234.81 gross GWh, slightly lower than expected gross 9374 GWh. These were the main events affecting the operation: - On January 20th, load reduction due unavailability of sea water cleaning grids. Power reduced to 70%. - On February 29th, load reduction to 70% due to load dispatching (grid operator) - On April, two load reductions to 70% due to load dispatching (grid operator) - On May, load reduction to 70% due to load dispatching (grid operator). - On June, load reduction to 81% in order to investigate and repair a water leak on main condenser. - On July, load reduction to 95% to further investigate water leak on condenser. - On September 1st, load reduction to 8% and main turbine shutdown due to corrective maintenance on stator cooling water system. - On November and December corrective maintenance on AF-P01B condensate drainage pump. Due to these incidents, the load factor was 96.71%. The net production was 8865.41 GWh, versus expected 8997.44 GWh, resulting in a measured/expected ratio of 98.53%.