## KUOSHENG-1
2020 Operating Experience
TW-3 | [8 empty] | KUOSHENG-1 | [26 empty] | TAIWAN, CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TPC (Taiwan Power Co.)
Owner | [7 empty] | : | TPC (Taiwan Power Co.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-11-19
Thermal power | [12 empty] | : |  |  | 2894 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-05-21
Gross electrical power | [12 empty] | : |  |  | 985 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-12-28
Reference unit power (net) | [12 empty] | : |  |  | 985 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.32
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.06
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 29 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.18 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.64
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 624 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 145 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7374.21 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.6 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.21 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.4 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.05 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.55 %
Load Factor (LF) | [18 empty] | : | 85.23 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.84 %
Operating Factor (OF) | [18 empty] | : | 87.3 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1116 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 726.30 | 448.31 |  |  |  | 4.59 |  | 688.74 | [8 empty] | 652.20 |  |  | 693.38 | [6 empty] | 710.86 |  | 710.98 |  |  |  | 689.69 |  |  | 727.83 |  |  | 706.89 | [9 empty] | 614.44 |  |  | 7374.21
EAF [%] |  |  |  |  | 99.05 | 65.25 |  |  |  | 0.63 |  | 97.08 | [8 empty] | 89.00 |  |  | 97.77 | [6 empty] | 97.00 |  | 97.02 |  |  |  | 97.25 |  |  | 99.32 |  |  | 99.67 | [9 empty] | 83.84 |  |  | 85.21
UCF [%] |  |  |  |  | 99.33 | 65.25 |  |  |  | 0.65 |  | 97.08 | [8 empty] | 89.40 |  |  | 99.13 | [6 empty] | 99.89 |  | 99.80 |  |  |  | 99.16 |  |  | 99.58 |  |  | 99.76 | [9 empty] | 83.86 |  |  | 86.05
LF [%] |  |  |  |  | 99.11 | 65.39 |  |  |  | 0.63 |  | 97.11 | [8 empty] | 89.00 |  |  | 97.77 | [6 empty] | 97.00 |  | 97.02 |  |  |  | 97.25 |  |  | 99.32 |  |  | 99.67 | [9 empty] | 83.84 |  |  | 85.23
OF [%] |  |  |  |  | 100.00 | 65.66 |  |  |  | 3.76 |  | 100.00 | [8 empty] | 91.67 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 86.69 |  |  | 87.30
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.35 | [8 empty] | 0.09 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 16.14 |  |  | 1.60
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.34 | [8 empty] | 0.08 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 16.14 |  |  | 1.40
PUF [%] |  |  |  |  | 0.67 | 34.75 |  |  |  | 99.35 |  | 2.58 | [8 empty] | 10.52 |  |  | 0.87 | [6 empty] | 0.11 |  | 0.20 |  |  |  | 0.84 |  |  | 0.42 |  |  | 0.24 | [9 empty] | 0.00 |  |  | 12.55
XUF [%] |  |  |  |  | 0.27 | 0.00 |  |  |  | 0.03 |  | 0.00 | [8 empty] | 0.40 |  |  | 1.37 | [6 empty] | 2.89 |  | 2.78 |  |  |  | 1.91 |  |  | 0.26 |  |  | 0.09 | [9 empty] | 0.02 |  |  | 0.84
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 266956.1 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.26 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.12 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.66 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.22 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.73 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.39 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | Data not provided
1982 |  |  |  | "
1983 |  |  |  | "
1984 |  |  |  | "
1985 |  |  |  | "
1986 |  |  |  | "
1987 |  |  |  | "
1988 |  |  |  | "
1989 |  |  |  | 5329.05 |  |  | 6447 |  |  |  | 951 | [10 empty] | 62.97 |  |  |  | 64.94 | [5 empty] | 63.97 |  |  | 73.60 |  |  |  | 2.70 |  | 1.80 | [8 empty] | 33.27 |  |  |  |  | 1.96
1990 |  |  |  | 6898.01 |  |  | 8201 |  |  |  | 918 | [10 empty] | 86.76 |  |  |  | 87.39 | [5 empty] | 85.78 |  |  | 93.62 |  |  |  | 4.72 |  | 4.32 | [8 empty] | 8.28 |  |  |  |  | 0.63
1991 |  |  |  | 5850.77 |  |  | 6678 |  |  |  | 951 | [10 empty] | 71.40 |  |  |  | 71.40 | [5 empty] | 70.23 |  |  | 76.23 |  |  |  | 4.87 |  | 3.65 | [8 empty] | 24.95 |  |  |  |  | 0.00
1992 |  |  |  | 6152.35 |  |  | 7126 |  |  |  | 951 | [10 empty] | 78.43 |  |  |  | 78.43 | [5 empty] | 73.65 |  |  | 81.12 |  |  |  | 6.31 |  | 5.28 | [8 empty] | 16.28 |  |  |  |  | 0.00
1993 |  |  |  | 5679.52 |  |  | 6457 |  |  |  | 951 | [10 empty] | 71.07 |  |  |  | 71.07 | [5 empty] | 68.18 |  |  | 73.71 |  |  |  | 4.91 |  | 3.67 | [8 empty] | 25.25 |  |  |  |  | 0.00
1994 |  |  |  | 6302.27 |  |  | 7077 |  |  |  | 950 | [10 empty] | 76.94 |  |  |  | 77.80 | [5 empty] | 75.73 |  |  | 80.79 |  |  |  | 1.78 |  | 1.41 | [8 empty] | 20.79 |  |  |  |  | 0.86
1995 |  |  |  | 6897.91 |  |  | 7734 |  |  |  | 948 | [10 empty] | 84.56 |  |  |  | 84.73 | [5 empty] | 83.06 |  |  | 88.29 |  |  |  | 10.72 |  | 10.17 | [8 empty] | 5.10 |  |  |  |  | 0.17
1996 |  |  |  | 6950.76 |  |  | 7573 |  |  |  | 948 | [10 empty] | 84.32 |  |  |  | 84.83 | [5 empty] | 83.47 |  |  | 86.21 |  |  |  | 2.53 |  | 2.20 | [8 empty] | 12.97 |  |  |  |  | 0.51
1997 |  |  |  | 6277.80 |  |  | 6978 |  |  |  | 948 | [10 empty] | 77.51 |  |  |  | 77.69 | [5 empty] | 75.60 |  |  | 79.66 |  |  |  | 6.02 |  | 4.97 | [8 empty] | 17.34 |  |  |  |  | 0.18
1998 |  |  |  | 6426.04 |  |  | 7209 |  |  |  | 948 | [10 empty] | 79.73 |  |  |  | 81.16 | [5 empty] | 77.38 |  |  | 82.29 |  |  |  | 4.79 |  | 4.08 | [8 empty] | 14.76 |  |  |  |  | 1.44
1999 |  |  |  | 7686.77 |  |  | 8439 |  |  |  | 948 | [10 empty] | 93.81 |  |  |  | 95.10 | [5 empty] | 92.56 |  |  | 96.34 |  |  |  | 4.03 |  | 3.99 | [8 empty] | 0.91 |  |  |  |  | 1.28
2000 |  |  |  | 6588.58 |  |  | 7391 |  |  |  | 948 | [10 empty] | 80.17 |  |  |  | 81.33 | [5 empty] | 79.12 |  |  | 84.14 |  |  |  | 6.06 |  | 5.24 | [8 empty] | 13.43 |  |  |  |  | 1.16
2001 |  |  |  | 6452.28 |  |  | 7070 |  |  |  | 948 | [10 empty] | 78.81 |  |  |  | 79.38 | [5 empty] | 77.70 |  |  | 80.71 |  |  |  | 0.86 |  | 0.69 | [8 empty] | 19.93 |  |  |  |  | 0.57
2002 |  |  |  | 8068.54 |  |  | 8693 |  |  |  | 948 | [10 empty] | 98.14 |  |  |  | 98.49 | [5 empty] | 97.16 |  |  | 99.24 |  |  |  | 0.97 |  | 0.96 | [8 empty] | 0.55 |  |  |  |  | 0.35
2003 |  |  |  | 6444.90 |  |  | 6968 |  |  |  | 948 | [10 empty] | 78.30 |  |  |  | 78.48 | [5 empty] | 77.61 |  |  | 79.54 |  |  |  | 0.05 |  | 4.95 | [8 empty] | 16.57 |  |  |  |  | 0.18
2004 |  |  |  | 6978.48 |  |  | 7516 |  |  |  | 948 | [10 empty] | 84.65 |  |  |  | 85.15 | [5 empty] | 83.80 |  |  | 85.56 |  |  |  | 1.52 |  | 1.32 | [8 empty] | 13.54 |  |  |  |  | 0.49
2005 |  |  |  | 8150.12 |  |  | 8749 |  |  |  | 948 | [10 empty] | 98.45 |  |  |  | 99.66 | [5 empty] | 98.14 |  |  | 99.87 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 0.32 |  |  |  |  | 1.21
2006 |  |  |  | 6903.61 |  |  | 7325 |  |  |  | 985 | [10 empty] | 81.88 |  |  |  | 82.57 | [5 empty] | 81.01 |  |  | 83.62 |  |  |  | 1.91 |  | 1.61 | [8 empty] | 15.83 |  |  |  |  | 0.69
2007 |  |  |  | 7104.56 |  |  | 7429 |  |  |  | 985 | [10 empty] | 82.33 |  |  |  | 83.49 | [5 empty] | 82.34 |  |  | 84.81 |  |  |  | 0.81 |  | 0.68 | [8 empty] | 15.83 |  |  |  |  | 1.16
2008 |  |  |  | 8384.82 |  |  | 8673 |  |  |  | 985 | [10 empty] | 96.89 |  |  |  | 97.97 | [5 empty] | 96.91 |  |  | 98.74 |  |  |  | 1.68 |  | 1.68 | [8 empty] | 0.35 |  |  |  |  | 1.08
2009 |  |  |  | 7558.45 |  |  | 7823 |  |  |  | 985 | [10 empty] | 87.52 |  |  |  | 88.31 | [5 empty] | 87.60 |  |  | 89.30 |  |  |  | 0.97 |  | 0.87 | [8 empty] | 10.83 |  |  |  |  | 0.78
2010 |  |  |  | 7949.61 |  |  | 8150 |  |  |  | 985 | [10 empty] | 91.91 |  |  |  | 92.42 | [5 empty] | 92.13 |  |  | 93.04 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 7.57 |  |  |  |  | 0.50
2011 |  |  |  | 8564.68 |  |  | 8760 |  |  |  | 985 | [10 empty] | 99.10 |  |  |  | 99.67 | [5 empty] | 99.26 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.33 |  |  |  |  | 0.57
2012 |  |  |  | 6170.62 |  |  | 6412 |  |  |  | 985 | [10 empty] | 71.31 |  |  |  | 71.83 | [5 empty] | 71.32 |  |  | 73.00 |  |  |  | 1.48 |  | 1.08 | [8 empty] | 27.09 |  |  |  |  | 0.51
2013 |  |  |  | 7859.12 |  |  | 8165 |  |  |  | 985 | [10 empty] | 91.05 |  |  |  | 92.16 | [5 empty] | 91.08 |  |  | 93.21 |  |  |  | 0.90 |  | 0.84 | [8 empty] | 7.00 |  |  |  |  | 1.11
2014 |  |  |  | 8490.72 |  |  | 8664 |  |  |  | 985 | [10 empty] | 97.96 |  |  |  | 98.25 | [5 empty] | 98.40 |  |  | 98.90 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 1.72 |  |  |  |  | 0.28
2015 |  |  |  | 7575.91 |  |  | 7807 |  |  |  | 985 | [10 empty] | 87.49 |  |  |  | 88.53 | [5 empty] | 87.80 |  |  | 89.12 |  |  |  | 0.81 |  | 1.23 | [8 empty] | 10.25 |  |  |  |  | 1.04
2016 |  |  |  | 7665.07 |  |  | 7980 |  |  |  | 985 | [10 empty] | 88.43 |  |  |  | 90.27 | [5 empty] | 88.59 |  |  | 90.85 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.72 |  |  |  |  | 1.84
2017 |  |  |  | 4716.99 |  |  | 4916 |  |  |  | 985 | [10 empty] | 54.63 |  |  |  | 55.24 | [5 empty] | 54.67 |  |  | 56.12 |  |  |  | 0.52 |  | 0.29 | [8 empty] | 44.47 |  |  |  |  | 0.61
2018 |  |  |  | 7236.39 |  |  | 7486 |  |  |  | 985 | [10 empty] | 83.71 |  |  |  | 84.52 | [5 empty] | 83.87 |  |  | 85.46 |  |  |  | 0.22 |  | 0.19 | [8 empty] | 15.30 |  |  |  |  | 0.81
2019 |  |  |  | 8549.07 |  |  | 8760 |  |  |  | 985 | [10 empty] | 98.97 |  |  |  | 99.57 | [5 empty] | 99.08 |  |  | 100.00 |  |  |  | 0.11 |  | 0.11 | [8 empty] | 0.33 |  |  |  |  | 0.59
2020 |  |  |  | 7374.21 |  |  | 7668 |  |  |  | 985 | [10 empty] | 85.21 |  |  |  | 86.05 | [5 empty] | 85.23 |  |  | 87.30 |  |  |  | 1.60 |  | 1.40 | [8 empty] | 12.55 |  |  |  |  | 0.84
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 99 | [14 empty] | 101
B. |  | Refuelling without maintenance | [35 empty] | 35
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 955 | [14 empty] | 982
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 62 | [14 empty] | 58
E. |  | Testing of plant systems or components | [35 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 10
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
Z. |  | Other | [51 empty] | 2
Subtotal | [22 empty] | 1017 |  |  |  | 99 | [10 empty] | 1082 |  |  |  | 111 | [11 empty] | 8
Total | [22 empty] | 1116 | [14 empty] | 1201
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 19
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [19 empty] | 99 | [14 empty] | 26
32. |  |  | Feedwater and Main Steam System | [34 empty] | 22
33. |  |  | Circulating Water System | [34 empty] | 7
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 14
42. |  |  | Electrical Power Supply Systems | [34 empty] | 10
Total | [22 empty] | 99 | [14 empty] | 115

## KUOSHENG-2
2020 Operating Experience
TW-4 | [8 empty] | KUOSHENG-2 | [26 empty] | TAIWAN, CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TPC (Taiwan Power Co.)
Owner | [7 empty] | : | TPC (Taiwan Power Co.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-03-15
Thermal power | [12 empty] | : |  |  | 2894 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-06-29
Gross electrical power | [12 empty] | : |  |  | 985 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-03-16
Reference unit power (net) | [12 empty] | : |  |  | 985 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.32
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.06
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 29 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.18 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.64
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 624 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 145 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7589.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.34 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.56 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.3 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.16 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.53 %
Load Factor (LF) | [18 empty] | : | 87.71 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.61 %
Operating Factor (OF) | [18 empty] | : | 88.81 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 983 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 737.86 | 683.55 |  |  |  | 735.68 |  | 686.40 | [8 empty] | 723.35 |  |  | 704.37 | [6 empty] | 722.73 |  | 707.10 |  |  |  | 696.20 |  |  | 722.52 |  |  | 469.51 | [9 empty] | 0.00 |  |  | 7589.27
EAF [%] |  |  |  |  | 99.93 | 99.15 |  |  |  | 99.91 |  | 96.69 | [8 empty] | 98.70 |  |  | 99.32 | [6 empty] | 98.62 |  | 96.49 |  |  |  | 98.17 |  |  | 98.59 |  |  | 66.20 | [9 empty] | 0.00 |  |  | 87.56
UCF [%] |  |  |  |  | 99.93 | 99.51 |  |  |  | 99.91 |  | 96.69 | [8 empty] | 99.38 |  |  | 99.92 | [6 empty] | 99.95 |  | 98.78 |  |  |  | 99.38 |  |  | 99.32 |  |  | 66.23 | [9 empty] | 0.00 |  |  | 88.16
LF [%] |  |  |  |  | 100.69 | 99.71 |  |  |  | 100.39 |  | 96.79 | [8 empty] | 98.70 |  |  | 99.32 | [6 empty] | 98.62 |  | 96.49 |  |  |  | 98.17 |  |  | 98.59 |  |  | 66.20 | [9 empty] | 0.00 |  |  | 87.71
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 66.81 | [9 empty] | 0.00 |  |  | 88.81
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 3.22 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.49 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.34
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 3.22 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.49 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.30
PUF [%] |  |  |  |  | 0.07 | 0.49 |  |  |  | 0.09 |  | 0.10 | [8 empty] | 0.62 |  |  | 0.08 | [6 empty] | 0.05 |  | 1.22 |  |  |  | 0.13 |  |  | 0.66 |  |  | 33.77 | [9 empty] | 100.00 |  |  | 11.53
XUF [%] |  |  |  |  | 0.00 | 0.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.68 |  |  | 0.60 | [6 empty] | 1.33 |  | 2.29 |  |  |  | 1.22 |  |  | 0.73 |  |  | 0.03 | [9 empty] | 0.00 |  |  | 0.61
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 248570.76 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.48 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.33 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.56 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.66 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.97 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | Data not provided
1984 |  |  |  | "
1985 |  |  |  | "
1986 |  |  |  | "
1987 |  |  |  | "
1988 |  |  |  | "
1989 |  |  |  | 5227.30 |  |  | 6390 |  |  |  | 951 | [10 empty] | 61.88 |  |  |  | 65.32 | [5 empty] | 62.75 |  |  | 72.95 |  |  |  | 6.82 |  | 4.78 | [8 empty] | 29.90 |  |  |  |  | 3.43
1990 |  |  |  | 6000.55 |  |  | 6819 |  |  |  | 936 | [10 empty] | 73.46 |  |  |  | 73.99 | [5 empty] | 73.18 |  |  | 77.84 |  |  |  | 2.86 |  | 2.18 | [8 empty] | 23.83 |  |  |  |  | 0.53
1991 |  |  |  | 7186.35 |  |  | 8101 |  |  |  | 951 | [10 empty] | 89.34 |  |  |  | 89.34 | [5 empty] | 86.26 |  |  | 92.48 |  |  |  | 1.90 |  | 1.73 | [8 empty] | 8.93 |  |  |  |  | 0.00
1992 |  |  |  | 6176.28 |  |  | 6985 |  |  |  | 951 | [10 empty] | 76.77 |  |  |  | 76.77 | [5 empty] | 73.94 |  |  | 79.52 |  |  |  | 4.16 |  | 3.33 | [8 empty] | 19.89 |  |  |  |  | 0.00
1993 |  |  |  | 6138.11 |  |  | 6921 |  |  |  | 951 | [10 empty] | 74.94 |  |  |  | 74.94 | [5 empty] | 73.68 |  |  | 79.01 |  |  |  | 5.10 |  | 4.03 | [8 empty] | 21.03 |  |  |  |  | 0.00
1994 |  |  |  | 6224.08 |  |  | 6868 |  |  |  | 950 | [10 empty] | 74.80 |  |  |  | 76.04 | [5 empty] | 74.79 |  |  | 78.40 |  |  |  | 2.42 |  | 1.89 | [8 empty] | 22.07 |  |  |  |  | 1.24
1995 |  |  |  | 5999.72 |  |  | 6543 |  |  |  | 948 | [10 empty] | 72.20 |  |  |  | 72.92 | [5 empty] | 72.25 |  |  | 74.69 |  |  |  | 3.91 |  | 2.96 | [8 empty] | 24.12 |  |  |  |  | 0.72
1996 |  |  |  | 7423.24 |  |  | 7978 |  |  |  | 948 | [10 empty] | 89.61 |  |  |  | 90.03 | [5 empty] | 89.14 |  |  | 90.82 |  |  |  | 1.76 |  | 1.61 | [8 empty] | 8.36 |  |  |  |  | 0.42
1997 |  |  |  | 7087.25 |  |  | 7745 |  |  |  | 948 | [10 empty] | 86.08 |  |  |  | 88.69 | [5 empty] | 85.34 |  |  | 88.41 |  |  |  | 6.15 |  | 5.82 | [8 empty] | 5.50 |  |  |  |  | 2.61
1998 |  |  |  | 6549.57 |  |  | 7242 |  |  |  | 948 | [10 empty] | 79.35 |  |  |  | 80.27 | [5 empty] | 78.87 |  |  | 82.67 |  |  |  | 4.52 |  | 3.80 | [8 empty] | 15.93 |  |  |  |  | 0.92
1999 |  |  |  | 6831.88 |  |  | 7544 |  |  |  | 948 | [10 empty] | 84.17 |  |  |  | 85.92 | [5 empty] | 82.27 |  |  | 86.12 |  |  |  | 1.11 |  | 0.97 | [8 empty] | 13.12 |  |  |  |  | 1.75
2000 |  |  |  | 7237.59 |  |  | 8234 |  |  |  | 948 | [10 empty] | 89.28 |  |  |  | 91.45 | [5 empty] | 86.91 |  |  | 93.74 |  |  |  | 7.11 |  | 7.00 | [8 empty] | 1.55 |  |  |  |  | 2.16
2001 |  |  |  | 5976.73 |  |  | 6772 |  |  |  | 948 | [10 empty] | 72.43 |  |  |  | 74.10 | [5 empty] | 71.97 |  |  | 77.31 |  |  |  | 4.93 |  | 3.84 | [8 empty] | 22.06 |  |  |  |  | 1.67
2002 |  |  |  | 6922.55 |  |  | 7530 |  |  |  | 948 | [10 empty] | 85.05 |  |  |  | 85.47 | [5 empty] | 83.36 |  |  | 85.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.53 |  |  |  |  | 0.42
2003 |  |  |  | 7623.10 |  |  | 8427 |  |  |  | 948 | [10 empty] | 93.52 |  |  |  | 93.68 | [5 empty] | 91.80 |  |  | 96.20 |  |  |  | 4.62 |  | 4.54 | [8 empty] | 1.78 |  |  |  |  | 0.16
2004 |  |  |  | 6493.97 |  |  | 7301 |  |  |  | 948 | [10 empty] | 79.75 |  |  |  | 81.29 | [5 empty] | 77.98 |  |  | 83.12 |  |  |  | 0.95 |  | 0.78 | [8 empty] | 17.93 |  |  |  |  | 1.54
2005 |  |  |  | 6737.82 |  |  | 7424 |  |  |  | 948 | [10 empty] | 82.26 |  |  |  | 83.53 | [5 empty] | 81.13 |  |  | 84.75 |  |  |  | 0.22 |  | 0.42 | [8 empty] | 16.04 |  |  |  |  | 1.27
2006 |  |  |  | 7868.39 |  |  | 8560 |  |  |  | 948 | [10 empty] | 95.93 |  |  |  | 96.58 | [5 empty] | 94.75 |  |  | 97.72 |  |  |  | 0.29 |  | 0.28 | [8 empty] | 3.14 |  |  |  |  | 0.65
2007 |  |  |  | 7031.52 |  |  | 7716 |  |  |  | 948 | [10 empty] | 86.07 |  |  |  | 86.74 | [5 empty] | 84.67 |  |  | 88.08 |  |  |  | 1.22 |  | 1.07 | [8 empty] | 12.18 |  |  |  |  | 0.67
2008 |  |  |  | 7304.97 |  |  | 8029 |  |  |  | 948 | [10 empty] | 87.72 |  |  |  | 89.92 | [5 empty] | 87.72 |  |  | 91.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.08 |  |  |  |  | 2.19
2009 |  |  |  | 8068.14 |  |  | 8739 |  |  |  | 948 | [10 empty] | 97.15 |  |  |  | 99.22 | [5 empty] | 97.15 |  |  | 99.76 |  |  |  | 0.33 |  | 0.33 | [8 empty] | 0.45 |  |  |  |  | 2.07
2010 |  |  |  | 6997.81 |  |  | 7649 |  |  |  | 948 | [10 empty] | 84.27 |  |  |  | 86.28 | [5 empty] | 84.27 |  |  | 87.32 |  |  |  | 2.82 |  | 2.51 | [8 empty] | 11.22 |  |  |  |  | 2.01
2011 |  |  |  | 7443.47 |  |  | 7909 |  |  |  | 985 | [10 empty] | 88.78 |  |  |  | 89.13 | [5 empty] | 89.34 |  |  | 90.29 |  |  |  | 0.43 |  | 0.39 | [8 empty] | 10.49 |  |  |  |  | 0.35
2012 |  |  |  | 8530.25 |  |  | 8765 |  |  |  | 985 | [10 empty] | 98.51 |  |  |  | 99.26 | [5 empty] | 98.59 |  |  | 99.78 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.26 |  |  |  |  | 0.75
2013 |  |  |  | 7784.60 |  |  | 8057 |  |  |  | 985 | [10 empty] | 90.16 |  |  |  | 90.96 | [5 empty] | 90.22 |  |  | 91.97 |  |  |  | 0.49 |  | 0.45 | [8 empty] | 8.59 |  |  |  |  | 0.80
2014 |  |  |  | 7917.00 |  |  | 8098 |  |  |  | 985 | [10 empty] | 91.27 |  |  |  | 91.53 | [5 empty] | 91.75 |  |  | 92.44 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 8.17 |  |  |  |  | 0.26
2015 |  |  |  | 8571.33 |  |  | 8760 |  |  |  | 985 | [10 empty] | 98.86 |  |  |  | 99.59 | [5 empty] | 99.34 |  |  | 100.00 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 0.34 |  |  |  |  | 0.73
2016 |  |  |  | 2415.47 |  |  | 2450 |  |  |  | 985 | [10 empty] | 79.09 |  |  |  | 79.12 | [5 empty] | 27.92 |  |  | 27.89 |  |  |  | 12.57 |  | 11.38 | [8 empty] | 9.50 |  |  |  |  | 0.03
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 985 | [10 empty] | 75.07 |  |  |  | 75.07 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.93 |  |  |  |  | 0.00
2018 |  |  |  | 4661.56 |  |  | 4960 |  |  |  | 985 | [10 empty] | 54.02 |  |  |  | 54.74 | [5 empty] | 54.02 |  |  | 56.62 |  |  |  | 2.80 |  | 1.58 | [8 empty] | 43.68 |  |  |  |  | 0.71
2019 |  |  |  | 7481.74 |  |  | 7712 |  |  |  | 985 | [10 empty] | 86.59 |  |  |  | 87.02 | [5 empty] | 86.71 |  |  | 88.04 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 12.94 |  |  |  |  | 0.43
2020 |  |  |  | 7589.27 |  |  | 7801 |  |  |  | 985 | [10 empty] | 87.56 |  |  |  | 88.16 | [5 empty] | 87.71 |  |  | 88.81 |  |  |  | 0.34 |  | 0.30 | [8 empty] | 11.53 |  |  |  |  | 0.61
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 123
B. |  | Refuelling without maintenance | [35 empty] | 35
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 983 | [14 empty] | 780
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 253
E. |  | Testing of plant systems or components | [35 empty] | 13
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 10
M. |  | Governmental requirements or court decisions | [51 empty] | 347
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 10
Z. |  | Other | [39 empty] | 1 | [11 empty] | 1
Subtotal | [22 empty] | 983 | [14 empty] | 1081 |  |  |  | 134 | [11 empty] | 364
Total | [22 empty] | 983 | [14 empty] | 1579
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 30
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 14
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 10
32. |  |  | Feedwater and Main Steam System | [34 empty] | 20
33. |  |  | Circulating Water System | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 388
Total | [37 empty] | 490

## MAANSHAN-1
2020 Operating Experience
TW-5 | [8 empty] | MAANSHAN-1 | [26 empty] | TAIWAN, CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TPC (Taiwan Power Co.)
Owner | [7 empty] | : | TPC (Taiwan Power Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (WE 312) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-08-21
Thermal power | [12 empty] | : |  |  | 2822 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-05-09
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-07-27
Reference unit power (net) | [12 empty] | : |  |  | 936 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.22
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 3
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.56
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.75 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8222.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.74 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.19 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.74 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.19 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.07 %
Load Factor (LF) | [18 empty] | : | 100 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.36 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 56 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 705.77 | 660.84 |  |  |  | 706.82 |  | 683.30 | [8 empty] | 698.64 |  |  | 676.38 | [6 empty] | 697.35 |  | 698.01 |  |  |  | 614.51 |  |  | 699.37 |  |  | 679.00 | [9 empty] | 702.14 |  |  | 8222.12
EAF [%] |  |  |  |  | 99.95 | 99.95 |  |  |  | 99.96 |  | 99.95 | [8 empty] | 99.66 |  |  | 99.95 | [6 empty] | 100.00 |  | 99.89 |  |  |  | 91.01 |  |  | 99.95 |  |  | 99.95 | [9 empty] | 99.95 |  |  | 99.19
UCF [%] |  |  |  |  | 99.95 | 99.95 |  |  |  | 99.96 |  | 99.95 | [8 empty] | 99.66 |  |  | 99.95 | [6 empty] | 100.00 |  | 99.89 |  |  |  | 91.01 |  |  | 99.95 |  |  | 99.95 | [9 empty] | 99.95 |  |  | 99.19
LF [%] |  |  |  |  | 101.35 | 101.44 |  |  |  | 101.50 |  | 101.39 | [8 empty] | 100.32 |  |  | 100.36 | [6 empty] | 100.14 |  | 100.23 |  |  |  | 91.18 |  |  | 100.43 |  |  | 100.75 | [9 empty] | 100.83 |  |  | 100.00
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 92.22 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.36
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 8.99 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.74
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 8.99 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.74
PUF [%] |  |  |  |  | 0.05 | 0.05 |  |  |  | 0.04 |  | 0.05 | [8 empty] | 0.34 |  |  | 0.05 | [6 empty] | 0.00 |  | 0.11 |  |  |  | 0.00 |  |  | 0.05 |  |  | 0.05 | [9 empty] | 0.05 |  |  | 0.07
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 239618.9 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.91 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.73 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.71 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.74 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.67 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.82 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | Data not provided
1985 |  |  |  | "
1986 |  |  |  | "
1987 |  |  |  | "
1988 |  |  |  | "
1989 |  |  |  | 5418.45 |  |  | 6305 |  |  |  | 890 | [10 empty] | 65.98 |  |  |  | 66.28 | [5 empty] | 69.50 |  |  | 71.97 |  |  |  | 27.44 |  | 25.06 | [8 empty] | 8.66 |  |  |  |  | 0.30
1990 |  |  |  | 6098.90 |  |  | 7079 |  |  |  | 894 | [10 empty] | 76.76 |  |  |  | 77.76 | [5 empty] | 77.88 |  |  | 80.81 |  |  |  | 4.19 |  | 3.40 | [8 empty] | 18.84 |  |  |  |  | 1.00
1991 |  |  |  | 6479.06 |  |  | 7368 |  |  |  | 890 | [10 empty] | 82.72 |  |  |  | 84.01 | [5 empty] | 83.10 |  |  | 84.11 |  |  |  | 2.67 |  | 2.30 | [8 empty] | 13.68 |  |  |  |  | 1.30
1992 |  |  |  | 6038.78 |  |  | 6826 |  |  |  | 890 | [10 empty] | 76.16 |  |  |  | 76.75 | [5 empty] | 77.24 |  |  | 77.71 |  |  |  | 1.02 |  | 0.79 | [8 empty] | 22.47 |  |  |  |  | 0.58
1993 |  |  |  | 6258.75 |  |  | 6930 |  |  |  | 890 | [10 empty] | 78.48 |  |  |  | 78.48 | [5 empty] | 80.28 |  |  | 79.11 |  |  |  | 5.43 |  | 4.50 | [8 empty] | 17.01 |  |  |  |  | 0.00
1994 |  |  |  | 6322.62 |  |  | 7098 |  |  |  | 890 | [10 empty] | 79.62 |  |  |  | 79.75 | [5 empty] | 81.10 |  |  | 81.03 |  |  |  | 3.76 |  | 3.11 | [8 empty] | 17.14 |  |  |  |  | 0.13
1995 |  |  |  | 6741.14 |  |  | 7495 |  |  |  | 890 | [10 empty] | 84.36 |  |  |  | 84.51 | [5 empty] | 86.46 |  |  | 85.56 |  |  |  | 0.67 |  | 0.57 | [8 empty] | 14.92 |  |  |  |  | 0.14
1996 |  |  |  | 7537.00 |  |  | 8329 |  |  |  | 890 | [10 empty] | 93.79 |  |  |  | 95.81 | [5 empty] | 96.41 |  |  | 94.82 |  |  |  | 3.80 |  | 3.79 | [8 empty] | 0.41 |  |  |  |  | 2.02
1997 |  |  |  | 5949.22 |  |  | 6752 |  |  |  | 890 | [10 empty] | 74.35 |  |  |  | 74.80 | [5 empty] | 76.31 |  |  | 77.08 |  |  |  | 11.04 |  | 9.28 | [8 empty] | 15.92 |  |  |  |  | 0.45
1998 |  |  |  | 5514.47 |  |  | 6101 |  |  |  | 890 | [10 empty] | 69.16 |  |  |  | 69.16 | [5 empty] | 70.73 |  |  | 69.65 |  |  |  | 20.87 |  | 18.23 | [8 empty] | 12.61 |  |  |  |  | 0.00
1999 |  |  |  | 7392.65 |  |  | 8328 |  |  |  | 890 | [10 empty] | 92.61 |  |  |  | 96.34 | [5 empty] | 94.82 |  |  | 95.07 |  |  |  | 1.56 |  | 1.53 | [8 empty] | 2.13 |  |  |  |  | 3.73
2000 |  |  |  | 6729.03 |  |  | 7502 |  |  |  | 890 | [10 empty] | 84.33 |  |  |  | 84.59 | [5 empty] | 86.07 |  |  | 85.41 |  |  |  | 0.69 |  | 0.59 | [8 empty] | 14.82 |  |  |  |  | 0.26
2001 |  |  |  | 5333.31 |  |  | 6046 |  |  |  | 890 | [10 empty] | 67.57 |  |  |  | 86.08 | [5 empty] | 68.41 |  |  | 69.02 |  |  |  | 2.66 |  | 2.35 | [8 empty] | 11.56 |  |  |  |  | 18.52
2002 |  |  |  | 7800.80 |  |  | 8726 |  |  |  | 890 | [10 empty] | 98.70 |  |  |  | 98.85 | [5 empty] | 100.06 |  |  | 99.61 |  |  |  | 0.24 |  | 0.24 | [8 empty] | 0.91 |  |  |  |  | 0.15
2003 |  |  |  | 6751.01 |  |  | 7579 |  |  |  | 890 | [10 empty] | 86.23 |  |  |  | 87.35 | [5 empty] | 86.59 |  |  | 86.52 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 12.62 |  |  |  |  | 1.11
2004 |  |  |  | 6793.74 |  |  | 7742 |  |  |  | 890 | [10 empty] | 86.79 |  |  |  | 87.41 | [5 empty] | 86.90 |  |  | 88.14 |  |  |  | 0.17 |  | 0.83 | [8 empty] | 11.76 |  |  |  |  | 0.62
2005 |  |  |  | 7701.72 |  |  | 8693 |  |  |  | 890 | [10 empty] | 97.97 |  |  |  | 98.09 | [5 empty] | 98.79 |  |  | 99.24 |  |  |  | 1.88 |  | 1.88 | [8 empty] | 0.04 |  |  |  |  | 0.11
2006 |  |  |  | 6763.25 |  |  | 7599 |  |  |  | 890 | [10 empty] | 85.78 |  |  |  | 85.78 | [5 empty] | 86.75 |  |  | 86.75 |  |  |  | 1.31 |  | 1.14 | [8 empty] | 13.08 |  |  |  |  | 0.00
2007 |  |  |  | 7168.16 |  |  | 8001 |  |  |  | 890 | [10 empty] | 90.81 |  |  |  | 90.86 | [5 empty] | 91.94 |  |  | 91.34 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 9.06 |  |  |  |  | 0.06
2008 |  |  |  | 7904.88 |  |  | 8784 |  |  |  | 900 | [10 empty] | 99.96 |  |  |  | 99.96 | [5 empty] | 99.99 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  |  |  | 0.00
2009 |  |  |  | 7205.22 |  |  | 7959 |  |  |  | 918 | [10 empty] | 90.31 |  |  |  | 90.52 | [5 empty] | 90.33 |  |  | 90.86 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 9.41 |  |  |  |  | 0.21
2010 |  |  |  | 7272.45 |  |  | 8009 |  |  |  | 919 | [10 empty] | 90.73 |  |  |  | 90.73 | [5 empty] | 90.34 |  |  | 91.43 |  |  |  | 0.47 |  | 0.43 | [8 empty] | 8.84 |  |  |  |  | 0.00
2011 |  |  |  | 8022.09 |  |  | 8760 |  |  |  | 918 | [10 empty] | 99.87 |  |  |  | 99.91 | [5 empty] | 99.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.09 |  |  |  |  | 0.03
2012 |  |  |  | 6994.76 |  |  | 7620 |  |  |  | 928 | [10 empty] | 86.02 |  |  |  | 86.24 | [5 empty] | 86.27 |  |  | 86.75 |  |  |  | 0.88 |  | 2.53 | [8 empty] | 11.23 |  |  |  |  | 0.22
2013 |  |  |  | 7011.65 |  |  | 7615 |  |  |  | 926 | [10 empty] | 86.11 |  |  |  | 86.62 | [5 empty] | 86.44 |  |  | 86.93 |  |  |  | 0.98 |  | 0.86 | [8 empty] | 12.53 |  |  |  |  | 0.51
2014 |  |  |  | 7913.59 |  |  | 8517 |  |  |  | 926 | [10 empty] | 96.64 |  |  |  | 96.65 | [5 empty] | 97.56 |  |  | 97.23 |  |  |  | 0.56 |  | 0.65 | [8 empty] | 2.71 |  |  |  |  | 0.01
2015 |  |  |  | 7492.71 |  |  | 8035 |  |  |  | 936 | [10 empty] | 91.27 |  |  |  | 91.27 | [5 empty] | 91.38 |  |  | 91.72 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.72 |  |  |  |  | 0.00
2016 |  |  |  | 7228.08 |  |  | 7799 |  |  |  | 936 | [10 empty] | 87.79 |  |  |  | 88.92 | [5 empty] | 87.91 |  |  | 88.79 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 11.06 |  |  |  |  | 1.13
2017 |  |  |  | 8136.28 |  |  | 8682 |  |  |  | 936 | [10 empty] | 98.85 |  |  |  | 98.85 | [5 empty] | 99.23 |  |  | 99.11 |  |  |  | 0.74 |  | 0.73 | [8 empty] | 0.42 |  |  |  |  | 0.00
2018 |  |  |  | 7201.98 |  |  | 7681 |  |  |  | 936 | [10 empty] | 87.27 |  |  |  | 87.27 | [5 empty] | 87.84 |  |  | 87.68 |  |  |  | 0.52 |  | 0.45 | [8 empty] | 12.28 |  |  |  |  | 0.00
2019 |  |  |  | 7118.57 |  |  | 7652 |  |  |  | 936 | [10 empty] | 86.50 |  |  |  | 86.61 | [5 empty] | 86.82 |  |  | 87.35 |  |  |  | 1.75 |  | 1.54 | [8 empty] | 11.84 |  |  |  |  | 0.12
2020 |  |  |  | 8222.12 |  |  | 8728 |  |  |  | 936 | [10 empty] | 99.19 |  |  |  | 99.19 | [5 empty] | 100.00 |  |  | 99.36 |  |  |  | 0.74 |  | 0.74 | [8 empty] | 0.07 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 197
B. |  | Refuelling without maintenance | [35 empty] | 24
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 761
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 16
E. |  | Testing of plant systems or components | [35 empty] | 5
H. |  | Nuclear regulatory requirements | [39 empty] | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 52
L. |  | Human factor related | [39 empty] | 6
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 5
Z. |  | Other | [51 empty] | 6
Subtotal | [37 empty] | 806 |  |  |  | 203 | [11 empty] | 63
Total | [22 empty] | 0 | [14 empty] | 1072
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 66
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 17
16. |  |  | Steam generation systems | [34 empty] | 17
31. |  |  | Turbine and auxiliaries | [34 empty] | 13
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 53
42. |  |  | Electrical Power Supply Systems | [34 empty] | 30
Total | [37 empty] | 210
Highlights (2020)
2020-09-12 Unit shutdown forRepaired condensate AD-P011 Pump and AD-P010 motor.

## MAANSHAN-2
2020 Operating Experience
TW-6 | [8 empty] | MAANSHAN-2 | [26 empty] | TAIWAN, CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TPC (Taiwan Power Co.)
Owner | [7 empty] | : | TPC (Taiwan Power Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (WE 312) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-02-21
Thermal power | [12 empty] | : |  |  | 2822 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-02-25
Gross electrical power | [12 empty] | : |  |  | 951 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-05-18
Reference unit power (net) | [12 empty] | : |  |  | 938 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.22
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 3
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.56
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.75 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7156.32 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.34 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.34 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.65 %
Load Factor (LF) | [18 empty] | : | 86.85 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 86.7 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1168 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 700.54 | 654.95 |  |  |  | 699.97 |  | 133.42 | [8 empty] | 119.64 |  |  | 679.23 | [6 empty] | 699.76 |  | 701.10 |  |  |  | 677.38 |  |  | 703.01 |  |  | 681.48 | [9 empty] | 705.84 |  |  | 7156.32
EAF [%] |  |  |  |  | 99.94 | 99.91 |  |  |  | 99.93 |  | 19.69 | [8 empty] | 17.06 |  |  | 99.95 | [6 empty] | 99.95 |  | 99.95 |  |  |  | 99.86 |  |  | 99.96 |  |  | 99.96 | [9 empty] | 100.00 |  |  | 86.34
UCF [%] |  |  |  |  | 99.94 | 99.91 |  |  |  | 99.93 |  | 19.69 | [8 empty] | 17.06 |  |  | 99.95 | [6 empty] | 99.95 |  | 99.95 |  |  |  | 99.86 |  |  | 99.96 |  |  | 99.96 | [9 empty] | 100.00 |  |  | 86.34
LF [%] |  |  |  |  | 100.38 | 100.32 |  |  |  | 100.30 |  | 19.76 | [8 empty] | 17.14 |  |  | 100.57 | [6 empty] | 100.27 |  | 100.46 |  |  |  | 100.30 |  |  | 100.74 |  |  | 100.91 | [9 empty] | 101.14 |  |  | 86.85
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 20.28 | [8 empty] | 20.16 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.70
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.05 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.05 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.06 | 0.09 |  |  |  | 0.07 |  | 80.31 | [8 empty] | 82.94 |  |  | 0.05 | [6 empty] | 0.05 |  | 0.05 |  |  |  | 0.08 |  |  | 0.04 |  |  | 0.04 | [9 empty] | 0.00 |  |  | 13.65
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 241092.37 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.14 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.19 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.45 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.41 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.14 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.46 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.22 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.07 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | Data not provided
1986 |  |  |  | "
1987 |  |  |  | "
1988 |  |  |  | "
1989 |  |  |  | 5283.33 |  |  | 6434 |  |  |  | 890 | [10 empty] | 58.14 |  |  |  | 58.84 | [5 empty] | 67.77 |  |  | 73.45 |  |  |  | 17.86 |  | 12.79 | [8 empty] | 28.37 |  |  |  |  | 0.70
1990 |  |  |  | 6141.34 |  |  | 7143 |  |  |  | 896 | [10 empty] | 77.26 |  |  |  | 78.82 | [5 empty] | 78.24 |  |  | 81.54 |  |  |  | 3.72 |  | 3.05 | [8 empty] | 18.13 |  |  |  |  | 1.56
1991 |  |  |  | 6187.13 |  |  | 7155 |  |  |  | 890 | [10 empty] | 78.61 |  |  |  | 80.42 | [5 empty] | 79.36 |  |  | 81.68 |  |  |  | 2.75 |  | 2.28 | [8 empty] | 17.30 |  |  |  |  | 1.82
1992 |  |  |  | 5956.55 |  |  | 7541 |  |  |  | 890 | [10 empty] | 75.50 |  |  |  | 84.28 | [5 empty] | 76.19 |  |  | 85.85 |  |  |  | 0.35 |  | 0.29 | [8 empty] | 15.43 |  |  |  |  | 8.78
1993 |  |  |  | 6550.99 |  |  | 7442 |  |  |  | 890 | [10 empty] | 84.08 |  |  |  | 84.08 | [5 empty] | 84.03 |  |  | 84.95 |  |  |  | 1.93 |  | 1.66 | [8 empty] | 14.26 |  |  |  |  | 0.01
1994 |  |  |  | 7006.49 |  |  | 8216 |  |  |  | 890 | [10 empty] | 88.69 |  |  |  | 93.29 | [5 empty] | 89.87 |  |  | 93.79 |  |  |  | 2.78 |  | 2.67 | [8 empty] | 4.04 |  |  |  |  | 4.60
1995 |  |  |  | 6118.58 |  |  | 6947 |  |  |  | 890 | [10 empty] | 77.09 |  |  |  | 77.14 | [5 empty] | 78.48 |  |  | 79.30 |  |  |  | 3.77 |  | 3.02 | [8 empty] | 19.84 |  |  |  |  | 0.05
1996 |  |  |  | 6349.81 |  |  | 7091 |  |  |  | 890 | [10 empty] | 79.75 |  |  |  | 80.99 | [5 empty] | 81.22 |  |  | 80.73 |  |  |  | 5.79 |  | 4.98 | [8 empty] | 14.03 |  |  |  |  | 1.24
1997 |  |  |  | 6415.41 |  |  | 7153 |  |  |  | 890 | [10 empty] | 81.14 |  |  |  | 81.56 | [5 empty] | 82.29 |  |  | 81.66 |  |  |  | 4.22 |  | 3.60 | [8 empty] | 14.84 |  |  |  |  | 0.42
1998 |  |  |  | 7781.11 |  |  | 8557 |  |  |  | 890 | [10 empty] | 97.23 |  |  |  | 97.39 | [5 empty] | 99.80 |  |  | 97.68 |  |  |  | 1.53 |  | 1.51 | [8 empty] | 1.09 |  |  |  |  | 0.17
1999 |  |  |  | 6628.36 |  |  | 7427 |  |  |  | 890 | [10 empty] | 82.72 |  |  |  | 85.28 | [5 empty] | 85.02 |  |  | 84.78 |  |  |  | 1.07 |  | 0.92 | [8 empty] | 13.79 |  |  |  |  | 2.57
2000 |  |  |  | 6618.56 |  |  | 7401 |  |  |  | 890 | [10 empty] | 82.59 |  |  |  | 84.10 | [5 empty] | 84.66 |  |  | 84.26 |  |  |  | 1.54 |  | 1.32 | [8 empty] | 14.58 |  |  |  |  | 1.51
2001 |  |  |  | 6993.79 |  |  | 7729 |  |  |  | 890 | [10 empty] | 87.34 |  |  |  | 99.36 | [5 empty] | 89.71 |  |  | 88.23 |  |  |  | 0.61 |  | 0.61 | [8 empty] | 0.02 |  |  |  |  | 12.02
2002 |  |  |  | 6639.81 |  |  | 7507 |  |  |  | 890 | [10 empty] | 82.42 |  |  |  | 82.42 | [5 empty] | 85.17 |  |  | 85.70 |  |  |  | 3.83 |  | 3.28 | [8 empty] | 14.30 |  |  |  |  | 0.00
2003 |  |  |  | 6737.60 |  |  | 7549 |  |  |  | 890 | [10 empty] | 85.15 |  |  |  | 86.59 | [5 empty] | 86.42 |  |  | 86.18 |  |  |  | 2.29 |  | 2.03 | [8 empty] | 11.38 |  |  |  |  | 1.44
2004 |  |  |  | 7882.97 |  |  | 8784 |  |  |  | 890 | [10 empty] | 99.51 |  |  |  | 99.55 | [5 empty] | 100.83 |  |  | 100.00 |  |  |  | 0.40 |  | 0.40 | [8 empty] | 0.05 |  |  |  |  | 0.03
2005 |  |  |  | 6709.97 |  |  | 7656 |  |  |  | 890 | [10 empty] | 85.07 |  |  |  | 85.47 | [5 empty] | 86.06 |  |  | 87.40 |  |  |  | 4.44 |  | 3.97 | [8 empty] | 10.56 |  |  |  |  | 0.40
2006 |  |  |  | 6928.78 |  |  | 7729 |  |  |  | 890 | [10 empty] | 87.23 |  |  |  | 87.69 | [5 empty] | 88.87 |  |  | 88.23 |  |  |  | 0.47 |  | 0.41 | [8 empty] | 11.90 |  |  |  |  | 0.46
2007 |  |  |  | 7829.87 |  |  | 8631 |  |  |  | 890 | [10 empty] | 98.32 |  |  |  | 98.32 | [5 empty] | 100.43 |  |  | 98.53 |  |  |  | 1.61 |  | 1.61 | [8 empty] | 0.07 |  |  |  |  | 0.00
2008 |  |  |  | 7280.02 |  |  | 8036 |  |  |  | 908 | [10 empty] | 91.25 |  |  |  | 91.25 | [5 empty] | 91.28 |  |  | 91.48 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.73 |  |  |  |  | 0.00
2009 |  |  |  | 7389.24 |  |  | 8074 |  |  |  | 921 | [10 empty] | 91.55 |  |  |  | 91.78 | [5 empty] | 91.59 |  |  | 92.17 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 8.19 |  |  |  |  | 0.23
2010 |  |  |  | 8056.90 |  |  | 8760 |  |  |  | 922 | [10 empty] | 99.81 |  |  |  | 99.81 | [5 empty] | 99.75 |  |  | 100.00 |  |  |  | 0.12 |  | 0.12 | [8 empty] | 0.08 |  |  |  |  | 0.00
2011 |  |  |  | 6901.46 |  |  | 7581 |  |  |  | 922 | [10 empty] | 85.49 |  |  |  | 85.49 | [5 empty] | 85.45 |  |  | 86.54 |  |  |  | 5.00 |  | 4.50 | [8 empty] | 10.01 |  |  |  |  | 0.00
2012 |  |  |  | 7185.04 |  |  | 7851 |  |  |  | 922 | [10 empty] | 88.67 |  |  |  | 89.10 | [5 empty] | 88.72 |  |  | 89.38 |  |  |  | 0.00 |  | 1.31 | [8 empty] | 9.59 |  |  |  |  | 0.43
2013 |  |  |  | 8167.87 |  |  | 8728 |  |  |  | 928 | [10 empty] | 99.38 |  |  |  | 99.86 | [5 empty] | 100.47 |  |  | 99.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.14 |  |  |  |  | 0.48
2014 |  |  |  | 6708.52 |  |  | 7198 |  |  |  | 928 | [10 empty] | 81.42 |  |  |  | 81.43 | [5 empty] | 82.52 |  |  | 82.17 |  |  |  | 0.69 |  | 0.57 | [8 empty] | 18.01 |  |  |  |  | 0.01
2015 |  |  |  | 6637.10 |  |  | 7048 |  |  |  | 938 | [10 empty] | 80.35 |  |  |  | 80.35 | [5 empty] | 80.77 |  |  | 80.46 |  |  |  | 5.93 |  | 11.85 | [8 empty] | 7.80 |  |  |  |  | 0.00
2016 |  |  |  | 7944.16 |  |  | 8472 |  |  |  | 938 | [10 empty] | 95.89 |  |  |  | 96.40 | [5 empty] | 96.42 |  |  | 96.45 |  |  |  | 0.32 |  | 1.11 | [8 empty] | 2.49 |  |  |  |  | 0.51
2017 |  |  |  | 6564.98 |  |  | 7021 |  |  |  | 938 | [10 empty] | 79.64 |  |  |  | 79.64 | [5 empty] | 79.90 |  |  | 80.15 |  |  |  | 0.85 |  | 8.54 | [8 empty] | 11.82 |  |  |  |  | 0.00
2018 |  |  |  | 7556.50 |  |  | 8065 |  |  |  | 938 | [10 empty] | 91.78 |  |  |  | 91.97 | [5 empty] | 91.96 |  |  | 92.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.03 |  |  |  |  | 0.19
2019 |  |  |  | 7998.06 |  |  | 8507 |  |  |  | 938 | [10 empty] | 96.81 |  |  |  | 96.81 | [5 empty] | 97.34 |  |  | 97.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.19 |  |  |  |  | 0.00
2020 |  |  |  | 7156.32 |  |  | 7616 |  |  |  | 938 | [10 empty] | 86.34 |  |  |  | 86.34 | [5 empty] | 86.85 |  |  | 86.70 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 13.65 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 162
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1167 | [14 empty] | 839 |  |  |  | 2
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 9
E. |  | Testing of plant systems or components | [35 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 32
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 8
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 1167 | [14 empty] | 849 |  |  |  | 166 | [11 empty] | 40
Total | [22 empty] | 1167 | [14 empty] | 1055
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 21
12. |  |  | Reactor I&C Systems | [34 empty] | 32
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 25
16. |  |  | Steam generation systems | [34 empty] | 6
31. |  |  | Turbine and auxiliaries | [34 empty] | 14
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 26
42. |  |  | Electrical Power Supply Systems | [34 empty] | 63
Total | [37 empty] | 199
Highlights (2020)
2020/04/07 02:23 Unit off-line for EOC-25