## DUNGENESS B-1
2020 Operating Experience
GB-18A | [8 empty] | DUNGENESS B-1 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | APC (ATOMIC POWER CONSTRUCTION, LTD.)
Turbine Supplier | [7 empty] | : | PARSONS (C.A.PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1965-10-01
Thermal power | [12 empty] | : |  |  | 1500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-04-03
Gross electrical power | [12 empty] | : |  |  | 615 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-04-01
Reference unit power (net) | [12 empty] | : |  |  | 545 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 3.43
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 673
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 4 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 9.4 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 16.3
| Active core height/length [m] | [13 empty] | : |  |  | 7.3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 11
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2856 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 36 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | -92.66 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 100 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | -1.94 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | -8.58 | -7.29 |  |  |  | -7.79 |  | -6.60 | [8 empty] | -7.62 |  |  | -8.01 | [6 empty] | -7.67 |  | -7.36 |  |  |  | -6.36 |  |  | -6.78 |  |  | -6.90 | [9 empty] | -11.69 |  |  | -92.66
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | -2.12 | -1.92 |  |  |  | -1.92 |  | -1.68 | [8 empty] | -1.88 |  |  | -2.04 | [6 empty] | -1.89 |  | -1.81 |  |  |  | -1.62 |  |  | -1.67 |  |  | -1.76 | [9 empty] | -2.88 |  |  | -1.94
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 94531.43 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 27.32 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 43.51 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 30.14 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 44.74 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 25.13 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 42.62 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.23 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 52.04 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 2438.25 |  |  | 6117 |  |  |  | 450 | [10 empty] | 62.84 |  |  |  | 64.81 | [5 empty] | 61.93 |  |  | 67.80 |  |  |  | 23.37 |  | 19.77 | [8 empty] | 15.42 |  |  |  |  | 1.97
1986 |  |  |  | 1172.56 |  |  | 4447 |  |  |  | 450 | [10 empty] | 29.07 |  |  |  | 33.65 | [5 empty] | 29.83 |  |  | 50.90 |  |  |  | 38.13 |  | 20.74 | [8 empty] | 45.61 |  |  |  |  | 4.58
1987 |  |  |  | 210.32 |  |  | 1179 |  |  |  | 450 | [10 empty] | 6.47 |  |  |  | 13.24 | [5 empty] | 5.25 |  |  | 13.24 |  |  |  | 41.87 |  | 9.54 | [8 empty] | 77.22 |  |  |  |  | 6.77
1988 |  |  |  | 1233.94 |  |  | 3857 |  |  |  | 450 | [10 empty] | 33.33 |  |  |  | 45.49 | [5 empty] | 31.39 |  |  | 44.15 |  |  |  | 6.80 |  | 3.32 | [8 empty] | 51.19 |  |  |  |  | 12.16
1989 |  |  |  | 647.20 |  |  | 2650 |  |  |  | 412 | [10 empty] | 24.78 |  |  |  | 43.75 | [5 empty] | 17.99 |  |  | 30.33 |  |  |  | 0.37 |  | 0.16 | [8 empty] | 56.09 |  |  |  |  | 18.97
1990 |  |  |  | 757.96 |  |  | 5093 |  |  |  | 360 | [10 empty] | 26.32 |  |  |  | 26.32 | [5 empty] | 24.10 |  |  | 58.30 |  |  |  | 10.34 |  | 3.04 | [8 empty] | 70.64 |  |  |  |  | 0.00
1991 |  |  |  | 2656.18 |  |  | 7329 |  |  |  | 410 | [10 empty] | 74.54 |  |  |  | 74.54 | [5 empty] | 74.02 |  |  | 83.89 |  |  |  | 7.06 |  | 5.66 | [8 empty] | 19.80 |  |  |  |  | 0.00
1992 |  |  |  | 1052.26 |  |  | 2670 |  |  |  | 441 | [10 empty] | 27.43 |  |  |  | 27.54 | [5 empty] | 26.69 |  |  | 29.99 |  |  |  | 54.87 |  | 33.49 | [8 empty] | 38.97 |  |  |  |  | 0.11
1993 |  |  |  | 3493.16 |  |  | 7138 |  |  |  | 516 | [10 empty] | 77.05 |  |  |  | 77.45 | [5 empty] | 77.45 |  |  | 81.71 |  |  |  | 6.43 |  | 5.32 | [8 empty] | 17.23 |  |  |  |  | 0.40
1994 |  |  |  | 2385.68 |  |  | 4676 |  |  |  | 555 | [10 empty] | 49.24 |  |  |  | 51.48 | [5 empty] | 49.20 |  |  | 53.53 |  |  |  | 28.25 |  | 20.27 | [8 empty] | 28.24 |  |  |  |  | 2.25
1995 |  |  |  | 873.72 |  |  | 1587 |  |  |  | 555 | [10 empty] | 18.20 |  |  |  | 18.20 | [5 empty] | 17.92 |  |  | 18.07 |  |  |  | 78.90 |  | 68.03 | [8 empty] | 13.78 |  |  |  |  | 0.00
1996 |  |  |  | 2516.97 |  |  | 5311 |  |  |  | 555 | [10 empty] | 51.63 |  |  |  | 51.63 | [5 empty] | 51.63 |  |  | 60.46 |  |  |  | 20.19 |  | 13.06 | [8 empty] | 35.31 |  |  |  |  | 0.00
1997 |  |  |  | 2078.19 |  |  | 4549 |  |  |  | 555 | [10 empty] | 42.90 |  |  |  | 42.90 | [5 empty] | 42.63 |  |  | 51.79 |  |  |  | 41.77 |  | 30.78 | [8 empty] | 26.32 |  |  |  |  | 0.00
1998 |  |  |  | 2198.30 |  |  | 5716 |  |  |  | 555 | [10 empty] | 47.03 |  |  |  | 47.42 | [5 empty] | 45.09 |  |  | 65.07 |  |  |  | 37.44 |  | 28.38 | [8 empty] | 24.20 |  |  |  |  | 0.39
1999 |  |  |  | 1584.20 |  |  | 4752 |  |  |  | 555 | [10 empty] | 33.04 |  |  |  | 33.04 | [5 empty] | 32.50 |  |  | 54.10 |  |  |  | 42.29 |  | 24.21 | [8 empty] | 42.74 |  |  |  |  | 0.00
2000 |  |  |  | 409.64 |  |  | 1201 |  |  |  | 555 | [10 empty] | 8.40 |  |  |  | 8.40 | [5 empty] | 8.40 |  |  | 13.67 |  |  |  | 85.65 |  | 50.16 | [8 empty] | 41.44 |  |  |  |  | 0.00
2001 |  |  |  | 3049.09 |  |  | 7108 |  |  |  | 555 | [10 empty] | 61.88 |  |  |  | 62.20 | [5 empty] | 62.54 |  |  | 80.92 |  |  |  | 30.49 |  | 27.29 | [8 empty] | 10.52 |  |  |  |  | 0.31
2002 |  |  |  | 2167.58 |  |  | 5043 |  |  |  | 555 | [10 empty] | 45.52 |  |  |  | 45.57 | [5 empty] | 44.58 |  |  | 57.57 |  |  |  | 45.59 |  | 41.46 | [8 empty] | 12.97 |  |  |  |  | 0.05
2003 |  |  |  | 2482.86 |  |  | 5212 |  |  |  | 555 | [10 empty] | 51.92 |  |  |  | 54.62 | [5 empty] | 51.07 |  |  | 59.50 |  |  |  | 26.22 |  | 23.25 | [8 empty] | 22.14 |  |  |  |  | 2.70
2004 |  |  |  | 3082.47 |  |  | 6305 |  |  |  | 555 | [10 empty] | 63.83 |  |  |  | 63.83 | [5 empty] | 63.23 |  |  | 71.78 |  |  |  | 25.75 |  | 23.71 | [8 empty] | 12.46 |  |  |  |  | 0.00
2005 |  |  |  | 2955.14 |  |  | 6039 |  |  |  | 555 | [10 empty] | 61.59 |  |  |  | 61.67 | [5 empty] | 60.78 |  |  | 68.94 |  |  |  | 15.96 |  | 18.41 | [8 empty] | 19.92 |  |  |  |  | 0.08
2006 |  |  |  | 2453.84 |  |  | 5246 |  |  |  | 555 | [10 empty] | 51.64 |  |  |  | 51.67 | [5 empty] | 51.17 |  |  | 59.89 |  |  |  | 12.01 |  | 20.37 | [8 empty] | 27.96 |  |  |  |  | 0.03
2007 |  |  |  | 2981.31 |  |  | 6447 |  |  |  | 545 | [10 empty] | 63.30 |  |  |  | 63.30 | [5 empty] | 62.45 |  |  | 73.60 |  |  |  | 10.44 |  | 9.31 | [8 empty] | 27.39 |  |  |  |  | 0.00
2008 |  |  |  | 1999.90 |  |  | 4467 |  |  |  | 520 | [10 empty] | 43.67 |  |  |  | 43.67 | [5 empty] | 43.27 |  |  | 50.85 |  |  |  | 7.34 |  | 31.38 | [8 empty] | 24.94 |  |  |  |  | 0.00
2009 |  |  |  | 1627.03 |  |  | 3527 |  |  |  | 520 | [10 empty] | 35.99 |  |  |  | 35.99 | [5 empty] | 35.72 |  |  | 40.26 |  |  |  | 17.14 |  | 35.58 | [8 empty] | 28.42 |  |  |  |  | 0.00
2010 |  |  |  | 948.94 |  |  | 3233 |  |  |  | 520 | [10 empty] | 20.83 |  |  |  | 20.83 | [5 empty] | 20.83 |  |  | 36.91 |  |  |  | 42.34 |  | 79.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 655.60 |  |  | 2517 |  |  |  | 520 | [10 empty] | 16.14 |  |  |  | 16.14 | [5 empty] | 14.39 |  |  | 28.73 |  |  |  | 57.52 |  | 63.16 | [8 empty] | 20.70 |  |  |  |  | 0.00
2012 |  |  |  | 1979.08 |  |  | 4632 |  |  |  | 520 | [10 empty] | 44.40 |  |  |  | 44.40 | [5 empty] | 43.33 |  |  | 52.73 |  |  |  | 31.16 |  | 34.09 | [8 empty] | 21.51 |  |  |  |  | 0.00
2013 |  |  |  | 2891.06 |  |  | 6215 |  |  |  | 520 | [10 empty] | 69.52 |  |  |  | 69.52 | [5 empty] | 63.47 |  |  | 70.95 |  |  |  | 9.46 |  | 22.82 | [8 empty] | 7.66 |  |  |  |  | 0.00
2014 |  |  |  | 1641.91 |  |  | 4409 |  |  |  | 520 | [10 empty] | 37.41 |  |  |  | 37.41 | [5 empty] | 36.04 |  |  | 50.33 |  |  |  | 39.57 |  | 31.95 | [8 empty] | 30.65 |  |  |  |  | 0.00
2015 |  |  |  | 3870.67 |  |  | 7679 |  |  |  | 525 | [10 empty] | 83.44 |  |  |  | 83.46 | [5 empty] | 84.16 |  |  | 87.66 |  |  |  | 4.58 |  | 4.56 | [8 empty] | 11.98 |  |  |  |  | 0.01
2016 |  |  |  | 3959.17 |  |  | 7786 |  |  |  | 525 | [10 empty] | 84.69 |  |  |  | 84.88 | [5 empty] | 85.85 |  |  | 88.64 |  |  |  | 3.52 |  | 4.59 | [8 empty] | 10.54 |  |  |  |  | 0.19
2017 |  |  |  | 2356.85 |  |  | 5050 |  |  |  | 525 | [10 empty] | 51.54 |  |  |  | 51.54 | [5 empty] | 51.25 |  |  | 57.65 |  |  |  | 19.25 |  | 20.27 | [8 empty] | 28.19 |  |  |  |  | 0.00
2018 |  |  |  | 2902.74 |  |  | 5677 |  |  |  | 545 | [10 empty] | 61.51 |  |  |  | 61.59 | [5 empty] | 60.80 |  |  | 64.81 |  |  |  | 2.06 |  | 21.90 | [8 empty] | 16.51 |  |  |  |  | 0.09
2019 |  |  |  | -85.83 |  |  | 0 |  |  |  | 545 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | -1.80 |  |  | 0.00 |  |  |  | 0.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | -92.66 |  |  | 0 |  |  |  | 545 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | -1.94 |  |  | 0.00 |  |  |  | 0.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 8784 | [14 empty] | 1617
B. |  | Refuelling without maintenance | [35 empty] | 276 |  |  |  | 73
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 637 |  |  |  | 145
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 884 |  |  |  | 50
E. |  | Testing of plant systems or components | [39 empty] | 8
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 19
L. |  | Human factor related | [39 empty] | 30
P. |  | Fire | [39 empty] | 5
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 44
Z. |  | Other | [35 empty] | 65 |  |  |  | 64 | [11 empty] | 3
Subtotal | [26 empty] | 8784 | [10 empty] | 1862 |  |  |  | 2040 | [11 empty] | 22
Total | [22 empty] | 8784 | [14 empty] | 3924
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 206
12. |  |  | Reactor I&C Systems | [34 empty] | 61
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 113
16. |  |  | Steam generation systems | [34 empty] | 40
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 226
31. |  |  | Turbine and auxiliaries | [34 empty] | 65
32. |  |  | Feedwater and Main Steam System | [19 empty] | 8784 | [14 empty] | 979
33. |  |  | Circulating Water System | [34 empty] | 36
34. |  |  | Miscellaneous Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 89
42. |  |  | Electrical Power Supply Systems | [34 empty] | 34
Total | [22 empty] | 8784 | [14 empty] | 1863
Highlights (2020)
Remained on outage all year to address various safety case issues

## DUNGENESS B-2
2020 Operating Experience
GB-18B | [8 empty] | DUNGENESS B-2 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | APC (ATOMIC POWER CONSTRUCTION, LTD.)
Turbine Supplier | [7 empty] | : | PARSONS (C.A.PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1965-10-01
Thermal power | [12 empty] | : |  |  | 1500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-12-29
Gross electrical power | [12 empty] | : |  |  | 615 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-01
Reference unit power (net) | [12 empty] | : |  |  | 545 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 3.43
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 673
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 4 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 9.4 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 16.3
| Active core height/length [m] | [13 empty] | : |  |  | 7.3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 11
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2856 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 36 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | -92.66 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 100 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | -1.94 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8784 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | -8.58 | -7.29 |  |  |  | -7.79 |  | -6.60 | [8 empty] | -7.62 |  |  | -8.01 | [6 empty] | -7.67 |  | -7.36 |  |  |  | -6.36 |  |  | -6.78 |  |  | -6.90 | [9 empty] | -11.69 |  |  | -92.66
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | -2.12 | -1.92 |  |  |  | -1.92 |  | -1.68 | [8 empty] | -1.88 |  |  | -2.04 | [6 empty] | -1.89 |  | -1.81 |  |  |  | -1.62 |  |  | -1.67 |  |  | -1.76 | [9 empty] | -2.88 |  |  | -1.94
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 99543.1 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 24.98 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 48.65 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 27.5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 48.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 23.63 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 48.45 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.22 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 55.6 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 232.55 |  |  | 696 |  |  |  | 412 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 99.99 |  | 49.54 | [8 empty] | 50.45 |  |  |  |  | 0.00
1990 |  |  |  | 726.00 |  |  | 4060 |  |  |  | 360 | [10 empty] | 23.08 |  |  |  | 23.08 | [5 empty] | 23.08 |  |  | 46.47 |  |  |  | 6.67 |  | 1.65 | [8 empty] | 75.27 |  |  |  |  | 0.00
1991 |  |  |  | 1467.22 |  |  | 4295 |  |  |  | 410 | [10 empty] | 44.78 |  |  |  | 44.78 | [5 empty] | 40.89 |  |  | 49.16 |  |  |  | 15.50 |  | 8.22 | [8 empty] | 47.00 |  |  |  |  | 0.00
1992 |  |  |  | 2360.35 |  |  | 6525 |  |  |  | 441 | [10 empty] | 61.92 |  |  |  | 61.95 | [5 empty] | 59.87 |  |  | 73.28 |  |  |  | 10.44 |  | 7.23 | [8 empty] | 30.82 |  |  |  |  | 0.03
1993 |  |  |  | 2306.70 |  |  | 4672 |  |  |  | 517 | [10 empty] | 50.00 |  |  |  | 50.20 | [5 empty] | 51.02 |  |  | 53.48 |  |  |  | 5.79 |  | 3.08 | [8 empty] | 46.72 |  |  |  |  | 0.20
1994 |  |  |  | 2568.27 |  |  | 5075 |  |  |  | 555 | [10 empty] | 56.99 |  |  |  | 57.09 | [5 empty] | 52.97 |  |  | 58.09 |  |  |  | 35.26 |  | 31.10 | [8 empty] | 11.81 |  |  |  |  | 0.10
1995 |  |  |  | 773.84 |  |  | 1358 |  |  |  | 555 | [10 empty] | 16.15 |  |  |  | 16.15 | [5 empty] | 15.87 |  |  | 15.46 |  |  |  | 75.16 |  | 48.86 | [8 empty] | 34.99 |  |  |  |  | 0.00
1996 |  |  |  | 3614.97 |  |  | 6882 |  |  |  | 555 | [10 empty] | 74.11 |  |  |  | 74.15 | [5 empty] | 74.15 |  |  | 78.35 |  |  |  | 12.39 |  | 10.49 | [8 empty] | 15.36 |  |  |  |  | 0.04
1997 |  |  |  | 3327.32 |  |  | 6975 |  |  |  | 555 | [10 empty] | 68.25 |  |  |  | 68.52 | [5 empty] | 68.25 |  |  | 79.41 |  |  |  | 14.30 |  | 11.43 | [8 empty] | 20.04 |  |  |  |  | 0.27
1998 |  |  |  | 1897.84 |  |  | 4390 |  |  |  | 555 | [10 empty] | 39.20 |  |  |  | 39.20 | [5 empty] | 38.93 |  |  | 49.98 |  |  |  | 36.89 |  | 22.91 | [8 empty] | 37.88 |  |  |  |  | 0.00
1999 |  |  |  | 2123.26 |  |  | 5504 |  |  |  | 555 | [10 empty] | 30.64 |  |  |  | 30.64 | [5 empty] | 43.55 |  |  | 62.66 |  |  |  | 52.62 |  | 34.03 | [8 empty] | 35.33 |  |  |  |  | 0.00
2000 |  |  |  | 1814.27 |  |  | 3767 |  |  |  | 555 | [10 empty] | 37.21 |  |  |  | 37.21 | [5 empty] | 37.21 |  |  | 42.88 |  |  |  | 47.18 |  | 33.24 | [8 empty] | 29.55 |  |  |  |  | 0.00
2001 |  |  |  | 3007.39 |  |  | 6393 |  |  |  | 555 | [10 empty] | 61.12 |  |  |  | 62.14 | [5 empty] | 61.69 |  |  | 72.78 |  |  |  | 31.60 |  | 28.70 | [8 empty] | 9.16 |  |  |  |  | 1.02
2002 |  |  |  | 2483.27 |  |  | 5135 |  |  |  | 555 | [10 empty] | 51.81 |  |  |  | 51.81 | [5 empty] | 51.08 |  |  | 58.62 |  |  |  | 25.68 |  | 22.00 | [8 empty] | 26.19 |  |  |  |  | 0.00
2003 |  |  |  | 3747.28 |  |  | 7275 |  |  |  | 555 | [10 empty] | 76.03 |  |  |  | 78.31 | [5 empty] | 77.08 |  |  | 83.05 |  |  |  | 6.95 |  | 5.85 | [8 empty] | 15.84 |  |  |  |  | 2.28
2004 |  |  |  | 3514.42 |  |  | 7138 |  |  |  | 555 | [10 empty] | 72.64 |  |  |  | 72.64 | [5 empty] | 72.09 |  |  | 81.26 |  |  |  | 14.73 |  | 16.34 | [8 empty] | 11.02 |  |  |  |  | 0.00
2005 |  |  |  | 2739.75 |  |  | 5612 |  |  |  | 555 | [10 empty] | 57.68 |  |  |  | 57.68 | [5 empty] | 56.35 |  |  | 64.06 |  |  |  | 7.05 |  | 10.63 | [8 empty] | 31.70 |  |  |  |  | 0.00
2006 |  |  |  | 2695.72 |  |  | 5712 |  |  |  | 555 | [10 empty] | 56.89 |  |  |  | 57.91 | [5 empty] | 56.21 |  |  | 65.21 |  |  |  | 18.98 |  | 18.20 | [8 empty] | 23.89 |  |  |  |  | 1.03
2007 |  |  |  | 2875.74 |  |  | 6301 |  |  |  | 545 | [10 empty] | 60.94 |  |  |  | 60.94 | [5 empty] | 60.24 |  |  | 71.93 |  |  |  | 18.34 |  | 24.02 | [8 empty] | 15.03 |  |  |  |  | 0.00
2008 |  |  |  | 1568.90 |  |  | 3356 |  |  |  | 520 | [10 empty] | 34.38 |  |  |  | 34.38 | [5 empty] | 33.94 |  |  | 38.21 |  |  |  | 15.58 |  | 22.56 | [8 empty] | 43.07 |  |  |  |  | 0.00
2009 |  |  |  | 2385.66 |  |  | 5597 |  |  |  | 520 | [10 empty] | 52.59 |  |  |  | 52.59 | [5 empty] | 52.37 |  |  | 63.89 |  |  |  | 31.06 |  | 31.47 | [8 empty] | 15.95 |  |  |  |  | 0.00
2010 |  |  |  | 2766.05 |  |  | 6173 |  |  |  | 520 | [10 empty] | 60.18 |  |  |  | 60.18 | [5 empty] | 60.72 |  |  | 70.47 |  |  |  | 36.19 |  | 34.13 | [8 empty] | 5.69 |  |  |  |  | 0.00
2011 |  |  |  | 691.07 |  |  | 2754 |  |  |  | 520 | [10 empty] | 16.90 |  |  |  | 16.90 | [5 empty] | 15.17 |  |  | 31.44 |  |  |  | 54.50 |  | 64.27 | [8 empty] | 18.82 |  |  |  |  | 0.00
2012 |  |  |  | 2099.69 |  |  | 4420 |  |  |  | 520 | [10 empty] | 46.22 |  |  |  | 46.22 | [5 empty] | 45.97 |  |  | 50.32 |  |  |  | 10.09 |  | 25.94 | [8 empty] | 27.84 |  |  |  |  | 0.00
2013 |  |  |  | 1869.00 |  |  | 4308 |  |  |  | 520 | [10 empty] | 44.92 |  |  |  | 44.92 | [5 empty] | 41.03 |  |  | 49.18 |  |  |  | 41.10 |  | 40.30 | [8 empty] | 14.78 |  |  |  |  | 0.00
2014 |  |  |  | 2745.12 |  |  | 6153 |  |  |  | 520 | [10 empty] | 62.80 |  |  |  | 62.80 | [5 empty] | 60.26 |  |  | 70.24 |  |  |  | 25.66 |  | 24.24 | [8 empty] | 12.96 |  |  |  |  | 0.00
2015 |  |  |  | 2781.99 |  |  | 5665 |  |  |  | 525 | [10 empty] | 59.74 |  |  |  | 59.74 | [5 empty] | 60.49 |  |  | 64.67 |  |  |  | 8.89 |  | 9.87 | [8 empty] | 30.39 |  |  |  |  | 0.00
2016 |  |  |  | 3740.04 |  |  | 7407 | [14 empty] | 79.55 |  |  |  | 81.13 | [5 empty] | 81.10 |  |  | 84.32 |  |  |  | 6.29 |  | 6.07 | [8 empty] | 12.79 |  |  |  |  | 1.58
2017 |  |  |  | 3362.55 |  |  | 6554 |  |  |  | 525 | [10 empty] | 71.72 |  |  |  | 71.72 | [5 empty] | 73.11 |  |  | 74.82 |  |  |  | 15.60 |  | 15.34 | [8 empty] | 12.94 |  |  |  |  | 0.00
2018 |  |  |  | 2834.30 |  |  | 5398 |  |  |  | 545 | [10 empty] | 59.89 |  |  |  | 60.02 | [5 empty] | 59.37 |  |  | 61.62 |  |  |  | 0.00 |  | 11.17 | [8 empty] | 28.81 |  |  |  |  | 0.13
2019 |  |  |  | -85.83 |  |  | 0 |  |  |  | 545 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | -1.80 |  |  | 0.00 |  |  |  | 0.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | -92.66 |  |  | 0 |  |  |  | 545 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | -1.94 |  |  | 0.00 |  |  |  | 0.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1111
B. |  | Refuelling without maintenance | [35 empty] | 328 |  |  |  | 119
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 898 |  |  |  | 119
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 935
E. |  | Testing of plant systems or components | [39 empty] | 8
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 20
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 4
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
P. |  | Fire | [39 empty] | 71
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 38
Z. |  | Other | [35 empty] | 98 |  |  |  | 71 | [11 empty] | 8
Subtotal | [37 empty] | 2259 |  |  |  | 1545 | [11 empty] | 36
Total | [22 empty] | 0 | [14 empty] | 3840
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
12. |  |  | Reactor I&C Systems | [34 empty] | 54
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 21
16. |  |  | Steam generation systems | [34 empty] | 50
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 314
31. |  |  | Turbine and auxiliaries | [34 empty] | 44
32. |  |  | Feedwater and Main Steam System | [34 empty] | 506
33. |  |  | Circulating Water System | [34 empty] | 86
34. |  |  | Miscellaneous Systems | [34 empty] | 91
41. |  |  | Main Generator Systems | [34 empty] | 43
42. |  |  | Electrical Power Supply Systems | [34 empty] | 25
Total | [37 empty] | 1259
Highlights (2020)
Remained on outage all year to address various safety case issues

## HARTLEPOOL A-1
2020 Operating Experience
GB-19A | [8 empty] | HARTLEPOOL A-1 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | NPC (NUCLEAR POWER CO., LTD.)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-10-01
Thermal power | [12 empty] | : |  |  | 1500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-08-01
Gross electrical power | [12 empty] | : |  |  | 655 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-01
Reference unit power (net) | [12 empty] | : |  |  | 590 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.14
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 650
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 4 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 7.5 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 15.96
| Active core height/length [m] | [13 empty] | : |  |  | 8.3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2592 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 44 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | 8 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4581.72 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.36 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.58 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.17 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.96 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.87 %
Load Factor (LF) | [18 empty] | : | 88.41 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.39 %
Operating Factor (OF) | [18 empty] | : | 91.79 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 721 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 440.37 | 412.02 |  |  |  | 439.16 |  | 423.54 | [8 empty] | 387.78 |  |  | 171.79 | [6 empty] | 432.62 |  | 434.97 |  |  |  | 414.07 |  |  | 417.26 |  |  | 176.76 | [9 empty] | 431.38 |  |  | 4581.72
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.69 | [8 empty] | 88.49 |  |  | 42.13 | [6 empty] | 98.56 |  | 99.09 |  |  |  | 97.47 |  |  | 94.93 |  |  | 42.70 | [9 empty] | 98.27 |  |  | 88.58
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.95 | [8 empty] | 88.85 |  |  | 42.26 | [6 empty] | 99.03 |  | 100.00 |  |  |  | 98.66 |  |  | 96.07 |  |  | 42.70 | [9 empty] | 98.47 |  |  | 88.96
LF [%] |  |  |  |  | 100.32 | 100.34 |  |  |  | 100.18 |  | 99.70 | [8 empty] | 88.34 |  |  | 40.44 | [6 empty] | 98.56 |  | 99.09 |  |  |  | 97.47 |  |  | 94.93 |  |  | 41.61 | [9 empty] | 98.27 |  |  | 88.41
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 94.76 |  |  | 50.97 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 54.31 | [9 empty] | 100.00 |  |  | 91.79
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.97 |  | 0.00 |  |  |  | 1.34 |  |  | 3.93 |  |  | 14.73 | [9 empty] | 1.11 |  |  | 1.36
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 24.91 | [6 empty] | 0.97 |  | 0.00 |  |  |  | 1.34 |  |  | 3.93 |  |  | 18.39 | [9 empty] | 1.11 |  |  | 4.17
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.05 | [8 empty] | 11.15 |  |  | 32.84 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.01 |  |  | 0.00 |  |  | 38.92 | [9 empty] | 0.43 |  |  | 6.87
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.26 | [8 empty] | 0.35 |  |  | 0.13 | [6 empty] | 0.47 |  | 0.91 |  |  |  | 1.18 |  |  | 1.14 |  |  | 0.00 | [9 empty] | 0.19 |  |  | 0.39
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 119391.92 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 8.95 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 70.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 15.01 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 70.41 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.59 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 68.75 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.12 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.41 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 1829.47 |  |  | 4683 |  |  |  | 539 | [10 empty] | 72.77 |  |  |  | 72.77 | [5 empty] | 39.07 |  |  | 45.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.23 |  |  |  |  | 0.00
1990 |  |  |  | 1698.68 |  |  | 3486 |  |  |  | 487 | [10 empty] | 40.12 |  |  |  | 40.12 | [5 empty] | 39.89 |  |  | 39.90 |  |  |  | 18.89 |  | 9.35 | [8 empty] | 50.53 |  |  |  |  | 0.00
1991 |  |  |  | 2953.39 |  |  | 6791 |  |  |  | 625 | [10 empty] | 75.05 |  |  |  | 75.05 | [5 empty] | 54.09 |  |  | 77.74 |  |  |  | 8.77 |  | 7.21 | [8 empty] | 17.74 |  |  |  |  | 0.00
1992 |  |  |  | 2910.40 |  |  | 6156 |  |  |  | 510 | [10 empty] | 63.46 |  |  |  | 63.64 | [5 empty] | 64.09 |  |  | 69.14 |  |  |  | 10.21 |  | 7.24 | [8 empty] | 29.12 |  |  |  |  | 0.18
1993 |  |  |  | 4449.59 |  |  | 7802 |  |  |  | 582 | [10 empty] | 87.11 |  |  |  | 87.44 | [5 empty] | 87.44 |  |  | 89.31 |  |  |  | 4.07 |  | 3.71 | [8 empty] | 8.85 |  |  |  |  | 0.32
1994 |  |  |  | 4296.60 |  |  | 7716 |  |  |  | 605 | [10 empty] | 81.36 |  |  |  | 81.70 | [5 empty] | 81.29 |  |  | 88.32 |  |  |  | 7.88 |  | 6.99 | [8 empty] | 11.31 |  |  |  |  | 0.34
1995 |  |  |  | 3584.24 |  |  | 5937 |  |  |  | 605 | [10 empty] | 67.72 |  |  |  | 67.72 | [5 empty] | 67.44 |  |  | 67.59 |  |  |  | 15.59 |  | 12.51 | [8 empty] | 19.78 |  |  |  |  | 0.00
1996 |  |  |  | 4518.01 |  |  | 7691 |  |  |  | 605 | [10 empty] | 85.63 |  |  |  | 85.67 | [5 empty] | 85.02 |  |  | 87.56 |  |  |  | 1.91 |  | 1.67 | [8 empty] | 12.66 |  |  |  |  | 0.04
1997 |  |  |  | 4441.68 |  |  | 7644 |  |  |  | 605 | [10 empty] | 83.58 |  |  |  | 83.85 | [5 empty] | 83.58 |  |  | 87.02 |  |  |  | 10.14 |  | 9.46 | [8 empty] | 6.69 |  |  |  |  | 0.27
1998 |  |  |  | 3892.34 |  |  | 7108 |  |  |  | 605 | [10 empty] | 73.52 |  |  |  | 73.52 | [5 empty] | 73.24 |  |  | 80.92 |  |  |  | 10.20 |  | 8.35 | [8 empty] | 18.13 |  |  |  |  | 0.00
1999 |  |  |  | 5000.14 |  |  | 8369 |  |  |  | 605 | [10 empty] | 94.38 |  |  |  | 94.38 | [5 empty] | 94.09 |  |  | 95.28 |  |  |  | 1.57 |  | 1.50 | [8 empty] | 4.12 |  |  |  |  | 0.00
2000 |  |  |  | 4757.35 |  |  | 8153 |  |  |  | 605 | [10 empty] | 88.63 |  |  |  | 89.52 | [5 empty] | 89.52 |  |  | 92.82 |  |  |  | 2.84 |  | 2.62 | [8 empty] | 7.86 |  |  |  |  | 0.89
2001 |  |  |  | 4291.19 |  |  | 7301 |  |  |  | 605 | [10 empty] | 80.93 |  |  |  | 81.00 | [5 empty] | 80.75 |  |  | 83.12 |  |  |  | 4.86 |  | 4.14 | [8 empty] | 14.87 |  |  |  |  | 0.07
2002 |  |  |  | 4627.85 |  |  | 7965 |  |  |  | 605 | [10 empty] | 87.51 |  |  |  | 87.51 | [5 empty] | 87.32 |  |  | 90.92 |  |  |  | 4.42 |  | 4.05 | [8 empty] | 8.44 |  |  |  |  | 0.00
2003 |  |  |  | 4583.30 |  |  | 7856 |  |  |  | 605 | [10 empty] | 86.63 |  |  |  | 86.63 | [5 empty] | 86.48 |  |  | 89.68 |  |  |  | 7.09 |  | 6.61 | [8 empty] | 6.76 |  |  |  |  | 0.00
2004 |  |  |  | 1942.67 |  |  | 3385 |  |  |  | 605 | [10 empty] | 36.88 |  |  |  | 36.88 | [5 empty] | 36.56 |  |  | 38.54 |  |  |  | 0.50 |  | 35.99 | [8 empty] | 27.13 |  |  |  |  | 0.00
2005 |  |  |  | 2322.93 |  |  | 4829 |  |  |  | 605 | [10 empty] | 43.94 |  |  |  | 43.94 | [5 empty] | 43.83 |  |  | 55.13 |  |  |  | 48.91 |  | 44.39 | [8 empty] | 11.67 |  |  |  |  | 0.00
2006 |  |  |  | 2378.89 |  |  | 4291 |  |  |  | 605 | [10 empty] | 45.94 |  |  |  | 45.94 | [5 empty] | 45.45 |  |  | 48.98 |  |  |  | 35.63 |  | 46.29 | [8 empty] | 7.77 |  |  |  |  | 0.00
2007 |  |  |  | 3295.79 |  |  | 5680 |  |  |  | 595 | [10 empty] | 63.08 |  |  |  | 63.08 | [5 empty] | 63.23 |  |  | 64.84 |  |  |  | 3.17 |  | 17.69 | [8 empty] | 19.23 |  |  |  |  | 0.00
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 595 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 97.78 | [8 empty] | 2.22 |  |  |  |  | 0.00
2009 |  |  |  | 3945.95 |  |  | 6986 |  |  |  | 595 | [10 empty] | 76.04 |  |  |  | 76.04 | [5 empty] | 75.71 |  |  | 79.75 |  |  |  | 4.77 |  | 16.31 | [8 empty] | 7.65 |  |  |  |  | 0.00
2010 |  |  |  | 4407.41 |  |  | 7547 |  |  |  | 595 | [10 empty] | 84.16 |  |  |  | 84.16 | [5 empty] | 84.56 |  |  | 86.15 |  |  |  | 4.84 |  | 7.89 | [8 empty] | 7.95 |  |  |  |  | 0.00
2011 |  |  |  | 3102.64 |  |  | 5514 |  |  |  | 595 | [10 empty] | 59.86 |  |  |  | 59.86 | [5 empty] | 59.53 |  |  | 62.95 |  |  |  | 2.28 |  | 10.66 | [8 empty] | 29.48 |  |  |  |  | 0.00
2012 |  |  |  | 4301.94 |  |  | 7613 |  |  |  | 595 | [10 empty] | 82.47 |  |  |  | 82.47 | [5 empty] | 82.31 |  |  | 86.67 |  |  |  | 4.83 |  | 10.31 | [8 empty] | 7.22 |  |  |  |  | 0.00
2013 |  |  |  | 3992.35 |  |  | 7557 |  |  |  | 595 | [10 empty] | 76.93 |  |  |  | 76.93 | [5 empty] | 76.60 |  |  | 86.27 |  |  |  | 6.24 |  | 11.50 | [8 empty] | 11.57 |  |  |  |  | 0.00
2014 |  |  |  | 3158.04 |  |  | 5782 |  |  |  | 595 | [10 empty] | 60.92 |  |  |  | 60.92 | [5 empty] | 60.59 |  |  | 66.00 |  |  |  | 3.01 |  | 12.87 | [8 empty] | 26.21 |  |  |  |  | 0.00
2015 |  |  |  | 3043.14 |  |  | 6817 |  |  |  | 595 | [10 empty] | 58.76 |  |  |  | 58.76 | [5 empty] | 58.38 |  |  | 77.82 |  |  |  | 1.04 |  | 9.74 | [8 empty] | 31.50 |  |  |  |  | 0.00
2016 |  |  |  | 2787.18 |  |  | 5559 | [14 empty] | 54.36 |  |  |  | 54.78 | [5 empty] | 53.33 |  |  | 63.29 |  |  |  | 39.82 |  | 42.11 | [8 empty] | 3.11 |  |  |  |  | 0.42
2017 |  |  |  | 0.00 | [17 empty] | 89.89 |  |  |  | 90.31 | [5 empty] | 89.65 |  |  | 92.23 |  |  |  | 1.07 |  | 3.36 | [8 empty] | 6.33 |  |  |  |  | 0.42
2018 |  |  |  | 3539.00 |  |  | 6101 |  |  |  | 590 | [10 empty] | 68.66 |  |  |  | 68.72 | [5 empty] | 68.47 |  |  | 69.65 |  |  |  | 0.01 |  | 11.07 | [8 empty] | 20.21 |  |  |  |  | 0.06
2019 |  |  |  | 4340.04 |  |  | 7677 |  |  |  | 590 | [10 empty] | 84.16 |  |  |  | 84.67 | [5 empty] | 83.97 |  |  | 87.64 |  |  |  | 4.63 |  | 5.62 | [8 empty] | 9.71 |  |  |  |  | 0.51
2020 |  |  |  | 4581.72 |  |  | 8063 |  |  |  | 590 | [10 empty] | 88.58 |  |  |  | 88.96 | [5 empty] | 88.41 |  |  | 91.79 |  |  |  | 1.36 |  | 4.17 | [8 empty] | 6.87 |  |  |  |  | 0.39
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 511 | [14 empty] | 1092
B. |  | Refuelling without maintenance | [20 empty] | 551 | [14 empty] | 207 |  |  |  | 17
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 537 |  |  |  | 9
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 809
E. |  | Testing of plant systems or components | [39 empty] | 14
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 68 |  |  |  | 29
H. |  | Nuclear regulatory requirements | [39 empty] | 99
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 6
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 5
Z. |  | Other | [35 empty] | 23 |  |  |  | 57
Subtotal | [22 empty] | 551 |  |  |  | 511 | [10 empty] | 1644 |  |  |  | 1328 | [11 empty] | 6
Total | [22 empty] | 1062 | [14 empty] | 2978
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 411
12. |  |  | Reactor I&C Systems | [34 empty] | 19
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 31
15. |  |  | Reactor Cooling Systems | [34 empty] | 27
16. |  |  | Steam generation systems | [34 empty] | 230
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [19 empty] | 511 | [14 empty] | 53
31. |  |  | Turbine and auxiliaries | [34 empty] | 68
32. |  |  | Feedwater and Main Steam System | [34 empty] | 76
33. |  |  | Circulating Water System | [34 empty] | 57
41. |  |  | Main Generator Systems | [34 empty] | 111
42. |  |  | Electrical Power Supply Systems | [34 empty] | 43
Total | [22 empty] | 511 | [14 empty] | 1128

## HARTLEPOOL A-2
2020 Operating Experience
GB-19B | [8 empty] | HARTLEPOOL A-2 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | NPC (NUCLEAR POWER CO., LTD.)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-10-01
Thermal power | [12 empty] | : |  |  | 1500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-10-31
Gross electrical power | [12 empty] | : |  |  | 655 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-01
Reference unit power (net) | [12 empty] | : |  |  | 595 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.14
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 650
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 4 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 7.5 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 15.96
| Active core height/length [m] | [13 empty] | : |  |  | 8.3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2592 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 44 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | 8 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3919.4 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 7.28 %
Energy Availability Factor (EAF) | [18 empty] | : | 75.41 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 16.17 %
Unit Capability Factor (UCF) | [18 empty] | : | 75.72 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.11 %
Load Factor (LF) | [18 empty] | : | 74.99 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.31 %
Operating Factor (OF) | [18 empty] | : | 82.33 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1552 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 442.15 | 415.04 |  |  |  | 183.83 |  | 264.76 | [8 empty] | 440.82 |  |  | 421.69 | [6 empty] | 436.30 |  | 192.34 |  |  |  | 50.68 |  |  | 262.18 |  |  | 371.25 | [9 empty] | 438.37 |  |  | 3919.40
EAF [%] |  |  |  |  | 99.79 | 100.00 |  |  |  | 42.45 |  | 63.05 | [8 empty] | 99.58 |  |  | 98.43 | [6 empty] | 98.56 |  | 44.52 |  |  |  | 13.76 |  |  | 59.15 |  |  | 86.90 | [9 empty] | 99.03 |  |  | 75.41
UCF [%] |  |  |  |  | 99.79 | 100.00 |  |  |  | 42.45 |  | 63.13 | [8 empty] | 99.82 |  |  | 99.50 | [6 empty] | 99.97 |  | 44.99 |  |  |  | 13.76 |  |  | 59.15 |  |  | 87.07 | [9 empty] | 99.26 |  |  | 75.72
LF [%] |  |  |  |  | 99.88 | 100.22 |  |  |  | 41.58 |  | 61.80 | [8 empty] | 99.58 |  |  | 98.43 | [6 empty] | 98.56 |  | 43.45 |  |  |  | 11.83 |  |  | 59.15 |  |  | 86.66 | [9 empty] | 99.03 |  |  | 74.99
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 43.20 |  | 67.78 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 46.37 |  |  |  | 36.94 |  |  | 97.99 |  |  | 95.83 | [9 empty] | 100.00 |  |  | 82.33
FLR [%] |  |  |  |  | 0.18 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 1.86 |  |  |  | 55.41 |  |  | 40.85 |  |  | 12.22 | [9 empty] | 0.00 |  |  | 7.28
UCL [%] |  |  |  |  | 0.18 | 0.00 |  |  |  | 19.70 |  | 36.86 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.85 |  |  |  | 84.67 |  |  | 40.85 |  |  | 12.12 | [9 empty] | 0.00 |  |  | 16.17
PUF [%] |  |  |  |  | 0.03 | 0.00 |  |  |  | 37.85 |  | 0.01 | [8 empty] | 0.18 |  |  | 0.50 | [6 empty] | 0.03 |  | 54.16 |  |  |  | 1.57 |  |  | 0.00 |  |  | 0.81 | [9 empty] | 0.74 |  |  | 8.11
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.08 | [8 empty] | 0.25 |  |  | 1.06 | [6 empty] | 1.41 |  | 0.47 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.16 | [9 empty] | 0.24 |  |  | 0.31
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 114071.8 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 12.72 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.64 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.6 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 71.79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.61 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.16 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 75.07 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 2234.82 |  |  | 4689 |  |  |  | 421 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 80.61 |  |  | 71.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 3238.38 |  |  | 6796 |  |  |  | 487 | [10 empty] | 74.14 |  |  |  | 74.14 | [5 empty] | 76.04 |  |  | 77.79 |  |  |  | 3.08 |  | 2.36 | [8 empty] | 23.50 |  |  |  |  | 0.00
1991 |  |  |  | 1855.91 |  |  | 3755 |  |  |  | 625 | [10 empty] | 55.12 |  |  |  | 55.12 | [5 empty] | 33.99 |  |  | 42.98 |  |  |  | 0.80 |  | 0.44 | [8 empty] | 44.44 |  |  |  |  | 0.00
1992 |  |  |  | 4316.78 |  |  | 7923 |  |  |  | 571 | [10 empty] | 87.01 |  |  |  | 87.32 | [5 empty] | 84.86 |  |  | 88.98 |  |  |  | 3.53 |  | 3.20 | [8 empty] | 9.49 |  |  |  |  | 0.31
1993 |  |  |  | 4264.64 |  |  | 7682 |  |  |  | 582 | [10 empty] | 83.76 |  |  |  | 84.88 | [5 empty] | 83.81 |  |  | 87.93 |  |  |  | 5.92 |  | 5.34 | [8 empty] | 9.78 |  |  |  |  | 1.12
1994 |  |  |  | 3703.92 |  |  | 6612 |  |  |  | 605 | [10 empty] | 69.91 |  |  |  | 70.24 | [5 empty] | 70.08 |  |  | 75.69 |  |  |  | 12.80 |  | 10.31 | [8 empty] | 19.45 |  |  |  |  | 0.33
1995 |  |  |  | 3750.74 |  |  | 6149 |  |  |  | 605 | [10 empty] | 70.85 |  |  |  | 70.85 | [5 empty] | 70.58 |  |  | 70.00 |  |  |  | 19.56 |  | 17.23 | [8 empty] | 11.92 |  |  |  |  | 0.00
1996 |  |  |  | 4370.30 |  |  | 8131 |  |  |  | 605 | [10 empty] | 82.13 |  |  |  | 82.24 | [5 empty] | 82.24 |  |  | 92.57 |  |  |  | 4.95 |  | 4.28 | [8 empty] | 13.48 |  |  |  |  | 0.10
1997 |  |  |  | 4127.88 |  |  | 6954 |  |  |  | 605 | [10 empty] | 77.18 |  |  |  | 77.95 | [5 empty] | 77.67 |  |  | 79.17 |  |  |  | 4.70 |  | 3.84 | [8 empty] | 18.21 |  |  |  |  | 0.76
1998 |  |  |  | 4555.10 |  |  | 7973 |  |  |  | 605 | [10 empty] | 85.58 |  |  |  | 85.99 | [5 empty] | 85.71 |  |  | 90.77 |  |  |  | 7.89 |  | 7.37 | [8 empty] | 6.64 |  |  |  |  | 0.40
1999 |  |  |  | 4472.45 |  |  | 7808 |  |  |  | 605 | [10 empty] | 83.64 |  |  |  | 84.43 | [5 empty] | 84.16 |  |  | 88.89 |  |  |  | 8.54 |  | 7.89 | [8 empty] | 7.68 |  |  |  |  | 0.79
2000 |  |  |  | 4265.86 |  |  | 7463 |  |  |  | 605 | [10 empty] | 80.27 |  |  |  | 80.27 | [5 empty] | 80.27 |  |  | 84.96 |  |  |  | 2.23 |  | 1.83 | [8 empty] | 17.90 |  |  |  |  | 0.00
2001 |  |  |  | 4635.88 |  |  | 8092 |  |  |  | 605 | [10 empty] | 87.46 |  |  |  | 87.46 | [5 empty] | 87.23 |  |  | 92.12 |  |  |  | 1.55 |  | 1.38 | [8 empty] | 11.16 |  |  |  |  | 0.00
2002 |  |  |  | 4910.32 |  |  | 8383 |  |  |  | 605 | [10 empty] | 92.73 |  |  |  | 92.73 | [5 empty] | 92.65 |  |  | 95.70 |  |  |  | 0.24 |  | 1.22 | [8 empty] | 6.05 |  |  |  |  | 0.00
2003 |  |  |  | 3488.43 |  |  | 6258 |  |  |  | 605 | [10 empty] | 66.45 |  |  |  | 66.45 | [5 empty] | 65.82 |  |  | 71.44 |  |  |  | 16.79 |  | 15.26 | [8 empty] | 18.29 |  |  |  |  | 0.00
2004 |  |  |  | 3380.61 |  |  | 6016 |  |  |  | 605 | [10 empty] | 64.01 |  |  |  | 64.01 | [5 empty] | 63.61 |  |  | 68.49 |  |  |  | 4.29 |  | 18.18 | [8 empty] | 17.81 |  |  |  |  | 0.00
2005 |  |  |  | 3651.64 |  |  | 6428 |  |  |  | 605 | [10 empty] | 69.24 |  |  |  | 69.24 | [5 empty] | 68.90 |  |  | 73.38 |  |  |  | 5.76 |  | 18.05 | [8 empty] | 12.71 |  |  |  |  | 0.00
2006 |  |  |  | 2481.11 |  |  | 4455 |  |  |  | 605 | [10 empty] | 47.76 |  |  |  | 47.76 | [5 empty] | 47.41 |  |  | 50.86 |  |  |  | 35.15 |  | 30.49 | [8 empty] | 21.76 |  |  |  |  | 0.00
2007 |  |  |  | 3593.55 |  |  | 6514 |  |  |  | 595 | [10 empty] | 69.15 |  |  |  | 69.15 | [5 empty] | 68.95 |  |  | 74.36 |  |  |  | 22.97 |  | 20.73 | [8 empty] | 10.12 |  |  |  |  | 0.00
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 595 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 97.73 | [8 empty] | 2.27 |  |  |  |  | 0.00
2009 |  |  |  | 2882.06 |  |  | 5360 |  |  |  | 595 | [10 empty] | 55.98 |  |  |  | 55.98 | [5 empty] | 55.29 |  |  | 61.19 |  |  |  | 26.57 |  | 24.54 | [8 empty] | 19.48 |  |  |  |  | 0.00
2010 |  |  |  | 3738.08 |  |  | 6674 |  |  |  | 595 | [10 empty] | 71.70 |  |  |  | 71.70 | [5 empty] | 71.72 |  |  | 76.19 |  |  |  | 7.77 |  | 20.13 | [8 empty] | 8.17 |  |  |  |  | 0.00
2011 |  |  |  | 4251.62 |  |  | 7533 |  |  |  | 595 | [10 empty] | 81.90 |  |  |  | 81.90 | [5 empty] | 81.57 |  |  | 85.99 |  |  |  | 2.84 |  | 8.65 | [8 empty] | 9.45 |  |  |  |  | 0.00
2012 |  |  |  | 4520.16 |  |  | 7880 |  |  |  | 585 | [10 empty] | 87.66 |  |  |  | 87.66 | [5 empty] | 87.96 |  |  | 89.71 |  |  |  | 1.11 |  | 3.22 | [8 empty] | 9.11 |  |  |  |  | 0.00
2013 |  |  |  | 3014.48 |  |  | 5517 |  |  |  | 585 | [10 empty] | 59.23 |  |  |  | 59.23 | [5 empty] | 58.82 |  |  | 62.98 |  |  |  | 17.79 |  | 13.57 | [8 empty] | 27.20 |  |  |  |  | 0.00
2014 |  |  |  | 2662.28 |  |  | 5290 |  |  |  | 585 | [10 empty] | 52.88 |  |  |  | 52.88 | [5 empty] | 51.95 |  |  | 60.39 |  |  |  | 39.79 |  | 38.24 | [8 empty] | 8.88 |  |  |  |  | 0.00
2015 |  |  |  | 3124.82 |  |  | 6811 |  |  |  | 585 | [10 empty] | 61.35 |  |  |  | 61.35 | [5 empty] | 60.98 |  |  | 77.75 |  |  |  | 4.50 |  | 10.22 | [8 empty] | 28.43 |  |  |  |  | 0.00
2016 |  |  |  | 3773.67 |  |  | 6842 | [14 empty] | 73.22 |  |  |  | 73.25 | [5 empty] | 73.44 |  |  | 77.89 |  |  |  | 5.02 |  | 7.54 | [8 empty] | 19.22 |  |  |  |  | 0.03
2017 |  |  |  | 4641.82 |  |  | 7980 | [14 empty] | 89.54 |  |  |  | 89.54 | [5 empty] | 90.58 |  |  | 91.10 |  |  |  | 0.43 |  | 1.29 | [8 empty] | 9.16 |  |  |  |  | 0.00
2018 |  |  |  | 4569.78 |  |  | 7950 |  |  |  | 595 | [10 empty] | 88.02 |  |  |  | 88.52 | [5 empty] | 87.67 |  |  | 90.75 |  |  |  | 5.59 |  | 5.36 | [8 empty] | 6.13 |  |  |  |  | 0.50
2019 |  |  |  | 3259.78 |  |  | 5910 |  |  |  | 595 | [10 empty] | 63.11 |  |  |  | 63.38 | [5 empty] | 62.54 |  |  | 67.47 |  |  |  | 4.53 |  | 11.49 | [8 empty] | 25.14 |  |  |  |  | 0.27
2020 |  |  |  | 3919.40 |  |  | 7232 |  |  |  | 595 | [10 empty] | 75.41 |  |  |  | 75.72 | [5 empty] | 74.99 |  |  | 82.33 |  |  |  | 7.28 |  | 16.17 | [8 empty] | 8.11 |  |  |  |  | 0.31
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 1131 | [14 empty] | 1023
B. |  | Refuelling without maintenance | [20 empty] | 686 | [14 empty] | 184 |  |  |  | 8
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 663 |  |  |  | 32
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 518
E. |  | Testing of plant systems or components | [39 empty] | 5
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 66 |  |  |  | 11
H. |  | Nuclear regulatory requirements | [39 empty] | 40
L. |  | Human factor related | [39 empty] | 5
P. |  | Fire | [39 empty] | 18
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 0
Z. |  | Other | [35 empty] | 101 |  |  |  | 6
Subtotal | [22 empty] | 686 |  |  |  | 1131 | [10 empty] | 1532 |  |  |  | 1148
Total | [22 empty] | 1817 | [14 empty] | 2680
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 347
12. |  |  | Reactor I&C Systems | [19 empty] | 45 | [14 empty] | 16
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 69
16. |  |  | Steam generation systems | [19 empty] | 442 | [14 empty] | 126
21. |  |  | Fuel Handling and Storage Facilities | [19 empty] | 643 | [14 empty] | 46
31. |  |  | Turbine and auxiliaries | [34 empty] | 45
32. |  |  | Feedwater and Main Steam System | [34 empty] | 124
33. |  |  | Circulating Water System | [34 empty] | 56
41. |  |  | Main Generator Systems | [34 empty] | 93
42. |  |  | Electrical Power Supply Systems | [34 empty] | 19
Total | [22 empty] | 1130 | [14 empty] | 948

## HEYSHAM A-1
2020 Operating Experience
GB-20A | [8 empty] | HEYSHAM A-1 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | NPC (NUCLEAR POWER CO., LTD.)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-12-01
Thermal power | [12 empty] | : |  |  | 1500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-07-09
Gross electrical power | [12 empty] | : |  |  | 625 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-01
Reference unit power (net) | [12 empty] | : |  |  | 485 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.14
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 650
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 4 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 7.5 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 15.96
| Active core height/length [m] | [13 empty] | : |  |  | 8.3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2592 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 44 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | 8 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2648.85 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 9.49 %
Energy Availability Factor (EAF) | [18 empty] | : | 61.95 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 13.52 %
Unit Capability Factor (UCF) | [18 empty] | : | 61.97 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 24.5 %
Load Factor (LF) | [18 empty] | : | 62.18 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.03 %
Operating Factor (OF) | [18 empty] | : | 64.2 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3145 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 373.27 | 346.20 |  |  |  | 369.42 |  | 347.27 | [8 empty] | 257.69 |  |  | 180.33 | [6 empty] | 357.09 |  | 186.32 |  |  |  | 244.02 |  |  | 0.00 |  |  | -0.61 | [9 empty] | -12.15 |  |  | 2648.85
EAF [%] |  |  |  |  | 100.00 | 99.57 |  |  |  | 100.00 |  | 99.00 | [8 empty] | 71.87 |  |  | 52.97 | [6 empty] | 97.99 |  | 52.98 |  |  |  | 70.71 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 61.95
UCF [%] |  |  |  |  | 100.00 | 99.57 |  |  |  | 100.00 |  | 99.00 | [8 empty] | 71.87 |  |  | 52.97 | [6 empty] | 97.99 |  | 52.98 |  |  |  | 71.04 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 61.97
LF [%] |  |  |  |  | 103.44 | 102.56 |  |  |  | 102.51 |  | 99.45 | [8 empty] | 71.41 |  |  | 51.64 | [6 empty] | 98.96 |  | 51.64 |  |  |  | 69.88 |  |  | 0.00 |  |  | -0.17 | [9 empty] | -3.37 |  |  | 62.18
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 77.42 |  |  | 66.11 | [6 empty] | 100.00 |  | 53.09 |  |  |  | 75.69 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 64.20
FLR [%] |  |  |  |  | 0.00 | 0.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 15.70 | [6 empty] | 2.01 |  | 47.02 |  |  |  | 20.50 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.49
UCL [%] |  |  |  |  | 0.00 | 0.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 18.15 | [6 empty] | 2.01 |  | 47.02 |  |  |  | 18.32 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 74.95 |  |  | 13.52
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 1.00 | [8 empty] | 28.13 |  |  | 28.88 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 10.64 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 25.05 |  |  | 24.50
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.33 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 110624.69 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 14.23 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 68.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 16.64 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 68.32 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.04 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.33 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.21 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.45 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 3045.30 |  |  | 7113 |  |  |  | 420 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 84.82 |  |  | 82.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 1786.74 |  |  | 4096 |  |  |  | 487 | [10 empty] | 43.38 |  |  |  | 43.38 | [5 empty] | 41.95 |  |  | 46.89 |  |  |  | 3.74 |  | 1.68 | [8 empty] | 54.94 |  |  |  |  | 0.00
1991 |  |  |  | 3826.17 |  |  | 7279 |  |  |  | 621 | [10 empty] | 86.45 |  |  |  | 86.45 | [5 empty] | 70.53 |  |  | 83.32 |  |  |  | 0.31 |  | 0.27 | [8 empty] | 13.28 |  |  |  |  | 0.00
1992 |  |  |  | 2764.17 |  |  | 5981 |  |  |  | 550 | [10 empty] | 55.59 |  |  |  | 55.76 | [5 empty] | 56.44 |  |  | 67.17 |  |  |  | 21.28 |  | 15.07 | [8 empty] | 29.17 |  |  |  |  | 0.17
1993 |  |  |  | 3638.22 |  |  | 6643 |  |  |  | 555 | [10 empty] | 74.28 |  |  |  | 75.00 | [5 empty] | 75.04 |  |  | 76.04 |  |  |  | 19.28 |  | 17.92 | [8 empty] | 7.09 |  |  |  |  | 0.71
1994 |  |  |  | 4563.37 |  |  | 8128 |  |  |  | 575 | [10 empty] | 90.40 |  |  |  | 90.54 | [5 empty] | 90.85 |  |  | 93.04 |  |  |  | 2.99 |  | 2.79 | [8 empty] | 6.67 |  |  |  |  | 0.14
1995 |  |  |  | 2808.87 |  |  | 4794 |  |  |  | 575 | [10 empty] | 55.94 |  |  |  | 55.89 | [5 empty] | 55.61 |  |  | 54.58 |  |  |  | 29.33 |  | 23.19 | [8 empty] | 20.92 |  |  |  |  | -0.06
1996 |  |  |  | 4056.80 |  |  | 7674 |  |  |  | 575 | [10 empty] | 80.19 |  |  |  | 80.32 | [5 empty] | 80.32 |  |  | 87.36 |  |  |  | 7.13 |  | 6.16 | [8 empty] | 13.52 |  |  |  |  | 0.13
1997 |  |  |  | 4298.79 |  |  | 7757 |  |  |  | 575 | [10 empty] | 84.53 |  |  |  | 85.38 | [5 empty] | 85.11 |  |  | 88.31 |  |  |  | 7.92 |  | 7.35 | [8 empty] | 7.27 |  |  |  |  | 0.86
1998 |  |  |  | 3766.08 |  |  | 6950 |  |  |  | 575 | [10 empty] | 73.77 |  |  |  | 74.84 | [5 empty] | 74.56 |  |  | 79.12 |  |  |  | 9.74 |  | 8.07 | [8 empty] | 17.09 |  |  |  |  | 1.07
1999 |  |  |  | 4549.83 |  |  | 7990 |  |  |  | 575 | [10 empty] | 89.73 |  |  |  | 90.35 | [5 empty] | 90.08 |  |  | 90.96 |  |  |  | 0.61 |  | 0.55 | [8 empty] | 9.09 |  |  |  |  | 0.62
2000 |  |  |  | 4587.90 |  |  | 8230 |  |  |  | 575 | [10 empty] | 90.39 |  |  |  | 90.84 | [5 empty] | 90.84 |  |  | 93.69 |  |  |  | 3.02 |  | 2.83 | [8 empty] | 6.34 |  |  |  |  | 0.44
2001 |  |  |  | 4034.58 |  |  | 6959 |  |  |  | 575 | [10 empty] | 77.62 |  |  |  | 78.03 | [5 empty] | 79.88 |  |  | 79.22 |  |  |  | 10.61 |  | 9.26 | [8 empty] | 12.71 |  |  |  |  | 0.41
2002 |  |  |  | 4445.53 |  |  | 7921 |  |  |  | 575 | [10 empty] | 87.93 |  |  |  | 88.39 | [5 empty] | 88.26 |  |  | 90.42 |  |  |  | 1.67 |  | 2.60 | [8 empty] | 9.01 |  |  |  |  | 0.46
2003 |  |  |  | 3746.22 |  |  | 6783 |  |  |  | 575 | [10 empty] | 74.40 |  |  |  | 74.75 | [5 empty] | 74.37 |  |  | 77.43 |  |  |  | 20.02 |  | 18.71 | [8 empty] | 6.54 |  |  |  |  | 0.35
2004 |  |  |  | 2638.07 |  |  | 4951 |  |  |  | 575 | [10 empty] | 52.51 |  |  |  | 52.83 | [5 empty] | 52.23 |  |  | 56.36 |  |  |  | 23.49 |  | 32.08 | [8 empty] | 15.09 |  |  |  |  | 0.31
2005 |  |  |  | 4033.07 |  |  | 7458 |  |  |  | 575 | [10 empty] | 80.14 |  |  |  | 80.14 | [5 empty] | 80.07 |  |  | 85.14 |  |  |  | 5.25 |  | 9.34 | [8 empty] | 10.52 |  |  |  |  | 0.00
2006 |  |  |  | 3839.08 |  |  | 7229 |  |  |  | 575 | [10 empty] | 75.50 |  |  |  | 75.50 | [5 empty] | 75.23 |  |  | 82.52 |  |  |  | 13.70 |  | 12.20 | [8 empty] | 12.29 |  |  |  |  | 0.00
2007 |  |  |  | 2498.55 |  |  | 4892 |  |  |  | 585 | [10 empty] | 49.07 |  |  |  | 49.07 | [5 empty] | 48.76 |  |  | 55.84 |  |  |  | 34.75 |  | 34.38 | [8 empty] | 16.54 |  |  |  |  | 0.00
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 585 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 98.85 | [8 empty] | 1.15 |  |  |  |  | 0.00
2009 |  |  |  | 3478.25 |  |  | 6363 |  |  |  | 585 | [10 empty] | 68.38 |  |  |  | 68.38 | [5 empty] | 67.87 |  |  | 72.64 |  |  |  | 16.25 |  | 18.31 | [8 empty] | 13.31 |  |  |  |  | 0.00
2010 |  |  |  | 2826.72 |  |  | 5117 |  |  |  | 585 | [10 empty] | 55.09 |  |  |  | 55.09 | [5 empty] | 55.16 |  |  | 58.41 |  |  |  | 14.73 |  | 25.92 | [8 empty] | 18.99 |  |  |  |  | 0.00
2011 |  |  |  | 4627.86 |  |  | 8225 |  |  |  | 585 | [10 empty] | 90.48 |  |  |  | 90.48 | [5 empty] | 90.31 |  |  | 93.89 |  |  |  | 2.86 |  | 2.74 | [8 empty] | 6.78 |  |  |  |  | 0.00
2012 |  |  |  | 3749.04 |  |  | 7055 |  |  |  | 585 | [10 empty] | 73.38 |  |  |  | 73.38 | [5 empty] | 72.96 |  |  | 80.32 |  |  |  | 21.36 |  | 20.03 | [8 empty] | 6.59 |  |  |  |  | 0.00
2013 |  |  |  | 2833.02 |  |  | 5384 |  |  |  | 585 | [10 empty] | 56.60 |  |  |  | 56.60 | [5 empty] | 55.28 |  |  | 61.46 |  |  |  | 8.93 |  | 26.72 | [8 empty] | 16.68 |  |  |  |  | 0.00
2014 |  |  |  | 1073.88 |  |  | 2841 |  |  |  | 580 | [10 empty] | 22.17 |  |  |  | 22.17 | [5 empty] | 21.14 |  |  | 32.43 |  |  |  | 35.42 |  | 59.13 | [8 empty] | 18.70 |  |  |  |  | 0.00
2015 |  |  |  | 2167.04 |  |  | 6886 |  |  |  | 580 | [10 empty] | 43.07 |  |  |  | 43.07 | [5 empty] | 42.65 |  |  | 78.61 |  |  |  | 7.13 |  | 25.99 | [8 empty] | 30.94 |  |  |  |  | 0.00
2016 |  |  |  | 3472.18 |  |  | 7663 | [14 empty] | 68.39 |  |  |  | 69.17 | [5 empty] | 68.15 |  |  | 87.24 |  |  |  | 1.00 |  | 2.11 | [8 empty] | 28.72 |  |  |  |  | 0.77
2017 |  |  |  | 0.00 | [17 empty] | 60.19 |  |  |  | 60.19 | [5 empty] | 59.91 |  |  | 72.91 |  |  |  | 0.00 |  | 8.83 | [8 empty] | 30.98 |  |  |  |  | 0.00
2018 |  |  |  | 3857.56 |  |  | 8018 |  |  |  | 485 | [10 empty] | 89.94 |  |  |  | 90.12 | [5 empty] | 90.80 |  |  | 91.53 |  |  |  | 1.73 |  | 3.36 | [8 empty] | 6.52 |  |  |  |  | 0.18
2019 |  |  |  | 3581.24 |  |  | 7826 |  |  |  | 485 | [10 empty] | 84.01 |  |  |  | 84.09 | [5 empty] | 84.29 |  |  | 89.34 |  |  |  | 4.73 |  | 7.97 | [8 empty] | 7.94 |  |  |  |  | 0.08
2020 |  |  |  | 2648.85 |  |  | 5639 |  |  |  | 485 | [10 empty] | 61.95 |  |  |  | 61.97 | [5 empty] | 62.18 |  |  | 64.20 |  |  |  | 9.49 |  | 13.52 | [8 empty] | 24.50 |  |  |  |  | 0.03
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 758 | [14 empty] | 865
B. |  | Refuelling without maintenance | [20 empty] | 376 | [14 empty] | 150 |  |  |  | 5
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1722 | [14 empty] | 803 |  |  |  | 168
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 517
E. |  | Testing of plant systems or components | [39 empty] | 80
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 53 |  |  |  | 5
H. |  | Nuclear regulatory requirements | [39 empty] | 57
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [24 empty] | 452 | [14 empty] | 61
Z. |  | Other | [35 empty] | 56 |  |  |  | 31 | [11 empty] | 6
Subtotal | [22 empty] | 2098 |  |  |  | 1210 | [10 empty] | 1579 |  |  |  | 1272 | [11 empty] | 8
Total | [22 empty] | 3308 | [14 empty] | 2859
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 341
12. |  |  | Reactor I&C Systems | [34 empty] | 25
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 23
15. |  |  | Reactor Cooling Systems | [34 empty] | 37
16. |  |  | Steam generation systems | [19 empty] | 558 | [14 empty] | 219
21. |  |  | Fuel Handling and Storage Facilities | [19 empty] | 200 | [14 empty] | 23
31. |  |  | Turbine and auxiliaries | [19 empty] | 452 | [14 empty] | 52
32. |  |  | Feedwater and Main Steam System | [34 empty] | 46
33. |  |  | Circulating Water System | [34 empty] | 123
34. |  |  | Miscellaneous Systems | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 71
42. |  |  | Electrical Power Supply Systems | [34 empty] | 31
Total | [22 empty] | 1210 | [14 empty] | 1004
Highlights (2020)
Carried out a statutory outage

## HEYSHAM A-2
2020 Operating Experience
GB-20B | [8 empty] | HEYSHAM A-2 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | NPC (NUCLEAR POWER CO., LTD.)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-12-01
Thermal power | [12 empty] | : |  |  | 1500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-10-11
Gross electrical power | [12 empty] | : |  |  | 625 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-01
Reference unit power (net) | [12 empty] | : |  |  | 575 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.14
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 650
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 4 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 7.5 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 15.96
| Active core height/length [m] | [13 empty] | : |  |  | 8.3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2592 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 44 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | 8 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3464.2 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 15.74 %
Energy Availability Factor (EAF) | [18 empty] | : | 69.05 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 22.38 %
Unit Capability Factor (UCF) | [18 empty] | : | 69.05 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.57 %
Load Factor (LF) | [18 empty] | : | 68.59 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 80.1 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1748 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 310.35 | 51.77 |  |  |  | 221.33 |  | 368.29 | [8 empty] | 376.52 |  |  | 361.74 | [6 empty] | 370.96 |  | 168.22 |  |  |  | 119.20 |  |  | 375.93 |  |  | 364.39 | [9 empty] | 375.49 |  |  | 3464.20
EAF [%] |  |  |  |  | 73.12 | 14.50 |  |  |  | 52.95 |  | 88.96 | [8 empty] | 88.01 |  |  | 87.38 | [6 empty] | 86.71 |  | 40.33 |  |  |  | 30.10 |  |  | 87.76 |  |  | 88.02 | [9 empty] | 87.77 |  |  | 69.05
UCF [%] |  |  |  |  | 73.12 | 14.50 |  |  |  | 52.95 |  | 88.96 | [8 empty] | 88.01 |  |  | 87.38 | [6 empty] | 86.71 |  | 40.33 |  |  |  | 30.10 |  |  | 87.76 |  |  | 88.02 | [9 empty] | 87.77 |  |  | 69.05
LF [%] |  |  |  |  | 72.54 | 12.94 |  |  |  | 51.81 |  | 88.96 | [8 empty] | 88.01 |  |  | 87.38 | [6 empty] | 86.71 |  | 39.32 |  |  |  | 28.79 |  |  | 87.76 |  |  | 88.02 | [9 empty] | 87.77 |  |  | 68.59
OF [%] |  |  |  |  | 86.02 | 17.24 |  |  |  | 62.72 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 51.61 |  |  |  | 40.14 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.10
FLR [%] |  |  |  |  | 20.39 | 75.55 |  |  |  | 8.78 |  | 11.04 | [8 empty] | 11.99 |  |  | 12.62 | [6 empty] | 6.43 |  | 8.00 |  |  |  | 17.20 |  |  | 12.24 |  |  | 11.98 | [9 empty] | 12.23 |  |  | 15.74
UCL [%] |  |  |  |  | 18.72 | 44.83 |  |  |  | 44.07 |  | 11.04 | [8 empty] | 11.99 |  |  | 12.62 | [6 empty] | 5.96 |  | 14.94 |  |  |  | 69.90 |  |  | 12.24 |  |  | 11.98 | [9 empty] | 12.23 |  |  | 22.38
PUF [%] |  |  |  |  | 8.16 | 40.67 |  |  |  | 2.98 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 7.32 |  | 44.73 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.57
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 106315.05 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 16.19 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 67.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 18.82 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 67.73 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.45 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 66.47 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.45 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.37 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 2505.64 |  |  | 5507 |  |  |  | 470 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 90.38 |  |  | 83.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 3044.18 |  |  | 6690 |  |  |  | 487 | [10 empty] | 71.98 |  |  |  | 71.98 | [5 empty] | 71.48 |  |  | 76.58 |  |  |  | 9.35 |  | 7.42 | [8 empty] | 20.59 |  |  |  |  | 0.00
1991 |  |  |  | 2647.73 |  |  | 5132 |  |  |  | 622 | [10 empty] | 64.65 |  |  |  | 64.99 | [5 empty] | 48.73 |  |  | 58.75 |  |  |  | 2.53 |  | 1.69 | [8 empty] | 33.32 |  |  |  |  | 0.34
1992 |  |  |  | 3548.13 |  |  | 6951 |  |  |  | 550 | [10 empty] | 72.79 |  |  |  | 74.58 | [5 empty] | 72.45 |  |  | 78.07 |  |  |  | 11.81 |  | 9.99 | [8 empty] | 15.43 |  |  |  |  | 1.79
1993 |  |  |  | 4336.47 |  |  | 7886 |  |  |  | 555 | [10 empty] | 88.10 |  |  |  | 88.50 | [5 empty] | 89.44 |  |  | 90.27 |  |  |  | 2.78 |  | 2.53 | [8 empty] | 8.97 |  |  |  |  | 0.40
1994 |  |  |  | 3707.46 |  |  | 6652 |  |  |  | 575 | [10 empty] | 72.83 |  |  |  | 75.31 | [5 empty] | 73.81 |  |  | 76.14 |  |  |  | 3.02 |  | 2.34 | [8 empty] | 22.34 |  |  |  |  | 2.48
1995 |  |  |  | 3367.50 |  |  | 5772 |  |  |  | 575 | [10 empty] | 66.95 |  |  |  | 66.95 | [5 empty] | 66.67 |  |  | 65.71 |  |  |  | 23.46 |  | 20.52 | [8 empty] | 12.54 |  |  |  |  | 0.00
1996 |  |  |  | 3561.87 |  |  | 6836 |  |  |  | 575 | [10 empty] | 70.47 |  |  |  | 70.80 | [5 empty] | 70.52 |  |  | 77.82 |  |  |  | 5.27 |  | 3.94 | [8 empty] | 25.26 |  |  |  |  | 0.33
1997 |  |  |  | 4443.31 |  |  | 8026 |  |  |  | 575 | [10 empty] | 86.91 |  |  |  | 88.25 | [5 empty] | 87.97 |  |  | 91.37 |  |  |  | 2.71 |  | 2.45 | [8 empty] | 9.30 |  |  |  |  | 1.33
1998 |  |  |  | 4497.56 |  |  | 7999 |  |  |  | 575 | [10 empty] | 86.67 |  |  |  | 89.32 | [5 empty] | 89.05 |  |  | 91.06 |  |  |  | 2.11 |  | 1.93 | [8 empty] | 8.75 |  |  |  |  | 2.65
1999 |  |  |  | 3712.69 |  |  | 6570 |  |  |  | 575 | [10 empty] | 71.74 |  |  |  | 73.78 | [5 empty] | 73.51 |  |  | 74.80 |  |  |  | 13.67 |  | 11.69 | [8 empty] | 14.53 |  |  |  |  | 2.04
2000 |  |  |  | 4342.62 |  |  | 7946 |  |  |  | 575 | [10 empty] | 86.13 |  |  |  | 86.25 | [5 empty] | 85.98 |  |  | 90.46 |  |  |  | 6.15 |  | 5.66 | [8 empty] | 8.09 |  |  |  |  | 0.13
2001 |  |  |  | 4495.02 |  |  | 8187 |  |  |  | 575 | [10 empty] | 89.27 |  |  |  | 90.80 | [5 empty] | 89.00 |  |  | 93.20 |  |  |  | 0.92 |  | 0.84 | [8 empty] | 8.35 |  |  |  |  | 1.54
2002 |  |  |  | 3407.89 |  |  | 6313 |  |  |  | 575 | [10 empty] | 68.12 |  |  |  | 68.34 | [5 empty] | 67.66 |  |  | 72.07 |  |  |  | 12.45 |  | 13.80 | [8 empty] | 17.86 |  |  |  |  | 0.21
2003 |  |  |  | 3646.95 |  |  | 6595 |  |  |  | 575 | [10 empty] | 72.53 |  |  |  | 72.53 | [5 empty] | 72.40 |  |  | 75.29 |  |  |  | 22.51 |  | 21.07 | [8 empty] | 6.41 |  |  |  |  | 0.00
2004 |  |  |  | 1974.61 |  |  | 3805 |  |  |  | 575 | [10 empty] | 39.74 |  |  |  | 39.90 | [5 empty] | 39.09 |  |  | 43.32 |  |  |  | 57.95 |  | 54.98 | [8 empty] | 5.12 |  |  |  |  | 0.16
2005 |  |  |  | 2112.60 |  |  | 3869 |  |  |  | 575 | [10 empty] | 43.66 |  |  |  | 43.66 | [5 empty] | 41.94 |  |  | 44.17 |  |  |  | 41.69 |  | 39.47 | [8 empty] | 16.87 |  |  |  |  | 0.00
2006 |  |  |  | 3972.25 |  |  | 7735 |  |  |  | 575 | [10 empty] | 79.00 |  |  |  | 79.00 | [5 empty] | 78.86 |  |  | 88.30 |  |  |  | 7.51 |  | 6.42 | [8 empty] | 14.59 |  |  |  |  | 0.00
2007 |  |  |  | 2981.62 |  |  | 6280 |  |  |  | 575 | [10 empty] | 59.35 |  |  |  | 59.35 | [5 empty] | 59.19 |  |  | 71.69 |  |  |  | 15.78 |  | 30.34 | [8 empty] | 10.31 |  |  |  |  | 0.00
2008 |  |  |  | 0.00 |  |  | 0 |  |  |  | 575 | [10 empty] | 0.01 |  |  |  | 0.01 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 83.27 | [8 empty] | 16.72 |  |  |  |  | 0.00
2009 |  |  |  | 2865.50 |  |  | 6414 |  |  |  | 575 | [10 empty] | 57.24 |  |  |  | 57.24 | [5 empty] | 56.89 |  |  | 73.22 |  |  |  | 20.33 |  | 37.55 | [8 empty] | 5.21 |  |  |  |  | 0.00
2010 |  |  |  | 2421.73 |  |  | 5862 |  |  |  | 575 | [10 empty] | 48.08 |  |  |  | 48.08 | [5 empty] | 48.08 |  |  | 66.92 |  |  |  | 48.53 |  | 45.68 | [8 empty] | 6.24 |  |  |  |  | 0.00
2011 |  |  |  | 3942.22 |  |  | 8117 |  |  |  | 575 | [10 empty] | 78.49 |  |  |  | 78.49 | [5 empty] | 78.27 |  |  | 92.66 |  |  |  | 16.25 |  | 15.22 | [8 empty] | 6.29 |  |  |  |  | 0.00
2012 |  |  |  | 2891.72 |  |  | 5565 |  |  |  | 575 | [10 empty] | 58.04 |  |  |  | 58.04 | [5 empty] | 57.25 |  |  | 63.35 |  |  |  | 23.21 |  | 19.20 | [8 empty] | 22.76 |  |  |  |  | 0.00
2013 |  |  |  | 4022.80 |  |  | 7464 |  |  |  | 575 | [10 empty] | 81.31 |  |  |  | 81.31 | [5 empty] | 79.87 |  |  | 85.21 |  |  |  | 10.40 |  | 10.40 | [8 empty] | 8.30 |  |  |  |  | 0.00
2014 |  |  |  | 2775.28 |  |  | 5385 |  |  |  | 575 | [10 empty] | 55.75 |  |  |  | 55.75 | [5 empty] | 55.10 |  |  | 61.47 |  |  |  | 34.05 |  | 31.86 | [8 empty] | 12.39 |  |  |  |  | 0.00
2015 |  |  |  | 2456.79 |  |  | 5498 |  |  |  | 575 | [10 empty] | 49.20 |  |  |  | 49.20 | [5 empty] | 48.77 |  |  | 62.76 |  |  |  | 3.19 |  | 15.71 | [8 empty] | 35.08 |  |  |  |  | 0.00
2016 |  |  |  | 4116.58 |  |  | 7646 | [14 empty] | 81.77 |  |  |  | 82.40 | [5 empty] | 81.50 |  |  | 87.04 |  |  |  | 4.15 |  | 5.50 | [8 empty] | 12.10 |  |  |  |  | 0.63
2017 |  |  |  | 0.00 | [17 empty] | 65.46 |  |  |  | 65.46 | [5 empty] | 64.89 |  |  | 79.17 |  |  |  | 27.60 |  | 31.28 | [8 empty] | 3.25 |  |  |  |  | 0.00
2018 |  |  |  | 3493.12 |  |  | 7015 |  |  |  | 575 | [10 empty] | 69.50 |  |  |  | 69.50 | [5 empty] | 69.35 |  |  | 80.08 |  |  |  | 12.90 |  | 11.02 | [8 empty] | 19.48 |  |  |  |  | 0.00
2019 |  |  |  | 3233.76 |  |  | 6648 |  |  |  | 575 | [10 empty] | 64.84 |  |  |  | 64.84 | [5 empty] | 64.20 |  |  | 75.89 |  |  |  | 25.72 |  | 26.31 | [8 empty] | 8.85 |  |  |  |  | 0.00
2020 |  |  |  | 3464.20 |  |  | 7036 |  |  |  | 575 | [10 empty] | 69.05 |  |  |  | 69.05 | [5 empty] | 68.59 |  |  | 80.10 |  |  |  | 15.74 |  | 22.38 | [8 empty] | 8.57 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 1343 | [14 empty] | 845
B. |  | Refuelling without maintenance | [20 empty] | 561 | [14 empty] | 189 |  |  |  | 7
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 692 |  |  |  | 21
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 509 |  |  |  | 226
E. |  | Testing of plant systems or components | [35 empty] | 6 |  |  |  | 20
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 18 |  |  |  | 32
H. |  | Nuclear regulatory requirements | [39 empty] | 106
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 3
P. |  | Fire | [39 empty] | 4
Z. |  | Other | [35 empty] | 83 |  |  |  | 54 | [11 empty] | 5
Subtotal | [22 empty] | 561 |  |  |  | 1343 | [10 empty] | 1497 |  |  |  | 1318 | [11 empty] | 16
Total | [22 empty] | 1904 | [14 empty] | 2831
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 399
12. |  |  | Reactor I&C Systems | [34 empty] | 32
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 15
15. |  |  | Reactor Cooling Systems | [34 empty] | 69
16. |  |  | Steam generation systems | [19 empty] | 516 | [14 empty] | 189
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [19 empty] | 156 | [14 empty] | 11
31. |  |  | Turbine and auxiliaries | [34 empty] | 78
32. |  |  | Feedwater and Main Steam System | [34 empty] | 47
33. |  |  | Circulating Water System | [19 empty] | 671 | [14 empty] | 130
34. |  |  | Miscellaneous Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 40
42. |  |  | Electrical Power Supply Systems | [34 empty] | 73
Total | [22 empty] | 1343 | [14 empty] | 1089
Highlights (2020)
Load limited to 90% of RUP to manage fuel clad temperatures

## HEYSHAM B-1
2020 Operating Experience
GB-22A | [8 empty] | HEYSHAM B-1 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | NPC (NUCLEAR POWER CO., LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-08-01
Thermal power | [12 empty] | : |  |  | 1550 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-07-12
Gross electrical power | [12 empty] | : |  |  | 680 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-01
Reference unit power (net) | [12 empty] | : |  |  | 620 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.3
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 635
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 2 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 27000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 15.9
| Active core height/length [m] | [13 empty] | : |  |  | 8.31 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 332 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4993.67 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 5.71 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.65 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.57 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.89 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.55 %
Load Factor (LF) | [18 empty] | : | 91.69 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.23 %
Operating Factor (OF) | [18 empty] | : | 97.32 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 235 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 404.89 | 432.62 |  |  |  | 432.56 |  | 274.50 | [8 empty] | 380.90 |  |  | 412.95 | [6 empty] | 457.83 |  | 423.69 |  |  |  | 432.23 |  |  | 450.07 |  |  | 447.14 | [9 empty] | 444.29 |  |  | 4993.67
EAF [%] |  |  |  |  | 87.31 | 100.00 |  |  |  | 93.77 |  | 61.86 | [8 empty] | 83.05 |  |  | 92.51 | [6 empty] | 99.25 |  | 91.85 |  |  |  | 96.83 |  |  | 97.19 |  |  | 99.97 | [9 empty] | 96.31 |  |  | 91.65
UCF [%] |  |  |  |  | 87.31 | 100.00 |  |  |  | 93.77 |  | 61.86 | [8 empty] | 83.14 |  |  | 93.04 | [6 empty] | 99.97 |  | 92.68 |  |  |  | 97.43 |  |  | 97.21 |  |  | 99.97 | [9 empty] | 96.31 |  |  | 91.89
LF [%] |  |  |  |  | 87.77 | 100.25 |  |  |  | 93.90 |  | 61.49 | [8 empty] | 82.58 |  |  | 92.51 | [6 empty] | 99.25 |  | 91.85 |  |  |  | 96.83 |  |  | 97.44 |  |  | 100.17 | [9 empty] | 96.32 |  |  | 91.69
OF [%] |  |  |  |  | 98.92 | 100.00 |  |  |  | 100.00 |  | 77.92 | [8 empty] | 90.86 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.32
FLR [%] |  |  |  |  | 6.27 | 0.00 |  |  |  | 2.36 |  | 38.14 | [8 empty] | 16.85 |  |  | 0.33 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 3.57 |  |  | 5.71
UCL [%] |  |  |  |  | 5.84 | 0.00 |  |  |  | 2.26 |  | 38.14 | [8 empty] | 16.85 |  |  | 0.31 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 3.56 |  |  | 5.57
PUF [%] |  |  |  |  | 6.85 | 0.00 |  |  |  | 3.96 |  | 0.00 | [8 empty] | 0.02 |  |  | 6.66 | [6 empty] | 0.03 |  | 7.32 |  |  |  | 2.57 |  |  | 2.79 |  |  | 0.03 | [9 empty] | 0.13 |  |  | 2.55
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.09 |  |  | 0.53 | [6 empty] | 0.71 |  | 0.83 |  |  |  | 0.60 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.23
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 135714.09 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.48 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.39 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.95 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 79.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.56 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.5 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 2204.46 |  |  | 4454 |  |  |  | 615 | [10 empty] | 56.92 |  |  |  | 56.92 | [5 empty] | 22.19 |  |  | 35.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 43.08 |  |  |  |  | 0.00
1990 |  |  |  | 1487.04 |  |  | 3509 |  |  |  | 615 | [10 empty] | 27.75 |  |  |  | 27.75 | [5 empty] | 27.68 |  |  | 40.17 |  |  |  | 1.22 |  | 0.34 | [8 empty] | 71.91 |  |  |  |  | 0.00
1991 |  |  |  | 1465.40 |  |  | 2786 |  |  |  | 615 | [10 empty] | 36.89 |  |  |  | 36.89 | [5 empty] | 27.28 |  |  | 31.89 |  |  |  | 3.91 |  | 1.50 | [8 empty] | 61.61 |  |  |  |  | 0.00
1992 |  |  |  | 4095.95 |  |  | 7240 |  |  |  | 615 | [10 empty] | 74.85 |  |  |  | 80.22 | [5 empty] | 74.80 |  |  | 81.31 |  |  |  | 3.95 |  | 3.30 | [8 empty] | 16.48 |  |  |  |  | 5.37
1993 |  |  |  | 4498.15 |  |  | 7376 |  |  |  | 622 | [10 empty] | 82.29 |  |  |  | 83.72 | [5 empty] | 82.70 |  |  | 84.43 |  |  |  | 2.77 |  | 2.38 | [8 empty] | 13.89 |  |  |  |  | 1.44
1994 |  |  |  | 4181.11 |  |  | 7255 |  |  |  | 625 | [10 empty] | 75.62 |  |  |  | 79.11 | [5 empty] | 76.58 |  |  | 83.05 |  |  |  | 2.13 |  | 1.72 | [8 empty] | 19.17 |  |  |  |  | 3.49
1995 |  |  |  | 5193.85 |  |  | 8286 |  |  |  | 625 | [10 empty] | 94.47 |  |  |  | 94.88 | [5 empty] | 94.61 |  |  | 94.33 |  |  |  | 1.61 |  | 1.55 | [8 empty] | 3.57 |  |  |  |  | 0.41
1996 |  |  |  | 4707.35 |  |  | 7699 |  |  |  | 625 | [10 empty] | 84.98 |  |  |  | 85.74 | [5 empty] | 85.74 |  |  | 87.65 |  |  |  | 3.25 |  | 2.88 | [8 empty] | 11.38 |  |  |  |  | 0.76
1997 |  |  |  | 4152.78 |  |  | 7105 |  |  |  | 625 | [10 empty] | 75.23 |  |  |  | 75.92 | [5 empty] | 75.64 |  |  | 80.89 |  |  |  | 7.88 |  | 6.49 | [8 empty] | 17.59 |  |  |  |  | 0.68
1998 |  |  |  | 5019.39 |  |  | 8688 |  |  |  | 625 | [10 empty] | 90.49 |  |  |  | 91.70 | [5 empty] | 91.43 |  |  | 98.91 |  |  |  | 1.20 |  | 1.12 | [8 empty] | 7.18 |  |  |  |  | 1.21
1999 |  |  |  | 4235.45 |  |  | 7212 |  |  |  | 625 | [10 empty] | 76.55 |  |  |  | 77.42 | [5 empty] | 77.15 |  |  | 82.10 |  |  |  | 9.49 |  | 8.12 | [8 empty] | 14.46 |  |  |  |  | 0.87
2000 |  |  |  | 4415.35 |  |  | 7502 |  |  |  | 625 | [10 empty] | 79.95 |  |  |  | 80.43 | [5 empty] | 80.43 |  |  | 85.41 |  |  |  | 16.32 |  | 15.69 | [8 empty] | 3.89 |  |  |  |  | 0.48
2001 |  |  |  | 5240.97 |  |  | 8534 |  |  |  | 625 | [10 empty] | 91.45 |  |  |  | 92.02 | [5 empty] | 95.46 |  |  | 97.15 |  |  |  | 4.27 |  | 4.10 | [8 empty] | 3.88 |  |  |  |  | 0.57
2002 |  |  |  | 4413.96 |  |  | 7501 |  |  |  | 625 | [10 empty] | 80.82 |  |  |  | 80.82 | [5 empty] | 80.62 |  |  | 85.63 |  |  |  | 4.45 |  | 4.31 | [8 empty] | 14.88 |  |  |  |  | 0.00
2003 |  |  |  | 5045.34 |  |  | 8444 |  |  |  | 625 | [10 empty] | 92.04 |  |  |  | 92.15 | [5 empty] | 92.15 |  |  | 96.39 |  |  |  | 4.77 |  | 4.61 | [8 empty] | 3.23 |  |  |  |  | 0.11
2004 |  |  |  | 4115.67 |  |  | 7250 |  |  |  | 625 | [10 empty] | 75.33 |  |  |  | 75.36 | [5 empty] | 74.97 |  |  | 82.54 |  |  |  | 22.13 |  | 21.42 | [8 empty] | 3.22 |  |  |  |  | 0.03
2005 |  |  |  | 4262.48 |  |  | 7317 |  |  |  | 625 | [10 empty] | 77.95 |  |  |  | 77.95 | [5 empty] | 77.85 |  |  | 83.53 |  |  |  | 6.10 |  | 5.20 | [8 empty] | 16.84 |  |  |  |  | 0.00
2006 |  |  |  | 4603.97 |  |  | 8057 |  |  |  | 625 | [10 empty] | 85.22 |  |  |  | 85.22 | [5 empty] | 85.12 |  |  | 91.97 |  |  |  | 9.11 |  | 8.66 | [8 empty] | 6.12 |  |  |  |  | 0.00
2007 |  |  |  | 4617.34 |  |  | 8006 |  |  |  | 615 | [10 empty] | 85.83 |  |  |  | 85.83 | [5 empty] | 85.71 |  |  | 91.39 |  |  |  | 8.94 |  | 10.48 | [8 empty] | 3.69 |  |  |  |  | 0.00
2008 |  |  |  | 3879.33 |  |  | 7038 |  |  |  | 615 | [10 empty] | 72.11 |  |  |  | 72.11 | [5 empty] | 71.81 |  |  | 80.12 |  |  |  | 5.87 |  | 8.03 | [8 empty] | 19.87 |  |  |  |  | 0.00
2009 |  |  |  | 4750.20 |  |  | 8497 |  |  |  | 620 | [10 empty] | 87.70 |  |  |  | 87.78 | [5 empty] | 87.64 |  |  | 97.00 |  |  |  | 4.23 |  | 9.12 | [8 empty] | 3.10 |  |  |  |  | 0.07
2010 |  |  |  | 5000.04 |  |  | 8637 |  |  |  | 620 | [10 empty] | 92.80 |  |  |  | 94.43 | [5 empty] | 92.06 |  |  | 98.60 |  |  |  | 1.27 |  | 1.81 | [8 empty] | 3.76 |  |  |  |  | 1.63
2011 |  |  |  | 3920.77 |  |  | 6772 |  |  |  | 605 | [10 empty] | 73.23 |  |  |  | 73.23 | [5 empty] | 73.98 |  |  | 77.31 |  |  |  | 1.87 |  | 7.70 | [8 empty] | 19.07 |  |  |  |  | 0.00
2012 |  |  |  | 4158.33 |  |  | 7238 |  |  |  | 610 | [10 empty] | 77.15 |  |  |  | 77.15 | [5 empty] | 77.61 |  |  | 82.40 |  |  |  | 17.30 |  | 16.90 | [8 empty] | 5.95 |  |  |  |  | 0.00
2013 |  |  |  | 4756.06 |  |  | 8071 |  |  |  | 610 | [10 empty] | 87.70 |  |  |  | 87.70 | [5 empty] | 89.00 |  |  | 92.13 |  |  |  | 8.74 |  | 8.48 | [8 empty] | 3.82 |  |  |  |  | 0.00
2014 |  |  |  | 5228.25 |  |  | 8760 |  |  |  | 610 | [10 empty] | 96.22 |  |  |  | 96.22 | [5 empty] | 97.84 |  |  | 100.00 |  |  |  | 0.11 |  | 0.19 | [8 empty] | 3.59 |  |  |  |  | 0.00
2015 |  |  |  | 4191.06 |  |  | 7038 |  |  |  | 615 | [10 empty] | 77.11 |  |  |  | 77.19 | [5 empty] | 77.79 |  |  | 80.34 |  |  |  | 1.79 |  | 1.41 | [8 empty] | 21.41 |  |  |  |  | 0.08
2016 |  |  |  | 5262.55 |  |  | 8784 | [14 empty] | 96.35 |  |  |  | 96.35 | [5 empty] | 97.42 |  |  | 100.00 |  |  |  | 0.04 |  | 0.48 | [8 empty] | 3.16 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 | [17 empty] | 93.14 |  |  |  | 93.17 | [5 empty] | 94.04 |  |  | 97.15 |  |  |  | 1.40 |  | 3.03 | [8 empty] | 3.80 |  |  |  |  | 0.03
2018 |  |  |  | 3805.18 |  |  | 6598 |  |  |  | 620 | [10 empty] | 70.39 |  |  |  | 70.55 | [5 empty] | 70.06 |  |  | 75.32 |  |  |  | 4.18 |  | 4.22 | [8 empty] | 25.23 |  |  |  |  | 0.16
2019 |  |  |  | 5242.90 |  |  | 8760 |  |  |  | 620 | [10 empty] | 95.96 |  |  |  | 96.03 | [5 empty] | 96.53 |  |  | 100.00 |  |  |  | 0.19 |  | 0.25 | [8 empty] | 3.72 |  |  |  |  | 0.07
2020 |  |  |  | 4993.67 |  |  | 8549 |  |  |  | 620 | [10 empty] | 91.65 |  |  |  | 91.89 | [5 empty] | 91.69 |  |  | 97.32 |  |  |  | 5.71 |  | 5.57 | [8 empty] | 2.55 |  |  |  |  | 0.23
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 236 | [14 empty] | 266
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 621 |  |  |  | 34
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 119 |  |  |  | 4
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 29
L. |  | Human factor related | [39 empty] | 24
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 92
Z. |  | Other | [39 empty] | 0 | [11 empty] | 10
Subtotal | [26 empty] | 236 | [10 empty] | 833 |  |  |  | 333 | [11 empty] | 39
Total | [22 empty] | 236 | [14 empty] | 1205
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 22
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [19 empty] | 236 | [14 empty] | 121
32. |  |  | Feedwater and Main Steam System | [34 empty] | 94
41. |  |  | Main Generator Systems | [34 empty] | 19
42. |  |  | Electrical Power Supply Systems | [34 empty] | 22
Total | [22 empty] | 236 | [14 empty] | 303

## HEYSHAM B-2
2020 Operating Experience
GB-22B | [8 empty] | HEYSHAM B-2 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | NPC (NUCLEAR POWER CO., LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-08-01
Thermal power | [12 empty] | : |  |  | 1550 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-11-11
Gross electrical power | [12 empty] | : |  |  | 680 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-01
Reference unit power (net) | [12 empty] | : |  |  | 620 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.3
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 635
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 2 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 27000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 15.9
| Active core height/length [m] | [13 empty] | : |  |  | 8.31 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 332 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 8
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3948.62 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.6 %
Energy Availability Factor (EAF) | [18 empty] | : | 72.85 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.35 %
Unit Capability Factor (UCF) | [18 empty] | : | 73.05 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 19.61 %
Load Factor (LF) | [18 empty] | : | 72.5 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.2 %
Operating Factor (OF) | [18 empty] | : | 77.21 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2002 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 448.96 | -3.38 |  |  |  | -3.45 |  | 105.68 | [8 empty] | 448.42 |  |  | 422.34 | [6 empty] | 457.25 |  | 423.49 |  |  |  | 359.93 |  |  | 455.60 |  |  | 444.03 | [9 empty] | 389.74 |  |  | 3948.62
EAF [%] |  |  |  |  | 97.32 | 0.00 |  |  |  | 0.00 |  | 26.17 | [8 empty] | 97.20 |  |  | 94.61 | [6 empty] | 99.13 |  | 91.81 |  |  |  | 80.80 |  |  | 98.64 |  |  | 99.47 | [9 empty] | 84.49 |  |  | 72.85
UCF [%] |  |  |  |  | 97.32 | 0.00 |  |  |  | 0.00 |  | 26.19 | [8 empty] | 97.35 |  |  | 95.22 | [6 empty] | 99.78 |  | 92.40 |  |  |  | 80.97 |  |  | 98.82 |  |  | 99.49 | [9 empty] | 84.49 |  |  | 73.05
LF [%] |  |  |  |  | 97.33 | -0.78 |  |  |  | -0.75 |  | 23.67 | [8 empty] | 97.21 |  |  | 94.61 | [6 empty] | 99.13 |  | 91.81 |  |  |  | 80.63 |  |  | 98.64 |  |  | 99.47 | [9 empty] | 84.49 |  |  | 72.50
OF [%] |  |  |  |  | 97.98 | 0.00 |  |  |  | 0.00 |  | 30.56 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 93.33 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 77.21
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.52 |  |  | 0.00 | [6 empty] | 0.22 |  | 0.53 |  |  |  | 14.04 |  |  | 0.71 |  |  | 0.00 | [9 empty] | 15.51 |  |  | 3.60
UCL [%] |  |  |  |  | 0.18 | 0.00 |  |  |  | 0.00 |  | 56.13 | [8 empty] | 2.52 |  |  | 0.00 | [6 empty] | 0.22 |  | 0.49 |  |  |  | 13.23 |  |  | 0.71 |  |  | 0.00 | [9 empty] | 15.51 |  |  | 7.35
PUF [%] |  |  |  |  | 2.50 | 100.00 |  |  |  | 100.00 |  | 17.69 | [8 empty] | 0.13 |  |  | 4.78 | [6 empty] | 0.00 |  | 7.11 |  |  |  | 5.81 |  |  | 0.47 |  |  | 0.51 | [9 empty] | 0.00 |  |  | 19.61
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.15 |  |  | 0.61 | [6 empty] | 0.66 |  | 0.59 |  |  |  | 0.16 |  |  | 0.19 |  |  | 0.03 | [9 empty] | 0.00 |  |  | 0.20
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 131192.95 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.37 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.32 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.49 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.11 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.4 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.64 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.79 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.58 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 3825.57 |  |  | 6989 |  |  |  | 615 | [10 empty] | 74.41 |  |  |  | 74.41 | [5 empty] | 63.81 |  |  | 73.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.59 |  |  |  |  | 0.00
1990 |  |  |  | 783.97 |  |  | 1901 |  |  |  | 615 | [10 empty] | 14.92 |  |  |  | 14.92 | [5 empty] | 14.59 |  |  | 21.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 85.08 |  |  |  |  | 0.00
1991 |  |  |  | 2423.97 |  |  | 4453 |  |  |  | 615 | [10 empty] | 53.43 |  |  |  | 53.66 | [5 empty] | 45.12 |  |  | 50.97 |  |  |  | 3.43 |  | 1.91 | [8 empty] | 44.43 |  |  |  |  | 0.23
1992 |  |  |  | 3486.52 |  |  | 6198 |  |  |  | 615 | [10 empty] | 64.72 |  |  |  | 66.40 | [5 empty] | 63.67 |  |  | 69.61 |  |  |  | 1.13 |  | 0.76 | [8 empty] | 32.84 |  |  |  |  | 1.68
1993 |  |  |  | 4384.85 |  |  | 7125 |  |  |  | 622 | [10 empty] | 79.59 |  |  |  | 91.61 | [5 empty] | 80.62 |  |  | 81.56 |  |  |  | 1.63 |  | 1.52 | [8 empty] | 6.88 |  |  |  |  | 12.02
1994 |  |  |  | 4435.32 |  |  | 7723 |  |  |  | 625 | [10 empty] | 80.75 |  |  |  | 83.96 | [5 empty] | 81.23 |  |  | 88.40 |  |  |  | 7.89 |  | 7.19 | [8 empty] | 8.85 |  |  |  |  | 3.21
1995 |  |  |  | 4498.83 |  |  | 7249 |  |  |  | 625 | [10 empty] | 82.30 |  |  |  | 82.22 | [5 empty] | 81.95 |  |  | 82.53 |  |  |  | 7.24 |  | 6.41 | [8 empty] | 11.37 |  |  |  |  | -0.08
1996 |  |  |  | 4265.35 |  |  | 7103 |  |  |  | 625 | [10 empty] | 78.39 |  |  |  | 78.58 | [5 empty] | 77.69 |  |  | 80.86 |  |  |  | 13.73 |  | 12.50 | [8 empty] | 8.92 |  |  |  |  | 0.19
1997 |  |  |  | 4780.70 |  |  | 8021 |  |  |  | 625 | [10 empty] | 85.46 |  |  |  | 87.35 | [5 empty] | 87.08 |  |  | 91.31 |  |  |  | 1.26 |  | 1.12 | [8 empty] | 11.53 |  |  |  |  | 1.89
1998 |  |  |  | 4209.73 |  |  | 7574 |  |  |  | 625 | [10 empty] | 76.15 |  |  |  | 76.95 | [5 empty] | 76.68 |  |  | 86.22 |  |  |  | 6.77 |  | 5.59 | [8 empty] | 17.46 |  |  |  |  | 0.80
1999 |  |  |  | 2987.21 |  |  | 4987 |  |  |  | 625 | [10 empty] | 54.59 |  |  |  | 54.69 | [5 empty] | 54.41 |  |  | 56.77 |  |  |  | 44.43 |  | 43.72 | [8 empty] | 1.59 |  |  |  |  | 0.09
2000 |  |  |  | 5001.88 |  |  | 8660 |  |  |  | 625 | [10 empty] | 90.49 |  |  |  | 91.11 | [5 empty] | 91.11 |  |  | 98.59 |  |  |  | 3.12 |  | 2.94 | [8 empty] | 5.95 |  |  |  |  | 0.62
2001 |  |  |  | 4234.22 |  |  | 7103 |  |  |  | 625 | [10 empty] | 90.80 |  |  |  | 91.44 | [5 empty] | 77.13 |  |  | 80.86 |  |  |  | 4.46 |  | 4.27 | [8 empty] | 4.29 |  |  |  |  | 0.63
2002 |  |  |  | 5010.34 |  |  | 8521 |  |  |  | 625 | [10 empty] | 91.53 |  |  |  | 91.53 | [5 empty] | 91.51 |  |  | 97.27 |  |  |  | 3.78 |  | 3.87 | [8 empty] | 4.60 |  |  |  |  | 0.00
2003 |  |  |  | 4582.83 |  |  | 7712 |  |  |  | 625 | [10 empty] | 83.75 |  |  |  | 83.91 | [5 empty] | 83.70 |  |  | 88.04 |  |  |  | 14.27 |  | 14.06 | [8 empty] | 2.04 |  |  |  |  | 0.15
2004 |  |  |  | 4244.16 |  |  | 7383 |  |  |  | 625 | [10 empty] | 77.48 |  |  |  | 77.48 | [5 empty] | 77.31 |  |  | 84.05 |  |  |  | 7.02 |  | 7.63 | [8 empty] | 14.89 |  |  |  |  | 0.00
2005 |  |  |  | 5056.80 |  |  | 8564 |  |  |  | 625 | [10 empty] | 92.32 |  |  |  | 92.32 | [5 empty] | 92.36 |  |  | 97.76 |  |  |  | 3.29 |  | 3.21 | [8 empty] | 4.47 |  |  |  |  | 0.00
2006 |  |  |  | 4816.70 |  |  | 8293 |  |  |  | 625 | [10 empty] | 89.08 |  |  |  | 89.08 | [5 empty] | 89.05 |  |  | 94.67 |  |  |  | 4.91 |  | 4.79 | [8 empty] | 6.14 |  |  |  |  | 0.00
2007 |  |  |  | 4046.74 |  |  | 7104 |  |  |  | 615 | [10 empty] | 74.92 |  |  |  | 74.92 | [5 empty] | 75.11 |  |  | 81.10 |  |  |  | 3.81 |  | 5.74 | [8 empty] | 19.34 |  |  |  |  | 0.00
2008 |  |  |  | 4709.31 |  |  | 8252 |  |  |  | 620 | [10 empty] | 86.70 |  |  |  | 86.71 | [5 empty] | 86.65 |  |  | 93.94 |  |  |  | 9.64 |  | 9.82 | [8 empty] | 3.47 |  |  |  |  | 0.01
2009 |  |  |  | 4012.10 |  |  | 7268 |  |  |  | 620 | [10 empty] | 74.22 |  |  |  | 76.77 | [5 empty] | 73.87 |  |  | 82.97 |  |  |  | 15.69 |  | 16.80 | [8 empty] | 6.43 |  |  |  |  | 2.55
2010 |  |  |  | 1437.40 |  |  | 2719 |  |  |  | 620 | [10 empty] | 27.24 |  |  |  | 27.24 | [5 empty] | 26.47 |  |  | 31.04 |  |  |  | 12.02 |  | 56.55 | [8 empty] | 16.21 |  |  |  |  | 0.00
2011 |  |  |  | 4545.68 |  |  | 7968 |  |  |  | 605 | [10 empty] | 84.99 |  |  |  | 84.99 | [5 empty] | 85.77 |  |  | 90.96 |  |  |  | 11.75 |  | 11.39 | [8 empty] | 3.62 |  |  |  |  | 0.00
2012 |  |  |  | 5214.03 |  |  | 8784 |  |  |  | 610 | [10 empty] | 95.80 |  |  |  | 95.86 | [5 empty] | 97.31 |  |  | 100.00 |  |  |  | 0.15 |  | 0.42 | [8 empty] | 3.72 |  |  |  |  | 0.06
2013 |  |  |  | 4057.17 |  |  | 6945 |  |  |  | 610 | [10 empty] | 75.17 |  |  |  | 75.17 | [5 empty] | 75.93 |  |  | 79.28 |  |  |  | 1.42 |  | 1.20 | [8 empty] | 23.63 |  |  |  |  | 0.00
2014 |  |  |  | 5211.77 |  |  | 8713 |  |  |  | 610 | [10 empty] | 95.26 |  |  |  | 95.26 | [5 empty] | 97.53 |  |  | 99.46 |  |  |  | 0.80 |  | 0.77 | [8 empty] | 3.97 |  |  |  |  | 0.00
2015 |  |  |  | 5249.04 |  |  | 8760 |  |  |  | 615 | [10 empty] | 96.20 |  |  |  | 96.27 | [5 empty] | 97.43 |  |  | 100.00 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 3.65 |  |  |  |  | 0.07
2016 |  |  |  | 4319.05 |  |  | 7214 | [14 empty] | 79.08 |  |  |  | 79.09 | [5 empty] | 79.95 |  |  | 82.13 |  |  |  | 0.58 |  | 0.46 | [8 empty] | 20.45 |  |  |  |  | 0.01
2017 |  |  |  | 0.00 | [17 empty] | 95.49 |  |  |  | 95.56 | [5 empty] | 96.19 |  |  | 100.00 |  |  |  | 0.24 |  | 0.56 | [8 empty] | 3.88 |  |  |  |  | 0.07
2018 |  |  |  | 5116.17 |  |  | 8624 |  |  |  | 620 | [10 empty] | 94.20 |  |  |  | 94.50 | [5 empty] | 94.20 |  |  | 98.45 |  |  |  | 1.79 |  | 1.80 | [8 empty] | 3.70 |  |  |  |  | 0.30
2019 |  |  |  | 5042.29 |  |  | 8635 |  |  |  | 620 | [10 empty] | 92.82 |  |  |  | 93.07 | [5 empty] | 92.84 |  |  | 98.57 |  |  |  | 2.28 |  | 2.57 | [8 empty] | 4.37 |  |  |  |  | 0.25
2020 |  |  |  | 3948.62 |  |  | 6782 |  |  |  | 620 | [10 empty] | 72.85 |  |  |  | 73.05 | [5 empty] | 72.50 |  |  | 77.21 |  |  |  | 3.60 |  | 7.35 | [8 empty] | 19.61 |  |  |  |  | 0.20
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 522 | [14 empty] | 505
B. |  | Refuelling without maintenance | [35 empty] | 8 |  |  |  | 5
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1580 | [14 empty] | 646 |  |  |  | 15
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 209
E. |  | Testing of plant systems or components | [39 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 29
L. |  | Human factor related | [39 empty] | 6
P. |  | Fire | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 15
Z. |  | Other | [51 empty] | 34
Subtotal | [22 empty] | 1580 |  |  |  | 522 | [10 empty] | 878 |  |  |  | 539 | [11 empty] | 63
Total | [22 empty] | 2102 | [14 empty] | 1480
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 100 | [14 empty] | 19
12. |  |  | Reactor I&C Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 1
16. |  |  | Steam generation systems | [34 empty] | 15
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 204
32. |  |  | Feedwater and Main Steam System | [19 empty] | 49 | [14 empty] | 32
33. |  |  | Circulating Water System | [34 empty] | 140
41. |  |  | Main Generator Systems | [19 empty] | 374 | [14 empty] | 84
42. |  |  | Electrical Power Supply Systems | [34 empty] | 10
Total | [22 empty] | 523 | [14 empty] | 523

## HINKLEY POINT B-1
2020 Operating Experience
GB-16A | [8 empty] | HINKLEY POINT B-1 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | TNPG (THE NUCLEAR POWER GROUP, LTD.)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-09-01
Thermal power | [12 empty] | : |  |  | 1494 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-10-30
Gross electrical power | [12 empty] | : |  |  | 655 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1978-10-02
Reference unit power (net) | [12 empty] | : |  |  | 485 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.24
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 645.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 15.85
| Active core height/length [m] | [13 empty] | : |  |  | 8.312 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2464 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 81 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 5
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 1275.63 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 27.96 %
Energy Availability Factor (EAF) | [18 empty] | : | 30.9 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 14.89 %
Unit Capability Factor (UCF) | [18 empty] | : | 30.93 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 54.18 %
Load Factor (LF) | [18 empty] | : | 29.94 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.02 %
Operating Factor (OF) | [18 empty] | : | 31.88 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 5984 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 364.89 | 285.58 |  |  |  | -15.85 |  | 225.44 | [8 empty] | 361.65 |  |  | 77.46 | [6 empty] | -4.71 |  | -4.31 |  |  |  | -3.00 |  |  | -2.22 |  |  | -2.09 | [9 empty] | -7.21 |  |  | 1275.63
EAF [%] |  |  |  |  | 100.00 | 84.16 |  |  |  | 0.00 |  | 65.64 | [8 empty] | 99.90 |  |  | 23.43 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 30.90
UCF [%] |  |  |  |  | 100.00 | 84.16 |  |  |  | 0.00 |  | 65.64 | [8 empty] | 100.00 |  |  | 23.63 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 30.93
LF [%] |  |  |  |  | 101.12 | 84.60 |  |  |  | -4.40 |  | 64.56 | [8 empty] | 100.23 |  |  | 22.18 | [6 empty] | -1.30 |  | -1.19 |  |  |  | -0.86 |  |  | -0.62 |  |  | -0.60 | [9 empty] | -2.00 |  |  | 29.94
OF [%] |  |  |  |  | 100.00 | 90.95 |  |  |  | 0.00 |  | 69.58 | [8 empty] | 100.00 |  |  | 24.72 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 31.88
FLR [%] |  |  |  |  | 0.00 | 9.83 |  |  |  | 100.00 |  | 34.36 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 27.96
UCL [%] |  |  |  |  | 0.00 | 9.18 |  |  |  | 100.00 |  | 34.36 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 34.12 |  |  | 14.89
PUF [%] |  |  |  |  | 0.00 | 6.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 76.37 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 65.88 |  |  | 54.18
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.10 |  |  | 0.20 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 147370.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.41 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.81 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.56 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.34 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.1 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.86 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.53 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.43 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1978 |  |  |  | Data not provided
1979 |  |  |  | 3079.80 |  |  | 6646 |  |  |  | 400 | [10 empty] | 73.47 |  |  |  | 79.41 | [5 empty] | 88.14 |  |  | 76.08 |  |  |  | 20.59 |  | 20.59 | [8 empty] | 0.00 |  |  |  |  | 5.94
1980 |  |  |  | 2337.16 |  |  | 5394 |  |  |  | 475 | [10 empty] | 55.37 |  |  |  | 59.86 | [5 empty] | 56.32 |  |  | 61.74 |  |  |  | 5.89 |  | 3.74 | [8 empty] | 36.39 |  |  |  |  | 4.50
1981 |  |  |  | 3441.60 |  |  | 7118 |  |  |  | 520 | [10 empty] | 74.27 |  |  |  | 78.55 | [5 empty] | 74.33 |  |  | 79.94 |  |  |  | 1.70 |  | 1.35 | [8 empty] | 20.10 |  |  |  |  | 4.28
1982 |  |  |  | 2950.76 |  |  | 6000 |  |  |  | 520 | [10 empty] | 65.36 |  |  |  | 67.79 | [5 empty] | 64.96 |  |  | 68.68 |  |  |  | 1.36 |  | 0.94 | [8 empty] | 31.28 |  |  |  |  | 2.42
1983 |  |  |  | 4082.98 |  |  | 8127 |  |  |  | 520 | [10 empty] | 86.62 |  |  |  | 88.31 | [5 empty] | 89.88 |  |  | 93.03 |  |  |  | 4.47 |  | 4.14 | [8 empty] | 7.56 |  |  |  |  | 1.68
1984 |  |  |  | 3408.22 |  |  | 6589 |  |  |  | 520 | [10 empty] | 71.56 |  |  |  | 71.95 | [5 empty] | 75.03 |  |  | 75.42 |  |  |  | 10.11 |  | 8.09 | [8 empty] | 19.96 |  |  |  |  | 0.39
1985 |  |  |  | 4263.02 |  |  | 8167 |  |  |  | 520 | [10 empty] | 82.20 |  |  |  | 82.32 | [5 empty] | 93.84 |  |  | 93.49 |  |  |  | 8.86 |  | 8.00 | [8 empty] | 9.68 |  |  |  |  | 0.11
1986 |  |  |  | 3199.19 |  |  | 6110 |  |  |  | 560 | [10 empty] | 67.24 |  |  |  | 68.17 | [5 empty] | 65.39 |  |  | 69.94 |  |  |  | 4.70 |  | 3.36 | [8 empty] | 28.47 |  |  |  |  | 0.93
1987 |  |  |  | 1837.99 |  |  | 3554 |  |  |  | 560 | [10 empty] | 38.79 |  |  |  | 39.61 | [5 empty] | 36.86 |  |  | 39.91 |  |  |  | 59.65 |  | 58.54 | [8 empty] | 1.85 |  |  |  |  | 0.82
1988 |  |  |  | 2905.41 |  |  | 5370 |  |  |  | 560 | [10 empty] | 59.14 |  |  |  | 59.86 | [5 empty] | 59.39 |  |  | 61.47 |  |  |  | 5.20 |  | 3.28 | [8 empty] | 36.86 |  |  |  |  | 0.73
1989 |  |  |  | 4195.30 |  |  | 7878 |  |  |  | 560 | [10 empty] | 85.50 |  |  |  | 85.64 | [5 empty] | 85.76 |  |  | 90.18 |  |  |  | 1.14 |  | 0.99 | [8 empty] | 13.37 |  |  |  |  | 0.14
1990 |  |  |  | 3101.98 |  |  | 5732 |  |  |  | 560 | [10 empty] | 63.37 |  |  |  | 63.88 | [5 empty] | 63.41 |  |  | 65.61 |  |  |  | 15.37 |  | 11.60 | [8 empty] | 24.51 |  |  |  |  | 0.52
1991 |  |  |  | 4601.89 |  |  | 8430 |  |  |  | 560 | [10 empty] | 94.35 |  |  |  | 94.35 | [5 empty] | 94.07 |  |  | 96.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.65 |  |  |  |  | 0.00
1992 |  |  |  | 3614.47 |  |  | 6565 |  |  |  | 583 | [10 empty] | 69.78 |  |  |  | 70.24 | [5 empty] | 69.54 |  |  | 73.73 |  |  |  | 9.17 |  | 7.09 | [8 empty] | 22.67 |  |  |  |  | 0.46
1993 |  |  |  | 4843.29 |  |  | 8587 |  |  |  | 585 | [10 empty] | 94.56 |  |  |  | 94.79 | [5 empty] | 94.01 |  |  | 97.50 |  |  |  | 2.63 |  | 2.56 | [8 empty] | 2.66 |  |  |  |  | 0.23
1994 |  |  |  | 4126.20 |  |  | 7342 |  |  |  | 585 | [10 empty] | 78.32 |  |  |  | 78.71 | [5 empty] | 80.74 |  |  | 84.04 |  |  |  | 5.05 |  | 4.19 | [8 empty] | 17.10 |  |  |  |  | 0.39
1995 |  |  |  | 4812.46 |  |  | 7910 |  |  |  | 610 | [10 empty] | 89.63 |  |  |  | 90.09 | [5 empty] | 89.81 |  |  | 90.05 |  |  |  | 5.38 |  | 5.13 | [8 empty] | 4.79 |  |  |  |  | 0.46
1996 |  |  |  | 4797.27 |  |  | 8418 |  |  |  | 610 | [10 empty] | 89.74 |  |  |  | 90.25 | [5 empty] | 89.53 |  |  | 95.83 |  |  |  | 5.57 |  | 5.33 | [8 empty] | 4.43 |  |  |  |  | 0.50
1997 |  |  |  | 4185.70 |  |  | 7341 |  |  |  | 610 | [10 empty] | 78.27 |  |  |  | 78.39 | [5 empty] | 78.12 |  |  | 83.57 |  |  |  | 4.69 |  | 3.86 | [8 empty] | 17.75 |  |  |  |  | 0.12
1998 |  |  |  | 4252.57 |  |  | 7740 |  |  |  | 610 | [10 empty] | 80.89 |  |  |  | 79.64 | [5 empty] | 79.37 |  |  | 88.11 |  |  |  | 7.43 |  | 6.39 | [8 empty] | 13.97 |  |  |  |  | -1.26
1999 |  |  |  | 4045.23 |  |  | 7221 |  |  |  | 610 | [10 empty] | 76.98 |  |  |  | 75.77 | [5 empty] | 75.50 |  |  | 82.21 |  |  |  | 21.10 |  | 20.26 | [8 empty] | 3.97 |  |  |  |  | -1.21
2000 |  |  |  | 3850.58 |  |  | 7208 |  |  |  | 610 | [10 empty] | 71.86 |  |  |  | 71.86 | [5 empty] | 71.86 |  |  | 82.06 |  |  |  | 14.66 |  | 12.34 | [8 empty] | 15.80 |  |  |  |  | 0.00
2001 |  |  |  | 4801.96 |  |  | 8545 |  |  |  | 610 | [10 empty] | 86.97 |  |  |  | 86.97 | [5 empty] | 89.62 |  |  | 97.28 |  |  |  | 8.57 |  | 8.16 | [8 empty] | 4.87 |  |  |  |  | 0.00
2002 |  |  |  | 4580.96 |  |  | 8021 |  |  |  | 610 | [10 empty] | 84.96 |  |  |  | 84.98 | [5 empty] | 85.73 |  |  | 91.56 |  |  |  | 6.79 |  | 7.52 | [8 empty] | 7.51 |  |  |  |  | 0.01
2003 |  |  |  | 4076.35 |  |  | 7032 |  |  |  | 610 | [10 empty] | 74.84 |  |  |  | 74.84 | [5 empty] | 76.28 |  |  | 80.27 |  |  |  | 6.49 |  | 9.83 | [8 empty] | 15.34 |  |  |  |  | 0.00
2004 |  |  |  | 4578.71 |  |  | 8091 |  |  |  | 610 | [10 empty] | 84.77 |  |  |  | 84.77 | [5 empty] | 85.45 |  |  | 92.11 |  |  |  | 11.39 |  | 11.01 | [8 empty] | 4.22 |  |  |  |  | 0.00
2005 |  |  |  | 4580.58 |  |  | 8257 |  |  |  | 610 | [10 empty] | 85.23 |  |  |  | 85.23 | [5 empty] | 85.72 |  |  | 94.26 |  |  |  | 5.24 |  | 5.06 | [8 empty] | 9.71 |  |  |  |  | 0.00
2006 |  |  |  | 3370.18 |  |  | 6200 |  |  |  | 610 | [10 empty] | 62.36 |  |  |  | 62.36 | [5 empty] | 62.30 |  |  | 70.78 |  |  |  | 9.67 |  | 14.85 | [8 empty] | 22.79 |  |  |  |  | 0.00
2007 |  |  |  | 1877.41 |  |  | 5204 |  |  |  | 430 | [10 empty] | 45.21 |  |  |  | 45.24 | [5 empty] | 44.94 |  |  | 59.41 |  |  |  | 14.64 |  | 53.62 | [8 empty] | 1.14 |  |  |  |  | 0.03
2008 |  |  |  | 2628.76 |  |  | 6935 |  |  |  | 410 | [10 empty] | 72.77 |  |  |  | 72.77 | [5 empty] | 72.12 |  |  | 78.95 |  |  |  | 16.47 |  | 14.37 | [8 empty] | 12.86 |  |  |  |  | 0.01
2009 |  |  |  | 1931.52 |  |  | 4963 |  |  |  | 410 | [10 empty] | 53.72 |  |  |  | 55.40 | [5 empty] | 53.78 |  |  | 56.66 |  |  |  | 23.30 |  | 19.39 | [8 empty] | 25.21 |  |  |  |  | 1.67
2010 |  |  |  | 3152.41 |  |  | 7411 |  |  |  | 410 | [10 empty] | 81.78 |  |  |  | 81.80 | [5 empty] | 87.77 |  |  | 84.60 |  |  |  | 16.71 |  | 16.46 | [8 empty] | 1.75 |  |  |  |  | 0.01
2011 |  |  |  | 3329.95 |  |  | 7863 |  |  |  | 435 | [10 empty] | 86.79 |  |  |  | 86.79 | [5 empty] | 87.39 |  |  | 89.76 |  |  |  | 11.05 |  | 10.78 | [8 empty] | 2.43 |  |  |  |  | 0.00
2012 |  |  |  | 2793.96 |  |  | 6693 |  |  |  | 435 | [10 empty] | 72.81 |  |  |  | 72.81 | [5 empty] | 73.12 |  |  | 76.20 |  |  |  | 6.36 |  | 8.71 | [8 empty] | 18.49 |  |  |  |  | 0.00
2013 |  |  |  | 3880.00 |  |  | 8553 |  |  |  | 440 | [10 empty] | 94.72 |  |  |  | 94.72 | [5 empty] | 100.66 |  |  | 97.64 |  |  |  | 2.63 |  | 2.75 | [8 empty] | 2.54 |  |  |  |  | 0.00
2014 |  |  |  | 3751.17 |  |  | 7968 |  |  |  | 475 | [10 empty] | 88.19 |  |  |  | 88.19 | [5 empty] | 90.15 |  |  | 90.96 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 11.79 |  |  |  |  | 0.00
2015 |  |  |  | 3989.08 |  |  | 8614 |  |  |  | 480 | [10 empty] | 93.67 |  |  |  | 93.71 | [5 empty] | 94.87 |  |  | 98.33 |  |  |  | 2.48 |  | 2.66 | [8 empty] | 3.63 |  |  |  |  | 0.04
2016 |  |  |  | 3239.17 |  |  | 6928 | [14 empty] | 75.91 |  |  |  | 75.91 | [5 empty] | 76.82 |  |  | 78.87 |  |  |  | 7.28 |  | 5.96 | [8 empty] | 18.13 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 | [17 empty] | 89.47 |  |  |  | 89.52 | [5 empty] | 90.60 |  |  | 91.94 |  |  |  | 4.23 |  | 3.95 | [8 empty] | 6.52 |  |  |  |  | 0.05
2018 |  |  |  | 3863.64 |  |  | 8305 |  |  |  | 485 | [10 empty] | 90.64 |  |  |  | 91.13 | [5 empty] | 90.94 |  |  | 94.81 |  |  |  | 1.34 |  | 1.24 | [8 empty] | 7.63 |  |  |  |  | 0.49
2019 |  |  |  | 2963.04 |  |  | 6427 |  |  |  | 485 | [10 empty] | 70.24 |  |  |  | 70.56 | [5 empty] | 69.74 |  |  | 73.37 |  |  |  | 4.24 |  | 5.36 | [8 empty] | 24.08 |  |  |  |  | 0.32
2020 |  |  |  | 1275.63 |  |  | 2800 |  |  |  | 485 | [10 empty] | 30.90 |  |  |  | 30.93 | [5 empty] | 29.94 |  |  | 31.88 |  |  |  | 27.96 |  | 14.89 | [8 empty] | 54.18 |  |  |  |  | 0.02
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1978 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 1025 | [14 empty] | 485
B. |  | Refuelling without maintenance | [35 empty] | 1
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 251 |  |  |  | 21
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 4704 | [14 empty] | 537
E. |  | Testing of plant systems or components | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 19
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 3
Z. |  | Other | [24 empty] | 254 | [10 empty] | 1 |  |  |  | 7 | [11 empty] | 1
Subtotal | [22 empty] | 4704 |  |  |  | 1279 | [10 empty] | 790 |  |  |  | 533 | [11 empty] | 7
Total | [22 empty] | 5983 | [14 empty] | 1330
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1978 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 254 | [14 empty] | 15
12. |  |  | Reactor I&C Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 7
16. |  |  | Steam generation systems | [34 empty] | 114
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [19 empty] | 1025 | [14 empty] | 24
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 6
31. |  |  | Turbine and auxiliaries | [34 empty] | 142
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
41. |  |  | Main Generator Systems | [34 empty] | 80
42. |  |  | Electrical Power Supply Systems | [34 empty] | 88
Total | [22 empty] | 1279 | [14 empty] | 503
Highlights (2020)
Shut down in June for a graphite core inspection and remains off pending a return to service safety case

## HINKLEY POINT B-2
2020 Operating Experience
GB-16B | [8 empty] | HINKLEY POINT B-2 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | TNPG (THE NUCLEAR POWER GROUP, LTD.)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-09-01
Thermal power | [12 empty] | : |  |  | 1494 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-02-05
Gross electrical power | [12 empty] | : |  |  | 655 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-09-27
Reference unit power (net) | [12 empty] | : |  |  | 480 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.24
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 645.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 16
| Active core height/length [m] | [13 empty] | : |  |  | 8.312 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2464 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 81 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 5
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 500.91 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 13.57 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 78.1 %
Unit Capability Factor (UCF) | [18 empty] | : | 13.57 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.33 %
Load Factor (LF) | [18 empty] | : | 11.88 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 14.18 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 7538 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 335.88 | 234.01 |  |  |  | -4.27 |  | -3.83 | [8 empty] | -3.38 |  |  | -9.49 | [6 empty] | -10.63 |  | -10.69 |  |  |  | -9.64 |  |  | -5.59 |  |  | -5.63 | [9 empty] | -5.83 |  |  | 500.91
EAF [%] |  |  |  |  | 94.00 | 70.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.57
UCF [%] |  |  |  |  | 94.00 | 70.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.57
LF [%] |  |  |  |  | 94.05 | 70.05 |  |  |  | -1.20 |  | -1.11 | [8 empty] | -0.95 |  |  | -2.75 | [6 empty] | -2.98 |  | -2.99 |  |  |  | -2.79 |  |  | -1.56 |  |  | -1.63 | [9 empty] | -1.63 |  |  | 11.88
OF [%] |  |  |  |  | 100.00 | 72.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 14.18
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 34.94 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.10
PUF [%] |  |  |  |  | 6.00 | 29.28 |  |  |  | 65.06 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.33
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 143677.63 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.77 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.22 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.58 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.54 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.93 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.28 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | Data not provided
1977 |  |  |  | 1044.00 |  |  | 2756 |  |  |  | 400 | [10 empty] | 74.58 |  |  |  | 74.58 | [5 empty] | 29.88 |  |  | 31.55 |  |  |  | 23.23 |  | 22.56 | [8 empty] | 2.86 |  |  |  |  | 0.00
1978 |  |  |  | Data not provided
1979 |  |  |  | 1499.67 |  |  | 3512 |  |  |  | 400 | [10 empty] | 38.16 |  |  |  | 43.97 | [5 empty] | 42.92 |  |  | 40.20 |  |  |  | 4.51 |  | 2.08 | [8 empty] | 53.96 |  |  |  |  | 5.81
1980 |  |  |  | 3008.94 |  |  | 6390 |  |  |  | 475 | [10 empty] | 69.31 |  |  |  | 71.35 | [5 empty] | 72.51 |  |  | 73.15 |  |  |  | 9.08 |  | 7.13 | [8 empty] | 21.53 |  |  |  |  | 2.04
1981 |  |  |  | 2488.82 |  |  | 5054 |  |  |  | 520 | [10 empty] | 54.68 |  |  |  | 57.09 | [5 empty] | 53.75 |  |  | 56.76 |  |  |  | 20.99 |  | 15.16 | [8 empty] | 27.75 |  |  |  |  | 2.41
1982 |  |  |  | 3155.05 |  |  | 6834 |  |  |  | 520 | [10 empty] | 69.75 |  |  |  | 73.64 | [5 empty] | 69.45 |  |  | 78.23 |  |  |  | 16.51 |  | 14.56 | [8 empty] | 11.80 |  |  |  |  | 3.89
1983 |  |  |  | 3454.48 |  |  | 6839 |  |  |  | 520 | [10 empty] | 74.14 |  |  |  | 75.59 | [5 empty] | 76.04 |  |  | 78.29 |  |  |  | 3.14 |  | 2.45 | [8 empty] | 21.95 |  |  |  |  | 1.45
1984 |  |  |  | 4393.54 |  |  | 8228 |  |  |  | 520 | [10 empty] | 89.39 |  |  |  | 89.56 | [5 empty] | 96.72 |  |  | 94.18 |  |  |  | 5.95 |  | 5.67 | [8 empty] | 4.77 |  |  |  |  | 0.17
1985 |  |  |  | 3229.92 |  |  | 5950 |  |  |  | 520 | [10 empty] | 66.72 |  |  |  | 66.73 | [5 empty] | 71.10 |  |  | 68.11 |  |  |  | 6.71 |  | 4.80 | [8 empty] | 28.48 |  |  |  |  | 0.00
1986 |  |  |  | 3497.25 |  |  | 7257 |  |  |  | 560 | [10 empty] | 75.11 |  |  |  | 81.23 | [5 empty] | 72.48 |  |  | 84.23 |  |  |  | 13.47 |  | 12.64 | [8 empty] | 6.13 |  |  |  |  | 6.12
1987 |  |  |  | 2971.07 |  |  | 6333 |  |  |  | 560 | [10 empty] | 60.64 |  |  |  | 68.32 | [5 empty] | 59.59 |  |  | 71.13 |  |  |  | 5.34 |  | 3.85 | [8 empty] | 27.83 |  |  |  |  | 7.68
1988 |  |  |  | 4268.17 |  |  | 8467 |  |  |  | 560 | [10 empty] | 86.64 |  |  |  | 91.11 | [5 empty] | 87.25 |  |  | 96.92 |  |  |  | 4.05 |  | 3.85 | [8 empty] | 5.05 |  |  |  |  | 4.47
1989 |  |  |  | 2484.57 |  |  | 4896 |  |  |  | 560 | [10 empty] | 65.35 |  |  |  | 65.59 | [5 empty] | 50.79 |  |  | 56.04 |  |  |  | 0.44 |  | 0.29 | [8 empty] | 34.11 |  |  |  |  | 0.24
1990 |  |  |  | 4463.54 |  |  | 8565 |  |  |  | 560 | [10 empty] | 91.24 |  |  |  | 92.36 | [5 empty] | 91.24 |  |  | 98.04 |  |  |  | 1.75 |  | 1.65 | [8 empty] | 5.99 |  |  |  |  | 1.12
1991 |  |  |  | 2353.52 |  |  | 4432 |  |  |  | 560 | [10 empty] | 57.40 |  |  |  | 57.40 | [5 empty] | 48.11 |  |  | 50.73 |  |  |  | 17.01 |  | 11.76 | [8 empty] | 30.84 |  |  |  |  | 0.00
1992 |  |  |  | 3901.97 |  |  | 7225 |  |  |  | 583 | [10 empty] | 76.27 |  |  |  | 76.60 | [5 empty] | 75.07 |  |  | 81.14 |  |  |  | 21.22 |  | 20.63 | [8 empty] | 2.76 |  |  |  |  | 0.33
1993 |  |  |  | 3743.03 |  |  | 6575 |  |  |  | 597 | [10 empty] | 71.38 |  |  |  | 71.72 | [5 empty] | 71.71 |  |  | 75.26 |  |  |  | 11.07 |  | 8.93 | [8 empty] | 19.35 |  |  |  |  | 0.34
1994 |  |  |  | 4852.23 |  |  | 8602 |  |  |  | 610 | [10 empty] | 91.08 |  |  |  | 91.51 | [5 empty] | 91.05 |  |  | 98.47 |  |  |  | 3.05 |  | 2.88 | [8 empty] | 5.60 |  |  |  |  | 0.43
1995 |  |  |  | 4518.09 |  |  | 7411 |  |  |  | 610 | [10 empty] | 84.59 |  |  |  | 84.59 | [5 empty] | 84.32 |  |  | 84.37 |  |  |  | 10.90 |  | 10.35 | [8 empty] | 5.06 |  |  |  |  | 0.00
1996 |  |  |  | 3119.85 |  |  | 5615 |  |  |  | 610 | [10 empty] | 59.14 |  |  |  | 58.94 | [5 empty] | 58.23 |  |  | 63.92 |  |  |  | 16.82 |  | 11.92 | [8 empty] | 29.14 |  |  |  |  | -0.20
1997 |  |  |  | 4512.87 |  |  | 7958 |  |  |  | 610 | [10 empty] | 84.95 |  |  |  | 84.50 | [5 empty] | 84.22 |  |  | 90.60 |  |  |  | 11.86 |  | 11.37 | [8 empty] | 4.13 |  |  |  |  | -0.45
1998 |  |  |  | 4738.89 |  |  | 8641 |  |  |  | 610 | [10 empty] | 88.34 |  |  |  | 88.71 | [5 empty] | 88.44 |  |  | 98.37 |  |  |  | 5.34 |  | 5.01 | [8 empty] | 6.28 |  |  |  |  | 0.38
1999 |  |  |  | 4082.29 |  |  | 7402 |  |  |  | 610 | [10 empty] | 75.83 |  |  |  | 76.90 | [5 empty] | 76.19 |  |  | 84.27 |  |  |  | 5.45 |  | 4.43 | [8 empty] | 18.67 |  |  |  |  | 1.08
2000 |  |  |  | 4189.37 |  |  | 7851 |  |  |  | 610 | [10 empty] | 78.90 |  |  |  | 78.90 | [5 empty] | 78.19 |  |  | 89.38 |  |  |  | 15.92 |  | 14.94 | [8 empty] | 6.16 |  |  |  |  | 0.00
2001 |  |  |  | 4772.43 |  |  | 8406 |  |  |  | 610 | [10 empty] | 84.12 |  |  |  | 84.12 | [5 empty] | 89.07 |  |  | 95.70 |  |  |  | 7.28 |  | 6.60 | [8 empty] | 9.28 |  |  |  |  | 0.00
2002 |  |  |  | 3257.33 |  |  | 6163 |  |  |  | 610 | [10 empty] | 61.23 |  |  |  | 61.23 | [5 empty] | 60.96 |  |  | 70.35 |  |  |  | 24.50 |  | 21.58 | [8 empty] | 17.19 |  |  |  |  | 0.00
2003 |  |  |  | 4619.46 |  |  | 8575 |  |  |  | 610 | [10 empty] | 86.52 |  |  |  | 86.52 | [5 empty] | 86.45 |  |  | 97.89 |  |  |  | 8.89 |  | 8.44 | [8 empty] | 5.03 |  |  |  |  | 0.00
2004 |  |  |  | 4150.52 |  |  | 8163 |  |  |  | 610 | [10 empty] | 77.73 |  |  |  | 77.73 | [5 empty] | 77.46 |  |  | 92.93 |  |  |  | 13.83 |  | 13.25 | [8 empty] | 9.02 |  |  |  |  | 0.00
2005 |  |  |  | 3357.19 |  |  | 6544 |  |  |  | 610 | [10 empty] | 63.28 |  |  |  | 63.28 | [5 empty] | 62.83 |  |  | 74.70 |  |  |  | 10.01 |  | 8.79 | [8 empty] | 27.94 |  |  |  |  | 0.00
2006 |  |  |  | 3132.91 |  |  | 6051 |  |  |  | 610 | [10 empty] | 59.78 |  |  |  | 61.46 | [5 empty] | 59.36 |  |  | 69.08 |  |  |  | 31.08 |  | 32.37 | [8 empty] | 6.17 |  |  |  |  | 1.68
2007 |  |  |  | 1812.88 |  |  | 4806 |  |  |  | 430 | [10 empty] | 44.04 |  |  |  | 44.04 | [5 empty] | 43.85 |  |  | 54.86 |  |  |  | 55.44 |  | 54.78 | [8 empty] | 1.18 |  |  |  |  | 0.00
2008 |  |  |  | 2709.85 |  |  | 6821 |  |  |  | 410 | [10 empty] | 74.06 |  |  |  | 74.06 | [5 empty] | 74.34 |  |  | 77.65 |  |  |  | 3.13 |  | 2.54 | [8 empty] | 23.41 |  |  |  |  | 0.00
2009 |  |  |  | 3016.26 |  |  | 7268 |  |  |  | 430 | [10 empty] | 79.63 |  |  |  | 79.63 | [5 empty] | 81.00 |  |  | 82.97 |  |  |  | 18.39 |  | 18.10 | [8 empty] | 2.27 |  |  |  |  | 0.00
2010 |  |  |  | 3263.25 |  |  | 7693 |  |  |  | 430 | [10 empty] | 84.78 |  |  |  | 84.80 | [5 empty] | 86.63 |  |  | 87.82 |  |  |  | 4.37 |  | 6.62 | [8 empty] | 8.58 |  |  |  |  | 0.02
2011 |  |  |  | 2746.32 |  |  | 6580 |  |  |  | 435 | [10 empty] | 72.05 |  |  |  | 72.05 | [5 empty] | 72.07 |  |  | 75.11 |  |  |  | 6.03 |  | 7.58 | [8 empty] | 20.37 |  |  |  |  | 0.00
2012 |  |  |  | 3480.49 |  |  | 8264 |  |  |  | 435 | [10 empty] | 90.43 |  |  |  | 90.43 | [5 empty] | 91.09 |  |  | 94.08 |  |  |  | 5.41 |  | 6.85 | [8 empty] | 2.72 |  |  |  |  | 0.00
2013 |  |  |  | 3651.26 |  |  | 8196 |  |  |  | 440 | [10 empty] | 90.52 |  |  |  | 90.52 | [5 empty] | 94.73 |  |  | 93.56 |  |  |  | 0.66 |  | 0.63 | [8 empty] | 8.85 |  |  |  |  | 0.00
2014 |  |  |  | 4091.01 |  |  | 8760 |  |  |  | 470 | [10 empty] | 96.73 |  |  |  | 96.73 | [5 empty] | 99.36 |  |  | 100.00 |  |  |  | 0.02 |  | 0.17 | [8 empty] | 3.10 |  |  |  |  | 0.00
2015 |  |  |  | 3113.74 |  |  | 6722 |  |  |  | 475 | [10 empty] | 73.96 |  |  |  | 73.96 | [5 empty] | 74.83 |  |  | 76.74 |  |  |  | 0.00 |  | 1.52 | [8 empty] | 24.51 |  |  |  |  | 0.00
2016 |  |  |  | 4022.36 |  |  | 8649 | [14 empty] | 95.04 |  |  |  | 95.04 | [5 empty] | 96.40 |  |  | 98.46 |  |  |  | 1.83 |  | 1.78 | [8 empty] | 3.18 |  |  |  |  | 0.00
2017 |  |  |  | 3485.07 |  |  | 7509 | [14 empty] | 83.14 |  |  |  | 83.24 | [5 empty] | 83.76 |  |  | 85.72 |  |  |  | 11.29 |  | 10.59 | [8 empty] | 6.17 |  |  |  |  | 0.10
2018 |  |  |  | 3379.89 |  |  | 7222 |  |  |  | 480 | [10 empty] | 80.15 |  |  |  | 80.46 | [5 empty] | 80.38 |  |  | 82.44 |  |  |  | 0.31 |  | 1.92 | [8 empty] | 17.62 |  |  |  |  | 0.31
2019 |  |  |  | 3983.59 |  |  | 8652 |  |  |  | 480 | [10 empty] | 94.44 |  |  |  | 95.01 | [5 empty] | 94.74 |  |  | 98.77 |  |  |  | 1.58 |  | 1.84 | [8 empty] | 3.15 |  |  |  |  | 0.56
2020 |  |  |  | 500.91 |  |  | 1246 |  |  |  | 480 | [10 empty] | 13.57 |  |  |  | 13.57 | [5 empty] | 11.88 |  |  | 14.18 |  |  |  | 0.00 |  | 78.10 | [8 empty] | 8.33 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1976 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 591
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 235 |  |  |  | 17
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 677 | [14 empty] | 192
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 8
H. |  | Nuclear regulatory requirements | [39 empty] | 47
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 2
Z. |  | Other | [24 empty] | 6861 | [10 empty] | 1 |  |  |  | 168
Subtotal | [22 empty] | 677 |  |  |  | 6861 | [10 empty] | 431 |  |  |  | 833 | [11 empty] | 2
Total | [22 empty] | 7538 | [14 empty] | 1266
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1976 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 6861 | [14 empty] | 195
12. |  |  | Reactor I&C Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 16
16. |  |  | Steam generation systems | [34 empty] | 200
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 6
31. |  |  | Turbine and auxiliaries | [34 empty] | 126
32. |  |  | Feedwater and Main Steam System | [34 empty] | 123
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 53
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [22 empty] | 6861 | [14 empty] | 758
Highlights (2020)
Shut down in February for a graphite core inspection and remains off pending a return to service safety case

## HUNTERSTON B-1
2020 Operating Experience
GB-17A | [8 empty] | HUNTERSTON B-1 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | TNPG (THE NUCLEAR POWER GROUP, LTD.)
Turbine Supplier | [7 empty] | : | PARSONS (C.A.PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-11-01
Thermal power | [12 empty] | : |  |  | 1496 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-02-06
Gross electrical power | [12 empty] | : |  |  | 644 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-02-06
Reference unit power (net) | [12 empty] | : |  |  | 490 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.24
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 648.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.11 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 16.28
| Active core height/length [m] | [13 empty] | : |  |  | 8.312 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2464 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 81 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 5
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 1253.87 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 31.2 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 67.59 %
Unit Capability Factor (UCF) | [18 empty] | : | 31.25 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 1.16 %
Load Factor (LF) | [18 empty] | : | 29.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.05 %
Operating Factor (OF) | [18 empty] | : | 33.62 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 5831 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | -8.81 | -10.63 |  |  |  | -13.53 |  | -7.16 | [8 empty] | -15.00 |  |  | -9.32 | [6 empty] | -9.35 |  | -13.63 |  |  |  | 317.86 |  |  | 341.01 |  |  | 353.04 | [9 empty] | 329.39 |  |  | 1253.87
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.94 |  |  |  | 89.98 |  |  | 93.24 |  |  | 99.91 | [9 empty] | 90.24 |  |  | 31.20
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.94 |  |  |  | 90.03 |  |  | 93.33 |  |  | 100.00 | [9 empty] | 90.64 |  |  | 31.25
LF [%] |  |  |  |  | -2.42 | -3.12 |  |  |  | -3.72 |  | -2.03 | [8 empty] | -4.12 |  |  | -2.64 | [6 empty] | -2.56 |  | -3.74 |  |  |  | 90.10 |  |  | 93.42 |  |  | 100.07 | [9 empty] | 90.35 |  |  | 29.13
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 3.23 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 33.62
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.06 |  |  |  | 9.97 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 2.37 |  |  | 67.59
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 6.67 |  |  | 0.00 | [9 empty] | 7.00 |  |  | 1.16
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.05 |  |  | 0.10 |  |  | 0.09 | [9 empty] | 0.39 |  |  | 0.05
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 141872.73 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.8 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 69.39 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 15.24 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 69.67 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.09 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 68.46 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.28 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.63 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | 1349.00 |  |  | 4293 |  |  |  | 459 | [10 empty] | 35.97 |  |  |  | 35.97 | [5 empty] | 35.70 |  |  | 52.15 |  |  |  | 45.70 |  | 30.26 | [8 empty] | 33.77 |  |  |  |  | 0.00
1977 |  |  |  | 1709.20 |  |  | 4313 |  |  |  | 500 | [10 empty] | 40.07 |  |  |  | 40.07 | [5 empty] | 39.13 |  |  | 49.37 |  |  |  | 31.14 |  | 18.12 | [8 empty] | 41.81 |  |  |  |  | 0.00
1978 |  |  |  | 2158.40 |  |  | 5375 |  |  |  | 500 | [10 empty] | 49.37 |  |  |  | 49.37 | [5 empty] | 49.41 |  |  | 61.53 |  |  |  | 22.27 |  | 14.14 | [8 empty] | 36.49 |  |  |  |  | 0.00
1979 |  |  |  | 2250.00 |  |  | 5259 |  |  |  | 500 | [10 empty] | 52.25 |  |  |  | 52.25 | [5 empty] | 51.51 |  |  | 60.20 |  |  |  | 21.61 |  | 14.41 | [8 empty] | 33.34 |  |  |  |  | 0.00
1980 |  |  |  | 1486.00 |  |  | 3750 |  |  |  | 500 | [10 empty] | 34.44 |  |  |  | 34.44 | [5 empty] | 34.02 |  |  | 42.93 |  |  |  | 52.72 |  | 38.40 | [8 empty] | 27.15 |  |  |  |  | 0.00
1981 |  |  |  | 1794.80 |  |  | 3941 |  |  |  | 500 | [10 empty] | 40.77 |  |  |  | 40.77 | [5 empty] | 40.31 |  |  | 44.26 |  |  |  | 59.23 |  | 59.23 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 3484.10 |  |  | 7408 |  |  |  | 515 | [10 empty] | 77.27 |  |  |  | 77.27 | [5 empty] | 77.43 |  |  | 84.79 |  |  |  | 21.45 |  | 21.10 | [8 empty] | 1.62 |  |  |  |  | 0.00
1983 |  |  |  | 2912.00 |  |  | 6107 |  |  |  | 520 | [10 empty] | 63.13 |  |  |  | 63.13 | [5 empty] | 64.10 |  |  | 69.91 |  |  |  | 16.91 |  | 12.85 | [8 empty] | 24.02 |  |  |  |  | 0.00
1984 |  |  |  | 4214.00 |  |  | 8080 |  |  |  | 550 | [10 empty] | 85.45 |  |  |  | 85.45 | [5 empty] | 87.70 |  |  | 92.49 |  |  |  | 6.87 |  | 6.30 | [8 empty] | 8.25 |  |  |  |  | 0.00
1985 |  |  |  | 3644.20 |  |  | 6655 |  |  |  | 575 | [10 empty] | 71.06 |  |  |  | 71.06 | [5 empty] | 72.55 |  |  | 76.18 |  |  |  | 7.42 |  | 5.69 | [8 empty] | 23.25 |  |  |  |  | 0.00
1986 |  |  |  | 4571.20 |  |  | 8268 |  |  |  | 575 | [10 empty] | 89.12 |  |  |  | 89.12 | [5 empty] | 91.00 |  |  | 94.64 |  |  |  | 5.33 |  | 5.01 | [8 empty] | 5.87 |  |  |  |  | 0.00
1987 |  |  |  | 3268.40 |  |  | 6358 |  |  |  | 575 | [10 empty] | 63.73 |  |  |  | 63.73 | [5 empty] | 63.84 |  |  | 71.41 |  |  |  | 6.88 |  | 4.71 | [8 empty] | 31.57 |  |  |  |  | 0.00
1988 |  |  |  | 4492.30 |  |  | 8568 |  |  |  | 575 | [10 empty] | 89.25 |  |  |  | 89.25 | [5 empty] | 89.43 |  |  | 98.08 |  |  |  | 3.92 |  | 3.65 | [8 empty] | 7.11 |  |  |  |  | 0.00
1989 |  |  |  | 2959.70 |  |  | 5467 |  |  |  | 575 | [10 empty] | 58.22 |  |  |  | 58.22 | [5 empty] | 58.92 |  |  | 62.58 |  |  |  | 5.01 |  | 3.07 | [8 empty] | 38.71 |  |  |  |  | 0.00
1990 |  |  |  | 4744.10 |  |  | 8585 |  |  |  | 575 | [10 empty] | 92.66 |  |  |  | 92.66 | [5 empty] | 94.44 |  |  | 98.27 |  |  |  | 0.78 |  | 0.72 | [8 empty] | 6.61 |  |  |  |  | 0.00
1991 |  |  |  | 2033.80 |  |  | 3827 |  |  |  | 575 | [10 empty] | 40.12 |  |  |  | 40.12 | [5 empty] | 40.49 |  |  | 43.81 |  |  |  | 4.42 |  | 1.86 | [8 empty] | 58.02 |  |  |  |  | 0.00
1992 |  |  |  | 4315.70 |  |  | 8771 |  |  |  | 575 | [10 empty] | 84.40 |  |  |  | 92.03 | [5 empty] | 84.29 |  |  | 98.51 |  |  |  | 1.74 |  | 1.63 | [8 empty] | 6.34 |  |  |  |  | 7.63
1993 |  |  |  | 2928.90 |  |  | 5581 |  |  |  | 575 | [10 empty] | 58.25 |  |  |  | 59.48 | [5 empty] | 58.31 |  |  | 63.89 |  |  |  | 6.86 |  | 4.38 | [8 empty] | 36.14 |  |  |  |  | 1.23
1994 |  |  |  | 4698.10 |  |  | 8545 |  |  |  | 582 | [10 empty] | 92.42 |  |  |  | 92.84 | [5 empty] | 92.31 |  |  | 97.81 |  |  |  | 0.62 |  | 0.58 | [8 empty] | 6.59 |  |  |  |  | 0.41
1995 |  |  |  | 3829.98 |  |  | 6917 |  |  |  | 585 | [10 empty] | 74.23 |  |  |  | 74.23 | [5 empty] | 72.49 |  |  | 76.58 |  |  |  | 2.68 |  | 2.05 | [8 empty] | 23.72 |  |  |  |  | 0.00
1996 |  |  |  | 1643.70 |  |  | 2839 |  |  |  | 585 | [10 empty] | 98.49 |  |  |  | 98.49 | [5 empty] | 31.99 |  |  | 32.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.51 |  |  |  |  | 0.00
1997 |  |  |  | 3833.99 |  |  | 7035 |  |  |  | 595 | [10 empty] | 73.63 |  |  |  | 73.63 | [5 empty] | 73.36 |  |  | 80.09 |  |  |  | 6.49 |  | 5.11 | [8 empty] | 21.26 |  |  |  |  | 0.00
1998 |  |  |  | 4835.44 |  |  | 8584 |  |  |  | 595 | [10 empty] | 92.79 |  |  |  | 92.79 | [5 empty] | 92.52 |  |  | 97.72 |  |  |  | 3.65 |  | 3.52 | [8 empty] | 3.69 |  |  |  |  | 0.00
1999 |  |  |  | 4811.50 |  |  | 8591 |  |  |  | 595 | [10 empty] | 92.33 |  |  |  | 92.33 | [5 empty] | 92.06 |  |  | 97.80 |  |  |  | 2.79 |  | 2.65 | [8 empty] | 5.01 |  |  |  |  | 0.00
2000 |  |  |  | 4035.56 |  |  | 7497 |  |  |  | 595 | [10 empty] | 77.21 |  |  |  | 77.21 | [5 empty] | 77.21 |  |  | 85.35 |  |  |  | 10.03 |  | 8.61 | [8 empty] | 14.18 |  |  |  |  | 0.00
2001 |  |  |  | 5030.39 |  |  | 8598 |  |  |  | 595 | [10 empty] | 86.64 |  |  |  | 86.64 | [5 empty] | 96.25 |  |  | 97.88 |  |  |  | 8.80 |  | 8.36 | [8 empty] | 5.00 |  |  |  |  | 0.00
2002 |  |  |  | 4678.54 |  |  | 8356 |  |  |  | 595 | [10 empty] | 89.08 |  |  |  | 89.15 | [5 empty] | 89.76 |  |  | 95.39 |  |  |  | 5.36 |  | 5.70 | [8 empty] | 5.15 |  |  |  |  | 0.07
2003 |  |  |  | 3936.46 |  |  | 7225 |  |  |  | 595 | [10 empty] | 74.64 |  |  |  | 74.68 | [5 empty] | 75.52 |  |  | 82.48 |  |  |  | 11.81 |  | 12.47 | [8 empty] | 12.85 |  |  |  |  | 0.04
2004 |  |  |  | 4522.73 |  |  | 8271 |  |  |  | 595 | [10 empty] | 85.56 |  |  |  | 85.77 | [5 empty] | 86.53 |  |  | 94.16 |  |  |  | 10.45 |  | 10.01 | [8 empty] | 4.22 |  |  |  |  | 0.22
2005 |  |  |  | 4096.42 |  |  | 8207 |  |  |  | 595 | [10 empty] | 78.42 |  |  |  | 78.78 | [5 empty] | 78.59 |  |  | 93.69 |  |  |  | 14.36 |  | 13.31 | [8 empty] | 7.91 |  |  |  |  | 0.36
2006 |  |  |  | 1991.38 |  |  | 3838 |  |  |  | 595 | [10 empty] | 37.79 |  |  |  | 37.79 | [5 empty] | 37.49 |  |  | 43.81 |  |  |  | 24.89 |  | 38.39 | [8 empty] | 23.82 |  |  |  |  | 0.00
2007 |  |  |  | 1303.35 |  |  | 4315 |  |  |  | 420 | [10 empty] | 32.49 |  |  |  | 32.49 | [5 empty] | 31.87 |  |  | 49.26 |  |  |  | 37.76 |  | 66.70 | [8 empty] | 0.81 |  |  |  |  | 0.00
2008 |  |  |  | 2213.36 |  |  | 5894 |  |  |  | 410 | [10 empty] | 60.85 |  |  |  | 60.85 | [5 empty] | 61.09 |  |  | 67.10 |  |  |  | 19.07 |  | 19.29 | [8 empty] | 19.86 |  |  |  |  | 0.00
2009 |  |  |  | 2827.96 |  |  | 6969 |  |  |  | 430 | [10 empty] | 73.89 |  |  |  | 73.91 | [5 empty] | 75.95 |  |  | 79.55 |  |  |  | 2.37 |  | 3.08 | [8 empty] | 23.01 |  |  |  |  | 0.02
2010 |  |  |  | 3635.46 |  |  | 8409 |  |  |  | 430 | [10 empty] | 90.52 |  |  |  | 90.53 | [5 empty] | 96.51 |  |  | 95.99 |  |  |  | 5.71 |  | 6.38 | [8 empty] | 3.08 |  |  |  |  | 0.01
2011 |  |  |  | 3382.26 |  |  | 7698 |  |  |  | 460 | [10 empty] | 83.63 |  |  |  | 83.64 | [5 empty] | 83.94 |  |  | 87.88 |  |  |  | 5.87 |  | 6.31 | [8 empty] | 10.05 |  |  |  |  | 0.01
2012 |  |  |  | 3254.96 |  |  | 7350 |  |  |  | 460 | [10 empty] | 79.30 |  |  |  | 79.33 | [5 empty] | 80.56 |  |  | 83.67 |  |  |  | 0.08 |  | 1.50 | [8 empty] | 19.17 |  |  |  |  | 0.03
2013 |  |  |  | 4058.32 |  |  | 8760 |  |  |  | 460 | [10 empty] | 96.25 |  |  |  | 96.25 | [5 empty] | 100.71 |  |  | 100.00 |  |  |  | 0.03 |  | 0.51 | [8 empty] | 3.24 |  |  |  |  | 0.00
2014 |  |  |  | 3798.18 |  |  | 8103 |  |  |  | 475 | [10 empty] | 88.97 |  |  |  | 88.97 | [5 empty] | 91.28 |  |  | 92.50 |  |  |  | 4.62 |  | 4.31 | [8 empty] | 6.72 |  |  |  |  | 0.00
2015 |  |  |  | 3333.82 |  |  | 7047 |  |  |  | 480 | [10 empty] | 77.93 |  |  |  | 79.89 | [5 empty] | 79.29 |  |  | 80.45 |  |  |  | 0.99 |  | 1.56 | [8 empty] | 18.55 |  |  |  |  | 1.96
2016 |  |  |  | 3851.10 |  |  | 8120 | [14 empty] | 89.60 |  |  |  | 89.60 | [5 empty] | 91.34 |  |  | 92.44 |  |  |  | 8.59 |  | 8.42 | [8 empty] | 1.98 |  |  |  |  | 0.00
2017 |  |  |  | 3860.89 |  |  | 8104 | [14 empty] | 90.06 |  |  |  | 90.06 | [5 empty] | 91.82 |  |  | 92.51 |  |  |  | 1.87 |  | 1.72 | [8 empty] | 8.22 |  |  |  |  | 0.00
2018 |  |  |  | 631.33 |  |  | 1488 |  |  |  | 490 | [10 empty] | 15.99 |  |  |  | 15.99 | [5 empty] | 14.71 |  |  | 16.99 |  |  |  | 11.78 |  | 76.14 | [8 empty] | 7.87 |  |  |  |  | 0.00
2019 |  |  |  | -78.20 |  |  | 0 |  |  |  | 490 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | -1.82 |  |  | 0.00 |  |  |  | 0.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 1253.87 |  |  | 2953 |  |  |  | 490 | [10 empty] | 31.20 |  |  |  | 31.25 | [5 empty] | 29.13 |  |  | 33.62 |  |  |  | 0.00 |  | 67.59 | [8 empty] | 1.16 |  |  |  |  | 0.05
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1976 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 461
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 339 |  |  |  | 18
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 644 |  |  |  | 11
E. |  | Testing of plant systems or components | [35 empty] | 59 |  |  |  | 6
H. |  | Nuclear regulatory requirements | [39 empty] | 339
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 2 |  |  |  | 2
Z. |  | Other | [24 empty] | 6215 | [10 empty] | 69 |  |  |  | 149
Subtotal | [26 empty] | 6215 | [10 empty] | 1113 |  |  |  | 988 | [11 empty] | 11
Total | [22 empty] | 6215 | [14 empty] | 2112
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1976 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 6215 | [14 empty] | 479
12. |  |  | Reactor I&C Systems | [34 empty] | 18
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 50
16. |  |  | Steam generation systems | [34 empty] | 195
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 84
32. |  |  | Feedwater and Main Steam System | [34 empty] | 33
33. |  |  | Circulating Water System | [34 empty] | 15
34. |  |  | Miscellaneous Systems | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 44
42. |  |  | Electrical Power Supply Systems | [34 empty] | 21
Total | [22 empty] | 6215 | [14 empty] | 957
Highlights (2020)
Started the year on outage for graphite core safety case work and re-started in August

## HUNTERSTON B-2
2020 Operating Experience
GB-17B | [8 empty] | HUNTERSTON B-2 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | TNPG (THE NUCLEAR POWER GROUP, LTD.)
Turbine Supplier | [7 empty] | : | PARSONS (C.A.PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-11-01
Thermal power | [12 empty] | : |  |  | 1496 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-03-31
Gross electrical power | [12 empty] | : |  |  | 644 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-03-31
Reference unit power (net) | [12 empty] | : |  |  | 495 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.24
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 648.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.11 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 16.28
| Active core height/length [m] | [13 empty] | : |  |  | 8.312 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 2464 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 81 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 5
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 1022.14 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.82 %
Energy Availability Factor (EAF) | [18 empty] | : | 24.8 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 54.57 %
Unit Capability Factor (UCF) | [18 empty] | : | 24.88 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.55 %
Load Factor (LF) | [18 empty] | : | 23.51 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.08 %
Operating Factor (OF) | [18 empty] | : | 26 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 6500 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | -4.76 | -3.65 |  |  |  | -6.47 |  | -6.20 | [8 empty] | -5.74 |  |  | -5.58 | [6 empty] | -5.45 |  | -6.11 |  |  |  | 10.67 |  |  | 370.30 |  |  | 327.86 | [9 empty] | 357.26 |  |  | 1022.14
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 7.86 |  |  | 99.81 |  |  | 91.30 | [9 empty] | 96.91 |  |  | 24.80
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 7.90 |  |  | 100.00 |  |  | 91.30 | [9 empty] | 97.57 |  |  | 24.88
LF [%] |  |  |  |  | -1.29 | -1.06 |  |  |  | -1.76 |  | -1.74 | [8 empty] | -1.56 |  |  | -1.57 | [6 empty] | -1.48 |  | -1.66 |  |  |  | 2.99 |  |  | 100.41 |  |  | 91.99 | [9 empty] | 97.01 |  |  | 23.51
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 10.42 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 26.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 2.43 |  |  | 0.82
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 58.01 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 92.10 |  |  | 0.00 |  |  | 1.30 | [9 empty] | 2.43 |  |  | 54.57
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.99 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 7.39 | [9 empty] | 0.00 |  |  | 20.55
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.04 |  |  | 0.19 |  |  | 0.00 | [9 empty] | 0.66 |  |  | 0.08
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 138927.11 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 14.2 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 15.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 71.39 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.28 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 69.57 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.1 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.99 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 1047.70 |  |  | 3071 |  |  |  | 500 | [10 empty] | 32.47 |  |  |  | 32.47 | [5 empty] | 31.63 |  |  | 46.35 |  |  |  | 58.11 |  | 45.04 | [8 empty] | 22.49 |  |  |  |  | 0.00
1978 |  |  |  | 0.00 |  |  | 0 |  |  |  | 500 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1979 |  |  |  | 0.00 |  |  | 0 |  |  |  | 500 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 2544.00 |  |  | 5147 |  |  |  | 500 | [10 empty] | 58.92 |  |  |  | 58.92 | [5 empty] | 58.24 |  |  | 58.92 |  |  |  | 20.97 |  | 15.64 | [8 empty] | 25.45 |  |  |  |  | 0.00
1981 |  |  |  | 3019.90 |  |  | 7219 |  |  |  | 500 | [10 empty] | 68.17 |  |  |  | 68.17 | [5 empty] | 67.83 |  |  | 81.08 |  |  |  | 31.83 |  | 31.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 2706.20 |  |  | 5596 |  |  |  | 515 | [10 empty] | 59.82 |  |  |  | 59.82 | [5 empty] | 60.14 |  |  | 64.05 |  |  |  | 20.24 |  | 15.18 | [8 empty] | 25.00 |  |  |  |  | 0.00
1983 |  |  |  | 4153.00 |  |  | 8524 |  |  |  | 520 | [10 empty] | 88.41 |  |  |  | 88.41 | [5 empty] | 91.42 |  |  | 97.57 |  |  |  | 7.22 |  | 6.88 | [8 empty] | 4.70 |  |  |  |  | 0.00
1984 |  |  |  | 3287.00 |  |  | 6365 |  |  |  | 550 | [10 empty] | 67.71 |  |  |  | 67.71 | [5 empty] | 68.41 |  |  | 72.86 |  |  |  | 10.42 |  | 7.88 | [8 empty] | 24.41 |  |  |  |  | 0.00
1985 |  |  |  | 4507.70 |  |  | 8303 |  |  |  | 575 | [10 empty] | 88.71 |  |  |  | 88.73 | [5 empty] | 89.74 |  |  | 95.04 |  |  |  | 6.47 |  | 6.14 | [8 empty] | 5.13 |  |  |  |  | 0.02
1986 |  |  |  | 3616.10 |  |  | 6496 |  |  |  | 575 | [10 empty] | 70.84 |  |  |  | 70.84 | [5 empty] | 71.99 |  |  | 74.36 |  |  |  | 9.76 |  | 7.66 | [8 empty] | 21.50 |  |  |  |  | 0.00
1987 |  |  |  | 4623.40 |  |  | 8710 |  |  |  | 575 | [10 empty] | 90.47 |  |  |  | 90.77 | [5 empty] | 90.30 |  |  | 97.82 |  |  |  | 4.70 |  | 4.47 | [8 empty] | 4.76 |  |  |  |  | 0.30
1988 |  |  |  | 3115.50 |  |  | 5754 |  |  |  | 575 | [10 empty] | 61.26 |  |  |  | 61.26 | [5 empty] | 62.02 |  |  | 65.87 |  |  |  | 3.33 |  | 2.11 | [8 empty] | 36.62 |  |  |  |  | 0.00
1989 |  |  |  | 4728.00 |  |  | 8643 |  |  |  | 575 | [10 empty] | 93.51 |  |  |  | 93.51 | [5 empty] | 94.12 |  |  | 98.94 |  |  |  | 1.99 |  | 1.90 | [8 empty] | 4.58 |  |  |  |  | 0.00
1990 |  |  |  | 3231.25 |  |  | 5858 |  |  |  | 575 | [10 empty] | 63.78 |  |  |  | 63.78 | [5 empty] | 64.33 |  |  | 67.06 |  |  |  | 1.47 |  | 0.95 | [8 empty] | 35.27 |  |  |  |  | 0.00
1991 |  |  |  | 4727.80 |  |  | 8707 |  |  |  | 575 | [10 empty] | 94.04 |  |  |  | 94.65 | [5 empty] | 94.12 |  |  | 99.67 |  |  |  | 1.37 |  | 1.31 | [8 empty] | 4.04 |  |  |  |  | 0.61
1992 |  |  |  | 1969.70 |  |  | 3733 |  |  |  | 575 | [10 empty] | 39.20 |  |  |  | 39.20 | [5 empty] | 38.47 |  |  | 41.92 |  |  |  | 1.90 |  | 0.76 | [8 empty] | 60.04 |  |  |  |  | 0.00
1993 |  |  |  | 4322.10 |  |  | 8128 |  |  |  | 575 | [10 empty] | 86.13 |  |  |  | 86.67 | [5 empty] | 86.04 |  |  | 93.04 |  |  |  | 2.05 |  | 1.81 | [8 empty] | 11.51 |  |  |  |  | 0.54
1994 |  |  |  | 3784.72 |  |  | 6949 |  |  |  | 582 | [10 empty] | 74.68 |  |  |  | 74.91 | [5 empty] | 74.36 |  |  | 79.54 |  |  |  | 2.23 |  | 1.71 | [8 empty] | 23.38 |  |  |  |  | 0.24
1995 |  |  |  | 4671.30 |  |  | 8315 |  |  |  | 585 | [10 empty] | 90.07 |  |  |  | 90.07 | [5 empty] | 87.94 |  |  | 91.57 |  |  |  | 3.09 |  | 2.87 | [8 empty] | 7.06 |  |  |  |  | 0.00
1996 |  |  |  | 1276.60 |  |  | 2377 |  |  |  | 585 | [10 empty] | 91.85 |  |  |  | 91.85 | [5 empty] | 24.84 |  |  | 27.06 |  |  |  | 1.46 |  | 1.36 | [8 empty] | 6.78 |  |  |  |  | 0.00
1997 |  |  |  | 4559.72 |  |  | 8200 |  |  |  | 595 | [10 empty] | 87.52 |  |  |  | 87.52 | [5 empty] | 87.24 |  |  | 93.35 |  |  |  | 8.92 |  | 8.57 | [8 empty] | 3.91 |  |  |  |  | 0.00
1998 |  |  |  | 4518.00 |  |  | 8149 |  |  |  | 595 | [10 empty] | 86.72 |  |  |  | 86.72 | [5 empty] | 86.44 |  |  | 92.77 |  |  |  | 9.35 |  | 8.95 | [8 empty] | 4.34 |  |  |  |  | 0.00
1999 |  |  |  | 4101.97 |  |  | 7302 |  |  |  | 595 | [10 empty] | 78.76 |  |  |  | 78.76 | [5 empty] | 78.48 |  |  | 83.13 |  |  |  | 9.78 |  | 8.53 | [8 empty] | 12.71 |  |  |  |  | 0.00
2000 |  |  |  | 3241.62 |  |  | 6411 |  |  |  | 595 | [10 empty] | 62.02 |  |  |  | 62.02 | [5 empty] | 62.02 |  |  | 72.98 |  |  |  | 31.06 |  | 27.95 | [8 empty] | 10.03 |  |  |  |  | 0.00
2001 |  |  |  | 3785.00 |  |  | 6485 |  |  |  | 595 | [10 empty] | 83.71 |  |  |  | 83.71 | [5 empty] | 72.42 |  |  | 73.83 |  |  |  | 7.48 |  | 6.77 | [8 empty] | 9.52 |  |  |  |  | 0.00
2002 |  |  |  | 4413.06 |  |  | 7721 |  |  |  | 595 | [10 empty] | 83.07 |  |  |  | 83.07 | [5 empty] | 84.67 |  |  | 88.14 |  |  |  | 1.08 |  | 1.94 | [8 empty] | 14.98 |  |  |  |  | 0.00
2003 |  |  |  | 4627.26 |  |  | 8381 |  |  |  | 595 | [10 empty] | 87.51 |  |  |  | 87.77 | [5 empty] | 88.78 |  |  | 95.67 |  |  |  | 5.96 |  | 5.56 | [8 empty] | 6.67 |  |  |  |  | 0.26
2004 |  |  |  | 4238.69 |  |  | 7799 |  |  |  | 595 | [10 empty] | 83.47 |  |  |  | 83.71 | [5 empty] | 81.10 |  |  | 88.79 |  |  |  | 7.67 |  | 9.94 | [8 empty] | 6.35 |  |  |  |  | 0.24
2005 |  |  |  | 3633.64 |  |  | 7017 |  |  |  | 595 | [10 empty] | 69.41 |  |  |  | 69.99 | [5 empty] | 69.71 |  |  | 80.10 |  |  |  | 7.67 |  | 10.79 | [8 empty] | 19.21 |  |  |  |  | 0.58
2006 |  |  |  | 3745.99 |  |  | 6753 |  |  |  | 595 | [10 empty] | 71.04 |  |  |  | 71.04 | [5 empty] | 70.97 |  |  | 77.09 |  |  |  | 25.69 |  | 24.97 | [8 empty] | 3.98 |  |  |  |  | 0.00
2007 |  |  |  | 1658.38 |  |  | 4642 |  |  |  | 420 | [10 empty] | 41.29 |  |  |  | 41.29 | [5 empty] | 40.66 |  |  | 52.99 |  |  |  | 58.11 |  | 57.28 | [8 empty] | 1.43 |  |  |  |  | 0.00
2008 |  |  |  | 2240.71 |  |  | 6054 |  |  |  | 410 | [10 empty] | 61.92 |  |  |  | 61.92 | [5 empty] | 61.84 |  |  | 68.92 |  |  |  | 11.75 |  | 9.74 | [8 empty] | 28.34 |  |  |  |  | 0.00
2009 |  |  |  | 3217.65 |  |  | 8065 |  |  |  | 430 | [10 empty] | 85.39 |  |  |  | 85.39 | [5 empty] | 86.41 |  |  | 92.07 |  |  |  | 11.62 |  | 12.20 | [8 empty] | 2.41 |  |  |  |  | 0.00
2010 |  |  |  | 3218.67 |  |  | 7876 |  |  |  | 430 | [10 empty] | 85.07 |  |  |  | 85.13 | [5 empty] | 85.45 |  |  | 89.91 |  |  |  | 1.07 |  | 1.87 | [8 empty] | 13.00 |  |  |  |  | 0.06
2011 |  |  |  | 2959.85 |  |  | 7211 |  |  |  | 430 | [10 empty] | 78.34 |  |  |  | 79.18 | [5 empty] | 78.58 |  |  | 82.32 |  |  |  | 0.89 |  | 1.79 | [8 empty] | 19.03 |  |  |  |  | 0.84
2012 |  |  |  | 3635.82 |  |  | 8784 |  |  |  | 430 | [10 empty] | 95.39 |  |  |  | 95.41 | [5 empty] | 96.26 |  |  | 100.00 |  |  |  | 0.44 |  | 0.72 | [8 empty] | 3.87 |  |  |  |  | 0.02
2013 |  |  |  | 3432.84 |  |  | 7601 |  |  |  | 430 | [10 empty] | 83.37 |  |  |  | 83.37 | [5 empty] | 91.13 |  |  | 86.77 |  |  |  | 0.07 |  | 7.38 | [8 empty] | 9.25 |  |  |  |  | 0.00
2014 |  |  |  | 2832.36 |  |  | 6114 |  |  |  | 485 | [10 empty] | 66.46 |  |  |  | 66.46 | [5 empty] | 66.67 |  |  | 69.79 |  |  |  | 1.95 |  | 6.50 | [8 empty] | 27.04 |  |  |  |  | 0.00
2015 |  |  |  | 4134.20 |  |  | 8640 |  |  |  | 485 | [10 empty] | 95.44 |  |  |  | 95.53 | [5 empty] | 97.31 |  |  | 98.63 |  |  |  | 1.75 |  | 1.70 | [8 empty] | 2.76 |  |  |  |  | 0.09
2016 |  |  |  | 4028.95 |  |  | 8399 | [14 empty] | 92.99 |  |  |  | 93.01 | [5 empty] | 94.57 |  |  | 95.62 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 6.94 |  |  |  |  | 0.02
2017 |  |  |  | 0.00 | [17 empty] | 79.48 |  |  |  | 79.48 | [5 empty] | 80.53 |  |  | 82.04 |  |  |  | 0.48 |  | 1.81 | [8 empty] | 18.71 |  |  |  |  | 0.00
2018 |  |  |  | 3142.06 |  |  | 6599 |  |  |  | 495 | [10 empty] | 73.19 |  |  |  | 73.48 | [5 empty] | 72.46 |  |  | 75.33 |  |  |  | 0.00 |  | 17.24 | [8 empty] | 9.27 |  |  |  |  | 0.30
2019 |  |  |  | 1116.54 |  |  | 2572 |  |  |  | 495 | [10 empty] | 27.77 |  |  |  | 27.78 | [5 empty] | 25.75 |  |  | 29.36 |  |  |  | 0.00 |  | 65.81 | [8 empty] | 6.41 |  |  |  |  | 0.01
2020 |  |  |  | 1022.14 |  |  | 2284 |  |  |  | 495 | [10 empty] | 24.80 |  |  |  | 24.88 | [5 empty] | 23.51 |  |  | 26.00 |  |  |  | 0.82 |  | 54.57 | [8 empty] | 20.55 |  |  |  |  | 0.08
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1977 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 732
B. |  | Refuelling without maintenance | [35 empty] | 0
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 310 |  |  |  | 19
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 1752 | [14 empty] | 628 |  |  |  | 49
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 130
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 5
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [24 empty] | 4799 | [10 empty] | 20 |  |  |  | 112 | [11 empty] | 1
Subtotal | [22 empty] | 1752 |  |  |  | 4799 | [10 empty] | 959 |  |  |  | 1049 | [11 empty] | 10
Total | [22 empty] | 6551 | [14 empty] | 2018
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1977 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 4799 | [14 empty] | 291
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 25
16. |  |  | Steam generation systems | [34 empty] | 98
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 55
32. |  |  | Feedwater and Main Steam System | [34 empty] | 503
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 18
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [22 empty] | 4799 | [14 empty] | 1024
Highlights (2020)
Started the year on outage for graphite core safety case work and re-started in September

## SIZEWELL B
2020 Operating Experience
GB-24 | [8 empty] | SIZEWELL B | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | PPC (PWR POWER PROJECTS, Ltd.)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / SNUPPS | [11 empty] | Construction Date | [15 empty] | : |  |  | 1988-07-18
Thermal power | [12 empty] | : |  |  | 3425 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1995-02-14
Gross electrical power | [12 empty] | : |  |  | 1250 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1995-09-22
Reference unit power (net) | [12 empty] | : |  |  | 1198 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 25 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.01
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.35
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 43 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.71
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 6
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8393.47 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.57 %
Energy Availability Factor (EAF) | [18 empty] | : | 79.54 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.57 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.43 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 79.76 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 19.89 %
Operating Factor (OF) | [18 empty] | : | 99.53 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 41 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 896.06 | 837.98 |  |  |  | 894.71 |  | 865.56 | [8 empty] | 523.92 |  |  | 410.39 | [6 empty] | 421.13 |  | 397.59 |  |  |  | 495.42 |  |  | 893.82 |  |  | 865.89 | [9 empty] | 890.99 |  |  | 8393.47
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 58.75 |  |  | 47.58 | [6 empty] | 47.25 |  | 44.63 |  |  |  | 57.44 |  |  | 99.97 |  |  | 100.00 | [9 empty] | 99.71 |  |  | 79.54
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 93.56 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.71 |  |  | 99.43
LF [%] |  |  |  |  | 100.53 | 100.50 |  |  |  | 100.52 |  | 100.35 | [8 empty] | 58.78 |  |  | 47.58 | [6 empty] | 47.25 |  | 44.61 |  |  |  | 57.44 |  |  | 100.15 |  |  | 100.39 | [9 empty] | 99.96 |  |  | 79.76
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 94.49 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.53
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 6.44 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.29 |  |  | 0.57
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 6.44 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.29 |  |  | 0.57
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 41.25 |  |  | 52.42 | [6 empty] | 52.75 |  | 48.92 |  |  |  | 42.56 |  |  | 0.03 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 19.89
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 199587.49 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.66 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.39 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.54 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.25 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.21 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.68 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.86 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.65 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1995 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1188 | [10 empty] | 99.79 |  |  |  | 100.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.21
1996 |  |  |  | 8488.47 |  |  | 7367 |  |  |  | 1188 | [10 empty] | 81.38 |  |  |  | 81.34 | [5 empty] | 81.34 |  |  | 83.87 |  |  |  | 5.51 |  | 4.74 | [8 empty] | 13.91 |  |  |  |  | -0.04
1997 |  |  |  | 8469.81 |  |  | 6992 |  |  |  | 1188 | [10 empty] | 81.51 |  |  |  | 81.44 | [5 empty] | 81.16 |  |  | 79.60 |  |  |  | 5.68 |  | 4.91 | [8 empty] | 13.65 |  |  |  |  | -0.07
1998 |  |  |  | 10123.09 |  |  | 8705 |  |  |  | 1188 | [10 empty] | 97.38 |  |  |  | 97.28 | [5 empty] | 97.01 |  |  | 99.10 |  |  |  | 2.71 |  | 2.71 | [8 empty] | 0.01 |  |  |  |  | -0.10
1999 |  |  |  | 7959.01 |  |  | 7134 |  |  |  | 1188 | [10 empty] | 76.53 |  |  |  | 76.54 | [5 empty] | 76.27 |  |  | 81.22 |  |  |  | 11.22 |  | 9.68 | [8 empty] | 13.78 |  |  |  |  | 0.01
2000 |  |  |  | 8527.18 |  |  | 7612 |  |  |  | 1188 | [10 empty] | 81.62 |  |  |  | 81.71 | [5 empty] | 81.71 |  |  | 86.66 |  |  |  | 9.10 |  | 8.18 | [8 empty] | 10.10 |  |  |  |  | 0.09
2001 |  |  |  | 9197.96 |  |  | 7784 |  |  |  | 1188 | [10 empty] | 77.17 |  |  |  | 77.44 | [5 empty] | 88.14 |  |  | 88.62 |  |  |  | 12.71 |  | 11.28 | [8 empty] | 11.28 |  |  |  |  | 0.27
2002 |  |  |  | 9195.04 |  |  | 7862 |  |  |  | 1188 | [10 empty] | 88.48 |  |  |  | 88.90 | [5 empty] | 88.36 |  |  | 89.75 |  |  |  | 2.36 |  | 2.15 | [8 empty] | 8.95 |  |  |  |  | 0.42
2003 |  |  |  | 8854.19 |  |  | 7613 |  |  |  | 1188 | [10 empty] | 88.74 |  |  |  | 89.26 | [5 empty] | 85.08 |  |  | 86.91 |  |  |  | 2.36 |  | 2.16 | [8 empty] | 8.58 |  |  |  |  | 0.52
2004 |  |  |  | 9329.11 |  |  | 8685 |  |  |  | 1188 | [10 empty] | 89.42 |  |  |  | 89.42 | [5 empty] | 89.40 |  |  | 98.87 |  |  |  | 9.72 |  | 9.63 | [8 empty] | 0.94 |  |  |  |  | 0.00
2005 |  |  |  | 8696.25 |  |  | 7476 |  |  |  | 1188 | [10 empty] | 83.93 |  |  |  | 83.93 | [5 empty] | 83.56 |  |  | 85.34 |  |  |  | 0.00 |  | 4.53 | [8 empty] | 11.54 |  |  |  |  | 0.00
2006 |  |  |  | 8908.26 |  |  | 7570 |  |  |  | 1196 | [10 empty] | 85.25 |  |  |  | 85.25 | [5 empty] | 85.17 |  |  | 86.42 |  |  |  | 0.33 |  | 0.28 | [8 empty] | 14.47 |  |  |  |  | 0.00
2007 |  |  |  | 10264.31 |  |  | 8760 |  |  |  | 1188 | [10 empty] | 98.46 |  |  |  | 98.46 | [5 empty] | 98.47 |  |  | 100.00 |  |  |  | 0.38 |  | 0.38 | [8 empty] | 1.16 |  |  |  |  | 0.00
2008 |  |  |  | 9301.23 |  |  | 8097 |  |  |  | 1188 | [10 empty] | 89.23 |  |  |  | 89.23 | [5 empty] | 89.13 |  |  | 92.18 |  |  |  | 2.05 |  | 2.06 | [8 empty] | 8.71 |  |  |  |  | 0.00
2009 |  |  |  | 9094.88 |  |  | 7863 |  |  |  | 1188 | [10 empty] | 87.35 |  |  |  | 87.35 | [5 empty] | 87.39 |  |  | 89.76 |  |  |  | 0.92 |  | 3.80 | [8 empty] | 8.85 |  |  |  |  | 0.00
2010 |  |  |  | 4774.80 |  |  | 4032 |  |  |  | 1188 | [10 empty] | 45.63 |  |  |  | 45.63 | [5 empty] | 45.88 |  |  | 46.03 |  |  |  | 54.31 |  | 54.24 | [8 empty] | 0.13 |  |  |  |  | 0.00
2011 |  |  |  | 8627.40 |  |  | 7463 |  |  |  | 1191 | [10 empty] | 82.54 |  |  |  | 82.54 | [5 empty] | 82.69 |  |  | 85.19 |  |  |  | 3.43 |  | 5.77 | [8 empty] | 11.69 |  |  |  |  | 0.00
2012 |  |  |  | 9346.24 |  |  | 8348 |  |  |  | 1191 | [10 empty] | 89.20 |  |  |  | 89.20 | [5 empty] | 89.34 |  |  | 95.04 |  |  |  | 9.95 |  | 9.86 | [8 empty] | 0.95 |  |  |  |  | 0.00
2013 |  |  |  | 8714.72 |  |  | 7612 |  |  |  | 1198 | [10 empty] | 83.03 |  |  |  | 83.03 | [5 empty] | 83.04 |  |  | 86.89 |  |  |  | 0.23 |  | 3.97 | [8 empty] | 13.00 |  |  |  |  | 0.00
2014 |  |  |  | 8828.14 |  |  | 7589 |  |  |  | 1198 | [10 empty] | 84.08 |  |  |  | 84.08 | [5 empty] | 84.12 |  |  | 86.63 |  |  |  | 0.69 |  | 1.58 | [8 empty] | 14.34 |  |  |  |  | 0.00
2015 |  |  |  | 10507.34 |  |  | 8760 |  |  |  | 1198 | [10 empty] | 99.91 |  |  |  | 99.98 | [5 empty] | 100.12 |  |  | 100.00 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 0.00 |  |  |  |  | 0.06
2016 |  |  |  | 8626.70 |  |  | 7280 |  |  |  | 1198 | [10 empty] | 81.89 |  |  |  | 82.00 | [5 empty] | 81.98 |  |  | 82.88 |  |  |  | 0.14 |  | 2.13 | [8 empty] | 15.87 |  |  |  |  | 0.11
2017 |  |  |  | 0.00 | [6 empty] | 1198 | [10 empty] | 83.72 |  |  |  | 83.82 | [5 empty] | 83.90 |  |  | 83.94 |  |  |  | 0.01 |  | 5.84 | [8 empty] | 10.35 |  |  |  |  | 0.10
2018 |  |  |  | 9388.12 |  |  | 8039 |  |  |  | 1198 | [10 empty] | 89.22 |  |  |  | 89.37 | [5 empty] | 89.46 |  |  | 91.77 |  |  |  | 2.20 |  | 10.63 | [8 empty] | 0.00 |  |  |  |  | 0.15
2019 |  |  |  | 8452.10 |  |  | 7175 |  |  |  | 1198 | [10 empty] | 80.54 |  |  |  | 80.64 | [5 empty] | 80.54 |  |  | 81.91 |  |  |  | 0.18 |  | 4.32 | [8 empty] | 15.04 |  |  |  |  | 0.10
2020 |  |  |  | 8393.47 |  |  | 8743 |  |  |  | 1198 | [10 empty] | 79.54 |  |  |  | 99.43 | [5 empty] | 79.76 |  |  | 99.53 |  |  |  | 0.57 |  | 0.57 | [8 empty] | 0.00 |  |  |  |  | 19.89
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1995 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 405
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 680 |  |  |  | 56
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 1
E. |  | Testing of plant systems or components | [39 empty] | 3
L. |  | Human factor related | [24 empty] | 41 | [14 empty] | 3
Subtotal | [26 empty] | 41 | [10 empty] | 681 |  |  |  | 467
Total | [22 empty] | 41 | [14 empty] | 1148
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1995 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 18
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 15
14. |  |  | Safety Systems | [34 empty] | 34
15. |  |  | Reactor Cooling Systems | [34 empty] | 191
16. |  |  | Steam generation systems | [34 empty] | 53
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
34. |  |  | Miscellaneous Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 59
42. |  |  | Electrical Power Supply Systems | [19 empty] | 41 | [14 empty] | 14
Total | [22 empty] | 41 | [14 empty] | 400
Highlights (2020)
Operated at around 50% RUP between May and August at request of Grid Operator

## TORNESS-1
2020 Operating Experience
GB-23A | [8 empty] | TORNESS-1 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | NNC (NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-08-01
Thermal power | [12 empty] | : |  |  | 1623 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-05-25
Gross electrical power | [12 empty] | : |  |  | 682 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-05-25
Reference unit power (net) | [12 empty] | : |  |  | 595 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.3
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 635
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 2 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 27000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 15.9
| Active core height/length [m] | [13 empty] | : |  |  | 8.31 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 332 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4946.16 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.48 %
Energy Availability Factor (EAF) | [18 empty] | : | 94 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.54 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.95 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 3.51 %
Load Factor (LF) | [18 empty] | : | 94.64 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.96 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 429.68 | 412.05 |  |  |  | 396.24 |  | 405.36 | [8 empty] | 422.56 |  |  | 434.35 | [6 empty] | 411.62 |  | 350.57 |  |  |  | 421.45 |  |  | 417.44 |  |  | 396.37 | [9 empty] | 448.48 |  |  | 4946.16
EAF [%] |  |  |  |  | 96.29 | 99.32 |  |  |  | 89.63 |  | 94.15 | [8 empty] | 94.43 |  |  | 99.82 | [6 empty] | 92.63 |  | 78.91 |  |  |  | 97.97 |  |  | 93.24 |  |  | 92.17 | [9 empty] | 100.00 |  |  | 94.00
UCF [%] |  |  |  |  | 96.29 | 99.32 |  |  |  | 89.63 |  | 94.17 | [8 empty] | 94.43 |  |  | 99.82 | [6 empty] | 92.66 |  | 100.00 |  |  |  | 100.00 |  |  | 93.25 |  |  | 92.17 | [9 empty] | 100.00 |  |  | 95.95
LF [%] |  |  |  |  | 97.06 | 99.50 |  |  |  | 89.63 |  | 94.62 | [8 empty] | 95.45 |  |  | 101.39 | [6 empty] | 92.98 |  | 79.19 |  |  |  | 98.38 |  |  | 94.17 |  |  | 92.52 | [9 empty] | 101.31 |  |  | 94.64
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.68 |  |  |  | 4.50 |  | 0.50 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.18 | [9 empty] | 0.00 |  |  | 0.48
UCL [%] |  |  |  |  | 0.00 | 0.68 |  |  |  | 4.84 |  | 0.47 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.29 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.16 | [9 empty] | 0.00 |  |  | 0.54
PUF [%] |  |  |  |  | 3.71 | 0.00 |  |  |  | 5.53 |  | 5.36 | [8 empty] | 5.57 |  |  | 0.18 | [6 empty] | 7.05 |  | 0.00 |  |  |  | 0.00 |  |  | 6.75 |  |  | 7.66 | [9 empty] | 0.00 |  |  | 3.51
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.02 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.03 |  | 21.09 |  |  |  | 2.03 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.96
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 128935.07 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.6 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.96 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.51 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.58 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.91 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.27 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.62 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.47 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 2287.10 |  |  | 4330 |  |  |  | 638 | [10 empty] | 69.41 |  |  |  | 92.32 | [5 empty] | 68.07 |  |  | 82.99 |  |  |  | 7.68 |  | 7.68 | [8 empty] | 0.00 |  |  |  |  | 22.91
1989 |  |  |  | 2162.10 |  |  | 4582 |  |  |  | 625 | [10 empty] | 39.47 |  |  |  | 53.23 | [5 empty] | 39.60 |  |  | 52.45 |  |  |  | 4.16 |  | 2.31 | [8 empty] | 44.46 |  |  |  |  | 13.76
1990 |  |  |  | 1938.35 |  |  | 3943 |  |  |  | 625 | [10 empty] | 35.66 |  |  |  | 35.66 | [5 empty] | 35.50 |  |  | 45.14 |  |  |  | 10.53 |  | 4.20 | [8 empty] | 60.14 |  |  |  |  | 0.00
1991 |  |  |  | 2513.60 |  |  | 5011 |  |  |  | 625 | [10 empty] | 45.97 |  |  |  | 45.97 | [5 empty] | 46.04 |  |  | 57.36 |  |  |  | 6.72 |  | 3.31 | [8 empty] | 50.72 |  |  |  |  | 0.00
1992 |  |  |  | 4532.90 |  |  | 7792 |  |  |  | 632 | [10 empty] | 81.66 |  |  |  | 81.66 | [5 empty] | 80.55 |  |  | 87.51 |  |  |  | 4.22 |  | 3.60 | [8 empty] | 14.74 |  |  |  |  | 0.00
1993 |  |  |  | 3603.10 |  |  | 6358 |  |  |  | 632 | [10 empty] | 67.68 |  |  |  | 67.89 | [5 empty] | 62.91 |  |  | 70.15 |  |  |  | 10.75 |  | 8.18 | [8 empty] | 23.93 |  |  |  |  | 0.21
1994 |  |  |  | 4329.90 |  |  | 7716 |  |  |  | 632 | [10 empty] | 79.51 |  |  |  | 86.73 | [5 empty] | 78.42 |  |  | 88.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.27 |  |  |  |  | 7.22
1995 |  |  |  | 4058.60 |  |  | 6867 |  |  |  | 632 | [10 empty] | 75.19 |  |  |  | 75.19 | [5 empty] | 71.54 |  |  | 76.50 |  |  |  | 0.48 |  | 0.36 | [8 empty] | 24.44 |  |  |  |  | 0.00
1996 |  |  |  | 1178.10 |  |  | 2043 |  |  |  | 632 | [10 empty] | 96.64 |  |  |  | 96.64 | [5 empty] | 21.22 |  |  | 23.26 |  |  |  | 0.38 |  | 0.37 | [8 empty] | 2.99 |  |  |  |  | 0.00
1997 |  |  |  | 4909.44 |  |  | 8050 |  |  |  | 625 | [10 empty] | 89.70 |  |  |  | 89.70 | [5 empty] | 89.43 |  |  | 91.64 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 10.22 |  |  |  |  | 0.00
1998 |  |  |  | 4297.87 |  |  | 7153 |  |  |  | 625 | [10 empty] | 78.56 |  |  |  | 78.56 | [5 empty] | 78.29 |  |  | 81.43 |  |  |  | 2.61 |  | 2.11 | [8 empty] | 19.33 |  |  |  |  | 0.00
1999 |  |  |  | 5157.76 |  |  | 8737 |  |  |  | 625 | [10 empty] | 94.22 |  |  |  | 94.22 | [5 empty] | 93.95 |  |  | 99.46 |  |  |  | 0.22 |  | 0.21 | [8 empty] | 5.57 |  |  |  |  | 0.00
2000 |  |  |  | 4376.80 |  |  | 8769 |  |  |  | 625 | [10 empty] | 79.72 |  |  |  | 79.72 | [5 empty] | 79.72 |  |  | 99.83 |  |  |  | 16.50 |  | 15.76 | [8 empty] | 4.52 |  |  |  |  | 0.00
2001 |  |  |  | 3968.48 |  |  | 7613 |  |  |  | 625 | [10 empty] | 70.24 |  |  |  | 70.24 | [5 empty] | 72.29 |  |  | 86.67 |  |  |  | 18.14 |  | 15.57 | [8 empty] | 14.19 |  |  |  |  | 0.00
2002 |  |  |  | 3761.93 |  |  | 6719 |  |  |  | 625 | [10 empty] | 68.71 |  |  |  | 69.64 | [5 empty] | 68.71 |  |  | 76.70 |  |  |  | 24.65 |  | 24.01 | [8 empty] | 6.35 |  |  |  |  | 0.93
2003 |  |  |  | 4681.94 |  |  | 8347 |  |  |  | 625 | [10 empty] | 85.61 |  |  |  | 85.76 | [5 empty] | 85.51 |  |  | 95.29 |  |  |  | 7.20 |  | 8.00 | [8 empty] | 6.24 |  |  |  |  | 0.15
2004 |  |  |  | 3921.80 |  |  | 6993 |  |  |  | 625 | [10 empty] | 71.68 |  |  |  | 71.68 | [5 empty] | 71.44 |  |  | 79.61 |  |  |  | 12.51 |  | 12.74 | [8 empty] | 15.58 |  |  |  |  | 0.00
2005 |  |  |  | 4667.73 |  |  | 8372 |  |  |  | 625 | [10 empty] | 85.34 |  |  |  | 85.34 | [5 empty] | 85.26 |  |  | 95.57 |  |  |  | 6.95 |  | 7.34 | [8 empty] | 7.32 |  |  |  |  | 0.00
2006 |  |  |  | 4000.87 |  |  | 7939 |  |  |  | 625 | [10 empty] | 73.31 |  |  |  | 76.74 | [5 empty] | 73.08 |  |  | 90.63 |  |  |  | 14.29 |  | 16.15 | [8 empty] | 7.11 |  |  |  |  | 3.43
2007 |  |  |  | 3500.94 |  |  | 6234 |  |  |  | 625 | [10 empty] | 64.16 |  |  |  | 65.32 | [5 empty] | 63.94 |  |  | 71.16 |  |  |  | 14.34 |  | 15.57 | [8 empty] | 19.11 |  |  |  |  | 1.16
2008 |  |  |  | 4488.12 |  |  | 8110 |  |  |  | 615 | [10 empty] | 82.89 |  |  |  | 83.47 | [5 empty] | 82.75 |  |  | 92.33 |  |  |  | 8.62 |  | 7.88 | [8 empty] | 8.65 |  |  |  |  | 0.59
2009 |  |  |  | 4963.55 |  |  | 8760 |  |  |  | 600 | [10 empty] | 93.86 |  |  |  | 93.86 | [5 empty] | 93.86 |  |  | 100.00 |  |  |  | 1.42 |  | 1.55 | [8 empty] | 4.59 |  |  |  |  | 0.00
2010 |  |  |  | 2565.36 |  |  | 5302 |  |  |  | 600 | [10 empty] | 48.82 |  |  |  | 48.82 | [5 empty] | 48.81 |  |  | 60.53 |  |  |  | 34.51 |  | 35.95 | [8 empty] | 15.23 |  |  |  |  | 0.00
2011 |  |  |  | 4582.85 |  |  | 8393 |  |  |  | 600 | [10 empty] | 87.99 |  |  |  | 88.91 | [5 empty] | 87.19 |  |  | 95.81 |  |  |  | 5.98 |  | 7.56 | [8 empty] | 3.53 |  |  |  |  | 0.92
2012 |  |  |  | 4878.05 |  |  | 8784 |  |  |  | 595 | [10 empty] | 93.33 |  |  |  | 93.35 | [5 empty] | 93.33 |  |  | 100.00 |  |  |  | 1.12 |  | 1.57 | [8 empty] | 5.08 |  |  |  |  | 0.01
2013 |  |  |  | 4637.66 |  |  | 8451 |  |  |  | 590 | [10 empty] | 89.80 |  |  |  | 93.80 | [5 empty] | 89.73 |  |  | 96.47 |  |  |  | 1.96 |  | 2.40 | [8 empty] | 3.79 |  |  |  |  | 4.01
2014 |  |  |  | 3758.73 |  |  | 6823 |  |  |  | 590 | [10 empty] | 73.02 |  |  |  | 73.05 | [5 empty] | 72.73 |  |  | 77.89 |  |  |  | 4.81 |  | 4.82 | [8 empty] | 22.14 |  |  |  |  | 0.03
2015 |  |  |  | 4954.38 |  |  | 8760 |  |  |  | 590 | [10 empty] | 95.37 |  |  |  | 95.45 | [5 empty] | 95.86 |  |  | 100.00 |  |  |  | 1.44 |  | 1.39 | [8 empty] | 3.15 |  |  |  |  | 0.08
2016 |  |  |  | 4968.15 |  |  | 8678 |  |  |  | 590 | [10 empty] | 95.29 |  |  |  | 97.07 | [5 empty] | 95.86 |  |  | 98.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.92 |  |  |  |  | 1.78
2017 |  |  |  | 4056.96 |  |  | 7235 | [14 empty] | 79.60 |  |  |  | 80.02 | [5 empty] | 78.50 |  |  | 82.59 |  |  |  | 0.01 |  | 0.16 | [8 empty] | 19.82 |  |  |  |  | 0.42
2018 |  |  |  | 4908.39 |  |  | 8610 |  |  |  | 595 | [10 empty] | 93.14 |  |  |  | 95.08 | [5 empty] | 94.17 |  |  | 98.29 |  |  |  | 1.45 |  | 1.43 | [8 empty] | 3.49 |  |  |  |  | 1.94
2019 |  |  |  | 5006.74 |  |  | 8760 |  |  |  | 595 | [10 empty] | 94.66 |  |  |  | 94.75 | [5 empty] | 96.06 |  |  | 100.00 |  |  |  | 1.12 |  | 1.67 | [8 empty] | 3.58 |  |  |  |  | 0.09
2020 |  |  |  | 4946.16 |  |  | 8784 |  |  |  | 595 | [10 empty] | 94.00 |  |  |  | 95.95 | [5 empty] | 94.64 |  |  | 100.00 |  |  |  | 0.48 |  | 0.54 | [8 empty] | 3.51 |  |  |  |  | 1.96
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 223
B. |  | Refuelling without maintenance | [35 empty] | 21
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 559 |  |  |  | 22
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 154
E. |  | Testing of plant systems or components | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 30
M. |  | Governmental requirements or court decisions | [51 empty] | 10
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 18
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 9
Z. |  | Other | [35 empty] | 77 |  |  |  | 24 | [11 empty] | 45
Subtotal | [37 empty] | 811 |  |  |  | 309 | [11 empty] | 75
Total | [22 empty] | 0 | [14 empty] | 1195
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 12
12. |  |  | Reactor I&C Systems | [34 empty] | 20
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 53
16. |  |  | Steam generation systems | [34 empty] | 6
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 27
41. |  |  | Main Generator Systems | [34 empty] | 57
42. |  |  | Electrical Power Supply Systems | [34 empty] | 60
Total | [37 empty] | 267

## TORNESS-2
2020 Operating Experience
GB-23B | [8 empty] | TORNESS-2 | [26 empty] | UNITED KINGDOM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EDF UK (EDF Energy)
Owner | [7 empty] | : | EDF UK (EDF Energy)
Reactor Supplier | [7 empty] | : | NNC (NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | GCR / AGR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-08-01
Thermal power | [12 empty] | : |  |  | 1623 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1989-02-03
Gross electrical power | [12 empty] | : |  |  | 682 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-02-03
Reference unit power (net) | [12 empty] | : |  |  | 605 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.3
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 635
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | NA
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 2 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 27000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 9.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 15.9
| Active core height/length [m] | [13 empty] | : |  |  | 8.31 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 332 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | CO2 | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4904.72 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.01 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.26 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.04 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 3.7 %
Load Factor (LF) | [18 empty] | : | 92.29 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.03 %
Operating Factor (OF) | [18 empty] | : | 98.08 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 169 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 413.60 | 422.72 |  |  |  | 379.07 |  | 403.24 | [8 empty] | 406.23 |  |  | 309.37 | [6 empty] | 409.99 |  | 449.24 |  |  |  | 402.13 |  |  | 456.62 |  |  | 400.18 | [9 empty] | 452.34 |  |  | 4904.72
EAF [%] |  |  |  |  | 91.53 | 99.78 |  |  |  | 84.33 |  | 92.54 | [8 empty] | 90.19 |  |  | 71.70 | [6 empty] | 91.08 |  | 99.72 |  |  |  | 92.29 |  |  | 100.00 |  |  | 91.09 | [9 empty] | 99.71 |  |  | 92.01
UCF [%] |  |  |  |  | 91.55 | 99.78 |  |  |  | 84.33 |  | 92.56 | [8 empty] | 90.19 |  |  | 71.70 | [6 empty] | 91.09 |  | 99.82 |  |  |  | 92.44 |  |  | 100.00 |  |  | 91.09 | [9 empty] | 99.73 |  |  | 92.04
LF [%] |  |  |  |  | 91.89 | 100.39 |  |  |  | 84.33 |  | 92.57 | [8 empty] | 90.25 |  |  | 71.02 | [6 empty] | 91.08 |  | 99.80 |  |  |  | 92.32 |  |  | 101.31 |  |  | 91.87 | [9 empty] | 100.49 |  |  | 92.29
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 76.53 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.08
FLR [%] |  |  |  |  | 0.31 | 0.22 |  |  |  | 9.11 |  | 6.38 | [8 empty] | 0.89 |  |  | 28.30 | [6 empty] | 1.96 |  | 0.16 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.40 | [9 empty] | 0.00 |  |  | 4.03
UCL [%] |  |  |  |  | 1.16 | 0.22 |  |  |  | 8.46 |  | 7.35 | [8 empty] | 2.58 |  |  | 28.30 | [6 empty] | 1.82 |  | 0.16 |  |  |  | 0.67 |  |  | 0.00 |  |  | 0.56 | [9 empty] | 0.22 |  |  | 4.26
PUF [%] |  |  |  |  | 7.29 | 0.00 |  |  |  | 7.22 |  | 0.10 | [8 empty] | 7.23 |  |  | 0.00 | [6 empty] | 7.09 |  | 0.03 |  |  |  | 6.88 |  |  | 0.00 |  |  | 8.35 | [9 empty] | 0.05 |  |  | 3.70
XUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.09 |  |  |  | 0.15 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 0.03
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 126181.73 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.86 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.35 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.76 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.86 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.82 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.11 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 3633.80 |  |  | 7068 |  |  |  | 625 | [10 empty] | 74.21 |  |  |  | 87.39 | [5 empty] | 73.28 |  |  | 89.08 |  |  |  | 4.32 |  | 3.94 | [8 empty] | 8.67 |  |  |  |  | 13.18
1990 |  |  |  | 1948.30 |  |  | 4211 |  |  |  | 625 | [10 empty] | 36.08 |  |  |  | 36.08 | [5 empty] | 35.68 |  |  | 48.20 |  |  |  | 6.46 |  | 2.49 | [8 empty] | 61.43 |  |  |  |  | 0.00
1991 |  |  |  | 2651.30 |  |  | 5068 |  |  |  | 625 | [10 empty] | 48.37 |  |  |  | 48.37 | [5 empty] | 48.56 |  |  | 58.01 |  |  |  | 4.70 |  | 2.38 | [8 empty] | 49.25 |  |  |  |  | 0.00
1992 |  |  |  | 3732.70 |  |  | 6560 |  |  |  | 625 | [10 empty] | 67.02 |  |  |  | 67.02 | [5 empty] | 67.07 |  |  | 73.67 |  |  |  | 5.42 |  | 3.84 | [8 empty] | 29.14 |  |  |  |  | 0.00
1993 |  |  |  | 4038.00 |  |  | 7168 |  |  |  | 632 | [10 empty] | 74.35 |  |  |  | 74.35 | [5 empty] | 73.14 |  |  | 82.05 |  |  |  | 3.86 |  | 2.99 | [8 empty] | 22.66 |  |  |  |  | 0.00
1994 |  |  |  | 3478.09 |  |  | 6264 |  |  |  | 632 | [10 empty] | 65.46 |  |  |  | 71.21 | [5 empty] | 62.82 |  |  | 71.51 |  |  |  | 1.36 |  | 0.98 | [8 empty] | 27.81 |  |  |  |  | 5.74
1995 |  |  |  | 4651.90 |  |  | 7909 |  |  |  | 632 | [10 empty] | 85.88 |  |  |  | 85.88 | [5 empty] | 81.31 |  |  | 87.37 |  |  |  | 1.10 |  | 0.95 | [8 empty] | 13.17 |  |  |  |  | 0.00
1996 |  |  |  | 1571.30 |  |  | 2409 |  |  |  | 632 | [10 empty] | 96.20 |  |  |  | 96.20 | [5 empty] | 28.30 |  |  | 27.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.80 |  |  |  |  | 0.00
1997 |  |  |  | 4217.98 |  |  | 7181 |  |  |  | 625 | [10 empty] | 77.72 |  |  |  | 77.72 | [5 empty] | 76.83 |  |  | 81.75 |  |  |  | 1.33 |  | 1.04 | [8 empty] | 21.24 |  |  |  |  | 0.00
1998 |  |  |  | 5094.36 |  |  | 8713 |  |  |  | 625 | [10 empty] | 93.68 |  |  |  | 93.68 | [5 empty] | 92.79 |  |  | 99.19 |  |  |  | 0.63 |  | 0.60 | [8 empty] | 5.72 |  |  |  |  | 0.00
1999 |  |  |  | 4983.97 |  |  | 8588 |  |  |  | 625 | [10 empty] | 91.06 |  |  |  | 91.06 | [5 empty] | 90.78 |  |  | 97.77 |  |  |  | 4.07 |  | 3.86 | [8 empty] | 5.08 |  |  |  |  | 0.00
2000 |  |  |  | 3936.12 |  |  | 7686 |  |  |  | 625 | [10 empty] | 71.70 |  |  |  | 71.70 | [5 empty] | 71.70 |  |  | 87.50 |  |  |  | 17.72 |  | 15.45 | [8 empty] | 12.86 |  |  |  |  | 0.00
2001 |  |  |  | 4293.57 |  |  | 8476 |  |  |  | 625 | [10 empty] | 76.57 |  |  |  | 77.15 | [5 empty] | 78.21 |  |  | 96.49 |  |  |  | 19.60 |  | 18.81 | [8 empty] | 4.03 |  |  |  |  | 0.58
2002 |  |  |  | 1945.61 |  |  | 3751 |  |  |  | 625 | [10 empty] | 35.73 |  |  |  | 36.99 | [5 empty] | 35.54 |  |  | 42.82 |  |  |  | 61.93 |  | 60.74 | [8 empty] | 2.27 |  |  |  |  | 1.26
2003 |  |  |  | 3782.85 |  |  | 6874 |  |  |  | 625 | [10 empty] | 69.44 |  |  |  | 69.44 | [5 empty] | 69.09 |  |  | 78.47 |  |  |  | 14.58 |  | 14.03 | [8 empty] | 16.53 |  |  |  |  | 0.00
2004 |  |  |  | 4082.96 |  |  | 7682 |  |  |  | 625 | [10 empty] | 74.61 |  |  |  | 74.61 | [5 empty] | 74.37 |  |  | 87.45 |  |  |  | 10.63 |  | 14.69 | [8 empty] | 10.69 |  |  |  |  | 0.00
2005 |  |  |  | 4821.85 |  |  | 8570 |  |  |  | 625 | [10 empty] | 87.85 |  |  |  | 87.85 | [5 empty] | 88.07 |  |  | 97.83 |  |  |  | 4.80 |  | 4.64 | [8 empty] | 7.51 |  |  |  |  | 0.00
2006 |  |  |  | 3297.00 |  |  | 6456 |  |  |  | 625 | [10 empty] | 60.46 |  |  |  | 64.44 | [5 empty] | 60.22 |  |  | 73.70 |  |  |  | 12.00 |  | 14.99 | [8 empty] | 20.57 |  |  |  |  | 3.98
2007 |  |  |  | 4829.04 |  |  | 8480 |  |  |  | 625 | [10 empty] | 88.26 |  |  |  | 89.19 | [5 empty] | 88.20 |  |  | 96.80 |  |  |  | 5.15 |  | 4.87 | [8 empty] | 5.94 |  |  |  |  | 0.93
2008 |  |  |  | 4780.78 |  |  | 8494 |  |  |  | 615 | [10 empty] | 88.23 |  |  |  | 88.40 | [5 empty] | 88.14 |  |  | 96.70 |  |  |  | 7.06 |  | 7.23 | [8 empty] | 4.37 |  |  |  |  | 0.17
2009 |  |  |  | 4151.18 |  |  | 7303 |  |  |  | 605 | [10 empty] | 78.30 |  |  |  | 78.30 | [5 empty] | 78.01 |  |  | 83.37 |  |  |  | 3.43 |  | 5.01 | [8 empty] | 16.70 |  |  |  |  | 0.00
2010 |  |  |  | 4531.25 |  |  | 8345 |  |  |  | 605 | [10 empty] | 85.50 |  |  |  | 87.13 | [5 empty] | 85.50 |  |  | 95.26 |  |  |  | 9.83 |  | 9.97 | [8 empty] | 2.91 |  |  |  |  | 1.63
2011 |  |  |  | 4417.91 |  |  | 8235 |  |  |  | 605 | [10 empty] | 83.48 |  |  |  | 85.67 | [5 empty] | 83.36 |  |  | 94.01 |  |  |  | 12.08 |  | 11.95 | [8 empty] | 2.39 |  |  |  |  | 2.18
2012 |  |  |  | 3717.79 |  |  | 6632 |  |  |  | 595 | [10 empty] | 71.43 |  |  |  | 71.43 | [5 empty] | 71.13 |  |  | 75.50 |  |  |  | 3.31 |  | 10.85 | [8 empty] | 17.72 |  |  |  |  | 0.00
2013 |  |  |  | 4672.85 |  |  | 8287 |  |  |  | 595 | [10 empty] | 89.68 |  |  |  | 91.85 | [5 empty] | 89.65 |  |  | 94.60 |  |  |  | 4.83 |  | 4.74 | [8 empty] | 3.41 |  |  |  |  | 2.16
2014 |  |  |  | 4718.74 |  |  | 8274 |  |  |  | 595 | [10 empty] | 90.41 |  |  |  | 90.50 | [5 empty] | 90.53 |  |  | 94.45 |  |  |  | 2.71 |  | 2.52 | [8 empty] | 6.98 |  |  |  |  | 0.09
2015 |  |  |  | 3711.61 |  |  | 6684 |  |  |  | 595 | [10 empty] | 70.90 |  |  |  | 70.91 | [5 empty] | 71.21 |  |  | 76.30 |  |  |  | 4.29 |  | 7.83 | [8 empty] | 21.25 |  |  |  |  | 0.02
2016 |  |  |  | 4982.13 |  |  | 8746 |  |  |  | 595 | [10 empty] | 95.11 |  |  |  | 95.32 | [5 empty] | 95.32 |  |  | 99.57 |  |  |  | 0.96 |  | 1.44 | [8 empty] | 3.23 |  |  |  |  | 0.21
2017 |  |  |  | 4853.06 |  |  | 8710 | [14 empty] | 94.02 |  |  |  | 94.35 | [5 empty] | 93.11 |  |  | 99.43 |  |  |  | 0.80 |  | 2.36 | [8 empty] | 3.29 |  |  |  |  | 0.33
2018 |  |  |  | 3680.98 |  |  | 6602 |  |  |  | 605 | [10 empty] | 69.34 |  |  |  | 70.78 | [5 empty] | 69.46 |  |  | 75.37 |  |  |  | 8.41 |  | 6.49 | [8 empty] | 22.73 |  |  |  |  | 1.44
2019 |  |  |  | 5059.93 |  |  | 8760 |  |  |  | 605 | [10 empty] | 94.81 |  |  |  | 95.01 | [5 empty] | 95.47 |  |  | 100.00 |  |  |  | 0.91 |  | 1.48 | [8 empty] | 3.52 |  |  |  |  | 0.20
2020 |  |  |  | 4904.72 |  |  | 8615 |  |  |  | 605 | [10 empty] | 92.01 |  |  |  | 92.04 | [5 empty] | 92.29 |  |  | 98.08 |  |  |  | 4.03 |  | 4.26 | [8 empty] | 3.70 |  |  |  |  | 0.03
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 169 | [14 empty] | 292
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 576 |  |  |  | 39
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 170
E. |  | Testing of plant systems or components | [39 empty] | 5
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 14 |  |  |  | 15
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 26
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 5
Z. |  | Other | [39 empty] | 10 | [11 empty] | 19
Subtotal | [26 empty] | 169 | [10 empty] | 765 |  |  |  | 364 | [11 empty] | 45
Total | [22 empty] | 169 | [14 empty] | 1174
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 23
12. |  |  | Reactor I&C Systems | [34 empty] | 17
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 167
16. |  |  | Steam generation systems | [34 empty] | 37
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 13
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 9
32. |  |  | Feedwater and Main Steam System | [19 empty] | 169 | [14 empty] | 15
33. |  |  | Circulating Water System | [34 empty] | 26
34. |  |  | Miscellaneous Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 18
Total | [22 empty] | 169 | [14 empty] | 341