## KHMELNITSKI-1
2020 Operating Experience
UA-40 | [8 empty] | KHMELNITSKI-1 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-11-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-12-31
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-08-13
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5624.09 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.22 %
Energy Availability Factor (EAF) | [18 empty] | : | 70.86 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 27.58 %
Unit Capability Factor (UCF) | [18 empty] | : | 70.86 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 1.56 %
Load Factor (LF) | [18 empty] | : | 67.4 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.01 %
Operating Factor (OF) | [18 empty] | : | 71.21 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2529 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 37.19 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 462.09 | [8 empty] | 702.82 |  |  | 582.62 | [6 empty] | 678.96 |  | 394.60 |  |  |  | 680.67 |  |  | 716.13 |  |  | 691.81 | [9 empty] | 714.39 |  |  | 5624.09
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 68.57 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.93 |  | 79.82 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 70.86
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 68.57 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 79.82 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 70.86
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 67.56 | [8 empty] | 99.44 |  |  | 85.18 | [6 empty] | 96.06 |  | 55.83 |  |  |  | 99.51 |  |  | 101.18 |  |  | 101.14 | [9 empty] | 101.07 |  |  | 67.40
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 69.86 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 82.66 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 71.21
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 2.22 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.22
UCL [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 31.43 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 1.81 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 27.58
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 18.36 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.56
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.07 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 187901.09 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.48 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.66 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.73 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 72.85 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 22.42 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.33 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.19 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.2 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 3578.19 |  |  | 5266 |  |  |  | 950 | [10 empty] | 67.05 |  |  |  | 67.05 | [5 empty] | 61.13 |  |  | 74.95 |  |  |  | 32.78 |  | 32.70 | [8 empty] | 0.25 |  |  |  |  | 0.00
1989 |  |  |  | 5872.26 |  |  | 6295 |  |  |  | 950 | [10 empty] | 70.62 |  |  |  | 70.68 | [5 empty] | 70.56 |  |  | 71.86 |  |  |  | 6.04 |  | 4.54 | [8 empty] | 24.78 |  |  |  |  | 0.06
1990 |  |  |  | 6498.57 |  |  | 6870 |  |  |  | 950 | [10 empty] | 77.35 |  |  |  | 77.35 | [5 empty] | 78.09 |  |  | 78.42 |  |  |  | 7.25 |  | 6.05 | [8 empty] | 16.60 |  |  |  |  | 0.00
1991 |  |  |  | 5172.49 |  |  | 5551 |  |  |  | 950 | [10 empty] | 61.23 |  |  |  | 61.23 | [5 empty] | 62.15 |  |  | 63.37 |  |  |  | 11.34 |  | 7.83 | [8 empty] | 30.94 |  |  |  |  | 0.00
1992 |  |  |  | 6075.13 |  |  | 6167 |  |  |  | 950 | [10 empty] | 66.53 |  |  |  | 67.62 | [5 empty] | 72.80 |  |  | 70.21 |  |  |  | 3.06 |  | 2.13 | [8 empty] | 30.25 |  |  |  |  | 1.09
1993 |  |  |  | 5487.72 |  |  | 5782 |  |  |  | 950 | [10 empty] | 65.22 |  |  |  | 65.22 | [5 empty] | 65.94 |  |  | 66.00 |  |  |  | 7.10 |  | 4.98 | [8 empty] | 29.79 |  |  |  |  | 0.00
1994 |  |  |  | 6303.41 |  |  | 6775 |  |  |  | 950 | [10 empty] | 75.51 |  |  |  | 76.05 | [5 empty] | 75.74 |  |  | 77.34 |  |  |  | 4.68 |  | 3.74 | [8 empty] | 20.21 |  |  |  |  | 0.54
1995 |  |  |  | 5700.26 |  |  | 6014 |  |  |  | 950 | [10 empty] | 67.98 |  |  |  | 68.00 | [5 empty] | 68.50 |  |  | 68.65 |  |  |  | 2.15 |  | 1.49 | [8 empty] | 30.51 |  |  |  |  | 0.02
1996 |  |  |  | 4497.91 |  |  | 4854 |  |  |  | 950 | [10 empty] | 53.90 |  |  |  | 54.25 | [5 empty] | 53.90 |  |  | 55.26 |  |  |  | 15.74 |  | 10.13 | [8 empty] | 35.62 |  |  |  |  | 0.34
1997 |  |  |  | 6152.10 |  |  | 6415 |  |  |  | 950 | [10 empty] | 72.56 |  |  |  | 72.78 | [5 empty] | 73.93 |  |  | 73.23 |  |  |  | 7.87 |  | 6.21 | [8 empty] | 21.01 |  |  |  |  | 0.22
1998 |  |  |  | 5499.20 |  |  | 5904 |  |  |  | 950 | [10 empty] | 65.82 |  |  |  | 67.08 | [5 empty] | 66.08 |  |  | 67.40 |  |  |  | 0.11 |  | 0.08 | [8 empty] | 32.85 |  |  |  |  | 1.26
1999 |  |  |  | 5526.69 |  |  | 6506 |  |  |  | 950 | [10 empty] | 66.37 |  |  |  | 66.77 | [5 empty] | 66.41 |  |  | 74.27 |  |  |  | 1.38 |  | 0.94 | [8 empty] | 32.30 |  |  |  |  | 0.39
2000 |  |  |  | 5899.61 |  |  | 6541 |  |  |  | 950 | [10 empty] | 70.36 |  |  |  | 74.25 | [5 empty] | 70.70 |  |  | 74.46 |  |  |  | 0.92 |  | 0.69 | [8 empty] | 25.06 |  |  |  |  | 3.89
2001 |  |  |  | 6167.28 |  |  | 6781 |  |  |  | 950 | [10 empty] | 73.63 |  |  |  | 76.47 | [5 empty] | 73.91 |  |  | 77.20 |  |  |  | 4.40 |  | 3.52 | [8 empty] | 20.01 |  |  |  |  | 2.84
2002 |  |  |  | 6730.45 |  |  | 7049 |  |  |  | 950 | [10 empty] | 79.90 |  |  |  | 80.26 | [5 empty] | 80.88 |  |  | 80.47 |  |  |  | 0.08 |  | 0.06 | [8 empty] | 19.68 |  |  |  |  | 0.35
2003 |  |  |  | 7137.70 |  |  | 7512 |  |  |  | 950 | [10 empty] | 84.89 |  |  |  | 85.42 | [5 empty] | 85.77 |  |  | 85.75 |  |  |  | 0.42 |  | 0.36 | [8 empty] | 14.23 |  |  |  |  | 0.52
2004 |  |  |  | 6325.09 |  |  | 6935 |  |  |  | 950 | [10 empty] | 75.42 |  |  |  | 80.92 | [5 empty] | 75.80 |  |  | 78.95 |  |  |  | 1.33 |  | 1.09 | [8 empty] | 17.99 |  |  |  |  | 5.51
2005 |  |  |  | 6862.81 |  |  | 7433 |  |  |  | 950 | [10 empty] | 84.80 |  |  |  | 84.86 | [5 empty] | 82.47 |  |  | 84.85 |  |  |  | 0.29 |  | 0.24 | [8 empty] | 14.89 |  |  |  |  | 0.06
2006 |  |  |  | 6684.91 |  |  | 7407 |  |  |  | 950 | [10 empty] | 83.49 |  |  |  | 83.88 | [5 empty] | 80.33 |  |  | 84.55 |  |  |  | 0.97 |  | 0.83 | [8 empty] | 15.29 |  |  |  |  | 0.39
2007 |  |  |  | 6905.26 |  |  | 7297 |  |  |  | 950 | [10 empty] | 83.01 |  |  |  | 83.11 | [5 empty] | 82.98 |  |  | 83.30 |  |  |  | 0.30 |  | 1.17 | [8 empty] | 15.72 |  |  |  |  | 0.10
2008 |  |  |  | 6547.17 |  |  | 7237 |  |  |  | 950 | [10 empty] | 81.31 |  |  |  | 82.29 | [5 empty] | 78.46 |  |  | 82.39 |  |  |  | 0.35 |  | 0.29 | [8 empty] | 17.42 |  |  |  |  | 0.98
2009 |  |  |  | 6380.56 |  |  | 7031 |  |  |  | 950 | [10 empty] | 77.84 |  |  |  | 80.05 | [5 empty] | 76.67 |  |  | 80.26 |  |  |  | 0.19 |  | 0.15 | [8 empty] | 19.81 |  |  |  |  | 2.20
2010 |  |  |  | 6587.15 |  |  | 6966 |  |  |  | 950 | [10 empty] | 78.60 |  |  |  | 79.10 | [5 empty] | 79.15 |  |  | 79.52 |  |  |  | 0.73 |  | 0.58 | [8 empty] | 20.32 |  |  |  |  | 0.50
2011 |  |  |  | 6967.34 |  |  | 7253 |  |  |  | 950 | [10 empty] | 82.61 |  |  |  | 82.63 | [5 empty] | 83.72 |  |  | 82.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.37 |  |  |  |  | 0.02
2012 |  |  |  | 7087.23 |  |  | 7592 |  |  |  | 950 | [10 empty] | 84.70 |  |  |  | 86.33 | [5 empty] | 84.93 |  |  | 86.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.67 |  |  |  |  | 1.64
2013 |  |  |  | 6877.19 |  |  | 7681 |  |  |  | 950 | [10 empty] | 87.43 |  |  |  | 87.47 | [5 empty] | 82.64 |  |  | 87.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.53 |  |  |  |  | 0.04
2014 |  |  |  | 3551.74 |  |  | 5920 |  |  |  | 950 | [10 empty] | 48.60 |  |  |  | 48.60 | [5 empty] | 42.68 |  |  | 67.58 |  |  |  | 3.32 |  | 1.67 | [8 empty] | 49.73 |  |  |  |  | 0.00
2015 |  |  |  | 6753.90 |  |  | 7307 |  |  |  | 950 | [10 empty] | 80.97 |  |  |  | 83.01 | [5 empty] | 81.16 |  |  | 83.41 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 16.91 |  |  |  |  | 2.04
2016 |  |  |  | 7276.34 |  |  | 7568 |  |  |  | 950 | [10 empty] | 85.98 |  |  |  | 86.05 | [5 empty] | 87.20 |  |  | 86.16 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 13.94 |  |  |  |  | 0.07
2017 |  |  |  | 5807.27 |  |  | 7443 |  |  |  | 950 | [10 empty] | 71.65 |  |  |  | 84.94 | [5 empty] | 69.78 |  |  | 84.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.06 |  |  |  |  | 13.30
2018 |  |  |  | 5501.15 |  |  | 5799 |  |  |  | 950 | [10 empty] | 65.75 |  |  |  | 65.93 | [5 empty] | 66.10 |  |  | 66.20 |  |  |  | 16.98 |  | 13.49 | [8 empty] | 20.58 |  |  |  |  | 0.19
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 950 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 39.72 | [8 empty] | 60.28 |  |  |  |  | 0.00
2020 |  |  |  | 5624.09 |  |  | 6255 |  |  |  | 950 | [10 empty] | 70.86 |  |  |  | 70.86 | [5 empty] | 67.40 |  |  | 71.21 |  |  |  | 0.22 |  | 27.58 | [8 empty] | 1.56 |  |  |  |  | 0.01
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 2400 | [14 empty] | 370
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1473
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 129 | [14 empty] | 194
E. |  | Testing of plant systems or components | [35 empty] | 12
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 190
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 4
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 129 |  |  |  | 2400 | [10 empty] | 1869 |  |  |  | 375 | [11 empty] | 6
Total | [22 empty] | 2529 | [14 empty] | 2250
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 18
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 16
16. |  |  | Steam generation systems | [34 empty] | 5
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
33. |  |  | Circulating Water System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [19 empty] | 2400 | [14 empty] | 286
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 2400 | [14 empty] | 367

## KHMELNITSKI-2
2020 Operating Experience
UA-41 | [8 empty] | KHMELNITSKI-2 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-02-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2004-08-07
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2005-12-15
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 16 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4835.27 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 63.67 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 65.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 34.16 %
Load Factor (LF) | [18 empty] | : | 57.94 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.15 %
Operating Factor (OF) | [18 empty] | : | 65.86 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2999 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 50.05 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 720.57 | 674.10 |  |  |  | 719.71 |  | 558.07 | [8 empty] | 465.15 |  |  | 589.06 | [6 empty] | 668.80 |  | 439.81 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4835.27
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.94 | [8 empty] | 99.81 |  |  | 100.00 | [6 empty] | 96.99 |  | 68.03 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 63.67
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.94 | [8 empty] | 99.81 |  |  | 100.00 | [6 empty] | 100.00 |  | 90.41 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 65.82
LF [%] |  |  |  |  | 101.95 | 101.95 |  |  |  | 101.96 |  | 81.59 | [8 empty] | 65.81 |  |  | 86.12 | [6 empty] | 94.62 |  | 62.23 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 57.94
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 90.59 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 65.86
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.19 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.19 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.06 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 9.59 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 34.16
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 3.01 |  | 22.38 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.15
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 103265.27 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.75 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.06 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.36 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.6 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.71 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.3 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.31 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2005 |  |  |  | 5581.51 |  |  | 6376 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 36.98 |  |  | 39.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 7178.29 |  |  | 7697 |  |  |  | 950 | [10 empty] | 86.15 |  |  |  | 87.36 | [5 empty] | 86.26 |  |  | 87.87 |  |  |  | 1.35 |  | 1.19 | [8 empty] | 11.45 |  |  |  |  | 1.21
2007 |  |  |  | 7213.44 |  |  | 8008 |  |  |  | 950 | [10 empty] | 89.11 |  |  |  | 91.23 | [5 empty] | 86.68 |  |  | 91.42 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 8.69 |  |  |  |  | 2.11
2008 |  |  |  | 4944.85 |  |  | 5263 |  |  |  | 950 | [10 empty] | 59.64 |  |  |  | 59.69 | [5 empty] | 59.26 |  |  | 59.92 |  |  |  | 30.51 |  | 26.20 | [8 empty] | 14.11 |  |  |  |  | 0.04
2009 |  |  |  | 5841.16 |  |  | 6126 |  |  |  | 950 | [10 empty] | 69.50 |  |  |  | 69.76 | [5 empty] | 70.19 |  |  | 69.93 |  |  |  | 0.09 |  | 14.33 | [8 empty] | 15.91 |  |  |  |  | 0.26
2010 |  |  |  | 5873.72 |  |  | 6124 |  |  |  | 950 | [10 empty] | 69.64 |  |  |  | 69.67 | [5 empty] | 70.58 |  |  | 69.91 |  |  |  | 13.47 |  | 10.84 | [8 empty] | 19.49 |  |  |  |  | 0.03
2011 |  |  |  | 6845.60 |  |  | 7333 |  |  |  | 950 | [10 empty] | 82.13 |  |  |  | 83.51 | [5 empty] | 82.26 |  |  | 83.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.49 |  |  |  |  | 1.38
2012 |  |  |  | 5917.74 |  |  | 6774 |  |  |  | 950 | [10 empty] | 71.02 |  |  |  | 76.29 | [5 empty] | 70.92 |  |  | 77.12 |  |  |  | 7.49 |  | 6.17 | [8 empty] | 17.54 |  |  |  |  | 5.26
2013 |  |  |  | 7027.15 |  |  | 7391 |  |  |  | 950 | [10 empty] | 83.99 |  |  |  | 84.26 | [5 empty] | 84.44 |  |  | 84.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.74 |  |  |  |  | 0.27
2014 |  |  |  | 6773.28 |  |  | 7121 |  |  |  | 950 | [10 empty] | 80.58 |  |  |  | 80.70 | [5 empty] | 81.39 |  |  | 81.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.30 |  |  |  |  | 0.12
2015 |  |  |  | 6042.26 |  |  | 7523 |  |  |  | 950 | [10 empty] | 83.04 |  |  |  | 85.31 | [5 empty] | 72.61 |  |  | 85.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.69 |  |  |  |  | 2.27
2016 |  |  |  | 6996.59 |  |  | 7587 |  |  |  | 950 | [10 empty] | 85.44 |  |  |  | 86.24 | [5 empty] | 83.84 |  |  | 86.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.76 |  |  |  |  | 0.79
2017 |  |  |  | 6908.09 |  |  | 7354 |  |  |  | 950 | [10 empty] | 81.91 |  |  |  | 83.75 | [5 empty] | 83.01 |  |  | 83.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.25 |  |  |  |  | 1.84
2018 |  |  |  | 6493.12 |  |  | 6816 |  |  |  | 950 | [10 empty] | 77.09 |  |  |  | 77.55 | [5 empty] | 78.02 |  |  | 77.81 |  |  |  | 2.52 |  | 2.01 | [8 empty] | 20.44 |  |  |  |  | 0.46
2019 |  |  |  | 7219.58 |  |  | 7679 |  |  |  | 950 | [10 empty] | 86.17 |  |  |  | 87.54 | [5 empty] | 86.75 |  |  | 87.66 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 12.42 |  |  |  |  | 1.36
2020 |  |  |  | 4835.27 |  |  | 5785 |  |  |  | 950 | [10 empty] | 63.67 |  |  |  | 65.82 | [5 empty] | 57.94 |  |  | 65.86 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 34.16 |  |  |  |  | 2.15
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2005 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 268
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2998 | [14 empty] | 1403
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 40
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 83
Subtotal | [22 empty] | 2998 | [14 empty] | 1443 |  |  |  | 351
Total | [22 empty] | 2998 | [14 empty] | 1794
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2005 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 253
Total | [37 empty] | 268

## ROVNO-1
2020 Operating Experience
UA-27 | [8 empty] | ROVNO-1 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-08-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-12-22
Gross electrical power | [12 empty] | : |  |  | 420 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-09-22
Reference unit power (net) | [12 empty] | : |  |  | 381 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 295.8
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2895 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.91 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.57 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.71 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.57 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.72 %
Load Factor (LF) | [18 empty] | : | 86.5 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 88.49 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1011 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 11.97 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 47.82 | 145.74 |  |  |  | 234.86 |  | 231.74 | [8 empty] | 268.63 |  |  | 281.77 | [6 empty] | 293.23 |  | 289.58 |  |  |  | 277.04 |  |  | 297.59 |  |  | 288.61 | [9 empty] | 238.39 |  |  | 2895.00
EAF [%] |  |  |  |  | 17.31 | 53.18 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 97.76 |  |  | 100.00 | [6 empty] | 99.36 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 82.65 |  |  | 87.57
UCF [%] |  |  |  |  | 17.31 | 53.18 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 97.76 |  |  | 100.00 | [6 empty] | 99.36 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 82.65 |  |  | 87.57
LF [%] |  |  |  |  | 16.87 | 54.96 |  |  |  | 82.96 |  | 84.48 | [8 empty] | 94.77 |  |  | 102.72 | [6 empty] | 103.44 |  | 102.16 |  |  |  | 100.99 |  |  | 104.84 |  |  | 105.21 | [9 empty] | 84.10 |  |  | 86.50
OF [%] |  |  |  |  | 17.47 | 54.02 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 92.61 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 97.04 |  |  | 88.49
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.24 |  |  | 0.00 | [6 empty] | 0.57 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 17.35 |  |  | 1.91
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.24 |  |  | 0.00 | [6 empty] | 0.57 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 17.35 |  |  | 1.71
PUF [%] |  |  |  |  | 82.69 | 46.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.07 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.72
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 100417 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.76 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.27 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.74 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.99 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.13 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.64 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.52 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 1685.10 |  |  | 6968 |  |  |  | 361 | [10 empty] | 88.09 |  |  |  | 88.09 | [5 empty] | 90.12 |  |  | 99.95 |  |  |  | 11.91 |  | 11.91 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 1725.21 |  |  | 5498 |  |  |  | 361 | [10 empty] | 51.94 |  |  |  | 51.94 | [5 empty] | 54.55 |  |  | 62.76 |  |  |  | 13.79 |  | 8.31 | [8 empty] | 39.75 |  |  |  |  | 0.00
1983 |  |  |  | 2036.59 |  |  | 6752 |  |  |  | 361 | [10 empty] | 61.57 |  |  |  | 61.57 | [5 empty] | 64.40 |  |  | 77.08 |  |  |  | 23.01 |  | 18.40 | [8 empty] | 20.03 |  |  |  |  | 0.00
1984 |  |  |  | 2686.26 |  |  | 7782 |  |  |  | 361 | [10 empty] | 82.48 |  |  |  | 82.48 | [5 empty] | 84.71 |  |  | 88.59 |  |  |  | 6.69 |  | 5.92 | [8 empty] | 11.60 |  |  |  |  | 0.00
1985 |  |  |  | 2664.82 |  |  | 7636 |  |  |  | 365 | [10 empty] | 81.42 |  |  |  | 81.42 | [5 empty] | 83.34 |  |  | 87.17 |  |  |  | 6.45 |  | 5.61 | [8 empty] | 12.97 |  |  |  |  | 0.00
1986 |  |  |  | 2712.73 |  |  | 7606 |  |  |  | 361 | [10 empty] | 77.54 |  |  |  | 77.54 | [5 empty] | 85.78 |  |  | 86.83 |  |  |  | 10.18 |  | 8.79 | [8 empty] | 13.67 |  |  |  |  | 0.00
1987 |  |  |  | 3040.76 |  |  | 7756 |  |  |  | 402 | [10 empty] | 86.63 |  |  |  | 86.63 | [5 empty] | 86.35 |  |  | 88.54 |  |  |  | 3.48 |  | 3.12 | [8 empty] | 10.25 |  |  |  |  | 0.00
1988 |  |  |  | 2717.96 |  |  | 7877 |  |  |  | 361 | [10 empty] | 86.02 |  |  |  | 86.02 | [5 empty] | 85.71 |  |  | 89.67 |  |  |  | 3.35 |  | 2.98 | [8 empty] | 11.00 |  |  |  |  | 0.00
1989 |  |  |  | 2823.85 |  |  | 7994 |  |  |  | 361 | [10 empty] | 89.20 |  |  |  | 89.20 | [5 empty] | 89.30 |  |  | 91.26 |  |  |  | 2.61 |  | 2.39 | [8 empty] | 8.41 |  |  |  |  | 0.00
1990 |  |  |  | 2590.56 |  |  | 7265 |  |  |  | 361 | [10 empty] | 79.27 |  |  |  | 79.27 | [5 empty] | 81.92 |  |  | 82.93 |  |  |  | 4.30 |  | 3.57 | [8 empty] | 17.17 |  |  |  |  | 0.00
1991 |  |  |  | 2640.06 |  |  | 7430 |  |  |  | 361 | [10 empty] | 81.37 |  |  |  | 81.37 | [5 empty] | 83.48 |  |  | 84.82 |  |  |  | 4.85 |  | 4.15 | [8 empty] | 14.49 |  |  |  |  | 0.00
1992 |  |  |  | 3082.91 |  |  | 7989 |  |  |  | 403 | [10 empty] | 87.29 |  |  |  | 88.47 | [5 empty] | 87.00 |  |  | 90.95 |  |  |  | 1.66 |  | 1.49 | [8 empty] | 10.04 |  |  |  |  | 1.18
1993 |  |  |  | 2584.41 |  |  | 7159 |  |  |  | 406 | [10 empty] | 81.42 |  |  |  | 82.96 | [5 empty] | 72.67 |  |  | 81.72 |  |  |  | 0.64 |  | 0.53 | [8 empty] | 16.51 |  |  |  |  | 1.54
1994 |  |  |  | 2578.63 |  |  | 7378 |  |  |  | 361 | [10 empty] | 81.70 |  |  |  | 81.75 | [5 empty] | 81.54 |  |  | 84.22 |  |  |  | 0.81 |  | 0.67 | [8 empty] | 17.59 |  |  |  |  | 0.05
1995 |  |  |  | 2747.40 |  |  | 7756 |  |  |  | 361 | [10 empty] | 86.12 |  |  |  | 88.36 | [5 empty] | 86.88 |  |  | 88.54 |  |  |  | 0.73 |  | 0.65 | [8 empty] | 10.99 |  |  |  |  | 2.24
1996 |  |  |  | 2432.03 |  |  | 6960 |  |  |  | 361 | [10 empty] | 76.70 |  |  |  | 78.99 | [5 empty] | 76.70 |  |  | 79.23 |  |  |  | 1.97 |  | 1.59 | [8 empty] | 19.42 |  |  |  |  | 2.29
1997 |  |  |  | 2701.14 |  |  | 7867 |  |  |  | 361 | [10 empty] | 81.61 |  |  |  | 82.20 | [5 empty] | 85.42 |  |  | 89.81 |  |  |  | 0.96 |  | 0.79 | [8 empty] | 17.01 |  |  |  |  | 0.59
1998 |  |  |  | 2612.94 |  |  | 6912 |  |  |  | 361 | [10 empty] | 77.76 |  |  |  | 78.11 | [5 empty] | 82.63 |  |  | 78.90 |  |  |  | 1.39 |  | 1.10 | [8 empty] | 20.79 |  |  |  |  | 0.35
1999 |  |  |  | 2240.49 |  |  | 6214 |  |  |  | 361 | [10 empty] | 82.83 |  |  |  | 82.83 | [5 empty] | 70.85 |  |  | 70.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.17 |  |  |  |  | 0.00
2000 |  |  |  | 2733.72 |  |  | 7580 |  |  |  | 361 | [10 empty] | 82.63 |  |  |  | 85.70 | [5 empty] | 86.21 |  |  | 86.29 |  |  |  | 2.16 |  | 1.89 | [8 empty] | 12.41 |  |  |  |  | 3.06
2001 |  |  |  | 2753.81 |  |  | 7369 |  |  |  | 381 | [10 empty] | 81.38 |  |  |  | 82.64 | [5 empty] | 82.28 |  |  | 83.89 |  |  |  | 0.88 |  | 0.74 | [8 empty] | 16.63 |  |  |  |  | 1.25
2002 |  |  |  | 2656.23 |  |  | 7242 |  |  |  | 381 | [10 empty] | 79.91 |  |  |  | 81.04 | [5 empty] | 79.59 |  |  | 82.67 |  |  |  | 2.33 |  | 1.93 | [8 empty] | 17.02 |  |  |  |  | 1.14
2003 |  |  |  | 2816.14 |  |  | 7560 |  |  |  | 381 | [10 empty] | 83.46 |  |  |  | 84.53 | [5 empty] | 84.38 |  |  | 86.30 |  |  |  | 2.55 |  | 2.46 | [8 empty] | 13.00 |  |  |  |  | 1.07
2004 |  |  |  | 2876.62 |  |  | 7914 |  |  |  | 381 | [10 empty] | 86.54 |  |  |  | 87.91 | [5 empty] | 85.95 |  |  | 90.10 |  |  |  | 2.25 |  | 2.02 | [8 empty] | 10.06 |  |  |  |  | 1.37
2005 |  |  |  | 2362.64 |  |  | 7753 |  |  |  | 381 | [10 empty] | 84.53 |  |  |  | 85.82 | [5 empty] | 70.79 |  |  | 88.50 |  |  |  | 3.23 |  | 2.87 | [8 empty] | 11.31 |  |  |  |  | 1.29
2006 |  |  |  | 2493.56 |  |  | 7012 |  |  |  | 381 | [10 empty] | 77.99 |  |  |  | 78.43 | [5 empty] | 74.71 |  |  | 80.05 |  |  |  | 1.38 |  | 1.10 | [8 empty] | 20.47 |  |  |  |  | 0.44
2007 |  |  |  | 2079.02 |  |  | 5882 |  |  |  | 381 | [10 empty] | 65.73 |  |  |  | 66.26 | [5 empty] | 62.29 |  |  | 67.15 |  |  |  | 0.65 |  | 0.44 | [8 empty] | 33.30 |  |  |  |  | 0.53
2008 |  |  |  | 2445.73 |  |  | 6815 |  |  |  | 381 | [10 empty] | 75.60 |  |  |  | 76.22 | [5 empty] | 73.08 |  |  | 77.58 |  |  |  | 1.76 |  | 1.36 | [8 empty] | 22.42 |  |  |  |  | 0.62
2009 |  |  |  | 113.11 |  |  | 308 |  |  |  | 381 | [10 empty] | 3.48 |  |  |  | 3.48 | [5 empty] | 3.39 |  |  | 3.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 96.52 |  |  |  |  | 0.00
2010 |  |  |  | 2087.55 |  |  | 5572 |  |  |  | 381 | [10 empty] | 63.70 |  |  |  | 64.20 | [5 empty] | 62.55 |  |  | 63.61 |  |  |  | 0.33 |  | 0.21 | [8 empty] | 35.59 |  |  |  |  | 0.49
2011 |  |  |  | 2517.09 |  |  | 6867 |  |  |  | 381 | [10 empty] | 81.69 |  |  |  | 81.91 | [5 empty] | 75.42 |  |  | 78.39 |  |  |  | 0.09 |  | 0.07 | [8 empty] | 18.02 |  |  |  |  | 0.22
2012 |  |  |  | 2293.50 |  |  | 6596 |  |  |  | 381 | [10 empty] | 84.59 |  |  |  | 85.11 | [5 empty] | 68.53 |  |  | 75.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.89 |  |  |  |  | 0.53
2013 |  |  |  | 1507.59 |  |  | 4362 |  |  |  | 381 | [10 empty] | 82.77 |  |  |  | 83.61 | [5 empty] | 45.17 |  |  | 49.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.39 |  |  |  |  | 0.84
2014 |  |  |  | 2941.31 |  |  | 8052 |  |  |  | 381 | [10 empty] | 95.95 |  |  |  | 96.88 | [5 empty] | 88.13 |  |  | 91.92 |  |  |  | 0.24 |  | 0.24 | [8 empty] | 2.88 |  |  |  |  | 0.94
2015 |  |  |  | 2713.77 |  |  | 7284 |  |  |  | 381 | [10 empty] | 81.35 |  |  |  | 81.99 | [5 empty] | 81.31 |  |  | 83.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.01 |  |  |  |  | 0.63
2016 |  |  |  | 3031.66 |  |  | 7918 |  |  |  | 381 | [10 empty] | 89.07 |  |  |  | 89.60 | [5 empty] | 90.59 |  |  | 90.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.40 |  |  |  |  | 0.53
2017 |  |  |  | 2944.90 |  |  | 7978 |  |  |  | 381 | [10 empty] | 89.64 |  |  |  | 90.09 | [5 empty] | 88.24 |  |  | 91.07 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 9.89 |  |  |  |  | 0.45
2018 |  |  |  | 2986.77 |  |  | 7778 |  |  |  | 381 | [10 empty] | 87.24 |  |  |  | 87.99 | [5 empty] | 89.49 |  |  | 88.79 |  |  |  | 1.00 |  | 0.89 | [8 empty] | 11.12 |  |  |  |  | 0.75
2019 |  |  |  | 2828.40 |  |  | 7419 |  |  |  | 381 | [10 empty] | 83.35 |  |  |  | 84.05 | [5 empty] | 84.74 |  |  | 84.69 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 15.90 |  |  |  |  | 0.70
2020 |  |  |  | 2895.00 |  |  | 7773 |  |  |  | 381 | [10 empty] | 87.57 |  |  |  | 87.57 | [5 empty] | 86.50 |  |  | 88.49 |  |  |  | 1.91 |  | 1.71 | [8 empty] | 10.72 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 38 | [14 empty] | 38
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 933 | [14 empty] | 1367
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 106
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 10
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 38 | [19 empty] | 112
L. |  | Human factor related | [39 empty] | 0
M. |  | Governmental requirements or court decisions | [39 empty] | 1
Subtotal | [22 empty] | 933 |  |  |  | 38 | [6 empty] | 38 |  |  |  | 1473 |  |  |  | 39 | [11 empty] | 122
Total | [22 empty] | 1009 | [14 empty] | 1634
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [19 empty] | 17 | [14 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 6
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [19 empty] | 22 | [14 empty] | 5
Total | [22 empty] | 39 | [14 empty] | 36

## ROVNO-2
2020 Operating Experience
UA-28 | [8 empty] | ROVNO-2 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-10-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-12-22
Gross electrical power | [12 empty] | : |  |  | 415 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1982-07-29
Reference unit power (net) | [12 empty] | : |  |  | 376 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 295.8
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2896.19 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.33 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.68 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.29 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.49 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.22 %
Load Factor (LF) | [18 empty] | : | 87.69 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.8 %
Operating Factor (OF) | [18 empty] | : | 90.1 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 870 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 22.98 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 288.88 | 267.23 |  |  |  | 117.67 |  | 54.05 | [8 empty] | 285.31 |  |  | 251.29 | [6 empty] | 268.03 |  | 234.83 |  |  |  | 265.65 |  |  | 289.12 |  |  | 284.69 | [9 empty] | 289.45 |  |  | 2896.19
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 42.47 |  | 20.96 | [8 empty] | 100.00 |  |  | 93.87 | [6 empty] | 97.19 |  | 97.57 |  |  |  | 99.69 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.68
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 45.05 |  | 21.88 | [8 empty] | 100.00 |  |  | 96.46 | [6 empty] | 99.11 |  | 98.96 |  |  |  | 99.90 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.49
LF [%] |  |  |  |  | 103.26 | 102.11 |  |  |  | 42.12 |  | 19.96 | [8 empty] | 101.99 |  |  | 92.82 | [6 empty] | 95.81 |  | 83.94 |  |  |  | 98.13 |  |  | 103.21 |  |  | 105.16 | [9 empty] | 103.47 |  |  | 87.69
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 45.22 |  | 35.69 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.10
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 3.54 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.33
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 3.54 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.29
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 54.95 |  | 78.12 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.89 |  | 1.04 |  |  |  | 0.10 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 11.22
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 2.57 |  | 0.92 | [8 empty] | 0.00 |  |  | 2.59 | [6 empty] | 1.93 |  | 1.39 |  |  |  | 0.21 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.80
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 101367.19 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.33 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.39 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.8 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.34 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.86 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.56 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.95 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.77 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1982 |  |  |  | 2062.20 |  |  | 8011 |  |  |  | 384 | [10 empty] | 88.98 |  |  |  | 88.98 | [5 empty] | 85.84 |  |  | 99.70 |  |  |  | 11.02 |  | 11.02 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 1926.94 |  |  | 5572 |  |  |  | 384 | [10 empty] | 58.00 |  |  |  | 58.00 | [5 empty] | 57.28 |  |  | 63.61 |  |  |  | 9.34 |  | 5.98 | [8 empty] | 36.02 |  |  |  |  | 0.00
1984 |  |  |  | 2808.20 |  |  | 7884 |  |  |  | 384 | [10 empty] | 83.05 |  |  |  | 83.05 | [5 empty] | 83.25 |  |  | 89.75 |  |  |  | 6.84 |  | 6.09 | [8 empty] | 10.85 |  |  |  |  | 0.00
1985 |  |  |  | 2913.46 |  |  | 7994 |  |  |  | 384 | [10 empty] | 86.04 |  |  |  | 86.04 | [5 empty] | 86.61 |  |  | 91.26 |  |  |  | 6.57 |  | 6.05 | [8 empty] | 7.91 |  |  |  |  | 0.00
1986 |  |  |  | 2891.75 |  |  | 7819 |  |  |  | 384 | [10 empty] | 82.99 |  |  |  | 82.99 | [5 empty] | 85.97 |  |  | 89.26 |  |  |  | 5.16 |  | 4.52 | [8 empty] | 12.50 |  |  |  |  | 0.00
1987 |  |  |  | 3166.38 |  |  | 7649 |  |  |  | 416 | [10 empty] | 86.26 |  |  |  | 86.26 | [5 empty] | 86.89 |  |  | 87.32 |  |  |  | 1.88 |  | 1.65 | [8 empty] | 12.09 |  |  |  |  | 0.00
1988 |  |  |  | 2778.30 |  |  | 7875 |  |  |  | 384 | [10 empty] | 85.78 |  |  |  | 85.78 | [5 empty] | 82.37 |  |  | 89.65 |  |  |  | 5.54 |  | 5.03 | [8 empty] | 9.19 |  |  |  |  | 0.00
1989 |  |  |  | 2700.39 |  |  | 7989 |  |  |  | 384 | [10 empty] | 86.27 |  |  |  | 86.27 | [5 empty] | 80.28 |  |  | 91.20 |  |  |  | 4.14 |  | 3.73 | [8 empty] | 10.01 |  |  |  |  | 0.00
1990 |  |  |  | 2798.97 |  |  | 7815 |  |  |  | 384 | [10 empty] | 83.14 |  |  |  | 83.14 | [5 empty] | 83.21 |  |  | 89.21 |  |  |  | 8.39 |  | 7.62 | [8 empty] | 9.24 |  |  |  |  | 0.00
1991 |  |  |  | 2393.20 |  |  | 6560 |  |  |  | 384 | [10 empty] | 70.99 |  |  |  | 70.99 | [5 empty] | 71.14 |  |  | 74.89 |  |  |  | 5.07 |  | 3.79 | [8 empty] | 25.22 |  |  |  |  | 0.00
1992 |  |  |  | 2983.74 |  |  | 7487 |  |  |  | 416 | [10 empty] | 82.92 |  |  |  | 83.76 | [5 empty] | 81.65 |  |  | 85.23 |  |  |  | 7.26 |  | 6.56 | [8 empty] | 9.69 |  |  |  |  | 0.84
1993 |  |  |  | 2053.75 |  |  | 5981 |  |  |  | 406 | [10 empty] | 64.35 |  |  |  | 66.00 | [5 empty] | 57.75 |  |  | 68.28 |  |  |  | 24.88 |  | 21.86 | [8 empty] | 12.14 |  |  |  |  | 1.65
1994 |  |  |  | 2690.67 |  |  | 7626 |  |  |  | 384 | [10 empty] | 83.12 |  |  |  | 83.14 | [5 empty] | 79.99 |  |  | 87.05 |  |  |  | 2.77 |  | 2.36 | [8 empty] | 14.50 |  |  |  |  | 0.02
1995 |  |  |  | 2568.47 |  |  | 7215 |  |  |  | 384 | [10 empty] | 76.36 |  |  |  | 79.58 | [5 empty] | 76.36 |  |  | 82.36 |  |  |  | 0.86 |  | 0.69 | [8 empty] | 19.72 |  |  |  |  | 3.23
1996 |  |  |  | 2783.13 |  |  | 7905 |  |  |  | 384 | [10 empty] | 82.46 |  |  |  | 87.76 | [5 empty] | 82.51 |  |  | 89.99 |  |  |  | 1.44 |  | 1.29 | [8 empty] | 10.95 |  |  |  |  | 5.29
1997 |  |  |  | 2585.58 |  |  | 6847 |  |  |  | 384 | [10 empty] | 76.50 |  |  |  | 77.60 | [5 empty] | 76.86 |  |  | 78.16 |  |  |  | 3.29 |  | 2.64 | [8 empty] | 19.76 |  |  |  |  | 1.10
1998 |  |  |  | 2739.64 |  |  | 7424 |  |  |  | 384 | [10 empty] | 81.23 |  |  |  | 83.18 | [5 empty] | 81.44 |  |  | 84.75 |  |  |  | 3.17 |  | 2.72 | [8 empty] | 14.10 |  |  |  |  | 1.95
1999 |  |  |  | 2543.67 |  |  | 6958 |  |  |  | 384 | [10 empty] | 75.47 |  |  |  | 77.96 | [5 empty] | 75.62 |  |  | 79.43 |  |  |  | 2.35 |  | 1.88 | [8 empty] | 20.16 |  |  |  |  | 2.49
2000 |  |  |  | 2718.18 |  |  | 7460 |  |  |  | 384 | [10 empty] | 80.29 |  |  |  | 84.00 | [5 empty] | 80.59 |  |  | 84.93 |  |  |  | 4.50 |  | 3.95 | [8 empty] | 12.04 |  |  |  |  | 3.71
2001 |  |  |  | 2796.91 |  |  | 7691 |  |  |  | 376 | [10 empty] | 83.23 |  |  |  | 86.63 | [5 empty] | 84.68 |  |  | 87.56 |  |  |  | 1.38 |  | 1.21 | [8 empty] | 12.16 |  |  |  |  | 3.40
2002 |  |  |  | 2861.82 |  |  | 7756 |  |  |  | 376 | [10 empty] | 85.72 |  |  |  | 86.51 | [5 empty] | 86.89 |  |  | 88.54 |  |  |  | 1.57 |  | 1.38 | [8 empty] | 12.12 |  |  |  |  | 0.79
2003 |  |  |  | 2784.22 |  |  | 7376 |  |  |  | 376 | [10 empty] | 81.60 |  |  |  | 82.65 | [5 empty] | 84.53 |  |  | 84.20 |  |  |  | 1.55 |  | 1.30 | [8 empty] | 16.06 |  |  |  |  | 1.04
2004 |  |  |  | 2999.69 |  |  | 8047 |  |  |  | 376 | [10 empty] | 88.38 |  |  |  | 89.45 | [5 empty] | 90.82 |  |  | 91.61 |  |  |  | 1.25 |  | 1.13 | [8 empty] | 9.42 |  |  |  |  | 1.06
2005 |  |  |  | 2548.99 |  |  | 7527 |  |  |  | 376 | [10 empty] | 85.95 |  |  |  | 86.54 | [5 empty] | 77.39 |  |  | 85.92 |  |  |  | 0.98 |  | 0.85 | [8 empty] | 12.60 |  |  |  |  | 0.59
2006 |  |  |  | 2627.46 |  |  | 7727 |  |  |  | 376 | [10 empty] | 83.31 |  |  |  | 84.46 | [5 empty] | 79.77 |  |  | 88.21 |  |  |  | 2.42 |  | 2.10 | [8 empty] | 13.45 |  |  |  |  | 1.15
2007 |  |  |  | 2082.89 |  |  | 5672 |  |  |  | 376 | [10 empty] | 62.75 |  |  |  | 63.70 | [5 empty] | 63.24 |  |  | 64.75 |  |  |  | 1.59 |  | 1.03 | [8 empty] | 35.28 |  |  |  |  | 0.94
2008 |  |  |  | 2650.26 |  |  | 7203 |  |  |  | 376 | [10 empty] | 80.98 |  |  |  | 81.47 | [5 empty] | 80.24 |  |  | 82.00 |  |  |  | 1.28 |  | 1.06 | [8 empty] | 17.48 |  |  |  |  | 0.49
2009 |  |  |  | 2536.86 |  |  | 7603 |  |  |  | 376 | [10 empty] | 84.82 |  |  |  | 85.56 | [5 empty] | 77.02 |  |  | 86.79 |  |  |  | 0.54 |  | 0.46 | [8 empty] | 13.97 |  |  |  |  | 0.74
2010 |  |  |  | 1531.71 |  |  | 4270 |  |  |  | 376 | [10 empty] | 47.41 |  |  |  | 47.55 | [5 empty] | 46.50 |  |  | 48.74 |  |  |  | 0.57 |  | 0.27 | [8 empty] | 52.18 |  |  |  |  | 0.14
2011 |  |  |  | 2211.80 |  |  | 6632 |  |  |  | 376 | [10 empty] | 77.68 |  |  |  | 78.67 | [5 empty] | 67.15 |  |  | 75.71 |  |  |  | 0.27 |  | 0.22 | [8 empty] | 21.11 |  |  |  |  | 0.99
2012 |  |  |  | 2568.64 |  |  | 7115 |  |  |  | 376 | [10 empty] | 80.08 |  |  |  | 80.81 | [5 empty] | 77.77 |  |  | 81.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.19 |  |  |  |  | 0.73
2013 |  |  |  | 2246.85 |  |  | 5886 |  |  |  | 376 | [10 empty] | 88.35 |  |  |  | 88.63 | [5 empty] | 68.22 |  |  | 67.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.37 |  |  |  |  | 0.28
2014 |  |  |  | 2192.26 |  |  | 6579 |  |  |  | 376 | [10 empty] | 81.01 |  |  |  | 81.45 | [5 empty] | 66.56 |  |  | 75.10 |  |  |  | 0.74 |  | 0.61 | [8 empty] | 17.94 |  |  |  |  | 0.43
2015 |  |  |  | 2711.54 |  |  | 7363 |  |  |  | 376 | [10 empty] | 83.05 |  |  |  | 83.71 | [5 empty] | 82.32 |  |  | 84.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.29 |  |  |  |  | 0.66
2016 |  |  |  | 2883.55 |  |  | 7606 |  |  |  | 376 | [10 empty] | 85.43 |  |  |  | 85.77 | [5 empty] | 87.31 |  |  | 86.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.23 |  |  |  |  | 0.35
2017 |  |  |  | 2941.91 |  |  | 7890 |  |  |  | 376 | [10 empty] | 88.88 |  |  |  | 89.15 | [5 empty] | 89.32 |  |  | 90.07 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 10.84 |  |  |  |  | 0.27
2018 |  |  |  | 2981.26 |  |  | 7794 |  |  |  | 376 | [10 empty] | 87.40 |  |  |  | 87.85 | [5 empty] | 90.51 |  |  | 88.97 |  |  |  | 0.51 |  | 0.45 | [8 empty] | 11.70 |  |  |  |  | 0.45
2019 |  |  |  | 2785.09 |  |  | 7395 |  |  |  | 376 | [10 empty] | 83.01 |  |  |  | 83.84 | [5 empty] | 84.56 |  |  | 84.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.16 |  |  |  |  | 0.82
2020 |  |  |  | 2896.19 |  |  | 7914 |  |  |  | 376 | [10 empty] | 87.68 |  |  |  | 88.49 | [5 empty] | 87.69 |  |  | 90.10 |  |  |  | 0.33 |  | 0.29 | [8 empty] | 11.22 |  |  |  |  | 0.80
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1982 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 102
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 870 | [14 empty] | 1129
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 165
E. |  | Testing of plant systems or components | [35 empty] | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 9
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 67
L. |  | Human factor related | [39 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 1
Z. |  | Other | [35 empty] | 28
Subtotal | [22 empty] | 870 | [14 empty] | 1322 |  |  |  | 104 | [11 empty] | 76
Total | [22 empty] | 870 | [14 empty] | 1502
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1982 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 61
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 0
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 6
Total | [37 empty] | 100

## ROVNO-3
2020 Operating Experience
UA-29 | [8 empty] | ROVNO-3 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-02-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-12-21
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-05-16
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.4
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4974.66 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.65 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.41 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.56 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.86 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.57 %
Load Factor (LF) | [18 empty] | : | 59.61 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.46 %
Operating Factor (OF) | [18 empty] | : | 65.93 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2993 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 31.7 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 690.32 | 607.85 |  |  |  | 689.67 |  | 649.95 | [8 empty] | 355.37 |  |  | 0.00 | [6 empty] | 0.00 |  | 561.92 |  |  |  | 657.80 |  |  | 584.66 |  |  | 177.11 | [9 empty] | 0.00 |  |  | 4974.66
EAF [%] |  |  |  |  | 99.10 | 93.24 |  |  |  | 98.90 |  | 95.66 | [8 empty] | 97.84 |  |  | 100.00 | [6 empty] | 100.00 |  | 96.55 |  |  |  | 96.95 |  |  | 83.85 |  |  | 27.18 | [9 empty] | 0.00 |  |  | 82.41
UCF [%] |  |  |  |  | 99.66 | 94.29 |  |  |  | 99.65 |  | 96.99 | [8 empty] | 99.62 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.28 |  |  |  | 98.25 |  |  | 99.78 |  |  | 43.26 | [9 empty] | 0.00 |  |  | 85.86
LF [%] |  |  |  |  | 97.67 | 91.93 |  |  |  | 97.71 |  | 95.02 | [8 empty] | 50.28 |  |  | 0.00 | [6 empty] | 0.00 |  | 79.50 |  |  |  | 96.17 |  |  | 82.61 |  |  | 25.89 | [9 empty] | 0.00 |  |  | 59.61
OF [%] |  |  |  |  | 100.00 | 96.41 |  |  |  | 100.00 |  | 99.31 | [8 empty] | 66.26 |  |  | 0.00 | [6 empty] | 0.00 |  | 87.10 |  |  |  | 100.00 |  |  | 100.00 |  |  | 43.33 | [9 empty] | 0.00 |  |  | 65.93
FLR [%] |  |  |  |  | 0.00 | 3.97 |  |  |  | 0.00 |  | 2.33 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.79 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.65
UCL [%] |  |  |  |  | 0.00 | 3.90 |  |  |  | 0.00 |  | 2.31 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.79 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.56
PUF [%] |  |  |  |  | 0.34 | 1.81 |  |  |  | 0.35 |  | 0.70 | [8 empty] | 0.38 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.72 |  |  |  | 0.97 |  |  | 0.22 |  |  | 56.74 | [9 empty] | 100.00 |  |  | 13.57
XUF [%] |  |  |  |  | 0.56 | 1.06 |  |  |  | 0.75 |  | 1.33 | [8 empty] | 1.78 |  |  | 0.00 | [6 empty] | 0.00 |  | 2.72 |  |  |  | 1.30 |  |  | 15.93 |  |  | 16.08 | [9 empty] | 0.00 |  |  | 3.46
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 185306.66 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.9 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 69.37 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.6 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 71.27 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 24.13 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.82 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.9 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.4 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 5202.19 |  |  | 6485 |  |  |  | 1000 | [10 empty] | 82.32 |  |  |  | 82.32 | [5 empty] | 70.62 |  |  | 79.97 |  |  |  | 13.74 |  | 13.11 | [8 empty] | 4.57 |  |  |  |  | 0.00
1988 |  |  |  | 5661.32 |  |  | 6357 |  |  |  | 950 | [10 empty] | 71.05 |  |  |  | 71.05 | [5 empty] | 67.84 |  |  | 72.37 |  |  |  | 4.72 |  | 3.52 | [8 empty] | 25.43 |  |  |  |  | 0.00
1989 |  |  |  | 6046.10 |  |  | 6771 |  |  |  | 950 | [10 empty] | 75.08 |  |  |  | 75.08 | [5 empty] | 72.65 |  |  | 77.29 |  |  |  | 8.99 |  | 7.42 | [8 empty] | 17.50 |  |  |  |  | 0.00
1990 |  |  |  | 6360.06 |  |  | 6981 |  |  |  | 950 | [10 empty] | 77.33 |  |  |  | 77.33 | [5 empty] | 76.42 |  |  | 79.69 |  |  |  | 8.83 |  | 7.49 | [8 empty] | 15.18 |  |  |  |  | 0.00
1991 |  |  |  | 5454.79 |  |  | 5971 |  |  |  | 950 | [10 empty] | 66.02 |  |  |  | 66.02 | [5 empty] | 65.55 |  |  | 68.16 |  |  |  | 4.54 |  | 3.14 | [8 empty] | 30.84 |  |  |  |  | 0.00
1992 |  |  |  | 7084.94 |  |  | 7323 |  |  |  | 1000 | [10 empty] | 82.18 |  |  |  | 82.20 | [5 empty] | 80.66 |  |  | 83.37 |  |  |  | 5.22 |  | 4.53 | [8 empty] | 13.27 |  |  |  |  | 0.02
1993 |  |  |  | 6195.07 |  |  | 6861 |  |  |  | 950 | [10 empty] | 75.87 |  |  |  | 76.55 | [5 empty] | 74.44 |  |  | 78.32 |  |  |  | 4.63 |  | 3.71 | [8 empty] | 19.74 |  |  |  |  | 0.68
1994 |  |  |  | 5574.71 |  |  | 6042 |  |  |  | 950 | [10 empty] | 67.67 |  |  |  | 67.67 | [5 empty] | 66.99 |  |  | 68.97 |  |  |  | 0.88 |  | 0.60 | [8 empty] | 31.73 |  |  |  |  | 0.01
1995 |  |  |  | 5018.27 |  |  | 5500 |  |  |  | 950 | [10 empty] | 60.28 |  |  |  | 61.04 | [5 empty] | 60.30 |  |  | 62.79 |  |  |  | 17.12 |  | 12.61 | [8 empty] | 26.35 |  |  |  |  | 0.76
1996 |  |  |  | 5550.91 |  |  | 6064 |  |  |  | 950 | [10 empty] | 66.52 |  |  |  | 66.77 | [5 empty] | 66.52 |  |  | 69.03 |  |  |  | 10.54 |  | 7.87 | [8 empty] | 25.36 |  |  |  |  | 0.26
1997 |  |  |  | 6249.62 |  |  | 6730 |  |  |  | 950 | [10 empty] | 74.70 |  |  |  | 75.86 | [5 empty] | 75.10 |  |  | 76.83 |  |  |  | 2.56 |  | 1.99 | [8 empty] | 22.15 |  |  |  |  | 1.16
1998 |  |  |  | 5603.50 |  |  | 6036 |  |  |  | 950 | [10 empty] | 67.32 |  |  |  | 68.22 | [5 empty] | 67.33 |  |  | 68.90 |  |  |  | 1.01 |  | 0.70 | [8 empty] | 31.08 |  |  |  |  | 0.90
1999 |  |  |  | 5303.46 |  |  | 6342 |  |  |  | 950 | [10 empty] | 63.73 |  |  |  | 72.55 | [5 empty] | 63.73 |  |  | 72.40 |  |  |  | 0.65 |  | 0.48 | [8 empty] | 26.97 |  |  |  |  | 8.83
2000 |  |  |  | 4991.27 |  |  | 5641 |  |  |  | 950 | [10 empty] | 59.81 |  |  |  | 72.39 | [5 empty] | 59.81 |  |  | 64.22 |  |  |  | 14.22 |  | 12.00 | [8 empty] | 15.61 |  |  |  |  | 12.58
2001 |  |  |  | 5783.63 |  |  | 6387 |  |  |  | 950 | [10 empty] | 69.58 |  |  |  | 75.26 | [5 empty] | 69.31 |  |  | 72.71 |  |  |  | 3.28 |  | 2.55 | [8 empty] | 22.18 |  |  |  |  | 5.68
2002 |  |  |  | 5562.59 |  |  | 6320 |  |  |  | 950 | [10 empty] | 68.37 |  |  |  | 69.77 | [5 empty] | 66.84 |  |  | 72.15 |  |  |  | 2.05 |  | 1.46 | [8 empty] | 28.77 |  |  |  |  | 1.40
2003 |  |  |  | 6250.46 |  |  | 6815 |  |  |  | 950 | [10 empty] | 74.31 |  |  |  | 75.18 | [5 empty] | 75.11 |  |  | 77.80 |  |  |  | 4.54 |  | 3.68 | [8 empty] | 21.14 |  |  |  |  | 0.87
2004 |  |  |  | 6693.27 |  |  | 7321 |  |  |  | 950 | [10 empty] | 83.21 |  |  |  | 84.16 | [5 empty] | 80.21 |  |  | 83.34 |  |  |  | 0.79 |  | 0.67 | [8 empty] | 15.17 |  |  |  |  | 0.95
2005 |  |  |  | 4768.06 |  |  | 6158 |  |  |  | 950 | [10 empty] | 68.30 |  |  |  | 69.68 | [5 empty] | 57.29 |  |  | 70.30 |  |  |  | 2.25 |  | 1.60 | [8 empty] | 28.72 |  |  |  |  | 1.38
2006 |  |  |  | 4614.03 |  |  | 6777 |  |  |  | 950 | [10 empty] | 64.56 |  |  |  | 65.57 | [5 empty] | 55.44 |  |  | 77.36 |  |  |  | 28.11 |  | 25.64 | [8 empty] | 8.79 |  |  |  |  | 1.01
2007 |  |  |  | 5317.21 |  |  | 6622 |  |  |  | 950 | [10 empty] | 66.79 |  |  |  | 67.45 | [5 empty] | 63.89 |  |  | 75.59 |  |  |  | 1.07 |  | 0.73 | [8 empty] | 31.82 |  |  |  |  | 0.66
2008 |  |  |  | 6279.30 |  |  | 7097 |  |  |  | 950 | [10 empty] | 76.83 |  |  |  | 77.28 | [5 empty] | 75.25 |  |  | 80.79 |  |  |  | 1.36 |  | 1.06 | [8 empty] | 21.65 |  |  |  |  | 0.45
2009 |  |  |  | 3134.99 |  |  | 4078 |  |  |  | 950 | [10 empty] | 41.99 |  |  |  | 46.36 | [5 empty] | 37.67 |  |  | 46.55 |  |  |  | 1.03 |  | 4.81 | [8 empty] | 48.83 |  |  |  |  | 4.37
2010 |  |  |  | 5811.94 |  |  | 6731 |  |  |  | 950 | [10 empty] | 74.80 |  |  |  | 78.49 | [5 empty] | 69.84 |  |  | 76.84 |  |  |  | 4.76 |  | 3.92 | [8 empty] | 17.59 |  |  |  |  | 3.69
2011 |  |  |  | 5945.19 |  |  | 7021 |  |  |  | 950 | [10 empty] | 75.19 |  |  |  | 75.65 | [5 empty] | 71.44 |  |  | 80.15 |  |  |  | 0.09 |  | 0.07 | [8 empty] | 24.28 |  |  |  |  | 0.47
2012 |  |  |  | 5419.73 |  |  | 6665 |  |  |  | 950 | [10 empty] | 71.01 |  |  |  | 71.40 | [5 empty] | 64.95 |  |  | 75.88 |  |  |  | 0.40 |  | 0.29 | [8 empty] | 28.31 |  |  |  |  | 0.39
2013 |  |  |  | 6064.61 |  |  | 7287 |  |  |  | 950 | [10 empty] | 80.18 |  |  |  | 81.18 | [5 empty] | 72.87 |  |  | 83.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.82 |  |  |  |  | 1.01
2014 |  |  |  | 5545.16 |  |  | 6863 |  |  |  | 950 | [10 empty] | 70.34 |  |  |  | 72.09 | [5 empty] | 66.63 |  |  | 78.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.91 |  |  |  |  | 1.76
2015 |  |  |  | 5591.79 |  |  | 7177 |  |  |  | 950 | [10 empty] | 76.44 |  |  |  | 81.29 | [5 empty] | 67.19 |  |  | 81.93 |  |  |  | 0.17 |  | 0.13 | [8 empty] | 18.58 |  |  |  |  | 4.85
2016 |  |  |  | 3495.26 |  |  | 4654 |  |  |  | 950 | [10 empty] | 50.00 |  |  |  | 52.72 | [5 empty] | 41.89 |  |  | 52.98 |  |  |  | 35.38 |  | 28.87 | [8 empty] | 18.41 |  |  |  |  | 2.72
2017 |  |  |  | 5339.44 |  |  | 6491 |  |  |  | 950 | [10 empty] | 65.32 |  |  |  | 67.29 | [5 empty] | 64.16 |  |  | 74.10 |  |  |  | 3.28 |  | 2.28 | [8 empty] | 30.42 |  |  |  |  | 1.97
2018 |  |  |  | 3508.00 |  |  | 3886 |  |  |  | 950 | [10 empty] | 42.77 |  |  |  | 43.40 | [5 empty] | 42.15 |  |  | 44.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 56.60 |  |  |  |  | 0.63
2019 |  |  |  | 5764.88 |  |  | 6332 |  |  |  | 950 | [10 empty] | 70.38 |  |  |  | 71.46 | [5 empty] | 69.27 |  |  | 72.28 |  |  |  | 3.01 |  | 2.22 | [8 empty] | 26.32 |  |  |  |  | 1.08
2020 |  |  |  | 4974.66 |  |  | 5791 |  |  |  | 950 | [10 empty] | 82.41 |  |  |  | 85.86 | [5 empty] | 59.61 |  |  | 65.93 |  |  |  | 0.65 |  | 0.56 | [8 empty] | 13.57 |  |  |  |  | 3.46
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 29 | [14 empty] | 296
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1152 | [14 empty] | 1609
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 213
E. |  | Testing of plant systems or components | [35 empty] | 17
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 162
H. |  | Nuclear regulatory requirements | [39 empty] | 11
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 1811 | [19 empty] | 68
L. |  | Human factor related | [39 empty] | 6
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 6
Z. |  | Other | [39 empty] | 2 | [11 empty] | 22
Subtotal | [22 empty] | 1152 |  |  |  | 29 | [6 empty] | 1811 |  |  |  | 2001 |  |  |  | 315 | [11 empty] | 101
Total | [22 empty] | 2992 | [14 empty] | 2417
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 24
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 16
16. |  |  | Steam generation systems | [34 empty] | 20
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [19 empty] | 25 | [14 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [19 empty] | 5 | [14 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 177
42. |  |  | Electrical Power Supply Systems | [34 empty] | 26
Total | [22 empty] | 30 | [14 empty] | 333

## ROVNO-4
2020 Operating Experience
UA-69 | [8 empty] | ROVNO-4 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAA (PRODUCTION AMALGAMATION 'ATOMMASH', VOLGODONSK)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1986-08-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2004-10-10
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2006-04-06
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 16 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.4
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5031.02 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 65.39 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 66.07 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 33.93 %
Load Factor (LF) | [18 empty] | : | 60.29 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.68 %
Operating Factor (OF) | [18 empty] | : | 64.87 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3086 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 45.9 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 685.41 | 392.90 |  |  |  | 635.98 |  | 620.37 | [8 empty] | 575.71 |  |  | 672.02 | [6 empty] | 697.23 |  | 665.21 |  |  |  | 86.18 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5031.02
EAF [%] |  |  |  |  | 100.00 | 75.93 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.17 | [6 empty] | 99.59 |  | 95.34 |  |  |  | 13.89 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 65.39
UCF [%] |  |  |  |  | 100.00 | 75.93 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.75 | [6 empty] | 99.90 |  | 99.90 |  |  |  | 16.55 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 66.07
LF [%] |  |  |  |  | 96.97 | 59.42 |  |  |  | 90.10 |  | 90.70 | [8 empty] | 81.45 |  |  | 98.25 | [6 empty] | 98.65 |  | 94.12 |  |  |  | 12.60 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 60.29
OF [%] |  |  |  |  | 100.00 | 67.96 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 92.74 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 16.67 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 64.87
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 24.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.25 | [6 empty] | 0.10 |  | 0.10 |  |  |  | 83.45 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 33.93
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.58 | [6 empty] | 0.31 |  | 4.56 |  |  |  | 2.66 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.68
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 93293.02 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.43 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.51 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.23 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.58 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.19 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.2 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.07 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.68 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2006 |  |  |  | 4781.15 |  |  | 6030 |  |  |  | 950 | [10 empty] | 57.03 |  |  |  | 57.93 | [5 empty] | 51.75 |  |  | 65.55 |  |  |  | 22.84 |  | 17.15 | [8 empty] | 24.92 |  |  |  |  | 0.90
2007 |  |  |  | 5560.92 |  |  | 7657 |  |  |  | 950 | [10 empty] | 69.47 |  |  |  | 69.56 | [5 empty] | 66.82 |  |  | 87.41 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 30.39 |  |  |  |  | 0.09
2008 |  |  |  | 4368.65 |  |  | 7058 |  |  |  | 950 | [10 empty] | 60.44 |  |  |  | 66.88 | [5 empty] | 52.35 |  |  | 80.35 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 33.10 |  |  |  |  | 6.43
2009 |  |  |  | 5402.74 |  |  | 8171 |  |  |  | 950 | [10 empty] | 68.89 |  |  |  | 72.82 | [5 empty] | 64.92 |  |  | 93.28 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 27.17 |  |  |  |  | 3.93
2010 |  |  |  | 6135.99 |  |  | 7001 |  |  |  | 950 | [10 empty] | 76.13 |  |  |  | 76.78 | [5 empty] | 73.73 |  |  | 79.92 |  |  |  | 3.68 |  | 4.52 | [8 empty] | 18.70 |  |  |  |  | 0.65
2011 |  |  |  | 5471.04 |  |  | 6764 |  |  |  | 950 | [10 empty] | 75.03 |  |  |  | 77.08 | [5 empty] | 65.74 |  |  | 77.21 |  |  |  | 0.34 |  | 0.26 | [8 empty] | 22.66 |  |  |  |  | 2.06
2012 |  |  |  | 6260.55 |  |  | 7558 |  |  |  | 950 | [10 empty] | 80.98 |  |  |  | 85.81 | [5 empty] | 75.02 |  |  | 86.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.19 |  |  |  |  | 4.84
2013 |  |  |  | 5045.41 |  |  | 7451 |  |  |  | 950 | [10 empty] | 83.70 |  |  |  | 84.65 | [5 empty] | 60.63 |  |  | 85.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.35 |  |  |  |  | 0.95
2014 |  |  |  | 6177.79 |  |  | 7076 |  |  |  | 950 | [10 empty] | 81.10 |  |  |  | 81.44 | [5 empty] | 74.23 |  |  | 80.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.56 |  |  |  |  | 0.34
2015 |  |  |  | 6503.98 |  |  | 7456 |  |  |  | 950 | [10 empty] | 82.53 |  |  |  | 84.82 | [5 empty] | 78.15 |  |  | 85.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.18 |  |  |  |  | 2.28
2016 |  |  |  | 6728.75 |  |  | 7643 |  |  |  | 950 | [10 empty] | 81.15 |  |  |  | 86.72 | [5 empty] | 80.63 |  |  | 87.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.28 |  |  |  |  | 5.56
2017 |  |  |  | 7107.65 |  |  | 7577 |  |  |  | 950 | [10 empty] | 86.10 |  |  |  | 86.29 | [5 empty] | 85.41 |  |  | 86.50 |  |  |  | 0.52 |  | 0.45 | [8 empty] | 13.26 |  |  |  |  | 0.19
2018 |  |  |  | 6819.17 |  |  | 7282 |  |  |  | 950 | [10 empty] | 82.74 |  |  |  | 83.00 | [5 empty] | 81.94 |  |  | 83.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.00 |  |  |  |  | 0.26
2019 |  |  |  | 6398.38 |  |  | 6930 |  |  |  | 950 | [10 empty] | 77.46 |  |  |  | 79.01 | [5 empty] | 76.89 |  |  | 79.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.99 |  |  |  |  | 1.55
2020 |  |  |  | 5031.02 |  |  | 5698 |  |  |  | 950 | [10 empty] | 65.39 |  |  |  | 66.07 | [5 empty] | 60.29 |  |  | 64.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.93 |  |  |  |  | 0.68
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2006 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 46
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2808 | [14 empty] | 1409
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 166 | [14 empty] | 144
H. |  | Nuclear regulatory requirements | [39 empty] | 9
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 111 | [19 empty] | 27
Subtotal | [22 empty] | 2974 | [10 empty] | 111 |  |  |  | 1553 |  |  |  | 55 | [11 empty] | 28
Total | [22 empty] | 3085 | [14 empty] | 1636
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2006 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 43
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [37 empty] | 46

## SOUTH UKRAINE-1
2020 Operating Experience
UA-44 | [8 empty] | SOUTH UKRAINE-1 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAA (PRODUCTION AMALGAMATION 'ATOMMASH', VOLGODONSK)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-302 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-08-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-12-31
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-12-02
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 49 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6521.17 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.97 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.67 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 14.33 %
Load Factor (LF) | [18 empty] | : | 78.15 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.7 %
Operating Factor (OF) | [18 empty] | : | 85.7 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1256 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 26.51 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 721.60 | 678.55 |  |  |  | 700.05 |  | 430.73 | [8 empty] | 547.87 |  |  | 536.28 | [6 empty] | 633.96 |  | 38.51 |  |  |  | 157.41 |  |  | 671.08 |  |  | 683.70 | [9 empty] | 721.42 |  |  | 6521.17
EAF [%] |  |  |  |  | 96.64 | 97.15 |  |  |  | 95.48 |  | 83.22 | [8 empty] | 94.23 |  |  | 91.70 | [6 empty] | 94.02 |  | 7.47 |  |  |  | 38.21 |  |  | 93.80 |  |  | 94.97 | [9 empty] | 97.12 |  |  | 81.97
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.12 |  | 85.37 | [8 empty] | 100.00 |  |  | 95.79 | [6 empty] | 100.00 |  | 7.87 |  |  |  | 40.17 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.67
LF [%] |  |  |  |  | 102.09 | 102.62 |  |  |  | 99.18 |  | 62.97 | [8 empty] | 77.51 |  |  | 78.40 | [6 empty] | 89.69 |  | 5.45 |  |  |  | 23.01 |  |  | 94.82 |  |  | 99.96 | [9 empty] | 102.07 |  |  | 78.15
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 82.92 | [8 empty] | 100.00 |  |  | 97.08 | [6 empty] | 100.00 |  | 8.06 |  |  |  | 40.56 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.70
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.88 |  | 14.63 | [8 empty] | 0.00 |  |  | 4.21 | [6 empty] | 0.00 |  | 92.13 |  |  |  | 59.83 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 14.33
XUF [%] |  |  |  |  | 3.36 | 2.85 |  |  |  | 3.64 |  | 2.15 | [8 empty] | 5.77 |  |  | 4.10 | [6 empty] | 5.98 |  | 0.39 |  |  |  | 1.96 |  |  | 6.20 |  |  | 5.03 | [9 empty] | 2.88 |  |  | 3.70
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 203283.17 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.69 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 68.01 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.31 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 70.28 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 25.41 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.22 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.27 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.21 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 2558.83 |  |  | 3708 |  |  |  | 950 | [10 empty] | 95.23 |  |  |  | 95.23 | [5 empty] | 95.74 |  |  | 95.30 |  |  |  | 4.77 |  | 4.77 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 6075.07 |  |  | 6364 |  |  |  | 950 | [10 empty] | 71.66 |  |  |  | 71.66 | [5 empty] | 72.80 |  |  | 72.45 |  |  |  | 11.12 |  | 8.97 | [8 empty] | 19.38 |  |  |  |  | 0.00
1985 |  |  |  | 6939.15 |  |  | 7148 |  |  |  | 950 | [10 empty] | 81.13 |  |  |  | 81.45 | [5 empty] | 83.38 |  |  | 81.60 |  |  |  | 1.37 |  | 1.13 | [8 empty] | 17.42 |  |  |  |  | 0.32
1986 |  |  |  | 6176.11 |  |  | 6735 |  |  |  | 950 | [10 empty] | 73.47 |  |  |  | 74.05 | [5 empty] | 74.21 |  |  | 76.88 |  |  |  | 14.47 |  | 12.53 | [8 empty] | 13.42 |  |  |  |  | 0.58
1987 |  |  |  | 6385.87 |  |  | 6642 |  |  |  | 1000 | [10 empty] | 75.58 |  |  |  | 75.58 | [5 empty] | 72.90 |  |  | 75.82 |  |  |  | 5.05 |  | 4.02 | [8 empty] | 20.40 |  |  |  |  | 0.00
1988 |  |  |  | 5467.47 |  |  | 6177 |  |  |  | 950 | [10 empty] | 65.90 |  |  |  | 65.90 | [5 empty] | 65.52 |  |  | 70.32 |  |  |  | 15.80 |  | 12.36 | [8 empty] | 21.73 |  |  |  |  | 0.00
1989 |  |  |  | 2501.58 |  |  | 3321 |  |  |  | 950 | [10 empty] | 30.85 |  |  |  | 30.85 | [5 empty] | 30.06 |  |  | 37.91 |  |  |  | 42.57 |  | 22.87 | [8 empty] | 46.29 |  |  |  |  | 0.00
1990 |  |  |  | 6174.36 |  |  | 7063 |  |  |  | 950 | [10 empty] | 74.99 |  |  |  | 75.25 | [5 empty] | 74.19 |  |  | 80.63 |  |  |  | 9.55 |  | 7.95 | [8 empty] | 16.81 |  |  |  |  | 0.26
1991 |  |  |  | 3865.86 |  |  | 5532 |  |  |  | 950 | [10 empty] | 46.47 |  |  |  | 46.47 | [5 empty] | 46.45 |  |  | 63.14 |  |  |  | 28.83 |  | 18.83 | [8 empty] | 34.70 |  |  |  |  | 0.00
1992 |  |  |  | 4946.83 |  |  | 6142 |  |  |  | 833 | [10 empty] | 49.06 |  |  |  | 49.21 | [5 empty] | 67.58 |  |  | 69.92 |  |  |  | 8.67 |  | 4.67 | [8 empty] | 46.12 |  |  |  |  | 0.15
1993 |  |  |  | 5277.81 |  |  | 5650 |  |  |  | 950 | [10 empty] | 61.36 |  |  |  | 62.30 | [5 empty] | 63.42 |  |  | 64.50 |  |  |  | 7.30 |  | 4.91 | [8 empty] | 32.80 |  |  |  |  | 0.93
1994 |  |  |  | 5117.43 |  |  | 5667 |  |  |  | 950 | [10 empty] | 58.65 |  |  |  | 58.67 | [5 empty] | 61.49 |  |  | 64.69 |  |  |  | 2.48 |  | 1.49 | [8 empty] | 39.84 |  |  |  |  | 0.02
1995 |  |  |  | 5438.63 |  |  | 6212 |  |  |  | 950 | [10 empty] | 65.35 |  |  |  | 66.10 | [5 empty] | 65.35 |  |  | 70.91 |  |  |  | 3.84 |  | 2.64 | [8 empty] | 31.25 |  |  |  |  | 0.75
1996 |  |  |  | 5138.24 |  |  | 5549 |  |  |  | 950 | [10 empty] | 61.57 |  |  |  | 62.12 | [5 empty] | 61.57 |  |  | 63.17 |  |  |  | 1.41 |  | 0.89 | [8 empty] | 36.99 |  |  |  |  | 0.55
1997 |  |  |  | 6196.06 |  |  | 6416 |  |  |  | 950 | [10 empty] | 72.47 |  |  |  | 73.01 | [5 empty] | 74.45 |  |  | 73.24 |  |  |  | 1.18 |  | 0.87 | [8 empty] | 26.12 |  |  |  |  | 0.53
1998 |  |  |  | 6164.95 |  |  | 6477 |  |  |  | 950 | [10 empty] | 73.10 |  |  |  | 73.65 | [5 empty] | 74.08 |  |  | 73.94 |  |  |  | 0.09 |  | 0.06 | [8 empty] | 26.28 |  |  |  |  | 0.55
1999 |  |  |  | 5558.92 |  |  | 5920 |  |  |  | 950 | [10 empty] | 66.55 |  |  |  | 67.14 | [5 empty] | 66.80 |  |  | 67.58 |  |  |  | 0.16 |  | 0.11 | [8 empty] | 32.75 |  |  |  |  | 0.59
2000 |  |  |  | 5203.05 |  |  | 5677 |  |  |  | 950 | [10 empty] | 61.21 |  |  |  | 63.93 | [5 empty] | 62.35 |  |  | 64.63 |  |  |  | 5.56 |  | 3.76 | [8 empty] | 32.31 |  |  |  |  | 2.71
2001 |  |  |  | 5563.71 |  |  | 6015 |  |  |  | 950 | [10 empty] | 66.58 |  |  |  | 68.32 | [5 empty] | 66.67 |  |  | 68.48 |  |  |  | 4.66 |  | 3.34 | [8 empty] | 28.34 |  |  |  |  | 1.74
2002 |  |  |  | 4254.82 |  |  | 4625 |  |  |  | 950 | [10 empty] | 50.87 |  |  |  | 52.19 | [5 empty] | 51.13 |  |  | 52.80 |  |  |  | 33.66 |  | 26.48 | [8 empty] | 21.33 |  |  |  |  | 1.32
2003 |  |  |  | 6008.24 |  |  | 6612 |  |  |  | 950 | [10 empty] | 72.58 |  |  |  | 74.23 | [5 empty] | 72.20 |  |  | 75.48 |  |  |  | 1.58 |  | 1.19 | [8 empty] | 24.58 |  |  |  |  | 1.65
2004 |  |  |  | 6988.95 |  |  | 7592 |  |  |  | 950 | [10 empty] | 83.96 |  |  |  | 85.04 | [5 empty] | 83.75 |  |  | 86.43 |  |  |  | 1.54 |  | 1.88 | [8 empty] | 13.07 |  |  |  |  | 1.08
2005 |  |  |  | 6068.49 |  |  | 6926 |  |  |  | 950 | [10 empty] | 77.06 |  |  |  | 78.26 | [5 empty] | 72.92 |  |  | 79.06 |  |  |  | 0.66 |  | 2.40 | [8 empty] | 19.34 |  |  |  |  | 1.19
2006 |  |  |  | 6345.12 |  |  | 6988 |  |  |  | 950 | [10 empty] | 76.89 |  |  |  | 79.05 | [5 empty] | 76.25 |  |  | 79.77 |  |  |  | 1.25 |  | 1.00 | [8 empty] | 19.95 |  |  |  |  | 2.16
2007 |  |  |  | 5159.76 |  |  | 5562 |  |  |  | 950 | [10 empty] | 61.58 |  |  |  | 62.75 | [5 empty] | 62.00 |  |  | 63.49 |  |  |  | 2.25 |  | 1.44 | [8 empty] | 35.81 |  |  |  |  | 1.17
2008 |  |  |  | 6895.39 |  |  | 7484 |  |  |  | 950 | [10 empty] | 84.80 |  |  |  | 85.10 | [5 empty] | 82.63 |  |  | 85.20 |  |  |  | 1.37 |  | 1.18 | [8 empty] | 13.72 |  |  |  |  | 0.30
2009 |  |  |  | 3790.57 |  |  | 5368 |  |  |  | 950 | [10 empty] | 74.25 |  |  |  | 78.30 | [5 empty] | 45.55 |  |  | 61.28 |  |  |  | 7.22 |  | 6.10 | [8 empty] | 15.60 |  |  |  |  | 4.06
2010 |  |  |  | 5151.44 |  |  | 6335 |  |  |  | 950 | [10 empty] | 84.63 |  |  |  | 90.56 | [5 empty] | 61.90 |  |  | 72.32 |  |  |  | 3.14 |  | 2.94 | [8 empty] | 6.50 |  |  |  |  | 5.93
2011 |  |  |  | 5026.85 |  |  | 6632 |  |  |  | 950 | [10 empty] | 60.33 |  |  |  | 72.00 | [5 empty] | 60.40 |  |  | 75.71 |  |  |  | 4.16 |  | 3.13 | [8 empty] | 24.87 |  |  |  |  | 11.66
2012 |  |  |  | 6524.13 |  |  | 7508 |  |  |  | 950 | [10 empty] | 74.58 |  |  |  | 77.82 | [5 empty] | 78.18 |  |  | 85.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.18 |  |  |  |  | 3.23
2013 |  |  |  | 1765.53 |  |  | 1987 |  |  |  | 950 | [10 empty] | 20.15 |  |  |  | 20.63 | [5 empty] | 21.22 |  |  | 22.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 79.37 |  |  |  |  | 0.48
2014 |  |  |  | 6420.56 |  |  | 7547 |  |  |  | 950 | [10 empty] | 77.35 |  |  |  | 82.51 | [5 empty] | 77.15 |  |  | 86.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.49 |  |  |  |  | 5.15
2015 |  |  |  | 6728.34 |  |  | 7777 |  |  |  | 950 | [10 empty] | 79.55 |  |  |  | 84.90 | [5 empty] | 80.85 |  |  | 88.78 |  |  |  | 0.11 |  | 0.09 | [8 empty] | 15.01 |  |  |  |  | 5.35
2016 |  |  |  | 5810.19 |  |  | 7451 |  |  |  | 950 | [10 empty] | 73.14 |  |  |  | 81.07 | [5 empty] | 69.63 |  |  | 84.82 |  |  |  | 0.29 |  | 0.24 | [8 empty] | 18.70 |  |  |  |  | 7.93
2017 |  |  |  | 5642.42 |  |  | 6828 |  |  |  | 950 | [10 empty] | 68.27 |  |  |  | 74.69 | [5 empty] | 67.80 |  |  | 77.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.31 |  |  |  |  | 6.42
2018 |  |  |  | 6487.01 |  |  | 6914 |  |  |  | 950 | [10 empty] | 74.80 |  |  |  | 78.20 | [5 empty] | 77.95 |  |  | 78.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.80 |  |  |  |  | 3.40
2019 |  |  |  | 6763.16 |  |  | 7700 |  |  |  | 950 | [10 empty] | 78.59 |  |  |  | 86.81 | [5 empty] | 81.27 |  |  | 87.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.19 |  |  |  |  | 8.22
2020 |  |  |  | 6521.17 |  |  | 7528 |  |  |  | 950 | [10 empty] | 81.97 |  |  |  | 85.67 | [5 empty] | 78.15 |  |  | 85.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.33 |  |  |  |  | 3.70
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 312
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1111 | [14 empty] | 1719
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 144 | [14 empty] | 282
E. |  | Testing of plant systems or components | [35 empty] | 8 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 108
L. |  | Human factor related | [39 empty] | 2
Z. |  | Other | [39 empty] | 29 | [11 empty] | 1
Subtotal | [22 empty] | 1255 | [14 empty] | 2009 |  |  |  | 344 | [11 empty] | 110
Total | [22 empty] | 1255 | [14 empty] | 2463
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
16. |  |  | Steam generation systems | [34 empty] | 149
31. |  |  | Turbine and auxiliaries | [34 empty] | 44
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 88
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [37 empty] | 307

## SOUTH UKRAINE-2
2020 Operating Experience
UA-45 | [8 empty] | SOUTH UKRAINE-2 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAA (PRODUCTION AMALGAMATION 'ATOMMASH', VOLGODONSK)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-338 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-07-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-01-06
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-04-06
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5970.49 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 68.83 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 72.63 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 27.37 %
Load Factor (LF) | [18 empty] | : | 71.55 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.8 %
Operating Factor (OF) | [18 empty] | : | 72.78 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2391 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 42.31 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 725.01 | 680.71 |  |  |  | 667.77 |  | 292.38 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 111.84 |  | 670.93 |  |  |  | 689.68 |  |  | 704.44 |  |  | 696.97 | [9 empty] | 730.74 |  |  | 5970.49
EAF [%] |  |  |  |  | 96.80 | 97.23 |  |  |  | 95.62 |  | 42.10 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 21.62 |  | 93.70 |  |  |  | 94.30 |  |  | 93.98 |  |  | 94.55 | [9 empty] | 96.48 |  |  | 68.83
UCF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 100.00 |  | 48.95 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 23.03 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 72.63
LF [%] |  |  |  |  | 102.58 | 102.95 |  |  |  | 94.61 |  | 42.75 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 15.82 |  | 94.93 |  |  |  | 100.83 |  |  | 99.53 |  |  | 101.90 | [9 empty] | 103.39 |  |  | 71.55
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 49.17 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 24.60 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 72.78
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 51.05 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 76.97 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 27.37
XUF [%] |  |  |  |  | 3.20 | 2.76 |  |  |  | 4.38 |  | 6.85 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.41 |  | 6.30 |  |  |  | 5.70 |  |  | 6.02 |  |  | 5.45 | [9 empty] | 3.52 |  |  | 3.80
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 190488.49 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 11.96 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 64.83 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.16 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 67.09 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 23.75 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 64.99 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.27 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 71.63 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 5603.65 |  |  | 6379 |  |  |  | 950 | [10 empty] | 73.30 |  |  |  | 73.30 | [5 empty] | 74.42 |  |  | 74.59 |  |  |  | 9.42 |  | 7.63 | [8 empty] | 19.07 |  |  |  |  | 0.00
1986 |  |  |  | 5565.48 |  |  | 6315 |  |  |  | 950 | [10 empty] | 66.25 |  |  |  | 67.00 | [5 empty] | 66.88 |  |  | 72.09 |  |  |  | 10.56 |  | 7.91 | [8 empty] | 25.09 |  |  |  |  | 0.75
1987 |  |  |  | 1641.67 |  |  | 1941 |  |  |  | 1000 | [10 empty] | 22.04 |  |  |  | 22.04 | [5 empty] | 18.74 |  |  | 22.16 |  |  |  | 77.96 |  | 77.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 4850.58 |  |  | 5198 |  |  |  | 950 | [10 empty] | 57.38 |  |  |  | 57.38 | [5 empty] | 58.13 |  |  | 59.18 |  |  |  | 32.69 |  | 27.86 | [8 empty] | 14.75 |  |  |  |  | 0.00
1989 |  |  |  | 4437.30 |  |  | 6674 |  |  |  | 950 | [10 empty] | 54.29 |  |  |  | 54.29 | [5 empty] | 53.32 |  |  | 76.19 |  |  |  | 32.49 |  | 26.12 | [8 empty] | 19.59 |  |  |  |  | 0.00
1990 |  |  |  | 1768.96 |  |  | 4522 |  |  |  | 950 | [10 empty] | 21.87 |  |  |  | 21.87 | [5 empty] | 21.26 |  |  | 51.62 |  |  |  | 58.65 |  | 31.02 | [8 empty] | 47.11 |  |  |  |  | 0.00
1991 |  |  |  | 6209.76 |  |  | 6722 |  |  |  | 950 | [10 empty] | 72.04 |  |  |  | 72.04 | [5 empty] | 74.62 |  |  | 76.74 |  |  |  | 9.16 |  | 7.26 | [8 empty] | 20.70 |  |  |  |  | 0.00
1992 |  |  |  | 6412.13 |  |  | 6574 |  |  |  | 1000 | [10 empty] | 71.66 |  |  |  | 72.91 | [5 empty] | 73.00 |  |  | 74.84 |  |  |  | 4.84 |  | 3.71 | [8 empty] | 23.38 |  |  |  |  | 1.25
1993 |  |  |  | 5204.03 |  |  | 6570 |  |  |  | 950 | [10 empty] | 61.71 |  |  |  | 64.00 | [5 empty] | 62.53 |  |  | 75.00 |  |  |  | 20.57 |  | 16.58 | [8 empty] | 19.43 |  |  |  |  | 2.28
1994 |  |  |  | 3958.54 |  |  | 6471 |  |  |  | 950 | [10 empty] | 46.86 |  |  |  | 47.32 | [5 empty] | 47.57 |  |  | 73.87 |  |  |  | 34.13 |  | 24.52 | [8 empty] | 28.16 |  |  |  |  | 0.46
1995 |  |  |  | 5429.43 |  |  | 6514 |  |  |  | 950 | [10 empty] | 65.24 |  |  |  | 66.12 | [5 empty] | 65.24 |  |  | 74.36 |  |  |  | 1.62 |  | 1.09 | [8 empty] | 32.80 |  |  |  |  | 0.87
1996 |  |  |  | 4593.75 |  |  | 5590 |  |  |  | 950 | [10 empty] | 55.05 |  |  |  | 55.43 | [5 empty] | 55.05 |  |  | 63.64 |  |  |  | 22.85 |  | 16.42 | [8 empty] | 28.15 |  |  |  |  | 0.38
1997 |  |  |  | 6326.54 |  |  | 7400 |  |  |  | 950 | [10 empty] | 75.38 |  |  |  | 77.16 | [5 empty] | 76.02 |  |  | 84.47 |  |  |  | 9.00 |  | 7.63 | [8 empty] | 15.21 |  |  |  |  | 1.78
1998 |  |  |  | 4542.39 |  |  | 4867 |  |  |  | 950 | [10 empty] | 53.97 |  |  |  | 55.15 | [5 empty] | 54.58 |  |  | 55.56 |  |  |  | 1.29 |  | 0.72 | [8 empty] | 44.13 |  |  |  |  | 1.18
1999 |  |  |  | 5537.94 |  |  | 6372 |  |  |  | 950 | [10 empty] | 66.42 |  |  |  | 72.01 | [5 empty] | 66.55 |  |  | 72.74 |  |  |  | 0.05 |  | 0.03 | [8 empty] | 27.95 |  |  |  |  | 5.59
2000 |  |  |  | 4103.49 |  |  | 4486 |  |  |  | 950 | [10 empty] | 49.17 |  |  |  | 50.04 | [5 empty] | 49.17 |  |  | 51.07 |  |  |  | 34.95 |  | 26.88 | [8 empty] | 23.08 |  |  |  |  | 0.86
2001 |  |  |  | 6206.51 |  |  | 6869 |  |  |  | 950 | [10 empty] | 74.40 |  |  |  | 74.75 | [5 empty] | 74.38 |  |  | 78.20 |  |  |  | 5.14 |  | 4.05 | [8 empty] | 21.20 |  |  |  |  | 0.36
2002 |  |  |  | 6057.20 |  |  | 6565 |  |  |  | 950 | [10 empty] | 72.65 |  |  |  | 74.16 | [5 empty] | 72.79 |  |  | 74.94 |  |  |  | 0.54 |  | 0.40 | [8 empty] | 25.44 |  |  |  |  | 1.51
2003 |  |  |  | 5507.74 |  |  | 5868 |  |  |  | 950 | [10 empty] | 65.82 |  |  |  | 66.18 | [5 empty] | 66.18 |  |  | 66.98 |  |  |  | 1.34 |  | 0.90 | [8 empty] | 32.92 |  |  |  |  | 0.36
2004 |  |  |  | 6899.71 |  |  | 7647 |  |  |  | 950 | [10 empty] | 82.23 |  |  |  | 86.14 | [5 empty] | 82.68 |  |  | 87.06 |  |  |  | 1.32 |  | 1.15 | [8 empty] | 12.71 |  |  |  |  | 3.92
2005 |  |  |  | 6479.16 |  |  | 7243 |  |  |  | 950 | [10 empty] | 81.07 |  |  |  | 82.01 | [5 empty] | 77.86 |  |  | 82.68 |  |  |  | 2.80 |  | 2.36 | [8 empty] | 15.63 |  |  |  |  | 0.93
2006 |  |  |  | 6110.19 |  |  | 6847 |  |  |  | 950 | [10 empty] | 75.28 |  |  |  | 77.53 | [5 empty] | 73.42 |  |  | 78.16 |  |  |  | 2.94 |  | 2.35 | [8 empty] | 20.12 |  |  |  |  | 2.25
2007 |  |  |  | 6241.70 |  |  | 6892 |  |  |  | 950 | [10 empty] | 75.76 |  |  |  | 77.95 | [5 empty] | 75.00 |  |  | 78.68 |  |  |  | 3.03 |  | 2.44 | [8 empty] | 19.61 |  |  |  |  | 2.19
2008 |  |  |  | 6623.64 |  |  | 7248 |  |  |  | 950 | [10 empty] | 81.11 |  |  |  | 81.38 | [5 empty] | 79.37 |  |  | 82.51 |  |  |  | 1.25 |  | 1.03 | [8 empty] | 17.59 |  |  |  |  | 0.27
2009 |  |  |  | 6402.79 |  |  | 7213 |  |  |  | 950 | [10 empty] | 80.99 |  |  |  | 81.64 | [5 empty] | 76.94 |  |  | 82.34 |  |  |  | 3.01 |  | 4.04 | [8 empty] | 14.32 |  |  |  |  | 0.66
2010 |  |  |  | 6461.48 |  |  | 7326 |  |  |  | 950 | [10 empty] | 77.75 |  |  |  | 79.43 | [5 empty] | 77.64 |  |  | 83.63 |  |  |  | 4.79 |  | 4.00 | [8 empty] | 16.57 |  |  |  |  | 1.69
2011 |  |  |  | 6039.15 |  |  | 7003 |  |  |  | 950 | [10 empty] | 72.87 |  |  |  | 76.96 | [5 empty] | 72.57 |  |  | 79.94 |  |  |  | 1.58 |  | 1.23 | [8 empty] | 21.80 |  |  |  |  | 4.09
2012 |  |  |  | 6002.99 |  |  | 6723 |  |  |  | 950 | [10 empty] | 70.69 |  |  |  | 74.30 | [5 empty] | 71.94 |  |  | 76.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.70 |  |  |  |  | 3.61
2013 |  |  |  | 6141.18 |  |  | 7160 |  |  |  | 950 | [10 empty] | 73.00 |  |  |  | 75.60 | [5 empty] | 73.79 |  |  | 81.74 |  |  |  | 0.21 |  | 0.16 | [8 empty] | 24.24 |  |  |  |  | 2.60
2014 |  |  |  | 6152.37 |  |  | 6846 |  |  |  | 950 | [10 empty] | 73.46 |  |  |  | 76.22 | [5 empty] | 73.93 |  |  | 78.15 |  |  |  | 0.47 |  | 0.36 | [8 empty] | 23.42 |  |  |  |  | 2.76
2015 |  |  |  | 3228.28 |  |  | 3537 |  |  |  | 950 | [10 empty] | 37.51 |  |  |  | 39.53 | [5 empty] | 38.79 |  |  | 40.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 60.47 |  |  |  |  | 2.03
2016 |  |  |  | 5489.65 |  |  | 6776 |  |  |  | 950 | [10 empty] | 64.76 |  |  |  | 76.28 | [5 empty] | 65.79 |  |  | 77.14 |  |  |  | 9.18 |  | 7.71 | [8 empty] | 16.02 |  |  |  |  | 11.51
2017 |  |  |  | 5513.69 |  |  | 6693 |  |  |  | 950 | [10 empty] | 67.21 |  |  |  | 75.93 | [5 empty] | 66.25 |  |  | 76.40 |  |  |  | 11.01 |  | 9.40 | [8 empty] | 14.67 |  |  |  |  | 8.72
2018 |  |  |  | 4935.64 |  |  | 5822 |  |  |  | 950 | [10 empty] | 56.71 |  |  |  | 66.11 | [5 empty] | 59.31 |  |  | 66.46 |  |  |  | 1.68 |  | 1.13 | [8 empty] | 32.76 |  |  |  |  | 9.40
2019 |  |  |  | 6377.49 |  |  | 6698 |  |  |  | 950 | [10 empty] | 72.95 |  |  |  | 76.08 | [5 empty] | 76.63 |  |  | 76.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.92 |  |  |  |  | 3.13
2020 |  |  |  | 5970.49 |  |  | 6393 |  |  |  | 950 | [10 empty] | 68.83 |  |  |  | 72.63 | [5 empty] | 71.55 |  |  | 72.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.37 |  |  |  |  | 3.80
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 398
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2391 | [14 empty] | 1476
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 339
E. |  | Testing of plant systems or components | [35 empty] | 8
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 146
H. |  | Nuclear regulatory requirements | [39 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 1
Z. |  | Other | [39 empty] | 43
Subtotal | [22 empty] | 2391 | [14 empty] | 1969 |  |  |  | 446 | [11 empty] | 4
Total | [22 empty] | 2391 | [14 empty] | 2419
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 43
12. |  |  | Reactor I&C Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 21
16. |  |  | Steam generation systems | [34 empty] | 265
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 20
32. |  |  | Feedwater and Main Steam System | [34 empty] | 24
34. |  |  | Miscellaneous Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 47
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 438

## SOUTH UKRAINE-3
2020 Operating Experience
UA-48 | [8 empty] | SOUTH UKRAINE-3 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAA (PRODUCTION AMALGAMATION 'ATOMMASH', VOLGODONSK)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-11-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1989-09-20
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-12-29
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5664.51 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.69 %
Energy Availability Factor (EAF) | [18 empty] | : | 77.55 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.64 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.38 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.97 %
Load Factor (LF) | [18 empty] | : | 67.88 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 14.84 %
Operating Factor (OF) | [18 empty] | : | 96.65 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 294 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 47.96 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 647.41 | 663.20 |  |  |  | 630.30 |  | 397.47 | [8 empty] | 403.49 |  |  | 393.39 | [6 empty] | 313.07 |  | 381.84 |  |  |  | 487.99 |  |  | 523.39 |  |  | 412.93 | [9 empty] | 410.03 |  |  | 5664.51
EAF [%] |  |  |  |  | 89.63 | 96.89 |  |  |  | 95.85 |  | 59.20 | [8 empty] | 58.04 |  |  | 92.72 | [6 empty] | 68.88 |  | 82.35 |  |  |  | 88.09 |  |  | 81.54 |  |  | 60.36 | [9 empty] | 57.98 |  |  | 77.55
UCF [%] |  |  |  |  | 92.15 | 99.39 |  |  |  | 98.93 |  | 96.87 | [8 empty] | 96.09 |  |  | 96.67 | [6 empty] | 73.21 |  | 86.76 |  |  |  | 92.97 |  |  | 88.07 |  |  | 93.63 | [9 empty] | 94.66 |  |  | 92.38
LF [%] |  |  |  |  | 91.60 | 100.30 |  |  |  | 89.30 |  | 58.11 | [8 empty] | 57.09 |  |  | 57.51 | [6 empty] | 44.29 |  | 54.02 |  |  |  | 71.34 |  |  | 73.95 |  |  | 60.37 | [9 empty] | 58.01 |  |  | 67.88
OF [%] |  |  |  |  | 93.68 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.19 |  |  | 100.00 | [6 empty] | 77.82 |  | 92.20 |  |  |  | 100.00 |  |  | 97.58 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 96.65
FLR [%] |  |  |  |  | 6.94 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.74 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.69
UCL [%] |  |  |  |  | 6.88 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.72 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.64
PUF [%] |  |  |  |  | 0.98 | 0.61 |  |  |  | 1.07 |  | 3.13 | [8 empty] | 3.19 |  |  | 3.33 | [6 empty] | 26.79 |  | 13.24 |  |  |  | 7.03 |  |  | 11.93 |  |  | 6.37 | [9 empty] | 5.34 |  |  | 6.97
XUF [%] |  |  |  |  | 2.52 | 2.50 |  |  |  | 3.08 |  | 37.67 | [8 empty] | 38.06 |  |  | 3.95 | [6 empty] | 4.33 |  | 4.41 |  |  |  | 4.88 |  |  | 6.53 |  |  | 33.27 | [9 empty] | 36.68 |  |  | 14.84
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 167148.51 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.09 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 68.6 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 71.93 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 24.04 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 66.54 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.33 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 1299.66 |  |  | 1992 |  |  |  | 950 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 5691.56 |  |  | 6408 |  |  |  | 950 | [10 empty] | 69.37 |  |  |  | 69.37 | [5 empty] | 68.39 |  |  | 73.15 |  |  |  | 13.24 |  | 10.58 | [8 empty] | 20.05 |  |  |  |  | 0.00
1991 |  |  |  | 5762.83 |  |  | 6996 |  |  |  | 950 | [10 empty] | 69.95 |  |  |  | 70.40 | [5 empty] | 69.25 |  |  | 79.86 |  |  |  | 13.28 |  | 10.78 | [8 empty] | 18.82 |  |  |  |  | 0.44
1992 |  |  |  | 6458.14 |  |  | 6646 |  |  |  | 1000 | [10 empty] | 75.25 |  |  |  | 75.25 | [5 empty] | 73.52 |  |  | 75.66 |  |  |  | 2.82 |  | 2.18 | [8 empty] | 22.57 |  |  |  |  | 0.00
1993 |  |  |  | 6043.39 |  |  | 6527 |  |  |  | 950 | [10 empty] | 71.69 |  |  |  | 72.78 | [5 empty] | 72.62 |  |  | 74.51 |  |  |  | 7.90 |  | 6.24 | [8 empty] | 20.98 |  |  |  |  | 1.08
1994 |  |  |  | 5565.05 |  |  | 6223 |  |  |  | 950 | [10 empty] | 66.43 |  |  |  | 66.46 | [5 empty] | 66.87 |  |  | 71.04 |  |  |  | 4.67 |  | 3.26 | [8 empty] | 30.28 |  |  |  |  | 0.03
1995 |  |  |  | 4954.78 |  |  | 6300 |  |  |  | 950 | [10 empty] | 59.54 |  |  |  | 60.17 | [5 empty] | 59.54 |  |  | 71.92 |  |  |  | 0.37 |  | 0.22 | [8 empty] | 39.61 |  |  |  |  | 0.63
1996 |  |  |  | 6155.02 |  |  | 7463 |  |  |  | 950 | [10 empty] | 73.76 |  |  |  | 76.41 | [5 empty] | 73.76 |  |  | 84.96 |  |  |  | 11.29 |  | 9.73 | [8 empty] | 13.86 |  |  |  |  | 2.66
1997 |  |  |  | 6514.77 |  |  | 7079 |  |  |  | 950 | [10 empty] | 77.70 |  |  |  | 79.75 | [5 empty] | 78.28 |  |  | 80.81 |  |  |  | 0.61 |  | 0.49 | [8 empty] | 19.76 |  |  |  |  | 2.05
1998 |  |  |  | 5850.99 |  |  | 6396 |  |  |  | 950 | [10 empty] | 69.91 |  |  |  | 70.99 | [5 empty] | 70.31 |  |  | 73.01 |  |  |  | 1.81 |  | 1.31 | [8 empty] | 27.70 |  |  |  |  | 1.09
1999 |  |  |  | 5464.32 |  |  | 6244 |  |  |  | 950 | [10 empty] | 65.51 |  |  |  | 67.19 | [5 empty] | 65.66 |  |  | 71.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.81 |  |  |  |  | 1.68
2000 |  |  |  | 5909.66 |  |  | 6588 |  |  |  | 950 | [10 empty] | 70.58 |  |  |  | 73.34 | [5 empty] | 70.82 |  |  | 75.00 |  |  |  | 4.15 |  | 3.18 | [8 empty] | 23.49 |  |  |  |  | 2.76
2001 |  |  |  | 6136.35 |  |  | 6985 |  |  |  | 950 | [10 empty] | 73.71 |  |  |  | 76.29 | [5 empty] | 73.53 |  |  | 79.52 |  |  |  | 8.00 |  | 6.64 | [8 empty] | 17.08 |  |  |  |  | 2.58
2002 |  |  |  | 6335.16 |  |  | 7043 |  |  |  | 950 | [10 empty] | 75.97 |  |  |  | 77.54 | [5 empty] | 76.13 |  |  | 80.40 |  |  |  | 3.23 |  | 2.59 | [8 empty] | 19.87 |  |  |  |  | 1.57
2003 |  |  |  | 6036.52 |  |  | 6680 |  |  |  | 950 | [10 empty] | 73.11 |  |  |  | 74.31 | [5 empty] | 72.54 |  |  | 76.26 |  |  |  | 4.34 |  | 3.37 | [8 empty] | 22.32 |  |  |  |  | 1.20
2004 |  |  |  | 6625.11 |  |  | 7246 |  |  |  | 950 | [10 empty] | 79.93 |  |  |  | 82.00 | [5 empty] | 79.39 |  |  | 82.49 |  |  |  | 3.82 |  | 3.26 | [8 empty] | 14.74 |  |  |  |  | 2.07
2005 |  |  |  | 6801.04 |  |  | 7548 |  |  |  | 950 | [10 empty] | 84.99 |  |  |  | 85.73 | [5 empty] | 81.72 |  |  | 86.16 |  |  |  | 0.47 |  | 0.40 | [8 empty] | 13.87 |  |  |  |  | 0.73
2006 |  |  |  | 4290.89 |  |  | 4734 |  |  |  | 950 | [10 empty] | 53.02 |  |  |  | 53.61 | [5 empty] | 51.56 |  |  | 54.04 |  |  |  | 34.76 |  | 28.57 | [8 empty] | 17.83 |  |  |  |  | 0.59
2007 |  |  |  | 5326.10 |  |  | 5978 |  |  |  | 950 | [10 empty] | 66.13 |  |  |  | 67.27 | [5 empty] | 64.00 |  |  | 68.24 |  |  |  | 14.05 |  | 11.00 | [8 empty] | 21.73 |  |  |  |  | 1.14
2008 |  |  |  | 4560.77 |  |  | 5961 |  |  |  | 950 | [10 empty] | 58.58 |  |  |  | 59.66 | [5 empty] | 54.65 |  |  | 67.86 |  |  |  | 7.69 |  | 4.97 | [8 empty] | 35.37 |  |  |  |  | 1.08
2009 |  |  |  | 5343.14 |  |  | 7024 |  |  |  | 950 | [10 empty] | 74.56 |  |  |  | 82.64 | [5 empty] | 64.20 |  |  | 80.18 |  |  |  | 2.09 |  | 1.76 | [8 empty] | 15.60 |  |  |  |  | 8.08
2010 |  |  |  | 5243.17 |  |  | 6778 |  |  |  | 950 | [10 empty] | 62.88 |  |  |  | 75.43 | [5 empty] | 63.00 |  |  | 77.37 |  |  |  | 2.05 |  | 1.58 | [8 empty] | 22.99 |  |  |  |  | 12.54
2011 |  |  |  | 5372.61 |  |  | 6404 |  |  |  | 950 | [10 empty] | 65.16 |  |  |  | 71.95 | [5 empty] | 64.56 |  |  | 73.11 |  |  |  | 0.63 |  | 0.46 | [8 empty] | 27.59 |  |  |  |  | 6.80
2012 |  |  |  | 4058.36 |  |  | 4448 |  |  |  | 950 | [10 empty] | 48.46 |  |  |  | 49.74 | [5 empty] | 48.63 |  |  | 50.64 |  |  |  | 0.00 |  | 5.68 | [8 empty] | 44.58 |  |  |  |  | 1.28
2013 |  |  |  | 4731.07 |  |  | 6704 |  |  |  | 950 | [10 empty] | 73.05 |  |  |  | 75.60 | [5 empty] | 56.85 |  |  | 76.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.40 |  |  |  |  | 2.55
2014 |  |  |  | 5911.15 |  |  | 6781 |  |  |  | 950 | [10 empty] | 87.39 |  |  |  | 92.52 | [5 empty] | 71.03 |  |  | 77.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.48 |  |  |  |  | 5.13
2015 |  |  |  | 4993.40 |  |  | 6481 |  |  |  | 950 | [10 empty] | 60.94 |  |  |  | 72.89 | [5 empty] | 60.00 |  |  | 73.98 |  |  |  | 1.58 |  | 1.17 | [8 empty] | 25.95 |  |  |  |  | 11.95
2016 |  |  |  | 5067.23 |  |  | 6445 |  |  |  | 950 | [10 empty] | 63.58 |  |  |  | 72.23 | [5 empty] | 60.72 |  |  | 73.37 |  |  |  | 0.71 |  | 0.52 | [8 empty] | 27.26 |  |  |  |  | 8.65
2017 |  |  |  | 5657.50 |  |  | 6219 |  |  |  | 950 | [10 empty] | 66.08 |  |  |  | 70.15 | [5 empty] | 67.98 |  |  | 70.99 |  |  |  | 4.71 |  | 3.47 | [8 empty] | 26.38 |  |  |  |  | 4.07
2018 |  |  |  | 5849.13 |  |  | 6260 |  |  |  | 950 | [10 empty] | 67.57 |  |  |  | 70.40 | [5 empty] | 70.29 |  |  | 71.46 |  |  |  | 1.81 |  | 1.30 | [8 empty] | 28.30 |  |  |  |  | 2.83
2019 |  |  |  | 3729.04 |  |  | 4031 |  |  |  | 950 | [10 empty] | 43.76 |  |  |  | 45.05 | [5 empty] | 44.81 |  |  | 46.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 54.95 |  |  |  |  | 1.29
2020 |  |  |  | 5664.51 |  |  | 8490 |  |  |  | 950 | [10 empty] | 77.55 |  |  |  | 92.38 | [5 empty] | 67.88 |  |  | 96.65 |  |  |  | 0.69 |  | 0.64 | [8 empty] | 6.97 |  |  |  |  | 14.84
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 53 | [14 empty] | 213
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1747
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 241 | [14 empty] | 220
E. |  | Testing of plant systems or components | [35 empty] | 13
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 67
L. |  | Human factor related | [39 empty] | 0
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 16
Subtotal | [22 empty] | 241 |  |  |  | 53 | [10 empty] | 1980 |  |  |  | 229 | [11 empty] | 67
Total | [22 empty] | 294 | [14 empty] | 2276
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 3
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 2
16. |  |  | Steam generation systems | [34 empty] | 5
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 19
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
33. |  |  | Circulating Water System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [19 empty] | 47 | [14 empty] | 174
42. |  |  | Electrical Power Supply Systems | [19 empty] | 6 | [14 empty] | 1
Total | [22 empty] | 53 | [14 empty] | 212

## ZAPOROZHYE-1
2020 Operating Experience
UA-54 | [8 empty] | ZAPOROZHYE-1 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-04-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-12-10
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-12-25
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6243.86 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.29 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.09 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 1.91 %
Load Factor (LF) | [18 empty] | : | 74.82 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.8 %
Operating Factor (OF) | [18 empty] | : | 80.9 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1678 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 44.45 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 702.93 | 660.81 |  |  |  | 701.84 |  | 638.17 | [8 empty] | 598.90 |  |  | 0.00 | [6 empty] | 0.00 |  | 382.24 |  |  |  | 635.37 |  |  | 685.72 |  |  | 664.33 | [9 empty] | 573.56 |  |  | 6243.86
EAF [%] |  |  |  |  | 97.20 | 97.49 |  |  |  | 96.86 |  | 96.74 | [8 empty] | 96.26 |  |  | 100.00 | [6 empty] | 100.00 |  | 95.28 |  |  |  | 93.31 |  |  | 94.35 |  |  | 95.15 | [9 empty] | 81.10 |  |  | 95.29
UCF [%] |  |  |  |  | 98.47 | 98.43 |  |  |  | 98.22 |  | 98.00 | [8 empty] | 98.09 |  |  | 100.00 | [6 empty] | 100.00 |  | 98.05 |  |  |  | 97.10 |  |  | 96.87 |  |  | 96.61 | [9 empty] | 97.24 |  |  | 98.09
LF [%] |  |  |  |  | 99.45 | 99.94 |  |  |  | 99.43 |  | 93.30 | [8 empty] | 84.73 |  |  | 0.00 | [6 empty] | 0.00 |  | 54.08 |  |  |  | 92.89 |  |  | 96.89 |  |  | 97.12 | [9 empty] | 81.15 |  |  | 74.82
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 1.53 | [6 empty] | 0.00 |  | 69.76 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.90
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 1.53 | 1.57 |  |  |  | 1.78 |  | 2.00 | [8 empty] | 1.91 |  |  | 0.00 | [6 empty] | 0.00 |  | 1.95 |  |  |  | 2.90 |  |  | 3.13 |  |  | 3.39 | [9 empty] | 2.76 |  |  | 1.91
XUF [%] |  |  |  |  | 1.26 | 0.95 |  |  |  | 1.36 |  | 1.26 | [8 empty] | 1.83 |  |  | 0.00 | [6 empty] | 0.00 |  | 2.77 |  |  |  | 3.79 |  |  | 2.52 |  |  | 1.46 | [9 empty] | 16.14 |  |  | 2.80
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 189423.86 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.1 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 66.72 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.41 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 68.85 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 25.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.14 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 71.02 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4051.06 |  |  | 5893 |  |  |  | 950 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 4826.26 |  |  | 5580 |  |  |  | 950 | [10 empty] | 58.26 |  |  |  | 61.54 | [5 empty] | 57.99 |  |  | 63.70 |  |  |  | 19.03 |  | 14.46 | [8 empty] | 24.00 |  |  |  |  | 3.28
1987 |  |  |  | 6720.93 |  |  | 7205 |  |  |  | 1000 | [10 empty] | 80.82 |  |  |  | 80.82 | [5 empty] | 76.72 |  |  | 82.25 |  |  |  | 8.64 |  | 7.64 | [8 empty] | 11.54 |  |  |  |  | 0.00
1988 |  |  |  | 5170.41 |  |  | 6225 |  |  |  | 950 | [10 empty] | 67.21 |  |  |  | 67.37 | [5 empty] | 61.96 |  |  | 70.87 |  |  |  | 18.83 |  | 15.63 | [8 empty] | 17.00 |  |  |  |  | 0.17
1989 |  |  |  | 0.00 |  |  | 0 |  |  |  | 950 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 9.86 | [8 empty] | 90.14 |  |  |  |  | 0.00
1990 |  |  |  | 4668.70 |  |  | 5684 |  |  |  | 950 | [10 empty] | 56.40 |  |  |  | 58.79 | [5 empty] | 56.10 |  |  | 64.89 |  |  |  | 20.08 |  | 14.77 | [8 empty] | 26.45 |  |  |  |  | 2.39
1991 |  |  |  | 5332.22 |  |  | 6343 |  |  |  | 950 | [10 empty] | 64.25 |  |  |  | 68.51 | [5 empty] | 64.07 |  |  | 72.41 |  |  |  | 10.27 |  | 7.84 | [8 empty] | 23.65 |  |  |  |  | 4.27
1992 |  |  |  | 6103.50 |  |  | 6739 |  |  |  | 950 | [10 empty] | 67.84 |  |  |  | 70.30 | [5 empty] | 73.14 |  |  | 76.72 |  |  |  | 7.99 |  | 6.10 | [8 empty] | 23.60 |  |  |  |  | 2.46
1993 |  |  |  | 4209.71 |  |  | 6591 |  |  |  | 950 | [10 empty] | 52.14 |  |  |  | 53.46 | [5 empty] | 50.59 |  |  | 75.24 |  |  |  | 39.69 |  | 35.18 | [8 empty] | 11.36 |  |  |  |  | 1.32
1994 |  |  |  | 3770.96 |  |  | 5062 |  |  |  | 950 | [10 empty] | 45.49 |  |  |  | 45.50 | [5 empty] | 45.31 |  |  | 57.79 |  |  |  | 26.88 |  | 16.73 | [8 empty] | 37.77 |  |  |  |  | 0.01
1995 |  |  |  | 3557.27 |  |  | 4213 |  |  |  | 950 | [10 empty] | 42.75 |  |  |  | 44.87 | [5 empty] | 42.75 |  |  | 48.09 |  |  |  | 3.78 |  | 1.76 | [8 empty] | 53.37 |  |  |  |  | 2.13
1996 |  |  |  | 4299.48 |  |  | 5224 |  |  |  | 950 | [10 empty] | 51.52 |  |  |  | 53.54 | [5 empty] | 51.52 |  |  | 59.47 |  |  |  | 11.20 |  | 6.75 | [8 empty] | 39.71 |  |  |  |  | 2.02
1997 |  |  |  | 4070.63 |  |  | 5531 |  |  |  | 950 | [10 empty] | 48.91 |  |  |  | 53.86 | [5 empty] | 48.91 |  |  | 63.14 |  |  |  | 2.16 |  | 1.19 | [8 empty] | 44.95 |  |  |  |  | 4.94
1998 |  |  |  | 5517.47 |  |  | 6122 |  |  |  | 950 | [10 empty] | 66.28 |  |  |  | 68.73 | [5 empty] | 66.30 |  |  | 69.89 |  |  |  | 2.70 |  | 1.90 | [8 empty] | 29.37 |  |  |  |  | 2.45
1999 |  |  |  | 5992.45 |  |  | 7422 |  |  |  | 950 | [10 empty] | 72.01 |  |  |  | 84.01 | [5 empty] | 72.01 |  |  | 84.73 |  |  |  | 1.25 |  | 1.06 | [8 empty] | 14.93 |  |  |  |  | 12.01
2000 |  |  |  | 4222.71 |  |  | 4589 |  |  |  | 950 | [10 empty] | 50.26 |  |  |  | 52.04 | [5 empty] | 50.60 |  |  | 52.24 |  |  |  | 6.12 |  | 3.39 | [8 empty] | 44.57 |  |  |  |  | 1.78
2001 |  |  |  | 5847.06 |  |  | 6434 |  |  |  | 950 | [10 empty] | 69.93 |  |  |  | 71.84 | [5 empty] | 70.07 |  |  | 73.25 |  |  |  | 1.17 |  | 0.85 | [8 empty] | 27.30 |  |  |  |  | 1.92
2002 |  |  |  | 6734.96 |  |  | 7334 |  |  |  | 950 | [10 empty] | 80.57 |  |  |  | 83.21 | [5 empty] | 80.93 |  |  | 83.72 |  |  |  | 1.80 |  | 1.52 | [8 empty] | 15.26 |  |  |  |  | 2.64
2003 |  |  |  | 6596.43 |  |  | 7223 |  |  |  | 950 | [10 empty] | 78.96 |  |  |  | 81.85 | [5 empty] | 79.26 |  |  | 82.45 |  |  |  | 2.33 |  | 1.95 | [8 empty] | 16.20 |  |  |  |  | 2.89
2004 |  |  |  | 6748.27 |  |  | 7290 |  |  |  | 950 | [10 empty] | 80.60 |  |  |  | 82.64 | [5 empty] | 80.87 |  |  | 82.99 |  |  |  | 0.50 |  | 0.42 | [8 empty] | 16.94 |  |  |  |  | 2.04
2005 |  |  |  | 6018.79 |  |  | 6823 |  |  |  | 950 | [10 empty] | 76.81 |  |  |  | 77.76 | [5 empty] | 72.32 |  |  | 77.89 |  |  |  | 2.21 |  | 1.75 | [8 empty] | 20.49 |  |  |  |  | 0.95
2006 |  |  |  | 6899.02 |  |  | 7380 |  |  |  | 950 | [10 empty] | 83.32 |  |  |  | 83.75 | [5 empty] | 82.90 |  |  | 84.25 |  |  |  | 0.48 |  | 0.40 | [8 empty] | 15.85 |  |  |  |  | 0.43
2007 |  |  |  | 6921.01 |  |  | 7406 |  |  |  | 950 | [10 empty] | 83.51 |  |  |  | 83.61 | [5 empty] | 83.17 |  |  | 84.54 |  |  |  | 0.97 |  | 0.82 | [8 empty] | 15.57 |  |  |  |  | 0.10
2008 |  |  |  | 6227.72 |  |  | 6748 |  |  |  | 950 | [10 empty] | 80.28 |  |  |  | 81.37 | [5 empty] | 74.63 |  |  | 76.82 |  |  |  | 0.64 |  | 0.53 | [8 empty] | 18.10 |  |  |  |  | 1.09
2009 |  |  |  | 6584.42 |  |  | 7174 |  |  |  | 950 | [10 empty] | 82.38 |  |  |  | 83.43 | [5 empty] | 79.12 |  |  | 81.89 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 16.19 |  |  |  |  | 1.06
2010 |  |  |  | 6586.76 |  |  | 7396 |  |  |  | 950 | [10 empty] | 81.88 |  |  |  | 83.27 | [5 empty] | 79.15 |  |  | 84.43 |  |  |  | 1.13 |  | 0.95 | [8 empty] | 15.78 |  |  |  |  | 1.38
2011 |  |  |  | 6095.13 |  |  | 6702 |  |  |  | 950 | [10 empty] | 74.11 |  |  |  | 75.35 | [5 empty] | 73.24 |  |  | 76.51 |  |  |  | 1.02 |  | 0.78 | [8 empty] | 23.88 |  |  |  |  | 1.24
2012 |  |  |  | 6191.10 |  |  | 6765 |  |  |  | 950 | [10 empty] | 73.43 |  |  |  | 75.59 | [5 empty] | 74.19 |  |  | 77.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.41 |  |  |  |  | 2.15
2013 |  |  |  | 5816.74 |  |  | 6585 |  |  |  | 950 | [10 empty] | 70.70 |  |  |  | 72.48 | [5 empty] | 69.90 |  |  | 75.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.52 |  |  |  |  | 1.78
2014 |  |  |  | 5661.63 |  |  | 6397 |  |  |  | 950 | [10 empty] | 70.17 |  |  |  | 72.02 | [5 empty] | 68.03 |  |  | 73.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.98 |  |  |  |  | 1.85
2015 |  |  |  | 6835.34 |  |  | 8147 |  |  |  | 950 | [10 empty] | 89.73 |  |  |  | 92.17 | [5 empty] | 82.14 |  |  | 93.00 |  |  |  | 0.58 |  | 0.53 | [8 empty] | 7.29 |  |  |  |  | 2.44
2016 |  |  |  | 2082.50 |  |  | 2431 |  |  |  | 950 | [10 empty] | 26.65 |  |  |  | 27.02 | [5 empty] | 24.96 |  |  | 27.68 |  |  |  | 0.01 |  | 32.72 | [8 empty] | 40.26 |  |  |  |  | 0.37
2017 |  |  |  | 5577.73 |  |  | 6302 |  |  |  | 950 | [10 empty] | 67.23 |  |  |  | 70.21 | [5 empty] | 67.02 |  |  | 71.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.79 |  |  |  |  | 2.98
2018 |  |  |  | 6314.69 |  |  | 7144 |  |  |  | 950 | [10 empty] | 75.10 |  |  |  | 77.32 | [5 empty] | 75.88 |  |  | 81.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.68 |  |  |  |  | 2.22
2019 |  |  |  | 5790.20 |  |  | 6601 |  |  |  | 950 | [10 empty] | 69.55 |  |  |  | 72.98 | [5 empty] | 69.58 |  |  | 75.35 |  |  |  | 1.55 |  | 1.15 | [8 empty] | 25.87 |  |  |  |  | 3.43
2020 |  |  |  | 6243.86 |  |  | 7106 |  |  |  | 950 | [10 empty] | 95.29 |  |  |  | 98.09 | [5 empty] | 74.82 |  |  | 80.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.91 |  |  |  |  | 2.80
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 226
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1558 |  |  |  | 23
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 487
E. |  | Testing of plant systems or components | [35 empty] | 4
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 108 |  |  |  | 82
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 1678 | [19 empty] | 72
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 6
Z. |  | Other | [39 empty] | 3
Subtotal | [33 empty] | 1678 |  |  |  | 2157 |  |  |  | 342 | [11 empty] | 78
Total | [22 empty] | 1678 | [14 empty] | 2577
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 31
15. |  |  | Reactor Cooling Systems | [34 empty] | 22
16. |  |  | Steam generation systems | [34 empty] | 59
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 37
32. |  |  | Feedwater and Main Steam System | [34 empty] | 24
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 24
42. |  |  | Electrical Power Supply Systems | [34 empty] | 10
Total | [37 empty] | 227
Highlights (2020)
During the year there was not maintenance combined with refuelling.

## ZAPOROZHYE-2
2020 Operating Experience
UA-56 | [8 empty] | ZAPOROZHYE-2 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-01-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-07-22
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-02-15
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5114.54 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.13 %
Energy Availability Factor (EAF) | [18 empty] | : | 66.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.07 %
Unit Capability Factor (UCF) | [18 empty] | : | 71.24 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.7 %
Load Factor (LF) | [18 empty] | : | 61.29 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 4.71 %
Operating Factor (OF) | [18 empty] | : | 65.84 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3001 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 30.82 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 721.50 | 683.24 |  |  |  | 713.42 |  | 390.05 | [8 empty] | 441.43 |  |  | 661.08 | [6 empty] | 466.57 |  | 142.68 |  |  |  | 0.00 |  |  | 0.00 |  |  | 167.74 | [9 empty] | 726.84 |  |  | 5114.55
EAF [%] |  |  |  |  | 98.12 | 99.40 |  |  |  | 98.86 |  | 99.01 | [8 empty] | 98.63 |  |  | 95.01 | [6 empty] | 65.65 |  | 21.09 |  |  |  | 0.00 |  |  | 0.00 |  |  | 24.94 | [9 empty] | 98.31 |  |  | 66.52
UCF [%] |  |  |  |  | 98.87 | 100.00 |  |  |  | 100.00 |  | 99.86 | [8 empty] | 99.93 |  |  | 99.90 | [6 empty] | 99.48 |  | 31.73 |  |  |  | 0.00 |  |  | 0.00 |  |  | 25.28 | [9 empty] | 99.84 |  |  | 71.24
LF [%] |  |  |  |  | 102.08 | 103.33 |  |  |  | 101.07 |  | 57.02 | [8 empty] | 62.45 |  |  | 96.65 | [6 empty] | 66.01 |  | 20.19 |  |  |  | 0.00 |  |  | 0.00 |  |  | 24.52 | [9 empty] | 102.84 |  |  | 61.29
OF [%] |  |  |  |  | 99.19 | 100.00 |  |  |  | 100.00 |  | 66.94 | [8 empty] | 64.65 |  |  | 100.00 | [6 empty] | 100.00 |  | 32.26 |  |  |  | 0.00 |  |  | 0.00 |  |  | 27.08 | [9 empty] | 100.00 |  |  | 65.84
FLR [%] |  |  |  |  | 1.13 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.13
UCL [%] |  |  |  |  | 1.13 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 36.25 | [9 empty] | 0.00 |  |  | 3.07
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.14 | [8 empty] | 0.07 |  |  | 0.10 | [6 empty] | 0.52 |  | 68.27 |  |  |  | 100.00 |  |  | 100.00 |  |  | 38.47 | [9 empty] | 0.16 |  |  | 25.70
XUF [%] |  |  |  |  | 0.75 | 0.60 |  |  |  | 1.14 |  | 0.85 | [8 empty] | 1.30 |  |  | 4.89 | [6 empty] | 33.83 |  | 10.65 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.33 | [9 empty] | 1.53 |  |  | 4.71
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 188718.54 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.93 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 68.38 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.01 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 70.93 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 25.06 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.96 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.55 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.56 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 5651.61 |  |  | 6417 |  |  |  | 950 | [10 empty] | 65.51 |  |  |  | 68.22 | [5 empty] | 65.41 |  |  | 70.29 |  |  |  | 13.53 |  | 10.68 | [8 empty] | 21.10 |  |  |  |  | 2.72
1987 |  |  |  | 6058.32 |  |  | 6675 |  |  |  | 1000 | [10 empty] | 76.04 |  |  |  | 76.04 | [5 empty] | 69.16 |  |  | 76.20 |  |  |  | 13.47 |  | 11.84 | [8 empty] | 12.12 |  |  |  |  | 0.00
1988 |  |  |  | 6088.56 |  |  | 7253 |  |  |  | 950 | [10 empty] | 81.18 |  |  |  | 81.18 | [5 empty] | 72.96 |  |  | 82.57 |  |  |  | 7.45 |  | 6.53 | [8 empty] | 12.29 |  |  |  |  | 0.00
1989 |  |  |  | 3050.89 |  |  | 3393 |  |  |  | 950 | [10 empty] | 45.14 |  |  |  | 45.14 | [5 empty] | 36.66 |  |  | 38.73 |  |  |  | 7.00 |  | 3.40 | [8 empty] | 51.47 |  |  |  |  | 0.00
1990 |  |  |  | 1869.06 |  |  | 2165 |  |  |  | 950 | [10 empty] | 22.35 |  |  |  | 22.55 | [5 empty] | 22.46 |  |  | 24.71 |  |  |  | 8.56 |  | 2.11 | [8 empty] | 75.34 |  |  |  |  | 0.21
1991 |  |  |  | 4583.92 |  |  | 5112 |  |  |  | 950 | [10 empty] | 55.40 |  |  |  | 56.13 | [5 empty] | 55.08 |  |  | 58.36 |  |  |  | 17.35 |  | 11.78 | [8 empty] | 32.09 |  |  |  |  | 0.73
1992 |  |  |  | 6551.69 |  |  | 7016 |  |  |  | 950 | [10 empty] | 76.24 |  |  |  | 77.66 | [5 empty] | 78.51 |  |  | 79.87 |  |  |  | 5.49 |  | 4.51 | [8 empty] | 17.84 |  |  |  |  | 1.42
1993 |  |  |  | 4386.11 |  |  | 6194 |  |  |  | 950 | [10 empty] | 53.80 |  |  |  | 56.55 | [5 empty] | 52.71 |  |  | 70.71 |  |  |  | 27.05 |  | 20.97 | [8 empty] | 22.48 |  |  |  |  | 2.75
1994 |  |  |  | 4103.48 |  |  | 5924 |  |  |  | 950 | [10 empty] | 49.83 |  |  |  | 49.93 | [5 empty] | 49.31 |  |  | 67.63 |  |  |  | 8.00 |  | 4.34 | [8 empty] | 45.73 |  |  |  |  | 0.10
1995 |  |  |  | 5051.78 |  |  | 7329 |  |  |  | 950 | [10 empty] | 60.70 |  |  |  | 63.47 | [5 empty] | 60.70 |  |  | 83.66 |  |  |  | 15.01 |  | 11.21 | [8 empty] | 25.32 |  |  |  |  | 2.76
1996 |  |  |  | 5373.03 |  |  | 6247 |  |  |  | 950 | [10 empty] | 64.39 |  |  |  | 67.53 | [5 empty] | 64.39 |  |  | 71.12 |  |  |  | 5.44 |  | 3.88 | [8 empty] | 28.59 |  |  |  |  | 3.14
1997 |  |  |  | 6081.68 |  |  | 6745 |  |  |  | 950 | [10 empty] | 73.01 |  |  |  | 76.47 | [5 empty] | 73.08 |  |  | 77.00 |  |  |  | 0.35 |  | 0.27 | [8 empty] | 23.26 |  |  |  |  | 3.46
1998 |  |  |  | 4922.76 |  |  | 5601 |  |  |  | 950 | [10 empty] | 58.97 |  |  |  | 62.95 | [5 empty] | 59.15 |  |  | 63.94 |  |  |  | 1.01 |  | 0.64 | [8 empty] | 36.41 |  |  |  |  | 3.98
1999 |  |  |  | 5476.01 |  |  | 5887 |  |  |  | 950 | [10 empty] | 65.68 |  |  |  | 66.94 | [5 empty] | 65.80 |  |  | 67.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.06 |  |  |  |  | 1.26
2000 |  |  |  | 5626.40 |  |  | 6281 |  |  |  | 950 | [10 empty] | 67.42 |  |  |  | 70.74 | [5 empty] | 67.42 |  |  | 71.51 |  |  |  | 1.31 |  | 0.94 | [8 empty] | 28.33 |  |  |  |  | 3.31
2001 |  |  |  | 5867.65 |  |  | 6422 |  |  |  | 950 | [10 empty] | 70.59 |  |  |  | 72.47 | [5 empty] | 70.31 |  |  | 73.11 |  |  |  | 1.37 |  | 1.01 | [8 empty] | 26.52 |  |  |  |  | 1.88
2002 |  |  |  | 6315.64 |  |  | 6834 |  |  |  | 950 | [10 empty] | 75.87 |  |  |  | 78.84 | [5 empty] | 75.89 |  |  | 78.01 |  |  |  | 0.78 |  | 0.62 | [8 empty] | 20.54 |  |  |  |  | 2.97
2003 |  |  |  | 6742.38 |  |  | 7387 |  |  |  | 950 | [10 empty] | 80.89 |  |  |  | 83.75 | [5 empty] | 81.02 |  |  | 84.33 |  |  |  | 0.33 |  | 0.28 | [8 empty] | 15.97 |  |  |  |  | 2.86
2004 |  |  |  | 6944.29 |  |  | 7531 |  |  |  | 950 | [10 empty] | 83.15 |  |  |  | 85.99 | [5 empty] | 83.22 |  |  | 85.74 |  |  |  | 0.39 |  | 0.33 | [8 empty] | 13.68 |  |  |  |  | 2.85
2005 |  |  |  | 6303.15 |  |  | 7332 |  |  |  | 950 | [10 empty] | 82.41 |  |  |  | 83.38 | [5 empty] | 75.74 |  |  | 83.70 |  |  |  | 0.35 |  | 0.29 | [8 empty] | 16.33 |  |  |  |  | 0.97
2006 |  |  |  | 6644.71 |  |  | 7297 |  |  |  | 950 | [10 empty] | 82.82 |  |  |  | 83.03 | [5 empty] | 79.85 |  |  | 83.30 |  |  |  | 0.38 |  | 0.31 | [8 empty] | 16.66 |  |  |  |  | 0.21
2007 |  |  |  | 7064.48 |  |  | 7528 |  |  |  | 950 | [10 empty] | 85.13 |  |  |  | 85.34 | [5 empty] | 84.89 |  |  | 85.94 |  |  |  | 0.60 |  | 0.51 | [8 empty] | 14.15 |  |  |  |  | 0.21
2008 |  |  |  | 6763.54 |  |  | 7470 |  |  |  | 950 | [10 empty] | 84.26 |  |  |  | 84.58 | [5 empty] | 81.05 |  |  | 85.04 |  |  |  | 0.36 |  | 0.31 | [8 empty] | 15.11 |  |  |  |  | 0.33
2009 |  |  |  | 6127.91 |  |  | 7206 |  |  |  | 950 | [10 empty] | 80.90 |  |  |  | 81.79 | [5 empty] | 73.64 |  |  | 82.26 |  |  |  | 0.35 |  | 0.29 | [8 empty] | 17.92 |  |  |  |  | 0.89
2010 |  |  |  | 6674.39 |  |  | 7180 |  |  |  | 950 | [10 empty] | 79.78 |  |  |  | 81.39 | [5 empty] | 80.20 |  |  | 81.96 |  |  |  | 1.25 |  | 1.03 | [8 empty] | 17.58 |  |  |  |  | 1.61
2011 |  |  |  | 6155.30 |  |  | 6881 |  |  |  | 950 | [10 empty] | 75.09 |  |  |  | 77.42 | [5 empty] | 73.96 |  |  | 78.55 |  |  |  | 0.82 |  | 0.64 | [8 empty] | 21.94 |  |  |  |  | 2.33
2012 |  |  |  | 6046.81 |  |  | 7202 |  |  |  | 950 | [10 empty] | 77.80 |  |  |  | 80.19 | [5 empty] | 72.46 |  |  | 81.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.81 |  |  |  |  | 2.39
2013 |  |  |  | 5857.28 |  |  | 7464 |  |  |  | 950 | [10 empty] | 95.09 |  |  |  | 97.30 | [5 empty] | 70.38 |  |  | 85.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.70 |  |  |  |  | 2.22
2014 |  |  |  | 6307.66 |  |  | 6811 |  |  |  | 950 | [10 empty] | 73.55 |  |  |  | 75.75 | [5 empty] | 75.80 |  |  | 77.75 |  |  |  | 0.12 |  | 0.09 | [8 empty] | 24.16 |  |  |  |  | 2.19
2015 |  |  |  | 5210.05 |  |  | 5982 |  |  |  | 950 | [10 empty] | 62.35 |  |  |  | 66.53 | [5 empty] | 62.61 |  |  | 68.29 |  |  |  | 0.53 |  | 0.36 | [8 empty] | 33.11 |  |  |  |  | 4.18
2016 |  |  |  | 2595.13 |  |  | 3041 |  |  |  | 950 | [10 empty] | 33.12 |  |  |  | 33.78 | [5 empty] | 31.10 |  |  | 34.62 |  |  |  | 3.99 |  | 37.03 | [8 empty] | 29.19 |  |  |  |  | 0.65
2017 |  |  |  | 5361.20 |  |  | 8387 |  |  |  | 950 | [10 empty] | 71.31 |  |  |  | 95.66 | [5 empty] | 64.42 |  |  | 95.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.34 |  |  |  |  | 24.35
2018 |  |  |  | 5104.80 |  |  | 5883 |  |  |  | 950 | [10 empty] | 61.06 |  |  |  | 65.34 | [5 empty] | 61.34 |  |  | 67.16 |  |  |  | 2.42 |  | 1.62 | [8 empty] | 33.04 |  |  |  |  | 4.28
2019 |  |  |  | 4691.92 |  |  | 5002 |  |  |  | 950 | [10 empty] | 55.07 |  |  |  | 56.59 | [5 empty] | 56.38 |  |  | 57.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 43.41 |  |  |  |  | 1.52
2020 |  |  |  | 5114.55 |  |  | 5783 |  |  |  | 950 | [10 empty] | 66.52 |  |  |  | 71.24 | [5 empty] | 61.29 |  |  | 65.84 |  |  |  | 0.13 |  | 3.07 | [8 empty] | 25.70 |  |  |  |  | 4.71
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 266 | [14 empty] | 279
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2233 | [14 empty] | 1548
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 342
E. |  | Testing of plant systems or components | [35 empty] | 4
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 72 |  |  |  | 90
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 501 | [19 empty] | 58
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 5
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 2233 |  |  |  | 266 | [6 empty] | 501 |  |  |  | 1966 |  |  |  | 374 | [11 empty] | 63
Total | [22 empty] | 3000 | [14 empty] | 2403
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
14. |  |  | Safety Systems | [19 empty] | 260 | [14 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 13
16. |  |  | Steam generation systems | [34 empty] | 159
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 24
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 7
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 43
42. |  |  | Electrical Power Supply Systems | [19 empty] | 6 | [14 empty] | 8
Total | [22 empty] | 266 | [14 empty] | 282

## ZAPOROZHYE-3
2020 Operating Experience
UA-78 | [8 empty] | ZAPOROZHYE-3 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-04-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-12-10
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-03-05
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4771.2 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 56.51 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 58.3 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 41.7 %
Load Factor (LF) | [18 empty] | : | 57.18 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.8 %
Operating Factor (OF) | [18 empty] | : | 58.47 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3648 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 24.51 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 658.27 | [6 empty] | 618.07 |  | 684.99 |  |  |  | 677.38 |  |  | 708.77 |  |  | 699.41 | [9 empty] | 724.31 |  |  | 4771.20
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 94.29 | [6 empty] | 95.52 |  | 95.51 |  |  |  | 96.22 |  |  | 97.28 |  |  | 98.51 | [9 empty] | 98.99 |  |  | 56.51
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 97.96 | [6 empty] | 99.87 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 58.30
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 96.24 | [6 empty] | 87.45 |  | 96.91 |  |  |  | 99.03 |  |  | 100.14 |  |  | 102.25 | [9 empty] | 102.48 |  |  | 57.18
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 99.86 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 58.47
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 2.04 | [6 empty] | 0.13 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 41.70
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 3.67 | [6 empty] | 4.34 |  | 4.49 |  |  |  | 3.78 |  |  | 2.72 |  |  | 1.49 | [9 empty] | 1.01 |  |  | 1.80
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 190997.2 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.42 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.62 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.01 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 23.37 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 69.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.71 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.49 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 6690.98 |  |  | 7222 |  |  |  | 1000 | [10 empty] | 80.32 |  |  |  | 80.32 | [5 empty] | 78.39 |  |  | 80.15 |  |  |  | 4.02 |  | 3.37 | [8 empty] | 16.31 |  |  |  |  | 0.00
1988 |  |  |  | 6414.29 |  |  | 7077 |  |  |  | 950 | [10 empty] | 81.35 |  |  |  | 81.35 | [5 empty] | 76.87 |  |  | 80.57 |  |  |  | 5.32 |  | 4.57 | [8 empty] | 14.08 |  |  |  |  | 0.00
1989 |  |  |  | 6614.43 |  |  | 7373 |  |  |  | 950 | [10 empty] | 80.85 |  |  |  | 80.85 | [5 empty] | 79.48 |  |  | 84.17 |  |  |  | 3.97 |  | 3.34 | [8 empty] | 15.80 |  |  |  |  | 0.00
1990 |  |  |  | 5625.32 |  |  | 6166 |  |  |  | 950 | [10 empty] | 67.66 |  |  |  | 68.10 | [5 empty] | 67.60 |  |  | 70.39 |  |  |  | 15.26 |  | 12.26 | [8 empty] | 19.64 |  |  |  |  | 0.44
1991 |  |  |  | 4958.75 |  |  | 5877 |  |  |  | 950 | [10 empty] | 59.91 |  |  |  | 61.09 | [5 empty] | 59.59 |  |  | 67.09 |  |  |  | 11.90 |  | 8.25 | [8 empty] | 30.66 |  |  |  |  | 1.18
1992 |  |  |  | 4140.90 |  |  | 5274 |  |  |  | 950 | [10 empty] | 50.54 |  |  |  | 53.97 | [5 empty] | 49.62 |  |  | 60.04 |  |  |  | 9.62 |  | 5.74 | [8 empty] | 40.28 |  |  |  |  | 3.43
1993 |  |  |  | 5416.55 |  |  | 7263 |  |  |  | 950 | [10 empty] | 66.01 |  |  |  | 67.60 | [5 empty] | 65.09 |  |  | 82.91 |  |  |  | 19.21 |  | 16.08 | [8 empty] | 16.32 |  |  |  |  | 1.59
1994 |  |  |  | 4273.71 |  |  | 6068 |  |  |  | 950 | [10 empty] | 52.51 |  |  |  | 52.53 | [5 empty] | 51.35 |  |  | 69.27 |  |  |  | 4.07 |  | 2.23 | [8 empty] | 45.24 |  |  |  |  | 0.02
1995 |  |  |  | 4027.80 |  |  | 5804 |  |  |  | 950 | [10 empty] | 48.38 |  |  |  | 49.72 | [5 empty] | 48.40 |  |  | 66.26 |  |  |  | 1.31 |  | 0.66 | [8 empty] | 49.62 |  |  |  |  | 1.35
1996 |  |  |  | 4940.20 |  |  | 6096 |  |  |  | 950 | [10 empty] | 59.20 |  |  |  | 62.34 | [5 empty] | 59.20 |  |  | 69.40 |  |  |  | 6.67 |  | 4.45 | [8 empty] | 33.21 |  |  |  |  | 3.14
1997 |  |  |  | 4869.79 |  |  | 6544 |  |  |  | 950 | [10 empty] | 58.52 |  |  |  | 70.09 | [5 empty] | 58.52 |  |  | 74.70 |  |  |  | 3.99 |  | 2.91 | [8 empty] | 27.00 |  |  |  |  | 11.57
1998 |  |  |  | 4953.19 |  |  | 6316 |  |  |  | 950 | [10 empty] | 59.52 |  |  |  | 63.14 | [5 empty] | 59.52 |  |  | 72.10 |  |  |  | 2.25 |  | 1.45 | [8 empty] | 35.41 |  |  |  |  | 3.62
1999 |  |  |  | 5114.49 |  |  | 6162 |  |  |  | 950 | [10 empty] | 61.46 |  |  |  | 64.75 | [5 empty] | 61.46 |  |  | 70.34 |  |  |  | 5.25 |  | 3.59 | [8 empty] | 31.66 |  |  |  |  | 3.29
2000 |  |  |  | 6123.23 |  |  | 6875 |  |  |  | 950 | [10 empty] | 73.01 |  |  |  | 76.56 | [5 empty] | 73.38 |  |  | 78.27 |  |  |  | 1.98 |  | 1.55 | [8 empty] | 21.89 |  |  |  |  | 3.56
2001 |  |  |  | 6307.79 |  |  | 7027 |  |  |  | 950 | [10 empty] | 75.72 |  |  |  | 80.85 | [5 empty] | 75.59 |  |  | 80.00 |  |  |  | 2.63 |  | 2.18 | [8 empty] | 16.97 |  |  |  |  | 5.13
2002 |  |  |  | 6602.04 |  |  | 7470 |  |  |  | 950 | [10 empty] | 79.17 |  |  |  | 84.44 | [5 empty] | 79.33 |  |  | 85.27 |  |  |  | 1.52 |  | 1.30 | [8 empty] | 14.25 |  |  |  |  | 5.27
2003 |  |  |  | 6588.92 |  |  | 7236 |  |  |  | 950 | [10 empty] | 79.01 |  |  |  | 81.93 | [5 empty] | 79.17 |  |  | 82.60 |  |  |  | 0.63 |  | 0.52 | [8 empty] | 17.55 |  |  |  |  | 2.92
2004 |  |  |  | 6308.69 |  |  | 7371 |  |  |  | 950 | [10 empty] | 75.50 |  |  |  | 85.42 | [5 empty] | 75.60 |  |  | 83.91 |  |  |  | 1.34 |  | 1.16 | [8 empty] | 13.43 |  |  |  |  | 9.91
2005 |  |  |  | 6224.11 |  |  | 7229 |  |  |  | 950 | [10 empty] | 83.55 |  |  |  | 84.38 | [5 empty] | 74.79 |  |  | 82.52 |  |  |  | 1.30 |  | 1.11 | [8 empty] | 14.51 |  |  |  |  | 0.83
2006 |  |  |  | 6048.05 |  |  | 7031 |  |  |  | 950 | [10 empty] | 83.30 |  |  |  | 84.83 | [5 empty] | 72.68 |  |  | 80.26 |  |  |  | 1.41 |  | 1.21 | [8 empty] | 13.95 |  |  |  |  | 1.53
2007 |  |  |  | 6631.37 |  |  | 7268 |  |  |  | 950 | [10 empty] | 80.48 |  |  |  | 81.72 | [5 empty] | 79.68 |  |  | 82.97 |  |  |  | 1.34 |  | 1.11 | [8 empty] | 17.17 |  |  |  |  | 1.24
2008 |  |  |  | 6843.24 |  |  | 7589 |  |  |  | 950 | [10 empty] | 83.67 |  |  |  | 85.31 | [5 empty] | 82.01 |  |  | 86.40 |  |  |  | 1.12 |  | 0.97 | [8 empty] | 13.72 |  |  |  |  | 1.64
2009 |  |  |  | 6504.34 |  |  | 7996 |  |  |  | 950 | [10 empty] | 88.93 |  |  |  | 93.15 | [5 empty] | 78.16 |  |  | 91.28 |  |  |  | 0.85 |  | 0.80 | [8 empty] | 6.05 |  |  |  |  | 4.22
2010 |  |  |  | 6319.92 |  |  | 7341 |  |  |  | 950 | [10 empty] | 78.31 |  |  |  | 82.70 | [5 empty] | 75.93 |  |  | 83.79 |  |  |  | 1.12 |  | 0.94 | [8 empty] | 16.36 |  |  |  |  | 4.38
2011 |  |  |  | 6791.75 |  |  | 7569 |  |  |  | 950 | [10 empty] | 82.59 |  |  |  | 84.71 | [5 empty] | 81.61 |  |  | 86.40 |  |  |  | 1.27 |  | 1.09 | [8 empty] | 14.20 |  |  |  |  | 2.12
2012 |  |  |  | 6178.42 |  |  | 6984 |  |  |  | 950 | [10 empty] | 76.02 |  |  |  | 78.41 | [5 empty] | 74.04 |  |  | 79.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.59 |  |  |  |  | 2.39
2013 |  |  |  | 5420.54 |  |  | 6518 |  |  |  | 950 | [10 empty] | 81.45 |  |  |  | 83.61 | [5 empty] | 65.14 |  |  | 74.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.39 |  |  |  |  | 2.16
2014 |  |  |  | 6279.95 |  |  | 7159 |  |  |  | 950 | [10 empty] | 79.18 |  |  |  | 80.92 | [5 empty] | 75.46 |  |  | 81.72 |  |  |  | 2.36 |  | 1.95 | [8 empty] | 17.13 |  |  |  |  | 1.74
2015 |  |  |  | 6983.04 |  |  | 7557 |  |  |  | 950 | [10 empty] | 83.36 |  |  |  | 85.40 | [5 empty] | 83.91 |  |  | 86.27 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 14.53 |  |  |  |  | 2.04
2016 |  |  |  | 6593.10 |  |  | 7004 |  |  |  | 950 | [10 empty] | 77.21 |  |  |  | 79.08 | [5 empty] | 79.01 |  |  | 79.74 |  |  |  | 0.24 |  | 0.19 | [8 empty] | 20.73 |  |  |  |  | 1.87
2017 |  |  |  | 2314.02 |  |  | 2440 |  |  |  | 950 | [10 empty] | 27.17 |  |  |  | 27.49 | [5 empty] | 27.81 |  |  | 27.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 72.51 |  |  |  |  | 0.32
2018 |  |  |  | 6166.88 |  |  | 6623 |  |  |  | 950 | [10 empty] | 72.39 |  |  |  | 75.52 | [5 empty] | 74.10 |  |  | 75.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.48 |  |  |  |  | 3.13
2019 |  |  |  | 6950.92 |  |  | 7590 |  |  |  | 950 | [10 empty] | 82.52 |  |  |  | 86.42 | [5 empty] | 83.52 |  |  | 86.64 |  |  |  | 4.52 |  | 4.09 | [8 empty] | 9.49 |  |  |  |  | 3.90
2020 |  |  |  | 4771.20 |  |  | 5136 |  |  |  | 950 | [10 empty] | 56.51 |  |  |  | 58.30 | [5 empty] | 57.18 |  |  | 58.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 41.70 |  |  |  |  | 1.80
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 1 | [14 empty] | 75
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 3648 | [14 empty] | 1541
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 149
E. |  | Testing of plant systems or components | [35 empty] | 14 |  |  |  | 2
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 187
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 8
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 56
L. |  | Human factor related | [39 empty] | 5
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 8
Z. |  | Other | [35 empty] | 1 |  |  |  | 3
Subtotal | [22 empty] | 3648 |  |  |  | 1 | [10 empty] | 1892 |  |  |  | 85 | [11 empty] | 72
Total | [22 empty] | 3649 | [14 empty] | 2049
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 3
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 5
15. |  |  | Reactor Cooling Systems | [34 empty] | 1
16. |  |  | Steam generation systems | [34 empty] | 10
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 6
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 30
42. |  |  | Electrical Power Supply Systems | [19 empty] | 1 | [14 empty] | 10
Total | [22 empty] | 1 | [14 empty] | 81

## ZAPOROZHYE-4
2020 Operating Experience
UA-79 | [8 empty] | ZAPOROZHYE-4 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1983-04-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-12-18
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-04-14
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 3748.24 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 44.18 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.82 %
Unit Capability Factor (UCF) | [18 empty] | : | 45.91 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 53.27 %
Load Factor (LF) | [18 empty] | : | 44.92 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.74 %
Operating Factor (OF) | [18 empty] | : | 46.16 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4729 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 22.23 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 723.45 | 677.24 |  |  |  | 714.43 |  | 553.63 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 366.66 | [9 empty] | 712.84 |  |  | 3748.25
EAF [%] |  |  |  |  | 99.50 | 99.40 |  |  |  | 98.71 |  | 82.28 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 54.06 | [9 empty] | 98.56 |  |  | 44.18
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 98.75 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 54.85 | [9 empty] | 100.00 |  |  | 45.91
LF [%] |  |  |  |  | 102.36 | 102.43 |  |  |  | 101.22 |  | 80.94 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 53.60 | [9 empty] | 100.85 |  |  | 44.92
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 56.67 | [9 empty] | 100.00 |  |  | 46.16
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 10.00 | [9 empty] | 0.00 |  |  | 0.82
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 1.25 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 35.15 | [9 empty] | 0.00 |  |  | 53.27
XUF [%] |  |  |  |  | 0.50 | 0.60 |  |  |  | 1.29 |  | 16.47 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.79 | [9 empty] | 1.44 |  |  | 1.74
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 190543.24 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.92 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 22.49 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.55 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.29 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.52 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 6431.44 |  |  | 7143 |  |  |  | 950 | [10 empty] | 79.07 |  |  |  | 79.07 | [5 empty] | 76.53 |  |  | 79.96 |  |  |  | 6.22 |  | 5.25 | [8 empty] | 15.68 |  |  |  |  | 0.00
1989 |  |  |  | 5828.07 |  |  | 6613 |  |  |  | 950 | [10 empty] | 73.08 |  |  |  | 73.08 | [5 empty] | 70.03 |  |  | 75.49 |  |  |  | 10.85 |  | 8.90 | [8 empty] | 18.02 |  |  |  |  | 0.00
1990 |  |  |  | 6637.35 |  |  | 7393 |  |  |  | 950 | [10 empty] | 78.86 |  |  |  | 79.78 | [5 empty] | 79.76 |  |  | 84.39 |  |  |  | 8.99 |  | 7.88 | [8 empty] | 12.34 |  |  |  |  | 0.92
1991 |  |  |  | 4259.50 |  |  | 5114 |  |  |  | 950 | [10 empty] | 51.08 |  |  |  | 51.25 | [5 empty] | 51.18 |  |  | 58.38 |  |  |  | 23.69 |  | 15.91 | [8 empty] | 32.84 |  |  |  |  | 0.17
1992 |  |  |  | 6962.30 |  |  | 6961 |  |  |  | 1000 | [10 empty] | 78.56 |  |  |  | 78.81 | [5 empty] | 79.26 |  |  | 79.25 |  |  |  | 2.75 |  | 2.23 | [8 empty] | 18.96 |  |  |  |  | 0.25
1993 |  |  |  | 6118.75 |  |  | 6821 |  |  |  | 950 | [10 empty] | 73.37 |  |  |  | 74.09 | [5 empty] | 73.53 |  |  | 77.87 |  |  |  | 12.30 |  | 10.39 | [8 empty] | 15.52 |  |  |  |  | 0.72
1994 |  |  |  | 5888.70 |  |  | 6718 |  |  |  | 950 | [10 empty] | 71.28 |  |  |  | 71.41 | [5 empty] | 70.76 |  |  | 76.69 |  |  |  | 2.19 |  | 1.60 | [8 empty] | 26.99 |  |  |  |  | 0.13
1995 |  |  |  | 4717.10 |  |  | 5902 |  |  |  | 950 | [10 empty] | 56.68 |  |  |  | 58.41 | [5 empty] | 56.68 |  |  | 67.37 |  |  |  | 5.56 |  | 3.44 | [8 empty] | 38.15 |  |  |  |  | 1.73
1996 |  |  |  | 5372.18 |  |  | 6372 |  |  |  | 950 | [10 empty] | 64.38 |  |  |  | 66.26 | [5 empty] | 64.38 |  |  | 72.54 |  |  |  | 6.81 |  | 4.84 | [8 empty] | 28.89 |  |  |  |  | 1.89
1997 |  |  |  | 6284.42 |  |  | 7060 |  |  |  | 950 | [10 empty] | 75.52 |  |  |  | 79.93 | [5 empty] | 75.52 |  |  | 80.59 |  |  |  | 2.47 |  | 2.03 | [8 empty] | 18.04 |  |  |  |  | 4.42
1998 |  |  |  | 6022.02 |  |  | 6839 |  |  |  | 950 | [10 empty] | 72.36 |  |  |  | 74.04 | [5 empty] | 72.36 |  |  | 78.07 |  |  |  | 3.06 |  | 2.33 | [8 empty] | 23.62 |  |  |  |  | 1.68
1999 |  |  |  | 3921.35 |  |  | 4630 |  |  |  | 950 | [10 empty] | 47.12 |  |  |  | 49.83 | [5 empty] | 47.12 |  |  | 52.85 |  |  |  | 0.58 |  | 0.29 | [8 empty] | 49.88 |  |  |  |  | 2.71
2000 |  |  |  | 6708.40 |  |  | 7423 |  |  |  | 950 | [10 empty] | 80.29 |  |  |  | 83.81 | [5 empty] | 80.39 |  |  | 84.51 |  |  |  | 0.90 |  | 0.77 | [8 empty] | 15.42 |  |  |  |  | 3.52
2001 |  |  |  | 6091.25 |  |  | 7884 |  |  |  | 950 | [10 empty] | 73.15 |  |  |  | 89.85 | [5 empty] | 72.99 |  |  | 89.75 |  |  |  | 0.42 |  | 0.38 | [8 empty] | 9.77 |  |  |  |  | 16.70
2002 |  |  |  | 6337.06 |  |  | 6895 |  |  |  | 950 | [10 empty] | 76.15 |  |  |  | 78.53 | [5 empty] | 76.15 |  |  | 78.71 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 21.43 |  |  |  |  | 2.38
2003 |  |  |  | 6736.32 |  |  | 7248 |  |  |  | 950 | [10 empty] | 80.87 |  |  |  | 82.45 | [5 empty] | 80.95 |  |  | 82.74 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 17.52 |  |  |  |  | 1.58
2004 |  |  |  | 6537.56 |  |  | 7247 |  |  |  | 950 | [10 empty] | 78.27 |  |  |  | 88.49 | [5 empty] | 78.34 |  |  | 82.50 |  |  |  | 0.21 |  | 0.19 | [8 empty] | 11.32 |  |  |  |  | 10.22
2005 |  |  |  | 6511.87 |  |  | 7498 |  |  |  | 950 | [10 empty] | 84.10 |  |  |  | 85.13 | [5 empty] | 78.25 |  |  | 85.59 |  |  |  | 0.36 |  | 0.30 | [8 empty] | 14.56 |  |  |  |  | 1.04
2006 |  |  |  | 6621.84 |  |  | 7186 |  |  |  | 950 | [10 empty] | 84.82 |  |  |  | 85.16 | [5 empty] | 79.57 |  |  | 82.03 |  |  |  | 0.25 |  | 0.21 | [8 empty] | 14.63 |  |  |  |  | 0.34
2007 |  |  |  | 7027.84 |  |  | 7645 |  |  |  | 950 | [10 empty] | 86.22 |  |  |  | 87.10 | [5 empty] | 84.45 |  |  | 87.27 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 12.88 |  |  |  |  | 0.88
2008 |  |  |  | 6031.59 |  |  | 7265 |  |  |  | 950 | [10 empty] | 79.65 |  |  |  | 82.20 | [5 empty] | 72.28 |  |  | 82.71 |  |  |  | 0.56 |  | 0.46 | [8 empty] | 17.34 |  |  |  |  | 2.55
2009 |  |  |  | 6121.29 |  |  | 7111 |  |  |  | 950 | [10 empty] | 86.67 |  |  |  | 87.28 | [5 empty] | 73.56 |  |  | 81.18 |  |  |  | 0.52 |  | 0.46 | [8 empty] | 12.27 |  |  |  |  | 0.61
2010 |  |  |  | 6388.85 |  |  | 7086 |  |  |  | 950 | [10 empty] | 81.31 |  |  |  | 83.77 | [5 empty] | 76.77 |  |  | 80.89 |  |  |  | 0.60 |  | 0.51 | [8 empty] | 15.72 |  |  |  |  | 2.46
2011 |  |  |  | 6353.81 |  |  | 6892 |  |  |  | 950 | [10 empty] | 76.58 |  |  |  | 77.65 | [5 empty] | 76.35 |  |  | 78.68 |  |  |  | 1.01 |  | 0.80 | [8 empty] | 21.56 |  |  |  |  | 1.06
2012 |  |  |  | 6403.06 |  |  | 6941 |  |  |  | 950 | [10 empty] | 77.11 |  |  |  | 77.44 | [5 empty] | 76.73 |  |  | 79.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.56 |  |  |  |  | 0.33
2013 |  |  |  | 6404.96 |  |  | 7580 |  |  |  | 950 | [10 empty] | 82.40 |  |  |  | 84.16 | [5 empty] | 76.96 |  |  | 86.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.84 |  |  |  |  | 1.76
2014 |  |  |  | 6582.83 |  |  | 7375 |  |  |  | 950 | [10 empty] | 80.89 |  |  |  | 82.57 | [5 empty] | 79.10 |  |  | 84.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.43 |  |  |  |  | 1.68
2015 |  |  |  | 6334.43 |  |  | 6921 |  |  |  | 950 | [10 empty] | 74.46 |  |  |  | 77.41 | [5 empty] | 76.12 |  |  | 79.01 |  |  |  | 0.18 |  | 0.14 | [8 empty] | 22.45 |  |  |  |  | 2.95
2016 |  |  |  | 5903.10 |  |  | 6670 |  |  |  | 950 | [10 empty] | 71.13 |  |  |  | 75.53 | [5 empty] | 70.74 |  |  | 75.93 |  |  |  | 2.66 |  | 2.07 | [8 empty] | 22.40 |  |  |  |  | 4.40
2017 |  |  |  | 6363.95 |  |  | 7006 |  |  |  | 950 | [10 empty] | 76.50 |  |  |  | 78.35 | [5 empty] | 76.47 |  |  | 79.98 |  |  |  | 4.79 |  | 3.94 | [8 empty] | 17.71 |  |  |  |  | 1.84
2018 |  |  |  | 3220.41 |  |  | 3407 |  |  |  | 950 | [10 empty] | 38.17 |  |  |  | 38.54 | [5 empty] | 38.70 |  |  | 38.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 61.46 |  |  |  |  | 0.37
2019 |  |  |  | 6249.05 |  |  | 6673 |  |  |  | 950 | [10 empty] | 73.81 |  |  |  | 75.98 | [5 empty] | 75.09 |  |  | 76.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.02 |  |  |  |  | 2.17
2020 |  |  |  | 3748.24 |  |  | 4055 |  |  |  | 950 | [10 empty] | 44.18 |  |  |  | 45.91 | [5 empty] | 44.92 |  |  | 46.16 |  |  |  | 0.00 |  | 0.82 | [8 empty] | 53.27 |  |  |  |  | 1.74
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 71 | [14 empty] | 112
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1464
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 4657 | [14 empty] | 398
E. |  | Testing of plant systems or components | [35 empty] | 11 |  |  |  | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 56
L. |  | Human factor related | [39 empty] | 20
Subtotal | [22 empty] | 4657 |  |  |  | 71 | [10 empty] | 1873 |  |  |  | 132 | [11 empty] | 56
Total | [22 empty] | 4728 | [14 empty] | 2061
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 21
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [19 empty] | 71 | [14 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 7
16. |  |  | Steam generation systems | [34 empty] | 13
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 58
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 71 | [14 empty] | 128

## ZAPOROZHYE-5
2020 Operating Experience
UA-126 | [8 empty] | ZAPOROZHYE-5 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-11-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1989-08-14
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-10-27
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2261.14 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 28.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 13.11 %
Unit Capability Factor (UCF) | [18 empty] | : | 28.71 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 58.18 %
Load Factor (LF) | [18 empty] | : | 27.1 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.18 %
Operating Factor (OF) | [18 empty] | : | 28.98 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 6238 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 25.39 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 713.83 | 670.86 |  |  |  | 607.13 |  | 269.33 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2261.14
EAF [%] |  |  |  |  | 98.86 | 98.76 |  |  |  | 98.47 |  | 48.74 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 28.52
UCF [%] |  |  |  |  | 99.34 | 99.35 |  |  |  | 99.21 |  | 49.14 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 28.71
LF [%] |  |  |  |  | 100.99 | 101.46 |  |  |  | 86.01 |  | 39.38 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 27.10
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 50.42 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 28.98
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 56.67 | [9 empty] | 100.00 |  |  | 13.11
PUF [%] |  |  |  |  | 0.66 | 0.65 |  |  |  | 0.79 |  | 50.86 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 43.33 | [9 empty] | 0.00 |  |  | 58.18
XUF [%] |  |  |  |  | 0.48 | 0.59 |  |  |  | 0.74 |  | 0.40 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.18
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 182393.14 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.02 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.84 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.78 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.82 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.4 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.98 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.49 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 2147.46 |  |  | 2938 |  |  |  | 950 | [10 empty] | 85.59 |  |  |  | 85.59 | [5 empty] | 80.54 |  |  | 86.20 |  |  |  | 10.02 |  | 9.54 | [8 empty] | 4.88 |  |  |  |  | 0.00
1990 |  |  |  | 4678.67 |  |  | 6002 |  |  |  | 950 | [10 empty] | 56.65 |  |  |  | 57.92 | [5 empty] | 56.22 |  |  | 68.52 |  |  |  | 20.69 |  | 15.11 | [8 empty] | 26.98 |  |  |  |  | 1.27
1991 |  |  |  | 6554.93 |  |  | 7319 |  |  |  | 950 | [10 empty] | 78.38 |  |  |  | 79.49 | [5 empty] | 78.77 |  |  | 83.55 |  |  |  | 8.70 |  | 7.57 | [8 empty] | 12.94 |  |  |  |  | 1.11
1992 |  |  |  | 6898.80 |  |  | 7032 |  |  |  | 1000 | [10 empty] | 79.16 |  |  |  | 80.12 | [5 empty] | 78.54 |  |  | 80.05 |  |  |  | 2.62 |  | 2.15 | [8 empty] | 17.73 |  |  |  |  | 0.95
1993 |  |  |  | 5661.77 |  |  | 6735 |  |  |  | 950 | [10 empty] | 68.26 |  |  |  | 68.92 | [5 empty] | 68.03 |  |  | 76.88 |  |  |  | 13.97 |  | 11.19 | [8 empty] | 19.88 |  |  |  |  | 0.66
1994 |  |  |  | 4858.94 |  |  | 6779 |  |  |  | 950 | [10 empty] | 59.12 |  |  |  | 59.13 | [5 empty] | 58.39 |  |  | 77.39 |  |  |  | 20.05 |  | 14.83 | [8 empty] | 26.04 |  |  |  |  | 0.02
1995 |  |  |  | 5391.90 |  |  | 6506 |  |  |  | 950 | [10 empty] | 64.73 |  |  |  | 66.00 | [5 empty] | 64.79 |  |  | 74.27 |  |  |  | 4.95 |  | 3.44 | [8 empty] | 30.56 |  |  |  |  | 1.27
1996 |  |  |  | 6126.05 |  |  | 6799 |  |  |  | 950 | [10 empty] | 73.41 |  |  |  | 74.14 | [5 empty] | 73.41 |  |  | 77.40 |  |  |  | 2.38 |  | 1.81 | [8 empty] | 24.05 |  |  |  |  | 0.73
1997 |  |  |  | 6381.48 |  |  | 6705 |  |  |  | 950 | [10 empty] | 75.77 |  |  |  | 76.23 | [5 empty] | 76.68 |  |  | 76.54 |  |  |  | 2.33 |  | 1.82 | [8 empty] | 21.95 |  |  |  |  | 0.46
1998 |  |  |  | 5856.23 |  |  | 6249 |  |  |  | 950 | [10 empty] | 70.12 |  |  |  | 70.72 | [5 empty] | 70.37 |  |  | 71.34 |  |  |  | 1.34 |  | 0.96 | [8 empty] | 28.31 |  |  |  |  | 0.60
1999 |  |  |  | 5070.20 |  |  | 5525 |  |  |  | 950 | [10 empty] | 60.60 |  |  |  | 62.96 | [5 empty] | 60.93 |  |  | 63.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.04 |  |  |  |  | 2.36
2000 |  |  |  | 6286.64 |  |  | 6928 |  |  |  | 950 | [10 empty] | 74.89 |  |  |  | 77.87 | [5 empty] | 75.34 |  |  | 78.87 |  |  |  | 1.02 |  | 0.80 | [8 empty] | 21.34 |  |  |  |  | 2.97
2001 |  |  |  | 5890.83 |  |  | 6751 |  |  |  | 950 | [10 empty] | 70.66 |  |  |  | 76.19 | [5 empty] | 70.59 |  |  | 76.86 |  |  |  | 1.90 |  | 1.48 | [8 empty] | 22.33 |  |  |  |  | 5.54
2002 |  |  |  | 6222.49 |  |  | 6983 |  |  |  | 950 | [10 empty] | 74.55 |  |  |  | 80.79 | [5 empty] | 74.77 |  |  | 79.71 |  |  |  | 1.22 |  | 0.99 | [8 empty] | 18.21 |  |  |  |  | 6.25
2003 |  |  |  | 6585.47 |  |  | 7107 |  |  |  | 950 | [10 empty] | 79.00 |  |  |  | 80.20 | [5 empty] | 79.13 |  |  | 81.13 |  |  |  | 8.06 |  | 7.03 | [8 empty] | 12.77 |  |  |  |  | 1.20
2004 |  |  |  | 6826.67 |  |  | 7551 |  |  |  | 950 | [10 empty] | 81.62 |  |  |  | 85.58 | [5 empty] | 81.81 |  |  | 85.96 |  |  |  | 0.28 |  | 0.24 | [8 empty] | 14.18 |  |  |  |  | 3.97
2005 |  |  |  | 6278.94 |  |  | 6975 |  |  |  | 950 | [10 empty] | 80.79 |  |  |  | 81.48 | [5 empty] | 75.45 |  |  | 79.62 |  |  |  | 0.66 |  | 0.54 | [8 empty] | 17.98 |  |  |  |  | 0.69
2006 |  |  |  | 6713.60 |  |  | 7297 |  |  |  | 950 | [10 empty] | 83.28 |  |  |  | 83.72 | [5 empty] | 80.67 |  |  | 83.30 |  |  |  | 0.24 |  | 0.20 | [8 empty] | 16.08 |  |  |  |  | 0.44
2007 |  |  |  | 6936.51 |  |  | 7408 |  |  |  | 950 | [10 empty] | 84.26 |  |  |  | 84.29 | [5 empty] | 83.35 |  |  | 84.57 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 15.56 |  |  |  |  | 0.03
2008 |  |  |  | 6935.93 |  |  | 7708 |  |  |  | 950 | [10 empty] | 86.95 |  |  |  | 87.59 | [5 empty] | 83.12 |  |  | 87.75 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 12.35 |  |  |  |  | 0.64
2009 |  |  |  | 6700.77 |  |  | 7445 |  |  |  | 950 | [10 empty] | 83.02 |  |  |  | 84.88 | [5 empty] | 80.52 |  |  | 84.99 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 15.11 |  |  |  |  | 1.86
2010 |  |  |  | 6507.63 |  |  | 7081 |  |  |  | 950 | [10 empty] | 78.30 |  |  |  | 80.42 | [5 empty] | 78.20 |  |  | 80.83 |  |  |  | 0.36 |  | 0.29 | [8 empty] | 19.29 |  |  |  |  | 2.13
2011 |  |  |  | 6280.40 |  |  | 6861 |  |  |  | 950 | [10 empty] | 76.04 |  |  |  | 77.71 | [5 empty] | 75.47 |  |  | 78.32 |  |  |  | 0.41 |  | 0.32 | [8 empty] | 21.97 |  |  |  |  | 1.67
2012 |  |  |  | 7022.33 |  |  | 7545 |  |  |  | 950 | [10 empty] | 82.91 |  |  |  | 84.95 | [5 empty] | 84.15 |  |  | 85.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.05 |  |  |  |  | 2.04
2013 |  |  |  | 6903.10 |  |  | 7381 |  |  |  | 950 | [10 empty] | 80.66 |  |  |  | 82.98 | [5 empty] | 82.95 |  |  | 84.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.02 |  |  |  |  | 2.31
2014 |  |  |  | 5920.96 |  |  | 7601 |  |  |  | 950 | [10 empty] | 95.58 |  |  |  | 97.01 | [5 empty] | 71.15 |  |  | 86.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.99 |  |  |  |  | 1.44
2015 |  |  |  | 4911.23 |  |  | 6519 |  |  |  | 950 | [10 empty] | 65.24 |  |  |  | 73.21 | [5 empty] | 59.01 |  |  | 74.41 |  |  |  | 1.31 |  | 0.97 | [8 empty] | 25.82 |  |  |  |  | 7.96
2016 |  |  |  | 5945.32 |  |  | 7345 |  |  |  | 950 | [10 empty] | 77.23 |  |  |  | 82.48 | [5 empty] | 71.25 |  |  | 83.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.52 |  |  |  |  | 5.26
2017 |  |  |  | 6452.82 |  |  | 7052 |  |  |  | 950 | [10 empty] | 76.79 |  |  |  | 79.39 | [5 empty] | 77.54 |  |  | 80.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.61 |  |  |  |  | 2.60
2018 |  |  |  | 6256.59 |  |  | 6742 |  |  |  | 950 | [10 empty] | 74.12 |  |  |  | 75.95 | [5 empty] | 75.18 |  |  | 76.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.05 |  |  |  |  | 1.83
2019 |  |  |  | 5239.69 |  |  | 5999 |  |  |  | 950 | [10 empty] | 66.35 |  |  |  | 67.56 | [5 empty] | 62.96 |  |  | 68.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.44 |  |  |  |  | 1.21
2020 |  |  |  | 2261.14 |  |  | 2546 |  |  |  | 950 | [10 empty] | 28.52 |  |  |  | 28.71 | [5 empty] | 27.10 |  |  | 28.98 |  |  |  | 0.00 |  | 13.11 | [8 empty] | 58.18 |  |  |  |  | 0.18
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 1151 | [14 empty] | 99
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1463
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 156
E. |  | Testing of plant systems or components | [35 empty] | 16
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [20 empty] | 5086 | [14 empty] | 163
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 46
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 5086 |  |  |  | 1151 | [10 empty] | 1798 |  |  |  | 105 | [11 empty] | 46
Total | [22 empty] | 6237 | [14 empty] | 1949
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 5
14. |  |  | Safety Systems | [19 empty] | 1151 | [14 empty] | 37
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 27
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 5
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [22 empty] | 1151 | [14 empty] | 98

## ZAPOROZHYE-6
2020 Operating Experience
UA-127 | [8 empty] | ZAPOROZHYE-6 | [26 empty] | UKRAINE
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Owner | [7 empty] | : | NNEGC (State Enterprise “National Nuclear Energy Generating Company ‘Energoatom”)
Reactor Supplier | [7 empty] | : | PAIP (PRODUCTION AMALGAMATION IZHORSKY PLANT ATOMMASH,VOLGODONSK,RUSSIA)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1986-06-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1995-10-19
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1996-09-17
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 25 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4998.2 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 67.05 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 68.32 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 31.68 %
Load Factor (LF) | [18 empty] | : | 59.9 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.27 %
Operating Factor (OF) | [18 empty] | : | 62.52 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3292 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 18.91 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 340.54 | [8 empty] | 446.20 |  |  | 76.30 | [6 empty] | 682.03 |  | 631.93 |  |  |  | 673.41 |  |  | 711.42 |  |  | 703.58 | [9 empty] | 732.79 |  |  | 4998.20
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 48.81 | [8 empty] | 75.00 |  |  | 99.31 | [6 empty] | 94.89 |  | 95.51 |  |  |  | 96.08 |  |  | 96.93 |  |  | 97.94 | [9 empty] | 98.06 |  |  | 67.05
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 49.29 | [8 empty] | 76.08 |  |  | 99.79 | [6 empty] | 98.49 |  | 98.70 |  |  |  | 98.81 |  |  | 98.85 |  |  | 98.90 | [9 empty] | 98.76 |  |  | 68.32
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 49.79 | [8 empty] | 63.13 |  |  | 11.15 | [6 empty] | 96.50 |  | 89.41 |  |  |  | 98.45 |  |  | 100.52 |  |  | 102.86 | [9 empty] | 103.68 |  |  | 59.90
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 51.25 | [8 empty] | 77.55 |  |  | 17.92 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 62.52
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 50.71 | [8 empty] | 23.92 |  |  | 0.21 | [6 empty] | 1.51 |  | 1.30 |  |  |  | 1.19 |  |  | 1.15 |  |  | 1.10 | [9 empty] | 1.24 |  |  | 31.68
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.49 | [8 empty] | 1.08 |  |  | 0.49 | [6 empty] | 3.60 |  | 3.19 |  |  |  | 2.72 |  |  | 1.92 |  |  | 0.96 | [9 empty] | 0.70 |  |  | 1.27
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 159165.2 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.55 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.45 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.43 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.13 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.33 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.09 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.15 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1996 |  |  |  | 6403.54 |  |  | 7871 |  |  |  | 950 | [10 empty] | 85.50 |  |  |  | 87.53 | [5 empty] | 85.50 |  |  | 87.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.47 |  |  |  |  | 2.02
1997 |  |  |  | 6332.68 |  |  | 6640 |  |  |  | 950 | [10 empty] | 75.18 |  |  |  | 75.50 | [5 empty] | 76.10 |  |  | 75.80 |  |  |  | 0.96 |  | 0.73 | [8 empty] | 23.77 |  |  |  |  | 0.32
1998 |  |  |  | 6132.18 |  |  | 6766 |  |  |  | 950 | [10 empty] | 73.41 |  |  |  | 76.19 | [5 empty] | 73.69 |  |  | 77.24 |  |  |  | 1.09 |  | 0.84 | [8 empty] | 22.97 |  |  |  |  | 2.78
1999 |  |  |  | 6165.39 |  |  | 6934 |  |  |  | 950 | [10 empty] | 74.09 |  |  |  | 78.37 | [5 empty] | 74.09 |  |  | 79.16 |  |  |  | 0.42 |  | 0.33 | [8 empty] | 21.30 |  |  |  |  | 4.28
2000 |  |  |  | 5844.18 |  |  | 6191 |  |  |  | 950 | [10 empty] | 69.29 |  |  |  | 70.13 | [5 empty] | 70.03 |  |  | 70.48 |  |  |  | 1.55 |  | 1.11 | [8 empty] | 28.76 |  |  |  |  | 0.84
2001 |  |  |  | 6336.18 |  |  | 7118 |  |  |  | 950 | [10 empty] | 75.23 |  |  |  | 80.10 | [5 empty] | 75.93 |  |  | 81.03 |  |  |  | 1.51 |  | 1.23 | [8 empty] | 18.68 |  |  |  |  | 4.86
2002 |  |  |  | 6790.62 |  |  | 7393 |  |  |  | 950 | [10 empty] | 80.96 |  |  |  | 83.41 | [5 empty] | 81.60 |  |  | 84.39 |  |  |  | 1.54 |  | 1.31 | [8 empty] | 15.28 |  |  |  |  | 2.46
2003 |  |  |  | 7006.44 |  |  | 7590 |  |  |  | 950 | [10 empty] | 83.47 |  |  |  | 86.29 | [5 empty] | 84.19 |  |  | 86.64 |  |  |  | 0.40 |  | 0.35 | [8 empty] | 13.37 |  |  |  |  | 2.82
2004 |  |  |  | 6867.82 |  |  | 7715 |  |  |  | 950 | [10 empty] | 81.73 |  |  |  | 87.35 | [5 empty] | 82.30 |  |  | 87.83 |  |  |  | 0.43 |  | 0.38 | [8 empty] | 12.27 |  |  |  |  | 5.62
2005 |  |  |  | 5850.74 |  |  | 6557 |  |  |  | 950 | [10 empty] | 83.53 |  |  |  | 84.47 | [5 empty] | 70.30 |  |  | 74.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.53 |  |  |  |  | 0.95
2006 |  |  |  | 6855.00 |  |  | 7317 |  |  |  | 950 | [10 empty] | 83.56 |  |  |  | 84.01 | [5 empty] | 82.37 |  |  | 83.53 |  |  |  | 1.49 |  | 1.27 | [8 empty] | 14.73 |  |  |  |  | 0.45
2007 |  |  |  | 6756.35 |  |  | 7275 |  |  |  | 950 | [10 empty] | 83.33 |  |  |  | 83.35 | [5 empty] | 81.19 |  |  | 83.05 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 16.57 |  |  |  |  | 0.02
2008 |  |  |  | 6355.28 |  |  | 6888 |  |  |  | 950 | [10 empty] | 83.70 |  |  |  | 83.85 | [5 empty] | 76.16 |  |  | 78.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.15 |  |  |  |  | 0.15
2009 |  |  |  | 6964.63 |  |  | 7285 |  |  |  | 950 | [10 empty] | 82.94 |  |  |  | 82.98 | [5 empty] | 83.69 |  |  | 83.16 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 17.01 |  |  |  |  | 0.04
2010 |  |  |  | 6583.55 |  |  | 7181 |  |  |  | 950 | [10 empty] | 80.27 |  |  |  | 81.80 | [5 empty] | 79.11 |  |  | 81.97 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 18.12 |  |  |  |  | 1.53
2011 |  |  |  | 6820.92 |  |  | 7254 |  |  |  | 950 | [10 empty] | 81.91 |  |  |  | 82.14 | [5 empty] | 81.96 |  |  | 82.81 |  |  |  | 0.20 |  | 0.17 | [8 empty] | 17.70 |  |  |  |  | 0.22
2012 |  |  |  | 6911.00 |  |  | 7496 |  |  |  | 950 | [10 empty] | 82.65 |  |  |  | 84.48 | [5 empty] | 82.82 |  |  | 85.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.52 |  |  |  |  | 1.82
2013 |  |  |  | 6356.96 |  |  | 6819 |  |  |  | 950 | [10 empty] | 76.01 |  |  |  | 77.15 | [5 empty] | 76.39 |  |  | 77.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.85 |  |  |  |  | 1.14
2014 |  |  |  | 6704.13 |  |  | 7217 |  |  |  | 950 | [10 empty] | 80.32 |  |  |  | 81.47 | [5 empty] | 80.56 |  |  | 82.39 |  |  |  | 0.38 |  | 0.31 | [8 empty] | 18.22 |  |  |  |  | 1.14
2015 |  |  |  | 6863.82 |  |  | 7601 |  |  |  | 950 | [10 empty] | 79.76 |  |  |  | 85.37 | [5 empty] | 82.48 |  |  | 86.77 |  |  |  | 0.29 |  | 0.24 | [8 empty] | 14.38 |  |  |  |  | 5.61
2016 |  |  |  | 6179.42 |  |  | 7225 |  |  |  | 950 | [10 empty] | 77.58 |  |  |  | 81.27 | [5 empty] | 74.05 |  |  | 82.25 |  |  |  | 0.86 |  | 0.71 | [8 empty] | 18.02 |  |  |  |  | 3.70
2017 |  |  |  | 6473.26 |  |  | 7450 |  |  |  | 950 | [10 empty] | 80.76 |  |  |  | 83.98 | [5 empty] | 77.78 |  |  | 85.05 |  |  |  | 1.60 |  | 1.37 | [8 empty] | 14.65 |  |  |  |  | 3.22
2018 |  |  |  | 6907.39 |  |  | 7188 |  |  |  | 950 | [10 empty] | 79.07 |  |  |  | 81.03 | [5 empty] | 83.00 |  |  | 82.05 |  |  |  | 0.37 |  | 0.30 | [8 empty] | 18.67 |  |  |  |  | 1.95
2019 |  |  |  | 7356.44 |  |  | 8015 |  |  |  | 950 | [10 empty] | 86.83 |  |  |  | 89.70 | [5 empty] | 88.40 |  |  | 91.50 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 10.26 |  |  |  |  | 2.86
2020 |  |  |  | 4998.20 |  |  | 5492 |  |  |  | 950 | [10 empty] | 67.05 |  |  |  | 68.32 | [5 empty] | 59.90 |  |  | 62.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.68 |  |  |  |  | 1.27
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1996 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 30
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2534 | [14 empty] | 1485
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 168 | [14 empty] | 67
E. |  | Testing of plant systems or components | [35 empty] | 19
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 591 | [19 empty] | 81
Subtotal | [22 empty] | 2702 | [10 empty] | 591 |  |  |  | 1571 |  |  |  | 30 | [11 empty] | 81
Total | [22 empty] | 3293 | [14 empty] | 1682
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1996 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 7
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 6
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [37 empty] | 29