## ANO-1
2020 Operating Experience
US-313 | [8 empty] | ANO-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Owner | [7 empty] | : | ENTARK (ENTERGY ARKANSAS, INC.)
Reactor Supplier | [7 empty] | : | B&W (BABCOCK & WILCOX CO.)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / B&W LLP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-10-01
Thermal power | [12 empty] | : |  |  | 2568 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-08-17
Gross electrical power | [12 empty] | : |  |  | 903 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-12-19
Reference unit power (net) | [12 empty] | : |  |  | 836 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.3
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.415
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 35000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.27 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.3
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 60 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7436.38 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.27 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 635.97 | 597.07 |  |  |  | 638.00 |  | 607.73 | [8 empty] | 624.96 |  |  | 597.36 | [6 empty] | 620.37 |  | 622.51 |  |  |  | 607.12 |  |  | 633.57 |  |  | 614.38 | [9 empty] | 637.34 |  |  | 7436.38
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 102.25 | 102.61 |  |  |  | 102.57 |  | 100.96 | [8 empty] | 100.48 |  |  | 99.24 | [6 empty] | 99.74 |  | 100.09 |  |  |  | 100.86 |  |  | 101.86 |  |  | 102.07 | [9 empty] | 102.47 |  |  | 101.27
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 254205.5 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.79 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.03 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.82 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.37 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.92 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | Data not provided
1975 |  |  |  | 4898.40 |  |  | 6661 |  |  |  | 797 | [10 empty] | 67.71 |  |  |  | 67.71 | [5 empty] | 70.16 |  |  | 76.04 |  |  |  | 10.27 |  | 7.75 | [8 empty] | 24.54 |  |  |  |  | 0.00
1976 |  |  |  | 3888.00 |  |  | 4966 |  |  |  | 836 | [10 empty] | 53.00 |  |  |  | 53.00 | [5 empty] | 52.95 |  |  | 56.53 |  |  |  | 25.47 |  | 18.11 | [8 empty] | 28.89 |  |  |  |  | 0.00
1977 |  |  |  | 5103.10 |  |  | 6688 |  |  |  | 836 | [10 empty] | 69.67 |  |  |  | 69.67 | [5 empty] | 69.68 |  |  | 76.35 |  |  |  | 6.76 |  | 5.05 | [8 empty] | 25.28 |  |  |  |  | 0.00
1978 |  |  |  | 5249.80 |  |  | 6676 |  |  |  | 836 | [10 empty] | 71.72 |  |  |  | 71.72 | [5 empty] | 71.69 |  |  | 76.21 |  |  |  | 12.66 |  | 10.40 | [8 empty] | 17.88 |  |  |  |  | 0.00
1979 |  |  |  | 3323.40 |  |  | 4253 |  |  |  | 836 | [10 empty] | 45.38 |  |  |  | 45.38 | [5 empty] | 45.38 |  |  | 48.55 |  |  |  | 38.62 |  | 28.55 | [8 empty] | 26.07 |  |  |  |  | 0.00
1980 |  |  |  | 3781.20 |  |  | 5570 |  |  |  | 836 | [10 empty] | 63.70 |  |  |  | 74.77 | [5 empty] | 51.49 |  |  | 63.41 |  |  |  | 21.95 |  | 21.03 | [8 empty] | 4.20 |  |  |  |  | 11.06
1981 |  |  |  | 4900.80 |  |  | 6336 |  |  |  | 836 | [10 empty] | 72.55 |  |  |  | 72.55 | [5 empty] | 66.92 |  |  | 72.33 |  |  |  | 8.69 |  | 6.90 | [8 empty] | 20.55 |  |  |  |  | 0.00
1982 |  |  |  | 3721.40 |  |  | 5671 |  |  |  | 836 | [10 empty] | 64.79 |  |  |  | 64.79 | [5 empty] | 50.82 |  |  | 64.74 |  |  |  | 12.50 |  | 9.26 | [8 empty] | 25.96 |  |  |  |  | 0.00
1983 |  |  |  | 3220.60 |  |  | 4191 |  |  |  | 836 | [10 empty] | 48.26 |  |  |  | 48.26 | [5 empty] | 43.98 |  |  | 47.84 |  |  |  | 33.32 |  | 24.12 | [8 empty] | 27.63 |  |  |  |  | 0.00
1984 |  |  |  | 4604.13 |  |  | 6150 |  |  |  | 836 | [10 empty] | 70.06 |  |  |  | 70.06 | [5 empty] | 62.70 |  |  | 70.01 |  |  |  | 1.20 |  | 0.85 | [8 empty] | 29.09 |  |  |  |  | 0.00
1985 |  |  |  | 5190.35 |  |  | 6852 |  |  |  | 836 | [10 empty] | 78.25 |  |  |  | 78.25 | [5 empty] | 70.87 |  |  | 78.22 |  |  |  | 16.02 |  | 14.92 | [8 empty] | 6.82 |  |  |  |  | 0.00
1986 |  |  |  | 3589.93 |  |  | 5446 |  |  |  | 836 | [10 empty] | 62.20 |  |  |  | 62.20 | [5 empty] | 49.02 |  |  | 62.17 |  |  |  | 8.05 |  | 5.45 | [8 empty] | 32.35 |  |  |  |  | 0.00
1987 |  |  |  | 4763.34 |  |  | 7720 |  |  |  | 836 | [10 empty] | 88.17 |  |  |  | 88.17 | [5 empty] | 65.04 |  |  | 88.13 |  |  |  | 4.45 |  | 4.11 | [8 empty] | 7.73 |  |  |  |  | 0.00
1988 |  |  |  | 3963.24 |  |  | 5996 |  |  |  | 836 | [10 empty] | 68.28 |  |  |  | 68.28 | [5 empty] | 53.97 |  |  | 68.26 |  |  |  | 3.24 |  | 2.28 | [8 empty] | 29.44 |  |  |  |  | 0.00
1989 |  |  |  | 3377.00 |  |  | 5871 |  |  |  | 836 | [10 empty] | 67.07 |  |  |  | 67.07 | [5 empty] | 46.11 |  |  | 67.02 |  |  |  | 27.55 |  | 25.50 | [8 empty] | 7.43 |  |  |  |  | 0.00
1990 |  |  |  | 4145.80 |  |  | 6437 |  |  |  | 836 | [10 empty] | 75.88 |  |  |  | 75.88 | [5 empty] | 56.61 |  |  | 73.48 |  |  |  | 1.60 |  | 1.23 | [8 empty] | 22.89 |  |  |  |  | 0.00
1991 |  |  |  | 6540.51 |  |  | 7991 |  |  |  | 836 | [10 empty] | 91.27 |  |  |  | 91.27 | [5 empty] | 89.31 |  |  | 91.22 |  |  |  | 3.54 |  | 3.34 | [8 empty] | 5.39 |  |  |  |  | 0.00
1992 |  |  |  | 5833.14 |  |  | 7088 |  |  |  | 836 | [10 empty] | 80.69 |  |  |  | 80.69 | [5 empty] | 79.43 |  |  | 80.69 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 19.25 |  |  |  |  | 0.00
1993 |  |  |  | 6126.55 |  |  | 7520 |  |  |  | 836 | [10 empty] | 85.86 |  |  |  | 85.86 | [5 empty] | 83.66 |  |  | 85.84 |  |  |  | 2.74 |  | 2.42 | [8 empty] | 11.72 |  |  |  |  | 0.00
1994 |  |  |  | 7198.56 |  |  | 8643 |  |  |  | 836 | [10 empty] | 98.69 |  |  |  | 98.69 | [5 empty] | 98.30 |  |  | 98.66 |  |  |  | 1.31 |  | 1.31 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 5978.22 |  |  | 7493 |  |  |  | 836 | [10 empty] | 85.59 |  |  |  | 85.59 | [5 empty] | 81.63 |  |  | 85.54 |  |  |  | 1.83 |  | 1.60 | [8 empty] | 12.81 |  |  |  |  | 0.00
1996 |  |  |  | 6287.02 |  |  | 7613 |  |  |  | 836 | [10 empty] | 86.70 |  |  |  | 86.70 | [5 empty] | 85.61 |  |  | 86.67 |  |  |  | 4.59 |  | 4.17 | [8 empty] | 9.13 |  |  |  |  | 0.00
1997 |  |  |  | 7251.10 |  |  | 8723 |  |  |  | 836 | [10 empty] | 99.59 |  |  |  | 99.59 | [5 empty] | 99.01 |  |  | 99.58 |  |  |  | 0.41 |  | 0.41 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 6216.85 |  |  | 7364 |  |  |  | 836 | [10 empty] | 84.11 |  |  |  | 84.11 | [5 empty] | 84.89 |  |  | 84.06 |  |  |  | 4.45 |  | 3.92 | [8 empty] | 11.98 |  |  |  |  | 0.00
1999 |  |  |  | 6714.72 |  |  | 7907 |  |  |  | 836 | [10 empty] | 90.30 |  |  |  | 90.30 | [5 empty] | 91.69 |  |  | 90.26 |  |  |  | 1.49 |  | 1.36 | [8 empty] | 8.34 |  |  |  |  | 0.00
2000 |  |  |  | 6410.14 |  |  | 7748 |  |  |  | 836 | [10 empty] | 88.22 |  |  |  | 88.22 | [5 empty] | 87.29 |  |  | 88.21 |  |  |  | 8.37 |  | 8.06 | [8 empty] | 3.71 |  |  |  |  | 0.00
2001 |  |  |  | 6875.47 |  |  | 8100 |  |  |  | 836 | [10 empty] | 91.81 |  |  |  | 91.81 | [5 empty] | 93.88 |  |  | 92.47 |  |  |  | 1.39 |  | 1.29 | [8 empty] | 6.90 |  |  |  |  | 0.00
2002 |  |  |  | 6568.63 |  |  | 7820 |  |  |  | 836 | [10 empty] | 89.15 |  |  |  | 89.15 | [5 empty] | 89.69 |  |  | 89.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.85 |  |  |  |  | 0.00
2003 |  |  |  | 6794.30 |  |  | 8050 |  |  |  | 836 | [10 empty] | 91.82 |  |  |  | 91.82 | [5 empty] | 92.78 |  |  | 91.89 |  |  |  | 8.18 |  | 8.18 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 6827.58 |  |  | 8045 |  |  |  | 836 | [10 empty] | 91.57 |  |  |  | 91.57 | [5 empty] | 92.98 |  |  | 91.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.43 |  |  |  |  | 0.00
2005 |  |  |  | 5743.24 |  |  | 6778 |  |  |  | 840 | [10 empty] | 77.38 |  |  |  | 77.38 | [5 empty] | 78.05 |  |  | 77.37 |  |  |  | 1.29 |  | 1.01 | [8 empty] | 21.61 |  |  |  |  | 0.00
2006 |  |  |  | 7474.87 |  |  | 8760 |  |  |  | 836 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.06 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 6882.81 |  |  | 8122 |  |  |  | 843 | [10 empty] | 92.80 |  |  |  | 92.80 | [5 empty] | 93.20 |  |  | 92.72 |  |  |  | 1.54 |  | 1.45 | [8 empty] | 5.75 |  |  |  |  | 0.00
2008 |  |  |  | 6124.05 |  |  | 7558 |  |  |  | 843 | [10 empty] | 86.06 |  |  |  | 86.06 | [5 empty] | 82.70 |  |  | 86.04 |  |  |  | 1.29 |  | 1.12 | [8 empty] | 12.82 |  |  |  |  | 0.00
2009 |  |  |  | 7302.10 |  |  | 8595 |  |  |  | 842 | [10 empty] | 98.12 |  |  |  | 98.12 | [5 empty] | 99.00 |  |  | 98.12 |  |  |  | 1.88 |  | 1.88 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 6607.09 |  |  | 7883 |  |  |  | 842 | [10 empty] | 90.00 |  |  |  | 90.00 | [5 empty] | 89.58 |  |  | 89.99 |  |  |  | 0.31 |  | 0.28 | [8 empty] | 9.71 |  |  |  |  | 0.00
2011 |  |  |  | 6395.49 |  |  | 7872 |  |  |  | 842 | [10 empty] | 89.87 |  |  |  | 89.87 | [5 empty] | 86.71 |  |  | 89.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.13 |  |  |  |  | 0.00
2012 |  |  |  | 7436.06 |  |  | 8784 |  |  |  | 842 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.54 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 4448.74 |  |  | 5415 |  |  |  | 836 | [10 empty] | 61.79 |  |  |  | 61.79 | [5 empty] | 60.74 |  |  | 61.81 |  |  |  | 1.22 |  | 0.76 | [8 empty] | 37.45 |  |  |  |  | 0.00
2014 |  |  |  | 7180.53 |  |  | 8760 |  |  |  | 836 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.05 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6528.76 |  |  | 7832 |  |  |  | 836 | [10 empty] | 89.40 |  |  |  | 89.40 | [5 empty] | 89.15 |  |  | 89.41 |  |  |  | 0.96 |  | 0.87 | [8 empty] | 9.73 |  |  |  |  | 0.00
2016 |  |  |  | 5681.14 |  |  | 6821 |  |  |  | 836 | [10 empty] | 77.65 |  |  |  | 77.65 | [5 empty] | 77.36 |  |  | 77.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.35 |  |  |  |  | 0.00
2017 |  |  |  | 6883.54 |  |  | 8193 |  |  |  | 836 | [10 empty] | 93.53 |  |  |  | 99.44 | [5 empty] | 93.99 |  |  | 93.53 |  |  |  | 0.56 |  | 0.56 | [8 empty] | 0.00 |  |  |  |  | 5.91
2018 |  |  |  | 5647.03 |  |  | 6966 |  |  |  | 836 | [10 empty] | 79.53 |  |  |  | 79.53 | [5 empty] | 77.11 |  |  | 79.52 |  |  |  | 2.67 |  | 2.18 | [8 empty] | 18.29 |  |  |  |  | 0.00
2019 |  |  |  | 6447.65 |  |  | 7644 |  |  |  | 836 | [10 empty] | 87.26 |  |  |  | 87.26 | [5 empty] | 88.04 |  |  | 87.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.74 |  |  |  |  | 0.00
2020 |  |  |  | 7436.38 |  |  | 8783 |  |  |  | 836 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.27 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 467
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 845
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 103
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 2
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 41
H. |  | Nuclear regulatory requirements | [39 empty] | 36
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 5
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 15
P. |  | Fire | [39 empty] | 3
Z. |  | Other | [35 empty] | 45 |  |  |  | 1
Subtotal | [37 empty] | 1037 |  |  |  | 514 | [11 empty] | 16
Total | [22 empty] | 0 | [14 empty] | 1567
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 64
12. |  |  | Reactor I&C Systems | [34 empty] | 28
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 27
15. |  |  | Reactor Cooling Systems | [34 empty] | 37
16. |  |  | Steam generation systems | [34 empty] | 41
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 16
31. |  |  | Turbine and auxiliaries | [34 empty] | 103
32. |  |  | Feedwater and Main Steam System | [34 empty] | 52
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 65
42. |  |  | Electrical Power Supply Systems | [34 empty] | 29
Total | [37 empty] | 484

## ANO-2
2020 Operating Experience
US-368 | [8 empty] | ANO-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Owner | [7 empty] | : | ENTARK (ENTERGY ARKANSAS, INC.)
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-12-06
Thermal power | [12 empty] | : |  |  | 3026 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-12-26
Gross electrical power | [12 empty] | : |  |  | 1065 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-03-26
Reference unit power (net) | [12 empty] | : |  |  | 988 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.38
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 35000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.12 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.08
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7626.67 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.84 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.84 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.64 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.84 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.52 %
Load Factor (LF) | [18 empty] | : | 87.88 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 87.83 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1069 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 749.52 | 701.23 |  |  |  | 304.61 |  | 183.44 | [8 empty] | 737.52 |  |  | 691.88 | [6 empty] | 737.39 |  | 739.84 |  |  |  | 717.60 |  |  | 747.98 |  |  | 648.77 | [9 empty] | 666.89 |  |  | 7626.67
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.94 |  | 31.64 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 90.46 | [9 empty] | 89.84 |  |  | 87.84
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.94 |  | 31.64 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 90.46 | [9 empty] | 89.84 |  |  | 87.84
LF [%] |  |  |  |  | 101.97 | 101.98 |  |  |  | 41.44 |  | 25.79 | [8 empty] | 100.33 |  |  | 97.26 | [6 empty] | 100.32 |  | 100.65 |  |  |  | 100.88 |  |  | 101.76 |  |  | 91.20 | [9 empty] | 90.72 |  |  | 87.88
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.80 |  | 31.67 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 90.56 | [9 empty] | 89.78 |  |  | 87.83
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 9.54 | [9 empty] | 10.16 |  |  | 1.84
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 9.54 | [9 empty] | 10.16 |  |  | 1.64
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 58.06 |  | 68.36 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.52
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 308139.2 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.5 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.15 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.19 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.28 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.53 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.1 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.13 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 3646.60 |  |  | 4913 |  |  |  | 884 | [10 empty] | 73.39 |  |  |  | 80.25 | [5 empty] | 60.50 |  |  | 72.74 |  |  |  | 19.75 |  | 19.75 | [8 empty] | 0.00 |  |  |  |  | 6.85
1981 |  |  |  | 4323.60 |  |  | 5622 |  |  |  | 858 | [10 empty] | 65.23 |  |  |  | 65.23 | [5 empty] | 57.52 |  |  | 64.18 |  |  |  | 10.27 |  | 7.47 | [8 empty] | 27.31 |  |  |  |  | 0.00
1982 |  |  |  | 3807.50 |  |  | 5023 |  |  |  | 858 | [10 empty] | 57.88 |  |  |  | 57.88 | [5 empty] | 50.66 |  |  | 57.34 |  |  |  | 22.77 |  | 17.07 | [8 empty] | 25.05 |  |  |  |  | 0.00
1983 |  |  |  | 4427.90 |  |  | 5380 |  |  |  | 858 | [10 empty] | 61.45 |  |  |  | 61.45 | [5 empty] | 58.91 |  |  | 61.42 |  |  |  | 19.19 |  | 14.60 | [8 empty] | 23.95 |  |  |  |  | 0.00
1984 |  |  |  | 6203.57 |  |  | 7439 |  |  |  | 858 | [10 empty] | 84.74 |  |  |  | 84.74 | [5 empty] | 82.31 |  |  | 84.69 |  |  |  | 7.34 |  | 6.71 | [8 empty] | 8.55 |  |  |  |  | 0.00
1985 |  |  |  | 4701.15 |  |  | 6040 |  |  |  | 858 | [10 empty] | 68.99 |  |  |  | 69.16 | [5 empty] | 62.55 |  |  | 68.95 |  |  |  | 13.85 |  | 11.12 | [8 empty] | 19.73 |  |  |  |  | 0.17
1986 |  |  |  | 5314.34 |  |  | 6274 |  |  |  | 858 | [10 empty] | 71.65 |  |  |  | 71.65 | [5 empty] | 70.71 |  |  | 71.62 |  |  |  | 4.57 |  | 3.43 | [8 empty] | 24.92 |  |  |  |  | 0.00
1987 |  |  |  | 6605.17 |  |  | 7678 |  |  |  | 858 | [10 empty] | 87.69 |  |  |  | 87.69 | [5 empty] | 87.88 |  |  | 87.65 |  |  |  | 12.31 |  | 12.31 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 4952.90 |  |  | 5867 |  |  |  | 858 | [10 empty] | 66.82 |  |  |  | 66.82 | [5 empty] | 65.72 |  |  | 66.79 |  |  |  | 8.13 |  | 5.91 | [8 empty] | 27.27 |  |  |  |  | 0.00
1989 |  |  |  | 5472.22 |  |  | 6514 |  |  |  | 858 | [10 empty] | 74.42 |  |  |  | 74.42 | [5 empty] | 72.81 |  |  | 74.36 |  |  |  | 11.75 |  | 9.91 | [8 empty] | 15.67 |  |  |  |  | 0.00
1990 |  |  |  | 7129.57 |  |  | 8211 |  |  |  | 858 | [10 empty] | 93.76 |  |  |  | 93.76 | [5 empty] | 94.86 |  |  | 93.73 |  |  |  | 3.76 |  | 3.66 | [8 empty] | 2.58 |  |  |  |  | 0.00
1991 |  |  |  | 6123.35 |  |  | 7187 |  |  |  | 858 | [10 empty] | 82.05 |  |  |  | 82.05 | [5 empty] | 81.47 |  |  | 82.04 |  |  |  | 2.60 |  | 2.19 | [8 empty] | 15.75 |  |  |  |  | 0.00
1992 |  |  |  | 5504.76 |  |  | 6390 |  |  |  | 858 | [10 empty] | 72.76 |  |  |  | 72.76 | [5 empty] | 73.04 |  |  | 72.75 |  |  |  | 16.96 |  | 14.86 | [8 empty] | 12.39 |  |  |  |  | 0.00
1993 |  |  |  | 7344.72 |  |  | 8346 |  |  |  | 858 | [10 empty] | 95.27 |  |  |  | 95.27 | [5 empty] | 97.72 |  |  | 95.27 |  |  |  | 0.44 |  | 0.42 | [8 empty] | 4.30 |  |  |  |  | 0.00
1994 |  |  |  | 6724.88 |  |  | 7707 |  |  |  | 858 | [10 empty] | 88.00 |  |  |  | 88.00 | [5 empty] | 89.47 |  |  | 87.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.00 |  |  |  |  | 0.00
1995 |  |  |  | 5694.52 |  |  | 6644 |  |  |  | 858 | [10 empty] | 75.92 |  |  |  | 75.92 | [5 empty] | 75.76 |  |  | 75.84 |  |  |  | 6.02 |  | 4.86 | [8 empty] | 19.21 |  |  |  |  | 0.00
1996 |  |  |  | 7063.90 |  |  | 8049 |  |  |  | 858 | [10 empty] | 91.64 |  |  |  | 91.64 | [5 empty] | 93.73 |  |  | 91.63 |  |  |  | 8.36 |  | 8.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 6957.03 |  |  | 8013 |  |  |  | 858 | [10 empty] | 91.50 |  |  |  | 91.50 | [5 empty] | 92.56 |  |  | 91.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.50 |  |  |  |  | 0.00
1998 |  |  |  | 6877.28 |  |  | 7995 |  |  |  | 858 | [10 empty] | 91.28 |  |  |  | 91.28 | [5 empty] | 91.50 |  |  | 91.27 |  |  |  | 2.01 |  | 1.87 | [8 empty] | 6.84 |  |  |  |  | 0.00
1999 |  |  |  | 6226.87 |  |  | 7219 |  |  |  | 858 | [10 empty] | 82.43 |  |  |  | 82.43 | [5 empty] | 82.85 |  |  | 82.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.57 |  |  |  |  | 0.00
2000 |  |  |  | 5265.35 |  |  | 6077 |  |  |  | 858 | [10 empty] | 69.20 |  |  |  | 69.20 | [5 empty] | 69.86 |  |  | 69.18 |  |  |  | 3.82 |  | 2.75 | [8 empty] | 28.05 |  |  |  |  | 0.00
2001 |  |  |  | 7917.02 |  |  | 8498 |  |  |  | 858 | [10 empty] | 96.84 |  |  |  | 96.84 | [5 empty] | 105.33 |  |  | 97.01 |  |  |  | 3.16 |  | 3.16 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 8002.15 |  |  | 8203 |  |  |  | 858 | [10 empty] | 93.10 |  |  |  | 93.10 | [5 empty] | 106.47 |  |  | 93.64 |  |  |  | 0.42 |  | 0.39 | [8 empty] | 6.51 |  |  |  |  | 0.00
2003 |  |  |  | 7925.72 |  |  | 8156 |  |  |  | 858 | [10 empty] | 92.55 |  |  |  | 92.55 | [5 empty] | 105.45 |  |  | 93.11 |  |  |  | 1.44 |  | 1.35 | [8 empty] | 6.10 |  |  |  |  | 0.00
2004 |  |  |  | 8627.56 |  |  | 8580 |  |  |  | 1000 | [10 empty] | 97.71 |  |  |  | 97.71 | [5 empty] | 98.22 |  |  | 97.68 |  |  |  | 1.41 |  | 1.40 | [8 empty] | 0.89 |  |  |  |  | 0.00
2005 |  |  |  | 7959.45 |  |  | 7966 |  |  |  | 1000 | [10 empty] | 90.95 |  |  |  | 90.95 | [5 empty] | 90.85 |  |  | 90.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.05 |  |  |  |  | 0.00
2006 |  |  |  | 7765.40 |  |  | 7793 |  |  |  | 998 | [10 empty] | 88.99 |  |  |  | 88.99 | [5 empty] | 88.82 |  |  | 88.96 |  |  |  | 0.43 |  | 0.38 | [8 empty] | 10.63 |  |  |  |  | 0.00
2007 |  |  |  | 8603.30 |  |  | 8584 |  |  |  | 995 | [10 empty] | 98.02 |  |  |  | 98.02 | [5 empty] | 98.70 |  |  | 97.99 |  |  |  | 1.98 |  | 1.98 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8060.45 |  |  | 8166 |  |  |  | 995 | [10 empty] | 92.98 |  |  |  | 92.98 | [5 empty] | 92.22 |  |  | 92.96 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 7.01 |  |  |  |  | 0.00
2009 |  |  |  | 7867.87 |  |  | 7986 |  |  |  | 997 | [10 empty] | 91.21 |  |  |  | 91.21 | [5 empty] | 90.09 |  |  | 91.16 |  |  |  | 1.85 |  | 1.72 | [8 empty] | 7.06 |  |  |  |  | 0.00
2010 |  |  |  | 8415.59 |  |  | 8472 |  |  |  | 993 | [10 empty] | 96.72 |  |  |  | 96.72 | [5 empty] | 96.75 |  |  | 96.71 |  |  |  | 3.28 |  | 3.28 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 7812.57 |  |  | 7944 |  |  |  | 993 | [10 empty] | 90.70 |  |  |  | 90.70 | [5 empty] | 89.81 |  |  | 90.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.30 |  |  |  |  | 0.00
2012 |  |  |  | 8063.57 |  |  | 8090 |  |  |  | 993 | [10 empty] | 92.13 |  |  |  | 92.13 | [5 empty] | 92.45 |  |  | 92.10 |  |  |  | 0.48 |  | 0.45 | [8 empty] | 7.43 |  |  |  |  | 0.00
2013 |  |  |  | 7522.80 |  |  | 7537 |  |  |  | 992 | [10 empty] | 86.02 |  |  |  | 86.02 | [5 empty] | 86.56 |  |  | 86.03 |  |  |  | 13.98 |  | 13.98 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 7313.90 |  |  | 7382 |  |  |  | 993 | [10 empty] | 88.39 |  |  |  | 88.39 | [5 empty] | 84.08 |  |  | 84.27 |  |  |  | 2.94 |  | 2.68 | [8 empty] | 8.93 |  |  |  |  | 0.00
2015 |  |  |  | 7329.68 |  |  | 7441 |  |  |  | 993 | [10 empty] | 84.94 |  |  |  | 84.94 | [5 empty] | 84.26 |  |  | 84.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.06 |  |  |  |  | 0.00
2016 |  |  |  | 7771.44 |  |  | 7854 |  |  |  | 993 | [10 empty] | 89.41 |  |  |  | 89.41 | [5 empty] | 89.10 |  |  | 89.41 |  |  |  | 2.82 |  | 2.59 | [8 empty] | 8.00 |  |  |  |  | 0.00
2017 |  |  |  | 5831.07 |  |  | 6325 |  |  |  | 993 | [10 empty] | 66.37 |  |  |  | 66.37 | [5 empty] | 67.03 |  |  | 72.20 |  |  |  | 7.51 |  | 16.19 | [8 empty] | 17.45 |  |  |  |  | 0.00
2018 |  |  |  | 7114.93 |  |  | 7196 |  |  |  | 988 | [10 empty] | 82.14 |  |  |  | 82.14 | [5 empty] | 82.21 |  |  | 82.15 |  |  |  | 3.98 |  | 3.41 | [8 empty] | 14.45 |  |  |  |  | 0.00
2019 |  |  |  | 7163.64 |  |  | 7216 |  |  |  | 988 | [10 empty] | 82.39 |  |  |  | 82.39 | [5 empty] | 82.77 |  |  | 82.37 |  |  |  | 17.61 |  | 17.61 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7626.67 |  |  | 7715 |  |  |  | 988 | [10 empty] | 87.84 |  |  |  | 87.84 | [5 empty] | 87.88 |  |  | 87.83 |  |  |  | 1.84 |  | 1.64 | [8 empty] | 10.52 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1980 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 470
B. |  | Refuelling without maintenance | [20 empty] | 924 | [14 empty] | 23
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 830
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 99
E. |  | Testing of plant systems or components | [35 empty] | 10 |  |  |  | 18
H. |  | Nuclear regulatory requirements | [35 empty] | 17 |  |  |  | 24
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 20
L. |  | Human factor related | [39 empty] | 10
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
P. |  | Fire | [39 empty] | 19
Z. |  | Other | [24 empty] | 144 | [14 empty] | 4
Subtotal | [22 empty] | 924 |  |  |  | 144 | [10 empty] | 979 |  |  |  | 545 | [11 empty] | 20
Total | [22 empty] | 1068 | [14 empty] | 1544
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1980 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 52
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 15
14. |  |  | Safety Systems | [34 empty] | 72
15. |  |  | Reactor Cooling Systems | [34 empty] | 147
16. |  |  | Steam generation systems | [34 empty] | 58
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 36
32. |  |  | Feedwater and Main Steam System | [34 empty] | 43
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 27
41. |  |  | Main Generator Systems | [34 empty] | 8
42. |  |  | Electrical Power Supply Systems | [34 empty] | 49
Total | [37 empty] | 515
Highlights (2020)
2 hour shutdown using OP-2203.053 Rapid Power Reduction due to 2E-2B FW heater leak.

## BEAVER VALLEY-1
2020 Operating Experience
US-334 | [8 empty] | BEAVER VALLEY-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FENOC (FIRST ENERGY NUCLEAR OPERATING CO.)
Owner | [7 empty] | : | PPL_SUSQ (PPL Susquehanna, LLC)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYSUB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-06-26
Thermal power | [12 empty] | : |  |  | 2900 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-06-14
Gross electrical power | [12 empty] | : |  |  | 959 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-10-01
Reference unit power (net) | [12 empty] | : |  |  | 908 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.82
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.38
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43727 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.05 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.3
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.06 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8047.73 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 100.9 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 701.64 | 656.67 |  |  |  | 693.62 |  | 671.45 | [8 empty] | 676.65 |  |  | 656.58 | [6 empty] | 579.62 |  | 685.71 |  |  |  | 659.84 |  |  | 690.73 |  |  | 674.79 | [9 empty] | 700.43 |  |  | 8047.73
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 103.86 | 103.91 |  |  |  | 102.67 |  | 102.71 | [8 empty] | 100.16 |  |  | 100.43 | [6 empty] | 85.80 |  | 101.50 |  |  |  | 100.93 |  |  | 102.25 |  |  | 103.22 | [9 empty] | 103.68 |  |  | 100.90
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 251573.78 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.75 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.52 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.49 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.52 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.99 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.13 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.25 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | 504.50 |  |  | 821 |  |  |  | 834 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 16.12 |  |  | 37.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1977 |  |  |  | 2870.30 |  |  | 4312 |  |  |  | 843 | [10 empty] | 39.24 |  |  |  | 39.24 | [5 empty] | 38.87 |  |  | 49.22 |  |  |  | 49.37 |  | 38.27 | [8 empty] | 22.49 |  |  |  |  | 0.00
1978 |  |  |  | 2481.40 |  |  | 3569 |  |  |  | 800 | [10 empty] | 35.43 |  |  |  | 35.43 | [5 empty] | 35.41 |  |  | 40.74 |  |  |  | 56.65 |  | 46.30 | [8 empty] | 18.27 |  |  |  |  | 0.00
1979 |  |  |  | 1778.40 |  |  | 3498 |  |  |  | 815 | [10 empty] | 24.85 |  |  |  | 24.85 | [5 empty] | 24.91 |  |  | 39.93 |  |  |  | 72.84 |  | 66.64 | [8 empty] | 8.51 |  |  |  |  | 0.00
1980 |  |  |  | 300.70 |  |  | 600 |  |  |  | 811 | [10 empty] | 6.92 |  |  |  | 6.92 | [5 empty] | 4.22 |  |  | 6.83 |  |  |  | 38.56 |  | 4.34 | [8 empty] | 88.74 |  |  |  |  | 0.00
1981 |  |  |  | 4674.70 |  |  | 6444 |  |  |  | 810 | [10 empty] | 73.88 |  |  |  | 73.88 | [5 empty] | 65.88 |  |  | 73.56 |  |  |  | 26.11 |  | 26.11 | [8 empty] | 0.01 |  |  |  |  | 0.00
1982 |  |  |  | 2717.40 |  |  | 3644 |  |  |  | 810 | [10 empty] | 41.73 |  |  |  | 41.73 | [5 empty] | 38.30 |  |  | 41.60 |  |  |  | 5.02 |  | 2.21 | [8 empty] | 56.06 |  |  |  |  | 0.00
1983 |  |  |  | 4682.20 |  |  | 5976 |  |  |  | 810 | [10 empty] | 68.55 |  |  |  | 68.55 | [5 empty] | 65.99 |  |  | 68.22 |  |  |  | 3.54 |  | 2.51 | [8 empty] | 28.94 |  |  |  |  | 0.00
1984 |  |  |  | 4756.84 |  |  | 6301 |  |  |  | 810 | [10 empty] | 71.77 |  |  |  | 71.77 | [5 empty] | 66.86 |  |  | 71.73 |  |  |  | 3.00 |  | 2.22 | [8 empty] | 26.01 |  |  |  |  | 0.00
1985 |  |  |  | 5901.46 |  |  | 8046 |  |  |  | 810 | [10 empty] | 91.92 |  |  |  | 91.92 | [5 empty] | 83.17 |  |  | 91.85 |  |  |  | 7.12 |  | 7.05 | [8 empty] | 1.03 |  |  |  |  | 0.00
1986 |  |  |  | 4784.15 |  |  | 6195 |  |  |  | 810 | [10 empty] | 70.74 |  |  |  | 70.74 | [5 empty] | 67.42 |  |  | 70.72 |  |  |  | 4.47 |  | 3.31 | [8 empty] | 25.95 |  |  |  |  | 0.00
1987 |  |  |  | 5620.94 |  |  | 7320 |  |  |  | 810 | [10 empty] | 84.03 |  |  |  | 84.03 | [5 empty] | 79.22 |  |  | 83.56 |  |  |  | 2.95 |  | 2.55 | [8 empty] | 13.42 |  |  |  |  | 0.00
1988 |  |  |  | 4993.62 |  |  | 6989 |  |  |  | 810 | [10 empty] | 79.59 |  |  |  | 79.59 | [5 empty] | 70.18 |  |  | 79.57 |  |  |  | 4.41 |  | 3.67 | [8 empty] | 16.73 |  |  |  |  | 0.00
1989 |  |  |  | 3794.29 |  |  | 5822 |  |  |  | 810 | [10 empty] | 66.49 |  |  |  | 66.49 | [5 empty] | 53.47 |  |  | 66.46 |  |  |  | 9.22 |  | 6.75 | [8 empty] | 26.76 |  |  |  |  | 0.00
1990 |  |  |  | 6167.05 |  |  | 8074 |  |  |  | 810 | [10 empty] | 92.20 |  |  |  | 92.20 | [5 empty] | 86.91 |  |  | 92.17 |  |  |  | 4.10 |  | 3.94 | [8 empty] | 3.86 |  |  |  |  | 0.00
1991 |  |  |  | 3710.88 |  |  | 4883 |  |  |  | 810 | [10 empty] | 55.76 |  |  |  | 55.76 | [5 empty] | 52.30 |  |  | 55.74 |  |  |  | 22.93 |  | 16.59 | [8 empty] | 27.65 |  |  |  |  | 0.00
1992 |  |  |  | 6298.39 |  |  | 8218 |  |  |  | 810 | [10 empty] | 93.58 |  |  |  | 93.58 | [5 empty] | 88.52 |  |  | 93.56 |  |  |  | 6.42 |  | 6.42 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 4359.75 |  |  | 5891 |  |  |  | 810 | [10 empty] | 67.26 |  |  |  | 67.26 | [5 empty] | 61.44 |  |  | 67.25 |  |  |  | 13.44 |  | 10.45 | [8 empty] | 22.29 |  |  |  |  | 0.00
1994 |  |  |  | 5504.38 |  |  | 6991 |  |  |  | 810 | [10 empty] | 79.87 |  |  |  | 79.87 | [5 empty] | 77.57 |  |  | 79.81 |  |  |  | 20.13 |  | 20.13 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 5449.22 |  |  | 6813 |  |  |  | 810 | [10 empty] | 77.83 |  |  |  | 77.83 | [5 empty] | 76.80 |  |  | 77.77 |  |  |  | 5.69 |  | 4.69 | [8 empty] | 17.48 |  |  |  |  | 0.00
1996 |  |  |  | 5698.05 |  |  | 7132 |  |  |  | 810 | [10 empty] | 81.25 |  |  |  | 81.25 | [5 empty] | 80.08 |  |  | 81.19 |  |  |  | 5.94 |  | 5.13 | [8 empty] | 13.62 |  |  |  |  | 0.00
1997 |  |  |  | 4025.78 |  |  | 4972 |  |  |  | 810 | [10 empty] | 56.77 |  |  |  | 56.77 | [5 empty] | 56.74 |  |  | 56.76 |  |  |  | 32.90 |  | 27.83 | [8 empty] | 15.40 |  |  |  |  | 0.00
1998 |  |  |  | 2829.29 |  |  | 3557 |  |  |  | 810 | [10 empty] | 40.43 |  |  |  | 40.43 | [5 empty] | 39.87 |  |  | 40.61 |  |  |  | 59.09 |  | 58.39 | [8 empty] | 1.18 |  |  |  |  | 0.00
1999 |  |  |  | 6106.21 |  |  | 7746 |  |  |  | 810 | [10 empty] | 88.47 |  |  |  | 88.47 | [5 empty] | 86.06 |  |  | 88.42 |  |  |  | 7.39 |  | 7.06 | [8 empty] | 4.47 |  |  |  |  | 0.00
2000 |  |  |  | 5883.02 |  |  | 7430 |  |  |  | 810 | [10 empty] | 84.60 |  |  |  | 84.60 | [5 empty] | 82.68 |  |  | 84.59 |  |  |  | 1.64 |  | 1.41 | [8 empty] | 14.00 |  |  |  |  | 0.00
2001 |  |  |  | 5991.02 |  |  | 7407 |  |  |  | 821 | [10 empty] | 84.64 |  |  |  | 84.64 | [5 empty] | 84.14 |  |  | 84.55 |  |  |  | 2.80 |  | 2.44 | [8 empty] | 12.92 |  |  |  |  | 0.00
2002 |  |  |  | 6989.86 |  |  | 8490 |  |  |  | 821 | [10 empty] | 96.96 |  |  |  | 96.96 | [5 empty] | 97.19 |  |  | 96.92 |  |  |  | 0.62 |  | 0.61 | [8 empty] | 2.43 |  |  |  |  | 0.00
2003 |  |  |  | 5985.36 |  |  | 7359 |  |  |  | 821 | [10 empty] | 84.13 |  |  |  | 84.13 | [5 empty] | 83.22 |  |  | 84.01 |  |  |  | 1.14 |  | 0.97 | [8 empty] | 14.90 |  |  |  |  | 0.00
2004 |  |  |  | 6678.55 |  |  | 8119 |  |  |  | 821 | [10 empty] | 92.44 |  |  |  | 92.44 | [5 empty] | 92.61 |  |  | 92.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.56 |  |  |  |  | 0.00
2005 |  |  |  | 7290.28 |  |  | 8760 |  |  |  | 821 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.37 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 5828.55 |  |  | 6973 |  |  |  | 851 | [10 empty] | 79.63 |  |  |  | 79.63 | [5 empty] | 78.18 |  |  | 79.59 |  |  |  | 0.96 |  | 0.78 | [8 empty] | 19.59 |  |  |  |  | 0.00
2007 |  |  |  | 7057.66 |  |  | 8017 |  |  |  | 892 | [10 empty] | 91.62 |  |  |  | 91.62 | [5 empty] | 90.32 |  |  | 91.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.38 |  |  |  |  | 0.00
2008 |  |  |  | 7945.03 |  |  | 8784 |  |  |  | 892 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.40 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 7217.48 |  |  | 7999 |  |  |  | 892 | [10 empty] | 91.32 |  |  |  | 91.32 | [5 empty] | 92.37 |  |  | 91.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.68 |  |  |  |  | 0.00
2010 |  |  |  | 7119.41 |  |  | 7963 |  |  |  | 892 | [10 empty] | 90.91 |  |  |  | 90.91 | [5 empty] | 91.11 |  |  | 90.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.09 |  |  |  |  | 0.00
2011 |  |  |  | 7854.57 |  |  | 8702 |  |  |  | 892 | [10 empty] | 99.34 |  |  |  | 99.34 | [5 empty] | 100.52 |  |  | 99.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.66 |  |  |  |  | 0.00
2012 |  |  |  | 7220.58 |  |  | 8010 |  |  |  | 892 | [10 empty] | 91.20 |  |  |  | 91.20 | [5 empty] | 92.15 |  |  | 91.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.80 |  |  |  |  | 0.00
2013 |  |  |  | 6963.06 |  |  | 7825 |  |  |  | 921 | [10 empty] | 89.35 |  |  |  | 89.35 | [5 empty] | 88.86 |  |  | 89.32 |  |  |  | 0.91 |  | 0.82 | [8 empty] | 9.83 |  |  |  |  | 0.00
2014 |  |  |  | 7477.39 |  |  | 8116 |  |  |  | 921 | [10 empty] | 92.65 |  |  |  | 92.65 | [5 empty] | 92.68 |  |  | 92.65 |  |  |  | 6.56 |  | 6.51 | [8 empty] | 0.84 |  |  |  |  | 0.00
2015 |  |  |  | 7282.19 |  |  | 7971 |  |  |  | 921 | [10 empty] | 91.00 |  |  |  | 91.00 | [5 empty] | 90.26 |  |  | 90.99 |  |  |  | 0.47 |  | 0.43 | [8 empty] | 8.57 |  |  |  |  | 0.00
2016 |  |  |  | 7351.14 |  |  | 8031 |  |  |  | 921 | [10 empty] | 91.43 |  |  |  | 91.43 | [5 empty] | 90.87 |  |  | 91.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.57 |  |  |  |  | 0.00
2017 |  |  |  | 7999.17 |  |  | 8624 |  |  |  | 921 | [10 empty] | 98.44 |  |  |  | 98.44 | [5 empty] | 99.15 |  |  | 98.45 |  |  |  | 1.56 |  | 1.56 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 7430.72 |  |  | 8156 |  |  |  | 908 | [10 empty] | 93.11 |  |  |  | 93.11 | [5 empty] | 93.42 |  |  | 93.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.89 |  |  |  |  | 0.00
2019 |  |  |  | 7416.90 |  |  | 8193 |  |  |  | 908 | [10 empty] | 93.53 |  |  |  | 93.53 | [5 empty] | 93.25 |  |  | 93.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.47 |  |  |  |  | 0.00
2020 |  |  |  | 8047.73 |  |  | 8783 |  |  |  | 908 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.90 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1976 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 519
B. |  | Refuelling without maintenance | [35 empty] | 14
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 993 |  |  |  | 4
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 85
E. |  | Testing of plant systems or components | [35 empty] | 7 |  |  |  | 15
H. |  | Nuclear regulatory requirements | [39 empty] | 88
L. |  | Human factor related | [39 empty] | 11
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Z. |  | Other | [35 empty] | 16 |  |  |  | 140
Subtotal | [37 empty] | 1115 |  |  |  | 777 | [11 empty] | 2
Total | [22 empty] | 0 | [14 empty] | 1894
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1976 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 37
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 25
14. |  |  | Safety Systems | [34 empty] | 31
15. |  |  | Reactor Cooling Systems | [34 empty] | 280
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 18
32. |  |  | Feedwater and Main Steam System | [34 empty] | 111
34. |  |  | Miscellaneous Systems | [34 empty] | 43
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 16
42. |  |  | Electrical Power Supply Systems | [34 empty] | 128
Total | [37 empty] | 703

## BEAVER VALLEY-2
2020 Operating Experience
US-412 | [8 empty] | BEAVER VALLEY-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FENOC (FIRST ENERGY NUCLEAR OPERATING CO.)
Owner | [7 empty] | : | OHIO ED (OHIO EDISON CO.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYSUB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-05-03
Thermal power | [12 empty] | : |  |  | 2900 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-08-17
Gross electrical power | [12 empty] | : |  |  | 958 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-11-17
Reference unit power (net) | [12 empty] | : |  |  | 905 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.38
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 36351 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.05 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.3
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.06 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7345.66 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.25 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.25 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.75 %
Load Factor (LF) | [18 empty] | : | 92.4 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.24 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 594 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 690.10 | 646.00 |  |  |  | 646.64 |  | 186.53 | [8 empty] | 529.80 |  |  | 653.54 | [6 empty] | 628.97 |  | 677.89 |  |  |  | 653.84 |  |  | 681.58 |  |  | 663.72 | [9 empty] | 687.05 |  |  | 7345.66
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 36.67 | [8 empty] | 81.65 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.25
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 36.67 | [8 empty] | 81.65 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.25
LF [%] |  |  |  |  | 102.49 | 102.56 |  |  |  | 96.04 |  | 28.63 | [8 empty] | 78.69 |  |  | 100.30 | [6 empty] | 93.41 |  | 100.68 |  |  |  | 100.34 |  |  | 101.23 |  |  | 101.86 | [9 empty] | 102.04 |  |  | 92.40
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 36.67 | [8 empty] | 81.59 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.24
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 63.33 | [8 empty] | 18.35 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.75
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 162091.55 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.39 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.77 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.07 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.77 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.16 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.81 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.23 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 738.10 |  |  | 950 |  |  |  | 822 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 93.42 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 6477.06 |  |  | 8224 |  |  |  | 833 | [10 empty] | 93.78 |  |  |  | 93.78 | [5 empty] | 88.52 |  |  | 93.62 |  |  |  | 2.42 |  | 2.33 | [8 empty] | 3.89 |  |  |  |  | 0.00
1989 |  |  |  | 4557.14 |  |  | 6245 |  |  |  | 833 | [10 empty] | 71.68 |  |  |  | 71.68 | [5 empty] | 62.45 |  |  | 71.29 |  |  |  | 11.01 |  | 8.87 | [8 empty] | 19.45 |  |  |  |  | 0.00
1990 |  |  |  | 4291.55 |  |  | 6734 |  |  |  | 827 | [10 empty] | 77.09 |  |  |  | 77.09 | [5 empty] | 59.20 |  |  | 76.87 |  |  |  | 1.66 |  | 1.30 | [8 empty] | 21.60 |  |  |  |  | 0.00
1991 |  |  |  | 6762.16 |  |  | 8720 |  |  |  | 820 | [10 empty] | 99.54 |  |  |  | 99.54 | [5 empty] | 94.14 |  |  | 99.54 |  |  |  | 0.46 |  | 0.46 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 5647.13 |  |  | 7342 |  |  |  | 820 | [10 empty] | 94.83 |  |  |  | 94.83 | [5 empty] | 78.40 |  |  | 83.58 |  |  |  | 0.18 |  | 0.17 | [8 empty] | 5.00 |  |  |  |  | 0.00
1993 |  |  |  | 5212.68 |  |  | 6770 |  |  |  | 820 | [10 empty] | 77.29 |  |  |  | 77.29 | [5 empty] | 72.57 |  |  | 77.28 |  |  |  | 1.57 |  | 1.23 | [8 empty] | 21.47 |  |  |  |  | 0.00
1994 |  |  |  | 7024.73 |  |  | 8481 |  |  |  | 820 | [10 empty] | 96.83 |  |  |  | 96.83 | [5 empty] | 97.79 |  |  | 96.82 |  |  |  | 3.17 |  | 3.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 6047.02 |  |  | 7616 |  |  |  | 820 | [10 empty] | 86.97 |  |  |  | 86.97 | [5 empty] | 84.18 |  |  | 86.94 |  |  |  | 0.50 |  | 0.43 | [8 empty] | 12.59 |  |  |  |  | 0.00
1996 |  |  |  | 4788.59 |  |  | 6169 |  |  |  | 820 | [10 empty] | 70.30 |  |  |  | 70.30 | [5 empty] | 66.48 |  |  | 70.23 |  |  |  | 18.40 |  | 15.85 | [8 empty] | 13.85 |  |  |  |  | 0.00
1997 |  |  |  | 6158.70 |  |  | 7583 |  |  |  | 820 | [10 empty] | 86.62 |  |  |  | 86.62 | [5 empty] | 85.74 |  |  | 86.56 |  |  |  | 13.38 |  | 13.38 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 1808.72 |  |  | 2179 |  |  |  | 820 | [10 empty] | 25.12 |  |  |  | 25.12 | [5 empty] | 25.18 |  |  | 24.87 |  |  |  | 74.87 |  | 74.86 | [8 empty] | 0.02 |  |  |  |  | 0.00
1999 |  |  |  | 5752.52 |  |  | 7155 |  |  |  | 820 | [10 empty] | 81.70 |  |  |  | 81.70 | [5 empty] | 80.08 |  |  | 81.68 |  |  |  | 8.23 |  | 7.33 | [8 empty] | 10.97 |  |  |  |  | 0.00
2000 |  |  |  | 6227.85 |  |  | 7804 |  |  |  | 820 | [10 empty] | 88.86 |  |  |  | 88.86 | [5 empty] | 86.46 |  |  | 88.84 |  |  |  | 2.45 |  | 2.23 | [8 empty] | 8.91 |  |  |  |  | 0.00
2001 |  |  |  | 7191.65 |  |  | 8702 |  |  |  | 831 | [10 empty] | 99.35 |  |  |  | 99.35 | [5 empty] | 99.78 |  |  | 99.34 |  |  |  | 0.65 |  | 0.65 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 6604.31 |  |  | 8133 |  |  |  | 831 | [10 empty] | 92.95 |  |  |  | 92.95 | [5 empty] | 90.72 |  |  | 92.84 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 6.85 |  |  |  |  | 0.00
2003 |  |  |  | 6636.99 |  |  | 8037 |  |  |  | 831 | [10 empty] | 91.76 |  |  |  | 91.76 | [5 empty] | 91.17 |  |  | 91.75 |  |  |  | 0.34 |  | 0.32 | [8 empty] | 7.92 |  |  |  |  | 0.00
2004 |  |  |  | 7314.83 |  |  | 8784 |  |  |  | 831 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.21 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 6680.03 |  |  | 8169 |  |  |  | 831 | [10 empty] | 93.26 |  |  |  | 93.26 | [5 empty] | 91.76 |  |  | 93.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.74 |  |  |  |  | 0.00
2006 |  |  |  | 6309.51 |  |  | 7673 |  |  |  | 851 | [10 empty] | 87.61 |  |  |  | 87.61 | [5 empty] | 84.64 |  |  | 87.59 |  |  |  | 1.10 |  | 0.98 | [8 empty] | 11.42 |  |  |  |  | 0.00
2007 |  |  |  | 7473.20 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.84 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 6726.20 |  |  | 7744 |  |  |  | 890 | [10 empty] | 87.93 |  |  |  | 87.93 | [5 empty] | 87.84 |  |  | 88.16 |  |  |  | 1.34 |  | 1.20 | [8 empty] | 10.88 |  |  |  |  | 0.00
2009 |  |  |  | 6193.96 |  |  | 7651 |  |  |  | 846 | [10 empty] | 86.69 |  |  |  | 86.69 | [5 empty] | 83.58 |  |  | 87.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.31 |  |  |  |  | 0.00
2010 |  |  |  | 7874.15 |  |  | 8760 |  |  |  | 885 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.57 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 7085.78 |  |  | 7920 |  |  |  | 885 | [10 empty] | 90.42 |  |  |  | 90.42 | [5 empty] | 91.40 |  |  | 90.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.58 |  |  |  |  | 0.00
2012 |  |  |  | 7032.52 |  |  | 7828 |  |  |  | 885 | [10 empty] | 89.13 |  |  |  | 89.13 | [5 empty] | 90.46 |  |  | 89.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.87 |  |  |  |  | 0.00
2013 |  |  |  | 7818.59 |  |  | 8458 |  |  |  | 885 | [10 empty] | 96.55 |  |  |  | 96.55 | [5 empty] | 100.84 |  |  | 96.54 |  |  |  | 3.45 |  | 3.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 7279.91 |  |  | 7929 |  |  |  | 904 | [10 empty] | 90.71 |  |  |  | 90.71 | [5 empty] | 91.93 |  |  | 90.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.29 |  |  |  |  | 0.00
2015 |  |  |  | 7255.59 |  |  | 7931 |  |  |  | 904 | [10 empty] | 90.53 |  |  |  | 90.53 | [5 empty] | 91.62 |  |  | 90.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.47 |  |  |  |  | 0.00
2016 |  |  |  | 7868.44 |  |  | 8579 |  |  |  | 904 | [10 empty] | 97.67 |  |  |  | 97.67 | [5 empty] | 99.09 |  |  | 97.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.33 |  |  |  |  | 0.00
2017 |  |  |  | 7312.33 |  |  | 8058 |  |  |  | 905 | [10 empty] | 91.99 |  |  |  | 91.99 | [5 empty] | 92.24 |  |  | 91.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.01 |  |  |  |  | 0.00
2018 |  |  |  | 7222.74 |  |  | 8085 |  |  |  | 905 | [10 empty] | 92.29 |  |  |  | 92.29 | [5 empty] | 91.11 |  |  | 92.29 |  |  |  | 1.08 |  | 1.01 | [8 empty] | 6.70 |  |  |  |  | 0.00
2019 |  |  |  | 8039.57 |  |  | 8760 |  |  |  | 905 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.41 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7345.66 |  |  | 8190 |  |  |  | 905 | [10 empty] | 93.25 |  |  |  | 93.25 | [5 empty] | 92.40 |  |  | 93.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.75 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 309
B. |  | Refuelling without maintenance | [20 empty] | 593 | [14 empty] | 18
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 595 |  |  |  | 2
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 18
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 13
L. |  | Human factor related | [39 empty] | 4
Z. |  | Other | [39 empty] | 42
Subtotal | [22 empty] | 593 | [14 empty] | 632 |  |  |  | 370
Total | [22 empty] | 593 | [14 empty] | 1002
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 30
14. |  |  | Safety Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 168
16. |  |  | Steam generation systems | [34 empty] | 17
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 19
35. |  |  | All other I&C Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 14
42. |  |  | Electrical Power Supply Systems | [34 empty] | 22
Total | [37 empty] | 333
Highlights (2020)
21st Refueling Outage (2R21)

## BRAIDWOOD-1
2020 Operating Experience
US-456 | [8 empty] | BRAIDWOOD-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-08-01
Thermal power | [12 empty] | : |  |  | 3645 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-07-12
Gross electrical power | [12 empty] | : |  |  | 1270 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-07-29
Reference unit power (net) | [12 empty] | : |  |  | 1194 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 43 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 49000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.63
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Pond (closed-cycle)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 25 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10604.45 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.11 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 908.15 | 849.61 |  |  |  | 906.87 |  | 875.78 | [8 empty] | 889.91 |  |  | 860.94 | [6 empty] | 879.77 |  | 884.03 |  |  |  | 860.54 |  |  | 903.55 |  |  | 878.94 | [9 empty] | 906.34 |  |  | 10604.45
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 102.23 | 102.24 |  |  |  | 102.09 |  | 101.87 | [8 empty] | 100.18 |  |  | 100.15 | [6 empty] | 99.04 |  | 99.52 |  |  |  | 100.10 |  |  | 101.71 |  |  | 102.24 | [9 empty] | 102.03 |  |  | 101.11
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 295005.1 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.58 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.46 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.14 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.45 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.17 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 3424.22 |  |  | 3409 |  |  |  | 1105 | [10 empty] | 91.55 |  |  |  | 91.55 | [5 empty] | 81.78 |  |  | 91.29 |  |  |  | 8.45 |  | 8.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 4649.10 |  |  | 5435 |  |  |  | 1120 | [10 empty] | 62.25 |  |  |  | 62.25 | [5 empty] | 47.39 |  |  | 62.04 |  |  |  | 2.74 |  | 1.76 | [8 empty] | 35.99 |  |  |  |  | 0.00
1990 |  |  |  | 8264.58 |  |  | 7778 |  |  |  | 1120 | [10 empty] | 89.11 |  |  |  | 89.11 | [5 empty] | 84.24 |  |  | 88.79 |  |  |  | 10.89 |  | 10.89 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 5018.62 |  |  | 5198 |  |  |  | 1120 | [10 empty] | 59.37 |  |  |  | 59.37 | [5 empty] | 51.15 |  |  | 59.34 |  |  |  | 40.63 |  | 40.63 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 7157.93 |  |  | 7142 |  |  |  | 1120 | [10 empty] | 81.36 |  |  |  | 81.36 | [5 empty] | 72.76 |  |  | 81.31 |  |  |  | 1.13 |  | 0.93 | [8 empty] | 17.71 |  |  |  |  | 0.00
1993 |  |  |  | 8693.12 |  |  | 8048 |  |  |  | 1120 | [10 empty] | 92.10 |  |  |  | 92.10 | [5 empty] | 88.60 |  |  | 91.87 |  |  |  | 7.48 |  | 7.44 | [8 empty] | 0.46 |  |  |  |  | 0.00
1994 |  |  |  | 7398.15 |  |  | 6940 |  |  |  | 1120 | [10 empty] | 79.81 |  |  |  | 79.81 | [5 empty] | 75.41 |  |  | 79.22 |  |  |  | 1.70 |  | 1.38 | [8 empty] | 18.81 |  |  |  |  | 0.00
1995 |  |  |  | 6614.28 |  |  | 6214 |  |  |  | 1120 | [10 empty] | 71.75 |  |  |  | 71.75 | [5 empty] | 67.42 |  |  | 70.94 |  |  |  | 2.77 |  | 2.04 | [8 empty] | 26.21 |  |  |  |  | 0.00
1996 |  |  |  | 7618.88 |  |  | 7021 |  |  |  | 1120 | [10 empty] | 80.50 |  |  |  | 80.50 | [5 empty] | 77.44 |  |  | 79.93 |  |  |  | 6.43 |  | 5.53 | [8 empty] | 13.97 |  |  |  |  | 0.00
1997 |  |  |  | 8096.33 |  |  | 7339 |  |  |  | 1120 | [10 empty] | 84.03 |  |  |  | 84.03 | [5 empty] | 82.52 |  |  | 83.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.97 |  |  |  |  | 0.00
1998 |  |  |  | 7578.79 |  |  | 6976 |  |  |  | 1118 | [10 empty] | 79.93 |  |  |  | 79.93 | [5 empty] | 77.36 |  |  | 79.63 |  |  |  | 1.20 |  | 0.97 | [8 empty] | 19.10 |  |  |  |  | 0.00
1999 |  |  |  | 9904.81 |  |  | 8680 |  |  |  | 1120 | [10 empty] | 99.11 |  |  |  | 99.11 | [5 empty] | 100.95 |  |  | 99.09 |  |  |  | 0.89 |  | 0.89 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 9311.32 |  |  | 8335 |  |  |  | 1100 | [10 empty] | 94.95 |  |  |  | 94.95 | [5 empty] | 96.08 |  |  | 94.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.05 |  |  |  |  | 0.00
2001 |  |  |  | 9557.87 |  |  | 8247 |  |  |  | 1168 | [10 empty] | 94.05 |  |  |  | 94.05 | [5 empty] | 97.70 |  |  | 94.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.95 |  |  |  |  | 0.00
2002 |  |  |  | 10612.24 |  |  | 8760 |  |  |  | 1161 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 104.08 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 10094.77 |  |  | 8353 |  |  |  | 1161 | [10 empty] | 95.26 |  |  |  | 95.26 | [5 empty] | 99.26 |  |  | 95.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.74 |  |  |  |  | 0.00
2004 |  |  |  | 9807.19 |  |  | 8310 |  |  |  | 1161 | [10 empty] | 94.49 |  |  |  | 94.49 | [5 empty] | 96.17 |  |  | 94.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.51 |  |  |  |  | 0.00
2005 |  |  |  | 10276.96 |  |  | 8630 |  |  |  | 1185 | [10 empty] | 98.53 |  |  |  | 98.53 | [5 empty] | 98.99 |  |  | 98.50 |  |  |  | 1.47 |  | 1.47 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 9945.95 |  |  | 8352 |  |  |  | 1178 | [10 empty] | 95.35 |  |  |  | 95.35 | [5 empty] | 96.38 |  |  | 95.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.65 |  |  |  |  | 0.00
2007 |  |  |  | 9526.68 |  |  | 8119 |  |  |  | 1178 | [10 empty] | 92.70 |  |  |  | 93.13 | [5 empty] | 92.32 |  |  | 92.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.87 |  |  |  |  | 0.43
2008 |  |  |  | 10462.94 |  |  | 8784 |  |  |  | 1178 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.12 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 9826.25 |  |  | 8259 |  |  |  | 1178 | [10 empty] | 94.29 |  |  |  | 94.29 | [5 empty] | 95.22 |  |  | 94.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.71 |  |  |  |  | 0.00
2010 |  |  |  | 9196.69 |  |  | 7806 |  |  |  | 1178 | [10 empty] | 89.13 |  |  |  | 89.13 | [5 empty] | 89.12 |  |  | 89.11 |  |  |  | 1.99 |  | 1.81 | [8 empty] | 9.06 |  |  |  |  | 0.00
2011 |  |  |  | 10411.70 |  |  | 8760 |  |  |  | 1178 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.90 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 9388.44 |  |  | 7969 |  |  |  | 1178 | [10 empty] | 90.73 |  |  |  | 90.73 | [5 empty] | 90.73 |  |  | 90.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.27 |  |  |  |  | 0.00
2013 |  |  |  | 9754.57 |  |  | 8238 |  |  |  | 1178 | [10 empty] | 94.04 |  |  |  | 94.04 | [5 empty] | 94.52 |  |  | 94.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.96 |  |  |  |  | 0.00
2014 |  |  |  | 10599.62 |  |  | 8760 |  |  |  | 1194 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.34 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 9994.36 |  |  | 8298 |  |  |  | 1194 | [10 empty] | 94.72 |  |  |  | 94.72 | [5 empty] | 95.55 |  |  | 94.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.28 |  |  |  |  | 0.00
2016 |  |  |  | 9622.74 |  |  | 8058 |  |  |  | 1194 | [10 empty] | 91.73 |  |  |  | 91.73 | [5 empty] | 91.75 |  |  | 91.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.27 |  |  |  |  | 0.00
2017 |  |  |  | 10579.19 |  |  | 8737 |  |  |  | 1194 | [10 empty] | 99.73 |  |  |  | 99.73 | [5 empty] | 101.14 |  |  | 99.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.27 |  |  |  |  | 0.00
2018 |  |  |  | 9803.97 |  |  | 8208 |  |  |  | 1194 | [10 empty] | 93.84 |  |  |  | 93.84 | [5 empty] | 93.73 |  |  | 93.70 |  |  |  | 0.58 |  | 0.54 | [8 empty] | 5.61 |  |  |  |  | 0.00
2019 |  |  |  | 9986.33 |  |  | 8360 |  |  |  | 1194 | [10 empty] | 95.45 |  |  |  | 95.45 | [5 empty] | 95.48 |  |  | 95.43 |  |  |  | 0.27 |  | 0.26 | [8 empty] | 4.29 |  |  |  |  | 0.00
2020 |  |  |  | 10604.45 |  |  | 8783 |  |  |  | 1194 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.11 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 195
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 559
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 81
E. |  | Testing of plant systems or components | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 14
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 5
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [35 empty] | 0 |  |  |  | 2
Subtotal | [37 empty] | 641 |  |  |  | 216 | [11 empty] | 4
Total | [22 empty] | 0 | [14 empty] | 861
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 4
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 15
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 22
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 21
34. |  |  | Miscellaneous Systems | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 102
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 197

## BRAIDWOOD-2
2020 Operating Experience
US-457 | [8 empty] | BRAIDWOOD-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-08-01
Thermal power | [12 empty] | : |  |  | 3645 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-05-25
Gross electrical power | [12 empty] | : |  |  | 1230 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-10-17
Reference unit power (net) | [12 empty] | : |  |  | 1160 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 43 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 49000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.63
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Pond (closed-cycle)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 25 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9767.22 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.57 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.57 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.43 %
Load Factor (LF) | [18 empty] | : | 95.86 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 95.56 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 390 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 880.65 | 823.75 |  |  |  | 879.37 |  | 492.89 | [8 empty] | 694.11 |  |  | 836.43 | [6 empty] | 853.58 |  | 858.53 |  |  |  | 841.45 |  |  | 876.50 |  |  | 851.61 | [9 empty] | 878.35 |  |  | 9767.22
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 63.47 | [8 empty] | 83.04 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.57
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 63.47 | [8 empty] | 83.04 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.57
LF [%] |  |  |  |  | 102.04 | 102.03 |  |  |  | 101.89 |  | 59.02 | [8 empty] | 80.43 |  |  | 100.15 | [6 empty] | 98.90 |  | 99.48 |  |  |  | 100.75 |  |  | 101.56 |  |  | 101.97 | [9 empty] | 101.77 |  |  | 95.86
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 63.47 | [8 empty] | 83.06 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.56
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 36.53 | [8 empty] | 16.96 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.43
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 302075.35 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.38 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.43 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.3 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.45 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.26 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 90.99 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 92.28 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 1350.94 |  |  | 1476 |  |  |  | 1097 | [10 empty] | 87.43 |  |  |  | 87.43 | [5 empty] | 72.73 |  |  | 87.30 |  |  |  | 12.57 |  | 12.57 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 7142.04 |  |  | 7581 |  |  |  | 1120 | [10 empty] | 86.89 |  |  |  | 86.89 | [5 empty] | 72.79 |  |  | 86.54 |  |  |  | 1.71 |  | 1.51 | [8 empty] | 11.60 |  |  |  |  | 0.00
1990 |  |  |  | 6353.59 |  |  | 6849 |  |  |  | 1120 | [10 empty] | 78.79 |  |  |  | 78.79 | [5 empty] | 64.76 |  |  | 78.18 |  |  |  | 2.04 |  | 1.64 | [8 empty] | 19.56 |  |  |  |  | 0.00
1991 |  |  |  | 6545.52 |  |  | 6626 |  |  |  | 1120 | [10 empty] | 75.72 |  |  |  | 75.72 | [5 empty] | 66.71 |  |  | 75.64 |  |  |  | 4.73 |  | 3.76 | [8 empty] | 20.51 |  |  |  |  | 0.00
1992 |  |  |  | 8751.14 |  |  | 8346 |  |  |  | 1120 | [10 empty] | 95.06 |  |  |  | 95.06 | [5 empty] | 88.95 |  |  | 95.01 |  |  |  | 2.20 |  | 2.14 | [8 empty] | 2.80 |  |  |  |  | 0.00
1993 |  |  |  | 7362.34 |  |  | 7098 |  |  |  | 1120 | [10 empty] | 81.46 |  |  |  | 81.46 | [5 empty] | 75.04 |  |  | 81.03 |  |  |  | 3.37 |  | 2.84 | [8 empty] | 15.70 |  |  |  |  | 0.00
1994 |  |  |  | 6636.15 |  |  | 6454 |  |  |  | 1120 | [10 empty] | 74.13 |  |  |  | 74.13 | [5 empty] | 67.64 |  |  | 73.68 |  |  |  | 16.56 |  | 14.71 | [8 empty] | 11.16 |  |  |  |  | 0.00
1995 |  |  |  | 9533.04 |  |  | 8583 |  |  |  | 1120 | [10 empty] | 98.06 |  |  |  | 98.06 | [5 empty] | 97.16 |  |  | 97.98 |  |  |  | 1.94 |  | 1.94 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 8011.80 |  |  | 7349 |  |  |  | 1120 | [10 empty] | 84.12 |  |  |  | 84.12 | [5 empty] | 81.44 |  |  | 83.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.88 |  |  |  |  | 0.00
1997 |  |  |  | 8234.75 |  |  | 7563 |  |  |  | 1120 | [10 empty] | 86.46 |  |  |  | 86.46 | [5 empty] | 83.93 |  |  | 86.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.54 |  |  |  |  | 0.00
1998 |  |  |  | 9694.64 |  |  | 8552 |  |  |  | 1118 | [10 empty] | 97.71 |  |  |  | 97.71 | [5 empty] | 98.96 |  |  | 97.63 |  |  |  | 2.29 |  | 2.29 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 9030.88 |  |  | 8070 |  |  |  | 1120 | [10 empty] | 92.35 |  |  |  | 92.35 | [5 empty] | 92.05 |  |  | 92.12 |  |  |  | 0.91 |  | 0.84 | [8 empty] | 6.81 |  |  |  |  | 0.00
2000 |  |  |  | 9510.95 |  |  | 8303 |  |  |  | 1100 | [10 empty] | 94.60 |  |  |  | 94.60 | [5 empty] | 98.14 |  |  | 94.52 |  |  |  | 1.23 |  | 1.18 | [8 empty] | 4.23 |  |  |  |  | 0.00
2001 |  |  |  | 9647.86 |  |  | 8481 |  |  |  | 1122 | [10 empty] | 96.74 |  |  |  | 96.74 | [5 empty] | 98.96 |  |  | 96.82 |  |  |  | 0.49 |  | 0.48 | [8 empty] | 2.78 |  |  |  |  | 0.00
2002 |  |  |  | 9449.48 |  |  | 8099 |  |  |  | 1154 | [10 empty] | 92.48 |  |  |  | 92.48 | [5 empty] | 94.28 |  |  | 92.45 |  |  |  | 0.54 |  | 0.50 | [8 empty] | 7.02 |  |  |  |  | 0.00
2003 |  |  |  | 9932.17 |  |  | 8337 |  |  |  | 1154 | [10 empty] | 95.08 |  |  |  | 95.08 | [5 empty] | 98.25 |  |  | 95.17 |  |  |  | 0.61 |  | 0.58 | [8 empty] | 4.34 |  |  |  |  | 0.00
2004 |  |  |  | 10200.98 |  |  | 8757 |  |  |  | 1129 | [10 empty] | 99.68 |  |  |  | 99.68 | [5 empty] | 102.67 |  |  | 99.69 |  |  |  | 0.32 |  | 0.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 9519.42 |  |  | 8244 |  |  |  | 1177 | [10 empty] | 94.11 |  |  |  | 94.11 | [5 empty] | 92.32 |  |  | 94.10 |  |  |  | 1.27 |  | 1.21 | [8 empty] | 4.68 |  |  |  |  | 0.00
2006 |  |  |  | 9624.59 |  |  | 8335 |  |  |  | 1152 | [10 empty] | 95.16 |  |  |  | 95.16 | [5 empty] | 95.37 |  |  | 95.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.84 |  |  |  |  | 0.00
2007 |  |  |  | 10131.17 |  |  | 8706 |  |  |  | 1152 | [10 empty] | 99.39 |  |  |  | 100.00 | [5 empty] | 100.39 |  |  | 99.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.61
2008 |  |  |  | 9323.22 |  |  | 8106 |  |  |  | 1152 | [10 empty] | 92.29 |  |  |  | 92.29 | [5 empty] | 92.13 |  |  | 92.28 |  |  |  | 0.57 |  | 0.53 | [8 empty] | 7.18 |  |  |  |  | 0.00
2009 |  |  |  | 9401.72 |  |  | 8121 |  |  |  | 1152 | [10 empty] | 92.74 |  |  |  | 92.74 | [5 empty] | 93.16 |  |  | 92.71 |  |  |  | 1.91 |  | 1.80 | [8 empty] | 5.46 |  |  |  |  | 0.00
2010 |  |  |  | 10003.25 |  |  | 8599 |  |  |  | 1152 | [10 empty] | 98.17 |  |  |  | 98.17 | [5 empty] | 99.13 |  |  | 98.16 |  |  |  | 1.83 |  | 1.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 9364.17 |  |  | 8177 |  |  |  | 1152 | [10 empty] | 93.36 |  |  |  | 93.36 | [5 empty] | 92.79 |  |  | 93.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.64 |  |  |  |  | 0.00
2012 |  |  |  | 9417.92 |  |  | 8188 |  |  |  | 1152 | [10 empty] | 93.23 |  |  |  | 93.23 | [5 empty] | 93.07 |  |  | 93.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.77 |  |  |  |  | 0.00
2013 |  |  |  | 9905.03 |  |  | 8580 |  |  |  | 1152 | [10 empty] | 97.95 |  |  |  | 97.95 | [5 empty] | 98.14 |  |  | 97.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.05 |  |  |  |  | 0.00
2014 |  |  |  | 9670.45 |  |  | 8276 |  |  |  | 1160 | [10 empty] | 94.52 |  |  |  | 94.52 | [5 empty] | 95.17 |  |  | 94.47 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 5.43 |  |  |  |  | 0.00
2015 |  |  |  | 9715.53 |  |  | 8312 |  |  |  | 1160 | [10 empty] | 94.88 |  |  |  | 94.88 | [5 empty] | 95.61 |  |  | 94.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.12 |  |  |  |  | 0.00
2016 |  |  |  | 10226.53 |  |  | 8784 |  |  |  | 1160 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.36 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 9406.23 |  |  | 8117 |  |  |  | 1160 | [10 empty] | 92.67 |  |  |  | 92.67 | [5 empty] | 92.57 |  |  | 92.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.33 |  |  |  |  | 0.00
2018 |  |  |  | 9479.35 |  |  | 8175 |  |  |  | 1160 | [10 empty] | 93.42 |  |  |  | 93.42 | [5 empty] | 93.29 |  |  | 93.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.58 |  |  |  |  | 0.00
2019 |  |  |  | 10264.82 |  |  | 8760 |  |  |  | 1160 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.02 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9767.22 |  |  | 8394 |  |  |  | 1160 | [10 empty] | 95.57 |  |  |  | 95.57 | [5 empty] | 95.86 |  |  | 95.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.43 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 103
B. |  | Refuelling without maintenance | [20 empty] | 389 | [14 empty] | 12
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 489
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 56
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
Z. |  | Other | [39 empty] | 9
Subtotal | [22 empty] | 389 | [14 empty] | 557 |  |  |  | 120 | [11 empty] | 3
Total | [22 empty] | 389 | [14 empty] | 680
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 9
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 8
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 13
42. |  |  | Electrical Power Supply Systems | [34 empty] | 40
Total | [37 empty] | 104
Highlights (2020)
Refueling Outage 21 (A2R21)

## BROWNS FERRY-1
2020 Operating Experience
US-259 | [8 empty] | BROWNS FERRY-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVA (Tennessee Valley Authority)
Owner | [7 empty] | : | TVA (Tennessee Valley Authority)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-05-01
Thermal power | [12 empty] | : |  |  | 3458 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-10-15
Gross electrical power | [12 empty] | : |  |  | 1256 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-08-01
Reference unit power (net) | [12 empty] | : |  |  | 1200 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 285
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 28 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 154 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.25 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9174.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.63 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.86 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.37 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.86 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.76 %
Load Factor (LF) | [18 empty] | : | 87.03 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 87.86 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1066 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 894.14 | 841.58 |  |  |  | 923.78 |  | 899.02 | [8 empty] | 930.17 |  |  | 895.46 | [6 empty] | 612.86 |  | 886.88 |  |  |  | 796.45 |  |  | 42.16 |  |  | 579.40 | [9 empty] | 872.22 |  |  | 9174.12
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 71.99 |  | 100.00 |  |  |  | 100.00 |  |  | 6.32 |  |  | 77.70 | [9 empty] | 100.00 |  |  | 87.86
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 71.99 |  | 100.00 |  |  |  | 100.00 |  |  | 6.32 |  |  | 77.70 | [9 empty] | 100.00 |  |  | 87.86
LF [%] |  |  |  |  | 100.15 | 100.76 |  |  |  | 103.47 |  | 104.05 | [8 empty] | 104.19 |  |  | 103.64 | [6 empty] | 68.64 |  | 99.34 |  |  |  | 92.18 |  |  | 4.72 |  |  | 67.06 | [9 empty] | 97.69 |  |  | 87.03
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 72.04 |  | 100.00 |  |  |  | 100.00 |  |  | 6.32 |  |  | 77.78 | [9 empty] | 100.00 |  |  | 87.86
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 28.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.63
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 28.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.37
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 93.68 |  |  | 22.30 | [9 empty] | 0.00 |  |  | 9.76
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 181837.75 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 11.19 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.26 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.76 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.53 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.71 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.45 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.27 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.08 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 5168.70 |  |  | 6523 |  |  |  | 1065 | [10 empty] | 85.76 |  |  |  | 85.76 | [5 empty] | 70.71 |  |  | 84.80 |  |  |  | 1.41 |  | 1.23 | [8 empty] | 13.02 |  |  |  |  | 0.00
1975 |  |  |  | 1378.50 |  |  | 1535 |  |  |  | 1065 | [10 empty] | 14.79 |  |  |  | 14.79 | [5 empty] | 14.78 |  |  | 17.52 |  |  |  | 84.64 |  | 81.48 | [8 empty] | 3.73 |  |  |  |  | 0.00
1976 |  |  |  | 1301.10 |  |  | 2174 |  |  |  | 1065 | [10 empty] | 13.94 |  |  |  | 13.94 | [5 empty] | 13.91 |  |  | 24.75 |  |  |  | 83.55 |  | 70.84 | [8 empty] | 15.22 |  |  |  |  | 0.00
1977 |  |  |  | 5043.10 |  |  | 5817 |  |  |  | 1065 | [10 empty] | 54.09 |  |  |  | 54.09 | [5 empty] | 54.06 |  |  | 66.40 |  |  |  | 18.68 |  | 12.42 | [8 empty] | 33.49 |  |  |  |  | 0.00
1978 |  |  |  | 5817.80 |  |  | 7042 |  |  |  | 1065 | [10 empty] | 62.37 |  |  |  | 62.37 | [5 empty] | 62.36 |  |  | 80.39 |  |  |  | 16.54 |  | 12.36 | [8 empty] | 25.26 |  |  |  |  | 0.00
1979 |  |  |  | 7495.70 |  |  | 7918 |  |  |  | 1065 | [10 empty] | 80.35 |  |  |  | 80.35 | [5 empty] | 80.34 |  |  | 90.39 |  |  |  | 10.30 |  | 9.23 | [8 empty] | 10.42 |  |  |  |  | 0.00
1980 |  |  |  | 6061.30 |  |  | 6376 |  |  |  | 1065 | [10 empty] | 73.34 |  |  |  | 73.47 | [5 empty] | 64.79 |  |  | 72.59 |  |  |  | 6.41 |  | 5.03 | [8 empty] | 21.49 |  |  |  |  | 0.13
1981 |  |  |  | 4405.30 |  |  | 4435 |  |  |  | 1065 | [10 empty] | 50.95 |  |  |  | 50.95 | [5 empty] | 47.22 |  |  | 50.63 |  |  |  | 3.11 |  | 1.64 | [8 empty] | 47.41 |  |  |  |  | 0.00
1982 |  |  |  | 7880.90 |  |  | 7967 |  |  |  | 1065 | [10 empty] | 91.25 |  |  |  | 91.25 | [5 empty] | 84.47 |  |  | 90.95 |  |  |  | 8.20 |  | 8.16 | [8 empty] | 0.60 |  |  |  |  | 0.00
1983 |  |  |  | 2175.50 |  |  | 2316 |  |  |  | 1065 | [10 empty] | 26.51 |  |  |  | 26.51 | [5 empty] | 23.32 |  |  | 26.44 |  |  |  | 7.92 |  | 2.28 | [8 empty] | 71.21 |  |  |  |  | 0.00
1984 |  |  |  | 7848.49 |  |  | 7930 |  |  |  | 1065 | [10 empty] | 90.30 |  |  |  | 90.30 | [5 empty] | 83.90 |  |  | 90.28 |  |  |  | 9.37 |  | 9.34 | [8 empty] | 0.36 |  |  |  |  | 0.00
1985 |  |  |  | 1603.03 |  |  | 1626 |  |  |  | 1065 | [10 empty] | 74.94 |  |  |  | 74.94 | [5 empty] | 69.68 |  |  | 75.28 |  |  |  | 25.06 |  | 25.06 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | Data not available - Long-term shutdown
1987 |  |  |  | "
1988 |  |  |  | "
1989 |  |  |  | "
1990 |  |  |  | "
1991 |  |  |  | "
1992 |  |  |  | "
1993 |  |  |  | "
1994 |  |  |  | "
1995 |  |  |  | "
1996 |  |  |  | "
1997 |  |  |  | "
1998 |  |  |  | "
1999 |  |  |  | "
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | "
2005 |  |  |  | "
2006 |  |  |  | "
2007 |  |  |  | 4535.28 |  |  | 4452 |  |  |  | 1065 | [10 empty] | 85.43 |  |  |  | 85.43 | [5 empty] | 82.90 |  |  | 86.67 |  |  |  | 8.84 |  | 8.28 | [8 empty] | 6.29 |  |  |  |  | 0.00
2008 |  |  |  | 8193.05 |  |  | 7693 |  |  |  | 1065 | [10 empty] | 87.60 |  |  |  | 87.60 | [5 empty] | 87.58 |  |  | 87.58 |  |  |  | 2.22 |  | 1.99 | [8 empty] | 10.41 |  |  |  |  | 0.00
2009 |  |  |  | 8758.70 |  |  | 8147 |  |  |  | 1065 | [10 empty] | 93.03 |  |  |  | 93.03 | [5 empty] | 93.88 |  |  | 93.00 |  |  |  | 6.97 |  | 6.97 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 8072.30 |  |  | 8007 |  |  |  | 1093 | [10 empty] | 91.45 |  |  |  | 91.45 | [5 empty] | 86.15 |  |  | 91.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.55 |  |  |  |  | 0.00
2011 |  |  |  | 8757.41 |  |  | 8048 |  |  |  | 1101 | [10 empty] | 91.95 |  |  |  | 98.21 | [5 empty] | 90.80 |  |  | 91.87 |  |  |  | 0.49 |  | 0.48 | [8 empty] | 1.31 |  |  |  |  | 6.26
2012 |  |  |  | 8505.98 |  |  | 7691 |  |  |  | 1101 | [10 empty] | 87.57 |  |  |  | 87.57 | [5 empty] | 87.95 |  |  | 87.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.43 |  |  |  |  | 0.00
2013 |  |  |  | 9485.99 |  |  | 8516 |  |  |  | 1101 | [10 empty] | 97.22 |  |  |  | 97.22 | [5 empty] | 98.34 |  |  | 97.20 |  |  |  | 2.49 |  | 2.48 | [8 empty] | 0.30 |  |  |  |  | 0.00
2014 |  |  |  | 8691.41 |  |  | 8021 |  |  |  | 1101 | [10 empty] | 91.56 |  |  |  | 91.56 | [5 empty] | 90.12 |  |  | 91.56 |  |  |  | 1.42 |  | 1.32 | [8 empty] | 7.11 |  |  |  |  | 0.00
2015 |  |  |  | 9455.32 |  |  | 8575 |  |  |  | 1101 | [10 empty] | 97.88 |  |  |  | 97.88 | [5 empty] | 98.04 |  |  | 97.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.12 |  |  |  |  | 0.00
2016 |  |  |  | 8382.89 |  |  | 7799 |  |  |  | 1101 | [10 empty] | 88.79 |  |  |  | 88.79 | [5 empty] | 86.68 |  |  | 88.79 |  |  |  | 0.25 |  | 0.22 | [8 empty] | 10.99 |  |  |  |  | 0.00
2017 |  |  |  | 9801.35 |  |  | 8760 |  |  |  | 1101 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.62 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 8114.12 |  |  | 7702 |  |  |  | 1101 | [10 empty] | 87.92 |  |  |  | 87.92 | [5 empty] | 84.13 |  |  | 87.92 |  |  |  | 1.39 |  | 1.24 | [8 empty] | 10.84 |  |  |  |  | 0.00
2019 |  |  |  | 10857.30 |  |  | 8760 |  |  |  | 1200 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9174.12 |  |  | 7718 |  |  |  | 1200 | [10 empty] | 87.86 |  |  |  | 87.86 | [5 empty] | 87.03 |  |  | 87.86 |  |  |  | 2.63 |  | 2.37 | [8 empty] | 9.76 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 269
B. |  | Refuelling without maintenance | [20 empty] | 858 | [14 empty] | 35
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1102 |  |  |  | 89
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 3714
E. |  | Testing of plant systems or components | [35 empty] | 12 |  |  |  | 17
H. |  | Nuclear regulatory requirements | [35 empty] | 362 |  |  |  | 2869
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 24
L. |  | Human factor related | [39 empty] | 9
P. |  | Fire | [39 empty] | 544
Z. |  | Other | [24 empty] | 208 | [14 empty] | 11
Subtotal | [22 empty] | 858 |  |  |  | 208 | [10 empty] | 5225 |  |  |  | 3808 | [11 empty] | 24
Total | [22 empty] | 1066 | [14 empty] | 9057
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 11
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 15
14. |  |  | Safety Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 79
31. |  |  | Turbine and auxiliaries | [34 empty] | 63
32. |  |  | Feedwater and Main Steam System | [34 empty] | 26
34. |  |  | Miscellaneous Systems | [34 empty] | 26
41. |  |  | Main Generator Systems | [34 empty] | 10
42. |  |  | Electrical Power Supply Systems | [34 empty] | 28
Total | [37 empty] | 278
Highlights (2020)
Refueling Outage U1R13 Refueling

## BROWNS FERRY-2
2020 Operating Experience
US-260 | [8 empty] | BROWNS FERRY-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVA (Tennessee Valley Authority)
Owner | [7 empty] | : | TVA (Tennessee Valley Authority)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-05-01
Thermal power | [12 empty] | : |  |  | 3458 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-08-28
Gross electrical power | [12 empty] | : |  |  | 1259 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-03-01
Reference unit power (net) | [12 empty] | : |  |  | 1200 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 285
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 28 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.49 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10098.92 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.27 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.22 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.27 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.5 %
Load Factor (LF) | [18 empty] | : | 95.81 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 95.26 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 416 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 929.70 | 848.77 |  |  |  | 925.68 |  | 901.14 | [8 empty] | 714.04 |  |  | 648.68 | [6 empty] | 613.76 |  | 890.35 |  |  |  | 839.04 |  |  | 933.45 |  |  | 905.70 | [9 empty] | 948.62 |  |  | 10098.92
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 88.37 |  |  | 81.47 | [6 empty] | 73.77 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.27
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 88.37 |  |  | 81.47 | [6 empty] | 73.77 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.27
LF [%] |  |  |  |  | 104.13 | 101.63 |  |  |  | 103.68 |  | 104.30 | [8 empty] | 79.98 |  |  | 75.08 | [6 empty] | 68.75 |  | 99.73 |  |  |  | 97.11 |  |  | 104.55 |  |  | 104.83 | [9 empty] | 106.25 |  |  | 95.81
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 88.31 |  |  | 81.53 | [6 empty] | 73.79 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.26
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 26.23 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.22
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.63 |  |  | 18.53 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.50
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 310815.58 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.71 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.1 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.05 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.3 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.65 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.2 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.9 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 1425.70 |  |  | 1578 |  |  |  | 1065 | [10 empty] | 7.04 |  |  |  | 7.04 | [5 empty] | 7.04 |  |  | 7.04 |  |  |  | 92.96 |  | 92.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
1976 |  |  |  | 1567.20 |  |  | 2547 |  |  |  | 1065 | [10 empty] | 16.78 |  |  |  | 16.78 | [5 empty] | 16.75 |  |  | 29.00 |  |  |  | 78.21 |  | 60.26 | [8 empty] | 22.96 |  |  |  |  | 0.00
1977 |  |  |  | 6225.00 |  |  | 6963 |  |  |  | 1065 | [10 empty] | 66.78 |  |  |  | 66.78 | [5 empty] | 66.72 |  |  | 79.49 |  |  |  | 31.21 |  | 30.29 | [8 empty] | 2.93 |  |  |  |  | 0.00
1978 |  |  |  | 5547.50 |  |  | 6032 |  |  |  | 1065 | [10 empty] | 59.45 |  |  |  | 59.45 | [5 empty] | 59.46 |  |  | 68.86 |  |  |  | 12.86 |  | 8.77 | [8 empty] | 31.78 |  |  |  |  | 0.00
1979 |  |  |  | 7441.40 |  |  | 7593 |  |  |  | 1065 | [10 empty] | 79.76 |  |  |  | 79.76 | [5 empty] | 79.76 |  |  | 86.68 |  |  |  | 8.98 |  | 7.87 | [8 empty] | 12.37 |  |  |  |  | 0.00
1980 |  |  |  | 5618.40 |  |  | 6073 |  |  |  | 1065 | [10 empty] | 69.46 |  |  |  | 69.78 | [5 empty] | 60.06 |  |  | 69.14 |  |  |  | 10.06 |  | 7.81 | [8 empty] | 22.42 |  |  |  |  | 0.32
1981 |  |  |  | 7471.90 |  |  | 7452 |  |  |  | 1065 | [10 empty] | 85.24 |  |  |  | 85.24 | [5 empty] | 80.09 |  |  | 85.07 |  |  |  | 9.56 |  | 9.01 | [8 empty] | 5.74 |  |  |  |  | 0.00
1982 |  |  |  | 4450.90 |  |  | 4778 |  |  |  | 1065 | [10 empty] | 54.92 |  |  |  | 54.92 | [5 empty] | 47.71 |  |  | 54.54 |  |  |  | 4.91 |  | 2.84 | [8 empty] | 42.25 |  |  |  |  | 0.00
1983 |  |  |  | 6385.60 |  |  | 6514 |  |  |  | 1065 | [10 empty] | 74.81 |  |  |  | 74.81 | [5 empty] | 68.45 |  |  | 74.36 |  |  |  | 4.85 |  | 3.81 | [8 empty] | 21.38 |  |  |  |  | 0.00
1984 |  |  |  | 4044.37 |  |  | 5844 |  |  |  | 1065 | [10 empty] | 66.55 |  |  |  | 66.55 | [5 empty] | 43.23 |  |  | 66.53 |  |  |  | 4.09 |  | 2.84 | [8 empty] | 30.61 |  |  |  |  | 0.00
1985 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1065 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1986 |  |  |  | Data not available - Long-term shutdown
1987 |  |  |  | "
1988 |  |  |  | "
1989 |  |  |  | "
1990 |  |  |  | "
1991 |  |  |  | 3804.01 |  |  | 4125 |  |  |  | 1065 | [10 empty] | 80.36 |  |  |  | 80.36 | [5 empty] | 69.53 |  |  | 80.30 |  |  |  | 15.46 |  | 14.70 | [8 empty] | 4.94 |  |  |  |  | 0.00
1992 |  |  |  | 8388.77 |  |  | 8401 |  |  |  | 1065 | [10 empty] | 95.69 |  |  |  | 95.69 | [5 empty] | 89.67 |  |  | 95.64 |  |  |  | 2.05 |  | 2.00 | [8 empty] | 2.31 |  |  |  |  | 0.00
1993 |  |  |  | 5776.84 |  |  | 5753 |  |  |  | 1065 | [10 empty] | 65.68 |  |  |  | 65.68 | [5 empty] | 61.92 |  |  | 65.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 34.32 |  |  |  |  | 0.00
1994 |  |  |  | 7345.17 |  |  | 7234 |  |  |  | 1065 | [10 empty] | 82.58 |  |  |  | 82.58 | [5 empty] | 78.73 |  |  | 82.58 |  |  |  | 2.24 |  | 1.89 | [8 empty] | 15.53 |  |  |  |  | 0.00
1995 |  |  |  | 9197.03 |  |  | 8629 |  |  |  | 1065 | [10 empty] | 98.50 |  |  |  | 98.50 | [5 empty] | 98.58 |  |  | 98.50 |  |  |  | 1.50 |  | 1.50 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 8046.29 |  |  | 7795 |  |  |  | 1065 | [10 empty] | 88.74 |  |  |  | 88.74 | [5 empty] | 86.01 |  |  | 88.74 |  |  |  | 2.76 |  | 2.52 | [8 empty] | 8.74 |  |  |  |  | 0.00
1997 |  |  |  | 8372.93 |  |  | 8130 |  |  |  | 1065 | [10 empty] | 92.82 |  |  |  | 92.82 | [5 empty] | 89.75 |  |  | 92.81 |  |  |  | 1.29 |  | 1.21 | [8 empty] | 5.97 |  |  |  |  | 0.00
1998 |  |  |  | 9301.04 |  |  | 8730 |  |  |  | 1065 | [10 empty] | 99.66 |  |  |  | 99.66 | [5 empty] | 99.70 |  |  | 99.66 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 8586.32 |  |  | 7985 |  |  |  | 1100 | [10 empty] | 91.02 |  |  |  | 91.02 | [5 empty] | 89.06 |  |  | 91.15 |  |  |  | 1.28 |  | 1.18 | [8 empty] | 7.80 |  |  |  |  | 0.00
2000 |  |  |  | 9733.46 |  |  | 8727 |  |  |  | 1118 | [10 empty] | 99.36 |  |  |  | 99.36 | [5 empty] | 99.11 |  |  | 99.35 |  |  |  | 0.64 |  | 0.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 8414.56 |  |  | 7636 |  |  |  | 1118 | [10 empty] | 87.18 |  |  |  | 87.18 | [5 empty] | 85.92 |  |  | 87.17 |  |  |  | 0.49 |  | 0.43 | [8 empty] | 12.39 |  |  |  |  | 0.00
2002 |  |  |  | 8911.26 |  |  | 8269 |  |  |  | 1118 | [10 empty] | 94.40 |  |  |  | 94.40 | [5 empty] | 90.99 |  |  | 94.39 |  |  |  | 0.78 |  | 0.75 | [8 empty] | 4.85 |  |  |  |  | 0.00
2003 |  |  |  | 8369.22 |  |  | 7888 |  |  |  | 1118 | [10 empty] | 90.06 |  |  |  | 90.06 | [5 empty] | 85.46 |  |  | 90.05 |  |  |  | 1.82 |  | 1.67 | [8 empty] | 8.28 |  |  |  |  | 0.00
2004 |  |  |  | 9785.98 |  |  | 8715 |  |  |  | 1118 | [10 empty] | 99.21 |  |  |  | 99.21 | [5 empty] | 99.65 |  |  | 99.21 |  |  |  | 0.79 |  | 0.79 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 8802.16 |  |  | 8052 |  |  |  | 1118 | [10 empty] | 91.94 |  |  |  | 91.94 | [5 empty] | 89.88 |  |  | 91.92 |  |  |  | 0.62 |  | 0.57 | [8 empty] | 7.49 |  |  |  |  | 0.00
2006 |  |  |  | 9232.64 |  |  | 8365 |  |  |  | 1118 | [10 empty] | 95.50 |  |  |  | 95.50 | [5 empty] | 94.27 |  |  | 95.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.50 |  |  |  |  | 0.00
2007 |  |  |  | 7606.63 |  |  | 7229 |  |  |  | 1104 | [10 empty] | 80.66 |  |  |  | 80.66 | [5 empty] | 78.65 |  |  | 82.52 |  |  |  | 1.12 |  | 0.91 | [8 empty] | 18.43 |  |  |  |  | 0.00
2008 |  |  |  | 9429.92 |  |  | 8545 |  |  |  | 1104 | [10 empty] | 97.29 |  |  |  | 97.29 | [5 empty] | 97.24 |  |  | 97.28 |  |  |  | 1.17 |  | 1.15 | [8 empty] | 1.56 |  |  |  |  | 0.00
2009 |  |  |  | 7808.51 |  |  | 7122 |  |  |  | 1103 | [10 empty] | 81.31 |  |  |  | 81.31 | [5 empty] | 80.81 |  |  | 81.30 |  |  |  | 3.37 |  | 2.84 | [8 empty] | 15.85 |  |  |  |  | 0.00
2010 |  |  |  | 8842.51 |  |  | 8568 |  |  |  | 1104 | [10 empty] | 97.82 |  |  |  | 97.82 | [5 empty] | 91.43 |  |  | 97.81 |  |  |  | 0.66 |  | 0.65 | [8 empty] | 1.53 |  |  |  |  | 0.00
2011 |  |  |  | 7720.39 |  |  | 7092 |  |  |  | 1104 | [10 empty] | 80.98 |  |  |  | 88.55 | [5 empty] | 79.83 |  |  | 80.96 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 11.40 |  |  |  |  | 7.57
2012 |  |  |  | 9576.00 |  |  | 8685 |  |  |  | 1104 | [10 empty] | 98.88 |  |  |  | 98.88 | [5 empty] | 98.75 |  |  | 98.87 |  |  |  | 1.12 |  | 1.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 7997.82 |  |  | 7527 |  |  |  | 1104 | [10 empty] | 85.93 |  |  |  | 85.93 | [5 empty] | 82.69 |  |  | 85.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.07 |  |  |  |  | 0.00
2014 |  |  |  | 9481.43 |  |  | 8657 |  |  |  | 1104 | [10 empty] | 98.83 |  |  |  | 98.83 | [5 empty] | 98.04 |  |  | 98.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.17 |  |  |  |  | 0.00
2015 |  |  |  | 8591.32 |  |  | 7947 |  |  |  | 1104 | [10 empty] | 90.72 |  |  |  | 90.72 | [5 empty] | 88.84 |  |  | 90.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.28 |  |  |  |  | 0.00
2016 |  |  |  | 9523.24 |  |  | 8722 |  |  |  | 1104 | [10 empty] | 99.29 |  |  |  | 99.29 | [5 empty] | 98.20 |  |  | 99.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.71 |  |  |  |  | 0.00
2017 |  |  |  | 8395.47 |  |  | 7940 |  |  |  | 1104 | [10 empty] | 90.64 |  |  |  | 90.64 | [5 empty] | 86.81 |  |  | 90.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.36 |  |  |  |  | 0.00
2018 |  |  |  | 9460.54 |  |  | 8622 |  |  |  | 1104 | [10 empty] | 98.42 |  |  |  | 98.42 | [5 empty] | 97.82 |  |  | 98.42 |  |  |  | 0.50 |  | 0.49 | [8 empty] | 1.09 |  |  |  |  | 0.00
2019 |  |  |  | 8448.74 |  |  | 7399 |  |  |  | 1200 | [10 empty] | 84.84 |  |  |  | 84.84 | [5 empty] | 83.12 |  |  | 84.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.16 |  |  |  |  | 0.00
2020 |  |  |  | 10098.92 |  |  | 8368 |  |  |  | 1200 | [10 empty] | 95.27 |  |  |  | 95.27 | [5 empty] | 95.81 |  |  | 95.26 |  |  |  | 0.00 |  | 2.22 | [8 empty] | 2.50 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 174
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 954 |  |  |  | 55
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 220 | [14 empty] | 99
E. |  | Testing of plant systems or components | [35 empty] | 7 |  |  |  | 3
H. |  | Nuclear regulatory requirements | [39 empty] | 1160
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 17
L. |  | Human factor related | [39 empty] | 20
P. |  | Fire | [39 empty] | 325
Z. |  | Other | [31 empty] | 195 | [7 empty] | 2 | [11 empty] | 5
Subtotal | [22 empty] | 220 | [10 empty] | 195 |  |  |  | 1060 |  |  |  | 1739 | [11 empty] | 22
Total | [22 empty] | 415 | [14 empty] | 2821
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 28
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 25
31. |  |  | Turbine and auxiliaries | [34 empty] | 45
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 16
42. |  |  | Electrical Power Supply Systems | [34 empty] | 22
Total | [37 empty] | 175
Highlights (2020)
Outage to Repair Drywell Leak

## BROWNS FERRY-3
2020 Operating Experience
US-296 | [8 empty] | BROWNS FERRY-3 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVA (Tennessee Valley Authority)
Owner | [7 empty] | : | TVA (Tennessee Valley Authority)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-07-01
Thermal power | [12 empty] | : |  |  | 3458 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-09-12
Gross electrical power | [12 empty] | : |  |  | 1260 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-03-01
Reference unit power (net) | [12 empty] | : |  |  | 1210 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 285
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 32 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 149 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9501.81 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.31 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.61 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.19 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.61 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.21 %
Load Factor (LF) | [18 empty] | : | 89.4 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 89.59 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 914 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 834.67 | 565.01 |  |  |  | 75.33 |  | 710.05 | [8 empty] | 952.01 |  |  | 902.40 | [6 empty] | 880.19 |  | 913.19 |  |  |  | 863.47 |  |  | 949.02 |  |  | 926.39 | [9 empty] | 930.06 |  |  | 9501.81
EAF [%] |  |  |  |  | 100.00 | 72.42 |  |  |  | 17.08 |  | 85.53 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.61
UCF [%] |  |  |  |  | 100.00 | 72.42 |  |  |  | 17.08 |  | 85.53 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.61
LF [%] |  |  |  |  | 92.72 | 67.09 |  |  |  | 8.37 |  | 81.50 | [8 empty] | 105.75 |  |  | 103.58 | [6 empty] | 97.77 |  | 101.44 |  |  |  | 99.11 |  |  | 105.42 |  |  | 106.33 | [9 empty] | 103.31 |  |  | 89.40
OF [%] |  |  |  |  | 100.00 | 72.41 |  |  |  | 16.94 |  | 85.56 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.59
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 14.47 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.31
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 14.47 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.19
PUF [%] |  |  |  |  | 0.00 | 27.58 |  |  |  | 82.92 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.21
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 280971.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.83 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.83 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.24 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.14 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.61 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.83 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.32 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 7247.50 |  |  | 7857 |  |  |  | 1065 | [10 empty] | 74.81 |  |  |  | 74.81 | [5 empty] | 74.81 |  |  | 88.49 |  |  |  | 25.19 |  | 25.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 5554.30 |  |  | 6225 |  |  |  | 1065 | [10 empty] | 59.52 |  |  |  | 59.52 | [5 empty] | 59.54 |  |  | 71.06 |  |  |  | 20.60 |  | 15.45 | [8 empty] | 25.03 |  |  |  |  | 0.00
1979 |  |  |  | 5482.50 |  |  | 5704 |  |  |  | 1065 | [10 empty] | 58.77 |  |  |  | 58.77 | [5 empty] | 58.77 |  |  | 65.11 |  |  |  | 12.99 |  | 8.77 | [8 empty] | 32.46 |  |  |  |  | 0.00
1980 |  |  |  | 6936.10 |  |  | 6949 |  |  |  | 1065 | [10 empty] | 79.26 |  |  |  | 79.89 | [5 empty] | 74.14 |  |  | 79.11 |  |  |  | 10.83 |  | 9.71 | [8 empty] | 10.41 |  |  |  |  | 0.63
1981 |  |  |  | 6264.80 |  |  | 6358 |  |  |  | 1065 | [10 empty] | 72.62 |  |  |  | 72.62 | [5 empty] | 67.15 |  |  | 72.58 |  |  |  | 7.11 |  | 5.56 | [8 empty] | 21.82 |  |  |  |  | 0.00
1982 |  |  |  | 4892.80 |  |  | 5022 |  |  |  | 1065 | [10 empty] | 57.43 |  |  |  | 57.43 | [5 empty] | 52.44 |  |  | 57.33 |  |  |  | 20.46 |  | 14.77 | [8 empty] | 27.80 |  |  |  |  | 0.00
1983 |  |  |  | 5394.30 |  |  | 5417 |  |  |  | 1065 | [10 empty] | 61.87 |  |  |  | 61.87 | [5 empty] | 57.82 |  |  | 61.84 |  |  |  | 9.33 |  | 6.37 | [8 empty] | 31.76 |  |  |  |  | 0.00
1984 |  |  |  | 290.50 |  |  | 503 |  |  |  | 1065 | [10 empty] | 5.75 |  |  |  | 5.75 | [5 empty] | 3.11 |  |  | 5.73 |  |  |  | 94.19 |  | 93.15 | [8 empty] | 1.10 |  |  |  |  | 0.00
1985 |  |  |  | 1526.47 |  |  | 1496 |  |  |  | 1065 | [10 empty] | 90.78 |  |  |  | 90.78 | [5 empty] | 86.95 |  |  | 90.75 |  |  |  | 9.22 |  | 9.22 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | Data not available - Long-term shutdown
1987 |  |  |  | "
1988 |  |  |  | "
1989 |  |  |  | "
1990 |  |  |  | "
1991 |  |  |  | "
1992 |  |  |  | "
1993 |  |  |  | "
1994 |  |  |  | "
1995 |  |  |  | 764.62 |  |  | 810 |  |  |  | 1065 | [10 empty] | 79.51 |  |  |  | 79.51 | [5 empty] | 70.39 |  |  | 79.41 |  |  |  | 0.98 |  | 0.78 | [8 empty] | 19.71 |  |  |  |  | 0.00
1996 |  |  |  | 8803.50 |  |  | 8412 |  |  |  | 1065 | [10 empty] | 95.81 |  |  |  | 95.81 | [5 empty] | 94.11 |  |  | 95.77 |  |  |  | 2.65 |  | 2.61 | [8 empty] | 1.58 |  |  |  |  | 0.00
1997 |  |  |  | 8523.36 |  |  | 8302 |  |  |  | 1065 | [10 empty] | 94.78 |  |  |  | 94.78 | [5 empty] | 91.36 |  |  | 94.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.22 |  |  |  |  | 0.00
1998 |  |  |  | 7884.88 |  |  | 7863 |  |  |  | 1078 | [10 empty] | 89.90 |  |  |  | 89.90 | [5 empty] | 83.46 |  |  | 89.76 |  |  |  | 3.56 |  | 3.32 | [8 empty] | 6.79 |  |  |  |  | 0.00
1999 |  |  |  | 9730.59 |  |  | 8760 |  |  |  | 1118 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.36 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 9097.37 |  |  | 8311 |  |  |  | 1118 | [10 empty] | 94.62 |  |  |  | 94.62 | [5 empty] | 92.64 |  |  | 94.62 |  |  |  | 0.65 |  | 0.62 | [8 empty] | 4.76 |  |  |  |  | 0.00
2001 |  |  |  | 9803.36 |  |  | 8760 |  |  |  | 1118 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.10 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 9260.08 |  |  | 8407 |  |  |  | 1118 | [10 empty] | 95.99 |  |  |  | 95.99 | [5 empty] | 94.55 |  |  | 95.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.01 |  |  |  |  | 0.00
2003 |  |  |  | 9325.73 |  |  | 8463 |  |  |  | 1118 | [10 empty] | 96.62 |  |  |  | 96.62 | [5 empty] | 95.22 |  |  | 96.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.38 |  |  |  |  | 0.00
2004 |  |  |  | 8701.83 |  |  | 8000 |  |  |  | 1118 | [10 empty] | 91.12 |  |  |  | 91.12 | [5 empty] | 88.61 |  |  | 91.07 |  |  |  | 0.68 |  | 0.62 | [8 empty] | 8.26 |  |  |  |  | 0.00
2005 |  |  |  | 9153.72 |  |  | 8384 |  |  |  | 1114 | [10 empty] | 95.73 |  |  |  | 96.18 | [5 empty] | 93.80 |  |  | 95.71 |  |  |  | 3.82 |  | 3.82 | [8 empty] | 0.00 |  |  |  |  | 0.45
2006 |  |  |  | 8638.83 |  |  | 7974 |  |  |  | 1114 | [10 empty] | 91.08 |  |  |  | 91.08 | [5 empty] | 88.29 |  |  | 91.03 |  |  |  | 2.94 |  | 2.76 | [8 empty] | 6.16 |  |  |  |  | 0.00
2007 |  |  |  | 9086.06 |  |  | 8372 |  |  |  | 1105 | [10 empty] | 95.57 |  |  |  | 95.57 | [5 empty] | 93.87 |  |  | 95.57 |  |  |  | 1.14 |  | 1.10 | [8 empty] | 3.33 |  |  |  |  | 0.00
2008 |  |  |  | 7300.59 |  |  | 6794 |  |  |  | 1104 | [10 empty] | 76.35 |  |  |  | 76.35 | [5 empty] | 75.27 |  |  | 77.35 |  |  |  | 6.87 |  | 5.63 | [8 empty] | 18.02 |  |  |  |  | 0.00
2009 |  |  |  | 9175.41 |  |  | 8433 |  |  |  | 1104 | [10 empty] | 95.86 |  |  |  | 95.86 | [5 empty] | 94.88 |  |  | 96.27 |  |  |  | 1.96 |  | 1.92 | [8 empty] | 2.22 |  |  |  |  | 0.00
2010 |  |  |  | 7858.11 |  |  | 7625 |  |  |  | 1105 | [10 empty] | 87.08 |  |  |  | 87.08 | [5 empty] | 81.18 |  |  | 87.04 |  |  |  | 2.22 |  | 1.97 | [8 empty] | 10.95 |  |  |  |  | 0.00
2011 |  |  |  | 8451.13 |  |  | 7731 |  |  |  | 1105 | [10 empty] | 88.27 |  |  |  | 97.64 | [5 empty] | 87.31 |  |  | 88.25 |  |  |  | 2.36 |  | 2.36 | [8 empty] | 0.00 |  |  |  |  | 9.37
2012 |  |  |  | 7999.54 |  |  | 7455 |  |  |  | 1105 | [10 empty] | 84.89 |  |  |  | 84.89 | [5 empty] | 82.42 |  |  | 84.87 |  |  |  | 1.77 |  | 1.53 | [8 empty] | 13.58 |  |  |  |  | 0.00
2013 |  |  |  | 9234.30 |  |  | 8443 |  |  |  | 1105 | [10 empty] | 96.38 |  |  |  | 96.38 | [5 empty] | 95.39 |  |  | 96.37 |  |  |  | 0.90 |  | 0.87 | [8 empty] | 2.75 |  |  |  |  | 0.00
2014 |  |  |  | 8565.45 |  |  | 7911 |  |  |  | 1105 | [10 empty] | 90.31 |  |  |  | 90.31 | [5 empty] | 88.49 |  |  | 90.31 |  |  |  | 1.22 |  | 1.11 | [8 empty] | 8.58 |  |  |  |  | 0.00
2015 |  |  |  | 9623.05 |  |  | 8760 |  |  |  | 1105 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.41 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 8308.77 |  |  | 7906 |  |  |  | 1105 | [10 empty] | 90.01 |  |  |  | 90.01 | [5 empty] | 85.60 |  |  | 90.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.99 |  |  |  |  | 0.00
2017 |  |  |  | 9651.06 |  |  | 8760 |  |  |  | 1105 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.70 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 8099.12 |  |  | 7243 |  |  |  | 1105 | [10 empty] | 82.69 |  |  |  | 82.69 | [5 empty] | 83.67 |  |  | 82.68 |  |  |  | 3.26 |  | 2.79 | [8 empty] | 14.52 |  |  |  |  | 0.00
2019 |  |  |  | 10313.85 |  |  | 8390 |  |  |  | 1210 | [10 empty] | 95.79 |  |  |  | 95.79 | [5 empty] | 97.30 |  |  | 95.78 |  |  |  | 1.48 |  | 1.43 | [8 empty] | 2.78 |  |  |  |  | 0.00
2020 |  |  |  | 9501.81 |  |  | 7870 |  |  |  | 1210 | [10 empty] | 89.61 |  |  |  | 89.61 | [5 empty] | 89.40 |  |  | 89.59 |  |  |  | 1.31 |  | 1.19 | [8 empty] | 9.21 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1977 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 235
B. |  | Refuelling without maintenance | [20 empty] | 809 | [14 empty] | 24
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 684 |  |  |  | 235
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 525
E. |  | Testing of plant systems or components | [35 empty] | 6 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 2303
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 25
L. |  | Human factor related | [39 empty] | 12
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 5
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 3
Z. |  | Other | [24 empty] | 104 | [14 empty] | 13
Subtotal | [22 empty] | 809 |  |  |  | 104 | [10 empty] | 1242 |  |  |  | 2799 | [11 empty] | 30
Total | [22 empty] | 913 | [14 empty] | 4071
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1977 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 17
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 14
14. |  |  | Safety Systems | [34 empty] | 15
15. |  |  | Reactor Cooling Systems | [34 empty] | 41
31. |  |  | Turbine and auxiliaries | [34 empty] | 71
32. |  |  | Feedwater and Main Steam System | [34 empty] | 25
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 270
41. |  |  | Main Generator Systems | [34 empty] | 17
42. |  |  | Electrical Power Supply Systems | [34 empty] | 27
Total | [37 empty] | 501
Highlights (2020)
U3C19 Refueling Outage

## BRUNSWICK-1
2020 Operating Experience
US-325 | [8 empty] | BRUNSWICK-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PROGRESS (Progress Energy)
Owner | [7 empty] | : | PROG_E_C (PROGRESS ENERGY Carolinas, Inc.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-02-07
Thermal power | [12 empty] | : |  |  | 2923 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-12-04
Gross electrical power | [12 empty] | : |  |  | 990 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-03-18
Reference unit power (net) | [12 empty] | : |  |  | 938 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 285
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.44
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 27800 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.42 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 137 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6917.77 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 5.57 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.62 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.99 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.62 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.39 %
Load Factor (LF) | [18 empty] | : | 83.96 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 84.61 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1352 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 708.91 | 635.96 |  |  |  | 45.28 |  | 635.04 | [8 empty] | 716.94 |  |  | 416.19 | [6 empty] | 700.74 |  | 258.05 |  |  |  | 688.25 |  |  | 710.82 |  |  | 684.03 | [9 empty] | 717.58 |  |  | 6917.77
EAF [%] |  |  |  |  | 100.00 | 96.66 |  |  |  | 12.93 |  | 100.00 | [8 empty] | 100.00 |  |  | 66.46 | [6 empty] | 100.00 |  | 41.10 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.62
UCF [%] |  |  |  |  | 100.00 | 96.66 |  |  |  | 12.93 |  | 100.00 | [8 empty] | 100.00 |  |  | 66.46 | [6 empty] | 100.00 |  | 41.10 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.62
LF [%] |  |  |  |  | 101.58 | 97.41 |  |  |  | 6.49 |  | 94.03 | [8 empty] | 102.73 |  |  | 61.62 | [6 empty] | 100.41 |  | 36.98 |  |  |  | 101.91 |  |  | 101.85 |  |  | 101.28 | [9 empty] | 102.82 |  |  | 83.96
OF [%] |  |  |  |  | 100.00 | 96.70 |  |  |  | 12.77 |  | 100.00 | [8 empty] | 100.00 |  |  | 66.39 | [6 empty] | 100.00 |  | 41.13 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.61
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 58.90 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.57
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 58.90 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.99
PUF [%] |  |  |  |  | 0.00 | 3.34 |  |  |  | 87.07 |  | 0.00 | [8 empty] | 0.00 |  |  | 33.54 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.39
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 259494 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.71 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.95 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.8 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.25 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.95 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.32 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.3 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.29 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 2984.50 |  |  | 4949 |  |  |  | 790 | [10 empty] | 43.63 |  |  |  | 43.63 | [5 empty] | 43.63 |  |  | 54.61 |  |  |  | 56.37 |  | 56.37 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 5122.90 |  |  | 7624 |  |  |  | 790 | [10 empty] | 74.11 |  |  |  | 74.11 | [5 empty] | 74.03 |  |  | 87.03 |  |  |  | 16.75 |  | 14.91 | [8 empty] | 10.99 |  |  |  |  | 0.00
1979 |  |  |  | 3169.20 |  |  | 4778 |  |  |  | 790 | [10 empty] | 45.79 |  |  |  | 45.79 | [5 empty] | 45.80 |  |  | 54.54 |  |  |  | 25.42 |  | 15.61 | [8 empty] | 38.59 |  |  |  |  | 0.00
1980 |  |  |  | 3939.20 |  |  | 6045 |  |  |  | 790 | [10 empty] | 69.75 |  |  |  | 69.75 | [5 empty] | 56.77 |  |  | 68.82 |  |  |  | 7.13 |  | 5.36 | [8 empty] | 24.90 |  |  |  |  | 0.00
1981 |  |  |  | 2574.80 |  |  | 4155 |  |  |  | 790 | [10 empty] | 48.98 |  |  |  | 48.98 | [5 empty] | 37.21 |  |  | 47.43 |  |  |  | 12.80 |  | 7.19 | [8 empty] | 43.83 |  |  |  |  | 0.00
1982 |  |  |  | 2935.40 |  |  | 5428 |  |  |  | 790 | [10 empty] | 62.93 |  |  |  | 62.93 | [5 empty] | 42.42 |  |  | 61.96 |  |  |  | 31.61 |  | 29.09 | [8 empty] | 7.98 |  |  |  |  | 0.00
1983 |  |  |  | 1419.10 |  |  | 2116 |  |  |  | 790 | [10 empty] | 26.40 |  |  |  | 26.40 | [5 empty] | 20.51 |  |  | 24.16 |  |  |  | 5.51 |  | 1.54 | [8 empty] | 72.06 |  |  |  |  | 0.00
1984 |  |  |  | 5037.71 |  |  | 6797 |  |  |  | 790 | [10 empty] | 79.77 |  |  |  | 81.45 | [5 empty] | 72.60 |  |  | 77.38 |  |  |  | 5.30 |  | 4.56 | [8 empty] | 13.99 |  |  |  |  | 1.68
1985 |  |  |  | 1942.51 |  |  | 3247 |  |  |  | 790 | [10 empty] | 38.92 |  |  |  | 38.92 | [5 empty] | 28.07 |  |  | 37.07 |  |  |  | 3.99 |  | 1.62 | [8 empty] | 59.46 |  |  |  |  | 0.00
1986 |  |  |  | 5973.81 |  |  | 8068 |  |  |  | 790 | [10 empty] | 92.23 |  |  |  | 92.23 | [5 empty] | 86.32 |  |  | 92.10 |  |  |  | 7.77 |  | 7.77 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 4057.95 |  |  | 5651 |  |  |  | 790 | [10 empty] | 65.57 |  |  |  | 65.57 | [5 empty] | 58.64 |  |  | 64.51 |  |  |  | 3.78 |  | 2.57 | [8 empty] | 31.86 |  |  |  |  | 0.00
1988 |  |  |  | 4458.42 |  |  | 6514 |  |  |  | 790 | [10 empty] | 74.45 |  |  |  | 74.45 | [5 empty] | 64.25 |  |  | 74.16 |  |  |  | 3.73 |  | 2.89 | [8 empty] | 22.66 |  |  |  |  | 0.00
1989 |  |  |  | 4193.76 |  |  | 5568 |  |  |  | 790 | [10 empty] | 64.63 |  |  |  | 64.63 | [5 empty] | 60.60 |  |  | 63.56 |  |  |  | 10.52 |  | 7.60 | [8 empty] | 27.77 |  |  |  |  | 0.00
1990 |  |  |  | 4340.35 |  |  | 5909 |  |  |  | 790 | [10 empty] | 68.40 |  |  |  | 68.40 | [5 empty] | 62.72 |  |  | 67.45 |  |  |  | 8.16 |  | 6.07 | [8 empty] | 25.52 |  |  |  |  | 0.00
1991 |  |  |  | 4400.35 |  |  | 5849 |  |  |  | 780 | [10 empty] | 67.35 |  |  |  | 67.35 | [5 empty] | 64.37 |  |  | 66.77 |  |  |  | 20.44 |  | 17.30 | [8 empty] | 15.35 |  |  |  |  | 0.00
1992 |  |  |  | 1874.55 |  |  | 2486 |  |  |  | 767 | [10 empty] | 28.31 |  |  |  | 28.31 | [5 empty] | 27.82 |  |  | 28.30 |  |  |  | 31.05 |  | 12.75 | [8 empty] | 58.94 |  |  |  |  | 0.00
1993 |  |  |  | 0.00 |  |  | 0 |  |  |  | 767 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1994 |  |  |  | 5956.34 |  |  | 7755 |  |  |  | 767 | [10 empty] | 88.56 |  |  |  | 88.56 | [5 empty] | 88.65 |  |  | 88.53 |  |  |  | 0.22 |  | 0.19 | [8 empty] | 11.24 |  |  |  |  | 0.00
1995 |  |  |  | 5780.71 |  |  | 7391 |  |  |  | 767 | [10 empty] | 84.42 |  |  |  | 84.42 | [5 empty] | 86.04 |  |  | 84.37 |  |  |  | 2.04 |  | 1.76 | [8 empty] | 13.82 |  |  |  |  | 0.00
1996 |  |  |  | 5708.15 |  |  | 7490 |  |  |  | 767 | [10 empty] | 85.33 |  |  |  | 88.57 | [5 empty] | 84.72 |  |  | 85.27 |  |  |  | 2.52 |  | 2.29 | [8 empty] | 9.14 |  |  |  |  | 3.24
1997 |  |  |  | 6857.03 |  |  | 8558 |  |  |  | 767 | [10 empty] | 97.71 |  |  |  | 97.71 | [5 empty] | 102.06 |  |  | 97.69 |  |  |  | 2.29 |  | 2.29 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 6360.44 |  |  | 7811 |  |  |  | 820 | [10 empty] | 89.89 |  |  |  | 91.39 | [5 empty] | 88.55 |  |  | 89.17 |  |  |  | 0.10 |  | 0.10 | [8 empty] | 8.51 |  |  |  |  | 1.51
1999 |  |  |  | 6998.16 |  |  | 8481 |  |  |  | 820 | [10 empty] | 96.82 |  |  |  | 98.97 | [5 empty] | 97.42 |  |  | 96.82 |  |  |  | 1.03 |  | 1.03 | [8 empty] | 0.00 |  |  |  |  | 2.16
2000 |  |  |  | 6746.48 |  |  | 8122 |  |  |  | 820 | [10 empty] | 92.46 |  |  |  | 92.46 | [5 empty] | 93.66 |  |  | 92.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.54 |  |  |  |  | 0.00
2001 |  |  |  | 7303.12 |  |  | 8760 |  |  |  | 820 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.67 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 6697.34 |  |  | 7874 |  |  |  | 820 | [10 empty] | 89.89 |  |  |  | 89.89 | [5 empty] | 93.24 |  |  | 89.89 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 10.08 |  |  |  |  | 0.00
2003 |  |  |  | 7701.83 |  |  | 8653 |  |  |  | 872 | [10 empty] | 98.85 |  |  |  | 98.85 | [5 empty] | 100.83 |  |  | 98.78 |  |  |  | 1.15 |  | 1.15 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 7093.38 |  |  | 7853 |  |  |  | 872 | [10 empty] | 89.42 |  |  |  | 90.53 | [5 empty] | 92.61 |  |  | 89.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.47 |  |  |  |  | 1.11
2005 |  |  |  | 7755.05 |  |  | 8275 |  |  |  | 872 | [10 empty] | 94.47 |  |  |  | 94.47 | [5 empty] | 101.51 |  |  | 94.45 |  |  |  | 3.37 |  | 3.29 | [8 empty] | 2.24 |  |  |  |  | 0.00
2006 |  |  |  | 7190.78 |  |  | 7601 |  |  |  | 938 | [10 empty] | 86.80 |  |  |  | 86.80 | [5 empty] | 87.51 |  |  | 86.77 |  |  |  | 3.94 |  | 3.56 | [8 empty] | 9.63 |  |  |  |  | 0.00
2007 |  |  |  | 7881.91 |  |  | 8290 |  |  |  | 938 | [10 empty] | 94.64 |  |  |  | 94.64 | [5 empty] | 95.92 |  |  | 94.63 |  |  |  | 1.45 |  | 1.39 | [8 empty] | 3.97 |  |  |  |  | 0.00
2008 |  |  |  | 7030.63 |  |  | 7458 |  |  |  | 938 | [10 empty] | 84.92 |  |  |  | 84.92 | [5 empty] | 85.33 |  |  | 84.90 |  |  |  | 0.99 |  | 0.85 | [8 empty] | 14.22 |  |  |  |  | 0.00
2009 |  |  |  | 8022.67 |  |  | 8493 |  |  |  | 938 | [10 empty] | 96.96 |  |  |  | 96.96 | [5 empty] | 97.64 |  |  | 96.95 |  |  |  | 3.04 |  | 3.04 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 6810.87 |  |  | 7255 |  |  |  | 938 | [10 empty] | 82.84 |  |  |  | 82.84 | [5 empty] | 82.89 |  |  | 82.82 |  |  |  | 1.16 |  | 0.98 | [8 empty] | 16.19 |  |  |  |  | 0.00
2011 |  |  |  | 8228.37 |  |  | 8663 |  |  |  | 938 | [10 empty] | 98.90 |  |  |  | 98.90 | [5 empty] | 100.14 |  |  | 98.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.10 |  |  |  |  | 0.00
2012 |  |  |  | 6323.87 |  |  | 6778 |  |  |  | 938 | [10 empty] | 77.20 |  |  |  | 77.20 | [5 empty] | 76.75 |  |  | 77.16 |  |  |  | 7.03 |  | 5.83 | [8 empty] | 16.97 |  |  |  |  | 0.00
2013 |  |  |  | 8074.21 |  |  | 8483 |  |  |  | 938 | [10 empty] | 96.83 |  |  |  | 96.83 | [5 empty] | 98.25 |  |  | 96.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.17 |  |  |  |  | 0.00
2014 |  |  |  | 7347.75 |  |  | 7751 |  |  |  | 938 | [10 empty] | 88.48 |  |  |  | 88.48 | [5 empty] | 89.42 |  |  | 88.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.52 |  |  |  |  | 0.00
2015 |  |  |  | 8192.60 |  |  | 8653 |  |  |  | 938 | [10 empty] | 98.78 |  |  |  | 98.78 | [5 empty] | 99.70 |  |  | 98.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.22 |  |  |  |  | 0.00
2016 |  |  |  | 7313.54 |  |  | 7959 |  |  |  | 938 | [10 empty] | 90.60 |  |  |  | 90.60 | [5 empty] | 88.76 |  |  | 90.61 |  |  |  | 2.18 |  | 2.01 | [8 empty] | 7.39 |  |  |  |  | 0.00
2017 |  |  |  | 8179.12 |  |  | 8685 |  |  |  | 938 | [10 empty] | 99.14 |  |  |  | 99.14 | [5 empty] | 99.54 |  |  | 99.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.86 |  |  |  |  | 0.00
2018 |  |  |  | 7094.07 |  |  | 7700 |  |  |  | 938 | [10 empty] | 87.90 |  |  |  | 90.31 | [5 empty] | 86.34 |  |  | 87.90 |  |  |  | 0.78 |  | 0.71 | [8 empty] | 8.98 |  |  |  |  | 2.41
2019 |  |  |  | 7744.25 |  |  | 8211 |  |  |  | 938 | [10 empty] | 93.75 |  |  |  | 94.79 | [5 empty] | 94.25 |  |  | 93.73 |  |  |  | 5.21 |  | 5.21 | [8 empty] | 0.00 |  |  |  |  | 1.04
2020 |  |  |  | 6917.77 |  |  | 7432 |  |  |  | 938 | [10 empty] | 84.62 |  |  |  | 84.62 | [5 empty] | 83.96 |  |  | 84.61 |  |  |  | 5.57 |  | 4.99 | [8 empty] | 10.39 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1977 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 303
B. |  | Refuelling without maintenance | [20 empty] | 671 | [14 empty] | 15
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1067
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 242 | [14 empty] | 376
E. |  | Testing of plant systems or components | [35 empty] | 5 |  |  |  | 49
H. |  | Nuclear regulatory requirements | [39 empty] | 10
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 29
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 27
Z. |  | Other | [24 empty] | 438 | [14 empty] | 16
Subtotal | [22 empty] | 913 |  |  |  | 438 | [10 empty] | 1463 |  |  |  | 407 | [11 empty] | 30
Total | [22 empty] | 1351 | [14 empty] | 1900
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1977 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 12
12. |  |  | Reactor I&C Systems | [34 empty] | 17
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 26
15. |  |  | Reactor Cooling Systems | [34 empty] | 48
31. |  |  | Turbine and auxiliaries | [34 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 64
41. |  |  | Main Generator Systems | [34 empty] | 92
42. |  |  | Electrical Power Supply Systems | [34 empty] | 44
Total | [37 empty] | 355
Highlights (2020)
Refueling Outage 23 (B1R23)

## BRUNSWICK-2
2020 Operating Experience
US-324 | [8 empty] | BRUNSWICK-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PROGRESS (Progress Energy)
Owner | [7 empty] | : | PROG_E_C (PROGRESS ENERGY Carolinas, Inc.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-02-07
Thermal power | [12 empty] | : |  |  | 2923 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-04-29
Gross electrical power | [12 empty] | : |  |  | 960 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-11-03
Reference unit power (net) | [12 empty] | : |  |  | 932 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 285
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.44
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 27800 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.61 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 137 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8088.45 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.49 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.51 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.49 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.51 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 98.8 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.5 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 44 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 704.75 | 650.61 |  |  |  | 699.03 |  | 679.25 | [8 empty] | 688.62 |  |  | 665.75 | [6 empty] | 686.06 |  | 683.96 |  |  |  | 606.09 |  |  | 658.41 |  |  | 671.33 | [9 empty] | 694.59 |  |  | 8088.45
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 96.77 |  |  | 97.29 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.51
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 96.77 |  |  | 97.29 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.51
LF [%] |  |  |  |  | 101.64 | 100.30 |  |  |  | 100.81 |  | 101.22 | [8 empty] | 99.31 |  |  | 99.21 | [6 empty] | 98.94 |  | 98.64 |  |  |  | 90.32 |  |  | 94.95 |  |  | 100.04 | [9 empty] | 100.17 |  |  | 98.80
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 96.81 |  |  | 97.31 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.50
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 3.23 |  |  | 2.71 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.49
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 3.23 |  |  | 2.71 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.49
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 209082.25 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.12 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.65 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.43 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.92 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.35 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.31 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.1 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 1423.80 |  |  | 3254 |  |  |  | 804 | [10 empty] | 93.19 |  |  |  | 93.19 | [5 empty] | 58.80 |  |  | 93.17 |  |  |  | 6.81 |  | 6.81 | [8 empty] | 0.00 |  |  |  |  | 0.00
1976 |  |  |  | 2486.60 |  |  | 4911 |  |  |  | 789 | [10 empty] | 35.81 |  |  |  | 35.81 | [5 empty] | 35.88 |  |  | 55.91 |  |  |  | 48.62 |  | 33.89 | [8 empty] | 30.30 |  |  |  |  | 0.00
1977 |  |  |  | 2436.60 |  |  | 4872 |  |  |  | 790 | [10 empty] | 35.26 |  |  |  | 35.26 | [5 empty] | 35.21 |  |  | 55.62 |  |  |  | 38.79 |  | 22.35 | [8 empty] | 42.39 |  |  |  |  | 0.00
1978 |  |  |  | 4794.60 |  |  | 7018 |  |  |  | 790 | [10 empty] | 69.26 |  |  |  | 69.26 | [5 empty] | 69.28 |  |  | 80.11 |  |  |  | 25.55 |  | 23.77 | [8 empty] | 6.97 |  |  |  |  | 0.00
1979 |  |  |  | 3652.10 |  |  | 5741 |  |  |  | 790 | [10 empty] | 52.78 |  |  |  | 52.78 | [5 empty] | 52.77 |  |  | 65.54 |  |  |  | 16.97 |  | 10.79 | [8 empty] | 36.44 |  |  |  |  | 0.00
1980 |  |  |  | 1864.60 |  |  | 3086 |  |  |  | 790 | [10 empty] | 38.13 |  |  |  | 38.13 | [5 empty] | 26.87 |  |  | 35.13 |  |  |  | 21.96 |  | 10.73 | [8 empty] | 51.14 |  |  |  |  | 0.00
1981 |  |  |  | 3283.90 |  |  | 5800 |  |  |  | 790 | [10 empty] | 67.96 |  |  |  | 67.96 | [5 empty] | 47.45 |  |  | 66.21 |  |  |  | 29.31 |  | 28.17 | [8 empty] | 3.86 |  |  |  |  | 0.00
1982 |  |  |  | 1942.10 |  |  | 3378 |  |  |  | 790 | [10 empty] | 41.42 |  |  |  | 41.42 | [5 empty] | 28.06 |  |  | 38.56 |  |  |  | 27.98 |  | 16.09 | [8 empty] | 42.48 |  |  |  |  | 0.00
1983 |  |  |  | 3941.70 |  |  | 5630 |  |  |  | 790 | [10 empty] | 65.29 |  |  |  | 65.29 | [5 empty] | 56.96 |  |  | 64.27 |  |  |  | 28.98 |  | 26.64 | [8 empty] | 8.07 |  |  |  |  | 0.00
1984 |  |  |  | 1429.01 |  |  | 2236 |  |  |  | 790 | [10 empty] | 28.90 |  |  |  | 28.90 | [5 empty] | 20.59 |  |  | 25.46 |  |  |  | 28.94 |  | 11.77 | [8 empty] | 59.33 |  |  |  |  | 0.00
1985 |  |  |  | 5021.91 |  |  | 6983 |  |  |  | 790 | [10 empty] | 80.01 |  |  |  | 84.09 | [5 empty] | 72.57 |  |  | 79.71 |  |  |  | 4.59 |  | 4.05 | [8 empty] | 11.86 |  |  |  |  | 4.08
1986 |  |  |  | 2933.07 |  |  | 4027 |  |  |  | 790 | [10 empty] | 48.47 |  |  |  | 48.47 | [5 empty] | 42.38 |  |  | 45.97 |  |  |  | 2.96 |  | 1.48 | [8 empty] | 50.05 |  |  |  |  | 0.00
1987 |  |  |  | 5694.10 |  |  | 8203 |  |  |  | 790 | [10 empty] | 93.96 |  |  |  | 93.96 | [5 empty] | 82.28 |  |  | 93.64 |  |  |  | 5.00 |  | 4.94 | [8 empty] | 1.10 |  |  |  |  | 0.00
1988 |  |  |  | 3929.22 |  |  | 5361 |  |  |  | 790 | [10 empty] | 62.80 |  |  |  | 62.80 | [5 empty] | 56.62 |  |  | 61.03 |  |  |  | 6.30 |  | 4.22 | [8 empty] | 32.98 |  |  |  |  | 0.00
1989 |  |  |  | 4195.43 |  |  | 5763 |  |  |  | 790 | [10 empty] | 67.36 |  |  |  | 67.36 | [5 empty] | 60.62 |  |  | 65.79 |  |  |  | 4.03 |  | 2.83 | [8 empty] | 29.81 |  |  |  |  | 0.00
1990 |  |  |  | 4067.43 |  |  | 5616 |  |  |  | 790 | [10 empty] | 66.07 |  |  |  | 66.07 | [5 empty] | 58.77 |  |  | 64.11 |  |  |  | 16.62 |  | 13.17 | [8 empty] | 20.76 |  |  |  |  | 0.00
1991 |  |  |  | 3664.18 |  |  | 4959 |  |  |  | 775 | [10 empty] | 57.79 |  |  |  | 57.79 | [5 empty] | 53.98 |  |  | 56.61 |  |  |  | 17.90 |  | 12.60 | [8 empty] | 29.61 |  |  |  |  | 0.00
1992 |  |  |  | 1315.10 |  |  | 2200 |  |  |  | 754 | [10 empty] | 25.06 |  |  |  | 25.06 | [5 empty] | 19.86 |  |  | 25.05 |  |  |  | 18.45 |  | 5.67 | [8 empty] | 69.27 |  |  |  |  | 0.00
1993 |  |  |  | 4000.88 |  |  | 5525 |  |  |  | 754 | [10 empty] | 63.07 |  |  |  | 63.07 | [5 empty] | 60.57 |  |  | 63.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.93 |  |  |  |  | 0.00
1994 |  |  |  | 4823.21 |  |  | 6436 |  |  |  | 754 | [10 empty] | 73.49 |  |  |  | 73.49 | [5 empty] | 73.02 |  |  | 73.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.51 |  |  |  |  | 0.00
1995 |  |  |  | 6215.96 |  |  | 8760 |  |  |  | 754 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 94.11 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 5188.12 |  |  | 7277 |  |  |  | 754 | [10 empty] | 82.90 |  |  |  | 86.90 | [5 empty] | 78.33 |  |  | 82.84 |  |  |  | 2.68 |  | 2.39 | [8 empty] | 10.71 |  |  |  |  | 4.00
1997 |  |  |  | 6055.38 |  |  | 7816 |  |  |  | 754 | [10 empty] | 89.25 |  |  |  | 89.25 | [5 empty] | 91.68 |  |  | 89.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.75 |  |  |  |  | 0.00
1998 |  |  |  | 6963.48 |  |  | 8539 |  |  |  | 811 | [10 empty] | 97.66 |  |  |  | 98.93 | [5 empty] | 98.02 |  |  | 97.48 |  |  |  | 1.07 |  | 1.07 | [8 empty] | 0.00 |  |  |  |  | 1.26
1999 |  |  |  | 6095.17 |  |  | 7577 |  |  |  | 811 | [10 empty] | 86.50 |  |  |  | 89.24 | [5 empty] | 85.79 |  |  | 86.50 |  |  |  | 7.18 |  | 6.90 | [8 empty] | 3.86 |  |  |  |  | 2.74
2000 |  |  |  | 7055.01 |  |  | 8616 |  |  |  | 811 | [10 empty] | 98.09 |  |  |  | 98.09 | [5 empty] | 99.03 |  |  | 98.09 |  |  |  | 1.91 |  | 1.91 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 6540.43 |  |  | 7996 |  |  |  | 811 | [10 empty] | 91.29 |  |  |  | 91.29 | [5 empty] | 92.06 |  |  | 91.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.71 |  |  |  |  | 0.00
2002 |  |  |  | 7078.62 |  |  | 8609 |  |  |  | 811 | [10 empty] | 98.28 |  |  |  | 98.28 | [5 empty] | 99.64 |  |  | 98.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.72 |  |  |  |  | 0.00
2003 |  |  |  | 7028.09 |  |  | 7966 |  |  |  | 811 | [10 empty] | 90.97 |  |  |  | 90.97 | [5 empty] | 98.93 |  |  | 90.94 |  |  |  | 1.60 |  | 1.47 | [8 empty] | 7.56 |  |  |  |  | 0.00
2004 |  |  |  | 7756.76 |  |  | 8639 |  |  |  | 900 | [10 empty] | 98.53 |  |  |  | 98.53 | [5 empty] | 98.12 |  |  | 98.35 |  |  |  | 0.86 |  | 0.85 | [8 empty] | 0.62 |  |  |  |  | 0.00
2005 |  |  |  | 6781.70 |  |  | 7724 |  |  |  | 811 | [10 empty] | 88.19 |  |  |  | 88.19 | [5 empty] | 95.45 |  |  | 88.16 |  |  |  | 3.10 |  | 2.82 | [8 empty] | 8.99 |  |  |  |  | 0.00
2006 |  |  |  | 7361.27 |  |  | 7972 |  |  |  | 937 | [10 empty] | 91.02 |  |  |  | 91.02 | [5 empty] | 89.68 |  |  | 91.00 |  |  |  | 6.35 |  | 6.17 | [8 empty] | 2.81 |  |  |  |  | 0.00
2007 |  |  |  | 7140.26 |  |  | 7645 |  |  |  | 937 | [10 empty] | 87.28 |  |  |  | 87.28 | [5 empty] | 86.99 |  |  | 87.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.72 |  |  |  |  | 0.00
2008 |  |  |  | 7854.24 |  |  | 8448 |  |  |  | 937 | [10 empty] | 96.18 |  |  |  | 96.18 | [5 empty] | 95.43 |  |  | 96.17 |  |  |  | 3.82 |  | 3.82 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 6410.20 |  |  | 7060 |  |  |  | 920 | [10 empty] | 80.27 |  |  |  | 80.27 | [5 empty] | 79.54 |  |  | 80.59 |  |  |  | 3.43 |  | 2.85 | [8 empty] | 16.88 |  |  |  |  | 0.00
2010 |  |  |  | 8000.04 |  |  | 8639 |  |  |  | 920 | [10 empty] | 98.63 |  |  |  | 98.63 | [5 empty] | 99.27 |  |  | 98.62 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 1.28 |  |  |  |  | 0.00
2011 |  |  |  | 6336.69 |  |  | 6995 |  |  |  | 920 | [10 empty] | 79.88 |  |  |  | 79.88 | [5 empty] | 78.63 |  |  | 79.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.12 |  |  |  |  | 0.00
2012 |  |  |  | 7987.81 |  |  | 8704 |  |  |  | 920 | [10 empty] | 99.10 |  |  |  | 99.10 | [5 empty] | 98.84 |  |  | 99.09 |  |  |  | 0.90 |  | 0.90 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 6385.33 |  |  | 7059 |  |  |  | 920 | [10 empty] | 80.58 |  |  |  | 80.58 | [5 empty] | 79.22 |  |  | 80.57 |  |  |  | 1.25 |  | 1.02 | [8 empty] | 18.40 |  |  |  |  | 0.00
2014 |  |  |  | 7987.55 |  |  | 8715 |  |  |  | 920 | [10 empty] | 99.48 |  |  |  | 99.48 | [5 empty] | 99.11 |  |  | 99.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.52 |  |  |  |  | 0.00
2015 |  |  |  | 7098.43 |  |  | 7704 |  |  |  | 920 | [10 empty] | 87.92 |  |  |  | 87.92 | [5 empty] | 88.08 |  |  | 87.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.08 |  |  |  |  | 0.00
2016 |  |  |  | 8075.19 |  |  | 8784 |  |  |  | 920 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.92 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7191.04 |  |  | 8010 |  |  |  | 920 | [10 empty] | 91.44 |  |  |  | 91.44 | [5 empty] | 89.23 |  |  | 91.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.56 |  |  |  |  | 0.00
2018 |  |  |  | 7532.90 |  |  | 8453 |  |  |  | 932 | [10 empty] | 96.50 |  |  |  | 98.23 | [5 empty] | 92.27 |  |  | 96.50 |  |  |  | 0.41 |  | 0.41 | [8 empty] | 1.36 |  |  |  |  | 1.74
2019 |  |  |  | 6972.51 |  |  | 7689 |  |  |  | 932 | [10 empty] | 87.79 |  |  |  | 88.42 | [5 empty] | 85.40 |  |  | 87.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.58 |  |  |  |  | 0.64
2020 |  |  |  | 8088.45 |  |  | 8740 |  |  |  | 932 | [10 empty] | 99.51 |  |  |  | 99.51 | [5 empty] | 98.80 |  |  | 99.50 |  |  |  | 0.49 |  | 0.49 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 513
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1039
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 313
E. |  | Testing of plant systems or components | [35 empty] | 10 |  |  |  | 3
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 5
L. |  | Human factor related | [39 empty] | 39
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 27
Z. |  | Other | [24 empty] | 43 | [14 empty] | 5 | [11 empty] | 1
Subtotal | [26 empty] | 43 | [10 empty] | 1362 |  |  |  | 565 | [11 empty] | 28
Total | [22 empty] | 43 | [14 empty] | 1955
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 18
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 29
15. |  |  | Reactor Cooling Systems | [34 empty] | 195
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 23
31. |  |  | Turbine and auxiliaries | [34 empty] | 68
32. |  |  | Feedwater and Main Steam System | [34 empty] | 42
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 14
41. |  |  | Main Generator Systems | [34 empty] | 32
42. |  |  | Electrical Power Supply Systems | [34 empty] | 61
Total | [37 empty] | 511
Highlights (2020)
Turbine offline to repair main generator phase 'C' no-load disconnect switch. Phase 'B' also repaired to prevent further downpowers from this issue

## BYRON-1
2020 Operating Experience
US-454 | [8 empty] | BYRON-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-04-01
Thermal power | [12 empty] | : |  |  | 3645 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-03-01
Gross electrical power | [12 empty] | : |  |  | 1242 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-09-16
Reference unit power (net) | [12 empty] | : |  |  | 1164 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 43 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 49000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.63
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 25 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9853.74 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.95 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.95 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.05 %
Load Factor (LF) | [18 empty] | : | 96.37 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 94.93 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 445 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 900.05 | 815.75 |  |  |  | 275.84 |  | 866.14 | [8 empty] | 888.16 |  |  | 850.58 | [6 empty] | 873.14 |  | 877.58 |  |  |  | 855.88 |  |  | 891.00 |  |  | 863.41 | [9 empty] | 896.22 |  |  | 9853.74
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 40.38 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.95
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 40.38 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.95
LF [%] |  |  |  |  | 103.93 | 100.69 |  |  |  | 31.85 |  | 103.35 | [8 empty] | 102.56 |  |  | 101.49 | [6 empty] | 100.82 |  | 101.33 |  |  |  | 102.12 |  |  | 102.88 |  |  | 103.02 | [9 empty] | 103.49 |  |  | 96.37
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 40.19 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.93
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 59.62 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.05
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 376681.15 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.81 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.07 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.74 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.14 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.12 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.9 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.08 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.97 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 1696.12 |  |  | 2025 |  |  |  | 1124 | [10 empty] | 41.27 |  |  |  | 41.27 | [5 empty] | 31.22 |  |  | 40.74 |  |  |  | 3.54 |  | 1.51 | [8 empty] | 57.21 |  |  |  |  | 0.00
1986 |  |  |  | 7396.00 |  |  | 7760 |  |  |  | 1129 | [10 empty] | 89.09 |  |  |  | 89.09 | [5 empty] | 74.78 |  |  | 88.58 |  |  |  | 7.52 |  | 7.24 | [8 empty] | 3.67 |  |  |  |  | 0.00
1987 |  |  |  | 5355.66 |  |  | 6005 |  |  |  | 1125 | [10 empty] | 68.74 |  |  |  | 69.62 | [5 empty] | 54.33 |  |  | 68.55 |  |  |  | 0.92 |  | 0.64 | [8 empty] | 29.74 |  |  |  |  | 0.89
1988 |  |  |  | 6303.67 |  |  | 6393 |  |  |  | 1112 | [10 empty] | 72.90 |  |  |  | 72.90 | [5 empty] | 64.51 |  |  | 72.78 |  |  |  | 1.88 |  | 1.40 | [8 empty] | 25.71 |  |  |  |  | 0.00
1989 |  |  |  | 8945.52 |  |  | 8737 |  |  |  | 1105 | [10 empty] | 99.74 |  |  |  | 99.74 | [5 empty] | 92.41 |  |  | 99.74 |  |  |  | 0.26 |  | 0.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 6951.66 |  |  | 7059 |  |  |  | 1105 | [10 empty] | 80.33 |  |  |  | 80.33 | [5 empty] | 71.82 |  |  | 80.58 |  |  |  | 2.95 |  | 2.44 | [8 empty] | 17.23 |  |  |  |  | 0.00
1991 |  |  |  | 6318.07 |  |  | 7148 |  |  |  | 1105 | [10 empty] | 81.35 |  |  |  | 81.35 | [5 empty] | 65.27 |  |  | 81.60 |  |  |  | 1.07 |  | 0.88 | [8 empty] | 17.77 |  |  |  |  | 0.00
1992 |  |  |  | 8986.36 |  |  | 8723 |  |  |  | 1105 | [10 empty] | 99.30 |  |  |  | 99.30 | [5 empty] | 92.58 |  |  | 99.31 |  |  |  | 0.70 |  | 0.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 7366.86 |  |  | 7104 |  |  |  | 1105 | [10 empty] | 80.85 |  |  |  | 80.85 | [5 empty] | 76.11 |  |  | 81.10 |  |  |  | 1.34 |  | 1.10 | [8 empty] | 18.05 |  |  |  |  | 0.00
1994 |  |  |  | 6801.55 |  |  | 7136 |  |  |  | 1105 | [10 empty] | 81.24 |  |  |  | 81.24 | [5 empty] | 70.27 |  |  | 81.46 |  |  |  | 4.04 |  | 3.42 | [8 empty] | 15.33 |  |  |  |  | 0.00
1995 |  |  |  | 7706.54 |  |  | 7228 |  |  |  | 1105 | [10 empty] | 82.30 |  |  |  | 82.30 | [5 empty] | 79.61 |  |  | 82.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.70 |  |  |  |  | 0.00
1996 |  |  |  | 6871.06 |  |  | 6588 |  |  |  | 1105 | [10 empty] | 74.70 |  |  |  | 74.70 | [5 empty] | 70.79 |  |  | 75.00 |  |  |  | 0.58 |  | 0.44 | [8 empty] | 24.87 |  |  |  |  | 0.00
1997 |  |  |  | 7161.73 |  |  | 6737 |  |  |  | 1105 | [10 empty] | 76.78 |  |  |  | 76.78 | [5 empty] | 73.99 |  |  | 76.91 |  |  |  | 2.97 |  | 2.35 | [8 empty] | 20.87 |  |  |  |  | 0.00
1998 |  |  |  | 7804.60 |  |  | 7145 |  |  |  | 1105 | [10 empty] | 81.54 |  |  |  | 81.54 | [5 empty] | 80.63 |  |  | 81.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.46 |  |  |  |  | 0.00
1999 |  |  |  | 8908.49 |  |  | 7944 |  |  |  | 1105 | [10 empty] | 90.59 |  |  |  | 90.59 | [5 empty] | 92.03 |  |  | 90.68 |  |  |  | 1.47 |  | 1.35 | [8 empty] | 8.06 |  |  |  |  | 0.00
2000 |  |  |  | 9291.86 |  |  | 8284 |  |  |  | 1105 | [10 empty] | 94.24 |  |  |  | 94.24 | [5 empty] | 95.73 |  |  | 94.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.76 |  |  |  |  | 0.00
2001 |  |  |  | 10389.90 |  |  | 8760 |  |  |  | 1163 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 104.13 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 9827.85 |  |  | 8256 |  |  |  | 1163 | [10 empty] | 94.08 |  |  |  | 94.08 | [5 empty] | 96.47 |  |  | 94.25 |  |  |  | 0.76 |  | 0.72 | [8 empty] | 5.20 |  |  |  |  | 0.00
2003 |  |  |  | 9858.83 |  |  | 8248 |  |  |  | 1163 | [10 empty] | 94.01 |  |  |  | 94.01 | [5 empty] | 96.77 |  |  | 94.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.99 |  |  |  |  | 0.00
2004 |  |  |  | 10381.33 |  |  | 8784 |  |  |  | 1152 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.19 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 9589.71 |  |  | 8135 |  |  |  | 1194 | [10 empty] | 92.88 |  |  |  | 92.88 | [5 empty] | 91.67 |  |  | 92.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.12 |  |  |  |  | 0.00
2006 |  |  |  | 9317.03 |  |  | 7914 |  |  |  | 1164 | [10 empty] | 90.35 |  |  |  | 90.35 | [5 empty] | 91.37 |  |  | 90.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.65 |  |  |  |  | 0.00
2007 |  |  |  | 10024.16 |  |  | 8482 |  |  |  | 1164 | [10 empty] | 96.83 |  |  |  | 96.83 | [5 empty] | 98.31 |  |  | 96.83 |  |  |  | 3.17 |  | 3.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 9733.36 |  |  | 8266 |  |  |  | 1164 | [10 empty] | 94.11 |  |  |  | 94.11 | [5 empty] | 95.20 |  |  | 94.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.89 |  |  |  |  | 0.00
2009 |  |  |  | 9609.39 |  |  | 8169 |  |  |  | 1164 | [10 empty] | 93.26 |  |  |  | 93.26 | [5 empty] | 94.24 |  |  | 93.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.74 |  |  |  |  | 0.00
2010 |  |  |  | 10337.29 |  |  | 8760 |  |  |  | 1164 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.38 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8978.80 |  |  | 7759 |  |  |  | 1164 | [10 empty] | 88.58 |  |  |  | 88.58 | [5 empty] | 88.06 |  |  | 88.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.42 |  |  |  |  | 0.00
2012 |  |  |  | 8925.08 |  |  | 7984 |  |  |  | 1164 | [10 empty] | 90.91 |  |  |  | 90.91 | [5 empty] | 87.29 |  |  | 90.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.09 |  |  |  |  | 0.00
2013 |  |  |  | 10283.27 |  |  | 8760 |  |  |  | 1164 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.84 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 9879.89 |  |  | 8328 |  |  |  | 1164 | [10 empty] | 95.06 |  |  |  | 95.06 | [5 empty] | 96.89 |  |  | 95.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.94 |  |  |  |  | 0.00
2015 |  |  |  | 9456.59 |  |  | 8158 |  |  |  | 1164 | [10 empty] | 93.12 |  |  |  | 94.88 | [5 empty] | 92.74 |  |  | 93.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.12 |  |  |  |  | 1.76
2016 |  |  |  | 10356.72 |  |  | 8784 |  |  |  | 1164 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.29 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 9593.03 |  |  | 8098 |  |  |  | 1164 | [10 empty] | 92.45 |  |  |  | 92.45 | [5 empty] | 94.08 |  |  | 92.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.55 |  |  |  |  | 0.00
2018 |  |  |  | 9868.77 |  |  | 8385 |  |  |  | 1164 | [10 empty] | 95.74 |  |  |  | 95.74 | [5 empty] | 96.78 |  |  | 95.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.26 |  |  |  |  | 0.00
2019 |  |  |  | 10459.12 |  |  | 8760 |  |  |  | 1164 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.57 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9853.74 |  |  | 8339 |  |  |  | 1164 | [10 empty] | 94.95 |  |  |  | 94.95 | [5 empty] | 96.37 |  |  | 94.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.05 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 47
B. |  | Refuelling without maintenance | [20 empty] | 444 | [14 empty] | 23
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 655
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 124
E. |  | Testing of plant systems or components | [39 empty] | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 10
L. |  | Human factor related | [39 empty] | 7
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 8
Z. |  | Other | [35 empty] | 3 |  |  |  | 2
Subtotal | [22 empty] | 444 | [14 empty] | 805 |  |  |  | 66 | [11 empty] | 8
Total | [22 empty] | 444 | [14 empty] | 879
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 2
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 50
Highlights (2020)
Refueling Outage 23 (B1R23)

## BYRON-2
2020 Operating Experience
US-455 | [8 empty] | BYRON-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-04-01
Thermal power | [12 empty] | : |  |  | 3645 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-02-06
Gross electrical power | [12 empty] | : |  |  | 1210 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-08-02
Reference unit power (net) | [12 empty] | : |  |  | 1136 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 43 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 49000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.63
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 25 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9671.16 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.98 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.02 %
Load Factor (LF) | [18 empty] | : | 96.92 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 95.97 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 354 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 873.47 | 816.99 |  |  |  | 868.97 |  | 841.54 | [8 empty] | 854.78 |  |  | 826.16 | [6 empty] | 851.13 |  | 854.90 |  |  |  | 764.27 |  |  | 396.03 |  |  | 846.59 | [9 empty] | 876.36 |  |  | 9671.16
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 52.56 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.98
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 52.56 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.98
LF [%] |  |  |  |  | 103.35 | 103.33 |  |  |  | 102.81 |  | 102.89 | [8 empty] | 101.13 |  |  | 101.01 | [6 empty] | 100.70 |  | 101.15 |  |  |  | 93.44 |  |  | 46.86 |  |  | 103.50 | [9 empty] | 103.69 |  |  | 96.92
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 52.55 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.97
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 47.44 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.02
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 297572.98 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.85 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 93.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.8 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.09 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.11 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 90.77 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 92.65 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 3876.06 |  |  | 5071 |  |  |  | 1128 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 47.54 |  |  | 62.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 6357.92 |  |  | 8419 |  |  |  | 1112 | [10 empty] | 95.86 |  |  |  | 95.86 | [5 empty] | 65.06 |  |  | 95.84 |  |  |  | 2.04 |  | 1.99 | [8 empty] | 2.14 |  |  |  |  | 0.00
1989 |  |  |  | 6069.54 |  |  | 6981 |  |  |  | 1105 | [10 empty] | 79.46 |  |  |  | 79.46 | [5 empty] | 62.70 |  |  | 79.69 |  |  |  | 4.88 |  | 4.08 | [8 empty] | 16.46 |  |  |  |  | 0.00
1990 |  |  |  | 6052.68 |  |  | 6598 |  |  |  | 1105 | [10 empty] | 75.00 |  |  |  | 75.00 | [5 empty] | 62.53 |  |  | 75.32 |  |  |  | 1.02 |  | 0.78 | [8 empty] | 24.23 |  |  |  |  | 0.00
1991 |  |  |  | 8772.68 |  |  | 8489 |  |  |  | 1105 | [10 empty] | 96.89 |  |  |  | 96.89 | [5 empty] | 90.63 |  |  | 96.91 |  |  |  | 3.11 |  | 3.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 7000.34 |  |  | 7027 |  |  |  | 1105 | [10 empty] | 79.76 |  |  |  | 79.76 | [5 empty] | 72.12 |  |  | 80.00 |  |  |  | 1.27 |  | 1.03 | [8 empty] | 19.21 |  |  |  |  | 0.00
1993 |  |  |  | 7622.47 |  |  | 7399 |  |  |  | 1105 | [10 empty] | 84.26 |  |  |  | 84.26 | [5 empty] | 78.75 |  |  | 84.46 |  |  |  | 1.35 |  | 1.16 | [8 empty] | 14.58 |  |  |  |  | 0.00
1994 |  |  |  | 9504.17 |  |  | 8704 |  |  |  | 1105 | [10 empty] | 99.36 |  |  |  | 99.36 | [5 empty] | 98.19 |  |  | 99.36 |  |  |  | 0.64 |  | 0.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 8183.77 |  |  | 7710 |  |  |  | 1105 | [10 empty] | 87.87 |  |  |  | 87.87 | [5 empty] | 84.54 |  |  | 88.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.13 |  |  |  |  | 0.00
1996 |  |  |  | 7830.62 |  |  | 7225 |  |  |  | 1105 | [10 empty] | 82.05 |  |  |  | 82.05 | [5 empty] | 80.68 |  |  | 82.25 |  |  |  | 5.51 |  | 4.79 | [8 empty] | 13.17 |  |  |  |  | 0.00
1997 |  |  |  | 9102.89 |  |  | 8344 |  |  |  | 1105 | [10 empty] | 95.21 |  |  |  | 95.21 | [5 empty] | 94.04 |  |  | 95.25 |  |  |  | 0.44 |  | 0.42 | [8 empty] | 4.37 |  |  |  |  | 0.00
1998 |  |  |  | 8592.83 |  |  | 7855 |  |  |  | 1105 | [10 empty] | 89.54 |  |  |  | 89.54 | [5 empty] | 88.76 |  |  | 89.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.46 |  |  |  |  | 0.00
1999 |  |  |  | 9174.10 |  |  | 8182 |  |  |  | 1105 | [10 empty] | 93.32 |  |  |  | 93.32 | [5 empty] | 94.78 |  |  | 93.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.68 |  |  |  |  | 0.00
2000 |  |  |  | 10005.38 |  |  | 8724 |  |  |  | 1105 | [10 empty] | 99.32 |  |  |  | 99.32 | [5 empty] | 103.08 |  |  | 99.32 |  |  |  | 0.68 |  | 0.68 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 9826.73 |  |  | 8353 |  |  |  | 1131 | [10 empty] | 95.30 |  |  |  | 95.30 | [5 empty] | 100.14 |  |  | 95.35 |  |  |  | 0.33 |  | 0.31 | [8 empty] | 4.38 |  |  |  |  | 0.00
2002 |  |  |  | 9537.62 |  |  | 8119 |  |  |  | 1131 | [10 empty] | 92.31 |  |  |  | 92.31 | [5 empty] | 96.27 |  |  | 92.68 |  |  |  | 1.72 |  | 1.62 | [8 empty] | 6.07 |  |  |  |  | 0.00
2003 |  |  |  | 10298.69 |  |  | 8760 |  |  |  | 1131 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.95 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 9623.24 |  |  | 8360 |  |  |  | 1125 | [10 empty] | 95.04 |  |  |  | 95.04 | [5 empty] | 97.17 |  |  | 95.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.96 |  |  |  |  | 0.00
2005 |  |  |  | 9521.05 |  |  | 8328 |  |  |  | 1162 | [10 empty] | 95.08 |  |  |  | 95.08 | [5 empty] | 93.54 |  |  | 95.07 |  |  |  | 0.35 |  | 0.33 | [8 empty] | 4.59 |  |  |  |  | 0.00
2006 |  |  |  | 10158.74 |  |  | 8760 |  |  |  | 1136 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.08 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 8828.60 |  |  | 7736 |  |  |  | 1136 | [10 empty] | 88.33 |  |  |  | 88.33 | [5 empty] | 88.72 |  |  | 88.31 |  |  |  | 3.34 |  | 3.05 | [8 empty] | 8.62 |  |  |  |  | 0.00
2008 |  |  |  | 9624.16 |  |  | 8339 |  |  |  | 1136 | [10 empty] | 94.94 |  |  |  | 94.94 | [5 empty] | 96.45 |  |  | 94.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.06 |  |  |  |  | 0.00
2009 |  |  |  | 10108.89 |  |  | 8760 |  |  |  | 1136 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.58 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 9518.42 |  |  | 8300 |  |  |  | 1136 | [10 empty] | 94.76 |  |  |  | 94.76 | [5 empty] | 95.65 |  |  | 94.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.24 |  |  |  |  | 0.00
2011 |  |  |  | 9223.94 |  |  | 8115 |  |  |  | 1136 | [10 empty] | 92.65 |  |  |  | 92.65 | [5 empty] | 92.69 |  |  | 92.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.35 |  |  |  |  | 0.00
2012 |  |  |  | 9393.22 |  |  | 8536 |  |  |  | 1136 | [10 empty] | 97.19 |  |  |  | 97.19 | [5 empty] | 94.13 |  |  | 97.18 |  |  |  | 2.19 |  | 2.17 | [8 empty] | 0.64 |  |  |  |  | 0.00
2013 |  |  |  | 9263.79 |  |  | 8160 |  |  |  | 1136 | [10 empty] | 93.15 |  |  |  | 93.15 | [5 empty] | 93.08 |  |  | 93.14 |  |  |  | 0.52 |  | 0.49 | [8 empty] | 6.36 |  |  |  |  | 0.00
2014 |  |  |  | 9372.50 |  |  | 8158 |  |  |  | 1136 | [10 empty] | 93.13 |  |  |  | 93.13 | [5 empty] | 94.18 |  |  | 93.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.87 |  |  |  |  | 0.00
2015 |  |  |  | 10015.44 |  |  | 8760 |  |  |  | 1136 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.64 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 9243.53 |  |  | 8064 |  |  |  | 1136 | [10 empty] | 91.80 |  |  |  | 91.80 | [5 empty] | 92.63 |  |  | 91.80 |  |  |  | 0.23 |  | 0.21 | [8 empty] | 7.99 |  |  |  |  | 0.00
2017 |  |  |  | 9560.01 |  |  | 8295 |  |  |  | 1136 | [10 empty] | 94.69 |  |  |  | 94.69 | [5 empty] | 96.07 |  |  | 94.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.31 |  |  |  |  | 0.00
2018 |  |  |  | 10182.25 |  |  | 8760 |  |  |  | 1136 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.32 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 9658.86 |  |  | 8372 |  |  |  | 1136 | [10 empty] | 95.58 |  |  |  | 95.58 | [5 empty] | 97.06 |  |  | 95.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.42 |  |  |  |  | 0.00
2020 |  |  |  | 9671.16 |  |  | 8430 |  |  |  | 1136 | [10 empty] | 95.98 |  |  |  | 95.98 | [5 empty] | 96.92 |  |  | 95.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.02 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 58
B. |  | Refuelling without maintenance | [20 empty] | 353 | [14 empty] | 11
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 497
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 32
H. |  | Nuclear regulatory requirements | [39 empty] | 8
Z. |  | Other | [39 empty] | 5
Subtotal | [22 empty] | 353 | [14 empty] | 540 |  |  |  | 71
Total | [22 empty] | 353 | [14 empty] | 611
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 7
16. |  |  | Steam generation systems | [34 empty] | 13
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 7
42. |  |  | Electrical Power Supply Systems | [34 empty] | 6
Total | [37 empty] | 58
Highlights (2020)
Refueling Outage B2R22

## CALLAWAY-1
2020 Operating Experience
US-483 | [8 empty] | CALLAWAY-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | AmerenUE (AMEREN UE, Union Electric Company)
Owner | [7 empty] | : | AmerenUE (AMEREN UE, Union Electric Company)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-09-01
Thermal power | [12 empty] | : |  |  | 3565 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-10-24
Gross electrical power | [12 empty] | : |  |  | 1275 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-12-19
Reference unit power (net) | [12 empty] | : |  |  | 1215 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.34
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 42000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.78
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19.13 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7742.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.68 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.93 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.68 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.93 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.39 %
Load Factor (LF) | [18 empty] | : | 72.54 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 73.74 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2307 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 937.23 | 844.72 |  |  |  | 885.73 |  | 777.26 | [8 empty] | 907.01 |  |  | 862.35 | [6 empty] | 887.51 |  | 892.76 |  |  |  | 748.77 |  |  | 0.00 |  |  | 0.00 | [9 empty] | -1.22 |  |  | 7742.12
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 93.06 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 86.95 |  |  | 13.98 |  |  | 0.00 | [9 empty] | 6.16 |  |  | 74.93
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 93.06 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 86.95 |  |  | 13.98 |  |  | 0.00 | [9 empty] | 6.16 |  |  | 74.93
LF [%] |  |  |  |  | 103.68 | 99.89 |  |  |  | 97.98 |  | 88.85 | [8 empty] | 100.34 |  |  | 98.58 | [6 empty] | 98.18 |  | 98.76 |  |  |  | 85.59 |  |  | 0.00 |  |  | 0.00 | [9 empty] | -0.13 |  |  | 72.54
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 93.06 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 86.94 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 6.18 |  |  | 73.74
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 6.94 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 13.05 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 79.65 |  |  | 4.68
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 6.94 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 13.05 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 24.12 |  |  | 3.68
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 86.02 |  |  | 100.00 | [9 empty] | 69.72 |  |  | 21.39
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 344513.03 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.11 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.39 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.91 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.39 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.7 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.56 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.12 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 577.21 |  |  | 863 |  |  |  | 1140 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 8045.76 |  |  | 7882 |  |  |  | 1120 | [10 empty] | 89.99 |  |  |  | 89.99 | [5 empty] | 82.01 |  |  | 89.98 |  |  |  | 6.38 |  | 6.14 | [8 empty] | 3.87 |  |  |  |  | 0.00
1986 |  |  |  | 7199.11 |  |  | 7121 |  |  |  | 1120 | [10 empty] | 81.57 |  |  |  | 81.57 | [5 empty] | 73.38 |  |  | 81.29 |  |  |  | 3.29 |  | 2.78 | [8 empty] | 15.65 |  |  |  |  | 0.00
1987 |  |  |  | 6321.78 |  |  | 6141 |  |  |  | 1120 | [10 empty] | 70.02 |  |  |  | 70.02 | [5 empty] | 64.43 |  |  | 70.10 |  |  |  | 1.98 |  | 1.42 | [8 empty] | 28.56 |  |  |  |  | 0.00
1988 |  |  |  | 8144.18 |  |  | 7413 |  |  |  | 1120 | [10 empty] | 92.53 |  |  |  | 92.53 | [5 empty] | 82.75 |  |  | 84.39 |  |  |  | 3.18 |  | 3.03 | [8 empty] | 4.44 |  |  |  |  | 0.00
1989 |  |  |  | 8350.92 |  |  | 7368 |  |  |  | 1118 | [10 empty] | 84.04 |  |  |  | 84.04 | [5 empty] | 85.27 |  |  | 84.11 |  |  |  | 1.04 |  | 0.89 | [8 empty] | 15.08 |  |  |  |  | 0.00
1990 |  |  |  | 8005.06 |  |  | 7167 |  |  |  | 1125 | [10 empty] | 81.84 |  |  |  | 81.84 | [5 empty] | 81.23 |  |  | 81.82 |  |  |  | 3.49 |  | 2.96 | [8 empty] | 15.21 |  |  |  |  | 0.00
1991 |  |  |  | 9979.37 |  |  | 8726 |  |  |  | 1125 | [10 empty] | 99.61 |  |  |  | 99.61 | [5 empty] | 101.26 |  |  | 99.61 |  |  |  | 0.39 |  | 0.39 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 8094.55 |  |  | 7204 |  |  |  | 1125 | [10 empty] | 82.04 |  |  |  | 82.04 | [5 empty] | 81.91 |  |  | 82.01 |  |  |  | 1.95 |  | 1.63 | [8 empty] | 16.34 |  |  |  |  | 0.00
1993 |  |  |  | 8389.95 |  |  | 7498 |  |  |  | 1120 | [10 empty] | 85.53 |  |  |  | 85.53 | [5 empty] | 85.51 |  |  | 85.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.47 |  |  |  |  | 0.00
1994 |  |  |  | 10006.49 |  |  | 8726 |  |  |  | 1115 | [10 empty] | 99.62 |  |  |  | 99.62 | [5 empty] | 102.45 |  |  | 99.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.38 |  |  |  |  | 0.00
1995 |  |  |  | 8252.83 |  |  | 7356 |  |  |  | 1125 | [10 empty] | 83.98 |  |  |  | 83.98 | [5 empty] | 83.74 |  |  | 83.97 |  |  |  | 3.29 |  | 2.85 | [8 empty] | 13.16 |  |  |  |  | 0.00
1996 |  |  |  | 8890.38 |  |  | 7864 |  |  |  | 1125 | [10 empty] | 89.56 |  |  |  | 89.56 | [5 empty] | 89.97 |  |  | 89.53 |  |  |  | 2.01 |  | 1.83 | [8 empty] | 8.61 |  |  |  |  | 0.00
1997 |  |  |  | 8954.60 |  |  | 8760 |  |  |  | 1125 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 90.86 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 8516.77 |  |  | 7913 |  |  |  | 1125 | [10 empty] | 90.36 |  |  |  | 90.36 | [5 empty] | 86.42 |  |  | 90.33 |  |  |  | 1.19 |  | 1.09 | [8 empty] | 8.55 |  |  |  |  | 0.00
1999 |  |  |  | 8596.43 |  |  | 7707 |  |  |  | 1125 | [10 empty] | 87.79 |  |  |  | 87.79 | [5 empty] | 87.23 |  |  | 87.98 |  |  |  | 2.75 |  | 2.48 | [8 empty] | 9.73 |  |  |  |  | 0.00
2000 |  |  |  | 9991.84 |  |  | 8762 |  |  |  | 1125 | [10 empty] | 99.75 |  |  |  | 100.00 | [5 empty] | 101.11 |  |  | 99.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.25
2001 |  |  |  | 8384.12 |  |  | 7500 |  |  |  | 1125 | [10 empty] | 85.39 |  |  |  | 85.39 | [5 empty] | 85.07 |  |  | 85.62 |  |  |  | 2.48 |  | 2.17 | [8 empty] | 12.44 |  |  |  |  | 0.00
2002 |  |  |  | 8386.58 |  |  | 7484 |  |  |  | 1125 | [10 empty] | 85.20 |  |  |  | 85.20 | [5 empty] | 85.10 |  |  | 85.43 |  |  |  | 5.84 |  | 5.29 | [8 empty] | 9.51 |  |  |  |  | 0.00
2003 |  |  |  | 9699.74 |  |  | 8397 |  |  |  | 1125 | [10 empty] | 95.81 |  |  |  | 95.81 | [5 empty] | 98.42 |  |  | 95.86 |  |  |  | 0.98 |  | 0.95 | [8 empty] | 3.25 |  |  |  |  | 0.00
2004 |  |  |  | 7842.38 |  |  | 6856 |  |  |  | 1125 | [10 empty] | 77.93 |  |  |  | 77.93 | [5 empty] | 79.36 |  |  | 78.05 |  |  |  | 5.38 |  | 4.43 | [8 empty] | 17.64 |  |  |  |  | 0.00
2005 |  |  |  | 8021.18 |  |  | 6966 |  |  |  | 1137 | [10 empty] | 79.57 |  |  |  | 79.57 | [5 empty] | 80.53 |  |  | 79.52 |  |  |  | 3.65 |  | 3.01 | [8 empty] | 17.42 |  |  |  |  | 0.00
2006 |  |  |  | 10098.88 |  |  | 8324 |  |  |  | 1190 | [10 empty] | 95.04 |  |  |  | 95.04 | [5 empty] | 96.88 |  |  | 95.02 |  |  |  | 4.96 |  | 4.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 9371.96 |  |  | 7742 |  |  |  | 1190 | [10 empty] | 88.40 |  |  |  | 88.40 | [5 empty] | 89.90 |  |  | 88.38 |  |  |  | 1.25 |  | 1.12 | [8 empty] | 10.48 |  |  |  |  | 0.00
2008 |  |  |  | 9378.23 |  |  | 7834 |  |  |  | 1190 | [10 empty] | 89.20 |  |  |  | 89.20 | [5 empty] | 89.72 |  |  | 89.18 |  |  |  | 3.43 |  | 3.16 | [8 empty] | 7.64 |  |  |  |  | 0.00
2009 |  |  |  | 10247.12 |  |  | 8408 |  |  |  | 1190 | [10 empty] | 96.01 |  |  |  | 96.01 | [5 empty] | 98.30 |  |  | 95.98 |  |  |  | 3.99 |  | 3.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 9011.04 |  |  | 7412 |  |  |  | 1190 | [10 empty] | 84.63 |  |  |  | 84.63 | [5 empty] | 86.44 |  |  | 84.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.37 |  |  |  |  | 0.00
2011 |  |  |  | 9387.87 |  |  | 7771 |  |  |  | 1215 | [10 empty] | 88.74 |  |  |  | 88.74 | [5 empty] | 89.90 |  |  | 88.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.26 |  |  |  |  | 0.00
2012 |  |  |  | 10718.32 |  |  | 8784 |  |  |  | 1215 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.43 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 8408.87 |  |  | 7008 |  |  |  | 1215 | [10 empty] | 79.99 |  |  |  | 79.99 | [5 empty] | 79.00 |  |  | 79.99 |  |  |  | 7.13 |  | 6.14 | [8 empty] | 13.87 |  |  |  |  | 0.00
2014 |  |  |  | 9297.34 |  |  | 7649 |  |  |  | 1215 | [10 empty] | 87.31 |  |  |  | 87.31 | [5 empty] | 87.35 |  |  | 87.32 |  |  |  | 1.19 |  | 1.05 | [8 empty] | 11.64 |  |  |  |  | 0.00
2015 |  |  |  | 10443.55 |  |  | 8648 |  |  |  | 1215 | [10 empty] | 98.73 |  |  |  | 98.73 | [5 empty] | 98.12 |  |  | 98.72 |  |  |  | 1.27 |  | 1.27 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 9445.58 |  |  | 7859 |  |  |  | 1215 | [10 empty] | 89.48 |  |  |  | 89.48 | [5 empty] | 88.50 |  |  | 89.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.52 |  |  |  |  | 0.00
2017 |  |  |  | 8338.45 |  |  | 6995 |  |  |  | 1215 | [10 empty] | 79.85 |  |  |  | 79.85 | [5 empty] | 78.34 |  |  | 79.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.15 |  |  |  |  | 0.00
2018 |  |  |  | 10657.75 |  |  | 8760 |  |  |  | 1215 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.13 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 9227.76 |  |  | 7603 |  |  |  | 1215 | [10 empty] | 86.81 |  |  |  | 86.81 | [5 empty] | 86.70 |  |  | 86.79 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 13.04 |  |  |  |  | 0.00
2020 |  |  |  | 7742.12 |  |  | 6477 |  |  |  | 1215 | [10 empty] | 74.93 |  |  |  | 74.93 | [5 empty] | 72.54 |  |  | 73.74 |  |  |  | 4.68 |  | 3.68 | [8 empty] | 21.39 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 146
B. |  | Refuelling without maintenance | [20 empty] | 1879 | [14 empty] | 52
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 735
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 61
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 0
L. |  | Human factor related | [39 empty] | 6
Z. |  | Other | [24 empty] | 427 | [14 empty] | 17 | [11 empty] | 1
Subtotal | [22 empty] | 1879 |  |  |  | 427 | [10 empty] | 848 |  |  |  | 170 | [11 empty] | 1
Total | [22 empty] | 2306 | [14 empty] | 1019
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 4
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 13
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 24
32. |  |  | Feedwater and Main Steam System | [34 empty] | 29
33. |  |  | Circulating Water System | [34 empty] | 10
34. |  |  | Miscellaneous Systems | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 10
42. |  |  | Electrical Power Supply Systems | [34 empty] | 38
Total | [37 empty] | 148
Highlights (2020)
Refueling Outage 24. Transitioned from forced outage to scheduled refueling outage 24 at 0800 10/4/2020.

## CALVERT CLIFFS-1
2020 Operating Experience
US-317 | [8 empty] | CALVERT CLIFFS-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-06-01
Thermal power | [12 empty] | : |  |  | 2737 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-01-03
Gross electrical power | [12 empty] | : |  |  | 918 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-05-08
Reference unit power (net) | [12 empty] | : |  |  | 877 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 314
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.352
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.45 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.47 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 217 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.62 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7371.35 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.2 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.2 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.8 %
Load Factor (LF) | [18 empty] | : | 95.69 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.18 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 599 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 685.64 | 319.57 |  |  |  | 401.58 |  | 660.80 | [8 empty] | 682.11 |  |  | 645.64 | [6 empty] | 660.81 |  | 656.79 |  |  |  | 643.46 |  |  | 673.80 |  |  | 658.38 | [9 empty] | 682.79 |  |  | 7371.35
EAF [%] |  |  |  |  | 100.00 | 55.18 |  |  |  | 61.61 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.20
UCF [%] |  |  |  |  | 100.00 | 55.18 |  |  |  | 61.61 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.20
LF [%] |  |  |  |  | 105.08 | 52.35 |  |  |  | 61.55 |  | 104.65 | [8 empty] | 104.54 |  |  | 102.25 | [6 empty] | 101.28 |  | 100.66 |  |  |  | 101.90 |  |  | 103.27 |  |  | 104.27 | [9 empty] | 104.64 |  |  | 95.69
OF [%] |  |  |  |  | 100.00 | 55.17 |  |  |  | 61.42 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.18
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 44.82 |  |  |  | 38.39 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.80
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 275586.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.14 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.85 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.55 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.1 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.36 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.88 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.25 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.25 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 4381.60 |  |  | 6667 |  |  |  | 800 | [10 empty] | 77.16 |  |  |  | 77.16 | [5 empty] | 77.40 |  |  | 81.75 |  |  |  | 15.38 |  | 14.02 | [8 empty] | 8.82 |  |  |  |  | 0.00
1976 |  |  |  | 6303.90 |  |  | 8356 |  |  |  | 800 | [10 empty] | 89.70 |  |  |  | 89.70 | [5 empty] | 89.71 |  |  | 95.13 |  |  |  | 2.27 |  | 2.08 | [8 empty] | 8.22 |  |  |  |  | 0.00
1977 |  |  |  | 4882.00 |  |  | 6313 |  |  |  | 807 | [10 empty] | 68.62 |  |  |  | 68.62 | [5 empty] | 69.06 |  |  | 72.07 |  |  |  | 8.77 |  | 6.60 | [8 empty] | 24.78 |  |  |  |  | 0.00
1978 |  |  |  | 4676.10 |  |  | 6150 |  |  |  | 810 | [10 empty] | 65.91 |  |  |  | 65.91 | [5 empty] | 65.90 |  |  | 70.21 |  |  |  | 16.09 |  | 12.64 | [8 empty] | 21.45 |  |  |  |  | 0.00
1979 |  |  |  | 4194.10 |  |  | 6154 |  |  |  | 810 | [10 empty] | 59.11 |  |  |  | 59.11 | [5 empty] | 59.11 |  |  | 70.25 |  |  |  | 23.95 |  | 18.62 | [8 empty] | 22.27 |  |  |  |  | 0.00
1980 |  |  |  | 4542.50 |  |  | 6349 |  |  |  | 810 | [10 empty] | 72.20 |  |  |  | 77.03 | [5 empty] | 63.84 |  |  | 72.28 |  |  |  | 4.97 |  | 4.03 | [8 empty] | 18.94 |  |  |  |  | 4.84
1981 |  |  |  | 6109.60 |  |  | 7544 |  |  |  | 821 | [10 empty] | 86.43 |  |  |  | 86.43 | [5 empty] | 84.95 |  |  | 86.12 |  |  |  | 10.53 |  | 10.17 | [8 empty] | 3.40 |  |  |  |  | 0.00
1982 |  |  |  | 5362.10 |  |  | 6419 |  |  |  | 825 | [10 empty] | 73.86 |  |  |  | 73.86 | [5 empty] | 74.20 |  |  | 73.28 |  |  |  | 0.64 |  | 0.48 | [8 empty] | 25.66 |  |  |  |  | 0.00
1983 |  |  |  | 5570.70 |  |  | 6719 |  |  |  | 825 | [10 empty] | 77.04 |  |  |  | 77.04 | [5 empty] | 77.08 |  |  | 76.70 |  |  |  | 2.67 |  | 2.11 | [8 empty] | 20.84 |  |  |  |  | 0.00
1984 |  |  |  | 6221.60 |  |  | 7422 |  |  |  | 825 | [10 empty] | 84.35 |  |  |  | 86.67 | [5 empty] | 85.85 |  |  | 84.49 |  |  |  | 13.33 |  | 13.33 | [8 empty] | 0.00 |  |  |  |  | 2.32
1985 |  |  |  | 4359.73 |  |  | 5186 |  |  |  | 825 | [10 empty] | 58.76 |  |  |  | 58.76 | [5 empty] | 60.33 |  |  | 59.20 |  |  |  | 5.79 |  | 3.61 | [8 empty] | 37.63 |  |  |  |  | 0.00
1986 |  |  |  | 5830.74 |  |  | 6855 |  |  |  | 825 | [10 empty] | 78.24 |  |  |  | 78.24 | [5 empty] | 80.68 |  |  | 78.25 |  |  |  | 1.66 |  | 1.32 | [8 empty] | 20.44 |  |  |  |  | 0.00
1987 |  |  |  | 5268.48 |  |  | 6233 |  |  |  | 825 | [10 empty] | 70.91 |  |  |  | 70.91 | [5 empty] | 72.90 |  |  | 71.15 |  |  |  | 26.14 |  | 25.09 | [8 empty] | 4.00 |  |  |  |  | 0.00
1988 |  |  |  | 5164.23 |  |  | 6263 |  |  |  | 825 | [10 empty] | 71.01 |  |  |  | 71.01 | [5 empty] | 71.26 |  |  | 71.30 |  |  |  | 2.39 |  | 1.74 | [8 empty] | 27.25 |  |  |  |  | 0.00
1989 |  |  |  | 1345.62 |  |  | 1727 |  |  |  | 825 | [10 empty] | 18.77 |  |  |  | 18.77 | [5 empty] | 18.62 |  |  | 19.71 |  |  |  | 3.06 |  | 0.59 | [8 empty] | 80.64 |  |  |  |  | 0.00
1990 |  |  |  | 1344.37 |  |  | 1840 |  |  |  | 825 | [10 empty] | 20.06 |  |  |  | 20.06 | [5 empty] | 18.60 |  |  | 21.00 |  |  |  | 1.87 |  | 0.38 | [8 empty] | 79.56 |  |  |  |  | 0.00
1991 |  |  |  | 5465.33 |  |  | 6638 |  |  |  | 825 | [10 empty] | 75.52 |  |  |  | 75.52 | [5 empty] | 75.62 |  |  | 75.78 |  |  |  | 12.00 |  | 10.29 | [8 empty] | 14.19 |  |  |  |  | 0.00
1992 |  |  |  | 4113.88 |  |  | 4927 |  |  |  | 825 | [10 empty] | 55.58 |  |  |  | 55.58 | [5 empty] | 56.77 |  |  | 56.09 |  |  |  | 3.87 |  | 2.24 | [8 empty] | 42.18 |  |  |  |  | 0.00
1993 |  |  |  | 7334.90 |  |  | 8599 |  |  |  | 827 | [10 empty] | 98.16 |  |  |  | 98.16 | [5 empty] | 101.18 |  |  | 98.16 |  |  |  | 1.84 |  | 1.84 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 4686.43 |  |  | 5656 |  |  |  | 832 | [10 empty] | 64.56 |  |  |  | 64.56 | [5 empty] | 64.23 |  |  | 64.57 |  |  |  | 11.21 |  | 8.15 | [8 empty] | 27.29 |  |  |  |  | 0.00
1995 |  |  |  | 7030.23 |  |  | 8487 |  |  |  | 835 | [10 empty] | 96.89 |  |  |  | 96.89 | [5 empty] | 96.11 |  |  | 96.88 |  |  |  | 3.11 |  | 3.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 4846.90 |  |  | 5762 |  |  |  | 835 | [10 empty] | 65.65 |  |  |  | 65.65 | [5 empty] | 66.08 |  |  | 65.60 |  |  |  | 13.65 |  | 10.38 | [8 empty] | 23.96 |  |  |  |  | 0.00
1997 |  |  |  | 7158.40 |  |  | 8400 |  |  |  | 835 | [10 empty] | 95.95 |  |  |  | 95.95 | [5 empty] | 97.86 |  |  | 95.89 |  |  |  | 1.76 |  | 1.72 | [8 empty] | 2.33 |  |  |  |  | 0.00
1998 |  |  |  | 6116.77 |  |  | 7184 |  |  |  | 835 | [10 empty] | 82.01 |  |  |  | 82.01 | [5 empty] | 83.62 |  |  | 82.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.99 |  |  |  |  | 0.00
1999 |  |  |  | 6994.34 |  |  | 8231 |  |  |  | 835 | [10 empty] | 93.99 |  |  |  | 96.81 | [5 empty] | 95.62 |  |  | 93.96 |  |  |  | 1.09 |  | 1.07 | [8 empty] | 2.12 |  |  |  |  | 2.82
2000 |  |  |  | 6449.61 |  |  | 7580 |  |  |  | 825 | [10 empty] | 86.18 |  |  |  | 86.18 | [5 empty] | 88.73 |  |  | 86.29 |  |  |  | 1.01 |  | 0.88 | [8 empty] | 12.94 |  |  |  |  | 0.00
2001 |  |  |  | 7454.78 |  |  | 8727 |  |  |  | 825 | [10 empty] | 99.63 |  |  |  | 99.63 | [5 empty] | 103.15 |  |  | 99.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.37 |  |  |  |  | 0.00
2002 |  |  |  | 4645.18 |  |  | 5506 |  |  |  | 825 | [10 empty] | 62.76 |  |  |  | 62.76 | [5 empty] | 64.28 |  |  | 62.85 |  |  |  | 2.08 |  | 1.33 | [8 empty] | 35.91 |  |  |  |  | 0.00
2003 |  |  |  | 7532.45 |  |  | 8760 |  |  |  | 825 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 104.23 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 6973.98 |  |  | 8034 |  |  |  | 870 | [10 empty] | 91.55 |  |  |  | 91.55 | [5 empty] | 93.26 |  |  | 91.46 |  |  |  | 0.44 |  | 0.40 | [8 empty] | 8.05 |  |  |  |  | 0.00
2005 |  |  |  | 7626.32 |  |  | 8726 |  |  |  | 845 | [10 empty] | 99.62 |  |  |  | 99.62 | [5 empty] | 103.02 |  |  | 99.60 |  |  |  | 0.38 |  | 0.38 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 6449.83 |  |  | 7386 |  |  |  | 873 | [10 empty] | 84.34 |  |  |  | 84.34 | [5 empty] | 84.34 |  |  | 84.32 |  |  |  | 2.28 |  | 1.96 | [8 empty] | 13.70 |  |  |  |  | 0.00
2007 |  |  |  | 7545.36 |  |  | 8701 |  |  |  | 873 | [10 empty] | 99.35 |  |  |  | 99.35 | [5 empty] | 98.66 |  |  | 99.33 |  |  |  | 0.31 |  | 0.31 | [8 empty] | 0.35 |  |  |  |  | 0.00
2008 |  |  |  | 7161.09 |  |  | 8275 |  |  |  | 873 | [10 empty] | 94.22 |  |  |  | 94.22 | [5 empty] | 93.38 |  |  | 94.21 |  |  |  | 0.44 |  | 0.42 | [8 empty] | 5.37 |  |  |  |  | 0.00
2009 |  |  |  | 7528.57 |  |  | 8661 |  |  |  | 873 | [10 empty] | 98.87 |  |  |  | 98.87 | [5 empty] | 98.45 |  |  | 98.87 |  |  |  | 1.13 |  | 1.13 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 6755.04 |  |  | 7814 |  |  |  | 855 | [10 empty] | 88.99 |  |  |  | 88.99 | [5 empty] | 90.19 |  |  | 89.20 |  |  |  | 3.09 |  | 2.83 | [8 empty] | 8.17 |  |  |  |  | 0.00
2011 |  |  |  | 7542.52 |  |  | 8676 |  |  |  | 855 | [10 empty] | 99.05 |  |  |  | 100.00 | [5 empty] | 100.70 |  |  | 99.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.95
2012 |  |  |  | 6070.18 |  |  | 6930 |  |  |  | 866 | [10 empty] | 79.08 |  |  |  | 79.08 | [5 empty] | 80.13 |  |  | 78.89 |  |  |  | 2.84 |  | 2.31 | [8 empty] | 18.61 |  |  |  |  | 0.00
2013 |  |  |  | 7815.24 |  |  | 8760 |  |  |  | 866 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.01 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 6928.82 |  |  | 7868 |  |  |  | 866 | [10 empty] | 89.82 |  |  |  | 89.82 | [5 empty] | 91.34 |  |  | 89.82 |  |  |  | 1.60 |  | 1.46 | [8 empty] | 8.72 |  |  |  |  | 0.00
2015 |  |  |  | 7772.62 |  |  | 8718 |  |  |  | 866 | [10 empty] | 99.52 |  |  |  | 100.00 | [5 empty] | 102.46 |  |  | 99.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.48
2016 |  |  |  | 7191.74 |  |  | 8132 |  |  |  | 866 | [10 empty] | 92.58 |  |  |  | 92.58 | [5 empty] | 94.54 |  |  | 92.58 |  |  |  | 0.73 |  | 0.68 | [8 empty] | 6.74 |  |  |  |  | 0.00
2017 |  |  |  | 7832.43 |  |  | 8760 |  |  |  | 863 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.49 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 7289.37 |  |  | 8128 |  |  |  | 877 | [10 empty] | 92.83 |  |  |  | 92.83 | [5 empty] | 95.90 |  |  | 92.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.17 |  |  |  |  | 0.00
2019 |  |  |  | 7913.33 |  |  | 8760 |  |  |  | 877 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.00 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7371.35 |  |  | 8185 |  |  |  | 877 | [10 empty] | 93.20 |  |  |  | 93.20 | [5 empty] | 95.69 |  |  | 93.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.80 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 265
B. |  | Refuelling without maintenance | [20 empty] | 598 | [14 empty] | 13
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 823
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 369
E. |  | Testing of plant systems or components | [35 empty] | 35
H. |  | Nuclear regulatory requirements | [39 empty] | 20
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 6
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 10
Z. |  | Other | [39 empty] | 18
Subtotal | [22 empty] | 598 | [14 empty] | 1240 |  |  |  | 309 | [11 empty] | 13
Total | [22 empty] | 598 | [14 empty] | 1562
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 9
12. |  |  | Reactor I&C Systems | [34 empty] | 11
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 49
14. |  |  | Safety Systems | [34 empty] | 29
15. |  |  | Reactor Cooling Systems | [34 empty] | 51
16. |  |  | Steam generation systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 49
32. |  |  | Feedwater and Main Steam System | [34 empty] | 41
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 25
Total | [37 empty] | 288
Highlights (2020)
Refueling Outage 24.

## CALVERT CLIFFS-2
2020 Operating Experience
US-318 | [8 empty] | CALVERT CLIFFS-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-06-01
Thermal power | [12 empty] | : |  |  | 2737 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-12-07
Gross electrical power | [12 empty] | : |  |  | 911 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-04-01
Reference unit power (net) | [12 empty] | : |  |  | 855 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 314
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.352
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.45 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.47 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 217 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.56 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7709.21 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 102.65 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 663.58 | 620.10 |  |  |  | 657.14 |  | 637.84 | [8 empty] | 657.45 |  |  | 633.00 | [6 empty] | 638.53 |  | 632.73 |  |  |  | 618.63 |  |  | 649.41 |  |  | 637.30 | [9 empty] | 663.50 |  |  | 7709.21
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 104.32 | 104.20 |  |  |  | 103.31 |  | 103.61 | [8 empty] | 103.35 |  |  | 102.83 | [6 empty] | 100.38 |  | 99.47 |  |  |  | 100.49 |  |  | 102.09 |  |  | 103.52 | [9 empty] | 104.30 |  |  | 102.65
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 273903.27 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.75 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.02 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.41 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.09 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.5 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.07 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.88 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 6009.80 |  |  | 7608 |  |  |  | 810 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 84.95 |  |  | 86.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 5226.60 |  |  | 7129 |  |  |  | 810 | [10 empty] | 72.85 |  |  |  | 72.85 | [5 empty] | 73.66 |  |  | 81.38 |  |  |  | 15.43 |  | 13.29 | [8 empty] | 13.86 |  |  |  |  | 0.00
1979 |  |  |  | 5489.00 |  |  | 6792 |  |  |  | 812 | [10 empty] | 76.60 |  |  |  | 76.60 | [5 empty] | 77.17 |  |  | 77.53 |  |  |  | 10.07 |  | 8.58 | [8 empty] | 14.82 |  |  |  |  | 0.00
1980 |  |  |  | 6412.30 |  |  | 8425 |  |  |  | 825 | [10 empty] | 96.25 |  |  |  | 98.88 | [5 empty] | 88.48 |  |  | 95.91 |  |  |  | 0.73 |  | 0.72 | [8 empty] | 0.39 |  |  |  |  | 2.63
1981 |  |  |  | 5416.00 |  |  | 7005 |  |  |  | 825 | [10 empty] | 80.08 |  |  |  | 80.08 | [5 empty] | 74.94 |  |  | 79.97 |  |  |  | 5.48 |  | 4.65 | [8 empty] | 15.27 |  |  |  |  | 0.00
1982 |  |  |  | 5005.20 |  |  | 6496 |  |  |  | 825 | [10 empty] | 74.21 |  |  |  | 74.21 | [5 empty] | 69.26 |  |  | 74.16 |  |  |  | 5.97 |  | 4.71 | [8 empty] | 21.08 |  |  |  |  | 0.00
1983 |  |  |  | 6113.10 |  |  | 7567 |  |  |  | 825 | [10 empty] | 86.39 |  |  |  | 86.39 | [5 empty] | 84.59 |  |  | 86.38 |  |  |  | 7.89 |  | 7.40 | [8 empty] | 6.21 |  |  |  |  | 0.00
1984 |  |  |  | 5338.45 |  |  | 6502 |  |  |  | 825 | [10 empty] | 73.68 |  |  |  | 73.68 | [5 empty] | 73.67 |  |  | 74.02 |  |  |  | 7.99 |  | 6.39 | [8 empty] | 19.93 |  |  |  |  | 0.00
1985 |  |  |  | 5608.05 |  |  | 6789 |  |  |  | 825 | [10 empty] | 77.41 |  |  |  | 77.41 | [5 empty] | 77.60 |  |  | 77.50 |  |  |  | 5.72 |  | 4.70 | [8 empty] | 17.89 |  |  |  |  | 0.00
1986 |  |  |  | 7006.67 |  |  | 8405 |  |  |  | 825 | [10 empty] | 95.98 |  |  |  | 95.98 | [5 empty] | 96.95 |  |  | 95.95 |  |  |  | 4.02 |  | 4.02 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 4831.98 |  |  | 5859 |  |  |  | 825 | [10 empty] | 66.35 |  |  |  | 66.35 | [5 empty] | 66.86 |  |  | 66.88 |  |  |  | 4.10 |  | 2.84 | [8 empty] | 30.81 |  |  |  |  | 0.00
1988 |  |  |  | 6602.69 |  |  | 7813 |  |  |  | 825 | [10 empty] | 88.78 |  |  |  | 88.78 | [5 empty] | 91.11 |  |  | 88.95 |  |  |  | 1.73 |  | 1.56 | [8 empty] | 9.66 |  |  |  |  | 0.00
1989 |  |  |  | 1448.46 |  |  | 1731 |  |  |  | 825 | [10 empty] | 18.32 |  |  |  | 18.32 | [5 empty] | 20.04 |  |  | 19.76 |  |  |  | 12.14 |  | 2.53 | [8 empty] | 79.15 |  |  |  |  | 0.00
1990 |  |  |  | 0.00 |  |  | 0 |  |  |  | 825 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1991 |  |  |  | 3635.58 |  |  | 4515 |  |  |  | 825 | [10 empty] | 51.29 |  |  |  | 51.29 | [5 empty] | 50.31 |  |  | 51.54 |  |  |  | 9.70 |  | 5.51 | [8 empty] | 43.21 |  |  |  |  | 0.00
1992 |  |  |  | 6590.28 |  |  | 7855 |  |  |  | 825 | [10 empty] | 89.30 |  |  |  | 89.30 | [5 empty] | 90.94 |  |  | 89.42 |  |  |  | 10.70 |  | 10.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 4975.19 |  |  | 5939 |  |  |  | 827 | [10 empty] | 67.36 |  |  |  | 67.36 | [5 empty] | 68.63 |  |  | 67.80 |  |  |  | 0.99 |  | 0.67 | [8 empty] | 31.97 |  |  |  |  | 0.00
1994 |  |  |  | 6576.52 |  |  | 7925 |  |  |  | 835 | [10 empty] | 90.56 |  |  |  | 90.56 | [5 empty] | 89.82 |  |  | 90.47 |  |  |  | 7.88 |  | 7.74 | [8 empty] | 1.70 |  |  |  |  | 0.00
1995 |  |  |  | 5911.11 |  |  | 7121 |  |  |  | 840 | [10 empty] | 81.36 |  |  |  | 81.36 | [5 empty] | 80.33 |  |  | 81.29 |  |  |  | 2.52 |  | 2.10 | [8 empty] | 16.54 |  |  |  |  | 0.00
1996 |  |  |  | 7247.74 |  |  | 8561 |  |  |  | 840 | [10 empty] | 97.50 |  |  |  | 97.50 | [5 empty] | 98.23 |  |  | 97.46 |  |  |  | 2.50 |  | 2.50 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 5979.88 |  |  | 7100 |  |  |  | 840 | [10 empty] | 81.10 |  |  |  | 81.10 | [5 empty] | 81.27 |  |  | 81.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.90 |  |  |  |  | 0.00
1998 |  |  |  | 7225.49 |  |  | 8393 |  |  |  | 840 | [10 empty] | 95.83 |  |  |  | 95.83 | [5 empty] | 98.19 |  |  | 95.81 |  |  |  | 4.17 |  | 4.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 6332.72 |  |  | 7400 |  |  |  | 840 | [10 empty] | 84.50 |  |  |  | 84.50 | [5 empty] | 86.06 |  |  | 84.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.50 |  |  |  |  | 0.00
2000 |  |  |  | 7391.04 |  |  | 8614 |  |  |  | 835 | [10 empty] | 98.05 |  |  |  | 98.05 | [5 empty] | 100.72 |  |  | 98.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.95 |  |  |  |  | 0.00
2001 |  |  |  | 6201.52 |  |  | 7297 |  |  |  | 835 | [10 empty] | 83.28 |  |  |  | 83.28 | [5 empty] | 84.78 |  |  | 83.30 |  |  |  | 0.76 |  | 0.64 | [8 empty] | 16.09 |  |  |  |  | 0.00
2002 |  |  |  | 7480.55 |  |  | 8760 |  |  |  | 835 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.27 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 6156.86 |  |  | 7124 |  |  |  | 835 | [10 empty] | 81.37 |  |  |  | 81.37 | [5 empty] | 84.17 |  |  | 81.32 |  |  |  | 0.44 |  | 0.36 | [8 empty] | 18.27 |  |  |  |  | 0.00
2004 |  |  |  | 7552.20 |  |  | 8729 |  |  |  | 858 | [10 empty] | 99.37 |  |  |  | 99.37 | [5 empty] | 101.33 |  |  | 99.37 |  |  |  | 0.63 |  | 0.63 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 7114.31 |  |  | 8249 |  |  |  | 858 | [10 empty] | 94.18 |  |  |  | 94.18 | [5 empty] | 94.64 |  |  | 94.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.82 |  |  |  |  | 0.00
2006 |  |  |  | 7406.34 |  |  | 8621 |  |  |  | 862 | [10 empty] | 98.43 |  |  |  | 98.43 | [5 empty] | 98.08 |  |  | 98.41 |  |  |  | 1.57 |  | 1.57 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 6807.83 |  |  | 7902 |  |  |  | 862 | [10 empty] | 90.22 |  |  |  | 90.22 | [5 empty] | 90.16 |  |  | 90.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.78 |  |  |  |  | 0.00
2008 |  |  |  | 7514.73 |  |  | 8784 |  |  |  | 862 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.25 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 7021.55 |  |  | 8227 |  |  |  | 862 | [10 empty] | 93.93 |  |  |  | 93.93 | [5 empty] | 92.99 |  |  | 93.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.07 |  |  |  |  | 0.00
2010 |  |  |  | 7238.91 |  |  | 8528 |  |  |  | 850 | [10 empty] | 97.32 |  |  |  | 97.32 | [5 empty] | 97.22 |  |  | 97.35 |  |  |  | 2.68 |  | 2.68 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 6787.88 |  |  | 8005 |  |  |  | 850 | [10 empty] | 91.41 |  |  |  | 91.41 | [5 empty] | 91.16 |  |  | 91.38 |  |  |  | 0.55 |  | 0.51 | [8 empty] | 8.08 |  |  |  |  | 0.00
2012 |  |  |  | 7506.54 |  |  | 8784 |  |  |  | 850 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.54 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 6486.75 |  |  | 7652 |  |  |  | 850 | [10 empty] | 87.35 |  |  |  | 87.35 | [5 empty] | 87.11 |  |  | 87.34 |  |  |  | 3.02 |  | 2.72 | [8 empty] | 9.93 |  |  |  |  | 0.00
2014 |  |  |  | 7422.54 |  |  | 8662 |  |  |  | 850 | [10 empty] | 98.88 |  |  |  | 98.88 | [5 empty] | 99.68 |  |  | 98.88 |  |  |  | 1.12 |  | 1.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6877.67 |  |  | 7969 |  |  |  | 850 | [10 empty] | 90.98 |  |  |  | 91.55 | [5 empty] | 92.37 |  |  | 90.97 |  |  |  | 1.46 |  | 1.36 | [8 empty] | 7.10 |  |  |  |  | 0.57
2016 |  |  |  | 7574.55 |  |  | 8753 |  |  |  | 850 | [10 empty] | 99.64 |  |  |  | 99.64 | [5 empty] | 101.45 |  |  | 99.65 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7278.30 |  |  | 8257 |  |  |  | 855 | [10 empty] | 94.28 |  |  |  | 94.28 | [5 empty] | 97.36 |  |  | 94.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.72 |  |  |  |  | 0.00
2018 |  |  |  | 7698.56 |  |  | 8760 |  |  |  | 855 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.79 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7099.58 |  |  | 8107 |  |  |  | 855 | [10 empty] | 92.56 |  |  |  | 92.56 | [5 empty] | 94.79 |  |  | 92.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.44 |  |  |  |  | 0.00
2020 |  |  |  | 7709.21 |  |  | 8783 |  |  |  | 855 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.65 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1977 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 193
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1013
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 63
E. |  | Testing of plant systems or components | [35 empty] | 7 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 13
Z. |  | Other | [39 empty] | 0
Subtotal | [37 empty] | 1083 |  |  |  | 213 | [11 empty] | 1
Total | [22 empty] | 0 | [14 empty] | 1297
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1977 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 14
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 20
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 61
16. |  |  | Steam generation systems | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [34 empty] | 21
32. |  |  | Feedwater and Main Steam System | [34 empty] | 32
34. |  |  | Miscellaneous Systems | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 12
42. |  |  | Electrical Power Supply Systems | [34 empty] | 27
Total | [37 empty] | 200

## CATAWBA-1
2020 Operating Experience
US-413 | [8 empty] | CATAWBA-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Owner | [7 empty] | : | NCEMCO (North Carolina Electric Membership Corp.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (ICECND) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-05-01
Thermal power | [12 empty] | : |  |  | 3411 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-01-22
Gross electrical power | [12 empty] | : |  |  | 1188 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-06-29
Reference unit power (net) | [12 empty] | : |  |  | 1160 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.204
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 39 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.83
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 25 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9235.52 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.28 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.58 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.17 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.58 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.25 %
Load Factor (LF) | [18 empty] | : | 90.64 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.56 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 829 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 877.23 | 707.87 |  |  |  | 869.11 |  | 822.95 | [8 empty] | 19.18 |  |  | 805.10 | [6 empty] | 864.93 |  | 865.41 |  |  |  | 809.83 |  |  | 858.14 |  |  | 852.31 | [9 empty] | 883.46 |  |  | 9235.52
EAF [%] |  |  |  |  | 100.00 | 88.20 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 3.76 |  |  | 98.81 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 97.14 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.58
UCF [%] |  |  |  |  | 100.00 | 88.20 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 3.76 |  |  | 98.81 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 97.14 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.58
LF [%] |  |  |  |  | 101.64 | 87.68 |  |  |  | 100.70 |  | 98.53 | [8 empty] | 2.22 |  |  | 96.40 | [6 empty] | 100.22 |  | 100.27 |  |  |  | 96.96 |  |  | 99.43 |  |  | 102.05 | [9 empty] | 102.37 |  |  | 90.64
OF [%] |  |  |  |  | 100.00 | 88.22 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 3.76 |  |  | 98.75 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 97.08 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.56
FLR [%] |  |  |  |  | 0.00 | 11.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 2.86 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.28
UCL [%] |  |  |  |  | 0.00 | 11.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 2.86 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.17
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 96.24 |  |  | 1.19 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.25
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 402409.12 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.19 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.05 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.87 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.05 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.08 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.63 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.96 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 3440.51 |  |  | 3513 |  |  |  | 1138 | [10 empty] | 78.55 |  |  |  | 78.55 | [5 empty] | 66.98 |  |  | 78.45 |  |  |  | 21.45 |  | 21.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 5199.12 |  |  | 5151 |  |  |  | 1145 | [10 empty] | 58.88 |  |  |  | 58.88 | [5 empty] | 51.83 |  |  | 58.80 |  |  |  | 18.75 |  | 13.59 | [8 empty] | 27.53 |  |  |  |  | 0.00
1987 |  |  |  | 6405.97 |  |  | 5924 |  |  |  | 1145 | [10 empty] | 68.00 |  |  |  | 68.00 | [5 empty] | 63.87 |  |  | 67.63 |  |  |  | 15.46 |  | 12.43 | [8 empty] | 19.57 |  |  |  |  | 0.00
1988 |  |  |  | 7639.97 |  |  | 7003 |  |  |  | 1129 | [10 empty] | 79.75 |  |  |  | 79.75 | [5 empty] | 77.04 |  |  | 79.72 |  |  |  | 8.32 |  | 7.24 | [8 empty] | 13.00 |  |  |  |  | 0.00
1989 |  |  |  | 7775.42 |  |  | 7278 |  |  |  | 1129 | [10 empty] | 84.67 |  |  |  | 84.67 | [5 empty] | 78.62 |  |  | 83.08 |  |  |  | 4.00 |  | 3.52 | [8 empty] | 11.81 |  |  |  |  | 0.00
1990 |  |  |  | 6900.50 |  |  | 6277 |  |  |  | 1129 | [10 empty] | 71.67 |  |  |  | 71.67 | [5 empty] | 69.77 |  |  | 71.66 |  |  |  | 9.05 |  | 7.13 | [8 empty] | 21.20 |  |  |  |  | 0.00
1991 |  |  |  | 6681.05 |  |  | 6227 |  |  |  | 1129 | [10 empty] | 71.11 |  |  |  | 71.11 | [5 empty] | 67.55 |  |  | 71.08 |  |  |  | 4.10 |  | 3.04 | [8 empty] | 25.86 |  |  |  |  | 0.00
1992 |  |  |  | 7050.94 |  |  | 6338 |  |  |  | 1129 | [10 empty] | 72.14 |  |  |  | 72.14 | [5 empty] | 71.10 |  |  | 72.15 |  |  |  | 7.46 |  | 5.82 | [8 empty] | 22.04 |  |  |  |  | 0.00
1993 |  |  |  | 7597.13 |  |  | 6916 |  |  |  | 1129 | [10 empty] | 78.97 |  |  |  | 78.97 | [5 empty] | 76.82 |  |  | 78.95 |  |  |  | 4.65 |  | 3.85 | [8 empty] | 17.18 |  |  |  |  | 0.00
1994 |  |  |  | 9778.83 |  |  | 8722 |  |  |  | 1129 | [10 empty] | 99.58 |  |  |  | 99.58 | [5 empty] | 98.88 |  |  | 99.57 |  |  |  | 0.41 |  | 0.41 | [8 empty] | 0.01 |  |  |  |  | 0.00
1995 |  |  |  | 8721.63 |  |  | 7712 |  |  |  | 1129 | [10 empty] | 88.07 |  |  |  | 88.07 | [5 empty] | 88.19 |  |  | 88.04 |  |  |  | 0.53 |  | 0.47 | [8 empty] | 11.46 |  |  |  |  | 0.00
1996 |  |  |  | 6341.10 |  |  | 5806 |  |  |  | 1129 | [10 empty] | 66.17 |  |  |  | 66.17 | [5 empty] | 63.94 |  |  | 66.10 |  |  |  | 4.16 |  | 2.87 | [8 empty] | 30.97 |  |  |  |  | 0.00
1997 |  |  |  | 9192.55 |  |  | 7966 |  |  |  | 1129 | [10 empty] | 90.68 |  |  |  | 90.68 | [5 empty] | 92.95 |  |  | 90.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.32 |  |  |  |  | 0.00
1998 |  |  |  | 8903.65 |  |  | 7923 |  |  |  | 1129 | [10 empty] | 90.47 |  |  |  | 90.47 | [5 empty] | 90.03 |  |  | 90.45 |  |  |  | 8.31 |  | 8.20 | [8 empty] | 1.34 |  |  |  |  | 0.00
1999 |  |  |  | 9073.74 |  |  | 7987 |  |  |  | 1129 | [10 empty] | 91.20 |  |  |  | 91.20 | [5 empty] | 91.75 |  |  | 91.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.80 |  |  |  |  | 0.00
2000 |  |  |  | 8923.00 |  |  | 7844 |  |  |  | 1129 | [10 empty] | 89.32 |  |  |  | 89.32 | [5 empty] | 89.98 |  |  | 89.30 |  |  |  | 0.45 |  | 0.41 | [8 empty] | 10.28 |  |  |  |  | 0.00
2001 |  |  |  | 9976.97 |  |  | 8722 |  |  |  | 1129 | [10 empty] | 99.57 |  |  |  | 99.57 | [5 empty] | 100.88 |  |  | 99.57 |  |  |  | 0.43 |  | 0.43 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 9481.61 |  |  | 8250 |  |  |  | 1129 | [10 empty] | 94.20 |  |  |  | 94.20 | [5 empty] | 95.87 |  |  | 94.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.80 |  |  |  |  | 0.00
2003 |  |  |  | 8198.52 |  |  | 7157 |  |  |  | 1129 | [10 empty] | 81.72 |  |  |  | 81.72 | [5 empty] | 82.90 |  |  | 81.70 |  |  |  | 8.02 |  | 7.12 | [8 empty] | 11.15 |  |  |  |  | 0.00
2004 |  |  |  | 9711.07 |  |  | 8608 |  |  |  | 1129 | [10 empty] | 98.01 |  |  |  | 98.01 | [5 empty] | 97.92 |  |  | 98.00 |  |  |  | 1.98 |  | 1.98 | [8 empty] | 0.02 |  |  |  |  | 0.00
2005 |  |  |  | 9177.33 |  |  | 8027 |  |  |  | 1129 | [10 empty] | 91.66 |  |  |  | 91.66 | [5 empty] | 92.78 |  |  | 91.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.34 |  |  |  |  | 0.00
2006 |  |  |  | 8114.96 |  |  | 7066 |  |  |  | 1129 | [10 empty] | 80.68 |  |  |  | 80.68 | [5 empty] | 82.05 |  |  | 80.66 |  |  |  | 6.75 |  | 5.84 | [8 empty] | 13.47 |  |  |  |  | 0.00
2007 |  |  |  | 10070.89 |  |  | 8728 |  |  |  | 1129 | [10 empty] | 99.65 |  |  |  | 99.65 | [5 empty] | 101.83 |  |  | 99.63 |  |  |  | 0.35 |  | 0.35 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8773.30 |  |  | 7610 |  |  |  | 1129 | [10 empty] | 86.64 |  |  |  | 86.64 | [5 empty] | 88.47 |  |  | 86.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.36 |  |  |  |  | 0.00
2009 |  |  |  | 9002.04 |  |  | 7834 |  |  |  | 1129 | [10 empty] | 89.45 |  |  |  | 89.45 | [5 empty] | 91.02 |  |  | 89.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.55 |  |  |  |  | 0.00
2010 |  |  |  | 9889.07 |  |  | 8629 |  |  |  | 1129 | [10 empty] | 98.51 |  |  |  | 98.51 | [5 empty] | 99.99 |  |  | 98.50 |  |  |  | 1.49 |  | 1.49 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8758.04 |  |  | 7630 |  |  |  | 1146 | [10 empty] | 87.23 |  |  |  | 87.23 | [5 empty] | 87.78 |  |  | 87.10 |  |  |  | 0.32 |  | 0.28 | [8 empty] | 12.49 |  |  |  |  | 0.00
2012 |  |  |  | 8767.33 |  |  | 7657 |  |  |  | 1146 | [10 empty] | 87.19 |  |  |  | 87.19 | [5 empty] | 87.09 |  |  | 87.17 |  |  |  | 3.73 |  | 3.38 | [8 empty] | 9.43 |  |  |  |  | 0.00
2013 |  |  |  | 10100.41 |  |  | 8760 |  |  |  | 1146 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.60 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 8619.61 |  |  | 7493 |  |  |  | 1146 | [10 empty] | 85.54 |  |  |  | 85.54 | [5 empty] | 85.86 |  |  | 85.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.46 |  |  |  |  | 0.00
2015 |  |  |  | 9283.45 |  |  | 8104 |  |  |  | 1146 | [10 empty] | 92.52 |  |  |  | 92.52 | [5 empty] | 92.47 |  |  | 92.51 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 7.38 |  |  |  |  | 0.00
2016 |  |  |  | 10242.36 |  |  | 8784 |  |  |  | 1146 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.75 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 9529.31 |  |  | 8179 |  |  |  | 1146 | [10 empty] | 93.36 |  |  |  | 93.36 | [5 empty] | 94.92 |  |  | 93.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.64 |  |  |  |  | 0.00
2018 |  |  |  | 9510.49 |  |  | 8171 |  |  |  | 1160 | [10 empty] | 93.28 |  |  |  | 93.28 | [5 empty] | 93.59 |  |  | 93.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.72 |  |  |  |  | 0.00
2019 |  |  |  | 10249.75 |  |  | 8760 |  |  |  | 1160 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.87 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9235.52 |  |  | 7955 |  |  |  | 1160 | [10 empty] | 90.58 |  |  |  | 90.58 | [5 empty] | 90.64 |  |  | 90.56 |  |  |  | 1.28 |  | 1.17 | [8 empty] | 8.25 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 231
B. |  | Refuelling without maintenance | [20 empty] | 725 | [14 empty] | 20
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 819
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 40
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 3
H. |  | Nuclear regulatory requirements | [39 empty] | 4
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [24 empty] | 103 | [10 empty] | 2 |  |  |  | 7
Subtotal | [22 empty] | 725 |  |  |  | 103 | [10 empty] | 883 |  |  |  | 250
Total | [22 empty] | 828 | [14 empty] | 1133
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 4
12. |  |  | Reactor I&C Systems | [34 empty] | 25
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 16
15. |  |  | Reactor Cooling Systems | [34 empty] | 86
16. |  |  | Steam generation systems | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 10
32. |  |  | Feedwater and Main Steam System | [34 empty] | 41
33. |  |  | Circulating Water System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 11
42. |  |  | Electrical Power Supply Systems | [34 empty] | 22
Total | [37 empty] | 244
Highlights (2020)
Auto scram following main generator trip due to loss of generator excitation voltage.

## CATAWBA-2
2020 Operating Experience
US-414 | [8 empty] | CATAWBA-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Owner | [7 empty] | : | NCMPA1 (North Carolina Municipal Power Agency No.1)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (ICECND) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-05-01
Thermal power | [12 empty] | : |  |  | 3411 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-05-18
Gross electrical power | [12 empty] | : |  |  | 1188 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-08-19
Reference unit power (net) | [12 empty] | : |  |  | 1150 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.204
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 46 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.4 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.83
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10121.15 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 100.19 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 867.50 | 810.65 |  |  |  | 864.76 |  | 835.93 | [8 empty] | 858.14 |  |  | 826.04 | [6 empty] | 847.99 |  | 846.84 |  |  |  | 824.27 |  |  | 836.54 |  |  | 834.99 | [9 empty] | 867.50 |  |  | 10121.15
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 101.39 | 101.28 |  |  |  | 101.07 |  | 100.96 | [8 empty] | 100.30 |  |  | 99.76 | [6 empty] | 99.11 |  | 98.98 |  |  |  | 99.55 |  |  | 97.77 |  |  | 100.84 | [9 empty] | 101.39 |  |  | 100.19
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 302633.83 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.68 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.36 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.11 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.53 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.63 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.8 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 1324.22 |  |  | 1325 |  |  |  | 1135 | [10 empty] | 35.55 |  |  |  | 35.55 | [5 empty] | 29.10 |  |  | 34.59 |  |  |  | 64.45 |  | 64.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 7169.49 |  |  | 7014 |  |  |  | 1145 | [10 empty] | 80.16 |  |  |  | 80.16 | [5 empty] | 71.48 |  |  | 80.07 |  |  |  | 18.04 |  | 17.64 | [8 empty] | 2.19 |  |  |  |  | 0.00
1988 |  |  |  | 5434.95 |  |  | 5571 |  |  |  | 1129 | [10 empty] | 71.80 |  |  |  | 71.80 | [5 empty] | 54.80 |  |  | 63.42 |  |  |  | 11.82 |  | 9.62 | [8 empty] | 18.58 |  |  |  |  | 0.00
1989 |  |  |  | 6527.10 |  |  | 6302 |  |  |  | 1129 | [10 empty] | 71.97 |  |  |  | 71.97 | [5 empty] | 66.00 |  |  | 71.94 |  |  |  | 4.01 |  | 3.00 | [8 empty] | 25.03 |  |  |  |  | 0.00
1990 |  |  |  | 6502.99 |  |  | 5984 |  |  |  | 1129 | [10 empty] | 69.00 |  |  |  | 69.00 | [5 empty] | 65.75 |  |  | 68.31 |  |  |  | 0.59 |  | 0.41 | [8 empty] | 30.59 |  |  |  |  | 0.00
1991 |  |  |  | 7274.89 |  |  | 6621 |  |  |  | 1129 | [10 empty] | 75.59 |  |  |  | 75.59 | [5 empty] | 73.56 |  |  | 75.58 |  |  |  | 6.64 |  | 5.38 | [8 empty] | 19.03 |  |  |  |  | 0.00
1992 |  |  |  | 9273.46 |  |  | 8281 |  |  |  | 1129 | [10 empty] | 94.29 |  |  |  | 94.29 | [5 empty] | 93.51 |  |  | 94.27 |  |  |  | 1.62 |  | 1.55 | [8 empty] | 4.17 |  |  |  |  | 0.00
1993 |  |  |  | 8177.41 |  |  | 7233 |  |  |  | 1129 | [10 empty] | 82.57 |  |  |  | 82.57 | [5 empty] | 82.68 |  |  | 82.57 |  |  |  | 0.60 |  | 0.50 | [8 empty] | 16.93 |  |  |  |  | 0.00
1994 |  |  |  | 7691.73 |  |  | 6978 |  |  |  | 1129 | [10 empty] | 79.75 |  |  |  | 79.75 | [5 empty] | 77.77 |  |  | 79.66 |  |  |  | 2.70 |  | 2.21 | [8 empty] | 18.04 |  |  |  |  | 0.00
1995 |  |  |  | 7960.18 |  |  | 7074 |  |  |  | 1129 | [10 empty] | 80.83 |  |  |  | 80.83 | [5 empty] | 80.49 |  |  | 80.75 |  |  |  | 9.08 |  | 8.07 | [8 empty] | 11.10 |  |  |  |  | 0.00
1996 |  |  |  | 9233.63 |  |  | 8107 |  |  |  | 1129 | [10 empty] | 92.33 |  |  |  | 92.33 | [5 empty] | 93.11 |  |  | 92.29 |  |  |  | 7.67 |  | 7.67 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 8593.36 |  |  | 7623 |  |  |  | 1129 | [10 empty] | 87.09 |  |  |  | 87.09 | [5 empty] | 86.89 |  |  | 87.02 |  |  |  | 1.47 |  | 1.30 | [8 empty] | 11.61 |  |  |  |  | 0.00
1998 |  |  |  | 8672.30 |  |  | 7580 |  |  |  | 1129 | [10 empty] | 86.55 |  |  |  | 86.55 | [5 empty] | 87.69 |  |  | 86.53 |  |  |  | 2.16 |  | 1.91 | [8 empty] | 11.54 |  |  |  |  | 0.00
1999 |  |  |  | 8855.38 |  |  | 7727 |  |  |  | 1129 | [10 empty] | 88.23 |  |  |  | 88.23 | [5 empty] | 89.54 |  |  | 88.21 |  |  |  | 11.77 |  | 11.77 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 8981.37 |  |  | 7928 |  |  |  | 1129 | [10 empty] | 90.29 |  |  |  | 90.29 | [5 empty] | 90.56 |  |  | 90.26 |  |  |  | 2.00 |  | 1.85 | [8 empty] | 7.86 |  |  |  |  | 0.00
2001 |  |  |  | 8574.14 |  |  | 7507 |  |  |  | 1129 | [10 empty] | 85.72 |  |  |  | 85.72 | [5 empty] | 86.69 |  |  | 85.70 |  |  |  | 5.44 |  | 4.93 | [8 empty] | 9.35 |  |  |  |  | 0.00
2002 |  |  |  | 10172.30 |  |  | 8760 |  |  |  | 1129 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.85 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 9318.16 |  |  | 8117 |  |  |  | 1129 | [10 empty] | 92.66 |  |  |  | 92.66 | [5 empty] | 94.22 |  |  | 92.66 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 7.21 |  |  |  |  | 0.00
2004 |  |  |  | 8835.74 |  |  | 7672 |  |  |  | 1129 | [10 empty] | 87.36 |  |  |  | 87.36 | [5 empty] | 89.10 |  |  | 87.34 |  |  |  | 0.81 |  | 0.71 | [8 empty] | 11.93 |  |  |  |  | 0.00
2005 |  |  |  | 10099.11 |  |  | 8737 |  |  |  | 1129 | [10 empty] | 99.74 |  |  |  | 99.74 | [5 empty] | 102.10 |  |  | 99.73 |  |  |  | 0.26 |  | 0.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 8779.22 |  |  | 7696 |  |  |  | 1129 | [10 empty] | 87.88 |  |  |  | 87.88 | [5 empty] | 88.77 |  |  | 87.85 |  |  |  | 2.00 |  | 1.80 | [8 empty] | 10.32 |  |  |  |  | 0.00
2007 |  |  |  | 8351.56 |  |  | 7262 |  |  |  | 1129 | [10 empty] | 82.92 |  |  |  | 82.92 | [5 empty] | 84.44 |  |  | 82.90 |  |  |  | 13.33 |  | 12.75 | [8 empty] | 4.33 |  |  |  |  | 0.00
2008 |  |  |  | 10203.16 |  |  | 8784 |  |  |  | 1129 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.88 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 8910.22 |  |  | 7727 |  |  |  | 1129 | [10 empty] | 88.22 |  |  |  | 88.22 | [5 empty] | 90.09 |  |  | 88.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.78 |  |  |  |  | 0.00
2010 |  |  |  | 9075.00 |  |  | 7934 |  |  |  | 1129 | [10 empty] | 90.58 |  |  |  | 90.58 | [5 empty] | 91.76 |  |  | 90.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.42 |  |  |  |  | 0.00
2011 |  |  |  | 10025.54 |  |  | 8716 |  |  |  | 1129 | [10 empty] | 99.50 |  |  |  | 99.50 | [5 empty] | 101.37 |  |  | 99.50 |  |  |  | 0.50 |  | 0.50 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 9061.97 |  |  | 7849 |  |  |  | 1146 | [10 empty] | 89.49 |  |  |  | 89.49 | [5 empty] | 90.35 |  |  | 89.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.51 |  |  |  |  | 0.00
2013 |  |  |  | 9065.55 |  |  | 7942 |  |  |  | 1146 | [10 empty] | 90.67 |  |  |  | 90.67 | [5 empty] | 90.29 |  |  | 90.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.33 |  |  |  |  | 0.00
2014 |  |  |  | 10091.90 |  |  | 8760 |  |  |  | 1146 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.53 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 9100.43 |  |  | 7886 |  |  |  | 1146 | [10 empty] | 90.01 |  |  |  | 90.01 | [5 empty] | 90.65 |  |  | 90.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.99 |  |  |  |  | 0.00
2016 |  |  |  | 9315.90 |  |  | 8090 |  |  |  | 1146 | [10 empty] | 92.10 |  |  |  | 92.10 | [5 empty] | 92.54 |  |  | 92.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.90 |  |  |  |  | 0.00
2017 |  |  |  | 10177.38 |  |  | 8760 |  |  |  | 1150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.03 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 9269.23 |  |  | 8080 |  |  |  | 1150 | [10 empty] | 92.23 |  |  |  | 92.23 | [5 empty] | 92.01 |  |  | 92.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.77 |  |  |  |  | 0.00
2019 |  |  |  | 9343.86 |  |  | 8155 |  |  |  | 1150 | [10 empty] | 93.10 |  |  |  | 93.10 | [5 empty] | 92.75 |  |  | 93.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.90 |  |  |  |  | 0.00
2020 |  |  |  | 10121.15 |  |  | 8783 |  |  |  | 1150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.19 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 279
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 695
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 52
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 3
H. |  | Nuclear regulatory requirements | [39 empty] | 4
L. |  | Human factor related | [39 empty] | 1
Z. |  | Other | [35 empty] | 0 |  |  |  | 6
Subtotal | [37 empty] | 750 |  |  |  | 293
Total | [22 empty] | 0 | [14 empty] | 1043
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 3
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 24
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 24
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 43
32. |  |  | Feedwater and Main Steam System | [34 empty] | 65
33. |  |  | Circulating Water System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 84
42. |  |  | Electrical Power Supply Systems | [34 empty] | 26
Total | [37 empty] | 290

## CLINTON-1
2020 Operating Experience
US-461 | [8 empty] | CLINTON-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-6 (Mark 3) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-10-01
Thermal power | [12 empty] | : |  |  | 3473 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-04-24
Gross electrical power | [12 empty] | : |  |  | 1098 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-11-24
Reference unit power (net) | [12 empty] | : |  |  | 1062 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.3
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 288.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.10
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.3 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.66
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 624 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Pond (closed-cycle)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.85 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 145 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9462.48 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.44 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 807.11 | 753.65 |  |  |  | 794.89 |  | 779.73 | [8 empty] | 802.66 |  |  | 771.26 | [6 empty] | 792.20 |  | 789.70 |  |  |  | 774.85 |  |  | 811.03 |  |  | 776.26 | [9 empty] | 809.14 |  |  | 9462.48
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 102.15 | 101.96 |  |  |  | 100.60 |  | 101.97 | [8 empty] | 101.59 |  |  | 100.87 | [6 empty] | 100.26 |  | 99.95 |  |  |  | 101.34 |  |  | 102.65 |  |  | 101.52 | [9 empty] | 102.41 |  |  | 101.44
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 229792.08 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.95 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.17 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.38 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.21 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.4 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.05 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.21 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 1628.83 |  |  | 3264 |  |  |  | 932 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 80.98 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 5860.74 |  |  | 7244 |  |  |  | 930 | [10 empty] | 82.50 |  |  |  | 82.50 | [5 empty] | 71.73 |  |  | 82.46 |  |  |  | 6.52 |  | 5.75 | [8 empty] | 11.75 |  |  |  |  | 0.00
1989 |  |  |  | 2861.90 |  |  | 3947 |  |  |  | 931 | [10 empty] | 45.13 |  |  |  | 45.13 | [5 empty] | 35.08 |  |  | 45.06 |  |  |  | 31.57 |  | 20.83 | [8 empty] | 34.04 |  |  |  |  | 0.00
1990 |  |  |  | 3596.62 |  |  | 4604 |  |  |  | 930 | [10 empty] | 52.57 |  |  |  | 52.57 | [5 empty] | 44.15 |  |  | 52.56 |  |  |  | 19.21 |  | 12.50 | [8 empty] | 34.93 |  |  |  |  | 0.00
1991 |  |  |  | 6048.01 |  |  | 6927 |  |  |  | 930 | [10 empty] | 79.10 |  |  |  | 79.10 | [5 empty] | 74.24 |  |  | 79.08 |  |  |  | 3.02 |  | 2.47 | [8 empty] | 18.44 |  |  |  |  | 0.00
1992 |  |  |  | 4935.26 |  |  | 5824 |  |  |  | 930 | [10 empty] | 66.31 |  |  |  | 66.31 | [5 empty] | 60.41 |  |  | 66.30 |  |  |  | 31.03 |  | 29.84 | [8 empty] | 3.85 |  |  |  |  | 0.00
1993 |  |  |  | 5879.18 |  |  | 6750 |  |  |  | 930 | [10 empty] | 77.05 |  |  |  | 77.10 | [5 empty] | 72.17 |  |  | 77.05 |  |  |  | 3.64 |  | 2.91 | [8 empty] | 19.99 |  |  |  |  | 0.05
1994 |  |  |  | 7410.34 |  |  | 8217 |  |  |  | 930 | [10 empty] | 93.85 |  |  |  | 93.85 | [5 empty] | 90.96 |  |  | 93.80 |  |  |  | 0.18 |  | 0.17 | [8 empty] | 5.98 |  |  |  |  | 0.00
1995 |  |  |  | 6109.18 |  |  | 7140 |  |  |  | 930 | [10 empty] | 81.60 |  |  |  | 81.60 | [5 empty] | 74.99 |  |  | 81.51 |  |  |  | 3.05 |  | 2.57 | [8 empty] | 15.83 |  |  |  |  | 0.00
1996 |  |  |  | 5312.93 |  |  | 5833 |  |  |  | 930 | [10 empty] | 66.46 |  |  |  | 66.46 | [5 empty] | 65.02 |  |  | 66.40 |  |  |  | 14.96 |  | 11.69 | [8 empty] | 21.85 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 930 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1998 |  |  |  | 0.00 |  |  | 0 |  |  |  | 930 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1999 |  |  |  | 4704.21 |  |  | 5270 |  |  |  | 930 | [10 empty] | 60.17 |  |  |  | 60.17 | [5 empty] | 57.74 |  |  | 60.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 39.83 |  |  |  |  | 0.00
2000 |  |  |  | 6888.84 |  |  | 7542 |  |  |  | 930 | [10 empty] | 85.89 |  |  |  | 85.89 | [5 empty] | 84.33 |  |  | 85.86 |  |  |  | 3.31 |  | 2.94 | [8 empty] | 11.16 |  |  |  |  | 0.00
2001 |  |  |  | 7877.25 |  |  | 8565 |  |  |  | 930 | [10 empty] | 97.80 |  |  |  | 97.80 | [5 empty] | 96.69 |  |  | 97.77 |  |  |  | 1.53 |  | 1.52 | [8 empty] | 0.69 |  |  |  |  | 0.00
2002 |  |  |  | 7657.46 |  |  | 7805 |  |  |  | 1022 | [10 empty] | 89.77 |  |  |  | 89.77 | [5 empty] | 88.84 |  |  | 89.10 |  |  |  | 1.35 |  | 1.22 | [8 empty] | 9.00 |  |  |  |  | 0.00
2003 |  |  |  | 8700.78 |  |  | 8634 |  |  |  | 1022 | [10 empty] | 98.62 |  |  |  | 98.62 | [5 empty] | 97.19 |  |  | 98.56 |  |  |  | 0.76 |  | 0.75 | [8 empty] | 0.63 |  |  |  |  | 0.00
2004 |  |  |  | 8000.42 |  |  | 7911 |  |  |  | 1022 | [10 empty] | 90.04 |  |  |  | 91.50 | [5 empty] | 89.12 |  |  | 90.06 |  |  |  | 1.94 |  | 1.81 | [8 empty] | 6.69 |  |  |  |  | 1.46
2005 |  |  |  | 8688.67 |  |  | 8497 |  |  |  | 1026 | [10 empty] | 97.01 |  |  |  | 97.01 | [5 empty] | 96.66 |  |  | 96.99 |  |  |  | 2.99 |  | 2.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 8233.30 |  |  | 7974 |  |  |  | 1052 | [10 empty] | 91.06 |  |  |  | 91.06 | [5 empty] | 89.34 |  |  | 91.03 |  |  |  | 1.44 |  | 1.33 | [8 empty] | 7.60 |  |  |  |  | 0.00
2007 |  |  |  | 9250.44 |  |  | 8714 |  |  |  | 1043 | [10 empty] | 99.48 |  |  |  | 99.48 | [5 empty] | 101.25 |  |  | 99.47 |  |  |  | 0.52 |  | 0.52 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8546.55 |  |  | 8160 |  |  |  | 1043 | [10 empty] | 92.90 |  |  |  | 92.90 | [5 empty] | 93.29 |  |  | 92.90 |  |  |  | 0.40 |  | 0.37 | [8 empty] | 6.72 |  |  |  |  | 0.00
2009 |  |  |  | 8887.91 |  |  | 8390 |  |  |  | 1043 | [10 empty] | 95.80 |  |  |  | 95.80 | [5 empty] | 97.28 |  |  | 95.78 |  |  |  | 4.20 |  | 4.20 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 8612.00 |  |  | 8089 |  |  |  | 1065 | [10 empty] | 92.51 |  |  |  | 92.51 | [5 empty] | 92.31 |  |  | 92.34 |  |  |  | 0.77 |  | 0.72 | [8 empty] | 6.76 |  |  |  |  | 0.00
2011 |  |  |  | 8671.47 |  |  | 8184 |  |  |  | 1065 | [10 empty] | 93.45 |  |  |  | 93.45 | [5 empty] | 92.95 |  |  | 93.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.55 |  |  |  |  | 0.00
2012 |  |  |  | 9373.73 |  |  | 8784 |  |  |  | 1065 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.20 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 8323.86 |  |  | 7861 |  |  |  | 1065 | [10 empty] | 89.74 |  |  |  | 89.74 | [5 empty] | 89.21 |  |  | 89.73 |  |  |  | 4.21 |  | 3.95 | [8 empty] | 6.32 |  |  |  |  | 0.00
2014 |  |  |  | 9098.05 |  |  | 8615 |  |  |  | 1065 | [10 empty] | 98.34 |  |  |  | 98.34 | [5 empty] | 97.52 |  |  | 98.34 |  |  |  | 0.47 |  | 0.47 | [8 empty] | 1.19 |  |  |  |  | 0.00
2015 |  |  |  | 8084.74 |  |  | 8167 |  |  |  | 1065 | [10 empty] | 93.24 |  |  |  | 93.24 | [5 empty] | 86.66 |  |  | 93.23 |  |  |  | 1.04 |  | 0.98 | [8 empty] | 5.78 |  |  |  |  | 0.00
2016 |  |  |  | 8915.50 |  |  | 8520 |  |  |  | 1065 | [10 empty] | 96.99 |  |  |  | 96.99 | [5 empty] | 95.30 |  |  | 96.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.01 |  |  |  |  | 0.00
2017 |  |  |  | 8357.89 |  |  | 7934 |  |  |  | 1062 | [10 empty] | 90.55 |  |  |  | 90.55 | [5 empty] | 89.84 |  |  | 90.57 |  |  |  | 3.62 |  | 3.40 | [8 empty] | 6.05 |  |  |  |  | 0.00
2018 |  |  |  | 8398.48 |  |  | 8027 |  |  |  | 1062 | [10 empty] | 91.95 |  |  |  | 91.95 | [5 empty] | 90.28 |  |  | 91.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.05 |  |  |  |  | 0.00
2019 |  |  |  | 8388.42 |  |  | 7899 |  |  |  | 1062 | [10 empty] | 90.19 |  |  |  | 90.19 | [5 empty] | 90.17 |  |  | 90.17 |  |  |  | 1.32 |  | 1.21 | [8 empty] | 8.61 |  |  |  |  | 0.00
2020 |  |  |  | 9462.48 |  |  | 8783 |  |  |  | 1062 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.44 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 255
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1202
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 130
E. |  | Testing of plant systems or components | [35 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 6
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 12
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
Z. |  | Other | [39 empty] | 36
Subtotal | [37 empty] | 1334 |  |  |  | 309 | [11 empty] | 4
Total | [22 empty] | 0 | [14 empty] | 1647
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 18
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 61
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 33
32. |  |  | Feedwater and Main Steam System | [34 empty] | 94
34. |  |  | Miscellaneous Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 13
42. |  |  | Electrical Power Supply Systems | [34 empty] | 30
Total | [37 empty] | 261

## COLUMBIA
2020 Operating Experience
US-397 | [8 empty] | COLUMBIA | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ENERGYNW (Energy Northwest)
Owner | [7 empty] | : | ENERGYNW (Energy Northwest)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 (Mark 2) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-08-01
Thermal power | [12 empty] | : |  |  | 3486 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-05-27
Gross electrical power | [12 empty] | : |  |  | 1190 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-12-13
Reference unit power (net) | [12 empty] | : |  |  | 1131 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.17
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.316
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 42000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.82
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 43 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9427.05 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.28 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.72 %
Load Factor (LF) | [18 empty] | : | 94.89 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.27 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 64 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 861.32 | 724.80 |  |  |  | 853.82 |  | 835.10 | [8 empty] | 788.14 |  |  | 420.42 | [6 empty] | 765.92 |  | 848.52 |  |  |  | 817.09 |  |  | 858.56 |  |  | 795.09 | [9 empty] | 858.27 |  |  | 9427.05
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 91.24 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.28
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 91.24 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.28
LF [%] |  |  |  |  | 102.36 | 92.08 |  |  |  | 101.47 |  | 102.55 | [8 empty] | 93.66 |  |  | 51.63 | [6 empty] | 91.02 |  | 100.84 |  |  |  | 100.34 |  |  | 102.03 |  |  | 97.64 | [9 empty] | 102.00 |  |  | 94.89
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 91.25 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.27
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 8.76 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.72
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 285920.22 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.09 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.51 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.07 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.53 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.71 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.56 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.36 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 1458.42 |  |  | 2393 |  |  |  | 1104 | [10 empty] | 90.49 |  |  |  | 90.49 | [5 empty] | 84.56 |  |  | 90.68 |  |  |  | 9.51 |  | 9.51 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 5176.39 |  |  | 6624 |  |  |  | 1100 | [10 empty] | 77.10 |  |  |  | 77.10 | [5 empty] | 53.70 |  |  | 75.62 |  |  |  | 8.28 |  | 6.96 | [8 empty] | 15.94 |  |  |  |  | 0.00
1986 |  |  |  | 5183.20 |  |  | 6133 |  |  |  | 1095 | [10 empty] | 74.11 |  |  |  | 74.11 | [5 empty] | 54.04 |  |  | 70.01 |  |  |  | 4.33 |  | 3.35 | [8 empty] | 22.54 |  |  |  |  | 0.00
1987 |  |  |  | 5397.98 |  |  | 5979 |  |  |  | 1095 | [10 empty] | 67.93 |  |  |  | 67.93 | [5 empty] | 56.27 |  |  | 68.25 |  |  |  | 8.83 |  | 6.58 | [8 empty] | 25.49 |  |  |  |  | 0.00
1988 |  |  |  | 6000.36 |  |  | 6020 |  |  |  | 1095 | [10 empty] | 68.24 |  |  |  | 68.24 | [5 empty] | 62.38 |  |  | 68.53 |  |  |  | 15.00 |  | 12.04 | [8 empty] | 19.72 |  |  |  |  | 0.00
1989 |  |  |  | 6127.94 |  |  | 6680 |  |  |  | 1095 | [10 empty] | 76.05 |  |  |  | 76.05 | [5 empty] | 63.88 |  |  | 76.26 |  |  |  | 4.41 |  | 3.51 | [8 empty] | 20.43 |  |  |  |  | 0.00
1990 |  |  |  | 5791.26 |  |  | 5752 |  |  |  | 1095 | [10 empty] | 65.31 |  |  |  | 65.31 | [5 empty] | 60.37 |  |  | 65.66 |  |  |  | 6.68 |  | 4.67 | [8 empty] | 30.02 |  |  |  |  | 0.00
1991 |  |  |  | 4272.55 |  |  | 4194 |  |  |  | 1090 | [10 empty] | 47.10 |  |  |  | 47.10 | [5 empty] | 44.75 |  |  | 47.88 |  |  |  | 42.75 |  | 35.16 | [8 empty] | 17.74 |  |  |  |  | 0.00
1992 |  |  |  | 5705.42 |  |  | 5505 |  |  |  | 1085 | [10 empty] | 61.96 |  |  |  | 61.96 | [5 empty] | 59.86 |  |  | 62.67 |  |  |  | 15.37 |  | 11.26 | [8 empty] | 26.78 |  |  |  |  | 0.00
1993 |  |  |  | 7141.96 |  |  | 6757 |  |  |  | 1107 | [10 empty] | 77.16 |  |  |  | 77.16 | [5 empty] | 73.61 |  |  | 77.13 |  |  |  | 8.30 |  | 6.98 | [8 empty] | 15.86 |  |  |  |  | 0.00
1994 |  |  |  | 6753.81 |  |  | 6500 |  |  |  | 1086 | [10 empty] | 73.73 |  |  |  | 73.73 | [5 empty] | 70.99 |  |  | 74.20 |  |  |  | 1.32 |  | 0.99 | [8 empty] | 25.29 |  |  |  |  | 0.00
1995 |  |  |  | 6947.98 |  |  | 6680 |  |  |  | 1091 | [10 empty] | 75.98 |  |  |  | 75.98 | [5 empty] | 72.67 |  |  | 76.26 |  |  |  | 5.02 |  | 4.02 | [8 empty] | 20.01 |  |  |  |  | 0.00
1996 |  |  |  | 5562.63 |  |  | 5999 |  |  |  | 1106 | [10 empty] | 68.30 |  |  |  | 79.66 | [5 empty] | 57.24 |  |  | 68.29 |  |  |  | 1.73 |  | 1.40 | [8 empty] | 18.94 |  |  |  |  | 11.36
1997 |  |  |  | 6129.89 |  |  | 6248 |  |  |  | 1107 | [10 empty] | 71.35 |  |  |  | 77.36 | [5 empty] | 63.21 |  |  | 71.32 |  |  |  | 0.21 |  | 0.16 | [8 empty] | 22.48 |  |  |  |  | 6.02
1998 |  |  |  | 6922.83 |  |  | 6373 |  |  |  | 1107 | [10 empty] | 72.78 |  |  |  | 72.78 | [5 empty] | 71.39 |  |  | 72.75 |  |  |  | 13.97 |  | 11.82 | [8 empty] | 15.40 |  |  |  |  | 0.00
1999 |  |  |  | 6099.69 |  |  | 6018 |  |  |  | 1107 | [10 empty] | 68.51 |  |  |  | 68.51 | [5 empty] | 62.90 |  |  | 68.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.49 |  |  |  |  | 0.00
2000 |  |  |  | 8605.23 |  |  | 8385 |  |  |  | 1107 | [10 empty] | 95.41 |  |  |  | 95.41 | [5 empty] | 88.50 |  |  | 95.46 |  |  |  | 3.21 |  | 3.16 | [8 empty] | 1.43 |  |  |  |  | 0.00
2001 |  |  |  | 8257.71 |  |  | 7553 |  |  |  | 1107 | [10 empty] | 86.14 |  |  |  | 86.14 | [5 empty] | 85.15 |  |  | 86.22 |  |  |  | 2.28 |  | 2.01 | [8 empty] | 11.85 |  |  |  |  | 0.00
2002 |  |  |  | 8981.29 |  |  | 8528 |  |  |  | 1107 | [10 empty] | 97.35 |  |  |  | 97.35 | [5 empty] | 92.62 |  |  | 97.35 |  |  |  | 2.65 |  | 2.65 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 7614.87 |  |  | 7039 |  |  |  | 1107 | [10 empty] | 80.39 |  |  |  | 80.39 | [5 empty] | 78.53 |  |  | 80.35 |  |  |  | 6.92 |  | 5.98 | [8 empty] | 13.63 |  |  |  |  | 0.00
2004 |  |  |  | 8981.58 |  |  | 8222 |  |  |  | 1107 | [10 empty] | 93.61 |  |  |  | 93.61 | [5 empty] | 92.37 |  |  | 93.60 |  |  |  | 6.39 |  | 6.39 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 8242.27 |  |  | 7537 |  |  |  | 1108 | [10 empty] | 86.05 |  |  |  | 86.05 | [5 empty] | 84.91 |  |  | 86.03 |  |  |  | 4.92 |  | 4.45 | [8 empty] | 9.50 |  |  |  |  | 0.00
2006 |  |  |  | 9328.28 |  |  | 8568 |  |  |  | 1131 | [10 empty] | 97.82 |  |  |  | 97.82 | [5 empty] | 94.15 |  |  | 97.81 |  |  |  | 2.18 |  | 2.18 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 8108.56 |  |  | 7481 |  |  |  | 1131 | [10 empty] | 85.43 |  |  |  | 85.43 | [5 empty] | 81.84 |  |  | 85.40 |  |  |  | 2.86 |  | 2.52 | [8 empty] | 12.05 |  |  |  |  | 0.00
2008 |  |  |  | 9269.64 |  |  | 8592 |  |  |  | 1131 | [10 empty] | 97.83 |  |  |  | 97.83 | [5 empty] | 93.31 |  |  | 97.81 |  |  |  | 0.71 |  | 0.70 | [8 empty] | 1.47 |  |  |  |  | 0.00
2009 |  |  |  | 6634.01 |  |  | 6382 |  |  |  | 1131 | [10 empty] | 72.93 |  |  |  | 72.93 | [5 empty] | 66.96 |  |  | 72.85 |  |  |  | 16.39 |  | 14.30 | [8 empty] | 12.77 |  |  |  |  | 0.00
2010 |  |  |  | 9241.13 |  |  | 8760 |  |  |  | 1131 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 93.27 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 4806.28 |  |  | 4466 |  |  |  | 1131 | [10 empty] | 51.01 |  |  |  | 51.96 | [5 empty] | 48.51 |  |  | 50.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 48.04 |  |  |  |  | 0.95
2012 |  |  |  | 9333.71 |  |  | 8545 |  |  |  | 1107 | [10 empty] | 97.28 |  |  |  | 97.28 | [5 empty] | 95.99 |  |  | 97.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.72 |  |  |  |  | 0.00
2013 |  |  |  | 8460.89 |  |  | 7678 |  |  |  | 1107 | [10 empty] | 87.65 |  |  |  | 87.65 | [5 empty] | 87.24 |  |  | 87.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.35 |  |  |  |  | 0.00
2014 |  |  |  | 9497.32 |  |  | 8760 |  |  |  | 1107 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.94 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 8160.91 |  |  | 7550 |  |  |  | 1107 | [10 empty] | 86.19 |  |  |  | 86.19 | [5 empty] | 84.16 |  |  | 86.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.81 |  |  |  |  | 0.00
2016 |  |  |  | 9625.62 |  |  | 8565 |  |  |  | 1107 | [10 empty] | 97.51 |  |  |  | 99.28 | [5 empty] | 98.99 |  |  | 97.51 |  |  |  | 0.72 |  | 0.72 | [8 empty] | 0.00 |  |  |  |  | 1.78
2017 |  |  |  | 8128.26 |  |  | 7548 |  |  |  | 1116 | [10 empty] | 86.22 |  |  |  | 86.22 | [5 empty] | 83.48 |  |  | 86.16 |  |  |  | 3.93 |  | 3.53 | [8 empty] | 10.25 |  |  |  |  | 0.00
2018 |  |  |  | 9708.44 |  |  | 8612 |  |  |  | 1131 | [10 empty] | 98.31 |  |  |  | 98.31 | [5 empty] | 97.99 |  |  | 98.31 |  |  |  | 1.69 |  | 1.69 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 8866.50 |  |  | 7770 |  |  |  | 1131 | [10 empty] | 88.70 |  |  |  | 88.70 | [5 empty] | 89.49 |  |  | 88.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.30 |  |  |  |  | 0.00
2020 |  |  |  | 9427.05 |  |  | 8720 |  |  |  | 1131 | [10 empty] | 99.28 |  |  |  | 99.28 | [5 empty] | 94.89 |  |  | 99.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.72 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 248
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1017
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 22 | [14 empty] | 94
E. |  | Testing of plant systems or components | [35 empty] | 17 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 99
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 42
L. |  | Human factor related | [39 empty] | 16
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 52 | [15 empty] | 2
Z. |  | Other | [20 empty] | 63 | [14 empty] | 2 |  |  |  | 21
Subtotal | [22 empty] | 85 | [14 empty] | 1182 |  |  |  | 385 | [11 empty] | 48
Total | [22 empty] | 85 | [14 empty] | 1615
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 11
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 27
15. |  |  | Reactor Cooling Systems | [34 empty] | 29
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 20
31. |  |  | Turbine and auxiliaries | [34 empty] | 78
32. |  |  | Feedwater and Main Steam System | [34 empty] | 29
33. |  |  | Circulating Water System | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 63
Total | [37 empty] | 273
Highlights (2020)
Dispatched by grid operator to go offline

## COMANCHE PEAK-1
2020 Operating Experience
US-445 | [8 empty] | COMANCHE PEAK-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LUMINANT (Luminant Generation Company, LLC)
Owner | [7 empty] | : | LUMINANT (Luminant Generation Company, LLC)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | AC (ALLIS CHALMERS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-12-19
Thermal power | [12 empty] | : |  |  | 3612 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-04-24
Gross electrical power | [12 empty] | : |  |  | 1259 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-08-13
Reference unit power (net) | [12 empty] | : |  |  | 1205 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.103
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.75
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.81 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9781.85 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.55 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.31 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.51 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.31 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.18 %
Load Factor (LF) | [18 empty] | : | 92.41 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.57 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 653 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 909.46 | 854.96 |  |  |  | 907.38 |  | 875.52 | [8 empty] | 900.30 |  |  | 870.87 | [6 empty] | 895.91 |  | 894.62 |  |  |  | 870.40 |  |  | 256.33 |  |  | 632.80 | [9 empty] | 913.30 |  |  | 9781.85
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 30.65 |  |  | 77.81 | [9 empty] | 100.00 |  |  | 92.31
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 30.65 |  |  | 77.81 | [9 empty] | 100.00 |  |  | 92.31
LF [%] |  |  |  |  | 101.44 | 101.94 |  |  |  | 101.21 |  | 100.91 | [8 empty] | 100.42 |  |  | 100.38 | [6 empty] | 99.93 |  | 99.79 |  |  |  | 100.32 |  |  | 28.59 |  |  | 72.94 | [9 empty] | 101.87 |  |  | 92.41
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 30.65 |  |  | 81.11 | [9 empty] | 100.00 |  |  | 92.57
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 7.45 | [9 empty] | 0.00 |  |  | 0.55
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 6.26 | [9 empty] | 0.00 |  |  | 0.51
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 69.35 |  |  | 15.93 | [9 empty] | 0.00 |  |  | 7.18
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 281135.26 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.52 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.62 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.63 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.98 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.14 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.5 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 3335.18 |  |  | 4399 |  |  |  | 1140 | [10 empty] | 80.61 |  |  |  | 80.61 | [5 empty] | 60.19 |  |  | 78.00 |  |  |  | 8.53 |  | 7.52 | [8 empty] | 11.87 |  |  |  |  | 0.00
1991 |  |  |  | 5360.52 |  |  | 5341 |  |  |  | 1150 | [10 empty] | 60.51 |  |  |  | 60.51 | [5 empty] | 53.21 |  |  | 60.97 |  |  |  | 12.05 |  | 8.29 | [8 empty] | 31.20 |  |  |  |  | 0.00
1992 |  |  |  | 6937.48 |  |  | 6947 |  |  |  | 1150 | [10 empty] | 79.11 |  |  |  | 79.11 | [5 empty] | 68.68 |  |  | 79.09 |  |  |  | 3.93 |  | 3.23 | [8 empty] | 17.66 |  |  |  |  | 0.00
1993 |  |  |  | 7150.44 |  |  | 6932 |  |  |  | 1150 | [10 empty] | 79.14 |  |  |  | 79.14 | [5 empty] | 70.98 |  |  | 79.13 |  |  |  | 1.92 |  | 1.55 | [8 empty] | 19.30 |  |  |  |  | 0.00
1994 |  |  |  | 9367.60 |  |  | 8653 |  |  |  | 1150 | [10 empty] | 98.78 |  |  |  | 98.78 | [5 empty] | 92.99 |  |  | 98.78 |  |  |  | 1.22 |  | 1.22 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 7803.75 |  |  | 7444 |  |  |  | 1150 | [10 empty] | 84.98 |  |  |  | 84.98 | [5 empty] | 77.46 |  |  | 84.98 |  |  |  | 3.11 |  | 2.73 | [8 empty] | 12.29 |  |  |  |  | 0.00
1996 |  |  |  | 7756.24 |  |  | 7265 |  |  |  | 1150 | [10 empty] | 82.73 |  |  |  | 83.00 | [5 empty] | 76.78 |  |  | 82.71 |  |  |  | 6.01 |  | 5.31 | [8 empty] | 11.69 |  |  |  |  | 0.27
1997 |  |  |  | 9478.88 |  |  | 8656 |  |  |  | 1150 | [10 empty] | 98.81 |  |  |  | 98.81 | [5 empty] | 94.09 |  |  | 98.81 |  |  |  | 1.19 |  | 1.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 8505.96 |  |  | 7848 |  |  |  | 1150 | [10 empty] | 89.59 |  |  |  | 89.59 | [5 empty] | 84.43 |  |  | 89.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.41 |  |  |  |  | 0.00
1999 |  |  |  | 8601.51 |  |  | 7922 |  |  |  | 1150 | [10 empty] | 90.44 |  |  |  | 90.44 | [5 empty] | 85.38 |  |  | 90.43 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.54 |  |  |  |  | 0.00
2000 |  |  |  | 9619.80 |  |  | 8784 |  |  |  | 1150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 95.23 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 8444.32 |  |  | 7781 |  |  |  | 1150 | [10 empty] | 88.86 |  |  |  | 88.86 | [5 empty] | 83.82 |  |  | 88.82 |  |  |  | 3.47 |  | 3.20 | [8 empty] | 7.95 |  |  |  |  | 0.00
2002 |  |  |  | 7785.26 |  |  | 7213 |  |  |  | 1150 | [10 empty] | 82.97 |  |  |  | 82.97 | [5 empty] | 77.28 |  |  | 82.34 |  |  |  | 5.99 |  | 5.29 | [8 empty] | 11.74 |  |  |  |  | 0.00
2003 |  |  |  | 9625.95 |  |  | 8653 |  |  |  | 1150 | [10 empty] | 98.85 |  |  |  | 98.85 | [5 empty] | 95.55 |  |  | 98.78 |  |  |  | 1.15 |  | 1.15 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 9018.13 |  |  | 7877 |  |  |  | 1150 | [10 empty] | 89.82 |  |  |  | 89.82 | [5 empty] | 89.27 |  |  | 89.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.18 |  |  |  |  | 0.00
2005 |  |  |  | 9217.83 |  |  | 8004 |  |  |  | 1084 | [10 empty] | 91.39 |  |  |  | 91.39 | [5 empty] | 97.07 |  |  | 91.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.61 |  |  |  |  | 0.00
2006 |  |  |  | 10297.95 |  |  | 8760 |  |  |  | 1150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.22 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 8596.75 |  |  | 7437 |  |  |  | 1150 | [10 empty] | 84.91 |  |  |  | 84.91 | [5 empty] | 85.34 |  |  | 84.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.09 |  |  |  |  | 0.00
2008 |  |  |  | 9658.71 |  |  | 8262 |  |  |  | 1209 | [10 empty] | 94.11 |  |  |  | 94.11 | [5 empty] | 94.80 |  |  | 94.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.89 |  |  |  |  | 0.00
2009 |  |  |  | 10640.87 |  |  | 8760 |  |  |  | 1209 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.47 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 9676.72 |  |  | 8074 |  |  |  | 1209 | [10 empty] | 92.19 |  |  |  | 92.19 | [5 empty] | 91.37 |  |  | 92.17 |  |  |  | 0.46 |  | 0.43 | [8 empty] | 7.38 |  |  |  |  | 0.00
2011 |  |  |  | 9667.76 |  |  | 8056 |  |  |  | 1209 | [10 empty] | 91.99 |  |  |  | 91.99 | [5 empty] | 91.28 |  |  | 91.96 |  |  |  | 2.51 |  | 2.37 | [8 empty] | 5.64 |  |  |  |  | 0.00
2012 |  |  |  | 10438.08 |  |  | 8537 |  |  |  | 1209 | [10 empty] | 97.20 |  |  |  | 97.20 | [5 empty] | 98.29 |  |  | 97.19 |  |  |  | 2.60 |  | 2.59 | [8 empty] | 0.21 |  |  |  |  | 0.00
2013 |  |  |  | 10028.69 |  |  | 8211 |  |  |  | 1205 | [10 empty] | 93.71 |  |  |  | 93.71 | [5 empty] | 95.00 |  |  | 93.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.29 |  |  |  |  | 0.00
2014 |  |  |  | 8976.75 |  |  | 7401 |  |  |  | 1209 | [10 empty] | 84.48 |  |  |  | 84.48 | [5 empty] | 84.76 |  |  | 84.49 |  |  |  | 0.90 |  | 0.77 | [8 empty] | 14.75 |  |  |  |  | 0.00
2015 |  |  |  | 10706.90 |  |  | 8760 |  |  |  | 1218 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.35 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 9821.67 |  |  | 8061 |  |  |  | 1218 | [10 empty] | 91.77 |  |  |  | 91.77 | [5 empty] | 91.80 |  |  | 91.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.23 |  |  |  |  | 0.00
2017 |  |  |  | 9795.19 |  |  | 8053 |  |  |  | 1218 | [10 empty] | 91.93 |  |  |  | 91.93 | [5 empty] | 91.80 |  |  | 91.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.07 |  |  |  |  | 0.00
2018 |  |  |  | 10733.89 |  |  | 8760 |  |  |  | 1218 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.60 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 9472.80 |  |  | 7895 |  |  |  | 1205 | [10 empty] | 90.03 |  |  |  | 90.03 | [5 empty] | 89.74 |  |  | 90.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.97 |  |  |  |  | 0.00
2020 |  |  |  | 9781.85 |  |  | 8131 |  |  |  | 1205 | [10 empty] | 92.31 |  |  |  | 92.31 | [5 empty] | 92.41 |  |  | 92.57 |  |  |  | 0.55 |  | 0.51 | [8 empty] | 7.18 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1990 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 113
B. |  | Refuelling without maintenance | [20 empty] | 631 | [14 empty] | 21
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 629
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 78
L. |  | Human factor related | [39 empty] | 11
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 5
Z. |  | Other | [24 empty] | 45 | [14 empty] | 1
Subtotal | [22 empty] | 631 |  |  |  | 45 | [10 empty] | 728 |  |  |  | 125 | [11 empty] | 5
Total | [22 empty] | 676 | [14 empty] | 858
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1990 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
16. |  |  | Steam generation systems | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 26
32. |  |  | Feedwater and Main Steam System | [34 empty] | 23
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 12
42. |  |  | Electrical Power Supply Systems | [34 empty] | 17
Total | [37 empty] | 116
Highlights (2020)
Refueling Outage 21 (1RF21).

## COMANCHE PEAK-2
2020 Operating Experience
US-446 | [8 empty] | COMANCHE PEAK-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LUMINANT (Luminant Generation Company, LLC)
Owner | [7 empty] | : | LUMINANT (Luminant Generation Company, LLC)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | AC (ALLIS CHALMERS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-12-19
Thermal power | [12 empty] | : |  |  | 3612 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-04-09
Gross electrical power | [12 empty] | : |  |  | 1250 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-08-03
Reference unit power (net) | [12 empty] | : |  |  | 1195 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.103
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 36000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.75
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.81 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9698.1 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.58 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.15 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.54 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.15 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.31 %
Load Factor (LF) | [18 empty] | : | 92.39 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.15 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 602 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 821.28 | 838.15 |  |  |  | 892.29 |  | 529.83 | [8 empty] | 520.29 |  |  | 854.63 | [6 empty] | 878.51 |  | 877.35 |  |  |  | 853.29 |  |  | 883.16 |  |  | 856.99 | [9 empty] | 892.33 |  |  | 9698.10
EAF [%] |  |  |  |  | 93.63 | 100.00 |  |  |  | 100.00 |  | 61.67 | [8 empty] | 62.65 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.15
UCF [%] |  |  |  |  | 93.63 | 100.00 |  |  |  | 100.00 |  | 61.67 | [8 empty] | 62.65 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.15
LF [%] |  |  |  |  | 92.37 | 100.77 |  |  |  | 100.36 |  | 61.58 | [8 empty] | 58.52 |  |  | 99.33 | [6 empty] | 98.81 |  | 98.68 |  |  |  | 99.17 |  |  | 99.33 |  |  | 99.60 | [9 empty] | 100.37 |  |  | 92.39
OF [%] |  |  |  |  | 93.68 | 100.00 |  |  |  | 99.87 |  | 61.67 | [8 empty] | 62.63 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.15
FLR [%] |  |  |  |  | 6.37 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.58
UCL [%] |  |  |  |  | 6.37 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.54
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 38.33 | [8 empty] | 37.35 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.31
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 237824.8 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.37 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.37 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.22 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.4 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.38 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.9 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.34 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 4131.71 |  |  | 4600 |  |  |  | 1150 | [10 empty] | 89.74 |  |  |  | 89.74 | [5 empty] | 82.77 |  |  | 89.74 |  |  |  | 10.26 |  | 10.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 5263.15 |  |  | 5697 |  |  |  | 1150 | [10 empty] | 65.07 |  |  |  | 65.07 | [5 empty] | 52.24 |  |  | 65.03 |  |  |  | 17.02 |  | 13.34 | [8 empty] | 21.59 |  |  |  |  | 0.00
1995 |  |  |  | 9166.58 |  |  | 8382 |  |  |  | 1150 | [10 empty] | 95.68 |  |  |  | 95.68 | [5 empty] | 90.99 |  |  | 95.68 |  |  |  | 1.60 |  | 1.55 | [8 empty] | 2.76 |  |  |  |  | 0.00
1996 |  |  |  | 7370.37 |  |  | 6911 |  |  |  | 1150 | [10 empty] | 78.68 |  |  |  | 79.42 | [5 empty] | 72.96 |  |  | 78.68 |  |  |  | 7.06 |  | 6.03 | [8 empty] | 14.55 |  |  |  |  | 0.74
1997 |  |  |  | 8062.05 |  |  | 7554 |  |  |  | 1150 | [10 empty] | 86.23 |  |  |  | 86.23 | [5 empty] | 80.03 |  |  | 86.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.77 |  |  |  |  | 0.00
1998 |  |  |  | 9345.30 |  |  | 8741 |  |  |  | 1150 | [10 empty] | 99.78 |  |  |  | 99.78 | [5 empty] | 92.77 |  |  | 99.78 |  |  |  | 0.22 |  | 0.22 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 8756.02 |  |  | 7901 |  |  |  | 1150 | [10 empty] | 90.19 |  |  |  | 90.19 | [5 empty] | 86.92 |  |  | 90.19 |  |  |  | 0.65 |  | 0.59 | [8 empty] | 9.21 |  |  |  |  | 0.00
2000 |  |  |  | 8868.05 |  |  | 7927 |  |  |  | 1150 | [10 empty] | 90.24 |  |  |  | 90.24 | [5 empty] | 87.79 |  |  | 90.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.76 |  |  |  |  | 0.00
2001 |  |  |  | 9877.95 |  |  | 8731 |  |  |  | 1150 | [10 empty] | 99.67 |  |  |  | 99.67 | [5 empty] | 98.05 |  |  | 99.67 |  |  |  | 0.33 |  | 0.33 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 8793.82 |  |  | 7888 |  |  |  | 1150 | [10 empty] | 90.11 |  |  |  | 90.11 | [5 empty] | 87.29 |  |  | 90.05 |  |  |  | 0.36 |  | 0.33 | [8 empty] | 9.56 |  |  |  |  | 0.00
2003 |  |  |  | 8123.39 |  |  | 7307 |  |  |  | 1150 | [10 empty] | 83.80 |  |  |  | 83.80 | [5 empty] | 80.64 |  |  | 83.41 |  |  |  | 10.11 |  | 9.43 | [8 empty] | 6.77 |  |  |  |  | 0.00
2004 |  |  |  | 10038.85 |  |  | 8784 |  |  |  | 1150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.38 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 9225.37 |  |  | 7979 |  |  |  | 1124 | [10 empty] | 91.10 |  |  |  | 91.10 | [5 empty] | 93.68 |  |  | 91.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.90 |  |  |  |  | 0.00
2006 |  |  |  | 9598.20 |  |  | 8260 |  |  |  | 1150 | [10 empty] | 94.30 |  |  |  | 94.30 | [5 empty] | 95.28 |  |  | 94.29 |  |  |  | 0.63 |  | 0.60 | [8 empty] | 5.10 |  |  |  |  | 0.00
2007 |  |  |  | 10249.00 |  |  | 8760 |  |  |  | 1150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.74 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 9575.91 |  |  | 8241 |  |  |  | 1150 | [10 empty] | 93.83 |  |  |  | 93.83 | [5 empty] | 94.80 |  |  | 93.82 |  |  |  | 0.41 |  | 0.39 | [8 empty] | 5.78 |  |  |  |  | 0.00
2009 |  |  |  | 9500.60 |  |  | 8155 |  |  |  | 1158 | [10 empty] | 93.15 |  |  |  | 93.15 | [5 empty] | 93.66 |  |  | 93.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.85 |  |  |  |  | 0.00
2010 |  |  |  | 10531.75 |  |  | 8760 |  |  |  | 1158 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.82 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 9751.59 |  |  | 8099 |  |  |  | 1197 | [10 empty] | 92.71 |  |  |  | 92.71 | [5 empty] | 93.00 |  |  | 92.45 |  |  |  | 1.00 |  | 0.94 | [8 empty] | 6.36 |  |  |  |  | 0.00
2012 |  |  |  | 9588.68 |  |  | 8027 |  |  |  | 1197 | [10 empty] | 91.41 |  |  |  | 91.41 | [5 empty] | 91.20 |  |  | 91.38 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 8.29 |  |  |  |  | 0.00
2013 |  |  |  | 10588.12 |  |  | 8721 |  |  |  | 1195 | [10 empty] | 99.55 |  |  |  | 99.55 | [5 empty] | 101.13 |  |  | 99.54 |  |  |  | 0.45 |  | 0.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 9784.63 |  |  | 8063 |  |  |  | 1197 | [10 empty] | 92.04 |  |  |  | 92.04 | [5 empty] | 93.31 |  |  | 92.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.96 |  |  |  |  | 0.00
2015 |  |  |  | 9393.65 |  |  | 7789 |  |  |  | 1207 | [10 empty] | 89.01 |  |  |  | 89.01 | [5 empty] | 88.84 |  |  | 88.92 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 10.97 |  |  |  |  | 0.00
2016 |  |  |  | 10682.62 |  |  | 8784 |  |  |  | 1207 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7262.76 |  |  | 6152 |  |  |  | 1207 | [10 empty] | 70.23 |  |  |  | 70.23 | [5 empty] | 68.69 |  |  | 70.23 |  |  |  | 22.57 |  | 20.48 | [8 empty] | 9.29 |  |  |  |  | 0.00
2018 |  |  |  | 9820.04 |  |  | 8141 |  |  |  | 1207 | [10 empty] | 93.01 |  |  |  | 93.01 | [5 empty] | 92.88 |  |  | 92.93 |  |  |  | 0.66 |  | 0.62 | [8 empty] | 6.37 |  |  |  |  | 0.00
2019 |  |  |  | 9965.35 |  |  | 8305 |  |  |  | 1195 | [10 empty] | 94.76 |  |  |  | 94.76 | [5 empty] | 95.20 |  |  | 94.81 |  |  |  | 0.30 |  | 0.29 | [8 empty] | 4.95 |  |  |  |  | 0.00
2020 |  |  |  | 9698.10 |  |  | 8182 |  |  |  | 1195 | [10 empty] | 93.15 |  |  |  | 93.15 | [5 empty] | 92.39 |  |  | 93.15 |  |  |  | 0.58 |  | 0.54 | [8 empty] | 6.31 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1993 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 182
B. |  | Refuelling without maintenance | [20 empty] | 554 | [14 empty] | 20
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 498
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 50
E. |  | Testing of plant systems or components | [35 empty] | 38
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 16
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 8
Z. |  | Other | [24 empty] | 47 | [14 empty] | 3
Subtotal | [22 empty] | 554 |  |  |  | 47 | [10 empty] | 614 |  |  |  | 186 | [11 empty] | 16
Total | [22 empty] | 601 | [14 empty] | 816
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1993 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 25
15. |  |  | Reactor Cooling Systems | [34 empty] | 33
16. |  |  | Steam generation systems | [34 empty] | 6
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 32
34. |  |  | Miscellaneous Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 63
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [37 empty] | 194
Highlights (2020)
Operators manually tripped the unit due to loss of both main feed water pumps.

## COOK-1
2020 Operating Experience
US-315 | [8 empty] | COOK-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | AEP (American Electric Power Company, Inc.)
Owner | [7 empty] | : | AEP (American Electric Power Company, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (ICECDN) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1969-03-25
Thermal power | [12 empty] | : |  |  | 3304 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-02-10
Gross electrical power | [12 empty] | : |  |  | 1131 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-08-28
Reference unit power (net) | [12 empty] | : |  |  | 1030 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 14.76
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 306
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.19
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.12
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 21.98 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8303.66 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.06 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.65 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.06 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.65 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.29 %
Load Factor (LF) | [18 empty] | : | 91.78 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.64 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 734 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 800.53 | 746.40 |  |  |  | 750.15 |  | 712.05 | [8 empty] | 790.04 |  |  | 743.74 | [6 empty] | 750.37 |  | 746.38 |  |  |  | 403.18 |  |  | 268.95 |  |  | 782.90 | [9 empty] | 808.98 |  |  | 8303.66
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 60.41 |  |  | 39.77 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.65
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 60.41 |  |  | 39.77 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.65
LF [%] |  |  |  |  | 104.46 | 104.12 |  |  |  | 97.89 |  | 96.02 | [8 empty] | 103.10 |  |  | 100.29 | [6 empty] | 97.92 |  | 97.40 |  |  |  | 54.37 |  |  | 35.10 |  |  | 105.57 | [9 empty] | 105.57 |  |  | 91.78
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 60.42 |  |  | 39.78 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.64
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 1.74 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.06
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.70 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.06
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 39.59 |  |  | 59.53 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.29
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 316292.4 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 15.17 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.88 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.06 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 73.01 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.93 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.66 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.13 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.41 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 4450.80 |  |  | 5955 |  |  |  | 848 | [10 empty] | 80.79 |  |  |  | 80.79 | [5 empty] | 80.81 |  |  | 82.48 |  |  |  | 5.03 |  | 4.28 | [8 empty] | 14.94 |  |  |  |  | 0.00
1976 |  |  |  | 6804.90 |  |  | 7298 |  |  |  | 983 | [10 empty] | 79.21 |  |  |  | 79.21 | [5 empty] | 78.81 |  |  | 83.08 |  |  |  | 3.86 |  | 3.18 | [8 empty] | 17.61 |  |  |  |  | 0.00
1977 |  |  |  | 4785.80 |  |  | 6658 |  |  |  | 1044 | [10 empty] | 52.38 |  |  |  | 52.38 | [5 empty] | 52.33 |  |  | 76.00 |  |  |  | 29.20 |  | 21.61 | [8 empty] | 26.02 |  |  |  |  | 0.00
1978 |  |  |  | 6286.90 |  |  | 6438 |  |  |  | 1044 | [10 empty] | 68.75 |  |  |  | 68.75 | [5 empty] | 68.74 |  |  | 73.49 |  |  |  | 6.67 |  | 4.91 | [8 empty] | 26.34 |  |  |  |  | 0.00
1979 |  |  |  | 5660.20 |  |  | 5666 |  |  |  | 1044 | [10 empty] | 61.89 |  |  |  | 61.89 | [5 empty] | 61.89 |  |  | 64.68 |  |  |  | 11.37 |  | 7.94 | [8 empty] | 30.17 |  |  |  |  | 0.00
1980 |  |  |  | 6461.30 |  |  | 6470 |  |  |  | 1044 | [10 empty] | 74.77 |  |  |  | 79.48 | [5 empty] | 70.46 |  |  | 73.66 |  |  |  | 0.99 |  | 0.79 | [8 empty] | 19.73 |  |  |  |  | 4.71
1981 |  |  |  | 6781.50 |  |  | 6663 |  |  |  | 1044 | [10 empty] | 77.13 |  |  |  | 77.13 | [5 empty] | 74.15 |  |  | 76.06 |  |  |  | 5.09 |  | 4.14 | [8 empty] | 18.73 |  |  |  |  | 0.00
1982 |  |  |  | 5352.70 |  |  | 5487 |  |  |  | 1044 | [10 empty] | 64.17 |  |  |  | 64.17 | [5 empty] | 58.53 |  |  | 62.64 |  |  |  | 15.78 |  | 12.02 | [8 empty] | 23.80 |  |  |  |  | 0.00
1983 |  |  |  | 5286.70 |  |  | 5628 |  |  |  | 1030 | [10 empty] | 64.33 |  |  |  | 64.33 | [5 empty] | 58.59 |  |  | 64.25 |  |  |  | 0.87 |  | 0.57 | [8 empty] | 35.11 |  |  |  |  | 0.00
1984 |  |  |  | 7550.76 |  |  | 8016 |  |  |  | 1020 | [10 empty] | 91.33 |  |  |  | 91.33 | [5 empty] | 84.27 |  |  | 91.26 |  |  |  | 4.92 |  | 4.72 | [8 empty] | 3.95 |  |  |  |  | 0.00
1985 |  |  |  | 2116.06 |  |  | 2489 |  |  |  | 1020 | [10 empty] | 29.85 |  |  |  | 29.85 | [5 empty] | 23.68 |  |  | 28.41 |  |  |  | 14.24 |  | 4.96 | [8 empty] | 65.19 |  |  |  |  | 0.00
1986 |  |  |  | 6650.07 |  |  | 7464 |  |  |  | 1020 | [10 empty] | 85.53 |  |  |  | 85.53 | [5 empty] | 74.43 |  |  | 85.21 |  |  |  | 14.46 |  | 14.46 | [8 empty] | 0.01 |  |  |  |  | 0.00
1987 |  |  |  | 5033.77 |  |  | 5917 |  |  |  | 1020 | [10 empty] | 68.21 |  |  |  | 68.21 | [5 empty] | 56.34 |  |  | 67.55 |  |  |  | 5.90 |  | 4.28 | [8 empty] | 27.52 |  |  |  |  | 0.00
1988 |  |  |  | 7467.79 |  |  | 8379 |  |  |  | 1020 | [10 empty] | 95.51 |  |  |  | 95.51 | [5 empty] | 83.35 |  |  | 95.39 |  |  |  | 1.79 |  | 1.74 | [8 empty] | 2.75 |  |  |  |  | 0.00
1989 |  |  |  | 5433.04 |  |  | 6069 |  |  |  | 1020 | [10 empty] | 69.90 |  |  |  | 69.90 | [5 empty] | 60.80 |  |  | 69.28 |  |  |  | 0.41 |  | 0.29 | [8 empty] | 29.81 |  |  |  |  | 0.00
1990 |  |  |  | 6301.64 |  |  | 6939 |  |  |  | 1020 | [10 empty] | 79.24 |  |  |  | 79.24 | [5 empty] | 70.53 |  |  | 79.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.76 |  |  |  |  | 0.00
1991 |  |  |  | 7338.24 |  |  | 7524 |  |  |  | 1013 | [10 empty] | 85.96 |  |  |  | 85.96 | [5 empty] | 82.67 |  |  | 85.89 |  |  |  | 2.91 |  | 2.58 | [8 empty] | 11.46 |  |  |  |  | 0.00
1992 |  |  |  | 4990.66 |  |  | 5690 |  |  |  | 1008 | [10 empty] | 65.09 |  |  |  | 65.09 | [5 empty] | 56.35 |  |  | 64.78 |  |  |  | 0.36 |  | 0.24 | [8 empty] | 34.67 |  |  |  |  | 0.00
1993 |  |  |  | 8759.43 |  |  | 8760 |  |  |  | 1006 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.34 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 5759.52 |  |  | 6214 |  |  |  | 1000 | [10 empty] | 70.96 |  |  |  | 70.96 | [5 empty] | 65.75 |  |  | 70.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.04 |  |  |  |  | 0.00
1995 |  |  |  | 5396.79 |  |  | 5809 |  |  |  | 1000 | [10 empty] | 66.37 |  |  |  | 66.37 | [5 empty] | 61.61 |  |  | 66.31 |  |  |  | 14.56 |  | 11.31 | [8 empty] | 22.32 |  |  |  |  | 0.00
1996 |  |  |  | 8373.26 |  |  | 8574 |  |  |  | 1000 | [10 empty] | 97.62 |  |  |  | 97.62 | [5 empty] | 95.32 |  |  | 97.61 |  |  |  | 2.38 |  | 2.38 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 4545.86 |  |  | 4608 |  |  |  | 1000 | [10 empty] | 52.41 |  |  |  | 52.41 | [5 empty] | 51.89 |  |  | 52.60 |  |  |  | 37.55 |  | 31.51 | [8 empty] | 16.07 |  |  |  |  | 0.00
1998 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1000 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1000 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 129.80 |  |  | 242 |  |  |  | 1000 | [10 empty] | 2.77 |  |  |  | 2.77 | [5 empty] | 1.48 |  |  | 2.76 |  |  |  | 97.23 |  | 97.23 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 7797.85 |  |  | 7840 |  |  |  | 1000 | [10 empty] | 89.53 |  |  |  | 90.55 | [5 empty] | 89.02 |  |  | 89.50 |  |  |  | 5.69 |  | 5.46 | [8 empty] | 3.98 |  |  |  |  | 1.03
2002 |  |  |  | 7740.90 |  |  | 7782 |  |  |  | 1000 | [10 empty] | 88.86 |  |  |  | 88.86 | [5 empty] | 88.37 |  |  | 88.84 |  |  |  | 1.23 |  | 1.11 | [8 empty] | 10.03 |  |  |  |  | 0.00
2003 |  |  |  | 6570.09 |  |  | 6489 |  |  |  | 1000 | [10 empty] | 74.10 |  |  |  | 74.10 | [5 empty] | 74.99 |  |  | 74.07 |  |  |  | 16.81 |  | 14.98 | [8 empty] | 10.92 |  |  |  |  | 0.00
2004 |  |  |  | 8831.48 |  |  | 8588 |  |  |  | 1000 | [10 empty] | 97.74 |  |  |  | 97.74 | [5 empty] | 100.54 |  |  | 97.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.26 |  |  |  |  | 0.00
2005 |  |  |  | 8055.85 |  |  | 7940 |  |  |  | 1016 | [10 empty] | 90.67 |  |  |  | 90.67 | [5 empty] | 90.50 |  |  | 90.63 |  |  |  | 0.28 |  | 0.25 | [8 empty] | 9.08 |  |  |  |  | 0.00
2006 |  |  |  | 7296.16 |  |  | 7256 |  |  |  | 1016 | [10 empty] | 82.85 |  |  |  | 82.85 | [5 empty] | 81.98 |  |  | 82.83 |  |  |  | 1.24 |  | 1.04 | [8 empty] | 16.11 |  |  |  |  | 0.00
2007 |  |  |  | 9252.68 |  |  | 8728 |  |  |  | 1009 | [10 empty] | 99.63 |  |  |  | 99.63 | [5 empty] | 104.68 |  |  | 99.63 |  |  |  | 0.37 |  | 0.37 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 5639.68 |  |  | 5407 |  |  |  | 1009 | [10 empty] | 61.57 |  |  |  | 61.57 | [5 empty] | 63.63 |  |  | 61.56 |  |  |  | 31.94 |  | 28.89 | [8 empty] | 9.54 |  |  |  |  | 0.00
2009 |  |  |  | 263.43 |  |  | 289 |  |  |  | 1009 | [10 empty] | 3.30 |  |  |  | 3.30 | [5 empty] | 2.98 |  |  | 3.30 |  |  |  | 96.70 |  | 96.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 7806.86 |  |  | 7859 |  |  |  | 1009 | [10 empty] | 89.73 |  |  |  | 89.73 | [5 empty] | 88.32 |  |  | 89.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.27 |  |  |  |  | 0.00
2011 |  |  |  | 7716.35 |  |  | 7716 |  |  |  | 1009 | [10 empty] | 88.11 |  |  |  | 88.11 | [5 empty] | 87.30 |  |  | 88.08 |  |  |  | 0.75 |  | 0.66 | [8 empty] | 11.23 |  |  |  |  | 0.00
2012 |  |  |  | 9224.63 |  |  | 8784 |  |  |  | 1045 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.49 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 7850.11 |  |  | 7470 |  |  |  | 1045 | [10 empty] | 85.49 |  |  |  | 85.49 | [5 empty] | 85.74 |  |  | 85.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.51 |  |  |  |  | 0.00
2014 |  |  |  | 8296.79 |  |  | 7974 |  |  |  | 1045 | [10 empty] | 91.16 |  |  |  | 91.16 | [5 empty] | 90.63 |  |  | 91.03 |  |  |  | 0.71 |  | 0.65 | [8 empty] | 8.19 |  |  |  |  | 0.00
2015 |  |  |  | 7822.53 |  |  | 7352 |  |  |  | 1045 | [10 empty] | 84.15 |  |  |  | 84.15 | [5 empty] | 85.45 |  |  | 83.93 |  |  |  | 15.85 |  | 15.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 8311.75 |  |  | 7914 |  |  |  | 1045 | [10 empty] | 90.09 |  |  |  | 90.09 | [5 empty] | 90.55 |  |  | 90.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.91 |  |  |  |  | 0.00
2017 |  |  |  | 7260.08 |  |  | 6932 |  |  |  | 1045 | [10 empty] | 78.29 |  |  |  | 78.29 | [5 empty] | 79.31 |  |  | 79.13 |  |  |  | 0.03 |  | 0.16 | [8 empty] | 21.55 |  |  |  |  | 0.00
2018 |  |  |  | 9299.54 |  |  | 8760 |  |  |  | 1030 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.07 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7343.23 |  |  | 7207 |  |  |  | 1030 | [10 empty] | 82.28 |  |  |  | 82.28 | [5 empty] | 81.39 |  |  | 82.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.72 |  |  |  |  | 0.00
2020 |  |  |  | 8303.66 |  |  | 8050 |  |  |  | 1030 | [10 empty] | 91.65 |  |  |  | 91.65 | [5 empty] | 91.78 |  |  | 91.64 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 8.29 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 419
B. |  | Refuelling without maintenance | [20 empty] | 1013 | [14 empty] | 22
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1059
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 102
E. |  | Testing of plant systems or components | [35 empty] | 7 |  |  |  | 5
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 686
L. |  | Human factor related | [39 empty] | 9
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
P. |  | Fire | [39 empty] | 11
Z. |  | Other | [24 empty] | 5 | [14 empty] | 1 | [11 empty] | 2
Subtotal | [22 empty] | 1013 |  |  |  | 5 | [10 empty] | 1192 |  |  |  | 1131 | [11 empty] | 6
Total | [22 empty] | 1018 | [14 empty] | 2329
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 15
14. |  |  | Safety Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 28
16. |  |  | Steam generation systems | [34 empty] | 6
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 289
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
33. |  |  | Circulating Water System | [34 empty] | 30
34. |  |  | Miscellaneous Systems | [34 empty] | 629
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 22
42. |  |  | Electrical Power Supply Systems | [34 empty] | 54
Total | [37 empty] | 1098
Highlights (2020)
Turb/Gen trip only following generator parallel (AR 2020-8808)

## COOK-2
2020 Operating Experience
US-316 | [8 empty] | COOK-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | AEP (American Electric Power Company, Inc.)
Owner | [7 empty] | : | AEP (American Electric Power Company, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | BB&C (BROWN BOVERI & CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (ICECDN) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1969-03-25
Thermal power | [12 empty] | : |  |  | 3468 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-03-22
Gross electrical power | [12 empty] | : |  |  | 1231 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1978-07-01
Reference unit power (net) | [12 empty] | : |  |  | 1168 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.82
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 319
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.19
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 48000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.81 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9962.98 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.11 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.89 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.11 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.89 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 97.11 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 95.89 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 361 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 904.02 | 841.06 |  |  |  | 895.95 |  | 864.87 | [8 empty] | 598.72 |  |  | 859.15 | [6 empty] | 864.86 |  | 862.44 |  |  |  | 723.28 |  |  | 787.73 |  |  | 867.02 | [9 empty] | 893.88 |  |  | 9962.98
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 69.07 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 88.99 |  |  | 93.13 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.89
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 69.07 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 88.99 |  |  | 93.13 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.89
LF [%] |  |  |  |  | 104.03 | 103.46 |  |  |  | 103.10 |  | 102.84 | [8 empty] | 68.90 |  |  | 102.16 | [6 empty] | 99.52 |  | 99.25 |  |  |  | 86.01 |  |  | 90.65 |  |  | 103.10 | [9 empty] | 102.86 |  |  | 97.11
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 69.09 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 89.03 |  |  | 93.15 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.89
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.93 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 11.01 |  |  | 6.88 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.11
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.93 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 11.01 |  |  | 6.88 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.11
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 295777.06 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 14.09 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 12.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.43 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.37 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.04 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.14 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.23 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1978 |  |  |  | 3814.00 |  |  | 4729 |  |  |  | 1078 | [10 empty] | 65.36 |  |  |  | 65.36 | [5 empty] | 65.34 |  |  | 77.22 |  |  |  | 21.39 |  | 17.78 | [8 empty] | 16.86 |  |  |  |  | 0.00
1979 |  |  |  | 5953.50 |  |  | 5773 |  |  |  | 1082 | [10 empty] | 62.81 |  |  |  | 62.81 | [5 empty] | 62.81 |  |  | 65.90 |  |  |  | 19.38 |  | 15.10 | [8 empty] | 22.08 |  |  |  |  | 0.00
1980 |  |  |  | 6691.20 |  |  | 6535 |  |  |  | 1082 | [10 empty] | 74.81 |  |  |  | 80.15 | [5 empty] | 70.40 |  |  | 74.40 |  |  |  | 16.26 |  | 15.56 | [8 empty] | 4.29 |  |  |  |  | 5.34
1981 |  |  |  | 6384.80 |  |  | 6178 |  |  |  | 1082 | [10 empty] | 71.21 |  |  |  | 71.21 | [5 empty] | 67.36 |  |  | 70.53 |  |  |  | 10.24 |  | 8.12 | [8 empty] | 20.67 |  |  |  |  | 0.00
1982 |  |  |  | 6995.60 |  |  | 6738 |  |  |  | 1082 | [10 empty] | 77.17 |  |  |  | 77.17 | [5 empty] | 73.81 |  |  | 76.92 |  |  |  | 13.09 |  | 11.62 | [8 empty] | 11.21 |  |  |  |  | 0.00
1983 |  |  |  | 7013.60 |  |  | 6835 |  |  |  | 1071 | [10 empty] | 78.32 |  |  |  | 78.32 | [5 empty] | 74.76 |  |  | 78.03 |  |  |  | 12.60 |  | 11.29 | [8 empty] | 10.39 |  |  |  |  | 0.00
1984 |  |  |  | 5364.36 |  |  | 5196 |  |  |  | 1060 | [10 empty] | 59.19 |  |  |  | 59.19 | [5 empty] | 57.61 |  |  | 59.15 |  |  |  | 10.64 |  | 7.05 | [8 empty] | 33.77 |  |  |  |  | 0.00
1985 |  |  |  | 5683.63 |  |  | 5852 |  |  |  | 1060 | [10 empty] | 66.85 |  |  |  | 66.85 | [5 empty] | 61.21 |  |  | 66.80 |  |  |  | 33.15 |  | 33.15 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 4335.57 |  |  | 5389 |  |  |  | 1060 | [10 empty] | 61.54 |  |  |  | 61.54 | [5 empty] | 46.69 |  |  | 61.52 |  |  |  | 3.41 |  | 2.17 | [8 empty] | 36.29 |  |  |  |  | 0.00
1987 |  |  |  | 5026.56 |  |  | 6248 |  |  |  | 1060 | [10 empty] | 71.38 |  |  |  | 71.38 | [5 empty] | 54.13 |  |  | 71.32 |  |  |  | 17.65 |  | 15.30 | [8 empty] | 13.32 |  |  |  |  | 0.00
1988 |  |  |  | 2323.26 |  |  | 2715 |  |  |  | 1060 | [10 empty] | 30.92 |  |  |  | 30.92 | [5 empty] | 24.95 |  |  | 30.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 69.08 |  |  |  |  | 0.00
1989 |  |  |  | 6660.99 |  |  | 6518 |  |  |  | 1060 | [10 empty] | 74.43 |  |  |  | 74.43 | [5 empty] | 71.73 |  |  | 74.41 |  |  |  | 1.50 |  | 1.14 | [8 empty] | 24.43 |  |  |  |  | 0.00
1990 |  |  |  | 4813.31 |  |  | 4854 |  |  |  | 1060 | [10 empty] | 55.42 |  |  |  | 55.42 | [5 empty] | 51.84 |  |  | 55.41 |  |  |  | 10.79 |  | 6.70 | [8 empty] | 37.88 |  |  |  |  | 0.00
1991 |  |  |  | 8185.91 |  |  | 8013 |  |  |  | 1065 | [10 empty] | 91.51 |  |  |  | 92.17 | [5 empty] | 87.74 |  |  | 91.47 |  |  |  | 7.83 |  | 7.83 | [8 empty] | 0.00 |  |  |  |  | 0.66
1992 |  |  |  | 1427.30 |  |  | 1714 |  |  |  | 1072 | [10 empty] | 20.47 |  |  |  | 20.47 | [5 empty] | 15.15 |  |  | 19.51 |  |  |  | 68.47 |  | 44.45 | [8 empty] | 35.08 |  |  |  |  | 0.00
1993 |  |  |  | 7553.81 |  |  | 8459 |  |  |  | 1070 | [10 empty] | 96.60 |  |  |  | 96.60 | [5 empty] | 80.60 |  |  | 96.56 |  |  |  | 3.40 |  | 3.40 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 3531.45 |  |  | 4757 |  |  |  | 1060 | [10 empty] | 54.38 |  |  |  | 54.38 | [5 empty] | 38.03 |  |  | 54.30 |  |  |  | 26.08 |  | 19.19 | [8 empty] | 26.43 |  |  |  |  | 0.00
1995 |  |  |  | 8602.53 |  |  | 8268 |  |  |  | 1060 | [10 empty] | 94.45 |  |  |  | 94.45 | [5 empty] | 92.64 |  |  | 94.38 |  |  |  | 5.55 |  | 5.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 8022.60 |  |  | 7641 |  |  |  | 1060 | [10 empty] | 87.01 |  |  |  | 87.01 | [5 empty] | 86.16 |  |  | 86.99 |  |  |  | 0.13 |  | 0.11 | [8 empty] | 12.88 |  |  |  |  | 0.00
1997 |  |  |  | 5875.21 |  |  | 5705 |  |  |  | 1060 | [10 empty] | 64.87 |  |  |  | 64.87 | [5 empty] | 63.27 |  |  | 65.12 |  |  |  | 14.76 |  | 11.23 | [8 empty] | 23.90 |  |  |  |  | 0.00
1998 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 98.15 | [8 empty] | 1.85 |  |  |  |  | 0.00
1999 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1060 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 4789.85 |  |  | 4557 |  |  |  | 1060 | [10 empty] | 51.88 |  |  |  | 51.88 | [5 empty] | 51.44 |  |  | 51.88 |  |  |  | 48.12 |  | 48.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 7963.43 |  |  | 7690 |  |  |  | 1060 | [10 empty] | 87.81 |  |  |  | 87.81 | [5 empty] | 85.76 |  |  | 87.79 |  |  |  | 12.19 |  | 12.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 7687.69 |  |  | 7335 |  |  |  | 1060 | [10 empty] | 83.80 |  |  |  | 83.80 | [5 empty] | 82.79 |  |  | 83.73 |  |  |  | 5.84 |  | 5.20 | [8 empty] | 11.00 |  |  |  |  | 0.00
2003 |  |  |  | 7112.17 |  |  | 6610 |  |  |  | 1060 | [10 empty] | 75.46 |  |  |  | 75.46 | [5 empty] | 76.59 |  |  | 75.46 |  |  |  | 13.38 |  | 11.66 | [8 empty] | 12.88 |  |  |  |  | 0.00
2004 |  |  |  | 7938.51 |  |  | 7407 |  |  |  | 1060 | [10 empty] | 84.33 |  |  |  | 84.33 | [5 empty] | 85.26 |  |  | 84.32 |  |  |  | 5.68 |  | 5.08 | [8 empty] | 10.59 |  |  |  |  | 0.00
2005 |  |  |  | 9415.54 |  |  | 8603 |  |  |  | 1077 | [10 empty] | 98.22 |  |  |  | 98.22 | [5 empty] | 99.79 |  |  | 98.20 |  |  |  | 0.97 |  | 0.96 | [8 empty] | 0.81 |  |  |  |  | 0.00
2006 |  |  |  | 8388.76 |  |  | 7732 |  |  |  | 1077 | [10 empty] | 88.28 |  |  |  | 88.28 | [5 empty] | 88.91 |  |  | 88.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.72 |  |  |  |  | 0.00
2007 |  |  |  | 8124.48 |  |  | 7492 |  |  |  | 1060 | [10 empty] | 85.30 |  |  |  | 85.30 | [5 empty] | 87.50 |  |  | 85.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.70 |  |  |  |  | 0.00
2008 |  |  |  | 9396.64 |  |  | 8650 |  |  |  | 1060 | [10 empty] | 98.48 |  |  |  | 98.48 | [5 empty] | 100.92 |  |  | 98.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.52 |  |  |  |  | 0.00
2009 |  |  |  | 8062.96 |  |  | 7434 |  |  |  | 1060 | [10 empty] | 84.88 |  |  |  | 84.88 | [5 empty] | 86.83 |  |  | 84.86 |  |  |  | 3.98 |  | 3.52 | [8 empty] | 11.60 |  |  |  |  | 0.00
2010 |  |  |  | 7839.20 |  |  | 7302 |  |  |  | 1060 | [10 empty] | 83.37 |  |  |  | 83.37 | [5 empty] | 84.42 |  |  | 83.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.63 |  |  |  |  | 0.00
2011 |  |  |  | 9641.90 |  |  | 8760 |  |  |  | 1077 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.20 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 8497.17 |  |  | 7818 |  |  |  | 1077 | [10 empty] | 89.03 |  |  |  | 89.03 | [5 empty] | 89.82 |  |  | 89.00 |  |  |  | 0.46 |  | 0.41 | [8 empty] | 10.56 |  |  |  |  | 0.00
2013 |  |  |  | 8430.45 |  |  | 7709 |  |  |  | 1077 | [10 empty] | 88.00 |  |  |  | 88.00 | [5 empty] | 89.35 |  |  | 87.99 |  |  |  | 0.75 |  | 0.66 | [8 empty] | 11.34 |  |  |  |  | 0.00
2014 |  |  |  | 9334.04 |  |  | 8505 |  |  |  | 1077 | [10 empty] | 97.09 |  |  |  | 97.09 | [5 empty] | 98.93 |  |  | 97.09 |  |  |  | 2.91 |  | 2.91 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 8696.59 |  |  | 7942 |  |  |  | 1107 | [10 empty] | 90.91 |  |  |  | 90.91 | [5 empty] | 89.68 |  |  | 90.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.09 |  |  |  |  | 0.00
2016 |  |  |  | 7048.50 |  |  | 6510 |  |  |  | 1107 | [10 empty] | 74.12 |  |  |  | 74.12 | [5 empty] | 72.49 |  |  | 74.11 |  |  |  | 2.42 |  | 1.84 | [8 empty] | 24.04 |  |  |  |  | 0.00
2017 |  |  |  | 10332.09 |  |  | 8717 |  |  |  | 1168 | [10 empty] | 99.53 |  |  |  | 99.53 | [5 empty] | 100.98 |  |  | 99.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.47 |  |  |  |  | 0.00
2018 |  |  |  | 8311.42 |  |  | 7056 |  |  |  | 1168 | [10 empty] | 80.55 |  |  |  | 80.55 | [5 empty] | 81.23 |  |  | 80.55 |  |  |  | 1.34 |  | 1.10 | [8 empty] | 18.35 |  |  |  |  | 0.00
2019 |  |  |  | 8816.66 |  |  | 7525 |  |  |  | 1168 | [10 empty] | 85.92 |  |  |  | 85.92 | [5 empty] | 86.17 |  |  | 85.90 |  |  |  | 1.16 |  | 1.01 | [8 empty] | 13.07 |  |  |  |  | 0.00
2020 |  |  |  | 9962.99 |  |  | 8423 |  |  |  | 1168 | [10 empty] | 95.89 |  |  |  | 95.89 | [5 empty] | 97.11 |  |  | 95.89 |  |  |  | 4.11 |  | 4.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1978 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 503
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1049
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 91
E. |  | Testing of plant systems or components | [35 empty] | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 546
L. |  | Human factor related | [39 empty] | 14
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [24 empty] | 361 | [14 empty] | 15
Subtotal | [26 empty] | 361 | [10 empty] | 1140 |  |  |  | 1078 | [11 empty] | 1
Total | [22 empty] | 361 | [14 empty] | 2219
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1978 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 0
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 36
15. |  |  | Reactor Cooling Systems | [34 empty] | 74
16. |  |  | Steam generation systems | [34 empty] | 131
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 115
32. |  |  | Feedwater and Main Steam System | [34 empty] | 17
33. |  |  | Circulating Water System | [34 empty] | 38
34. |  |  | Miscellaneous Systems | [34 empty] | 525
35. |  |  | All other I&C Systems | [34 empty] | 10
41. |  |  | Main Generator Systems | [34 empty] | 33
42. |  |  | Electrical Power Supply Systems | [34 empty] | 33
Total | [37 empty] | 1032
Highlights (2020)
Operational Procedure Error AR 2020-8488

## COOPER
2020 Operating Experience
US-298 | [8 empty] | COOPER | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Owner | [7 empty] | : | NPPD (NEBRASKA PUBLIC POWER DISTRICT)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-06-01
Thermal power | [12 empty] | : |  |  | 2419 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-05-10
Gross electrical power | [12 empty] | : |  |  | 801 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-07-01
Reference unit power (net) | [12 empty] | : |  |  | 769 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.28
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 285
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 17349 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.03 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.83
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 548 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 43.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 137 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6188.55 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.73 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.04 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.67 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.04 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.29 %
Load Factor (LF) | [18 empty] | : | 91.62 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.04 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 787 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 599.02 | 555.27 |  |  |  | 589.73 |  | 576.02 | [8 empty] | 588.37 |  |  | 562.03 | [6 empty] | 569.90 |  | 556.02 |  |  |  | 415.83 |  |  | 73.06 |  |  | 520.87 | [9 empty] | 582.42 |  |  | 6188.55
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 86.11 |  |  | 15.54 |  |  | 91.80 | [9 empty] | 100.00 |  |  | 91.04
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 86.11 |  |  | 15.54 |  |  | 91.80 | [9 empty] | 100.00 |  |  | 91.04
LF [%] |  |  |  |  | 104.70 | 103.74 |  |  |  | 103.08 |  | 104.04 | [8 empty] | 102.84 |  |  | 101.51 | [6 empty] | 99.61 |  | 97.18 |  |  |  | 75.10 |  |  | 12.77 |  |  | 94.07 | [9 empty] | 101.80 |  |  | 91.62
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 86.11 |  |  | 15.59 |  |  | 91.94 | [9 empty] | 100.00 |  |  | 91.04
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 8.20 | [9 empty] | 0.00 |  |  | 0.73
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 8.20 | [9 empty] | 0.00 |  |  | 0.67
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 13.89 |  |  | 84.46 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.29
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 223317.54 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.64 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.69 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.76 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.73 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.51 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.46 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.76 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 1885.60 |  |  | 3897 |  |  |  | 778 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 50.66 |  |  | 73.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1975 |  |  |  | 3363.20 |  |  | 7320 |  |  |  | 764 | [10 empty] | 50.30 |  |  |  | 50.30 | [5 empty] | 50.25 |  |  | 83.56 |  |  |  | 30.39 |  | 21.96 | [8 empty] | 27.73 |  |  |  |  | 0.00
1976 |  |  |  | 3642.60 |  |  | 6626 |  |  |  | 764 | [10 empty] | 54.32 |  |  |  | 54.32 | [5 empty] | 54.28 |  |  | 75.43 |  |  |  | 10.82 |  | 6.59 | [8 empty] | 39.08 |  |  |  |  | 0.00
1977 |  |  |  | 4540.10 |  |  | 7546 |  |  |  | 764 | [10 empty] | 67.89 |  |  |  | 67.89 | [5 empty] | 67.84 |  |  | 86.14 |  |  |  | 11.41 |  | 8.74 | [8 empty] | 23.36 |  |  |  |  | 0.00
1978 |  |  |  | 4886.80 |  |  | 7966 |  |  |  | 764 | [10 empty] | 73.01 |  |  |  | 73.01 | [5 empty] | 73.02 |  |  | 90.94 |  |  |  | 2.19 |  | 1.64 | [8 empty] | 25.35 |  |  |  |  | 0.00
1979 |  |  |  | 4995.00 |  |  | 7670 |  |  |  | 764 | [10 empty] | 74.63 |  |  |  | 74.63 | [5 empty] | 74.63 |  |  | 87.56 |  |  |  | 8.86 |  | 7.26 | [8 empty] | 18.11 |  |  |  |  | 0.00
1980 |  |  |  | 3787.50 |  |  | 6240 |  |  |  | 764 | [10 empty] | 70.59 |  |  |  | 71.64 | [5 empty] | 56.44 |  |  | 71.04 |  |  |  | 1.41 |  | 1.03 | [8 empty] | 27.33 |  |  |  |  | 1.05
1981 |  |  |  | 3851.10 |  |  | 6239 |  |  |  | 764 | [10 empty] | 71.00 |  |  |  | 71.00 | [5 empty] | 57.54 |  |  | 71.22 |  |  |  | 2.02 |  | 1.47 | [8 empty] | 27.54 |  |  |  |  | 0.00
1982 |  |  |  | 5276.10 |  |  | 7412 |  |  |  | 764 | [10 empty] | 84.39 |  |  |  | 84.39 | [5 empty] | 78.83 |  |  | 84.61 |  |  |  | 2.74 |  | 2.38 | [8 empty] | 13.23 |  |  |  |  | 0.00
1983 |  |  |  | 3343.30 |  |  | 5544 |  |  |  | 764 | [10 empty] | 62.68 |  |  |  | 62.68 | [5 empty] | 49.95 |  |  | 63.29 |  |  |  | 3.08 |  | 1.99 | [8 empty] | 35.33 |  |  |  |  | 0.00
1984 |  |  |  | 3469.95 |  |  | 5901 |  |  |  | 764 | [10 empty] | 67.14 |  |  |  | 67.64 | [5 empty] | 51.71 |  |  | 67.18 |  |  |  | 1.52 |  | 1.04 | [8 empty] | 31.31 |  |  |  |  | 0.50
1985 |  |  |  | 1067.75 |  |  | 1884 |  |  |  | 764 | [10 empty] | 20.09 |  |  |  | 20.09 | [5 empty] | 15.95 |  |  | 21.51 |  |  |  | 40.65 |  | 13.76 | [8 empty] | 66.14 |  |  |  |  | 0.00
1986 |  |  |  | 4052.14 |  |  | 6546 |  |  |  | 764 | [10 empty] | 74.71 |  |  |  | 74.71 | [5 empty] | 60.55 |  |  | 74.73 |  |  |  | 1.27 |  | 0.96 | [8 empty] | 24.33 |  |  |  |  | 0.00
1987 |  |  |  | 5522.13 |  |  | 8291 |  |  |  | 764 | [10 empty] | 94.61 |  |  |  | 94.61 | [5 empty] | 82.51 |  |  | 94.65 |  |  |  | 3.93 |  | 3.87 | [8 empty] | 1.52 |  |  |  |  | 0.00
1988 |  |  |  | 4200.61 |  |  | 5887 |  |  |  | 764 | [10 empty] | 66.47 |  |  |  | 66.47 | [5 empty] | 62.59 |  |  | 67.02 |  |  |  | 5.92 |  | 4.18 | [8 empty] | 29.35 |  |  |  |  | 0.00
1989 |  |  |  | 4790.90 |  |  | 6594 |  |  |  | 764 | [10 empty] | 74.91 |  |  |  | 74.91 | [5 empty] | 71.58 |  |  | 75.27 |  |  |  | 6.64 |  | 5.33 | [8 empty] | 19.76 |  |  |  |  | 0.00
1990 |  |  |  | 5111.39 |  |  | 6908 |  |  |  | 764 | [10 empty] | 78.49 |  |  |  | 78.49 | [5 empty] | 76.37 |  |  | 78.86 |  |  |  | 4.42 |  | 3.63 | [8 empty] | 17.88 |  |  |  |  | 0.00
1991 |  |  |  | 4803.81 |  |  | 6830 |  |  |  | 764 | [10 empty] | 77.93 |  |  |  | 77.93 | [5 empty] | 71.78 |  |  | 77.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.07 |  |  |  |  | 0.00
1992 |  |  |  | 6227.93 |  |  | 8436 |  |  |  | 764 | [10 empty] | 95.97 |  |  |  | 95.97 | [5 empty] | 92.80 |  |  | 96.04 |  |  |  | 1.56 |  | 1.52 | [8 empty] | 2.52 |  |  |  |  | 0.00
1993 |  |  |  | 3712.86 |  |  | 5041 |  |  |  | 764 | [10 empty] | 56.77 |  |  |  | 56.77 | [5 empty] | 55.48 |  |  | 57.55 |  |  |  | 3.13 |  | 1.84 | [8 empty] | 41.40 |  |  |  |  | 0.00
1994 |  |  |  | 2227.26 |  |  | 3033 |  |  |  | 764 | [10 empty] | 33.44 |  |  |  | 33.44 | [5 empty] | 33.28 |  |  | 34.62 |  |  |  | 66.56 |  | 66.56 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 4127.76 |  |  | 5663 |  |  |  | 764 | [10 empty] | 64.03 |  |  |  | 64.03 | [5 empty] | 61.68 |  |  | 64.65 |  |  |  | 18.35 |  | 14.39 | [8 empty] | 21.58 |  |  |  |  | 0.00
1996 |  |  |  | 6338.90 |  |  | 8540 |  |  |  | 764 | [10 empty] | 97.19 |  |  |  | 97.19 | [5 empty] | 94.46 |  |  | 97.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.81 |  |  |  |  | 0.00
1997 |  |  |  | 5455.70 |  |  | 7336 |  |  |  | 764 | [10 empty] | 83.64 |  |  |  | 83.64 | [5 empty] | 81.52 |  |  | 83.74 |  |  |  | 1.76 |  | 1.50 | [8 empty] | 14.86 |  |  |  |  | 0.00
1998 |  |  |  | 4869.91 |  |  | 6544 |  |  |  | 764 | [10 empty] | 74.41 |  |  |  | 74.41 | [5 empty] | 72.77 |  |  | 74.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.59 |  |  |  |  | 0.00
1999 |  |  |  | 6510.41 |  |  | 8563 |  |  |  | 764 | [10 empty] | 97.74 |  |  |  | 97.74 | [5 empty] | 97.28 |  |  | 97.75 |  |  |  | 2.26 |  | 2.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 4735.94 |  |  | 6414 |  |  |  | 764 | [10 empty] | 73.11 |  |  |  | 73.11 | [5 empty] | 70.57 |  |  | 73.02 |  |  |  | 16.33 |  | 14.27 | [8 empty] | 12.62 |  |  |  |  | 0.00
2001 |  |  |  | 5206.54 |  |  | 7009 |  |  |  | 764 | [10 empty] | 79.95 |  |  |  | 79.95 | [5 empty] | 77.80 |  |  | 80.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.05 |  |  |  |  | 0.00
2002 |  |  |  | 6318.15 |  |  | 8478 |  |  |  | 764 | [10 empty] | 96.83 |  |  |  | 96.83 | [5 empty] | 94.40 |  |  | 96.78 |  |  |  | 2.89 |  | 2.88 | [8 empty] | 0.30 |  |  |  |  | 0.00
2003 |  |  |  | 4492.33 |  |  | 6236 |  |  |  | 764 | [10 empty] | 71.29 |  |  |  | 71.29 | [5 empty] | 67.12 |  |  | 71.19 |  |  |  | 17.41 |  | 15.03 | [8 empty] | 13.68 |  |  |  |  | 0.00
2004 |  |  |  | 6171.77 |  |  | 8299 |  |  |  | 764 | [10 empty] | 94.55 |  |  |  | 94.55 | [5 empty] | 91.97 |  |  | 94.48 |  |  |  | 5.45 |  | 5.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 5891.92 |  |  | 7774 |  |  |  | 757 | [10 empty] | 88.77 |  |  |  | 88.77 | [5 empty] | 88.84 |  |  | 88.73 |  |  |  | 1.84 |  | 1.67 | [8 empty] | 9.57 |  |  |  |  | 0.00
2006 |  |  |  | 5910.48 |  |  | 7823 |  |  |  | 760 | [10 empty] | 89.34 |  |  |  | 89.34 | [5 empty] | 88.78 |  |  | 89.30 |  |  |  | 1.69 |  | 1.53 | [8 empty] | 9.13 |  |  |  |  | 0.00
2007 |  |  |  | 6671.25 |  |  | 8685 |  |  |  | 758 | [10 empty] | 99.14 |  |  |  | 99.14 | [5 empty] | 100.47 |  |  | 99.14 |  |  |  | 0.86 |  | 0.86 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 5964.14 |  |  | 7825 |  |  |  | 770 | [10 empty] | 89.06 |  |  |  | 89.06 | [5 empty] | 88.52 |  |  | 89.08 |  |  |  | 0.92 |  | 0.83 | [8 empty] | 10.11 |  |  |  |  | 0.00
2009 |  |  |  | 5734.58 |  |  | 7494 |  |  |  | 769 | [10 empty] | 85.54 |  |  |  | 85.54 | [5 empty] | 85.13 |  |  | 85.55 |  |  |  | 1.75 |  | 1.52 | [8 empty] | 12.94 |  |  |  |  | 0.00
2010 |  |  |  | 6792.88 |  |  | 8760 |  |  |  | 774 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.19 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 5768.10 |  |  | 7376 |  |  |  | 774 | [10 empty] | 84.21 |  |  |  | 84.21 | [5 empty] | 85.07 |  |  | 84.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.79 |  |  |  |  | 0.00
2012 |  |  |  | 5822.50 |  |  | 7657 |  |  |  | 768 | [10 empty] | 87.19 |  |  |  | 87.19 | [5 empty] | 86.31 |  |  | 87.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.81 |  |  |  |  | 0.00
2013 |  |  |  | 6801.93 |  |  | 8760 |  |  |  | 766 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.36 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 5915.35 |  |  | 7726 |  |  |  | 768 | [10 empty] | 88.20 |  |  |  | 88.20 | [5 empty] | 87.93 |  |  | 88.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.80 |  |  |  |  | 0.00
2015 |  |  |  | 6798.49 |  |  | 8692 |  |  |  | 768 | [10 empty] | 99.23 |  |  |  | 99.23 | [5 empty] | 101.05 |  |  | 99.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.77 |  |  |  |  | 0.00
2016 |  |  |  | 5922.80 |  |  | 7701 |  |  |  | 768 | [10 empty] | 87.67 |  |  |  | 87.67 | [5 empty] | 87.80 |  |  | 87.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.33 |  |  |  |  | 0.00
2017 |  |  |  | 6912.38 |  |  | 8741 |  |  |  | 769 | [10 empty] | 99.79 |  |  |  | 99.79 | [5 empty] | 102.61 |  |  | 99.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.21 |  |  |  |  | 0.00
2018 |  |  |  | 5632.14 |  |  | 7306 |  |  |  | 769 | [10 empty] | 83.39 |  |  |  | 83.39 | [5 empty] | 83.61 |  |  | 83.40 |  |  |  | 3.74 |  | 3.24 | [8 empty] | 13.37 |  |  |  |  | 0.00
2019 |  |  |  | 6951.60 |  |  | 8760 |  |  |  | 769 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.19 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 6188.55 |  |  | 7997 |  |  |  | 769 | [10 empty] | 91.04 |  |  |  | 91.04 | [5 empty] | 91.62 |  |  | 91.04 |  |  |  | 0.73 |  | 0.67 | [8 empty] | 8.29 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 161
B. |  | Refuelling without maintenance | [20 empty] | 728 | [14 empty] | 16
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1088
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 118
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 141
H. |  | Nuclear regulatory requirements | [39 empty] | 8
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 7
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
P. |  | Fire | [39 empty] | 3
Z. |  | Other | [24 empty] | 59 | [14 empty] | 33
Subtotal | [22 empty] | 728 |  |  |  | 59 | [10 empty] | 1223 |  |  |  | 353 | [11 empty] | 3
Total | [22 empty] | 787 | [14 empty] | 1579
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 20
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 14
31. |  |  | Turbine and auxiliaries | [34 empty] | 68
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
34. |  |  | Miscellaneous Systems | [34 empty] | 156
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 13
Total | [37 empty] | 309
Highlights (2020)
Equipment Condition Resolved

## DAVIS BESSE-1
2020 Operating Experience
US-346 | [8 empty] | DAVIS BESSE-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FENOC (FIRST ENERGY NUCLEAR OPERATING CO.)
Owner | [7 empty] | : | CEI (CLEVELAND ELECTRIC ILLUMINATING CO.)
Reactor Supplier | [7 empty] | : | B&W (BABCOCK & WILCOX CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / B&W RLP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-09-01
Thermal power | [12 empty] | : |  |  | 2817 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-08-28
Gross electrical power | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1978-07-31
Reference unit power (net) | [12 empty] | : |  |  | 894 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.38
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.9 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.22
| Active core height/length [m] | [13 empty] | : |  |  | 3.57 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 21.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7228.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.57 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.57 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.43 %
Load Factor (LF) | [18 empty] | : | 92.04 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.55 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 654 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 662.77 | 497.61 |  |  |  | 80.58 |  | 644.30 | [8 empty] | 677.54 |  |  | 650.29 | [6 empty] | 669.01 |  | 671.79 |  |  |  | 653.72 |  |  | 679.26 |  |  | 660.11 | [9 empty] | 681.08 |  |  | 7228.06
EAF [%] |  |  |  |  | 100.00 | 96.56 |  |  |  | 15.51 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.57
UCF [%] |  |  |  |  | 100.00 | 96.56 |  |  |  | 15.51 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.57
LF [%] |  |  |  |  | 99.64 | 79.97 |  |  |  | 12.12 |  | 100.10 | [8 empty] | 101.86 |  |  | 101.03 | [6 empty] | 100.58 |  | 101.00 |  |  |  | 101.56 |  |  | 102.12 |  |  | 102.55 | [9 empty] | 102.40 |  |  | 92.04
OF [%] |  |  |  |  | 100.00 | 96.55 |  |  |  | 15.32 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.55
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 3.44 |  |  |  | 84.49 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.43
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 243488.09 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.19 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.12 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.51 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.2 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.29 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.49 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.08 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.5 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1978 |  |  |  | 2614.50 |  |  | 4263 |  |  |  | 906 | [10 empty] | 39.26 |  |  |  | 39.26 | [5 empty] | 39.27 |  |  | 54.72 |  |  |  | 49.49 |  | 38.46 | [8 empty] | 22.28 |  |  |  |  | 0.00
1979 |  |  |  | 3129.10 |  |  | 4139 |  |  |  | 906 | [10 empty] | 39.43 |  |  |  | 39.43 | [5 empty] | 39.43 |  |  | 47.25 |  |  |  | 36.36 |  | 22.52 | [8 empty] | 38.05 |  |  |  |  | 0.00
1980 |  |  |  | 2093.60 |  |  | 3171 |  |  |  | 892 | [10 empty] | 34.95 |  |  |  | 34.95 | [5 empty] | 26.72 |  |  | 36.10 |  |  |  | 14.18 |  | 5.78 | [8 empty] | 59.27 |  |  |  |  | 0.00
1981 |  |  |  | 4363.40 |  |  | 5902 |  |  |  | 888 | [10 empty] | 67.39 |  |  |  | 67.39 | [5 empty] | 56.09 |  |  | 67.37 |  |  |  | 28.77 |  | 27.22 | [8 empty] | 5.39 |  |  |  |  | 0.00
1982 |  |  |  | 3218.10 |  |  | 4508 |  |  |  | 874 | [10 empty] | 51.52 |  |  |  | 51.52 | [5 empty] | 42.03 |  |  | 51.46 |  |  |  | 1.18 |  | 0.61 | [8 empty] | 47.87 |  |  |  |  | 0.00
1983 |  |  |  | 4883.30 |  |  | 6389 |  |  |  | 874 | [10 empty] | 72.26 |  |  |  | 72.26 | [5 empty] | 63.78 |  |  | 72.93 |  |  |  | 10.53 |  | 8.51 | [8 empty] | 19.23 |  |  |  |  | 0.00
1984 |  |  |  | 4291.56 |  |  | 5486 |  |  |  | 874 | [10 empty] | 62.48 |  |  |  | 62.48 | [5 empty] | 55.90 |  |  | 62.45 |  |  |  | 11.02 |  | 7.74 | [8 empty] | 29.78 |  |  |  |  | 0.00
1985 |  |  |  | 1942.92 |  |  | 2729 |  |  |  | 862 | [10 empty] | 30.92 |  |  |  | 30.92 | [5 empty] | 25.72 |  |  | 31.15 |  |  |  | 64.96 |  | 57.33 | [8 empty] | 11.75 |  |  |  |  | 0.00
1986 |  |  |  | 3.49 |  |  | 116 |  |  |  | 860 | [10 empty] | 1.33 |  |  |  | 1.33 | [5 empty] | 0.05 |  |  | 1.32 |  |  |  | 98.67 |  | 98.67 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 5063.98 |  |  | 7308 |  |  |  | 860 | [10 empty] | 82.82 |  |  |  | 82.82 | [5 empty] | 67.22 |  |  | 83.42 |  |  |  | 6.91 |  | 6.14 | [8 empty] | 11.04 |  |  |  |  | 0.00
1988 |  |  |  | 1164.40 |  |  | 1891 |  |  |  | 860 | [10 empty] | 20.35 |  |  |  | 20.35 | [5 empty] | 15.41 |  |  | 21.53 |  |  |  | 3.20 |  | 0.67 | [8 empty] | 78.98 |  |  |  |  | 0.00
1989 |  |  |  | 7322.11 |  |  | 8506 |  |  |  | 870 | [10 empty] | 97.08 |  |  |  | 97.08 | [5 empty] | 96.02 |  |  | 97.10 |  |  |  | 1.84 |  | 1.82 | [8 empty] | 1.10 |  |  |  |  | 0.00
1990 |  |  |  | 4161.47 |  |  | 4867 |  |  |  | 874 | [10 empty] | 55.62 |  |  |  | 55.62 | [5 empty] | 54.35 |  |  | 55.56 |  |  |  | 41.73 |  | 39.83 | [8 empty] | 4.55 |  |  |  |  | 0.00
1991 |  |  |  | 5843.86 |  |  | 6962 |  |  |  | 874 | [10 empty] | 78.62 |  |  |  | 78.62 | [5 empty] | 76.33 |  |  | 79.47 |  |  |  | 2.16 |  | 1.74 | [8 empty] | 19.64 |  |  |  |  | 0.00
1992 |  |  |  | 7650.49 |  |  | 8742 |  |  |  | 877 | [10 empty] | 99.54 |  |  |  | 99.54 | [5 empty] | 99.31 |  |  | 99.52 |  |  |  | 0.46 |  | 0.46 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 6083.40 |  |  | 7246 |  |  |  | 871 | [10 empty] | 82.70 |  |  |  | 82.70 | [5 empty] | 79.66 |  |  | 82.72 |  |  |  | 0.83 |  | 0.69 | [8 empty] | 16.61 |  |  |  |  | 0.00
1994 |  |  |  | 6385.00 |  |  | 7667 |  |  |  | 868 | [10 empty] | 86.92 |  |  |  | 86.92 | [5 empty] | 83.97 |  |  | 87.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.08 |  |  |  |  | 0.00
1995 |  |  |  | 7670.57 |  |  | 8760 |  |  |  | 869 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 6456.29 |  |  | 7452 |  |  |  | 872 | [10 empty] | 84.83 |  |  |  | 84.83 | [5 empty] | 84.29 |  |  | 84.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.17 |  |  |  |  | 0.00
1997 |  |  |  | 7183.36 |  |  | 8184 |  |  |  | 873 | [10 empty] | 93.45 |  |  |  | 93.45 | [5 empty] | 93.93 |  |  | 93.42 |  |  |  | 6.55 |  | 6.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 6130.68 |  |  | 7181 |  |  |  | 873 | [10 empty] | 82.01 |  |  |  | 85.38 | [5 empty] | 80.17 |  |  | 81.97 |  |  |  | 3.88 |  | 3.45 | [8 empty] | 11.18 |  |  |  |  | 3.37
1999 |  |  |  | 7369.99 |  |  | 8311 |  |  |  | 873 | [10 empty] | 94.89 |  |  |  | 94.89 | [5 empty] | 96.37 |  |  | 94.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.11 |  |  |  |  | 0.00
2000 |  |  |  | 6770.53 |  |  | 7633 |  |  |  | 882 | [10 empty] | 86.96 |  |  |  | 86.96 | [5 empty] | 87.91 |  |  | 86.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.04 |  |  |  |  | 0.00
2001 |  |  |  | 7690.85 |  |  | 8738 |  |  |  | 882 | [10 empty] | 99.75 |  |  |  | 99.75 | [5 empty] | 99.54 |  |  | 99.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.25 |  |  |  |  | 0.00
2002 |  |  |  | 929.02 |  |  | 1081 |  |  |  | 882 | [10 empty] | 12.36 |  |  |  | 12.36 | [5 empty] | 12.02 |  |  | 12.34 |  |  |  | 2.21 |  | 0.28 | [8 empty] | 87.36 |  |  |  |  | 0.00
2003 |  |  |  | 0.00 |  |  | 0 |  |  |  | 882 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2004 |  |  |  | 5778.43 |  |  | 6628 |  |  |  | 882 | [10 empty] | 75.56 |  |  |  | 75.56 | [5 empty] | 74.58 |  |  | 75.46 |  |  |  | 4.95 |  | 3.94 | [8 empty] | 20.51 |  |  |  |  | 0.00
2005 |  |  |  | 7177.43 |  |  | 8125 |  |  |  | 873 | [10 empty] | 92.77 |  |  |  | 92.77 | [5 empty] | 93.85 |  |  | 92.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.23 |  |  |  |  | 0.00
2006 |  |  |  | 6375.42 |  |  | 7265 |  |  |  | 891 | [10 empty] | 82.94 |  |  |  | 82.94 | [5 empty] | 81.68 |  |  | 82.93 |  |  |  | 0.90 |  | 0.85 | [8 empty] | 16.21 |  |  |  |  | 0.00
2007 |  |  |  | 7705.80 |  |  | 8712 |  |  |  | 879 | [10 empty] | 99.45 |  |  |  | 99.45 | [5 empty] | 100.07 |  |  | 99.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.55 |  |  |  |  | 0.00
2008 |  |  |  | 6829.44 |  |  | 7621 |  |  |  | 894 | [10 empty] | 86.61 |  |  |  | 86.61 | [5 empty] | 87.95 |  |  | 86.76 |  |  |  | 1.13 |  | 0.99 | [8 empty] | 12.40 |  |  |  |  | 0.00
2009 |  |  |  | 7609.61 |  |  | 8361 |  |  |  | 879 | [10 empty] | 95.38 |  |  |  | 95.38 | [5 empty] | 98.83 |  |  | 95.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.62 |  |  |  |  | 0.00
2010 |  |  |  | 5188.16 |  |  | 5851 |  |  |  | 894 | [10 empty] | 67.35 |  |  |  | 67.35 | [5 empty] | 66.25 |  |  | 66.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.65 |  |  |  |  | 0.00
2011 |  |  |  | 6339.24 |  |  | 7012 |  |  |  | 894 | [10 empty] | 80.07 |  |  |  | 80.07 | [5 empty] | 80.95 |  |  | 80.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.93 |  |  |  |  | 0.00
2012 |  |  |  | 7101.70 |  |  | 7868 |  |  |  | 894 | [10 empty] | 89.58 |  |  |  | 89.58 | [5 empty] | 90.43 |  |  | 89.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.42 |  |  |  |  | 0.00
2013 |  |  |  | 7679.22 |  |  | 8451 |  |  |  | 894 | [10 empty] | 96.48 |  |  |  | 96.48 | [5 empty] | 98.05 |  |  | 96.46 |  |  |  | 3.52 |  | 3.52 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 5972.42 |  |  | 6453 |  |  |  | 894 | [10 empty] | 73.67 |  |  |  | 73.67 | [5 empty] | 76.26 |  |  | 73.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.33 |  |  |  |  | 0.00
2015 |  |  |  | 7893.92 |  |  | 8684 |  |  |  | 894 | [10 empty] | 99.13 |  |  |  | 99.13 | [5 empty] | 100.80 |  |  | 99.13 |  |  |  | 0.87 |  | 0.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6394.93 |  |  | 7321 |  |  |  | 894 | [10 empty] | 83.35 |  |  |  | 83.35 | [5 empty] | 81.43 |  |  | 83.34 |  |  |  | 4.97 |  | 4.36 | [8 empty] | 12.28 |  |  |  |  | 0.00
2017 |  |  |  | 7876.43 |  |  | 8760 |  |  |  | 894 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.57 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 7380.27 |  |  | 8169 |  |  |  | 894 | [10 empty] | 93.25 |  |  |  | 93.25 | [5 empty] | 94.24 |  |  | 93.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.75 |  |  |  |  | 0.00
2019 |  |  |  | 7839.46 |  |  | 8632 |  |  |  | 894 | [10 empty] | 98.55 |  |  |  | 98.55 | [5 empty] | 100.10 |  |  | 98.54 |  |  |  | 0.84 |  | 0.84 | [8 empty] | 0.61 |  |  |  |  | 0.00
2020 |  |  |  | 7228.06 |  |  | 8130 |  |  |  | 894 | [10 empty] | 92.57 |  |  |  | 92.57 | [5 empty] | 92.04 |  |  | 92.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.43 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1978 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 632
B. |  | Refuelling without maintenance | [20 empty] | 653 | [14 empty] | 29
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 902
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 222
E. |  | Testing of plant systems or components | [35 empty] | 9 |  |  |  | 3
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 430
H. |  | Nuclear regulatory requirements | [39 empty] | 41
L. |  | Human factor related | [39 empty] | 11
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 7
Z. |  | Other | [39 empty] | 13
Subtotal | [22 empty] | 653 | [14 empty] | 1592 |  |  |  | 700 | [11 empty] | 7
Total | [22 empty] | 653 | [14 empty] | 2299
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1978 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 78
12. |  |  | Reactor I&C Systems | [34 empty] | 51
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 47
16. |  |  | Steam generation systems | [34 empty] | 0
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 353
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 8
42. |  |  | Electrical Power Supply Systems | [34 empty] | 61
Total | [37 empty] | 625
Highlights (2020)
Refueling Outage 21

## DIABLO CANYON-1
2020 Operating Experience
US-275 | [8 empty] | DIABLO CANYON-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PG&E (Pacific Gas and Electric Company )
Owner | [7 empty] | : | PG&E COR (PG&E Corporation)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-04-23
Thermal power | [12 empty] | : |  |  | 3411 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-11-11
Gross electrical power | [12 empty] | : |  |  | 1197 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-05-07
Reference unit power (net) | [12 empty] | : |  |  | 1138 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.83
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 320
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.331
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8910.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.81 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.81 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.19 %
Load Factor (LF) | [18 empty] | : | 89.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.8 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 720 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 849.20 | 791.01 |  |  |  | 838.10 |  | 817.02 | [8 empty] | 756.50 |  |  | 819.72 | [6 empty] | 831.53 |  | 839.97 |  |  |  | 789.83 |  |  | 62.20 |  |  | 696.27 | [9 empty] | 819.22 |  |  | 8910.57
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 9.27 |  |  | 93.80 | [9 empty] | 100.00 |  |  | 91.81
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 9.27 |  |  | 93.80 | [9 empty] | 100.00 |  |  | 91.81
LF [%] |  |  |  |  | 100.30 | 99.87 |  |  |  | 98.99 |  | 99.71 | [8 empty] | 89.35 |  |  | 100.04 | [6 empty] | 98.21 |  | 99.21 |  |  |  | 96.40 |  |  | 7.35 |  |  | 84.98 | [9 empty] | 96.76 |  |  | 89.14
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 9.27 |  |  | 93.89 | [9 empty] | 100.00 |  |  | 91.80
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 90.73 |  |  | 6.20 | [9 empty] | 0.00 |  |  | 8.19
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 305532.68 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.22 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.16 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.84 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.09 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.83 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 5234.23 |  |  | 5206 |  |  |  | 1073 | [10 empty] | 90.81 |  |  |  | 90.81 | [5 empty] | 85.07 |  |  | 90.79 |  |  |  | 4.54 |  | 4.31 | [8 empty] | 4.87 |  |  |  |  | 0.00
1986 |  |  |  | 5316.22 |  |  | 5757 |  |  |  | 1073 | [10 empty] | 65.74 |  |  |  | 65.74 | [5 empty] | 56.56 |  |  | 65.72 |  |  |  | 1.98 |  | 1.33 | [8 empty] | 32.93 |  |  |  |  | 0.00
1987 |  |  |  | 8284.20 |  |  | 8340 |  |  |  | 1073 | [10 empty] | 95.26 |  |  |  | 95.26 | [5 empty] | 88.13 |  |  | 95.21 |  |  |  | 4.74 |  | 4.74 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 5276.12 |  |  | 5555 |  |  |  | 1073 | [10 empty] | 34.58 |  |  |  | 34.58 | [5 empty] | 55.98 |  |  | 63.24 |  |  |  | 46.37 |  | 29.90 | [8 empty] | 35.52 |  |  |  |  | 0.00
1989 |  |  |  | 7199.90 |  |  | 7069 |  |  |  | 1073 | [10 empty] | 80.70 |  |  |  | 80.70 | [5 empty] | 76.60 |  |  | 80.70 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 19.27 |  |  |  |  | 0.00
1990 |  |  |  | 8713.52 |  |  | 8425 |  |  |  | 1073 | [10 empty] | 96.20 |  |  |  | 96.20 | [5 empty] | 92.70 |  |  | 96.18 |  |  |  | 3.80 |  | 3.80 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 7366.28 |  |  | 7125 |  |  |  | 1073 | [10 empty] | 80.42 |  |  |  | 80.42 | [5 empty] | 78.37 |  |  | 81.34 |  |  |  | 1.76 |  | 1.44 | [8 empty] | 18.14 |  |  |  |  | 0.00
1992 |  |  |  | 7454.72 |  |  | 7224 |  |  |  | 1073 | [10 empty] | 82.27 |  |  |  | 82.27 | [5 empty] | 79.09 |  |  | 82.24 |  |  |  | 1.85 |  | 1.55 | [8 empty] | 16.18 |  |  |  |  | 0.00
1993 |  |  |  | 9028.01 |  |  | 8630 |  |  |  | 1073 | [10 empty] | 98.52 |  |  |  | 98.52 | [5 empty] | 96.05 |  |  | 98.52 |  |  |  | 1.48 |  | 1.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 7371.98 |  |  | 6991 |  |  |  | 1073 | [10 empty] | 79.85 |  |  |  | 79.85 | [5 empty] | 78.43 |  |  | 79.81 |  |  |  | 5.35 |  | 4.51 | [8 empty] | 15.64 |  |  |  |  | 0.00
1995 |  |  |  | 7451.75 |  |  | 7175 |  |  |  | 1073 | [10 empty] | 81.94 |  |  |  | 81.94 | [5 empty] | 79.28 |  |  | 81.91 |  |  |  | 2.80 |  | 2.36 | [8 empty] | 15.70 |  |  |  |  | 0.00
1996 |  |  |  | 8786.81 |  |  | 8316 |  |  |  | 1073 | [10 empty] | 94.72 |  |  |  | 94.72 | [5 empty] | 93.23 |  |  | 94.67 |  |  |  | 4.21 |  | 4.17 | [8 empty] | 1.12 |  |  |  |  | 0.00
1997 |  |  |  | 8195.01 |  |  | 7700 |  |  |  | 1073 | [10 empty] | 87.92 |  |  |  | 87.92 | [5 empty] | 87.19 |  |  | 87.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.08 |  |  |  |  | 0.00
1998 |  |  |  | 8967.83 |  |  | 8564 |  |  |  | 1073 | [10 empty] | 97.77 |  |  |  | 97.77 | [5 empty] | 95.41 |  |  | 97.76 |  |  |  | 2.23 |  | 2.23 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 8224.84 |  |  | 7764 |  |  |  | 1073 | [10 empty] | 88.67 |  |  |  | 90.31 | [5 empty] | 87.50 |  |  | 88.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.69 |  |  |  |  | 1.64
2000 |  |  |  | 7853.51 |  |  | 7485 |  |  |  | 1073 | [10 empty] | 85.23 |  |  |  | 85.23 | [5 empty] | 83.32 |  |  | 85.21 |  |  |  | 4.20 |  | 3.73 | [8 empty] | 11.04 |  |  |  |  | 0.00
2001 |  |  |  | 9504.59 |  |  | 8708 |  |  |  | 1087 | [10 empty] | 99.42 |  |  |  | 99.42 | [5 empty] | 100.02 |  |  | 99.41 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 0.49 |  |  |  |  | 0.00
2002 |  |  |  | 7048.21 |  |  | 6652 |  |  |  | 1087 | [10 empty] | 75.97 |  |  |  | 75.97 | [5 empty] | 74.02 |  |  | 75.94 |  |  |  | 1.71 |  | 1.32 | [8 empty] | 22.71 |  |  |  |  | 0.00
2003 |  |  |  | 9585.43 |  |  | 8760 |  |  |  | 1087 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.66 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 7233.89 |  |  | 6869 |  |  |  | 1087 | [10 empty] | 78.23 |  |  |  | 78.23 | [5 empty] | 75.76 |  |  | 78.20 |  |  |  | 0.79 |  | 0.63 | [8 empty] | 21.14 |  |  |  |  | 0.00
2005 |  |  |  | 8323.35 |  |  | 7775 |  |  |  | 1087 | [10 empty] | 88.77 |  |  |  | 88.77 | [5 empty] | 87.41 |  |  | 88.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.23 |  |  |  |  | 0.00
2006 |  |  |  | 9944.98 |  |  | 8760 |  |  |  | 1122 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.18 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 8868.35 |  |  | 7870 |  |  |  | 1122 | [10 empty] | 89.87 |  |  |  | 89.87 | [5 empty] | 90.23 |  |  | 89.84 |  |  |  | 2.14 |  | 1.97 | [8 empty] | 8.16 |  |  |  |  | 0.00
2008 |  |  |  | 9884.24 |  |  | 8784 |  |  |  | 1122 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.29 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 8237.57 |  |  | 7295 |  |  |  | 1122 | [10 empty] | 83.29 |  |  |  | 83.29 | [5 empty] | 83.81 |  |  | 83.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.71 |  |  |  |  | 0.00
2010 |  |  |  | 8677.45 |  |  | 7753 |  |  |  | 1122 | [10 empty] | 88.53 |  |  |  | 88.53 | [5 empty] | 88.29 |  |  | 88.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.47 |  |  |  |  | 0.00
2011 |  |  |  | 9916.75 |  |  | 8760 |  |  |  | 1122 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.90 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 8295.66 |  |  | 7450 |  |  |  | 1122 | [10 empty] | 84.84 |  |  |  | 84.84 | [5 empty] | 84.17 |  |  | 84.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.16 |  |  |  |  | 0.00
2013 |  |  |  | 9653.45 |  |  | 8606 |  |  |  | 1122 | [10 empty] | 98.24 |  |  |  | 98.24 | [5 empty] | 98.21 |  |  | 98.23 |  |  |  | 1.76 |  | 1.76 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 8556.89 |  |  | 7652 |  |  |  | 1122 | [10 empty] | 87.35 |  |  |  | 87.35 | [5 empty] | 87.06 |  |  | 87.35 |  |  |  | 3.13 |  | 2.82 | [8 empty] | 9.83 |  |  |  |  | 0.00
2015 |  |  |  | 8793.72 |  |  | 7828 |  |  |  | 1138 | [10 empty] | 89.50 |  |  |  | 89.50 | [5 empty] | 88.21 |  |  | 89.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.50 |  |  |  |  | 0.00
2016 |  |  |  | 9974.63 |  |  | 8784 |  |  |  | 1138 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.78 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 8204.54 |  |  | 7296 |  |  |  | 1138 | [10 empty] | 83.29 |  |  |  | 83.29 | [5 empty] | 82.30 |  |  | 83.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.71 |  |  |  |  | 0.00
2018 |  |  |  | 9733.67 |  |  | 8760 |  |  |  | 1138 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.64 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 8871.17 |  |  | 7886 |  |  |  | 1138 | [10 empty] | 90.03 |  |  |  | 90.03 | [5 empty] | 88.99 |  |  | 90.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.97 |  |  |  |  | 0.00
2020 |  |  |  | 8910.58 |  |  | 8064 |  |  |  | 1138 | [10 empty] | 91.81 |  |  |  | 91.81 | [5 empty] | 89.14 |  |  | 91.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.19 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 165
B. |  | Refuelling without maintenance | [20 empty] | 720 | [14 empty] | 20
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 793
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 62
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 1
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
P. |  | Fire | [39 empty] | 2
Z. |  | Other | [39 empty] | 4
Subtotal | [22 empty] | 720 | [14 empty] | 875 |  |  |  | 182 | [11 empty] | 4
Total | [22 empty] | 720 | [14 empty] | 1061
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 3
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
16. |  |  | Steam generation systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 80
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 39
Total | [37 empty] | 173
Highlights (2020)
Refueling Outage 22

## DIABLO CANYON-2
2020 Operating Experience
US-323 | [8 empty] | DIABLO CANYON-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PG&E (Pacific Gas and Electric Company )
Owner | [7 empty] | : | PG&E COR (PG&E Corporation)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-12-09
Thermal power | [12 empty] | : |  |  | 3411 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-10-20
Gross electrical power | [12 empty] | : |  |  | 1197 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-03-13
Reference unit power (net) | [12 empty] | : |  |  | 1118 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.83
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.331
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7348.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 24.17 %
Energy Availability Factor (EAF) | [18 empty] | : | 75.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 24 %
Unit Capability Factor (UCF) | [18 empty] | : | 75.28 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.72 %
Load Factor (LF) | [18 empty] | : | 74.82 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 75.28 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2171 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 840.35 | 695.04 |  |  |  | 832.93 |  | 813.63 | [8 empty] | 841.15 |  |  | 808.35 | [6 empty] | 447.17 |  | 757.83 |  |  |  | 810.16 |  |  | 376.40 |  |  | 87.74 | [9 empty] | 37.38 |  |  | 7348.12
EAF [%] |  |  |  |  | 100.00 | 90.94 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 53.46 |  | 95.10 |  |  |  | 100.00 |  |  | 45.66 |  |  | 14.65 | [9 empty] | 5.01 |  |  | 75.28
UCF [%] |  |  |  |  | 100.00 | 90.94 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 53.46 |  | 95.10 |  |  |  | 100.00 |  |  | 45.66 |  |  | 14.65 | [9 empty] | 5.01 |  |  | 75.28
LF [%] |  |  |  |  | 101.03 | 89.32 |  |  |  | 100.14 |  | 101.08 | [8 empty] | 101.12 |  |  | 100.42 | [6 empty] | 53.76 |  | 91.11 |  |  |  | 100.65 |  |  | 45.25 |  |  | 10.90 | [9 empty] | 4.49 |  |  | 74.82
OF [%] |  |  |  |  | 100.00 | 90.95 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 53.49 |  | 95.16 |  |  |  | 100.00 |  |  | 45.70 |  |  | 14.72 | [9 empty] | 4.97 |  |  | 75.28
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 46.54 |  | 4.90 |  |  |  | 0.00 |  |  | 54.34 |  |  | 85.35 | [9 empty] | 94.99 |  |  | 24.17
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 46.54 |  | 4.90 |  |  |  | 0.00 |  |  | 54.34 |  |  | 85.35 | [9 empty] | 94.99 |  |  | 24.00
PUF [%] |  |  |  |  | 0.00 | 9.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.72
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 328196.58 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.79 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.85 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.55 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.94 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.51 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.11 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.09 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.81 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 6757.71 |  |  | 7078 |  |  |  | 1080 | [10 empty] | 95.39 |  |  |  | 95.39 | [5 empty] | 86.22 |  |  | 95.41 |  |  |  | 4.21 |  | 4.19 | [8 empty] | 0.42 |  |  |  |  | 0.00
1987 |  |  |  | 5728.78 |  |  | 5752 |  |  |  | 1079 | [10 empty] | 65.44 |  |  |  | 65.44 | [5 empty] | 60.61 |  |  | 65.66 |  |  |  | 9.03 |  | 6.50 | [8 empty] | 28.06 |  |  |  |  | 0.00
1988 |  |  |  | 6243.35 |  |  | 6086 |  |  |  | 1087 | [10 empty] | 69.33 |  |  |  | 69.33 | [5 empty] | 65.39 |  |  | 69.29 |  |  |  | 10.10 |  | 7.79 | [8 empty] | 22.88 |  |  |  |  | 0.00
1989 |  |  |  | 8615.97 |  |  | 8072 |  |  |  | 1087 | [10 empty] | 92.18 |  |  |  | 92.18 | [5 empty] | 90.48 |  |  | 92.15 |  |  |  | 5.91 |  | 5.79 | [8 empty] | 2.03 |  |  |  |  | 0.00
1990 |  |  |  | 7578.08 |  |  | 7284 |  |  |  | 1087 | [10 empty] | 83.15 |  |  |  | 83.15 | [5 empty] | 79.58 |  |  | 83.15 |  |  |  | 0.29 |  | 0.24 | [8 empty] | 16.61 |  |  |  |  | 0.00
1991 |  |  |  | 7718.47 |  |  | 7420 |  |  |  | 1087 | [10 empty] | 84.70 |  |  |  | 84.70 | [5 empty] | 81.06 |  |  | 84.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.30 |  |  |  |  | 0.00
1992 |  |  |  | 9247.73 |  |  | 8651 |  |  |  | 1087 | [10 empty] | 98.50 |  |  |  | 98.50 | [5 empty] | 96.85 |  |  | 98.49 |  |  |  | 1.50 |  | 1.50 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 7796.19 |  |  | 7324 |  |  |  | 1087 | [10 empty] | 83.64 |  |  |  | 83.64 | [5 empty] | 81.87 |  |  | 83.61 |  |  |  | 1.00 |  | 0.84 | [8 empty] | 15.51 |  |  |  |  | 0.00
1994 |  |  |  | 7896.10 |  |  | 7439 |  |  |  | 1087 | [10 empty] | 84.98 |  |  |  | 84.98 | [5 empty] | 82.92 |  |  | 84.92 |  |  |  | 6.18 |  | 5.59 | [8 empty] | 9.43 |  |  |  |  | 0.00
1995 |  |  |  | 8820.98 |  |  | 8430 |  |  |  | 1087 | [10 empty] | 96.28 |  |  |  | 96.28 | [5 empty] | 92.64 |  |  | 96.23 |  |  |  | 3.72 |  | 3.72 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 7932.91 |  |  | 7459 |  |  |  | 1087 | [10 empty] | 84.96 |  |  |  | 84.96 | [5 empty] | 83.08 |  |  | 84.92 |  |  |  | 2.12 |  | 1.84 | [8 empty] | 13.19 |  |  |  |  | 0.00
1997 |  |  |  | 8883.55 |  |  | 8441 |  |  |  | 1087 | [10 empty] | 96.39 |  |  |  | 96.39 | [5 empty] | 93.29 |  |  | 96.36 |  |  |  | 3.61 |  | 3.61 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 8158.97 |  |  | 7624 |  |  |  | 1087 | [10 empty] | 87.06 |  |  |  | 87.06 | [5 empty] | 85.68 |  |  | 87.03 |  |  |  | 1.67 |  | 1.48 | [8 empty] | 11.46 |  |  |  |  | 0.00
1999 |  |  |  | 8443.69 |  |  | 7902 |  |  |  | 1087 | [10 empty] | 90.22 |  |  |  | 91.31 | [5 empty] | 88.67 |  |  | 90.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.69 |  |  |  |  | 1.09
2000 |  |  |  | 9188.54 |  |  | 8512 |  |  |  | 1087 | [10 empty] | 96.91 |  |  |  | 96.91 | [5 empty] | 96.23 |  |  | 96.90 |  |  |  | 2.67 |  | 2.66 | [8 empty] | 0.43 |  |  |  |  | 0.00
2001 |  |  |  | 8658.37 |  |  | 8051 |  |  |  | 1087 | [10 empty] | 91.93 |  |  |  | 91.93 | [5 empty] | 90.93 |  |  | 91.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.07 |  |  |  |  | 0.00
2002 |  |  |  | 9286.06 |  |  | 8663 |  |  |  | 1087 | [10 empty] | 98.90 |  |  |  | 99.58 | [5 empty] | 97.52 |  |  | 98.89 |  |  |  | 0.42 |  | 0.42 | [8 empty] | 0.00 |  |  |  |  | 0.67
2003 |  |  |  | 7725.23 |  |  | 7225 |  |  |  | 1087 | [10 empty] | 82.50 |  |  |  | 82.50 | [5 empty] | 81.13 |  |  | 82.48 |  |  |  | 4.07 |  | 3.50 | [8 empty] | 14.01 |  |  |  |  | 0.00
2004 |  |  |  | 8017.93 |  |  | 7535 |  |  |  | 1087 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 83.97 |  |  | 85.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.21 |  |  |  |  | 0.00
2005 |  |  |  | 9441.73 |  |  | 8760 |  |  |  | 1087 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.14 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 8529.60 |  |  | 7734 |  |  |  | 1087 | [10 empty] | 88.30 |  |  |  | 88.30 | [5 empty] | 89.58 |  |  | 88.29 |  |  |  | 1.20 |  | 1.07 | [8 empty] | 10.63 |  |  |  |  | 0.00
2007 |  |  |  | 9720.14 |  |  | 8760 |  |  |  | 1118 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.25 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 7263.10 |  |  | 6578 |  |  |  | 1118 | [10 empty] | 74.93 |  |  |  | 75.65 | [5 empty] | 73.96 |  |  | 74.89 |  |  |  | 6.79 |  | 5.51 | [8 empty] | 18.83 |  |  |  |  | 0.72
2009 |  |  |  | 7998.16 |  |  | 7565 |  |  |  | 1118 | [10 empty] | 86.41 |  |  |  | 86.41 | [5 empty] | 81.67 |  |  | 86.36 |  |  |  | 3.62 |  | 3.25 | [8 empty] | 10.34 |  |  |  |  | 0.00
2010 |  |  |  | 9752.48 |  |  | 8760 |  |  |  | 1118 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.58 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8751.61 |  |  | 7789 |  |  |  | 1118 | [10 empty] | 88.94 |  |  |  | 88.94 | [5 empty] | 89.36 |  |  | 88.92 |  |  |  | 1.41 |  | 1.27 | [8 empty] | 9.79 |  |  |  |  | 0.00
2012 |  |  |  | 9474.76 |  |  | 8609 |  |  |  | 1118 | [10 empty] | 98.02 |  |  |  | 98.79 | [5 empty] | 96.48 |  |  | 98.01 |  |  |  | 1.21 |  | 1.21 | [8 empty] | 0.00 |  |  |  |  | 0.77
2013 |  |  |  | 8428.27 |  |  | 7499 |  |  |  | 1118 | [10 empty] | 85.61 |  |  |  | 85.61 | [5 empty] | 86.05 |  |  | 85.60 |  |  |  | 1.16 |  | 1.00 | [8 empty] | 13.39 |  |  |  |  | 0.00
2014 |  |  |  | 8499.41 |  |  | 7742 |  |  |  | 1118 | [10 empty] | 88.38 |  |  |  | 88.38 | [5 empty] | 86.78 |  |  | 88.38 |  |  |  | 2.84 |  | 2.58 | [8 empty] | 9.03 |  |  |  |  | 0.00
2015 |  |  |  | 9749.16 |  |  | 8757 |  |  |  | 1118 | [10 empty] | 99.96 |  |  |  | 99.96 | [5 empty] | 99.55 |  |  | 99.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  |  |  | 0.00
2016 |  |  |  | 8966.24 |  |  | 8001 |  |  |  | 1118 | [10 empty] | 91.09 |  |  |  | 91.09 | [5 empty] | 91.30 |  |  | 91.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.91 |  |  |  |  | 0.00
2017 |  |  |  | 9765.30 |  |  | 8760 |  |  |  | 1118 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.71 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 8560.44 |  |  | 7765 |  |  |  | 1118 | [10 empty] | 89.29 |  |  |  | 89.29 | [5 empty] | 87.41 |  |  | 88.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.71 |  |  |  |  | 0.00
2019 |  |  |  | 7350.12 |  |  | 6664 |  |  |  | 1118 | [10 empty] | 76.08 |  |  |  | 76.08 | [5 empty] | 75.05 |  |  | 76.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.92 |  |  |  |  | 0.00
2020 |  |  |  | 7348.12 |  |  | 6613 |  |  |  | 1118 | [10 empty] | 75.28 |  |  |  | 75.28 | [5 empty] | 74.82 |  |  | 75.28 |  |  |  | 24.17 |  | 24.00 | [8 empty] | 0.72 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 145
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 734
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 63 | [14 empty] | 14
E. |  | Testing of plant systems or components | [35 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 9
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 17
Z. |  | Other | [24 empty] | 3127 | [14 empty] | 100
Subtotal | [22 empty] | 63 |  |  |  | 3127 | [10 empty] | 749 |  |  |  | 254 | [11 empty] | 19
Total | [22 empty] | 3190 | [14 empty] | 1022
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 29
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 6
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 7
42. |  |  | Electrical Power Supply Systems | [34 empty] | 68
Total | [37 empty] | 156
Highlights (2020)
Shutdown due to hydrogen leak in the main generator

## DRESDEN-2
2020 Operating Experience
US-237 | [8 empty] | DRESDEN-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-3 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1966-01-10
Thermal power | [12 empty] | : |  |  | 2957 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1970-04-13
Gross electrical power | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1970-06-09
Reference unit power (net) | [12 empty] | : |  |  | 894 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 50 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.1
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.43
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 35 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.55 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.57
| Active core height/length [m] | [13 empty] | : |  |  | 3.6 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 724 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7966.53 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.97 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.03 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.97 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.45 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 98.75 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 110 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 587.40 | 652.89 |  |  |  | 692.79 |  | 637.16 | [8 empty] | 675.81 |  |  | 652.92 | [6 empty] | 674.09 |  | 676.37 |  |  |  | 665.05 |  |  | 686.51 |  |  | 673.99 | [9 empty] | 691.55 |  |  | 7966.53
EAF [%] |  |  |  |  | 99.66 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.97
UCF [%] |  |  |  |  | 99.66 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.97
LF [%] |  |  |  |  | 88.31 | 104.93 |  |  |  | 104.16 |  | 98.99 | [8 empty] | 101.60 |  |  | 101.44 | [6 empty] | 101.35 |  | 101.69 |  |  |  | 103.32 |  |  | 103.21 |  |  | 104.71 | [9 empty] | 103.97 |  |  | 101.45
OF [%] |  |  |  |  | 85.35 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.75
FLR [%] |  |  |  |  | 0.34 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
UCL [%] |  |  |  |  | 0.34 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 270011.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.18 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.35 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.14 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.51 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.83 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.28 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1970 |  |  |  | 1253.00 |  |  | 2558 |  |  |  | 804 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 23.94 |  |  | 37.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1971 |  |  |  | 2806.30 |  |  | 5694 |  |  |  | 815 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 39.31 |  |  | 65.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1972 |  |  |  | 3370.50 |  |  | 5240 |  |  |  | 815 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 47.08 |  |  | 59.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 5014.50 |  |  | 7672 |  |  |  | 800 | [10 empty] | 90.77 |  |  |  | 90.77 | [5 empty] | 71.55 |  |  | 87.58 |  |  |  | 3.23 |  | 3.03 | [8 empty] | 6.20 |  |  |  |  | 0.00
1974 |  |  |  | 3376.00 |  |  | 5113 |  |  |  | 800 | [10 empty] | 58.33 |  |  |  | 58.33 | [5 empty] | 48.17 |  |  | 58.37 |  |  |  | 28.52 |  | 23.27 | [8 empty] | 18.40 |  |  |  |  | 0.00
1975 |  |  |  | 2957.00 |  |  | 4826 |  |  |  | 800 | [10 empty] | 42.24 |  |  |  | 42.24 | [5 empty] | 42.19 |  |  | 55.09 |  |  |  | 21.18 |  | 11.35 | [8 empty] | 46.42 |  |  |  |  | 0.00
1976 |  |  |  | 4374.40 |  |  | 6660 |  |  |  | 781 | [10 empty] | 64.08 |  |  |  | 64.08 | [5 empty] | 63.76 |  |  | 75.82 |  |  |  | 14.77 |  | 11.11 | [8 empty] | 24.82 |  |  |  |  | 0.00
1977 |  |  |  | 3538.10 |  |  | 6297 |  |  |  | 772 | [10 empty] | 52.38 |  |  |  | 52.38 | [5 empty] | 52.32 |  |  | 71.88 |  |  |  | 25.03 |  | 17.48 | [8 empty] | 30.14 |  |  |  |  | 0.00
1978 |  |  |  | 5704.50 |  |  | 8244 |  |  |  | 772 | [10 empty] | 84.39 |  |  |  | 84.39 | [5 empty] | 84.35 |  |  | 94.11 |  |  |  | 14.03 |  | 13.78 | [8 empty] | 1.83 |  |  |  |  | 0.00
1979 |  |  |  | 4942.90 |  |  | 7141 |  |  |  | 772 | [10 empty] | 73.09 |  |  |  | 73.09 | [5 empty] | 73.09 |  |  | 81.52 |  |  |  | 9.04 |  | 7.27 | [8 empty] | 19.64 |  |  |  |  | 0.00
1980 |  |  |  | 4580.40 |  |  | 8193 |  |  |  | 772 | [10 empty] | 93.53 |  |  |  | 93.53 | [5 empty] | 67.55 |  |  | 93.27 |  |  |  | 4.90 |  | 4.82 | [8 empty] | 1.65 |  |  |  |  | 0.00
1981 |  |  |  | 3416.00 |  |  | 5260 |  |  |  | 772 | [10 empty] | 60.11 |  |  |  | 60.68 | [5 empty] | 50.51 |  |  | 60.05 |  |  |  | 6.66 |  | 4.33 | [8 empty] | 34.99 |  |  |  |  | 0.57
1982 |  |  |  | 5123.10 |  |  | 8094 |  |  |  | 772 | [10 empty] | 92.42 |  |  |  | 92.98 | [5 empty] | 75.76 |  |  | 92.40 |  |  |  | 5.86 |  | 5.79 | [8 empty] | 1.23 |  |  |  |  | 0.56
1983 |  |  |  | 3402.20 |  |  | 5076 |  |  |  | 772 | [10 empty] | 58.91 |  |  |  | 59.23 | [5 empty] | 50.31 |  |  | 57.95 |  |  |  | 15.72 |  | 11.05 | [8 empty] | 29.73 |  |  |  |  | 0.32
1984 |  |  |  | 4468.36 |  |  | 6402 |  |  |  | 772 | [10 empty] | 72.91 |  |  |  | 72.91 | [5 empty] | 65.89 |  |  | 72.88 |  |  |  | 4.33 |  | 3.30 | [8 empty] | 23.79 |  |  |  |  | 0.00
1985 |  |  |  | 3105.97 |  |  | 4678 |  |  |  | 772 | [10 empty] | 54.52 |  |  |  | 54.52 | [5 empty] | 45.93 |  |  | 53.40 |  |  |  | 12.95 |  | 8.11 | [8 empty] | 37.36 |  |  |  |  | 0.00
1986 |  |  |  | 4655.67 |  |  | 6761 |  |  |  | 772 | [10 empty] | 77.22 |  |  |  | 77.22 | [5 empty] | 68.84 |  |  | 77.18 |  |  |  | 15.21 |  | 13.85 | [8 empty] | 8.93 |  |  |  |  | 0.00
1987 |  |  |  | 3362.64 |  |  | 5342 |  |  |  | 772 | [10 empty] | 61.03 |  |  |  | 61.03 | [5 empty] | 49.72 |  |  | 60.98 |  |  |  | 8.49 |  | 5.67 | [8 empty] | 33.31 |  |  |  |  | 0.00
1988 |  |  |  | 4325.16 |  |  | 6931 |  |  |  | 772 | [10 empty] | 78.92 |  |  |  | 78.92 | [5 empty] | 63.78 |  |  | 78.90 |  |  |  | 0.10 |  | 0.08 | [8 empty] | 20.99 |  |  |  |  | 0.00
1989 |  |  |  | 4751.70 |  |  | 7023 |  |  |  | 772 | [10 empty] | 80.19 |  |  |  | 80.19 | [5 empty] | 70.26 |  |  | 80.17 |  |  |  | 2.74 |  | 2.26 | [8 empty] | 17.55 |  |  |  |  | 0.00
1990 |  |  |  | 4116.85 |  |  | 5920 |  |  |  | 772 | [10 empty] | 67.60 |  |  |  | 67.60 | [5 empty] | 60.88 |  |  | 67.58 |  |  |  | 6.89 |  | 5.00 | [8 empty] | 27.40 |  |  |  |  | 0.00
1991 |  |  |  | 2984.21 |  |  | 5031 |  |  |  | 772 | [10 empty] | 57.96 |  |  |  | 57.96 | [5 empty] | 44.13 |  |  | 57.43 |  |  |  | 34.46 |  | 30.48 | [8 empty] | 11.56 |  |  |  |  | 0.00
1992 |  |  |  | 4185.75 |  |  | 7419 |  |  |  | 772 | [10 empty] | 84.47 |  |  |  | 84.47 | [5 empty] | 61.73 |  |  | 84.46 |  |  |  | 15.53 |  | 15.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 3058.56 |  |  | 4790 |  |  |  | 772 | [10 empty] | 54.69 |  |  |  | 54.69 | [5 empty] | 45.23 |  |  | 54.68 |  |  |  | 15.70 |  | 10.18 | [8 empty] | 35.13 |  |  |  |  | 0.00
1994 |  |  |  | 4086.10 |  |  | 5808 |  |  |  | 772 | [10 empty] | 66.31 |  |  |  | 66.31 | [5 empty] | 60.42 |  |  | 66.30 |  |  |  | 33.69 |  | 33.69 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 1890.54 |  |  | 2938 |  |  |  | 772 | [10 empty] | 33.54 |  |  |  | 33.54 | [5 empty] | 27.96 |  |  | 33.54 |  |  |  | 20.62 |  | 8.71 | [8 empty] | 57.75 |  |  |  |  | 0.00
1996 |  |  |  | 2161.41 |  |  | 3731 |  |  |  | 772 | [10 empty] | 42.49 |  |  |  | 42.49 | [5 empty] | 31.87 |  |  | 42.47 |  |  |  | 37.92 |  | 25.96 | [8 empty] | 31.56 |  |  |  |  | 0.00
1997 |  |  |  | 5578.45 |  |  | 7738 |  |  |  | 772 | [10 empty] | 89.44 |  |  |  | 89.44 | [5 empty] | 82.49 |  |  | 88.33 |  |  |  | 10.56 |  | 10.56 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 5632.86 |  |  | 7496 |  |  |  | 772 | [10 empty] | 85.57 |  |  |  | 85.57 | [5 empty] | 83.29 |  |  | 85.57 |  |  |  | 3.40 |  | 3.01 | [8 empty] | 11.42 |  |  |  |  | 0.00
1999 |  |  |  | 6229.52 |  |  | 8122 |  |  |  | 772 | [10 empty] | 92.72 |  |  |  | 92.72 | [5 empty] | 92.12 |  |  | 92.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.28 |  |  |  |  | 0.00
2000 |  |  |  | 6867.43 |  |  | 8747 |  |  |  | 772 | [10 empty] | 99.58 |  |  |  | 99.58 | [5 empty] | 101.27 |  |  | 99.58 |  |  |  | 0.42 |  | 0.42 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 6072.69 |  |  | 8005 |  |  |  | 772 | [10 empty] | 91.21 |  |  |  | 91.21 | [5 empty] | 89.80 |  |  | 91.38 |  |  |  | 3.47 |  | 3.28 | [8 empty] | 5.50 |  |  |  |  | 0.00
2002 |  |  |  | 7527.47 |  |  | 8760 |  |  |  | 850 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.09 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 6703.11 |  |  | 7999 |  |  |  | 850 | [10 empty] | 91.96 |  |  |  | 91.96 | [5 empty] | 90.02 |  |  | 91.31 |  |  |  | 0.78 |  | 0.72 | [8 empty] | 7.32 |  |  |  |  | 0.00
2004 |  |  |  | 5909.32 |  |  | 7045 |  |  |  | 850 | [10 empty] | 80.20 |  |  |  | 80.20 | [5 empty] | 79.15 |  |  | 80.20 |  |  |  | 17.35 |  | 16.84 | [8 empty] | 2.96 |  |  |  |  | 0.00
2005 |  |  |  | 6590.08 |  |  | 7710 |  |  |  | 850 | [10 empty] | 88.04 |  |  |  | 88.04 | [5 empty] | 88.51 |  |  | 88.01 |  |  |  | 5.56 |  | 5.18 | [8 empty] | 6.77 |  |  |  |  | 0.00
2006 |  |  |  | 7273.22 |  |  | 8485 |  |  |  | 867 | [10 empty] | 96.88 |  |  |  | 96.88 | [5 empty] | 95.76 |  |  | 96.86 |  |  |  | 3.12 |  | 3.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 6972.69 |  |  | 8132 |  |  |  | 867 | [10 empty] | 92.84 |  |  |  | 92.84 | [5 empty] | 91.81 |  |  | 92.83 |  |  |  | 1.09 |  | 1.02 | [8 empty] | 6.13 |  |  |  |  | 0.00
2008 |  |  |  | 7469.52 |  |  | 8639 |  |  |  | 867 | [10 empty] | 98.37 |  |  |  | 98.37 | [5 empty] | 98.08 |  |  | 98.35 |  |  |  | 1.63 |  | 1.63 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 6902.62 |  |  | 8033 |  |  |  | 867 | [10 empty] | 91.71 |  |  |  | 91.71 | [5 empty] | 90.88 |  |  | 91.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.29 |  |  |  |  | 0.00
2010 |  |  |  | 7726.88 |  |  | 8760 |  |  |  | 867 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.74 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 7181.34 |  |  | 8150 |  |  |  | 883 | [10 empty] | 93.07 |  |  |  | 93.07 | [5 empty] | 94.26 |  |  | 93.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.93 |  |  |  |  | 0.00
2012 |  |  |  | 7912.78 |  |  | 8634 |  |  |  | 883 | [10 empty] | 98.30 |  |  |  | 98.30 | [5 empty] | 102.02 |  |  | 98.29 |  |  |  | 1.70 |  | 1.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 7546.81 |  |  | 8266 |  |  |  | 883 | [10 empty] | 94.36 |  |  |  | 94.36 | [5 empty] | 97.55 |  |  | 94.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.64 |  |  |  |  | 0.00
2014 |  |  |  | 7585.87 |  |  | 8315 |  |  |  | 894 | [10 empty] | 94.99 |  |  |  | 94.99 | [5 empty] | 96.86 |  |  | 94.92 |  |  |  | 5.01 |  | 5.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 7360.79 |  |  | 8106 |  |  |  | 894 | [10 empty] | 92.53 |  |  |  | 92.53 | [5 empty] | 93.99 |  |  | 92.53 |  |  |  | 2.35 |  | 2.23 | [8 empty] | 5.24 |  |  |  |  | 0.00
2016 |  |  |  | 8047.97 |  |  | 8784 |  |  |  | 894 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.48 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7409.85 |  |  | 8299 |  |  |  | 902 | [10 empty] | 94.78 |  |  |  | 94.78 | [5 empty] | 93.78 |  |  | 94.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.22 |  |  |  |  | 0.00
2018 |  |  |  | 8051.49 |  |  | 8760 |  |  |  | 894 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.81 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7139.16 |  |  | 8128 |  |  |  | 894 | [10 empty] | 92.80 |  |  |  | 92.80 | [5 empty] | 91.16 |  |  | 92.79 |  |  |  | 2.35 |  | 2.24 | [8 empty] | 4.97 |  |  |  |  | 0.00
2020 |  |  |  | 7966.53 |  |  | 8674 |  |  |  | 894 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 101.45 |  |  | 98.75 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1970 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 489
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1028
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 52
E. |  | Testing of plant systems or components | [35 empty] | 9 |  |  |  | 34
H. |  | Nuclear regulatory requirements | [39 empty] | 3
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 14
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
Z. |  | Other | [24 empty] | 3 | [14 empty] | 8 | [11 empty] | 1
Subtotal | [26 empty] | 3 | [10 empty] | 1089 |  |  |  | 548 | [11 empty] | 5
Total | [22 empty] | 3 | [14 empty] | 1642
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1970 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 56
12. |  |  | Reactor I&C Systems | [34 empty] | 60
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 20
15. |  |  | Reactor Cooling Systems | [19 empty] | 3 | [14 empty] | 80
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 118
32. |  |  | Feedwater and Main Steam System | [34 empty] | 31
34. |  |  | Miscellaneous Systems | [34 empty] | 38
35. |  |  | All other I&C Systems | [34 empty] | 16
41. |  |  | Main Generator Systems | [34 empty] | 45
42. |  |  | Electrical Power Supply Systems | [34 empty] | 53
Total | [22 empty] | 3 | [14 empty] | 529
Highlights (2020)
Restore cooling to TR2

## DRESDEN-3
2020 Operating Experience
US-249 | [8 empty] | DRESDEN-3 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-3 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1966-10-14
Thermal power | [12 empty] | : |  |  | 2957 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1971-07-22
Gross electrical power | [12 empty] | : |  |  | 935 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1971-11-16
Reference unit power (net) | [12 empty] | : |  |  | 879 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.1
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.43
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 35 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.55 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.57
| Active core height/length [m] | [13 empty] | : |  |  | 3.6 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 724 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7512.35 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.3 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.3 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.7 %
Load Factor (LF) | [18 empty] | : | 97.3 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 95.31 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 412 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 696.80 | 649.23 |  |  |  | 687.29 |  | 662.12 | [8 empty] | 672.23 |  |  | 652.04 | [6 empty] | 665.74 |  | 559.65 |  |  |  | 625.78 |  |  | 453.22 |  |  | 496.84 | [9 empty] | 691.41 |  |  | 7512.35
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 85.58 |  |  |  | 100.00 |  |  | 80.65 |  |  | 77.59 | [9 empty] | 100.00 |  |  | 95.30
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 85.58 |  |  |  | 100.00 |  |  | 80.65 |  |  | 77.59 | [9 empty] | 100.00 |  |  | 95.30
LF [%] |  |  |  |  | 106.55 | 106.12 |  |  |  | 105.09 |  | 104.62 | [8 empty] | 102.79 |  |  | 103.03 | [6 empty] | 101.80 |  | 85.58 |  |  |  | 98.88 |  |  | 69.30 |  |  | 78.51 | [9 empty] | 105.72 |  |  | 97.30
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 85.62 |  |  |  | 100.00 |  |  | 80.65 |  |  | 77.78 | [9 empty] | 100.00 |  |  | 95.31
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 14.42 |  |  |  | 0.00 |  |  | 19.35 |  |  | 22.41 | [9 empty] | 0.00 |  |  | 4.70
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 267573.67 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.44 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.63 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.95 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.1 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.24 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1971 |  |  |  | 1188.60 |  |  | 2137 |  |  |  | 794 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 27.90 |  |  | 32.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1972 |  |  |  | 5175.60 |  |  | 7549 |  |  |  | 815 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 72.30 |  |  | 85.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 3703.60 |  |  | 5905 |  |  |  | 800 | [10 empty] | 69.20 |  |  |  | 69.20 | [5 empty] | 52.85 |  |  | 67.41 |  |  |  | 3.22 |  | 2.30 | [8 empty] | 28.50 |  |  |  |  | 0.00
1974 |  |  |  | 3608.90 |  |  | 5778 |  |  |  | 800 | [10 empty] | 65.78 |  |  |  | 65.78 | [5 empty] | 51.50 |  |  | 65.96 |  |  |  | 12.31 |  | 9.24 | [8 empty] | 24.99 |  |  |  |  | 0.00
1975 |  |  |  | 2211.20 |  |  | 4505 |  |  |  | 800 | [10 empty] | 31.54 |  |  |  | 31.54 | [5 empty] | 31.55 |  |  | 51.43 |  |  |  | 39.55 |  | 20.64 | [8 empty] | 47.82 |  |  |  |  | 0.00
1976 |  |  |  | 4037.20 |  |  | 7231 |  |  |  | 781 | [10 empty] | 58.75 |  |  |  | 58.75 | [5 empty] | 58.85 |  |  | 82.32 |  |  |  | 21.91 |  | 16.48 | [8 empty] | 24.77 |  |  |  |  | 0.00
1977 |  |  |  | 5186.40 |  |  | 8072 |  |  |  | 773 | [10 empty] | 76.64 |  |  |  | 76.64 | [5 empty] | 76.59 |  |  | 92.15 |  |  |  | 20.11 |  | 19.29 | [8 empty] | 4.07 |  |  |  |  | 0.00
1978 |  |  |  | 3835.30 |  |  | 6280 |  |  |  | 773 | [10 empty] | 56.63 |  |  |  | 56.63 | [5 empty] | 56.64 |  |  | 71.69 |  |  |  | 22.30 |  | 16.25 | [8 empty] | 27.12 |  |  |  |  | 0.00
1979 |  |  |  | 3482.90 |  |  | 5930 |  |  |  | 773 | [10 empty] | 51.43 |  |  |  | 51.43 | [5 empty] | 51.43 |  |  | 67.69 |  |  |  | 42.55 |  | 38.09 | [8 empty] | 10.47 |  |  |  |  | 0.00
1980 |  |  |  | 4335.50 |  |  | 6307 |  |  |  | 773 | [10 empty] | 72.31 |  |  |  | 72.31 | [5 empty] | 63.85 |  |  | 71.80 |  |  |  | 2.52 |  | 1.87 | [8 empty] | 25.82 |  |  |  |  | 0.00
1981 |  |  |  | 5177.70 |  |  | 8256 |  |  |  | 773 | [10 empty] | 94.49 |  |  |  | 95.11 | [5 empty] | 76.46 |  |  | 94.25 |  |  |  | 4.89 |  | 4.89 | [8 empty] | 0.00 |  |  |  |  | 0.62
1982 |  |  |  | 3896.40 |  |  | 5562 |  |  |  | 773 | [10 empty] | 63.79 |  |  |  | 64.34 | [5 empty] | 57.54 |  |  | 63.49 |  |  |  | 3.40 |  | 2.27 | [8 empty] | 33.39 |  |  |  |  | 0.55
1983 |  |  |  | 4159.70 |  |  | 6401 |  |  |  | 773 | [10 empty] | 73.10 |  |  |  | 73.10 | [5 empty] | 61.43 |  |  | 73.07 |  |  |  | 2.21 |  | 1.65 | [8 empty] | 25.25 |  |  |  |  | 0.00
1984 |  |  |  | 2135.50 |  |  | 3309 |  |  |  | 773 | [10 empty] | 37.72 |  |  |  | 37.72 | [5 empty] | 31.45 |  |  | 37.67 |  |  |  | 14.16 |  | 6.22 | [8 empty] | 56.06 |  |  |  |  | 0.00
1985 |  |  |  | 4401.33 |  |  | 6618 |  |  |  | 773 | [10 empty] | 75.58 |  |  |  | 75.58 | [5 empty] | 65.00 |  |  | 75.55 |  |  |  | 5.73 |  | 4.59 | [8 empty] | 19.83 |  |  |  |  | 0.00
1986 |  |  |  | 1498.30 |  |  | 2456 |  |  |  | 773 | [10 empty] | 28.06 |  |  |  | 28.06 | [5 empty] | 22.13 |  |  | 28.04 |  |  |  | 15.97 |  | 5.33 | [8 empty] | 66.61 |  |  |  |  | 0.00
1987 |  |  |  | 4395.50 |  |  | 6591 |  |  |  | 773 | [10 empty] | 75.30 |  |  |  | 75.30 | [5 empty] | 64.91 |  |  | 75.24 |  |  |  | 23.78 |  | 23.50 | [8 empty] | 1.20 |  |  |  |  | 0.00
1988 |  |  |  | 4168.36 |  |  | 6278 |  |  |  | 773 | [10 empty] | 71.50 |  |  |  | 71.50 | [5 empty] | 61.39 |  |  | 71.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.50 |  |  |  |  | 0.00
1989 |  |  |  | 5119.46 |  |  | 7235 |  |  |  | 773 | [10 empty] | 82.62 |  |  |  | 82.62 | [5 empty] | 75.60 |  |  | 82.59 |  |  |  | 3.07 |  | 2.62 | [8 empty] | 14.77 |  |  |  |  | 0.00
1990 |  |  |  | 5149.79 |  |  | 7272 |  |  |  | 773 | [10 empty] | 83.01 |  |  |  | 83.01 | [5 empty] | 76.05 |  |  | 83.01 |  |  |  | 4.75 |  | 4.14 | [8 empty] | 12.84 |  |  |  |  | 0.00
1991 |  |  |  | 2584.21 |  |  | 5247 |  |  |  | 773 | [10 empty] | 59.91 |  |  |  | 59.91 | [5 empty] | 38.16 |  |  | 59.90 |  |  |  | 2.24 |  | 1.37 | [8 empty] | 38.72 |  |  |  |  | 0.00
1992 |  |  |  | 3077.06 |  |  | 5364 |  |  |  | 773 | [10 empty] | 61.08 |  |  |  | 61.08 | [5 empty] | 45.32 |  |  | 61.07 |  |  |  | 10.64 |  | 7.27 | [8 empty] | 31.65 |  |  |  |  | 0.00
1993 |  |  |  | 4969.04 |  |  | 7040 |  |  |  | 773 | [10 empty] | 80.39 |  |  |  | 80.39 | [5 empty] | 73.38 |  |  | 80.37 |  |  |  | 19.61 |  | 19.61 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 1666.36 |  |  | 3009 |  |  |  | 773 | [10 empty] | 34.35 |  |  |  | 34.35 | [5 empty] | 24.61 |  |  | 34.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 65.65 |  |  |  |  | 0.00
1995 |  |  |  | 3477.26 |  |  | 5209 |  |  |  | 773 | [10 empty] | 59.46 |  |  |  | 59.46 | [5 empty] | 51.35 |  |  | 59.46 |  |  |  | 40.54 |  | 40.54 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 2962.14 |  |  | 4273 |  |  |  | 773 | [10 empty] | 48.88 |  |  |  | 48.88 | [5 empty] | 43.62 |  |  | 48.65 |  |  |  | 51.12 |  | 51.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 4046.20 |  |  | 5900 |  |  |  | 773 | [10 empty] | 68.55 |  |  |  | 68.55 | [5 empty] | 59.75 |  |  | 67.35 |  |  |  | 11.27 |  | 8.71 | [8 empty] | 22.74 |  |  |  |  | 0.00
1998 |  |  |  | 6234.59 |  |  | 8157 |  |  |  | 773 | [10 empty] | 93.12 |  |  |  | 93.12 | [5 empty] | 92.07 |  |  | 93.12 |  |  |  | 3.26 |  | 3.14 | [8 empty] | 3.75 |  |  |  |  | 0.00
1999 |  |  |  | 6129.96 |  |  | 7978 |  |  |  | 773 | [10 empty] | 91.07 |  |  |  | 91.07 | [5 empty] | 90.53 |  |  | 91.07 |  |  |  | 1.69 |  | 1.56 | [8 empty] | 7.36 |  |  |  |  | 0.00
2000 |  |  |  | 6365.12 |  |  | 8243 |  |  |  | 773 | [10 empty] | 93.84 |  |  |  | 93.84 | [5 empty] | 93.74 |  |  | 93.84 |  |  |  | 0.73 |  | 0.69 | [8 empty] | 5.46 |  |  |  |  | 0.00
2001 |  |  |  | 6465.95 |  |  | 8359 |  |  |  | 773 | [10 empty] | 95.36 |  |  |  | 95.36 | [5 empty] | 95.49 |  |  | 95.42 |  |  |  | 3.98 |  | 3.95 | [8 empty] | 0.69 |  |  |  |  | 0.00
2002 |  |  |  | 6060.87 |  |  | 7915 |  |  |  | 850 | [10 empty] | 90.46 |  |  |  | 90.46 | [5 empty] | 87.31 |  |  | 90.35 |  |  |  | 2.39 |  | 2.21 | [8 empty] | 7.33 |  |  |  |  | 0.00
2003 |  |  |  | 6963.86 |  |  | 8206 |  |  |  | 850 | [10 empty] | 94.17 |  |  |  | 94.17 | [5 empty] | 93.52 |  |  | 93.68 |  |  |  | 2.16 |  | 2.07 | [8 empty] | 3.76 |  |  |  |  | 0.00
2004 |  |  |  | 6436.94 |  |  | 7544 |  |  |  | 850 | [10 empty] | 85.88 |  |  |  | 85.88 | [5 empty] | 86.21 |  |  | 85.88 |  |  |  | 2.87 |  | 2.54 | [8 empty] | 11.58 |  |  |  |  | 0.00
2005 |  |  |  | 7032.37 |  |  | 8169 |  |  |  | 850 | [10 empty] | 93.28 |  |  |  | 93.28 | [5 empty] | 94.43 |  |  | 93.24 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 6.59 |  |  |  |  | 0.00
2006 |  |  |  | 7171.93 |  |  | 8298 |  |  |  | 867 | [10 empty] | 94.73 |  |  |  | 94.73 | [5 empty] | 94.43 |  |  | 94.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.27 |  |  |  |  | 0.00
2007 |  |  |  | 7558.09 |  |  | 8715 |  |  |  | 867 | [10 empty] | 99.49 |  |  |  | 99.49 | [5 empty] | 99.52 |  |  | 99.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.51 |  |  |  |  | 0.00
2008 |  |  |  | 6919.05 |  |  | 8118 |  |  |  | 867 | [10 empty] | 92.43 |  |  |  | 92.43 | [5 empty] | 90.85 |  |  | 92.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.57 |  |  |  |  | 0.00
2009 |  |  |  | 7364.79 |  |  | 8557 |  |  |  | 867 | [10 empty] | 97.70 |  |  |  | 97.70 | [5 empty] | 96.97 |  |  | 97.68 |  |  |  | 1.65 |  | 1.64 | [8 empty] | 0.66 |  |  |  |  | 0.00
2010 |  |  |  | 6866.24 |  |  | 8076 |  |  |  | 867 | [10 empty] | 92.21 |  |  |  | 92.21 | [5 empty] | 90.41 |  |  | 92.19 |  |  |  | 0.79 |  | 0.73 | [8 empty] | 7.05 |  |  |  |  | 0.00
2011 |  |  |  | 7533.02 |  |  | 8760 |  |  |  | 867 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.18 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 6892.73 |  |  | 8218 |  |  |  | 867 | [10 empty] | 93.69 |  |  |  | 93.69 | [5 empty] | 90.51 |  |  | 93.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.31 |  |  |  |  | 0.00
2013 |  |  |  | 7869.99 |  |  | 8590 |  |  |  | 867 | [10 empty] | 98.10 |  |  |  | 98.10 | [5 empty] | 103.61 |  |  | 98.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.90 |  |  |  |  | 0.00
2014 |  |  |  | 7549.85 |  |  | 8361 |  |  |  | 879 | [10 empty] | 95.51 |  |  |  | 95.51 | [5 empty] | 98.05 |  |  | 95.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.49 |  |  |  |  | 0.00
2015 |  |  |  | 7832.94 |  |  | 8595 |  |  |  | 879 | [10 empty] | 98.11 |  |  |  | 98.11 | [5 empty] | 101.73 |  |  | 98.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.89 |  |  |  |  | 0.00
2016 |  |  |  | 7397.58 |  |  | 8376 |  |  |  | 879 | [10 empty] | 95.35 |  |  |  | 95.35 | [5 empty] | 95.81 |  |  | 95.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.65 |  |  |  |  | 0.00
2017 |  |  |  | 8036.77 |  |  | 8760 |  |  |  | 895 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 7514.36 |  |  | 8401 |  |  |  | 879 | [10 empty] | 95.94 |  |  |  | 95.94 | [5 empty] | 97.59 |  |  | 95.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.06 |  |  |  |  | 0.00
2019 |  |  |  | 7942.88 |  |  | 8674 |  |  |  | 879 | [10 empty] | 99.03 |  |  |  | 99.03 | [5 empty] | 103.15 |  |  | 99.02 |  |  |  | 0.97 |  | 0.97 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7512.35 |  |  | 8372 |  |  |  | 879 | [10 empty] | 95.30 |  |  |  | 95.30 | [5 empty] | 97.30 |  |  | 95.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.70 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1971 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 513
B. |  | Refuelling without maintenance | [20 empty] | 305 | [14 empty] | 14
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1074
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 107 | [14 empty] | 93
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 7
H. |  | Nuclear regulatory requirements | [39 empty] | 1
L. |  | Human factor related | [39 empty] | 18
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 1
Z. |  | Other | [39 empty] | 13
Subtotal | [22 empty] | 412 | [14 empty] | 1184 |  |  |  | 552 | [11 empty] | 1
Total | [22 empty] | 412 | [14 empty] | 1737
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1971 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 45
15. |  |  | Reactor Cooling Systems | [34 empty] | 45
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 50
31. |  |  | Turbine and auxiliaries | [34 empty] | 163
32. |  |  | Feedwater and Main Steam System | [34 empty] | 48
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 63
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 13
42. |  |  | Electrical Power Supply Systems | [34 empty] | 72
Total | [37 empty] | 528
Highlights (2020)
Refueling Outage D3R26

## DUANE ARNOLD-1
2020 Operating Experience
US-331 | [8 empty] | DUANE ARNOLD-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | NEXTERA (NextEra Energy Resources, LLC )
Owner | [7 empty] | : | NEXTERA (NextEra Energy Resources, LLC )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-06-22
Thermal power | [12 empty] | : |  |  | 1912 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-05-19
Gross electrical power | [12 empty] | : |  |  | 624 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-02-01
Reference unit power (net) | [12 empty] | : |  |  | 601 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.17
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.436
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 27800 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.33 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.68
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 368 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2904.86 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 18.78 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.22 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 18.78 %
Unit Capability Factor (UCF) | [18 empty] | : | 81.22 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 73.5 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 81.2 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1524 hours
Annual Summary
[5 empty] | Dec | Oct |  |  |  | Nov |  | Jan | [8 empty] | Feb |  |  | Mar | [6 empty] | Apr |  | May |  |  |  | Jun |  |  | Jul |  |  | Aug | [9 empty] | Sep |  |  | Annual
GW(e)-h | [11 empty] | 456.36 | [8 empty] | 425.23 |  |  | 452.68 | [6 empty] | 419.86 |  | 392.82 |  |  |  | 289.11 |  |  | 358.85 |  |  | 109.96 | [9 empty] | 0.00 |  |  | 2904.86
EAF [%] | [11 empty] | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 30.76 | [9 empty] | 0.00 |  |  | 81.22
UCF [%] | [11 empty] | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 30.76 | [9 empty] | 0.00 |  |  | 81.22
LF [%] | [11 empty] | 102.06 | [8 empty] | 101.66 |  |  | 101.24 | [6 empty] | 97.03 |  | 87.85 |  |  |  | 66.81 |  |  | 80.25 |  |  | 24.59 | [9 empty] | 0.00 |  |  | 73.50
OF [%] | [11 empty] | 100.00 | [8 empty] | 100.00 |  |  | 99.87 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 30.78 | [9 empty] | 0.00 |  |  | 81.20
FLR [%] | [11 empty] | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 69.24 | [9 empty] | 100.00 |  |  | 18.78
UCL [%] | [11 empty] | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 69.24 | [9 empty] | 100.00 |  |  | 18.78
PUF [%] | [11 empty] | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] | [11 empty] | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 62443.59 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.08 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.49 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.34 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.56 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.1 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 79.04 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.07 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.75 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 2298.20 |  |  | 6965 |  |  |  | 515 | [10 empty] | 79.39 |  |  |  | 79.39 | [5 empty] | 50.86 |  |  | 78.57 |  |  |  | 9.35 |  | 8.19 | [8 empty] | 12.41 |  |  |  |  | 0.00
1976 |  |  |  | 2489.40 |  |  | 6847 |  |  |  | 515 | [10 empty] | 55.09 |  |  |  | 55.09 | [5 empty] | 55.03 |  |  | 77.95 |  |  |  | 18.05 |  | 12.13 | [8 empty] | 32.78 |  |  |  |  | 0.00
1977 |  |  |  | 2897.80 |  |  | 6908 |  |  |  | 515 | [10 empty] | 64.30 |  |  |  | 64.30 | [5 empty] | 64.23 |  |  | 78.86 |  |  |  | 6.97 |  | 4.82 | [8 empty] | 30.89 |  |  |  |  | 0.00
1978 |  |  |  | 1227.50 |  |  | 2902 |  |  |  | 515 | [10 empty] | 27.21 |  |  |  | 27.21 | [5 empty] | 27.21 |  |  | 33.13 |  |  |  | 68.40 |  | 58.88 | [8 empty] | 13.91 |  |  |  |  | 0.00
1979 |  |  |  | 2898.90 |  |  | 6830 |  |  |  | 515 | [10 empty] | 64.25 |  |  |  | 64.25 | [5 empty] | 64.26 |  |  | 77.97 |  |  |  | 32.55 |  | 31.01 | [8 empty] | 4.74 |  |  |  |  | 0.00
1980 |  |  |  | 2796.30 |  |  | 6456 |  |  |  | 515 | [10 empty] | 73.15 |  |  |  | 74.76 | [5 empty] | 61.81 |  |  | 73.50 |  |  |  | 6.56 |  | 5.25 | [8 empty] | 19.99 |  |  |  |  | 1.60
1981 |  |  |  | 2219.50 |  |  | 6108 |  |  |  | 515 | [10 empty] | 69.29 |  |  |  | 69.29 | [5 empty] | 49.20 |  |  | 69.73 |  |  |  | 4.03 |  | 2.91 | [8 empty] | 27.80 |  |  |  |  | 0.00
1982 |  |  |  | 2280.40 |  |  | 6543 |  |  |  | 515 | [10 empty] | 74.15 |  |  |  | 74.15 | [5 empty] | 50.55 |  |  | 74.69 |  |  |  | 22.51 |  | 21.53 | [8 empty] | 4.31 |  |  |  |  | 0.00
1983 |  |  |  | 2324.30 |  |  | 5503 |  |  |  | 515 | [10 empty] | 61.83 |  |  |  | 61.83 | [5 empty] | 51.52 |  |  | 62.82 |  |  |  | 12.71 |  | 9.01 | [8 empty] | 29.16 |  |  |  |  | 0.00
1984 |  |  |  | 2717.56 |  |  | 6402 |  |  |  | 515 | [10 empty] | 72.24 |  |  |  | 72.24 | [5 empty] | 60.07 |  |  | 72.88 |  |  |  | 14.51 |  | 12.26 | [8 empty] | 15.50 |  |  |  |  | 0.00
1985 |  |  |  | 1940.49 |  |  | 4711 |  |  |  | 515 | [10 empty] | 52.63 |  |  |  | 52.63 | [5 empty] | 43.01 |  |  | 53.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 47.37 |  |  |  |  | 0.00
1986 |  |  |  | 3192.83 |  |  | 7495 |  |  |  | 515 | [10 empty] | 81.51 |  |  |  | 81.51 | [5 empty] | 70.77 |  |  | 85.56 |  |  |  | 4.14 |  | 3.52 | [8 empty] | 14.97 |  |  |  |  | 0.00
1987 |  |  |  | 2546.58 |  |  | 5513 |  |  |  | 515 | [10 empty] | 62.04 |  |  |  | 62.04 | [5 empty] | 56.45 |  |  | 62.93 |  |  |  | 18.67 |  | 14.24 | [8 empty] | 23.72 |  |  |  |  | 0.00
1988 |  |  |  | 3520.21 |  |  | 7128 |  |  |  | 520 | [10 empty] | 72.29 |  |  |  | 72.29 | [5 empty] | 77.05 |  |  | 81.15 |  |  |  | 1.08 |  | 0.79 | [8 empty] | 26.92 |  |  |  |  | 0.00
1989 |  |  |  | 3143.64 |  |  | 6561 |  |  |  | 536 | [10 empty] | 62.45 |  |  |  | 62.45 | [5 empty] | 66.95 |  |  | 74.90 |  |  |  | 24.40 |  | 20.15 | [8 empty] | 17.40 |  |  |  |  | 0.00
1990 |  |  |  | 3021.05 |  |  | 6498 |  |  |  | 538 | [10 empty] | 74.68 |  |  |  | 74.68 | [5 empty] | 64.10 |  |  | 74.18 |  |  |  | 5.06 |  | 3.98 | [8 empty] | 21.34 |  |  |  |  | 0.00
1991 |  |  |  | 4146.80 |  |  | 8217 |  |  |  | 532 | [10 empty] | 93.87 |  |  |  | 93.87 | [5 empty] | 88.95 |  |  | 93.80 |  |  |  | 2.44 |  | 2.34 | [8 empty] | 3.78 |  |  |  |  | 0.00
1992 |  |  |  | 3434.64 |  |  | 7112 |  |  |  | 515 | [10 empty] | 80.50 |  |  |  | 80.50 | [5 empty] | 75.92 |  |  | 80.97 |  |  |  | 2.64 |  | 2.18 | [8 empty] | 17.32 |  |  |  |  | 0.00
1993 |  |  |  | 3241.40 |  |  | 6755 |  |  |  | 515 | [10 empty] | 76.55 |  |  |  | 76.64 | [5 empty] | 71.85 |  |  | 77.11 |  |  |  | 1.47 |  | 1.15 | [8 empty] | 22.21 |  |  |  |  | 0.09
1994 |  |  |  | 4108.36 |  |  | 8078 |  |  |  | 515 | [10 empty] | 92.00 |  |  |  | 92.00 | [5 empty] | 91.07 |  |  | 92.21 |  |  |  | 2.49 |  | 2.35 | [8 empty] | 5.65 |  |  |  |  | 0.00
1995 |  |  |  | 3736.97 |  |  | 7253 |  |  |  | 515 | [10 empty] | 82.40 |  |  |  | 82.40 | [5 empty] | 82.83 |  |  | 82.80 |  |  |  | 1.08 |  | 0.90 | [8 empty] | 16.70 |  |  |  |  | 0.00
1996 |  |  |  | 3938.54 |  |  | 7906 |  |  |  | 520 | [10 empty] | 89.87 |  |  |  | 89.87 | [5 empty] | 86.23 |  |  | 90.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.13 |  |  |  |  | 0.00
1997 |  |  |  | 4155.53 |  |  | 8125 |  |  |  | 520 | [10 empty] | 92.70 |  |  |  | 92.70 | [5 empty] | 91.23 |  |  | 92.75 |  |  |  | 1.30 |  | 1.22 | [8 empty] | 6.09 |  |  |  |  | 0.00
1998 |  |  |  | 3839.16 |  |  | 7477 |  |  |  | 520 | [10 empty] | 85.16 |  |  |  | 85.16 | [5 empty] | 84.28 |  |  | 85.35 |  |  |  | 1.56 |  | 1.35 | [8 empty] | 13.49 |  |  |  |  | 0.00
1999 |  |  |  | 3649.04 |  |  | 7267 |  |  |  | 520 | [10 empty] | 82.97 |  |  |  | 82.97 | [5 empty] | 80.11 |  |  | 82.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.03 |  |  |  |  | 0.00
2000 |  |  |  | 4455.71 |  |  | 8553 |  |  |  | 520 | [10 empty] | 97.39 |  |  |  | 97.39 | [5 empty] | 97.55 |  |  | 97.37 |  |  |  | 2.61 |  | 2.61 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 3860.64 |  |  | 7473 |  |  |  | 565 | [10 empty] | 85.43 |  |  |  | 85.43 | [5 empty] | 84.13 |  |  | 85.31 |  |  |  | 2.84 |  | 2.50 | [8 empty] | 12.07 |  |  |  |  | 0.00
2002 |  |  |  | 4581.08 |  |  | 8147 |  |  |  | 565 | [10 empty] | 93.57 |  |  |  | 95.13 | [5 empty] | 92.74 |  |  | 93.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.87 |  |  |  |  | 1.57
2003 |  |  |  | 3998.57 |  |  | 7209 |  |  |  | 565 | [10 empty] | 83.76 |  |  |  | 83.76 | [5 empty] | 80.79 |  |  | 82.29 |  |  |  | 7.34 |  | 6.64 | [8 empty] | 9.61 |  |  |  |  | 0.00
2004 |  |  |  | 4929.91 |  |  | 8596 |  |  |  | 565 | [10 empty] | 97.88 |  |  |  | 97.88 | [5 empty] | 99.33 |  |  | 97.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.12 |  |  |  |  | 0.00
2005 |  |  |  | 4544.47 |  |  | 7882 |  |  |  | 562 | [10 empty] | 89.99 |  |  |  | 89.99 | [5 empty] | 92.30 |  |  | 89.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.01 |  |  |  |  | 0.00
2006 |  |  |  | 5095.41 |  |  | 8664 |  |  |  | 581 | [10 empty] | 98.91 |  |  |  | 98.91 | [5 empty] | 100.11 |  |  | 98.90 |  |  |  | 1.09 |  | 1.09 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 4518.88 |  |  | 7598 |  |  |  | 580 | [10 empty] | 86.74 |  |  |  | 86.74 | [5 empty] | 88.94 |  |  | 86.74 |  |  |  | 0.90 |  | 0.79 | [8 empty] | 12.48 |  |  |  |  | 0.00
2008 |  |  |  | 5282.81 |  |  | 8784 |  |  |  | 580 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.69 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 4678.93 |  |  | 7891 |  |  |  | 579 | [10 empty] | 90.08 |  |  |  | 90.08 | [5 empty] | 92.25 |  |  | 90.08 |  |  |  | 1.53 |  | 1.40 | [8 empty] | 8.52 |  |  |  |  | 0.00
2010 |  |  |  | 4454.36 |  |  | 7471 |  |  |  | 601 | [10 empty] | 85.85 |  |  |  | 85.85 | [5 empty] | 84.61 |  |  | 85.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.15 |  |  |  |  | 0.00
2011 |  |  |  | 5215.23 |  |  | 8611 |  |  |  | 601 | [10 empty] | 98.30 |  |  |  | 98.30 | [5 empty] | 99.06 |  |  | 98.30 |  |  |  | 1.70 |  | 1.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 4347.00 |  |  | 7391 |  |  |  | 601 | [10 empty] | 84.16 |  |  |  | 84.16 | [5 empty] | 82.34 |  |  | 84.14 |  |  |  | 1.93 |  | 1.66 | [8 empty] | 14.18 |  |  |  |  | 0.00
2013 |  |  |  | 5320.78 |  |  | 8760 |  |  |  | 601 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.05 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 4152.47 |  |  | 7482 |  |  |  | 601 | [10 empty] | 85.42 |  |  |  | 85.42 | [5 empty] | 78.87 |  |  | 85.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.58 |  |  |  |  | 0.00
2015 |  |  |  | 5243.45 |  |  | 8760 |  |  |  | 601 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.60 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 4702.67 |  |  | 8096 |  |  |  | 601 | [10 empty] | 92.17 |  |  |  | 92.17 | [5 empty] | 89.08 |  |  | 92.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.83 |  |  |  |  | 0.00
2017 |  |  |  | 5213.51 |  |  | 8683 |  |  |  | 601 | [10 empty] | 99.12 |  |  |  | 99.12 | [5 empty] | 99.03 |  |  | 99.12 |  |  |  | 0.88 |  | 0.88 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 4895.41 |  |  | 8258 |  |  |  | 601 | [10 empty] | 94.26 |  |  |  | 94.26 | [5 empty] | 92.98 |  |  | 94.27 |  |  |  | 0.67 |  | 0.63 | [8 empty] | 5.11 |  |  |  |  | 0.00
2019 |  |  |  | 5235.72 |  |  | 8711 |  |  |  | 601 | [10 empty] | 99.45 |  |  |  | 99.45 | [5 empty] | 99.45 |  |  | 99.44 |  |  |  | 0.55 |  | 0.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 2904.86 |  |  | 5340 |  |  |  | 601 | [10 empty] | 81.22 |  |  |  | 81.22 | [5 empty] | 73.50 |  |  | 81.20 |  |  |  | 18.78 |  | 18.78 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 332
B. |  | Refuelling without maintenance | [35 empty] | 10
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 772
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 223
E. |  | Testing of plant systems or components | [35 empty] | 19 |  |  |  | 18
H. |  | Nuclear regulatory requirements | [39 empty] | 28
L. |  | Human factor related | [39 empty] | 36
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
Z. |  | Other | [24 empty] | 1235 | [14 empty] | 43 | [11 empty] | 0
Subtotal | [26 empty] | 1235 | [10 empty] | 1024 |  |  |  | 457 | [11 empty] | 3
Total | [22 empty] | 1235 | [14 empty] | 1484
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 13
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 178
16. |  |  | Steam generation systems | [34 empty] | 0
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 52
32. |  |  | Feedwater and Main Steam System | [34 empty] | 29
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 23
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 8
42. |  |  | Electrical Power Supply Systems | [34 empty] | 16
Total | [37 empty] | 349
Highlights (2020)
Automatic Scram - Loss of Offsite Power due to Derecho Storm

## FARLEY-1
2020 Operating Experience
US-348 | [8 empty] | FARLEY-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SOUTHERN (Southern Nuclear Operating Company, Inc.)
Owner | [7 empty] | : | APCO (Alabama Power Company)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-10-01
Thermal power | [12 empty] | : |  |  | 2775 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-08-18
Gross electrical power | [12 empty] | : |  |  | 918 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-12-01
Reference unit power (net) | [12 empty] | : |  |  | 874 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.38
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.02 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.27
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 45 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7802.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.63 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 667.90 | 624.09 |  |  |  | 663.65 |  | 642.37 | [8 empty] | 661.44 |  |  | 634.76 | [6 empty] | 652.73 |  | 652.89 |  |  |  | 633.72 |  |  | 659.88 |  |  | 642.14 | [9 empty] | 666.85 |  |  | 7802.41
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 102.71 | 102.60 |  |  |  | 102.06 |  | 102.08 | [8 empty] | 101.72 |  |  | 100.87 | [6 empty] | 100.38 |  | 100.40 |  |  |  | 100.70 |  |  | 101.48 |  |  | 102.04 | [9 empty] | 102.55 |  |  | 101.63
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 303814.09 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.96 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.88 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.62 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.99 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.39 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.67 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.11 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 1047.90 |  |  | 1747 |  |  |  | 820 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 64.19 |  |  | 68.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 5919.80 |  |  | 7568 |  |  |  | 829 | [10 empty] | 81.52 |  |  |  | 81.52 | [5 empty] | 81.52 |  |  | 86.39 |  |  |  | 11.24 |  | 10.32 | [8 empty] | 8.16 |  |  |  |  | 0.00
1979 |  |  |  | 1732.40 |  |  | 2502 |  |  |  | 829 | [10 empty] | 23.85 |  |  |  | 23.85 | [5 empty] | 23.86 |  |  | 28.56 |  |  |  | 14.61 |  | 4.08 | [8 empty] | 72.07 |  |  |  |  | 0.00
1980 |  |  |  | 4607.80 |  |  | 6110 |  |  |  | 814 | [10 empty] | 70.17 |  |  |  | 74.38 | [5 empty] | 64.44 |  |  | 69.56 |  |  |  | 5.04 |  | 3.94 | [8 empty] | 21.68 |  |  |  |  | 4.21
1981 |  |  |  | 2653.00 |  |  | 3624 |  |  |  | 804 | [10 empty] | 41.54 |  |  |  | 41.54 | [5 empty] | 37.67 |  |  | 41.37 |  |  |  | 45.41 |  | 34.56 | [8 empty] | 23.90 |  |  |  |  | 0.00
1982 |  |  |  | 5233.30 |  |  | 6936 |  |  |  | 804 | [10 empty] | 79.29 |  |  |  | 79.29 | [5 empty] | 74.30 |  |  | 79.18 |  |  |  | 20.47 |  | 20.41 | [8 empty] | 0.31 |  |  |  |  | 0.00
1983 |  |  |  | 5268.60 |  |  | 6832 |  |  |  | 804 | [10 empty] | 77.73 |  |  |  | 77.73 | [5 empty] | 74.81 |  |  | 77.99 |  |  |  | 1.31 |  | 1.03 | [8 empty] | 21.24 |  |  |  |  | 0.00
1984 |  |  |  | 5432.66 |  |  | 6920 |  |  |  | 804 | [10 empty] | 78.50 |  |  |  | 78.50 | [5 empty] | 76.92 |  |  | 78.78 |  |  |  | 1.16 |  | 0.92 | [8 empty] | 20.58 |  |  |  |  | 0.00
1985 |  |  |  | 5868.67 |  |  | 7378 |  |  |  | 816 | [10 empty] | 84.29 |  |  |  | 84.29 | [5 empty] | 82.10 |  |  | 84.22 |  |  |  | 1.82 |  | 1.56 | [8 empty] | 14.15 |  |  |  |  | 0.00
1986 |  |  |  | 5738.56 |  |  | 7247 |  |  |  | 827 | [10 empty] | 82.41 |  |  |  | 82.41 | [5 empty] | 79.21 |  |  | 82.73 |  |  |  | 1.58 |  | 1.32 | [8 empty] | 16.27 |  |  |  |  | 0.00
1987 |  |  |  | 6444.86 |  |  | 8201 |  |  |  | 825 | [10 empty] | 93.68 |  |  |  | 93.68 | [5 empty] | 89.17 |  |  | 93.62 |  |  |  | 3.77 |  | 3.67 | [8 empty] | 2.64 |  |  |  |  | 0.00
1988 |  |  |  | 5908.21 |  |  | 7363 |  |  |  | 813 | [10 empty] | 83.80 |  |  |  | 83.80 | [5 empty] | 82.73 |  |  | 83.82 |  |  |  | 0.68 |  | 0.58 | [8 empty] | 15.62 |  |  |  |  | 0.00
1989 |  |  |  | 6022.64 |  |  | 7520 |  |  |  | 824 | [10 empty] | 86.02 |  |  |  | 86.02 | [5 empty] | 83.44 |  |  | 85.84 |  |  |  | 1.01 |  | 0.88 | [8 empty] | 13.10 |  |  |  |  | 0.00
1990 |  |  |  | 6908.57 |  |  | 8681 |  |  |  | 824 | [10 empty] | 99.11 |  |  |  | 99.11 | [5 empty] | 95.71 |  |  | 99.10 |  |  |  | 0.89 |  | 0.89 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 5416.06 |  |  | 6870 |  |  |  | 814 | [10 empty] | 78.44 |  |  |  | 78.90 | [5 empty] | 75.95 |  |  | 78.42 |  |  |  | 1.68 |  | 1.35 | [8 empty] | 19.75 |  |  |  |  | 0.46
1992 |  |  |  | 5667.94 |  |  | 7119 |  |  |  | 812 | [10 empty] | 80.98 |  |  |  | 80.98 | [5 empty] | 79.47 |  |  | 81.05 |  |  |  | 0.46 |  | 0.38 | [8 empty] | 18.65 |  |  |  |  | 0.00
1993 |  |  |  | 6873.90 |  |  | 8522 |  |  |  | 812 | [10 empty] | 97.28 |  |  |  | 97.28 | [5 empty] | 96.64 |  |  | 97.28 |  |  |  | 2.72 |  | 2.72 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 6059.84 |  |  | 7546 |  |  |  | 812 | [10 empty] | 86.11 |  |  |  | 86.11 | [5 empty] | 85.19 |  |  | 86.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.89 |  |  |  |  | 0.00
1995 |  |  |  | 5751.98 |  |  | 7220 |  |  |  | 812 | [10 empty] | 82.41 |  |  |  | 82.41 | [5 empty] | 80.86 |  |  | 82.42 |  |  |  | 4.72 |  | 4.08 | [8 empty] | 13.51 |  |  |  |  | 0.00
1996 |  |  |  | 7142.30 |  |  | 8740 |  |  |  | 812 | [10 empty] | 99.50 |  |  |  | 99.50 | [5 empty] | 100.14 |  |  | 99.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.50 |  |  |  |  | 0.00
1997 |  |  |  | 5433.98 |  |  | 6803 |  |  |  | 821 | [10 empty] | 77.72 |  |  |  | 77.72 | [5 empty] | 75.54 |  |  | 77.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.28 |  |  |  |  | 0.00
1998 |  |  |  | 5237.94 |  |  | 6539 |  |  |  | 822 | [10 empty] | 74.81 |  |  |  | 74.81 | [5 empty] | 72.74 |  |  | 74.65 |  |  |  | 6.58 |  | 5.27 | [8 empty] | 19.92 |  |  |  |  | 0.00
1999 |  |  |  | 7226.52 |  |  | 8695 |  |  |  | 847 | [10 empty] | 99.26 |  |  |  | 99.26 | [5 empty] | 97.40 |  |  | 99.26 |  |  |  | 0.74 |  | 0.74 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 5204.09 |  |  | 6775 |  |  |  | 828 | [10 empty] | 76.82 |  |  |  | 76.82 | [5 empty] | 71.55 |  |  | 77.13 |  |  |  | 0.42 |  | 0.32 | [8 empty] | 22.86 |  |  |  |  | 0.00
2001 |  |  |  | 6392.53 |  |  | 7736 |  |  |  | 833 | [10 empty] | 88.33 |  |  |  | 88.33 | [5 empty] | 87.60 |  |  | 88.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.67 |  |  |  |  | 0.00
2002 |  |  |  | 7221.79 |  |  | 8641 |  |  |  | 833 | [10 empty] | 98.65 |  |  |  | 98.65 | [5 empty] | 98.97 |  |  | 98.64 |  |  |  | 1.35 |  | 1.35 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 6609.90 |  |  | 7909 |  |  |  | 830 | [10 empty] | 90.30 |  |  |  | 90.30 | [5 empty] | 90.91 |  |  | 90.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.70 |  |  |  |  | 0.00
2004 |  |  |  | 6423.88 |  |  | 7627 |  |  |  | 851 | [10 empty] | 86.99 |  |  |  | 86.99 | [5 empty] | 86.83 |  |  | 86.83 |  |  |  | 0.53 |  | 0.46 | [8 empty] | 12.54 |  |  |  |  | 0.00
2005 |  |  |  | 7402.19 |  |  | 8709 |  |  |  | 833 | [10 empty] | 99.42 |  |  |  | 99.42 | [5 empty] | 101.43 |  |  | 99.41 |  |  |  | 0.58 |  | 0.58 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 6419.32 |  |  | 7578 |  |  |  | 851 | [10 empty] | 86.53 |  |  |  | 86.53 | [5 empty] | 86.11 |  |  | 86.51 |  |  |  | 0.71 |  | 0.62 | [8 empty] | 12.85 |  |  |  |  | 0.00
2007 |  |  |  | 6530.77 |  |  | 7663 |  |  |  | 851 | [10 empty] | 87.49 |  |  |  | 87.49 | [5 empty] | 87.61 |  |  | 87.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.51 |  |  |  |  | 0.00
2008 |  |  |  | 7281.47 |  |  | 8579 |  |  |  | 851 | [10 empty] | 97.68 |  |  |  | 97.68 | [5 empty] | 97.41 |  |  | 97.67 |  |  |  | 2.32 |  | 2.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 6711.12 |  |  | 7922 |  |  |  | 851 | [10 empty] | 90.46 |  |  |  | 90.46 | [5 empty] | 90.02 |  |  | 90.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.54 |  |  |  |  | 0.00
2010 |  |  |  | 6577.44 |  |  | 7806 |  |  |  | 851 | [10 empty] | 89.13 |  |  |  | 89.13 | [5 empty] | 88.23 |  |  | 89.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.87 |  |  |  |  | 0.00
2011 |  |  |  | 7764.30 |  |  | 8760 |  |  |  | 874 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.41 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 6929.42 |  |  | 7967 |  |  |  | 874 | [10 empty] | 90.71 |  |  |  | 90.71 | [5 empty] | 90.26 |  |  | 90.70 |  |  |  | 0.99 |  | 0.91 | [8 empty] | 8.38 |  |  |  |  | 0.00
2013 |  |  |  | 7021.41 |  |  | 8033 |  |  |  | 874 | [10 empty] | 91.70 |  |  |  | 91.70 | [5 empty] | 91.70 |  |  | 91.69 |  |  |  | 0.66 |  | 0.61 | [8 empty] | 7.69 |  |  |  |  | 0.00
2014 |  |  |  | 7777.43 |  |  | 8760 |  |  |  | 874 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.58 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6680.66 |  |  | 7652 |  |  |  | 874 | [10 empty] | 87.35 |  |  |  | 87.35 | [5 empty] | 87.26 |  |  | 87.35 |  |  |  | 0.82 |  | 0.73 | [8 empty] | 11.93 |  |  |  |  | 0.00
2016 |  |  |  | 6684.05 |  |  | 7617 |  |  |  | 874 | [10 empty] | 86.72 |  |  |  | 86.72 | [5 empty] | 87.06 |  |  | 86.71 |  |  |  | 3.78 |  | 3.41 | [8 empty] | 9.87 |  |  |  |  | 0.00
2017 |  |  |  | 7750.07 |  |  | 8760 |  |  |  | 874 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.23 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 6409.66 |  |  | 7567 |  |  |  | 874 | [10 empty] | 86.37 |  |  |  | 86.37 | [5 empty] | 83.72 |  |  | 86.38 |  |  |  | 4.03 |  | 3.63 | [8 empty] | 10.00 |  |  |  |  | 0.00
2019 |  |  |  | 7003.19 |  |  | 7993 |  |  |  | 874 | [10 empty] | 91.26 |  |  |  | 91.26 | [5 empty] | 91.47 |  |  | 91.24 |  |  |  | 1.92 |  | 1.79 | [8 empty] | 6.95 |  |  |  |  | 0.00
2020 |  |  |  | 7802.41 |  |  | 8783 |  |  |  | 874 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.63 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1977 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 196
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 946
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 52
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 18
L. |  | Human factor related | [39 empty] | 11
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
Z. |  | Other | [39 empty] | 2
Subtotal | [37 empty] | 1000 |  |  |  | 227 | [11 empty] | 4
Total | [22 empty] | 0 | [14 empty] | 1231
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1977 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 9
16. |  |  | Steam generation systems | [34 empty] | 21
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 80
32. |  |  | Feedwater and Main Steam System | [34 empty] | 17
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 53
Total | [37 empty] | 208

## FARLEY-2
2020 Operating Experience
US-364 | [8 empty] | FARLEY-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SOUTHERN (Southern Nuclear Operating Company, Inc.)
Owner | [7 empty] | : | APCO (Alabama Power Company)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-10-01
Thermal power | [12 empty] | : |  |  | 2775 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-05-25
Gross electrical power | [12 empty] | : |  |  | 928 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-07-30
Reference unit power (net) | [12 empty] | : |  |  | 883 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.38
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.02 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.27
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 45 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6973.38 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.37 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.37 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.63 %
Load Factor (LF) | [18 empty] | : | 89.91 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.37 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 846 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 668.42 | 624.75 |  |  |  | 663.30 |  | 619.76 | [8 empty] | 662.33 |  |  | 635.64 | [6 empty] | 654.48 |  | 654.04 |  |  |  | 634.99 |  |  | 205.45 |  |  | 286.80 | [9 empty] | 663.43 |  |  | 6973.38
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 33.33 |  |  | 51.44 | [9 empty] | 100.00 |  |  | 90.37
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 33.33 |  |  | 51.44 | [9 empty] | 100.00 |  |  | 90.37
LF [%] |  |  |  |  | 101.75 | 101.66 |  |  |  | 100.97 |  | 97.48 | [8 empty] | 100.82 |  |  | 99.98 | [6 empty] | 99.62 |  | 99.56 |  |  |  | 99.88 |  |  | 31.27 |  |  | 45.11 | [9 empty] | 100.99 |  |  | 89.91
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 33.33 |  |  | 51.53 | [9 empty] | 100.00 |  |  | 90.37
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 66.67 |  |  | 48.56 | [9 empty] | 0.00 |  |  | 9.63
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 237769.34 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.75 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.59 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.11 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.3 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.82 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 2920.80 |  |  | 3665 |  |  |  | 825 | [10 empty] | 99.28 |  |  |  | 99.28 | [5 empty] | 95.08 |  |  | 98.48 |  |  |  | 0.72 |  | 0.72 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 5311.30 |  |  | 6931 |  |  |  | 814 | [10 empty] | 79.41 |  |  |  | 79.41 | [5 empty] | 74.49 |  |  | 79.12 |  |  |  | 10.30 |  | 9.12 | [8 empty] | 11.47 |  |  |  |  | 0.00
1983 |  |  |  | 5984.10 |  |  | 7696 |  |  |  | 814 | [10 empty] | 87.72 |  |  |  | 87.72 | [5 empty] | 83.92 |  |  | 87.85 |  |  |  | 1.97 |  | 1.77 | [8 empty] | 10.52 |  |  |  |  | 0.00
1984 |  |  |  | 6618.90 |  |  | 8276 |  |  |  | 814 | [10 empty] | 94.18 |  |  |  | 94.41 | [5 empty] | 92.57 |  |  | 94.22 |  |  |  | 5.59 |  | 5.59 | [8 empty] | 0.00 |  |  |  |  | 0.22
1985 |  |  |  | 5474.18 |  |  | 6813 |  |  |  | 809 | [10 empty] | 77.36 |  |  |  | 77.85 | [5 empty] | 77.24 |  |  | 77.77 |  |  |  | 1.59 |  | 1.26 | [8 empty] | 20.89 |  |  |  |  | 0.49
1986 |  |  |  | 5959.87 |  |  | 7455 |  |  |  | 829 | [10 empty] | 85.22 |  |  |  | 85.22 | [5 empty] | 82.07 |  |  | 85.10 |  |  |  | 2.41 |  | 2.11 | [8 empty] | 12.67 |  |  |  |  | 0.00
1987 |  |  |  | 4910.40 |  |  | 6396 |  |  |  | 824 | [10 empty] | 73.02 |  |  |  | 73.02 | [5 empty] | 68.00 |  |  | 73.01 |  |  |  | 11.35 |  | 9.35 | [8 empty] | 17.64 |  |  |  |  | 0.00
1988 |  |  |  | 6550.39 |  |  | 8039 |  |  |  | 823 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 90.59 |  |  | 91.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 5621.62 |  |  | 7037 |  |  |  | 830 | [10 empty] | 80.48 |  |  |  | 80.48 | [5 empty] | 77.32 |  |  | 80.33 |  |  |  | 4.66 |  | 3.94 | [8 empty] | 15.59 |  |  |  |  | 0.00
1990 |  |  |  | 5276.96 |  |  | 6478 |  |  |  | 828 | [10 empty] | 71.77 |  |  |  | 71.77 | [5 empty] | 72.75 |  |  | 73.95 |  |  |  | 4.34 |  | 3.25 | [8 empty] | 24.98 |  |  |  |  | 0.00
1991 |  |  |  | 6739.94 |  |  | 8376 |  |  |  | 824 | [10 empty] | 95.64 |  |  |  | 95.96 | [5 empty] | 93.37 |  |  | 95.62 |  |  |  | 2.60 |  | 2.56 | [8 empty] | 1.48 |  |  |  |  | 0.32
1992 |  |  |  | 5409.94 |  |  | 6987 |  |  |  | 824 | [10 empty] | 79.53 |  |  |  | 79.53 | [5 empty] | 74.74 |  |  | 79.54 |  |  |  | 2.77 |  | 2.27 | [8 empty] | 18.20 |  |  |  |  | 0.00
1993 |  |  |  | 5248.51 |  |  | 6644 |  |  |  | 822 | [10 empty] | 75.76 |  |  |  | 75.76 | [5 empty] | 72.87 |  |  | 75.84 |  |  |  | 6.60 |  | 5.35 | [8 empty] | 18.89 |  |  |  |  | 0.00
1994 |  |  |  | 7147.21 |  |  | 8660 |  |  |  | 822 | [10 empty] | 98.88 |  |  |  | 98.88 | [5 empty] | 99.26 |  |  | 98.86 |  |  |  | 1.12 |  | 1.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 5091.35 |  |  | 6984 |  |  |  | 822 | [10 empty] | 79.74 |  |  |  | 79.74 | [5 empty] | 70.71 |  |  | 79.73 |  |  |  | 4.21 |  | 3.51 | [8 empty] | 16.75 |  |  |  |  | 0.00
1996 |  |  |  | 5741.28 |  |  | 7160 |  |  |  | 822 | [10 empty] | 81.46 |  |  |  | 81.46 | [5 empty] | 79.51 |  |  | 81.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.54 |  |  |  |  | 0.00
1997 |  |  |  | 7280.91 |  |  | 8760 |  |  |  | 822 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.11 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 6271.42 |  |  | 7514 |  |  |  | 824 | [10 empty] | 85.82 |  |  |  | 85.82 | [5 empty] | 86.83 |  |  | 85.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.18 |  |  |  |  | 0.00
1999 |  |  |  | 5356.22 |  |  | 7242 |  |  |  | 852 | [10 empty] | 82.68 |  |  |  | 82.68 | [5 empty] | 71.77 |  |  | 82.67 |  |  |  | 0.95 |  | 0.80 | [8 empty] | 16.52 |  |  |  |  | 0.00
2000 |  |  |  | 7362.56 |  |  | 8736 |  |  |  | 839 | [10 empty] | 99.45 |  |  |  | 99.45 | [5 empty] | 99.88 |  |  | 99.45 |  |  |  | 0.55 |  | 0.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 5777.73 |  |  | 6921 |  |  |  | 842 | [10 empty] | 79.03 |  |  |  | 79.03 | [5 empty] | 78.33 |  |  | 79.01 |  |  |  | 0.79 |  | 0.63 | [8 empty] | 20.34 |  |  |  |  | 0.00
2002 |  |  |  | 6463.44 |  |  | 7682 |  |  |  | 842 | [10 empty] | 87.71 |  |  |  | 87.71 | [5 empty] | 87.63 |  |  | 87.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.29 |  |  |  |  | 0.00
2003 |  |  |  | 7379.36 |  |  | 8687 |  |  |  | 839 | [10 empty] | 99.18 |  |  |  | 99.18 | [5 empty] | 100.40 |  |  | 99.17 |  |  |  | 0.46 |  | 0.45 | [8 empty] | 0.37 |  |  |  |  | 0.00
2004 |  |  |  | 6724.10 |  |  | 7949 |  |  |  | 849 | [10 empty] | 90.53 |  |  |  | 90.53 | [5 empty] | 90.70 |  |  | 90.49 |  |  |  | 0.31 |  | 0.28 | [8 empty] | 9.19 |  |  |  |  | 0.00
2005 |  |  |  | 6351.74 |  |  | 7566 |  |  |  | 842 | [10 empty] | 86.39 |  |  |  | 86.39 | [5 empty] | 86.11 |  |  | 86.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.61 |  |  |  |  | 0.00
2006 |  |  |  | 7620.30 |  |  | 8760 |  |  |  | 860 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.15 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 6572.09 |  |  | 7660 |  |  |  | 860 | [10 empty] | 87.46 |  |  |  | 87.46 | [5 empty] | 87.24 |  |  | 87.44 |  |  |  | 0.75 |  | 0.67 | [8 empty] | 11.87 |  |  |  |  | 0.00
2008 |  |  |  | 6795.52 |  |  | 7956 |  |  |  | 860 | [10 empty] | 90.47 |  |  |  | 90.47 | [5 empty] | 89.96 |  |  | 90.57 |  |  |  | 0.14 |  | 0.12 | [8 empty] | 9.41 |  |  |  |  | 0.00
2009 |  |  |  | 7262.45 |  |  | 8427 |  |  |  | 860 | [10 empty] | 96.22 |  |  |  | 96.22 | [5 empty] | 96.40 |  |  | 96.20 |  |  |  | 3.78 |  | 3.78 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 6592.24 |  |  | 7682 |  |  |  | 860 | [10 empty] | 87.71 |  |  |  | 87.71 | [5 empty] | 87.50 |  |  | 87.69 |  |  |  | 0.38 |  | 0.34 | [8 empty] | 11.95 |  |  |  |  | 0.00
2011 |  |  |  | 6666.95 |  |  | 7826 |  |  |  | 860 | [10 empty] | 89.37 |  |  |  | 89.37 | [5 empty] | 88.50 |  |  | 89.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.63 |  |  |  |  | 0.00
2012 |  |  |  | 7833.57 |  |  | 8784 |  |  |  | 883 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.00 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 7076.62 |  |  | 8142 |  |  |  | 883 | [10 empty] | 92.95 |  |  |  | 92.95 | [5 empty] | 91.48 |  |  | 92.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.05 |  |  |  |  | 0.00
2014 |  |  |  | 6727.96 |  |  | 7718 |  |  |  | 883 | [10 empty] | 88.10 |  |  |  | 88.10 | [5 empty] | 86.98 |  |  | 88.11 |  |  |  | 3.46 |  | 3.15 | [8 empty] | 8.75 |  |  |  |  | 0.00
2015 |  |  |  | 7606.92 |  |  | 8610 |  |  |  | 883 | [10 empty] | 98.28 |  |  |  | 98.28 | [5 empty] | 98.34 |  |  | 98.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.72 |  |  |  |  | 0.00
2016 |  |  |  | 7014.26 |  |  | 7954 |  |  |  | 883 | [10 empty] | 90.55 |  |  |  | 90.55 | [5 empty] | 90.43 |  |  | 90.55 |  |  |  | 1.15 |  | 1.05 | [8 empty] | 8.39 |  |  |  |  | 0.00
2017 |  |  |  | 7054.03 |  |  | 8019 |  |  |  | 883 | [10 empty] | 91.54 |  |  |  | 91.54 | [5 empty] | 91.20 |  |  | 91.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.46 |  |  |  |  | 0.00
2018 |  |  |  | 7655.38 |  |  | 8760 |  |  |  | 883 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.97 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7133.77 |  |  | 8091 |  |  |  | 883 | [10 empty] | 92.38 |  |  |  | 92.38 | [5 empty] | 92.23 |  |  | 92.36 |  |  |  | 0.48 |  | 0.44 | [8 empty] | 7.18 |  |  |  |  | 0.00
2020 |  |  |  | 6973.38 |  |  | 7938 |  |  |  | 883 | [10 empty] | 90.37 |  |  |  | 90.37 | [5 empty] | 89.91 |  |  | 90.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.63 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 128
B. |  | Refuelling without maintenance | [20 empty] | 846 | [14 empty] | 21
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 769
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 32
E. |  | Testing of plant systems or components | [35 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 11
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 0
Z. |  | Other | [39 empty] | 2 | [11 empty] | 1
Subtotal | [22 empty] | 846 | [14 empty] | 828 |  |  |  | 141 | [11 empty] | 2
Total | [22 empty] | 846 | [14 empty] | 971
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 15
15. |  |  | Reactor Cooling Systems | [34 empty] | 35
16. |  |  | Steam generation systems | [34 empty] | 20
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 135
Highlights (2020)
Refueling Outage 27.

## FERMI-2
2020 Operating Experience
US-341 | [8 empty] | FERMI-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DTEDISON (DETROIT EDISON CO.)
Owner | [7 empty] | : | DTE (DTE Energy Co.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GECTG (GEC TURBINE GENERATORS, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-09-26
Thermal power | [12 empty] | : |  |  | 3486 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-09-21
Gross electrical power | [12 empty] | : |  |  | 1198 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-01-23
Reference unit power (net) | [12 empty] | : |  |  | 1115 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.3
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.44
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 19404 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.8 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 37.73 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6070.78 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 62.35 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 62.35 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 37.65 %
Load Factor (LF) | [18 empty] | : | 61.98 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 62.33 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3309 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 835.25 | 789.45 |  |  |  | 542.95 |  | -4.05 | [8 empty] | -4.93 |  |  | -10.77 | [6 empty] | -12.20 |  | 605.28 |  |  |  | 816.40 |  |  | 826.57 |  |  | 825.02 | [9 empty] | 861.81 |  |  | 6070.78
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 64.54 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 84.45 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 62.35
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 64.54 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 84.45 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 62.35
LF [%] |  |  |  |  | 100.69 | 101.73 |  |  |  | 65.45 |  | -0.50 | [8 empty] | -0.59 |  |  | -1.34 | [6 empty] | -1.47 |  | 72.96 |  |  |  | 101.69 |  |  | 99.64 |  |  | 102.77 | [9 empty] | 103.89 |  |  | 61.98
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 64.38 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 84.41 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 62.33
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 35.46 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 15.55 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 37.65
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 212972.75 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.3 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.97 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.18 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.97 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.84 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.65 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.78 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 4060.06 |  |  | 4719 |  |  |  | 1093 | [10 empty] | 55.90 |  |  |  | 55.90 | [5 empty] | 43.95 |  |  | 56.13 |  |  |  | 42.89 |  | 41.98 | [8 empty] | 2.11 |  |  |  |  | 0.00
1989 |  |  |  | 5230.72 |  |  | 5575 |  |  |  | 1093 | [10 empty] | 63.42 |  |  |  | 63.42 | [5 empty] | 54.63 |  |  | 63.64 |  |  |  | 11.35 |  | 8.12 | [8 empty] | 28.46 |  |  |  |  | 0.00
1990 |  |  |  | 7118.28 |  |  | 7266 |  |  |  | 1059 | [10 empty] | 82.30 |  |  |  | 82.30 | [5 empty] | 76.70 |  |  | 82.95 |  |  |  | 1.82 |  | 1.53 | [8 empty] | 16.17 |  |  |  |  | 0.00
1991 |  |  |  | 6180.93 |  |  | 6466 |  |  |  | 1059 | [10 empty] | 72.83 |  |  |  | 72.83 | [5 empty] | 66.63 |  |  | 73.81 |  |  |  | 1.19 |  | 0.88 | [8 empty] | 26.29 |  |  |  |  | 0.00
1992 |  |  |  | 7356.77 |  |  | 7019 |  |  |  | 1060 | [10 empty] | 79.15 |  |  |  | 79.15 | [5 empty] | 79.01 |  |  | 79.91 |  |  |  | 2.84 |  | 2.32 | [8 empty] | 18.54 |  |  |  |  | 0.00
1993 |  |  |  | 8284.71 |  |  | 8076 |  |  |  | 1085 | [10 empty] | 92.10 |  |  |  | 92.10 | [5 empty] | 87.17 |  |  | 92.19 |  |  |  | 4.48 |  | 4.32 | [8 empty] | 3.59 |  |  |  |  | 0.00
1994 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1085 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 84.69 | [8 empty] | 15.31 |  |  |  |  | 0.00
1995 |  |  |  | 5132.02 |  |  | 6509 |  |  |  | 997 | [10 empty] | 71.75 |  |  |  | 71.75 | [5 empty] | 58.74 |  |  | 74.30 |  |  |  | 26.14 |  | 25.39 | [8 empty] | 2.86 |  |  |  |  | 0.00
1996 |  |  |  | 4790.02 |  |  | 5859 |  |  |  | 876 | [10 empty] | 58.23 |  |  |  | 58.23 | [5 empty] | 62.25 |  |  | 66.70 |  |  |  | 28.83 |  | 23.59 | [8 empty] | 18.18 |  |  |  |  | 0.00
1997 |  |  |  | 5579.95 |  |  | 5461 |  |  |  | 1000 | [10 empty] | 70.45 |  |  |  | 70.45 | [5 empty] | 63.60 |  |  | 62.34 |  |  |  | 28.62 |  | 28.24 | [8 empty] | 1.30 |  |  |  |  | 0.00
1998 |  |  |  | 7146.77 |  |  | 6868 |  |  |  | 1098 | [10 empty] | 78.39 |  |  |  | 78.39 | [5 empty] | 74.30 |  |  | 78.40 |  |  |  | 7.84 |  | 6.67 | [8 empty] | 14.95 |  |  |  |  | 0.00
1999 |  |  |  | 9484.66 |  |  | 8698 |  |  |  | 1081 | [10 empty] | 99.29 |  |  |  | 99.29 | [5 empty] | 100.11 |  |  | 99.29 |  |  |  | 0.71 |  | 0.71 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 8237.80 |  |  | 7514 |  |  |  | 1083 | [10 empty] | 85.72 |  |  |  | 85.72 | [5 empty] | 86.59 |  |  | 85.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.28 |  |  |  |  | 0.00
2001 |  |  |  | 8564.03 |  |  | 7837 |  |  |  | 1089 | [10 empty] | 89.27 |  |  |  | 89.27 | [5 empty] | 89.77 |  |  | 89.46 |  |  |  | 0.60 |  | 0.54 | [8 empty] | 10.19 |  |  |  |  | 0.00
2002 |  |  |  | 9302.88 |  |  | 8630 |  |  |  | 1089 | [10 empty] | 98.49 |  |  |  | 98.49 | [5 empty] | 97.52 |  |  | 98.52 |  |  |  | 1.51 |  | 1.51 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 8127.82 |  |  | 7479 |  |  |  | 1089 | [10 empty] | 85.28 |  |  |  | 85.28 | [5 empty] | 85.20 |  |  | 85.38 |  |  |  | 3.59 |  | 3.18 | [8 empty] | 11.54 |  |  |  |  | 0.00
2004 |  |  |  | 8453.11 |  |  | 7764 |  |  |  | 1089 | [10 empty] | 88.18 |  |  |  | 88.18 | [5 empty] | 88.37 |  |  | 88.39 |  |  |  | 4.58 |  | 4.23 | [8 empty] | 7.58 |  |  |  |  | 0.00
2005 |  |  |  | 8767.61 |  |  | 7955 |  |  |  | 1111 | [10 empty] | 90.85 |  |  |  | 90.85 | [5 empty] | 90.08 |  |  | 90.80 |  |  |  | 9.15 |  | 9.15 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 7497.33 |  |  | 7095 |  |  |  | 1111 | [10 empty] | 80.86 |  |  |  | 80.86 | [5 empty] | 77.67 |  |  | 80.99 |  |  |  | 1.83 |  | 1.50 | [8 empty] | 17.63 |  |  |  |  | 0.00
2007 |  |  |  | 8318.37 |  |  | 7542 |  |  |  | 1122 | [10 empty] | 86.11 |  |  |  | 86.11 | [5 empty] | 84.63 |  |  | 86.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.89 |  |  |  |  | 0.00
2008 |  |  |  | 9614.34 |  |  | 8706 |  |  |  | 1122 | [10 empty] | 99.14 |  |  |  | 99.14 | [5 empty] | 97.55 |  |  | 99.11 |  |  |  | 0.86 |  | 0.86 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 7424.68 |  |  | 6855 |  |  |  | 1122 | [10 empty] | 78.29 |  |  |  | 78.29 | [5 empty] | 75.54 |  |  | 78.25 |  |  |  | 13.62 |  | 12.34 | [8 empty] | 9.37 |  |  |  |  | 0.00
2010 |  |  |  | 7743.27 |  |  | 7373 |  |  |  | 1106 | [10 empty] | 87.05 |  |  |  | 87.05 | [5 empty] | 79.92 |  |  | 84.17 |  |  |  | 1.62 |  | 1.43 | [8 empty] | 11.52 |  |  |  |  | 0.00
2011 |  |  |  | 8916.72 |  |  | 8334 |  |  |  | 1085 | [10 empty] | 95.08 |  |  |  | 95.08 | [5 empty] | 93.52 |  |  | 95.14 |  |  |  | 0.16 |  | 0.16 | [8 empty] | 4.77 |  |  |  |  | 0.00
2012 |  |  |  | 5176.46 |  |  | 5562 |  |  |  | 1037 | [10 empty] | 63.37 |  |  |  | 63.37 | [5 empty] | 56.83 |  |  | 63.32 |  |  |  | 28.68 |  | 25.48 | [8 empty] | 11.15 |  |  |  |  | 0.00
2013 |  |  |  | 6609.50 |  |  | 8063 |  |  |  | 1037 | [10 empty] | 92.04 |  |  |  | 92.04 | [5 empty] | 72.75 |  |  | 92.03 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 7.78 |  |  |  |  | 0.00
2014 |  |  |  | 7809.50 |  |  | 7311 |  |  |  | 1122 | [10 empty] | 84.71 |  |  |  | 84.71 | [5 empty] | 79.46 |  |  | 83.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.29 |  |  |  |  | 0.00
2015 |  |  |  | 7346.14 |  |  | 6551 |  |  |  | 1122 | [10 empty] | 74.79 |  |  |  | 74.79 | [5 empty] | 74.74 |  |  | 74.78 |  |  |  | 10.18 |  | 8.48 | [8 empty] | 16.74 |  |  |  |  | 0.00
2016 |  |  |  | 9153.92 |  |  | 8396 |  |  |  | 1122 | [10 empty] | 95.58 |  |  |  | 95.58 | [5 empty] | 92.88 |  |  | 95.58 |  |  |  | 2.77 |  | 2.73 | [8 empty] | 1.69 |  |  |  |  | 0.00
2017 |  |  |  | 8698.33 |  |  | 7952 |  |  |  | 1122 | [10 empty] | 90.77 |  |  |  | 90.77 | [5 empty] | 88.50 |  |  | 90.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.23 |  |  |  |  | 0.00
2018 |  |  |  | 7438.80 |  |  | 6773 |  |  |  | 1115 | [10 empty] | 77.73 |  |  |  | 77.73 | [5 empty] | 76.16 |  |  | 77.32 |  |  |  | 14.08 |  | 12.74 | [8 empty] | 9.54 |  |  |  |  | 0.00
2019 |  |  |  | 9886.26 |  |  | 8743 |  |  |  | 1115 | [10 empty] | 99.81 |  |  |  | 99.81 | [5 empty] | 101.22 |  |  | 99.81 |  |  |  | 0.19 |  | 0.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 6070.78 |  |  | 5475 |  |  |  | 1115 | [10 empty] | 62.35 |  |  |  | 62.35 | [5 empty] | 61.98 |  |  | 62.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.65 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 809
B. |  | Refuelling without maintenance | [20 empty] | 3571 | [14 empty] | 108
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 649
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 186
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 12
L. |  | Human factor related | [39 empty] | 6
P. |  | Fire | [39 empty] | 1
Subtotal | [22 empty] | 3571 | [14 empty] | 943 |  |  |  | 816 | [11 empty] | 12
Total | [22 empty] | 3571 | [14 empty] | 1771
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 24
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 38
14. |  |  | Safety Systems | [34 empty] | 23
15. |  |  | Reactor Cooling Systems | [34 empty] | 19
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 13
31. |  |  | Turbine and auxiliaries | [34 empty] | 303
32. |  |  | Feedwater and Main Steam System | [34 empty] | 28
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 48
35. |  |  | All other I&C Systems | [34 empty] | 10
41. |  |  | Main Generator Systems | [34 empty] | 199
42. |  |  | Electrical Power Supply Systems | [34 empty] | 91
Total | [37 empty] | 813
Highlights (2020)
Refueling Outage 20 (RFO20)

## FITZPATRICK
2020 Operating Experience
US-333 | [8 empty] | FITZPATRICK | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-09-01
Thermal power | [12 empty] | : |  |  | 2536 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-02-01
Gross electrical power | [12 empty] | : |  |  | 849 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-07-28
Reference unit power (net) | [12 empty] | : |  |  | 813 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.06
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.44
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 31800 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.26 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 137 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6608.23 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.22 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.03 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.09 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.03 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.87 %
Load Factor (LF) | [18 empty] | : | 92.53 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.02 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 701 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 613.12 | 410.70 |  |  |  | 624.65 |  | 608.37 | [8 empty] | 626.15 |  |  | 598.31 | [6 empty] | 602.96 |  | 564.09 |  |  |  | 202.49 |  |  | 516.83 |  |  | 615.47 | [9 empty] | 625.09 |  |  | 6608.23
EAF [%] |  |  |  |  | 97.57 | 76.19 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 43.44 |  |  | 85.37 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.03
UCF [%] |  |  |  |  | 97.57 | 76.19 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 43.44 |  |  | 85.37 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.03
LF [%] |  |  |  |  | 101.36 | 72.58 |  |  |  | 103.27 |  | 103.93 | [8 empty] | 103.52 |  |  | 102.21 | [6 empty] | 99.68 |  | 93.26 |  |  |  | 34.59 |  |  | 85.44 |  |  | 105.14 | [9 empty] | 103.34 |  |  | 92.53
OF [%] |  |  |  |  | 97.58 | 76.15 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 43.47 |  |  | 85.35 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.02
FLR [%] |  |  |  |  | 2.43 | 23.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.22
UCL [%] |  |  |  |  | 2.43 | 23.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.09
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 56.56 |  |  | 14.63 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.87
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 331284.88 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.44 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.27 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.73 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.43 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.84 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.52 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.15 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.42 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 2153.70 |  |  | 4369 |  |  |  | 819 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 50.37 |  |  | 70.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1976 |  |  |  | 4156.40 |  |  | 6284 |  |  |  | 670 | [10 empty] | 70.45 |  |  |  | 70.45 | [5 empty] | 70.62 |  |  | 71.54 |  |  |  | 21.74 |  | 19.58 | [8 empty] | 9.97 |  |  |  |  | 0.00
1977 |  |  |  | 3893.40 |  |  | 5986 |  |  |  | 770 | [10 empty] | 57.72 |  |  |  | 57.72 | [5 empty] | 57.72 |  |  | 68.33 |  |  |  | 29.58 |  | 24.25 | [8 empty] | 18.03 |  |  |  |  | 0.00
1978 |  |  |  | 4197.40 |  |  | 6311 |  |  |  | 800 | [10 empty] | 59.87 |  |  |  | 59.87 | [5 empty] | 59.89 |  |  | 72.04 |  |  |  | 11.41 |  | 7.71 | [8 empty] | 32.41 |  |  |  |  | 0.00
1979 |  |  |  | 2964.70 |  |  | 4450 |  |  |  | 800 | [10 empty] | 42.30 |  |  |  | 42.30 | [5 empty] | 42.30 |  |  | 50.80 |  |  |  | 55.65 |  | 53.08 | [8 empty] | 4.61 |  |  |  |  | 0.00
1980 |  |  |  | 4334.10 |  |  | 6162 |  |  |  | 802 | [10 empty] | 70.45 |  |  |  | 71.04 | [5 empty] | 61.52 |  |  | 70.15 |  |  |  | 3.77 |  | 2.78 | [8 empty] | 26.18 |  |  |  |  | 0.59
1981 |  |  |  | 4779.70 |  |  | 6539 |  |  |  | 810 | [10 empty] | 74.75 |  |  |  | 74.75 | [5 empty] | 67.36 |  |  | 74.65 |  |  |  | 9.98 |  | 8.29 | [8 empty] | 16.96 |  |  |  |  | 0.00
1982 |  |  |  | 4959.70 |  |  | 6570 |  |  |  | 810 | [10 empty] | 75.28 |  |  |  | 75.28 | [5 empty] | 69.90 |  |  | 75.00 |  |  |  | 7.76 |  | 6.33 | [8 empty] | 18.39 |  |  |  |  | 0.00
1983 |  |  |  | 4634.30 |  |  | 6183 |  |  |  | 810 | [10 empty] | 70.66 |  |  |  | 70.66 | [5 empty] | 65.31 |  |  | 70.58 |  |  |  | 5.08 |  | 3.78 | [8 empty] | 25.56 |  |  |  |  | 0.00
1984 |  |  |  | 4899.36 |  |  | 6745 |  |  |  | 810 | [10 empty] | 76.88 |  |  |  | 76.88 | [5 empty] | 68.86 |  |  | 76.79 |  |  |  | 5.04 |  | 4.08 | [8 empty] | 19.04 |  |  |  |  | 0.00
1985 |  |  |  | 4166.52 |  |  | 5576 |  |  |  | 810 | [10 empty] | 64.08 |  |  |  | 64.08 | [5 empty] | 58.72 |  |  | 63.65 |  |  |  | 10.19 |  | 7.27 | [8 empty] | 28.65 |  |  |  |  | 0.00
1986 |  |  |  | 6015.61 |  |  | 7931 |  |  |  | 797 | [10 empty] | 90.52 |  |  |  | 90.52 | [5 empty] | 86.14 |  |  | 90.54 |  |  |  | 1.77 |  | 1.63 | [8 empty] | 7.84 |  |  |  |  | 0.00
1987 |  |  |  | 4198.34 |  |  | 5891 |  |  |  | 795 | [10 empty] | 67.11 |  |  |  | 67.11 | [5 empty] | 60.27 |  |  | 67.25 |  |  |  | 5.61 |  | 3.99 | [8 empty] | 28.90 |  |  |  |  | 0.00
1988 |  |  |  | 4356.87 |  |  | 5844 |  |  |  | 780 | [10 empty] | 66.53 |  |  |  | 66.53 | [5 empty] | 63.54 |  |  | 66.53 |  |  |  | 5.94 |  | 4.20 | [8 empty] | 29.26 |  |  |  |  | 0.00
1989 |  |  |  | 6155.35 |  |  | 7944 |  |  |  | 757 | [10 empty] | 90.27 |  |  |  | 90.27 | [5 empty] | 92.82 |  |  | 90.68 |  |  |  | 3.65 |  | 3.42 | [8 empty] | 6.31 |  |  |  |  | 0.00
1990 |  |  |  | 4601.93 |  |  | 6045 |  |  |  | 782 | [10 empty] | 68.42 |  |  |  | 68.42 | [5 empty] | 67.18 |  |  | 69.01 |  |  |  | 5.93 |  | 4.32 | [8 empty] | 27.26 |  |  |  |  | 0.00
1991 |  |  |  | 3376.75 |  |  | 4534 |  |  |  | 780 | [10 empty] | 55.98 |  |  |  | 55.98 | [5 empty] | 49.42 |  |  | 51.76 |  |  |  | 42.41 |  | 41.22 | [8 empty] | 2.80 |  |  |  |  | 0.00
1992 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1993 |  |  |  | 4746.46 |  |  | 6301 |  |  |  | 780 | [10 empty] | 71.57 |  |  |  | 71.57 | [5 empty] | 69.47 |  |  | 71.93 |  |  |  | 13.52 |  | 11.19 | [8 empty] | 17.24 |  |  |  |  | 0.00
1994 |  |  |  | 4972.63 |  |  | 7224 |  |  |  | 774 | [10 empty] | 81.91 |  |  |  | 81.91 | [5 empty] | 73.34 |  |  | 82.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.09 |  |  |  |  | 0.00
1995 |  |  |  | 4804.03 |  |  | 6336 |  |  |  | 777 | [10 empty] | 71.58 |  |  |  | 71.58 | [5 empty] | 70.53 |  |  | 72.33 |  |  |  | 6.06 |  | 4.62 | [8 empty] | 23.81 |  |  |  |  | 0.00
1996 |  |  |  | 5290.38 |  |  | 7036 |  |  |  | 765 | [10 empty] | 79.26 |  |  |  | 79.26 | [5 empty] | 78.63 |  |  | 80.10 |  |  |  | 8.37 |  | 7.24 | [8 empty] | 13.50 |  |  |  |  | 0.00
1997 |  |  |  | 6624.58 |  |  | 8310 |  |  |  | 799 | [10 empty] | 94.89 |  |  |  | 96.32 | [5 empty] | 94.65 |  |  | 94.86 |  |  |  | 1.65 |  | 1.61 | [8 empty] | 2.07 |  |  |  |  | 1.43
1998 |  |  |  | 4930.50 |  |  | 6613 |  |  |  | 785 | [10 empty] | 75.21 |  |  |  | 75.21 | [5 empty] | 71.70 |  |  | 75.49 |  |  |  | 8.50 |  | 6.99 | [8 empty] | 17.81 |  |  |  |  | 0.00
1999 |  |  |  | 6567.39 |  |  | 8205 |  |  |  | 799 | [10 empty] | 93.52 |  |  |  | 93.52 | [5 empty] | 93.73 |  |  | 93.66 |  |  |  | 6.48 |  | 6.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 6024.77 |  |  | 7617 |  |  |  | 813 | [10 empty] | 86.63 |  |  |  | 86.63 | [5 empty] | 84.36 |  |  | 86.71 |  |  |  | 3.18 |  | 2.84 | [8 empty] | 10.53 |  |  |  |  | 0.00
2001 |  |  |  | 7090.50 |  |  | 8639 |  |  |  | 813 | [10 empty] | 98.61 |  |  |  | 98.61 | [5 empty] | 99.56 |  |  | 98.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.39 |  |  |  |  | 0.00
2002 |  |  |  | 6595.02 |  |  | 8112 |  |  |  | 813 | [10 empty] | 92.36 |  |  |  | 92.36 | [5 empty] | 92.60 |  |  | 92.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.64 |  |  |  |  | 0.00
2003 |  |  |  | 6965.97 |  |  | 8435 |  |  |  | 813 | [10 empty] | 96.19 |  |  |  | 96.19 | [5 empty] | 97.81 |  |  | 96.29 |  |  |  | 3.81 |  | 3.81 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 6455.92 |  |  | 7984 |  |  |  | 813 | [10 empty] | 90.80 |  |  |  | 90.80 | [5 empty] | 90.40 |  |  | 90.89 |  |  |  | 0.99 |  | 0.91 | [8 empty] | 8.30 |  |  |  |  | 0.00
2005 |  |  |  | 7052.31 |  |  | 8403 |  |  |  | 825 | [10 empty] | 95.94 |  |  |  | 95.94 | [5 empty] | 97.57 |  |  | 95.91 |  |  |  | 4.06 |  | 4.06 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 6758.75 |  |  | 8108 |  |  |  | 852 | [10 empty] | 92.58 |  |  |  | 92.58 | [5 empty] | 90.56 |  |  | 92.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.42 |  |  |  |  | 0.00
2007 |  |  |  | 6918.35 |  |  | 8318 |  |  |  | 852 | [10 empty] | 94.98 |  |  |  | 97.81 | [5 empty] | 92.70 |  |  | 94.95 |  |  |  | 1.56 |  | 1.55 | [8 empty] | 0.64 |  |  |  |  | 2.83
2008 |  |  |  | 6691.05 |  |  | 8105 |  |  |  | 852 | [10 empty] | 92.28 |  |  |  | 92.28 | [5 empty] | 89.41 |  |  | 92.27 |  |  |  | 0.72 |  | 0.67 | [8 empty] | 7.05 |  |  |  |  | 0.00
2009 |  |  |  | 7398.07 |  |  | 8760 |  |  |  | 854 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.89 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 6361.48 |  |  | 7908 |  |  |  | 855 | [10 empty] | 90.30 |  |  |  | 90.30 | [5 empty] | 84.94 |  |  | 90.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.70 |  |  |  |  | 0.00
2011 |  |  |  | 7243.97 |  |  | 8760 |  |  |  | 855 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 96.72 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 6070.46 |  |  | 7536 |  |  |  | 813 | [10 empty] | 85.81 |  |  |  | 85.81 | [5 empty] | 85.00 |  |  | 85.79 |  |  |  | 5.48 |  | 4.97 | [8 empty] | 9.22 |  |  |  |  | 0.00
2013 |  |  |  | 6839.79 |  |  | 8557 |  |  |  | 813 | [10 empty] | 97.68 |  |  |  | 97.68 | [5 empty] | 96.03 |  |  | 97.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.32 |  |  |  |  | 0.00
2014 |  |  |  | 5828.69 |  |  | 7627 |  |  |  | 813 | [10 empty] | 87.08 |  |  |  | 87.08 | [5 empty] | 81.84 |  |  | 87.07 |  |  |  | 0.85 |  | 0.75 | [8 empty] | 12.18 |  |  |  |  | 0.00
2015 |  |  |  | 7382.19 |  |  | 8760 |  |  |  | 813 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.66 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 5857.96 |  |  | 8302 |  |  |  | 813 | [10 empty] | 94.50 |  |  |  | 96.49 | [5 empty] | 82.03 |  |  | 94.51 |  |  |  | 3.51 |  | 3.51 | [8 empty] | 0.00 |  |  |  |  | 1.98
2017 |  |  |  | 6183.13 |  |  | 7708 |  |  |  | 813 | [10 empty] | 85.78 |  |  |  | 85.78 | [5 empty] | 86.82 |  |  | 87.99 |  |  |  | 2.54 |  | 7.55 | [8 empty] | 6.67 |  |  |  |  | 0.00
2018 |  |  |  | 6527.73 |  |  | 8096 |  |  |  | 813 | [10 empty] | 92.43 |  |  |  | 92.43 | [5 empty] | 91.66 |  |  | 92.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.57 |  |  |  |  | 0.00
2019 |  |  |  | 7354.21 |  |  | 8760 |  |  |  | 813 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.26 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 6608.23 |  |  | 8083 |  |  |  | 813 | [10 empty] | 92.03 |  |  |  | 92.03 | [5 empty] | 92.53 |  |  | 92.02 |  |  |  | 2.22 |  | 2.09 | [8 empty] | 5.87 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 334
B. |  | Refuelling without maintenance | [20 empty] | 516 | [14 empty] | 26
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 926
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 181
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 3
H. |  | Nuclear regulatory requirements | [39 empty] | 102
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 41
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 12
Z. |  | Other | [24 empty] | 184 | [10 empty] | 3 |  |  |  | 19
Subtotal | [22 empty] | 516 |  |  |  | 184 | [10 empty] | 1138 |  |  |  | 499 | [11 empty] | 16
Total | [22 empty] | 700 | [14 empty] | 1653
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 18
12. |  |  | Reactor I&C Systems | [34 empty] | 17
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 63
15. |  |  | Reactor Cooling Systems | [34 empty] | 41
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 15
31. |  |  | Turbine and auxiliaries | [34 empty] | 53
32. |  |  | Feedwater and Main Steam System | [34 empty] | 29
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 25
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 18
42. |  |  | Electrical Power Supply Systems | [34 empty] | 48
Total | [37 empty] | 343
Highlights (2020)
Unit was at reduced power of 38% when auto scram occurred as a result of main turbine trip on high RPV water level.

## GINNA
2020 Operating Experience
US-244 | [8 empty] | GINNA | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1966-04-25
Thermal power | [12 empty] | : |  |  | 1775 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1969-12-02
Gross electrical power | [12 empty] | : |  |  | 608 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1970-07-01
Reference unit power (net) | [12 empty] | : |  |  | 560 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 51 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.82
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 317
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.423
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 74 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 39000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.1
| Active core height/length [m] | [13 empty] | : |  |  | 3.59 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19.02 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 17 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4353.1 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.73 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.73 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.27 %
Load Factor (LF) | [18 empty] | : | 88.49 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 86.73 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1166 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 432.05 | 424.41 |  |  |  | 429.20 |  | 62.64 | [8 empty] | 72.04 |  |  | 413.35 | [6 empty] | 416.83 |  | 415.55 |  |  |  | 408.49 |  |  | 428.43 |  |  | 418.27 | [9 empty] | 431.84 |  |  | 4353.10
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 16.67 | [8 empty] | 24.02 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.73
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 16.67 | [8 empty] | 24.02 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.73
LF [%] |  |  |  |  | 103.70 | 108.89 |  |  |  | 103.01 |  | 15.54 | [8 empty] | 17.29 |  |  | 102.52 | [6 empty] | 100.05 |  | 99.74 |  |  |  | 101.31 |  |  | 102.83 |  |  | 103.74 | [9 empty] | 103.65 |  |  | 88.49
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 16.67 | [8 empty] | 24.06 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.73
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 83.33 | [8 empty] | 75.98 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.27
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 190020.09 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.6 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.23 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.24 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.2 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.3 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1970 |  |  |  | 2313.00 |  |  | 6079 |  |  |  | 448 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 80.72 |  |  | 87.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1971 |  |  |  | 2871.80 |  |  | 6592 |  |  |  | 493 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 66.50 |  |  | 75.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1972 |  |  |  | 2572.10 |  |  | 6029 |  |  |  | 504 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 58.10 |  |  | 68.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 3398.80 |  |  | 8325 |  |  |  | 490 | [10 empty] | 95.04 |  |  |  | 95.04 | [5 empty] | 79.18 |  |  | 95.03 |  |  |  | 4.96 |  | 4.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
1974 |  |  |  | 2097.20 |  |  | 5465 |  |  |  | 490 | [10 empty] | 48.86 |  |  |  | 48.86 | [5 empty] | 48.86 |  |  | 62.39 |  |  |  | 23.21 |  | 14.77 | [8 empty] | 36.37 |  |  |  |  | 0.00
1975 |  |  |  | 3041.10 |  |  | 6709 |  |  |  | 470 | [10 empty] | 73.39 |  |  |  | 73.39 | [5 empty] | 73.86 |  |  | 76.59 |  |  |  | 6.78 |  | 5.34 | [8 empty] | 21.27 |  |  |  |  | 0.00
1976 |  |  |  | 2060.80 |  |  | 5113 |  |  |  | 470 | [10 empty] | 49.73 |  |  |  | 49.73 | [5 empty] | 49.92 |  |  | 58.21 |  |  |  | 37.28 |  | 29.55 | [8 empty] | 20.72 |  |  |  |  | 0.00
1977 |  |  |  | 3028.50 |  |  | 7489 |  |  |  | 470 | [10 empty] | 73.59 |  |  |  | 73.59 | [5 empty] | 73.56 |  |  | 85.49 |  |  |  | 10.47 |  | 8.61 | [8 empty] | 17.80 |  |  |  |  | 0.00
1978 |  |  |  | 3218.70 |  |  | 7058 |  |  |  | 470 | [10 empty] | 77.49 |  |  |  | 77.49 | [5 empty] | 78.18 |  |  | 80.57 |  |  |  | 5.96 |  | 4.91 | [8 empty] | 17.59 |  |  |  |  | 0.00
1979 |  |  |  | 2960.50 |  |  | 6375 |  |  |  | 470 | [10 empty] | 71.26 |  |  |  | 71.26 | [5 empty] | 71.91 |  |  | 72.77 |  |  |  | 6.50 |  | 4.96 | [8 empty] | 23.78 |  |  |  |  | 0.00
1980 |  |  |  | 3093.50 |  |  | 6673 |  |  |  | 470 | [10 empty] | 76.00 |  |  |  | 76.00 | [5 empty] | 74.93 |  |  | 75.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.00 |  |  |  |  | 0.00
1981 |  |  |  | 3322.50 |  |  | 7194 |  |  |  | 470 | [10 empty] | 82.15 |  |  |  | 82.15 | [5 empty] | 80.70 |  |  | 82.12 |  |  |  | 0.42 |  | 0.35 | [8 empty] | 17.50 |  |  |  |  | 0.00
1982 |  |  |  | 2408.00 |  |  | 5150 |  |  |  | 470 | [10 empty] | 58.91 |  |  |  | 58.91 | [5 empty] | 58.49 |  |  | 58.79 |  |  |  | 3.35 |  | 2.04 | [8 empty] | 39.05 |  |  |  |  | 0.00
1983 |  |  |  | 3040.10 |  |  | 6529 |  |  |  | 470 | [10 empty] | 74.88 |  |  |  | 74.88 | [5 empty] | 73.84 |  |  | 74.53 |  |  |  | 0.30 |  | 0.23 | [8 empty] | 24.90 |  |  |  |  | 0.00
1984 |  |  |  | 3156.78 |  |  | 6779 |  |  |  | 470 | [10 empty] | 77.19 |  |  |  | 77.19 | [5 empty] | 76.46 |  |  | 77.17 |  |  |  | 4.19 |  | 3.38 | [8 empty] | 19.43 |  |  |  |  | 0.00
1985 |  |  |  | 3620.30 |  |  | 7700 |  |  |  | 470 | [10 empty] | 87.93 |  |  |  | 87.93 | [5 empty] | 87.93 |  |  | 87.90 |  |  |  | 1.85 |  | 1.66 | [8 empty] | 10.41 |  |  |  |  | 0.00
1986 |  |  |  | 3610.27 |  |  | 7659 |  |  |  | 470 | [10 empty] | 87.45 |  |  |  | 87.45 | [5 empty] | 87.69 |  |  | 87.43 |  |  |  | 1.04 |  | 0.92 | [8 empty] | 11.63 |  |  |  |  | 0.00
1987 |  |  |  | 3797.70 |  |  | 7994 |  |  |  | 470 | [10 empty] | 91.26 |  |  |  | 91.26 | [5 empty] | 92.24 |  |  | 91.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.74 |  |  |  |  | 0.00
1988 |  |  |  | 3533.17 |  |  | 7592 |  |  |  | 470 | [10 empty] | 86.45 |  |  |  | 86.45 | [5 empty] | 85.58 |  |  | 86.43 |  |  |  | 4.26 |  | 3.84 | [8 empty] | 9.71 |  |  |  |  | 0.00
1989 |  |  |  | 3073.45 |  |  | 6569 |  |  |  | 470 | [10 empty] | 75.03 |  |  |  | 75.03 | [5 empty] | 74.65 |  |  | 74.99 |  |  |  | 5.89 |  | 4.70 | [8 empty] | 20.27 |  |  |  |  | 0.00
1990 |  |  |  | 3451.38 |  |  | 7325 |  |  |  | 470 | [10 empty] | 83.63 |  |  |  | 83.63 | [5 empty] | 83.83 |  |  | 83.62 |  |  |  | 4.59 |  | 4.02 | [8 empty] | 12.35 |  |  |  |  | 0.00
1991 |  |  |  | 3483.25 |  |  | 7536 |  |  |  | 470 | [10 empty] | 86.04 |  |  |  | 86.04 | [5 empty] | 84.60 |  |  | 86.03 |  |  |  | 0.40 |  | 0.34 | [8 empty] | 13.62 |  |  |  |  | 0.00
1992 |  |  |  | 3483.38 |  |  | 7536 |  |  |  | 470 | [10 empty] | 85.80 |  |  |  | 85.80 | [5 empty] | 84.37 |  |  | 85.79 |  |  |  | 2.04 |  | 1.79 | [8 empty] | 12.41 |  |  |  |  | 0.00
1993 |  |  |  | 3499.44 |  |  | 7509 |  |  |  | 470 | [10 empty] | 85.72 |  |  |  | 85.72 | [5 empty] | 85.00 |  |  | 85.72 |  |  |  | 2.11 |  | 1.85 | [8 empty] | 12.43 |  |  |  |  | 0.00
1994 |  |  |  | 3373.71 |  |  | 7219 |  |  |  | 470 | [10 empty] | 82.44 |  |  |  | 82.44 | [5 empty] | 81.94 |  |  | 82.41 |  |  |  | 5.66 |  | 4.94 | [8 empty] | 12.61 |  |  |  |  | 0.00
1995 |  |  |  | 3638.58 |  |  | 7776 |  |  |  | 470 | [10 empty] | 88.79 |  |  |  | 88.79 | [5 empty] | 88.38 |  |  | 88.77 |  |  |  | 0.58 |  | 0.51 | [8 empty] | 10.70 |  |  |  |  | 0.00
1996 |  |  |  | 2898.05 |  |  | 6175 |  |  |  | 470 | [10 empty] | 70.39 |  |  |  | 70.39 | [5 empty] | 70.20 |  |  | 70.30 |  |  |  | 12.58 |  | 10.13 | [8 empty] | 19.48 |  |  |  |  | 0.00
1997 |  |  |  | 3894.65 |  |  | 8011 |  |  |  | 480 | [10 empty] | 91.65 |  |  |  | 91.65 | [5 empty] | 92.62 |  |  | 91.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.35 |  |  |  |  | 0.00
1998 |  |  |  | 4308.56 |  |  | 8760 |  |  |  | 480 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.47 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 3534.05 |  |  | 7444 |  |  |  | 480 | [10 empty] | 85.31 |  |  |  | 85.31 | [5 empty] | 84.05 |  |  | 84.98 |  |  |  | 0.74 |  | 0.63 | [8 empty] | 14.06 |  |  |  |  | 0.00
2000 |  |  |  | 3814.15 |  |  | 8001 |  |  |  | 480 | [10 empty] | 91.02 |  |  |  | 91.02 | [5 empty] | 90.46 |  |  | 91.09 |  |  |  | 0.28 |  | 0.26 | [8 empty] | 8.73 |  |  |  |  | 0.00
2001 |  |  |  | 4286.28 |  |  | 8760 |  |  |  | 480 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.94 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 3843.35 |  |  | 7951 |  |  |  | 480 | [10 empty] | 90.44 |  |  |  | 90.44 | [5 empty] | 91.40 |  |  | 90.76 |  |  |  | 0.45 |  | 0.41 | [8 empty] | 9.14 |  |  |  |  | 0.00
2003 |  |  |  | 3868.59 |  |  | 7925 |  |  |  | 480 | [10 empty] | 90.13 |  |  |  | 90.13 | [5 empty] | 92.00 |  |  | 90.47 |  |  |  | 1.16 |  | 1.06 | [8 empty] | 8.81 |  |  |  |  | 0.00
2004 |  |  |  | 4308.49 |  |  | 8733 |  |  |  | 480 | [10 empty] | 99.40 |  |  |  | 99.40 | [5 empty] | 102.19 |  |  | 99.42 |  |  |  | 0.60 |  | 0.60 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 3996.68 |  |  | 8166 |  |  |  | 498 | [10 empty] | 93.26 |  |  |  | 93.26 | [5 empty] | 91.60 |  |  | 93.21 |  |  |  | 0.98 |  | 0.92 | [8 empty] | 5.82 |  |  |  |  | 0.00
2006 |  |  |  | 4119.17 |  |  | 8157 |  |  |  | 560 | [10 empty] | 92.21 |  |  |  | 92.21 | [5 empty] | 95.31 |  |  | 93.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.79 |  |  |  |  | 0.00
2007 |  |  |  | 4930.53 |  |  | 8675 |  |  |  | 560 | [10 empty] | 99.15 |  |  |  | 99.15 | [5 empty] | 100.51 |  |  | 99.03 |  |  |  | 0.85 |  | 0.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 4744.00 |  |  | 8280 |  |  |  | 560 | [10 empty] | 94.92 |  |  |  | 94.92 | [5 empty] | 96.44 |  |  | 94.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.08 |  |  |  |  | 0.00
2009 |  |  |  | 4630.90 |  |  | 8235 |  |  |  | 580 | [10 empty] | 94.87 |  |  |  | 94.87 | [5 empty] | 91.15 |  |  | 94.01 |  |  |  | 0.45 |  | 0.43 | [8 empty] | 4.70 |  |  |  |  | 0.00
2010 |  |  |  | 4948.36 |  |  | 8654 |  |  |  | 580 | [10 empty] | 98.79 |  |  |  | 98.79 | [5 empty] | 97.39 |  |  | 98.79 |  |  |  | 1.21 |  | 1.21 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 4311.21 |  |  | 7539 |  |  |  | 580 | [10 empty] | 86.08 |  |  |  | 86.08 | [5 empty] | 84.85 |  |  | 86.06 |  |  |  | 1.25 |  | 1.09 | [8 empty] | 12.83 |  |  |  |  | 0.00
2012 |  |  |  | 4601.72 |  |  | 8055 |  |  |  | 580 | [10 empty] | 91.71 |  |  |  | 91.71 | [5 empty] | 90.32 |  |  | 91.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.29 |  |  |  |  | 0.00
2013 |  |  |  | 4993.29 |  |  | 8668 |  |  |  | 581 | [10 empty] | 98.95 |  |  |  | 98.95 | [5 empty] | 98.10 |  |  | 98.94 |  |  |  | 1.05 |  | 1.05 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 4662.50 |  |  | 8142 |  |  |  | 580 | [10 empty] | 92.94 |  |  |  | 92.94 | [5 empty] | 91.77 |  |  | 92.95 |  |  |  | 0.62 |  | 0.58 | [8 empty] | 6.48 |  |  |  |  | 0.00
2015 |  |  |  | 4769.42 |  |  | 8313 |  |  |  | 580 | [10 empty] | 94.89 |  |  |  | 94.89 | [5 empty] | 93.87 |  |  | 94.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.11 |  |  |  |  | 0.00
2016 |  |  |  | 5042.06 |  |  | 8784 |  |  |  | 580 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.97 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 4697.68 |  |  | 8261 |  |  |  | 580 | [10 empty] | 94.31 |  |  |  | 94.31 | [5 empty] | 92.46 |  |  | 94.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.69 |  |  |  |  | 0.00
2018 |  |  |  | 4698.44 |  |  | 8283 |  |  |  | 560 | [10 empty] | 94.55 |  |  |  | 95.08 | [5 empty] | 95.78 |  |  | 94.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.92 |  |  |  |  | 0.53
2019 |  |  |  | 4993.69 |  |  | 8713 |  |  |  | 560 | [10 empty] | 99.47 |  |  |  | 99.47 | [5 empty] | 101.80 |  |  | 99.46 |  |  |  | 0.53 |  | 0.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 4353.10 |  |  | 7618 |  |  |  | 560 | [10 empty] | 86.73 |  |  |  | 86.73 | [5 empty] | 88.49 |  |  | 86.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.27 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1970 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 163
B. |  | Refuelling without maintenance | [20 empty] | 1165 | [14 empty] | 32
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 917
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 56
E. |  | Testing of plant systems or components | [35 empty] | 15 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 4
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
Z. |  | Other | [39 empty] | 7
Subtotal | [22 empty] | 1165 | [14 empty] | 1020 |  |  |  | 174 | [11 empty] | 2
Total | [22 empty] | 1165 | [14 empty] | 1196
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1970 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 34
31. |  |  | Turbine and auxiliaries | [34 empty] | 35
32. |  |  | Feedwater and Main Steam System | [34 empty] | 27
33. |  |  | Circulating Water System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 15
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 14
Total | [37 empty] | 171
Highlights (2020)
Refueling Outage 41.

## GRAND GULF-1
2020 Operating Experience
US-416 | [8 empty] | GRAND GULF-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Owner | [7 empty] | : | SERI (Systems Energy Resources, Inc)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-6 (Mark 3) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-05-04
Thermal power | [12 empty] | : |  |  | 4408 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-10-20
Gross electrical power | [12 empty] | : |  |  | 1500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-07-01
Reference unit power (net) | [12 empty] | : |  |  | 1401 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.31
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 288
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.105
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.925
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 800 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 193 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6470.93 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 20.62 %
Energy Availability Factor (EAF) | [18 empty] | : | 59.21 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 16.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 59.21 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 24.77 %
Load Factor (LF) | [18 empty] | : | 52.58 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 59.22 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3582 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1036.23 | 746.82 |  |  |  | -4.51 |  | -7.06 | [8 empty] | 0.41 |  |  | 772.96 | [6 empty] | 935.85 |  | 297.81 |  |  |  | 880.38 |  |  | 868.89 |  |  | 145.99 | [9 empty] | 797.18 |  |  | 6470.93
EAF [%] |  |  |  |  | 100.00 | 75.43 |  |  |  | 0.13 |  | 0.00 | [8 empty] | 5.22 |  |  | 94.25 | [6 empty] | 100.00 |  | 35.30 |  |  |  | 100.00 |  |  | 100.00 |  |  | 17.03 | [9 empty] | 83.40 |  |  | 59.21
UCF [%] |  |  |  |  | 100.00 | 75.43 |  |  |  | 0.13 |  | 0.00 | [8 empty] | 5.22 |  |  | 94.25 | [6 empty] | 100.00 |  | 35.30 |  |  |  | 100.00 |  |  | 100.00 |  |  | 17.03 | [9 empty] | 83.40 |  |  | 59.21
LF [%] |  |  |  |  | 99.41 | 76.59 |  |  |  | -0.43 |  | -0.70 | [8 empty] | 0.04 |  |  | 76.63 | [6 empty] | 89.78 |  | 28.57 |  |  |  | 87.28 |  |  | 83.36 |  |  | 14.47 | [9 empty] | 76.48 |  |  | 52.58
OF [%] |  |  |  |  | 100.00 | 75.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.24 |  |  | 94.31 | [6 empty] | 100.00 |  | 35.35 |  |  |  | 100.00 |  |  | 100.00 |  |  | 17.22 | [9 empty] | 83.33 |  |  | 59.22
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 80.79 |  |  | 5.75 | [6 empty] | 0.00 |  | 64.70 |  |  |  | 0.00 |  |  | 0.00 |  |  | 82.97 | [9 empty] | 9.80 |  |  | 20.62
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.97 |  |  | 5.75 | [6 empty] | 0.00 |  | 64.70 |  |  |  | 0.00 |  |  | 0.00 |  |  | 82.97 | [9 empty] | 16.60 |  |  | 16.02
PUF [%] |  |  |  |  | 0.00 | 24.57 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 72.81 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 24.77
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 356257.08 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.43 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.02 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.81 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.2 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.99 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.76 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.17 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.6 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4316.40 |  |  | 5042 |  |  |  | 1108 | [10 empty] | 58.70 |  |  |  | 58.70 | [5 empty] | 54.23 |  |  | 60.92 |  |  |  | 11.21 |  | 7.41 | [8 empty] | 33.89 |  |  |  |  | 0.00
1986 |  |  |  | 4098.05 |  |  | 5326 |  |  |  | 1108 | [10 empty] | 60.54 |  |  |  | 60.54 | [5 empty] | 42.22 |  |  | 60.80 |  |  |  | 11.22 |  | 7.65 | [8 empty] | 31.82 |  |  |  |  | 0.00
1987 |  |  |  | 7726.99 |  |  | 7098 |  |  |  | 1130 | [10 empty] | 80.87 |  |  |  | 80.87 | [5 empty] | 78.00 |  |  | 81.03 |  |  |  | 2.18 |  | 1.80 | [8 empty] | 17.33 |  |  |  |  | 0.00
1988 |  |  |  | 9590.95 |  |  | 8250 |  |  |  | 1142 | [10 empty] | 93.80 |  |  |  | 93.80 | [5 empty] | 95.61 |  |  | 93.92 |  |  |  | 4.83 |  | 4.76 | [8 empty] | 1.44 |  |  |  |  | 0.00
1989 |  |  |  | 7846.28 |  |  | 6815 |  |  |  | 1142 | [10 empty] | 76.93 |  |  |  | 76.93 | [5 empty] | 78.43 |  |  | 77.80 |  |  |  | 4.99 |  | 4.04 | [8 empty] | 19.02 |  |  |  |  | 0.00
1990 |  |  |  | 7404.01 |  |  | 6765 |  |  |  | 1142 | [10 empty] | 76.61 |  |  |  | 76.61 | [5 empty] | 74.01 |  |  | 77.23 |  |  |  | 9.35 |  | 7.90 | [8 empty] | 15.49 |  |  |  |  | 0.00
1991 |  |  |  | 9118.72 |  |  | 8035 |  |  |  | 1142 | [10 empty] | 88.36 |  |  |  | 89.62 | [5 empty] | 91.08 |  |  | 91.72 |  |  |  | 10.38 |  | 10.38 | [8 empty] | 0.00 |  |  |  |  | 1.27
1992 |  |  |  | 8171.15 |  |  | 7163 |  |  |  | 1143 | [10 empty] | 81.06 |  |  |  | 81.06 | [5 empty] | 81.39 |  |  | 81.55 |  |  |  | 4.89 |  | 4.17 | [8 empty] | 14.77 |  |  |  |  | 0.00
1993 |  |  |  | 7898.46 |  |  | 6845 |  |  |  | 1143 | [10 empty] | 77.61 |  |  |  | 77.61 | [5 empty] | 78.88 |  |  | 78.14 |  |  |  | 9.06 |  | 7.74 | [8 empty] | 14.65 |  |  |  |  | 0.00
1994 |  |  |  | 9614.75 |  |  | 8284 |  |  |  | 1143 | [10 empty] | 94.49 |  |  |  | 94.49 | [5 empty] | 96.03 |  |  | 94.57 |  |  |  | 5.51 |  | 5.51 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 7809.73 |  |  | 6829 |  |  |  | 1153 | [10 empty] | 77.67 |  |  |  | 77.67 | [5 empty] | 77.32 |  |  | 77.96 |  |  |  | 7.47 |  | 6.27 | [8 empty] | 16.06 |  |  |  |  | 0.00
1996 |  |  |  | 9224.70 |  |  | 7696 |  |  |  | 1175 | [10 empty] | 87.70 |  |  |  | 87.70 | [5 empty] | 89.34 |  |  | 87.61 |  |  |  | 3.90 |  | 3.56 | [8 empty] | 8.75 |  |  |  |  | 0.00
1997 |  |  |  | 10817.56 |  |  | 8760 |  |  |  | 1200 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.91 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 9190.81 |  |  | 7641 |  |  |  | 1200 | [10 empty] | 87.54 |  |  |  | 87.54 | [5 empty] | 87.41 |  |  | 87.23 |  |  |  | 1.70 |  | 1.51 | [8 empty] | 10.95 |  |  |  |  | 0.00
1999 |  |  |  | 8428.40 |  |  | 6944 |  |  |  | 1204 | [10 empty] | 79.30 |  |  |  | 79.30 | [5 empty] | 79.91 |  |  | 79.27 |  |  |  | 8.47 |  | 7.34 | [8 empty] | 13.36 |  |  |  |  | 0.00
2000 |  |  |  | 10694.61 |  |  | 8634 |  |  |  | 1208 | [10 empty] | 98.31 |  |  |  | 99.22 | [5 empty] | 100.74 |  |  | 98.29 |  |  |  | 0.78 |  | 0.78 | [8 empty] | 0.00 |  |  |  |  | 0.91
2001 |  |  |  | 9923.98 |  |  | 8040 |  |  |  | 1210 | [10 empty] | 91.80 |  |  |  | 92.28 | [5 empty] | 93.63 |  |  | 91.78 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 7.58 |  |  |  |  | 0.47
2002 |  |  |  | 10059.47 |  |  | 8139 |  |  |  | 1207 | [10 empty] | 92.91 |  |  |  | 93.75 | [5 empty] | 95.14 |  |  | 92.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.25 |  |  |  |  | 0.84
2003 |  |  |  | 10902.49 |  |  | 8574 |  |  |  | 1207 | [10 empty] | 97.88 |  |  |  | 97.88 | [5 empty] | 103.11 |  |  | 97.88 |  |  |  | 2.12 |  | 2.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 10235.07 |  |  | 8047 |  |  |  | 1207 | [10 empty] | 91.22 |  |  |  | 91.22 | [5 empty] | 96.54 |  |  | 91.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.78 |  |  |  |  | 0.00
2005 |  |  |  | 10077.85 |  |  | 7974 |  |  |  | 1263 | [10 empty] | 91.05 |  |  |  | 91.66 | [5 empty] | 91.09 |  |  | 91.03 |  |  |  | 0.16 |  | 0.15 | [8 empty] | 8.20 |  |  |  |  | 0.61
2006 |  |  |  | 10807.33 |  |  | 8570 |  |  |  | 1266 | [10 empty] | 97.83 |  |  |  | 97.83 | [5 empty] | 97.45 |  |  | 97.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.17 |  |  |  |  | 0.00
2007 |  |  |  | 9358.78 |  |  | 7643 |  |  |  | 1268 | [10 empty] | 87.29 |  |  |  | 87.29 | [5 empty] | 84.26 |  |  | 87.25 |  |  |  | 2.44 |  | 2.19 | [8 empty] | 10.52 |  |  |  |  | 0.00
2008 |  |  |  | 9417.15 |  |  | 7637 |  |  |  | 1268 | [10 empty] | 86.97 |  |  |  | 86.97 | [5 empty] | 84.55 |  |  | 86.94 |  |  |  | 3.53 |  | 3.18 | [8 empty] | 9.85 |  |  |  |  | 0.00
2009 |  |  |  | 10998.51 |  |  | 8760 |  |  |  | 1259 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.73 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 9643.24 |  |  | 7912 |  |  |  | 1251 | [10 empty] | 90.28 |  |  |  | 90.28 | [5 empty] | 88.00 |  |  | 90.32 |  |  |  | 1.23 |  | 1.13 | [8 empty] | 8.59 |  |  |  |  | 0.00
2011 |  |  |  | 10336.52 |  |  | 8760 |  |  |  | 1251 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 94.32 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 7336.44 |  |  | 5740 |  |  |  | 1401 | [10 empty] | 67.00 |  |  |  | 67.00 | [5 empty] | 63.58 |  |  | 65.35 |  |  |  | 1.16 |  | 0.79 | [8 empty] | 32.21 |  |  |  |  | 0.00
2013 |  |  |  | 10784.30 |  |  | 7891 |  |  |  | 1401 | [10 empty] | 91.04 |  |  |  | 91.04 | [5 empty] | 87.86 |  |  | 90.07 |  |  |  | 8.96 |  | 8.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 10279.50 |  |  | 7744 |  |  |  | 1401 | [10 empty] | 88.25 |  |  |  | 88.25 | [5 empty] | 83.76 |  |  | 88.40 |  |  |  | 2.42 |  | 2.19 | [8 empty] | 9.56 |  |  |  |  | 0.00
2015 |  |  |  | 11718.78 |  |  | 8563 |  |  |  | 1401 | [10 empty] | 97.72 |  |  |  | 97.72 | [5 empty] | 95.49 |  |  | 97.75 |  |  |  | 2.28 |  | 2.28 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 5981.59 |  |  | 4407 |  |  |  | 1401 | [10 empty] | 49.53 |  |  |  | 49.53 | [5 empty] | 48.61 |  |  | 50.17 |  |  |  | 44.68 |  | 39.99 | [8 empty] | 10.48 |  |  |  |  | 0.00
2017 |  |  |  | 7437.97 |  |  | 6208 |  |  |  | 1401 | [10 empty] | 62.76 |  |  |  | 62.76 | [5 empty] | 60.61 |  |  | 70.87 |  |  |  | 34.80 |  | 33.49 | [8 empty] | 3.75 |  |  |  |  | 0.00
2018 |  |  |  | 6957.96 |  |  | 5664 |  |  |  | 1401 | [10 empty] | 64.31 |  |  |  | 64.31 | [5 empty] | 56.69 |  |  | 64.66 |  |  |  | 9.88 |  | 7.05 | [8 empty] | 28.65 |  |  |  |  | 0.00
2019 |  |  |  | 11032.60 |  |  | 8068 |  |  |  | 1401 | [10 empty] | 92.12 |  |  |  | 94.06 | [5 empty] | 89.89 |  |  | 92.10 |  |  |  | 1.11 |  | 1.06 | [8 empty] | 4.89 |  |  |  |  | 1.94
2020 |  |  |  | 6470.93 |  |  | 5202 |  |  |  | 1401 | [10 empty] | 59.21 |  |  |  | 59.21 | [5 empty] | 52.58 |  |  | 59.22 |  |  |  | 20.62 |  | 16.02 | [8 empty] | 24.77 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 392
B. |  | Refuelling without maintenance | [20 empty] | 2176 | [14 empty] | 61
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 711 |  |  |  | 13
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 101
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 24
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 18
Z. |  | Other | [24 empty] | 1351 | [6 empty] | 56 | [7 empty] | 58 | [11 empty] | 4
Subtotal | [22 empty] | 2176 |  |  |  | 1351 | [6 empty] | 56 |  |  |  | 873 |  |  |  | 488 | [11 empty] | 24
Total | [22 empty] | 3583 | [14 empty] | 1385
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 22
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 93
14. |  |  | Safety Systems | [34 empty] | 47
15. |  |  | Reactor Cooling Systems | [34 empty] | 31
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 69
32. |  |  | Feedwater and Main Steam System | [34 empty] | 50
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 31
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 30
42. |  |  | Electrical Power Supply Systems | [34 empty] | 42
Total | [37 empty] | 432
Highlights (2020)
Automatic scram due to low flow on the generator primary water bushing.

## HARRIS-1
2020 Operating Experience
US-400 | [8 empty] | HARRIS-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PROGRESS (Progress Energy)
Owner | [7 empty] | : | PROG_E_C (PROGRESS ENERGY Carolinas, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-01-28
Thermal power | [12 empty] | : |  |  | 2900 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-01-19
Gross electrical power | [12 empty] | : |  |  | 980 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-05-02
Reference unit power (net) | [12 empty] | : |  |  | 964 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.32
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 31500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.03 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.56
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 52 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8275.59 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.98 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.02 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.98 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.02 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 97.73 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 97.01 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 263 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 743.48 | 694.49 |  |  |  | 677.01 |  | 716.21 | [8 empty] | 735.53 |  |  | 621.29 | [6 empty] | 716.87 |  | 649.87 |  |  |  | 702.75 |  |  | 732.02 |  |  | 715.18 | [9 empty] | 570.90 |  |  | 8275.59
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.08 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 92.03 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 79.72 |  |  | 97.02
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.08 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 92.03 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 79.72 |  |  | 97.02
LF [%] |  |  |  |  | 103.66 | 103.51 |  |  |  | 94.39 |  | 103.19 | [8 empty] | 102.55 |  |  | 89.51 | [6 empty] | 99.95 |  | 90.61 |  |  |  | 101.25 |  |  | 102.06 |  |  | 103.04 | [9 empty] | 79.60 |  |  | 97.73
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 92.88 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 92.07 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 79.70 |  |  | 97.01
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 6.92 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 7.97 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 20.28 |  |  | 2.98
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 6.92 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 7.97 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 20.28 |  |  | 2.98
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 208718.94 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.89 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.42 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.73 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.45 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.82 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.3 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.27 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | Data not provided
1988 |  |  |  | 5345.56 |  |  | 6458 |  |  |  | 860 | [10 empty] | 73.56 |  |  |  | 73.56 | [5 empty] | 70.76 |  |  | 73.52 |  |  |  | 4.05 |  | 3.10 | [8 empty] | 23.34 |  |  |  |  | 0.00
1989 |  |  |  | 5638.85 |  |  | 6873 |  |  |  | 860 | [10 empty] | 78.49 |  |  |  | 78.49 | [5 empty] | 74.85 |  |  | 78.46 |  |  |  | 1.86 |  | 1.49 | [8 empty] | 20.02 |  |  |  |  | 0.00
1990 |  |  |  | 6339.00 |  |  | 7812 |  |  |  | 860 | [10 empty] | 89.19 |  |  |  | 89.19 | [5 empty] | 84.14 |  |  | 89.18 |  |  |  | 4.03 |  | 3.74 | [8 empty] | 7.07 |  |  |  |  | 0.00
1991 |  |  |  | 5927.44 |  |  | 7080 |  |  |  | 860 | [10 empty] | 80.83 |  |  |  | 80.83 | [5 empty] | 78.68 |  |  | 80.82 |  |  |  | 0.80 |  | 0.65 | [8 empty] | 18.52 |  |  |  |  | 0.00
1992 |  |  |  | 5427.88 |  |  | 6501 |  |  |  | 860 | [10 empty] | 74.01 |  |  |  | 74.01 | [5 empty] | 71.85 |  |  | 74.01 |  |  |  | 5.07 |  | 3.95 | [8 empty] | 22.04 |  |  |  |  | 0.00
1993 |  |  |  | 7527.73 |  |  | 8721 |  |  |  | 860 | [10 empty] | 99.55 |  |  |  | 99.55 | [5 empty] | 99.92 |  |  | 99.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.45 |  |  |  |  | 0.00
1994 |  |  |  | 6065.06 |  |  | 7195 |  |  |  | 860 | [10 empty] | 82.17 |  |  |  | 82.17 | [5 empty] | 80.51 |  |  | 82.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.83 |  |  |  |  | 0.00
1995 |  |  |  | 5966.34 |  |  | 7279 |  |  |  | 860 | [10 empty] | 83.13 |  |  |  | 83.13 | [5 empty] | 79.20 |  |  | 83.09 |  |  |  | 4.92 |  | 4.30 | [8 empty] | 12.57 |  |  |  |  | 0.00
1996 |  |  |  | 7067.74 |  |  | 8301 |  |  |  | 860 | [10 empty] | 94.56 |  |  |  | 95.33 | [5 empty] | 93.56 |  |  | 94.50 |  |  |  | 2.50 |  | 2.45 | [8 empty] | 2.22 |  |  |  |  | 0.77
1997 |  |  |  | 5909.03 |  |  | 6934 |  |  |  | 860 | [10 empty] | 79.20 |  |  |  | 79.20 | [5 empty] | 78.44 |  |  | 79.16 |  |  |  | 4.09 |  | 3.38 | [8 empty] | 17.42 |  |  |  |  | 0.00
1998 |  |  |  | 6711.57 |  |  | 7891 |  |  |  | 860 | [10 empty] | 90.10 |  |  |  | 90.10 | [5 empty] | 89.09 |  |  | 90.08 |  |  |  | 7.87 |  | 7.69 | [8 empty] | 2.20 |  |  |  |  | 0.00
1999 |  |  |  | 7244.15 |  |  | 8484 |  |  |  | 860 | [10 empty] | 96.87 |  |  |  | 96.87 | [5 empty] | 96.16 |  |  | 96.85 |  |  |  | 3.13 |  | 3.13 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 6877.96 |  |  | 8098 |  |  |  | 860 | [10 empty] | 92.21 |  |  |  | 92.21 | [5 empty] | 91.05 |  |  | 92.19 |  |  |  | 0.35 |  | 0.32 | [8 empty] | 7.47 |  |  |  |  | 0.00
2001 |  |  |  | 5401.46 |  |  | 6335 |  |  |  | 860 | [10 empty] | 72.32 |  |  |  | 72.32 | [5 empty] | 71.70 |  |  | 72.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.68 |  |  |  |  | 0.00
2002 |  |  |  | 7835.04 |  |  | 8643 |  |  |  | 900 | [10 empty] | 98.67 |  |  |  | 98.97 | [5 empty] | 99.38 |  |  | 98.66 |  |  |  | 0.39 |  | 0.39 | [8 empty] | 0.65 |  |  |  |  | 0.29
2003 |  |  |  | 7236.92 |  |  | 8082 |  |  |  | 900 | [10 empty] | 92.27 |  |  |  | 92.27 | [5 empty] | 91.79 |  |  | 92.26 |  |  |  | 1.64 |  | 1.53 | [8 empty] | 6.20 |  |  |  |  | 0.00
2004 |  |  |  | 7008.43 |  |  | 7687 |  |  |  | 900 | [10 empty] | 87.54 |  |  |  | 87.54 | [5 empty] | 88.65 |  |  | 87.51 |  |  |  | 3.92 |  | 3.57 | [8 empty] | 8.89 |  |  |  |  | 0.00
2005 |  |  |  | 7930.83 |  |  | 8710 |  |  |  | 900 | [10 empty] | 99.43 |  |  |  | 99.43 | [5 empty] | 100.58 |  |  | 99.42 |  |  |  | 0.57 |  | 0.57 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 7029.27 |  |  | 7749 |  |  |  | 900 | [10 empty] | 88.48 |  |  |  | 88.48 | [5 empty] | 89.16 |  |  | 88.46 |  |  |  | 1.13 |  | 1.01 | [8 empty] | 10.51 |  |  |  |  | 0.00
2007 |  |  |  | 7403.05 |  |  | 8176 |  |  |  | 900 | [10 empty] | 93.35 |  |  |  | 93.35 | [5 empty] | 93.90 |  |  | 93.33 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 6.63 |  |  |  |  | 0.00
2008 |  |  |  | 7821.41 |  |  | 8534 |  |  |  | 900 | [10 empty] | 97.16 |  |  |  | 97.16 | [5 empty] | 98.94 |  |  | 97.15 |  |  |  | 2.84 |  | 2.84 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 7403.16 |  |  | 8091 |  |  |  | 900 | [10 empty] | 92.38 |  |  |  | 92.38 | [5 empty] | 93.90 |  |  | 92.36 |  |  |  | 1.43 |  | 1.34 | [8 empty] | 6.28 |  |  |  |  | 0.00
2010 |  |  |  | 7080.62 |  |  | 7746 |  |  |  | 900 | [10 empty] | 88.44 |  |  |  | 88.44 | [5 empty] | 89.81 |  |  | 88.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.56 |  |  |  |  | 0.00
2011 |  |  |  | 8111.77 |  |  | 8760 |  |  |  | 900 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.89 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 7121.94 |  |  | 7612 |  |  |  | 928 | [10 empty] | 86.87 |  |  |  | 86.87 | [5 empty] | 88.70 |  |  | 86.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.13 |  |  |  |  | 0.00
2013 |  |  |  | 6888.36 |  |  | 7392 |  |  |  | 928 | [10 empty] | 84.38 |  |  |  | 84.38 | [5 empty] | 84.73 |  |  | 84.37 |  |  |  | 6.89 |  | 6.24 | [8 empty] | 9.38 |  |  |  |  | 0.00
2014 |  |  |  | 8048.57 |  |  | 8522 |  |  |  | 928 | [10 empty] | 97.28 |  |  |  | 97.28 | [5 empty] | 99.01 |  |  | 97.28 |  |  |  | 1.09 |  | 1.08 | [8 empty] | 1.64 |  |  |  |  | 0.00
2015 |  |  |  | 7272.18 |  |  | 7712 |  |  |  | 928 | [10 empty] | 88.04 |  |  |  | 88.04 | [5 empty] | 89.46 |  |  | 88.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.96 |  |  |  |  | 0.00
2016 |  |  |  | 7513.05 |  |  | 7961 |  |  |  | 928 | [10 empty] | 90.63 |  |  |  | 90.63 | [5 empty] | 92.17 |  |  | 90.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.37 |  |  |  |  | 0.00
2017 |  |  |  | 8208.57 |  |  | 8708 |  |  |  | 928 | [10 empty] | 99.40 |  |  |  | 99.40 | [5 empty] | 100.98 |  |  | 99.41 |  |  |  | 0.60 |  | 0.60 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 7587.91 |  |  | 7843 |  |  |  | 964 | [10 empty] | 89.89 |  |  |  | 89.89 | [5 empty] | 89.85 |  |  | 89.53 |  |  |  | 1.27 |  | 1.16 | [8 empty] | 8.96 |  |  |  |  | 0.00
2019 |  |  |  | 7610.59 |  |  | 7857 |  |  |  | 964 | [10 empty] | 89.70 |  |  |  | 89.70 | [5 empty] | 90.12 |  |  | 89.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.30 |  |  |  |  | 0.00
2020 |  |  |  | 8275.59 |  |  | 8521 |  |  |  | 964 | [10 empty] | 97.02 |  |  |  | 97.02 | [5 empty] | 97.73 |  |  | 97.01 |  |  |  | 2.98 |  | 2.98 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 133
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 733
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 49
E. |  | Testing of plant systems or components | [35 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Z. |  | Other | [24 empty] | 262 | [14 empty] | 10
Subtotal | [26 empty] | 262 | [10 empty] | 783 |  |  |  | 144 | [11 empty] | 3
Total | [22 empty] | 262 | [14 empty] | 930
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 50
32. |  |  | Feedwater and Main Steam System | [34 empty] | 33
34. |  |  | Miscellaneous Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 10
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 135
Highlights (2020)
Automatic scram due to a fault on the non-segregated bus from the 1B aux transformer to the 1B aux bus.

## HATCH-1
2020 Operating Experience
US-321 | [8 empty] | HATCH-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SOUTHERN (Southern Nuclear Operating Company, Inc.)
Owner | [7 empty] | : | GPCO (GEORGIA POWER CO.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-09-30
Thermal power | [12 empty] | : |  |  | 2804 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-11-11
Gross electrical power | [12 empty] | : |  |  | 911 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-12-31
Reference unit power (net) | [12 empty] | : |  |  | 876 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 279
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.435
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 17000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.27 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.68
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 137 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6410.21 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.07 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.6 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.81 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.6 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.59 %
Load Factor (LF) | [18 empty] | : | 83.31 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 85.59 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1266 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 585.59 | -3.59 |  |  |  | 237.13 |  | 625.74 | [8 empty] | 659.05 |  |  | 464.45 | [6 empty] | 652.70 |  | 648.60 |  |  |  | 620.95 |  |  | 643.42 |  |  | 611.65 | [9 empty] | 664.53 |  |  | 6410.21
EAF [%] |  |  |  |  | 100.00 | 0.43 |  |  |  | 44.45 |  | 100.00 | [8 empty] | 100.00 |  |  | 77.96 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.60
UCF [%] |  |  |  |  | 100.00 | 0.43 |  |  |  | 44.45 |  | 100.00 | [8 empty] | 100.00 |  |  | 77.96 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.60
LF [%] |  |  |  |  | 89.85 | -0.59 |  |  |  | 36.38 |  | 99.21 | [8 empty] | 101.12 |  |  | 73.64 | [6 empty] | 100.15 |  | 99.52 |  |  |  | 98.45 |  |  | 98.72 |  |  | 96.98 | [9 empty] | 101.96 |  |  | 83.31
OF [%] |  |  |  |  | 100.00 | 0.43 |  |  |  | 44.35 |  | 100.00 | [8 empty] | 100.00 |  |  | 77.92 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.59
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 22.04 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.07
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 22.04 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.81
PUF [%] |  |  |  |  | 0.00 | 99.57 |  |  |  | 55.55 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.59
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 254052.46 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.02 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.73 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.42 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.75 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.83 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.65 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.85 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 3095.80 |  |  | 6158 |  |  |  | 786 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1976 |  |  |  | 4133.80 |  |  | 7299 |  |  |  | 786 | [10 empty] | 59.96 |  |  |  | 59.96 | [5 empty] | 59.87 |  |  | 83.09 |  |  |  | 29.04 |  | 24.54 | [8 empty] | 15.50 |  |  |  |  | 0.00
1977 |  |  |  | 3716.70 |  |  | 5802 |  |  |  | 700 | [10 empty] | 60.16 |  |  |  | 60.16 | [5 empty] | 60.61 |  |  | 66.23 |  |  |  | 28.13 |  | 23.55 | [8 empty] | 16.29 |  |  |  |  | 0.00
1978 |  |  |  | 4277.20 |  |  | 6370 |  |  |  | 717 | [10 empty] | 68.15 |  |  |  | 68.15 | [5 empty] | 68.10 |  |  | 72.72 |  |  |  | 21.90 |  | 19.11 | [8 empty] | 12.74 |  |  |  |  | 0.00
1979 |  |  |  | 3349.50 |  |  | 4781 |  |  |  | 739 | [10 empty] | 51.70 |  |  |  | 51.70 | [5 empty] | 51.74 |  |  | 54.58 |  |  |  | 16.57 |  | 10.27 | [8 empty] | 38.03 |  |  |  |  | 0.00
1980 |  |  |  | 4790.20 |  |  | 7174 |  |  |  | 764 | [10 empty] | 82.13 |  |  |  | 82.27 | [5 empty] | 71.38 |  |  | 81.67 |  |  |  | 17.73 |  | 17.73 | [8 empty] | 0.00 |  |  |  |  | 0.14
1981 |  |  |  | 2770.70 |  |  | 4384 |  |  |  | 757 | [10 empty] | 50.56 |  |  |  | 50.56 | [5 empty] | 41.78 |  |  | 50.05 |  |  |  | 12.31 |  | 7.10 | [8 empty] | 42.35 |  |  |  |  | 0.00
1982 |  |  |  | 2893.90 |  |  | 4313 |  |  |  | 758 | [10 empty] | 49.39 |  |  |  | 49.39 | [5 empty] | 43.58 |  |  | 49.24 |  |  |  | 25.88 |  | 17.25 | [8 empty] | 33.37 |  |  |  |  | 0.00
1983 |  |  |  | 3968.90 |  |  | 6240 |  |  |  | 764 | [10 empty] | 71.55 |  |  |  | 71.55 | [5 empty] | 59.30 |  |  | 71.23 |  |  |  | 5.34 |  | 4.03 | [8 empty] | 24.42 |  |  |  |  | 0.00
1984 |  |  |  | 3609.18 |  |  | 5473 |  |  |  | 752 | [10 empty] | 62.28 |  |  |  | 62.53 | [5 empty] | 54.64 |  |  | 62.31 |  |  |  | 14.75 |  | 10.82 | [8 empty] | 26.66 |  |  |  |  | 0.25
1985 |  |  |  | 4761.37 |  |  | 6694 |  |  |  | 752 | [10 empty] | 76.47 |  |  |  | 76.47 | [5 empty] | 72.28 |  |  | 76.42 |  |  |  | 12.33 |  | 10.76 | [8 empty] | 12.77 |  |  |  |  | 0.00
1986 |  |  |  | 3645.39 |  |  | 5162 |  |  |  | 768 | [10 empty] | 58.97 |  |  |  | 58.97 | [5 empty] | 54.18 |  |  | 58.93 |  |  |  | 3.47 |  | 2.12 | [8 empty] | 38.91 |  |  |  |  | 0.00
1987 |  |  |  | 5080.69 |  |  | 7043 |  |  |  | 750 | [10 empty] | 80.43 |  |  |  | 80.43 | [5 empty] | 77.33 |  |  | 80.40 |  |  |  | 2.18 |  | 1.80 | [8 empty] | 17.77 |  |  |  |  | 0.00
1988 |  |  |  | 4115.82 |  |  | 5802 |  |  |  | 756 | [10 empty] | 66.04 |  |  |  | 66.04 | [5 empty] | 61.98 |  |  | 66.05 |  |  |  | 15.56 |  | 12.17 | [8 empty] | 21.78 |  |  |  |  | 0.00
1989 |  |  |  | 6479.72 |  |  | 8760 |  |  |  | 757 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.71 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 4103.39 |  |  | 5722 |  |  |  | 753 | [10 empty] | 65.08 |  |  |  | 65.08 | [5 empty] | 62.21 |  |  | 65.32 |  |  |  | 5.81 |  | 4.02 | [8 empty] | 30.91 |  |  |  |  | 0.00
1991 |  |  |  | 4707.49 |  |  | 6530 |  |  |  | 741 | [10 empty] | 73.96 |  |  |  | 74.64 | [5 empty] | 72.52 |  |  | 74.54 |  |  |  | 6.19 |  | 4.92 | [8 empty] | 20.44 |  |  |  |  | 0.68
1992 |  |  |  | 6157.15 |  |  | 8444 |  |  |  | 741 | [10 empty] | 96.08 |  |  |  | 96.08 | [5 empty] | 94.60 |  |  | 96.13 |  |  |  | 2.98 |  | 2.95 | [8 empty] | 0.97 |  |  |  |  | 0.00
1993 |  |  |  | 4956.71 |  |  | 6913 |  |  |  | 737 | [10 empty] | 78.38 |  |  |  | 78.38 | [5 empty] | 76.78 |  |  | 78.92 |  |  |  | 5.25 |  | 4.34 | [8 empty] | 17.28 |  |  |  |  | 0.00
1994 |  |  |  | 5512.20 |  |  | 7542 |  |  |  | 741 | [10 empty] | 85.80 |  |  |  | 85.80 | [5 empty] | 84.92 |  |  | 86.10 |  |  |  | 1.57 |  | 1.37 | [8 empty] | 12.83 |  |  |  |  | 0.00
1995 |  |  |  | 6465.83 |  |  | 8760 |  |  |  | 741 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.61 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 5726.66 |  |  | 7666 |  |  |  | 788 | [10 empty] | 87.80 |  |  |  | 87.80 | [5 empty] | 82.65 |  |  | 87.27 |  |  |  | 2.35 |  | 2.11 | [8 empty] | 10.09 |  |  |  |  | 0.00
1997 |  |  |  | 6009.00 |  |  | 7637 |  |  |  | 800 | [10 empty] | 87.88 |  |  |  | 87.88 | [5 empty] | 85.74 |  |  | 87.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.12 |  |  |  |  | 0.00
1998 |  |  |  | 6951.75 |  |  | 8751 |  |  |  | 800 | [10 empty] | 99.91 |  |  |  | 99.91 | [5 empty] | 99.20 |  |  | 99.90 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 5968.79 |  |  | 7153 |  |  |  | 808 | [10 empty] | 82.16 |  |  |  | 82.16 | [5 empty] | 84.29 |  |  | 81.66 |  |  |  | 2.48 |  | 2.09 | [8 empty] | 15.76 |  |  |  |  | 0.00
2000 |  |  |  | 6413.39 |  |  | 7530 |  |  |  | 863 | [10 empty] | 86.23 |  |  |  | 86.23 | [5 empty] | 84.81 |  |  | 85.72 |  |  |  | 4.90 |  | 4.44 | [8 empty] | 9.33 |  |  |  |  | 0.00
2001 |  |  |  | 7496.17 |  |  | 8689 |  |  |  | 863 | [10 empty] | 99.14 |  |  |  | 99.14 | [5 empty] | 99.16 |  |  | 99.19 |  |  |  | 0.86 |  | 0.86 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 6627.11 |  |  | 7778 |  |  |  | 856 | [10 empty] | 88.81 |  |  |  | 88.81 | [5 empty] | 88.38 |  |  | 88.79 |  |  |  | 1.49 |  | 1.34 | [8 empty] | 9.85 |  |  |  |  | 0.00
2003 |  |  |  | 7146.92 |  |  | 8438 |  |  |  | 856 | [10 empty] | 96.33 |  |  |  | 96.33 | [5 empty] | 95.31 |  |  | 96.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.67 |  |  |  |  | 0.00
2004 |  |  |  | 6896.11 |  |  | 8046 |  |  |  | 869 | [10 empty] | 91.70 |  |  |  | 91.70 | [5 empty] | 90.79 |  |  | 91.60 |  |  |  | 0.29 |  | 0.27 | [8 empty] | 8.04 |  |  |  |  | 0.00
2005 |  |  |  | 6993.53 |  |  | 8121 |  |  |  | 856 | [10 empty] | 92.72 |  |  |  | 92.72 | [5 empty] | 93.26 |  |  | 92.71 |  |  |  | 4.88 |  | 4.76 | [8 empty] | 2.52 |  |  |  |  | 0.00
2006 |  |  |  | 6422.81 |  |  | 7516 |  |  |  | 876 | [10 empty] | 85.37 |  |  |  | 85.37 | [5 empty] | 86.27 |  |  | 85.80 |  |  |  | 0.98 |  | 0.84 | [8 empty] | 13.79 |  |  |  |  | 0.00
2007 |  |  |  | 7499.08 |  |  | 8550 |  |  |  | 876 | [10 empty] | 97.63 |  |  |  | 97.63 | [5 empty] | 97.72 |  |  | 97.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.37 |  |  |  |  | 0.00
2008 |  |  |  | 6433.74 |  |  | 7527 |  |  |  | 876 | [10 empty] | 85.72 |  |  |  | 85.72 | [5 empty] | 83.61 |  |  | 85.69 |  |  |  | 2.19 |  | 1.92 | [8 empty] | 12.36 |  |  |  |  | 0.00
2009 |  |  |  | 7190.01 |  |  | 8289 |  |  |  | 876 | [10 empty] | 94.63 |  |  |  | 94.63 | [5 empty] | 93.70 |  |  | 94.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.37 |  |  |  |  | 0.00
2010 |  |  |  | 6509.87 |  |  | 7690 |  |  |  | 876 | [10 empty] | 87.80 |  |  |  | 87.80 | [5 empty] | 84.83 |  |  | 87.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.20 |  |  |  |  | 0.00
2011 |  |  |  | 7529.65 |  |  | 8760 |  |  |  | 876 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.12 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 6802.03 |  |  | 7876 |  |  |  | 876 | [10 empty] | 89.69 |  |  |  | 89.69 | [5 empty] | 88.40 |  |  | 89.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.31 |  |  |  |  | 0.00
2013 |  |  |  | 7056.54 |  |  | 8251 |  |  |  | 876 | [10 empty] | 94.19 |  |  |  | 94.19 | [5 empty] | 91.95 |  |  | 94.18 |  |  |  | 5.81 |  | 5.81 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 6816.80 |  |  | 7901 |  |  |  | 876 | [10 empty] | 90.20 |  |  |  | 90.20 | [5 empty] | 88.83 |  |  | 90.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.80 |  |  |  |  | 0.00
2015 |  |  |  | 7570.54 |  |  | 8657 |  |  |  | 876 | [10 empty] | 98.84 |  |  |  | 98.84 | [5 empty] | 98.65 |  |  | 98.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.16 |  |  |  |  | 0.00
2016 |  |  |  | 6991.13 |  |  | 8096 |  |  |  | 876 | [10 empty] | 92.16 |  |  |  | 92.16 | [5 empty] | 90.86 |  |  | 92.17 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 7.71 |  |  |  |  | 0.00
2017 |  |  |  | 7318.73 |  |  | 8425 |  |  |  | 876 | [10 empty] | 94.36 |  |  |  | 94.36 | [5 empty] | 95.37 |  |  | 96.18 |  |  |  | 5.55 |  | 5.55 | [8 empty] | 0.09 |  |  |  |  | 0.00
2018 |  |  |  | 7009.59 |  |  | 8098 |  |  |  | 876 | [10 empty] | 92.44 |  |  |  | 92.44 | [5 empty] | 91.34 |  |  | 92.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.56 |  |  |  |  | 0.00
2019 |  |  |  | 7558.09 |  |  | 8624 |  |  |  | 876 | [10 empty] | 98.46 |  |  |  | 98.46 | [5 empty] | 98.49 |  |  | 98.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.54 |  |  |  |  | 0.00
2020 |  |  |  | 6410.21 |  |  | 7518 |  |  |  | 876 | [10 empty] | 85.60 |  |  |  | 85.60 | [5 empty] | 83.31 |  |  | 85.59 |  |  |  | 2.07 |  | 1.81 | [8 empty] | 12.59 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 290
B. |  | Refuelling without maintenance | [20 empty] | 1106 | [14 empty] | 25
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 927
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 89
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 16
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
P. |  | Fire | [39 empty] | 9
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 1
Z. |  | Other | [24 empty] | 159 | [10 empty] | 2 |  |  |  | 39
Subtotal | [22 empty] | 1106 |  |  |  | 159 | [10 empty] | 1044 |  |  |  | 357 | [11 empty] | 1
Total | [22 empty] | 1265 | [14 empty] | 1402
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 41
14. |  |  | Safety Systems | [34 empty] | 27
15. |  |  | Reactor Cooling Systems | [34 empty] | 37
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 62
32. |  |  | Feedwater and Main Steam System | [34 empty] | 61
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 16
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 22
42. |  |  | Electrical Power Supply Systems | [34 empty] | 26
Total | [37 empty] | 317
Highlights (2020)
Refueling Outage 29

## HATCH-2
2020 Operating Experience
US-366 | [8 empty] | HATCH-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SOUTHERN (Southern Nuclear Operating Company, Inc.)
Owner | [7 empty] | : | GPCO (GEORGIA POWER CO.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-02-01
Thermal power | [12 empty] | : |  |  | 2804 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-09-22
Gross electrical power | [12 empty] | : |  |  | 921 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-09-05
Reference unit power (net) | [12 empty] | : |  |  | 883 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.07
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 279
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.435
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 18750 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.27 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.68
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 137 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7557.67 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.8 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.8 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.2 %
Load Factor (LF) | [18 empty] | : | 97.44 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 97.79 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 194 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 656.16 | 626.44 |  |  |  | 666.18 |  | 417.28 | [8 empty] | 661.59 |  |  | 637.22 | [6 empty] | 653.24 |  | 653.86 |  |  |  | 636.30 |  |  | 655.61 |  |  | 642.75 | [9 empty] | 651.04 |  |  | 7557.67
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 73.15 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.80
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 73.15 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.80
LF [%] |  |  |  |  | 99.88 | 101.93 |  |  |  | 101.41 |  | 65.63 | [8 empty] | 100.71 |  |  | 100.23 | [6 empty] | 99.43 |  | 99.53 |  |  |  | 100.08 |  |  | 99.79 |  |  | 101.10 | [9 empty] | 99.10 |  |  | 97.44
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 73.19 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.79
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 26.85 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.20
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 244831.75 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.98 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.4 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.62 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.44 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.94 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.08 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 2632.60 |  |  | 4155 |  |  |  | 749 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 80.12 |  |  | 84.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 3653.10 |  |  | 5269 |  |  |  | 767 | [10 empty] | 59.14 |  |  |  | 61.00 | [5 empty] | 54.22 |  |  | 59.98 |  |  |  | 9.09 |  | 6.10 | [8 empty] | 32.90 |  |  |  |  | 1.86
1981 |  |  |  | 4481.50 |  |  | 6872 |  |  |  | 772 | [10 empty] | 78.68 |  |  |  | 78.68 | [5 empty] | 66.27 |  |  | 78.45 |  |  |  | 8.17 |  | 7.00 | [8 empty] | 14.33 |  |  |  |  | 0.00
1982 |  |  |  | 3734.20 |  |  | 5588 |  |  |  | 771 | [10 empty] | 63.90 |  |  |  | 63.90 | [5 empty] | 55.29 |  |  | 63.79 |  |  |  | 11.54 |  | 8.34 | [8 empty] | 27.76 |  |  |  |  | 0.00
1983 |  |  |  | 3817.20 |  |  | 5774 |  |  |  | 771 | [10 empty] | 66.14 |  |  |  | 66.14 | [5 empty] | 56.52 |  |  | 65.91 |  |  |  | 16.68 |  | 13.24 | [8 empty] | 20.62 |  |  |  |  | 0.00
1984 |  |  |  | 1893.50 |  |  | 2833 |  |  |  | 748 | [10 empty] | 26.70 |  |  |  | 26.70 | [5 empty] | 28.82 |  |  | 32.25 |  |  |  | 11.91 |  | 3.61 | [8 empty] | 69.69 |  |  |  |  | 0.00
1985 |  |  |  | 5376.13 |  |  | 7239 |  |  |  | 748 | [10 empty] | 82.65 |  |  |  | 82.65 | [5 empty] | 82.05 |  |  | 82.64 |  |  |  | 3.03 |  | 2.58 | [8 empty] | 14.77 |  |  |  |  | 0.00
1986 |  |  |  | 3618.71 |  |  | 6169 |  |  |  | 777 | [10 empty] | 70.41 |  |  |  | 70.41 | [5 empty] | 53.17 |  |  | 70.42 |  |  |  | 6.53 |  | 4.92 | [8 empty] | 24.67 |  |  |  |  | 0.00
1987 |  |  |  | 5755.61 |  |  | 8388 |  |  |  | 761 | [10 empty] | 95.73 |  |  |  | 95.73 | [5 empty] | 86.34 |  |  | 95.75 |  |  |  | 3.20 |  | 3.16 | [8 empty] | 1.11 |  |  |  |  | 0.00
1988 |  |  |  | 4254.48 |  |  | 5917 |  |  |  | 768 | [10 empty] | 65.65 |  |  |  | 65.65 | [5 empty] | 63.07 |  |  | 67.36 |  |  |  | 16.67 |  | 13.13 | [8 empty] | 21.22 |  |  |  |  | 0.00
1989 |  |  |  | 4147.17 |  |  | 6155 |  |  |  | 768 | [10 empty] | 68.60 |  |  |  | 68.60 | [5 empty] | 61.64 |  |  | 70.26 |  |  |  | 0.39 |  | 0.27 | [8 empty] | 31.13 |  |  |  |  | 0.00
1990 |  |  |  | 6527.75 |  |  | 8649 |  |  |  | 766 | [10 empty] | 98.66 |  |  |  | 98.66 | [5 empty] | 97.28 |  |  | 98.73 |  |  |  | 1.34 |  | 1.34 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 4932.15 |  |  | 6656 |  |  |  | 761 | [10 empty] | 74.38 |  |  |  | 74.38 | [5 empty] | 73.99 |  |  | 75.98 |  |  |  | 4.84 |  | 3.78 | [8 empty] | 21.84 |  |  |  |  | 0.00
1992 |  |  |  | 4692.39 |  |  | 6668 |  |  |  | 764 | [10 empty] | 74.52 |  |  |  | 74.52 | [5 empty] | 69.86 |  |  | 75.91 |  |  |  | 2.95 |  | 2.26 | [8 empty] | 23.21 |  |  |  |  | 0.00
1993 |  |  |  | 4999.71 |  |  | 7734 |  |  |  | 757 | [10 empty] | 87.45 |  |  |  | 87.45 | [5 empty] | 75.40 |  |  | 88.29 |  |  |  | 12.55 |  | 12.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 5275.59 |  |  | 7534 |  |  |  | 765 | [10 empty] | 85.19 |  |  |  | 85.19 | [5 empty] | 78.72 |  |  | 86.00 |  |  |  | 1.87 |  | 1.63 | [8 empty] | 13.19 |  |  |  |  | 0.00
1995 |  |  |  | 5055.51 |  |  | 6888 |  |  |  | 768 | [10 empty] | 77.45 |  |  |  | 77.45 | [5 empty] | 75.07 |  |  | 78.63 |  |  |  | 6.54 |  | 5.42 | [8 empty] | 17.13 |  |  |  |  | 0.00
1996 |  |  |  | 7021.70 |  |  | 8639 |  |  |  | 809 | [10 empty] | 98.36 |  |  |  | 98.36 | [5 empty] | 98.81 |  |  | 98.35 |  |  |  | 0.70 |  | 0.70 | [8 empty] | 0.94 |  |  |  |  | 0.00
1997 |  |  |  | 6033.58 |  |  | 7560 |  |  |  | 818 | [10 empty] | 86.43 |  |  |  | 86.43 | [5 empty] | 84.20 |  |  | 86.30 |  |  |  | 2.77 |  | 2.46 | [8 empty] | 11.11 |  |  |  |  | 0.00
1998 |  |  |  | 5829.91 |  |  | 7247 |  |  |  | 821 | [10 empty] | 82.84 |  |  |  | 82.84 | [5 empty] | 81.05 |  |  | 82.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.16 |  |  |  |  | 0.00
1999 |  |  |  | 7073.63 |  |  | 8173 |  |  |  | 855 | [10 empty] | 93.31 |  |  |  | 93.31 | [5 empty] | 94.44 |  |  | 93.30 |  |  |  | 5.10 |  | 5.01 | [8 empty] | 1.68 |  |  |  |  | 0.00
2000 |  |  |  | 6900.28 |  |  | 7884 |  |  |  | 878 | [10 empty] | 89.65 |  |  |  | 89.65 | [5 empty] | 89.93 |  |  | 89.75 |  |  |  | 0.24 |  | 0.21 | [8 empty] | 10.14 |  |  |  |  | 0.00
2001 |  |  |  | 6584.53 |  |  | 7618 |  |  |  | 878 | [10 empty] | 86.29 |  |  |  | 86.29 | [5 empty] | 85.61 |  |  | 86.96 |  |  |  | 2.95 |  | 2.62 | [8 empty] | 11.09 |  |  |  |  | 0.00
2002 |  |  |  | 7423.29 |  |  | 8544 |  |  |  | 870 | [10 empty] | 97.34 |  |  |  | 97.34 | [5 empty] | 97.40 |  |  | 97.53 |  |  |  | 2.66 |  | 2.66 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 6962.51 |  |  | 8052 |  |  |  | 883 | [10 empty] | 91.94 |  |  |  | 91.94 | [5 empty] | 91.13 |  |  | 91.92 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 7.99 |  |  |  |  | 0.00
2004 |  |  |  | 7520.63 |  |  | 8589 |  |  |  | 883 | [10 empty] | 97.79 |  |  |  | 97.79 | [5 empty] | 96.96 |  |  | 97.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.21 |  |  |  |  | 0.00
2005 |  |  |  | 6727.80 |  |  | 7724 |  |  |  | 883 | [10 empty] | 88.20 |  |  |  | 88.20 | [5 empty] | 86.97 |  |  | 88.16 |  |  |  | 1.78 |  | 1.60 | [8 empty] | 10.20 |  |  |  |  | 0.00
2006 |  |  |  | 7641.83 |  |  | 8694 |  |  |  | 883 | [10 empty] | 99.25 |  |  |  | 99.25 | [5 empty] | 98.79 |  |  | 99.25 |  |  |  | 0.75 |  | 0.75 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 6749.03 |  |  | 7744 |  |  |  | 883 | [10 empty] | 88.41 |  |  |  | 88.41 | [5 empty] | 87.25 |  |  | 88.40 |  |  |  | 0.73 |  | 0.65 | [8 empty] | 10.94 |  |  |  |  | 0.00
2008 |  |  |  | 7479.80 |  |  | 8516 |  |  |  | 883 | [10 empty] | 96.96 |  |  |  | 96.96 | [5 empty] | 96.44 |  |  | 96.95 |  |  |  | 0.81 |  | 0.79 | [8 empty] | 2.25 |  |  |  |  | 0.00
2009 |  |  |  | 5218.51 |  |  | 6119 |  |  |  | 883 | [10 empty] | 69.87 |  |  |  | 69.87 | [5 empty] | 67.47 |  |  | 69.85 |  |  |  | 1.54 |  | 1.09 | [8 empty] | 29.04 |  |  |  |  | 0.00
2010 |  |  |  | 7391.68 |  |  | 8456 |  |  |  | 883 | [10 empty] | 96.54 |  |  |  | 96.54 | [5 empty] | 95.56 |  |  | 96.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.46 |  |  |  |  | 0.00
2011 |  |  |  | 6052.02 |  |  | 7405 |  |  |  | 883 | [10 empty] | 84.57 |  |  |  | 84.57 | [5 empty] | 78.24 |  |  | 84.53 |  |  |  | 0.74 |  | 0.63 | [8 empty] | 14.80 |  |  |  |  | 0.00
2012 |  |  |  | 7581.41 |  |  | 8634 |  |  |  | 883 | [10 empty] | 98.30 |  |  |  | 98.30 | [5 empty] | 97.75 |  |  | 98.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.70 |  |  |  |  | 0.00
2013 |  |  |  | 6767.29 |  |  | 7728 |  |  |  | 883 | [10 empty] | 88.22 |  |  |  | 88.22 | [5 empty] | 87.48 |  |  | 88.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.78 |  |  |  |  | 0.00
2014 |  |  |  | 7693.19 |  |  | 8760 |  |  |  | 883 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.46 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6926.72 |  |  | 7950 |  |  |  | 883 | [10 empty] | 90.75 |  |  |  | 90.75 | [5 empty] | 89.55 |  |  | 90.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.25 |  |  |  |  | 0.00
2016 |  |  |  | 7656.23 |  |  | 8657 |  |  |  | 883 | [10 empty] | 98.55 |  |  |  | 98.55 | [5 empty] | 98.71 |  |  | 98.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.45 |  |  |  |  | 0.00
2017 |  |  |  | 7212.21 |  |  | 8254 |  |  |  | 883 | [10 empty] | 94.22 |  |  |  | 94.22 | [5 empty] | 93.24 |  |  | 94.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.78 |  |  |  |  | 0.00
2018 |  |  |  | 7393.99 |  |  | 8562 |  |  |  | 883 | [10 empty] | 97.74 |  |  |  | 97.74 | [5 empty] | 95.59 |  |  | 97.74 |  |  |  | 2.26 |  | 2.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 6358.89 |  |  | 7386 |  |  |  | 883 | [10 empty] | 84.33 |  |  |  | 84.33 | [5 empty] | 82.21 |  |  | 84.32 |  |  |  | 3.75 |  | 3.28 | [8 empty] | 12.39 |  |  |  |  | 0.00
2020 |  |  |  | 7557.67 |  |  | 8590 |  |  |  | 883 | [10 empty] | 97.80 |  |  |  | 97.80 | [5 empty] | 97.44 |  |  | 97.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.20 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1979 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 186
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 945
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 193 | [14 empty] | 134
E. |  | Testing of plant systems or components | [35 empty] | 12 |  |  |  | 66
L. |  | Human factor related | [39 empty] | 32
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 0
Z. |  | Other | [39 empty] | 29
Subtotal | [22 empty] | 193 | [14 empty] | 1091 |  |  |  | 313
Total | [22 empty] | 193 | [14 empty] | 1404
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1979 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 25
12. |  |  | Reactor I&C Systems | [34 empty] | 16
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 100
31. |  |  | Turbine and auxiliaries | [34 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 36
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 21
42. |  |  | Electrical Power Supply Systems | [34 empty] | 11
Total | [37 empty] | 261
Highlights (2020)
Repair of drywell/torus vacuum breaker

## HOPE CREEK-1
2020 Operating Experience
US-354 | [8 empty] | HOPE CREEK-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PSEG (PSEG Nuclear, LLC)
Owner | [7 empty] | : | PSEGPOWR (PSEG Power, Inc.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-03-01
Thermal power | [12 empty] | : |  |  | 3840 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-08-01
Gross electrical power | [12 empty] | : |  |  | 1240 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-12-20
Reference unit power (net) | [12 empty] | : |  |  | 1172 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.17
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 30000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.56
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.52 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10592.7 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 102.89 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 917.55 | 847.71 |  |  |  | 900.18 |  | 874.62 | [8 empty] | 901.90 |  |  | 853.13 | [6 empty] | 876.31 |  | 876.47 |  |  |  | 861.33 |  |  | 895.44 |  |  | 875.09 | [9 empty] | 912.97 |  |  | 10592.70
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 105.23 | 103.92 |  |  |  | 103.24 |  | 103.65 | [8 empty] | 103.43 |  |  | 101.10 | [6 empty] | 100.50 |  | 100.52 |  |  |  | 102.07 |  |  | 102.69 |  |  | 103.70 | [9 empty] | 104.70 |  |  | 102.89
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 296294.86 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.52 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.56 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.56 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.72 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | Data not provided
1987 |  |  |  | 7308.74 |  |  | 7457 |  |  |  | 1067 | [10 empty] | 92.67 |  |  |  | 92.67 | [5 empty] | 78.19 |  |  | 85.13 |  |  |  | 4.09 |  | 3.95 | [8 empty] | 3.38 |  |  |  |  | 0.00
1988 |  |  |  | 6470.87 |  |  | 6369 |  |  |  | 1061 | [10 empty] | 79.03 |  |  |  | 79.03 | [5 empty] | 69.43 |  |  | 72.51 |  |  |  | 5.32 |  | 4.44 | [8 empty] | 16.53 |  |  |  |  | 0.00
1989 |  |  |  | 6614.33 |  |  | 6717 |  |  |  | 1031 | [10 empty] | 76.72 |  |  |  | 76.72 | [5 empty] | 73.24 |  |  | 76.68 |  |  |  | 1.41 |  | 1.10 | [8 empty] | 22.18 |  |  |  |  | 0.00
1990 |  |  |  | 8100.14 |  |  | 7940 |  |  |  | 1031 | [10 empty] | 90.66 |  |  |  | 90.66 | [5 empty] | 89.69 |  |  | 90.64 |  |  |  | 6.26 |  | 6.05 | [8 empty] | 3.29 |  |  |  |  | 0.00
1991 |  |  |  | 7402.71 |  |  | 7280 |  |  |  | 1031 | [10 empty] | 83.07 |  |  |  | 83.07 | [5 empty] | 81.96 |  |  | 83.11 |  |  |  | 4.06 |  | 3.52 | [8 empty] | 13.41 |  |  |  |  | 0.00
1992 |  |  |  | 7059.11 |  |  | 6930 |  |  |  | 1031 | [10 empty] | 78.92 |  |  |  | 78.92 | [5 empty] | 77.95 |  |  | 78.89 |  |  |  | 2.57 |  | 2.08 | [8 empty] | 19.00 |  |  |  |  | 0.00
1993 |  |  |  | 8825.34 |  |  | 8526 |  |  |  | 1031 | [10 empty] | 97.35 |  |  |  | 97.35 | [5 empty] | 97.72 |  |  | 97.33 |  |  |  | 2.65 |  | 2.65 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 7125.64 |  |  | 6969 |  |  |  | 1031 | [10 empty] | 79.60 |  |  |  | 79.60 | [5 empty] | 78.90 |  |  | 79.55 |  |  |  | 6.85 |  | 5.86 | [8 empty] | 14.54 |  |  |  |  | 0.00
1995 |  |  |  | 7072.28 |  |  | 6937 |  |  |  | 1031 | [10 empty] | 79.21 |  |  |  | 79.21 | [5 empty] | 78.31 |  |  | 79.19 |  |  |  | 7.95 |  | 6.84 | [8 empty] | 13.95 |  |  |  |  | 0.00
1996 |  |  |  | 6770.72 |  |  | 6618 |  |  |  | 1031 | [10 empty] | 75.36 |  |  |  | 75.36 | [5 empty] | 74.76 |  |  | 75.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.64 |  |  |  |  | 0.00
1997 |  |  |  | 6417.76 |  |  | 6511 |  |  |  | 1031 | [10 empty] | 74.32 |  |  |  | 74.32 | [5 empty] | 71.06 |  |  | 74.33 |  |  |  | 0.93 |  | 0.70 | [8 empty] | 24.99 |  |  |  |  | 0.00
1998 |  |  |  | 8700.37 |  |  | 8539 |  |  |  | 1031 | [10 empty] | 97.48 |  |  |  | 97.48 | [5 empty] | 96.33 |  |  | 97.48 |  |  |  | 2.52 |  | 2.52 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 7701.08 |  |  | 7538 |  |  |  | 1031 | [10 empty] | 86.05 |  |  |  | 86.05 | [5 empty] | 85.27 |  |  | 86.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.95 |  |  |  |  | 0.00
2000 |  |  |  | 7271.74 |  |  | 7259 |  |  |  | 1031 | [10 empty] | 82.57 |  |  |  | 82.57 | [5 empty] | 80.29 |  |  | 82.64 |  |  |  | 8.12 |  | 7.30 | [8 empty] | 10.13 |  |  |  |  | 0.00
2001 |  |  |  | 8065.27 |  |  | 7859 |  |  |  | 1049 | [10 empty] | 89.79 |  |  |  | 89.79 | [5 empty] | 88.65 |  |  | 89.71 |  |  |  | 3.66 |  | 3.41 | [8 empty] | 6.80 |  |  |  |  | 0.00
2002 |  |  |  | 8843.08 |  |  | 8555 |  |  |  | 1049 | [10 empty] | 97.66 |  |  |  | 97.66 | [5 empty] | 96.23 |  |  | 97.66 |  |  |  | 1.33 |  | 1.31 | [8 empty] | 1.03 |  |  |  |  | 0.00
2003 |  |  |  | 7260.58 |  |  | 7137 |  |  |  | 1049 | [10 empty] | 81.47 |  |  |  | 81.47 | [5 empty] | 79.01 |  |  | 81.47 |  |  |  | 9.64 |  | 8.69 | [8 empty] | 9.84 |  |  |  |  | 0.00
2004 |  |  |  | 6048.87 |  |  | 6123 |  |  |  | 1049 | [10 empty] | 69.71 |  |  |  | 69.71 | [5 empty] | 65.65 |  |  | 69.71 |  |  |  | 9.29 |  | 7.14 | [8 empty] | 23.16 |  |  |  |  | 0.00
2005 |  |  |  | 7684.77 |  |  | 7379 |  |  |  | 1049 | [10 empty] | 84.24 |  |  |  | 84.24 | [5 empty] | 83.62 |  |  | 84.23 |  |  |  | 5.55 |  | 4.95 | [8 empty] | 10.81 |  |  |  |  | 0.00
2006 |  |  |  | 8617.78 |  |  | 8042 |  |  |  | 1059 | [10 empty] | 91.82 |  |  |  | 91.82 | [5 empty] | 92.90 |  |  | 91.80 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 8.10 |  |  |  |  | 0.00
2007 |  |  |  | 8104.54 |  |  | 7774 |  |  |  | 1061 | [10 empty] | 88.78 |  |  |  | 88.78 | [5 empty] | 87.20 |  |  | 88.74 |  |  |  | 1.27 |  | 1.14 | [8 empty] | 10.08 |  |  |  |  | 0.00
2008 |  |  |  | 10006.26 |  |  | 8756 |  |  |  | 1186 | [10 empty] | 99.67 |  |  |  | 99.67 | [5 empty] | 100.44 |  |  | 99.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.33 |  |  |  |  | 0.00
2009 |  |  |  | 9700.30 |  |  | 8104 |  |  |  | 1161 | [10 empty] | 92.37 |  |  |  | 92.37 | [5 empty] | 95.38 |  |  | 92.51 |  |  |  | 1.09 |  | 1.01 | [8 empty] | 6.61 |  |  |  |  | 0.00
2010 |  |  |  | 9438.54 |  |  | 8001 |  |  |  | 1191 | [10 empty] | 91.37 |  |  |  | 91.37 | [5 empty] | 92.60 |  |  | 91.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.63 |  |  |  |  | 0.00
2011 |  |  |  | 10505.93 |  |  | 8690 |  |  |  | 1191 | [10 empty] | 99.20 |  |  |  | 99.20 | [5 empty] | 100.70 |  |  | 99.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.80 |  |  |  |  | 0.00
2012 |  |  |  | 9586.25 |  |  | 8141 |  |  |  | 1172 | [10 empty] | 92.70 |  |  |  | 92.70 | [5 empty] | 93.12 |  |  | 92.68 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 7.12 |  |  |  |  | 0.00
2013 |  |  |  | 9112.68 |  |  | 7751 |  |  |  | 1172 | [10 empty] | 88.49 |  |  |  | 88.49 | [5 empty] | 88.75 |  |  | 88.47 |  |  |  | 4.20 |  | 3.88 | [8 empty] | 7.63 |  |  |  |  | 0.00
2014 |  |  |  | 10406.06 |  |  | 8636 |  |  |  | 1172 | [10 empty] | 98.58 |  |  |  | 98.58 | [5 empty] | 101.36 |  |  | 98.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.42 |  |  |  |  | 0.00
2015 |  |  |  | 9450.74 |  |  | 7895 |  |  |  | 1172 | [10 empty] | 90.13 |  |  |  | 90.13 | [5 empty] | 92.05 |  |  | 90.13 |  |  |  | 1.16 |  | 1.06 | [8 empty] | 8.81 |  |  |  |  | 0.00
2016 |  |  |  | 9639.69 |  |  | 8087 |  |  |  | 1172 | [10 empty] | 92.07 |  |  |  | 92.07 | [5 empty] | 93.64 |  |  | 92.07 |  |  |  | 0.25 |  | 0.23 | [8 empty] | 7.70 |  |  |  |  | 0.00
2017 |  |  |  | 10657.91 |  |  | 8760 |  |  |  | 1172 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.81 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 9583.40 |  |  | 8071 |  |  |  | 1172 | [10 empty] | 92.14 |  |  |  | 92.14 | [5 empty] | 93.34 |  |  | 92.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.86 |  |  |  |  | 0.00
2019 |  |  |  | 8767.20 |  |  | 7746 |  |  |  | 1172 | [10 empty] | 88.44 |  |  |  | 88.44 | [5 empty] | 85.39 |  |  | 88.42 |  |  |  | 0.57 |  | 0.51 | [8 empty] | 11.05 |  |  |  |  | 0.00
2020 |  |  |  | 10592.70 |  |  | 8783 |  |  |  | 1172 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.89 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 171
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 728
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 91
E. |  | Testing of plant systems or components | [35 empty] | 0
L. |  | Human factor related | [39 empty] | 15
P. |  | Fire | [39 empty] | 1
Z. |  | Other | [39 empty] | 3
Subtotal | [37 empty] | 819 |  |  |  | 190
Total | [22 empty] | 0 | [14 empty] | 1009
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 27
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 31
32. |  |  | Feedwater and Main Steam System | [34 empty] | 25
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 15
42. |  |  | Electrical Power Supply Systems | [34 empty] | 24
Total | [37 empty] | 175

## INDIAN POINT-2
2020 Operating Experience
US-247 | [8 empty] | INDIAN POINT-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Owner | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1966-10-14
Thermal power | [12 empty] | : |  |  | 3216 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-06-26
Gross electrical power | [12 empty] | : |  |  | 1067 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-08-01
Reference unit power (net) | [12 empty] | : |  |  | 998 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.82
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 309
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 36000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.09
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.81 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 2759.08 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.97 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.97 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.03 %
Load Factor (LF) | [18 empty] | : | 95.2 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.93 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2 hours
Annual Summary
[5 empty] | Oct | Nov |  |  |  | Dec |  | May | [8 empty] | Sep |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Jan |  |  | Feb |  |  | Mar | [9 empty] | Apr |  |  | Annual
GW(e)-h | [36 empty] | 759.14 |  |  | 713.31 |  |  | 733.66 | [9 empty] | 552.97 |  |  | 2759.08
EAF [%] | [36 empty] | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.86 |  |  | 99.97
UCF [%] | [36 empty] | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.86 |  |  | 99.97
LF [%] | [36 empty] | 102.24 |  |  | 102.69 |  |  | 98.81 | [9 empty] | 76.96 |  |  | 95.20
OF [%] | [36 empty] | 100.00 |  |  | 100.00 |  |  | 99.87 | [9 empty] | 99.86 |  |  | 99.93
FLR [%] | [36 empty] | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] | [36 empty] | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] | [36 empty] | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.14 |  |  | 0.03
XUF [%] | [36 empty] | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 291542.82 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 8.99 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.36 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.65 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.42 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.93 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.81 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.06 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.68 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 3329.00 |  |  | 5220 |  |  |  | 873 | [10 empty] | 79.85 |  |  |  | 79.85 | [5 empty] | 63.54 |  |  | 79.87 |  |  |  | 3.72 |  | 3.09 | [8 empty] | 17.07 |  |  |  |  | 0.00
1975 |  |  |  | 4646.00 |  |  | 6545 |  |  |  | 865 | [10 empty] | 61.32 |  |  |  | 61.32 | [5 empty] | 61.31 |  |  | 74.71 |  |  |  | 15.45 |  | 11.20 | [8 empty] | 27.48 |  |  |  |  | 0.00
1976 |  |  |  | 2287.10 |  |  | 3054 |  |  |  | 864 | [10 empty] | 30.18 |  |  |  | 30.18 | [5 empty] | 30.14 |  |  | 34.77 |  |  |  | 9.08 |  | 3.01 | [8 empty] | 66.81 |  |  |  |  | 0.00
1977 |  |  |  | 5210.30 |  |  | 6626 |  |  |  | 864 | [10 empty] | 68.90 |  |  |  | 68.90 | [5 empty] | 68.84 |  |  | 75.64 |  |  |  | 19.73 |  | 16.93 | [8 empty] | 14.17 |  |  |  |  | 0.00
1978 |  |  |  | 4372.90 |  |  | 5503 |  |  |  | 859 | [10 empty] | 58.22 |  |  |  | 58.22 | [5 empty] | 58.11 |  |  | 62.82 |  |  |  | 6.52 |  | 4.06 | [8 empty] | 37.72 |  |  |  |  | 0.00
1979 |  |  |  | 4808.40 |  |  | 6156 |  |  |  | 856 | [10 empty] | 64.07 |  |  |  | 64.07 | [5 empty] | 64.12 |  |  | 70.27 |  |  |  | 8.64 |  | 6.06 | [8 empty] | 29.87 |  |  |  |  | 0.00
1980 |  |  |  | 4273.20 |  |  | 5689 |  |  |  | 856 | [10 empty] | 63.87 |  |  |  | 66.77 | [5 empty] | 56.83 |  |  | 64.77 |  |  |  | 11.90 |  | 9.02 | [8 empty] | 24.21 |  |  |  |  | 2.89
1981 |  |  |  | 3065.00 |  |  | 4027 |  |  |  | 856 | [10 empty] | 44.90 |  |  |  | 44.90 | [5 empty] | 40.87 |  |  | 45.97 |  |  |  | 21.36 |  | 12.20 | [8 empty] | 42.91 |  |  |  |  | 0.00
1982 |  |  |  | 4458.60 |  |  | 5726 |  |  |  | 862 | [10 empty] | 65.01 |  |  |  | 65.01 | [5 empty] | 59.05 |  |  | 65.37 |  |  |  | 7.80 |  | 5.50 | [8 empty] | 29.49 |  |  |  |  | 0.00
1983 |  |  |  | 5895.30 |  |  | 7354 |  |  |  | 859 | [10 empty] | 83.49 |  |  |  | 83.49 | [5 empty] | 78.34 |  |  | 83.95 |  |  |  | 9.94 |  | 9.21 | [8 empty] | 7.30 |  |  |  |  | 0.00
1984 |  |  |  | 2891.63 |  |  | 4552 |  |  |  | 864 | [10 empty] | 48.37 |  |  |  | 48.37 | [5 empty] | 38.10 |  |  | 51.82 |  |  |  | 16.36 |  | 9.46 | [8 empty] | 42.16 |  |  |  |  | 0.00
1985 |  |  |  | 6665.04 |  |  | 8382 |  |  |  | 855 | [10 empty] | 95.51 |  |  |  | 95.51 | [5 empty] | 88.97 |  |  | 95.68 |  |  |  | 3.73 |  | 3.70 | [8 empty] | 0.79 |  |  |  |  | 0.00
1986 |  |  |  | 3827.37 |  |  | 4924 |  |  |  | 855 | [10 empty] | 52.63 |  |  |  | 52.63 | [5 empty] | 51.09 |  |  | 56.21 |  |  |  | 13.13 |  | 7.95 | [8 empty] | 39.42 |  |  |  |  | 0.00
1987 |  |  |  | 5149.59 |  |  | 6331 |  |  |  | 852 | [10 empty] | 69.77 |  |  |  | 69.77 | [5 empty] | 68.94 |  |  | 72.27 |  |  |  | 2.16 |  | 1.54 | [8 empty] | 28.69 |  |  |  |  | 0.00
1988 |  |  |  | 6063.99 |  |  | 7247 |  |  |  | 856 | [10 empty] | 81.02 |  |  |  | 81.02 | [5 empty] | 80.60 |  |  | 82.50 |  |  |  | 3.98 |  | 3.36 | [8 empty] | 15.62 |  |  |  |  | 0.00
1989 |  |  |  | 4476.87 |  |  | 5556 |  |  |  | 856 | [10 empty] | 60.35 |  |  |  | 60.35 | [5 empty] | 59.67 |  |  | 63.42 |  |  |  | 2.22 |  | 1.37 | [8 empty] | 38.28 |  |  |  |  | 0.00
1990 |  |  |  | 5222.15 |  |  | 5779 |  |  |  | 886 | [10 empty] | 64.30 |  |  |  | 64.30 | [5 empty] | 67.20 |  |  | 65.97 |  |  |  | 1.63 |  | 1.07 | [8 empty] | 34.64 |  |  |  |  | 0.00
1991 |  |  |  | 3873.43 |  |  | 4495 |  |  |  | 929 | [10 empty] | 51.22 |  |  |  | 51.22 | [5 empty] | 47.60 |  |  | 51.31 |  |  |  | 6.87 |  | 3.78 | [8 empty] | 45.01 |  |  |  |  | 0.00
1992 |  |  |  | 7880.64 |  |  | 8494 |  |  |  | 939 | [10 empty] | 96.70 |  |  |  | 96.70 | [5 empty] | 95.54 |  |  | 96.70 |  |  |  | 3.30 |  | 3.30 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 5931.71 |  |  | 6570 |  |  |  | 941 | [10 empty] | 75.27 |  |  |  | 75.27 | [5 empty] | 71.96 |  |  | 75.00 |  |  |  | 3.04 |  | 2.36 | [8 empty] | 22.37 |  |  |  |  | 0.00
1994 |  |  |  | 7634.60 |  |  | 8760 |  |  |  | 941 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 92.62 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 4896.89 |  |  | 5533 |  |  |  | 941 | [10 empty] | 63.62 |  |  |  | 63.62 | [5 empty] | 59.41 |  |  | 63.16 |  |  |  | 4.88 |  | 3.26 | [8 empty] | 33.12 |  |  |  |  | 0.00
1996 |  |  |  | 7831.79 |  |  | 8261 |  |  |  | 941 | [10 empty] | 94.17 |  |  |  | 94.17 | [5 empty] | 94.75 |  |  | 94.05 |  |  |  | 2.37 |  | 2.29 | [8 empty] | 3.55 |  |  |  |  | 0.00
1997 |  |  |  | 3179.72 |  |  | 3639 |  |  |  | 936 | [10 empty] | 41.74 |  |  |  | 41.74 | [5 empty] | 38.78 |  |  | 41.54 |  |  |  | 48.15 |  | 38.76 | [8 empty] | 19.50 |  |  |  |  | 0.00
1998 |  |  |  | 2512.52 |  |  | 2698 |  |  |  | 932 | [10 empty] | 30.95 |  |  |  | 30.95 | [5 empty] | 30.75 |  |  | 30.80 |  |  |  | 69.05 |  | 69.05 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 7300.44 |  |  | 7665 |  |  |  | 937 | [10 empty] | 87.60 |  |  |  | 87.60 | [5 empty] | 88.88 |  |  | 87.50 |  |  |  | 12.40 |  | 12.40 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 1062.31 |  |  | 1099 |  |  |  | 941 | [10 empty] | 12.51 |  |  |  | 12.51 | [5 empty] | 12.85 |  |  | 12.51 |  |  |  | 87.49 |  | 87.49 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 7792.73 |  |  | 8429 |  |  |  | 951 | [10 empty] | 96.20 |  |  |  | 96.20 | [5 empty] | 94.54 |  |  | 96.22 |  |  |  | 1.42 |  | 1.39 | [8 empty] | 2.42 |  |  |  |  | 0.00
2002 |  |  |  | 7556.55 |  |  | 7931 |  |  |  | 951 | [10 empty] | 90.25 |  |  |  | 90.25 | [5 empty] | 91.67 |  |  | 90.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.75 |  |  |  |  | 0.00
2003 |  |  |  | 8370.81 |  |  | 8597 |  |  |  | 956 | [10 empty] | 98.12 |  |  |  | 98.12 | [5 empty] | 100.30 |  |  | 98.14 |  |  |  | 1.88 |  | 1.88 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 7513.09 |  |  | 7851 |  |  |  | 956 | [10 empty] | 89.31 |  |  |  | 89.31 | [5 empty] | 89.47 |  |  | 89.38 |  |  |  | 2.42 |  | 2.21 | [8 empty] | 8.48 |  |  |  |  | 0.00
2005 |  |  |  | 8847.09 |  |  | 8730 |  |  |  | 965 | [10 empty] | 99.66 |  |  |  | 99.66 | [5 empty] | 104.65 |  |  | 99.65 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 7984.68 |  |  | 7937 |  |  |  | 1020 | [10 empty] | 90.63 |  |  |  | 90.63 | [5 empty] | 89.36 |  |  | 90.61 |  |  |  | 1.03 |  | 0.94 | [8 empty] | 8.42 |  |  |  |  | 0.00
2007 |  |  |  | 8842.64 |  |  | 8679 |  |  |  | 1020 | [10 empty] | 99.09 |  |  |  | 99.09 | [5 empty] | 98.96 |  |  | 99.08 |  |  |  | 0.91 |  | 0.91 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8205.17 |  |  | 8088 |  |  |  | 1020 | [10 empty] | 92.09 |  |  |  | 92.09 | [5 empty] | 91.58 |  |  | 92.08 |  |  |  | 0.99 |  | 0.92 | [8 empty] | 6.99 |  |  |  |  | 0.00
2009 |  |  |  | 8837.44 |  |  | 8667 |  |  |  | 1025 | [10 empty] | 98.96 |  |  |  | 98.96 | [5 empty] | 98.42 |  |  | 98.94 |  |  |  | 1.04 |  | 1.04 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 7325.92 |  |  | 7267 |  |  |  | 1022 | [10 empty] | 82.94 |  |  |  | 82.94 | [5 empty] | 81.83 |  |  | 82.96 |  |  |  | 8.75 |  | 7.96 | [8 empty] | 9.10 |  |  |  |  | 0.00
2011 |  |  |  | 8767.22 |  |  | 8648 |  |  |  | 1022 | [10 empty] | 98.72 |  |  |  | 98.72 | [5 empty] | 97.93 |  |  | 98.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.28 |  |  |  |  | 0.00
2012 |  |  |  | 7911.30 |  |  | 7867 |  |  |  | 1020 | [10 empty] | 89.59 |  |  |  | 89.59 | [5 empty] | 88.30 |  |  | 89.56 |  |  |  | 0.47 |  | 0.42 | [8 empty] | 9.99 |  |  |  |  | 0.00
2013 |  |  |  | 8763.08 |  |  | 8675 |  |  |  | 1020 | [10 empty] | 99.02 |  |  |  | 99.02 | [5 empty] | 98.06 |  |  | 99.02 |  |  |  | 0.98 |  | 0.98 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 8313.12 |  |  | 8194 |  |  |  | 1020 | [10 empty] | 93.54 |  |  |  | 93.54 | [5 empty] | 93.04 |  |  | 93.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.46 |  |  |  |  | 0.00
2015 |  |  |  | 8793.59 |  |  | 8691 |  |  |  | 1020 | [10 empty] | 99.21 |  |  |  | 99.21 | [5 empty] | 98.42 |  |  | 99.21 |  |  |  | 0.79 |  | 0.79 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6030.06 |  |  | 6226 |  |  |  | 1020 | [10 empty] | 70.88 |  |  |  | 70.88 | [5 empty] | 67.30 |  |  | 70.88 |  |  |  | 1.76 |  | 1.27 | [8 empty] | 27.85 |  |  |  |  | 0.00
2017 |  |  |  | 8315.20 |  |  | 8301 |  |  |  | 1020 | [10 empty] | 94.75 |  |  |  | 94.75 | [5 empty] | 93.06 |  |  | 94.76 |  |  |  | 0.76 |  | 0.72 | [8 empty] | 4.52 |  |  |  |  | 0.00
2018 |  |  |  | 7997.10 |  |  | 7957 |  |  |  | 998 | [10 empty] | 90.83 |  |  |  | 90.83 | [5 empty] | 91.47 |  |  | 90.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.17 |  |  |  |  | 0.00
2019 |  |  |  | 8352.75 |  |  | 8301 |  |  |  | 998 | [10 empty] | 94.77 |  |  |  | 94.77 | [5 empty] | 95.54 |  |  | 94.76 |  |  |  | 5.23 |  | 5.23 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 2759.08 |  |  | 2902 |  |  |  | 998 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 95.20 |  |  | 99.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 800
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 959
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 234
E. |  | Testing of plant systems or components | [35 empty] | 20
H. |  | Nuclear regulatory requirements | [39 empty] | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 7
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Z. |  | Other | [20 empty] | 1 | [14 empty] | 4 |  |  |  | 9
Subtotal | [22 empty] | 1 | [14 empty] | 1217 |  |  |  | 821 | [11 empty] | 8
Total | [22 empty] | 1 | [14 empty] | 2046
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 44
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 56
16. |  |  | Steam generation systems | [34 empty] | 64
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 8
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 63
31. |  |  | Turbine and auxiliaries | [34 empty] | 49
32. |  |  | Feedwater and Main Steam System | [34 empty] | 263
34. |  |  | Miscellaneous Systems | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 49
42. |  |  | Electrical Power Supply Systems | [34 empty] | 186
Total | [37 empty] | 801
Highlights (2020)
Indian Point Unit 2 was permanently shut down on April 30,2020 at 2300.

## INDIAN POINT-3
2020 Operating Experience
US-286 | [8 empty] | INDIAN POINT-3 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Owner | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-11-01
Thermal power | [12 empty] | : |  |  | 3216 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-04-27
Gross electrical power | [12 empty] | : |  |  | 1085 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-08-30
Reference unit power (net) | [12 empty] | : |  |  | 1030 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 17.47
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.8
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.33
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 16 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 14000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.028
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 21 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9108.82 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 100.68 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 774.80 | 724.48 |  |  |  | 772.62 |  | 749.75 | [8 empty] | 774.20 |  |  | 745.88 | [6 empty] | 760.53 |  | 760.52 |  |  |  | 743.81 |  |  | 773.87 |  |  | 752.97 | [9 empty] | 775.41 |  |  | 9108.82
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 101.11 | 101.06 |  |  |  | 100.82 |  | 101.10 | [8 empty] | 101.03 |  |  | 100.58 | [6 empty] | 99.24 |  | 99.24 |  |  |  | 100.30 |  |  | 100.99 |  |  | 101.53 | [9 empty] | 101.19 |  |  | 100.68
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 284724.26 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 13.6 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.14 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.83 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.16 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.01 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.92 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.74 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | 3072.00 |  |  | 4430 |  |  |  | 899 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 72.10 |  |  | 76.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1977 |  |  |  | 5520.80 |  |  | 6556 |  |  |  | 873 | [10 empty] | 72.11 |  |  |  | 72.11 | [5 empty] | 72.19 |  |  | 74.84 |  |  |  | 6.36 |  | 4.90 | [8 empty] | 22.99 |  |  |  |  | 0.00
1978 |  |  |  | 5457.60 |  |  | 6365 |  |  |  | 911 | [10 empty] | 68.33 |  |  |  | 68.33 | [5 empty] | 68.39 |  |  | 72.66 |  |  |  | 9.48 |  | 7.16 | [8 empty] | 24.51 |  |  |  |  | 0.00
1979 |  |  |  | 4794.60 |  |  | 5824 |  |  |  | 965 | [10 empty] | 56.72 |  |  |  | 56.72 | [5 empty] | 56.72 |  |  | 66.48 |  |  |  | 8.66 |  | 5.38 | [8 empty] | 37.90 |  |  |  |  | 0.00
1980 |  |  |  | 3070.40 |  |  | 4667 |  |  |  | 965 | [10 empty] | 53.59 |  |  |  | 53.59 | [5 empty] | 36.22 |  |  | 53.13 |  |  |  | 23.31 |  | 16.29 | [8 empty] | 30.11 |  |  |  |  | 0.00
1981 |  |  |  | 3033.40 |  |  | 5236 |  |  |  | 965 | [10 empty] | 59.44 |  |  |  | 59.44 | [5 empty] | 35.88 |  |  | 59.77 |  |  |  | 37.25 |  | 35.29 | [8 empty] | 5.27 |  |  |  |  | 0.00
1982 |  |  |  | 1436.10 |  |  | 1967 |  |  |  | 891 | [10 empty] | 22.53 |  |  |  | 22.53 | [5 empty] | 18.40 |  |  | 22.45 |  |  |  | 2.05 |  | 0.47 | [8 empty] | 77.00 |  |  |  |  | 0.00
1983 |  |  |  | 60.70 |  |  | 229 |  |  |  | 934 | [10 empty] | 2.37 |  |  |  | 2.37 | [5 empty] | 0.74 |  |  | 2.61 |  |  |  | 95.80 |  | 53.98 | [8 empty] | 43.65 |  |  |  |  | 0.00
1984 |  |  |  | 6041.69 |  |  | 6703 |  |  |  | 965 | [10 empty] | 76.19 |  |  |  | 76.19 | [5 empty] | 71.28 |  |  | 76.31 |  |  |  | 12.86 |  | 11.24 | [8 empty] | 12.57 |  |  |  |  | 0.00
1985 |  |  |  | 4728.52 |  |  | 5782 |  |  |  | 965 | [10 empty] | 65.52 |  |  |  | 65.52 | [5 empty] | 55.94 |  |  | 66.00 |  |  |  | 2.18 |  | 1.46 | [8 empty] | 33.02 |  |  |  |  | 0.00
1986 |  |  |  | 5525.58 |  |  | 6431 |  |  |  | 959 | [10 empty] | 72.93 |  |  |  | 72.93 | [5 empty] | 65.77 |  |  | 73.41 |  |  |  | 21.80 |  | 20.34 | [8 empty] | 6.73 |  |  |  |  | 0.00
1987 |  |  |  | 4850.59 |  |  | 5396 |  |  |  | 950 | [10 empty] | 60.47 |  |  |  | 60.47 | [5 empty] | 58.25 |  |  | 61.60 |  |  |  | 2.77 |  | 1.72 | [8 empty] | 37.80 |  |  |  |  | 0.00
1988 |  |  |  | 6711.90 |  |  | 7217 |  |  |  | 965 | [10 empty] | 81.93 |  |  |  | 81.93 | [5 empty] | 79.18 |  |  | 82.16 |  |  |  | 13.46 |  | 12.75 | [8 empty] | 5.32 |  |  |  |  | 0.00
1989 |  |  |  | 4968.73 |  |  | 5279 |  |  |  | 965 | [10 empty] | 59.67 |  |  |  | 59.67 | [5 empty] | 58.78 |  |  | 60.26 |  |  |  | 0.27 |  | 0.16 | [8 empty] | 40.17 |  |  |  |  | 0.00
1990 |  |  |  | 5031.77 |  |  | 5374 |  |  |  | 965 | [10 empty] | 60.79 |  |  |  | 60.79 | [5 empty] | 59.52 |  |  | 61.35 |  |  |  | 1.83 |  | 1.14 | [8 empty] | 38.07 |  |  |  |  | 0.00
1991 |  |  |  | 7300.77 |  |  | 7577 |  |  |  | 965 | [10 empty] | 88.75 |  |  |  | 88.75 | [5 empty] | 86.36 |  |  | 86.50 |  |  |  | 7.99 |  | 7.71 | [8 empty] | 3.54 |  |  |  |  | 0.00
1992 |  |  |  | 4760.60 |  |  | 5248 |  |  |  | 965 | [10 empty] | 59.15 |  |  |  | 59.15 | [5 empty] | 56.16 |  |  | 59.74 |  |  |  | 13.83 |  | 9.49 | [8 empty] | 31.36 |  |  |  |  | 0.00
1993 |  |  |  | 1192.55 |  |  | 1292 |  |  |  | 965 | [10 empty] | 13.44 |  |  |  | 13.44 | [5 empty] | 14.11 |  |  | 14.75 |  |  |  | 86.43 |  | 85.59 | [8 empty] | 0.97 |  |  |  |  | 0.00
1994 |  |  |  | 0.00 |  |  | 0 |  |  |  | 965 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 1471.53 |  |  | 1696 |  |  |  | 965 | [10 empty] | 18.15 |  |  |  | 18.15 | [5 empty] | 17.41 |  |  | 19.36 |  |  |  | 81.81 |  | 81.64 | [8 empty] | 0.21 |  |  |  |  | 0.00
1996 |  |  |  | 5872.49 |  |  | 6390 |  |  |  | 965 | [10 empty] | 72.36 |  |  |  | 72.36 | [5 empty] | 69.28 |  |  | 72.75 |  |  |  | 27.64 |  | 27.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 4337.34 |  |  | 4650 |  |  |  | 965 | [10 empty] | 57.44 |  |  |  | 57.44 | [5 empty] | 51.31 |  |  | 53.08 |  |  |  | 10.87 |  | 7.00 | [8 empty] | 35.56 |  |  |  |  | 0.00
1998 |  |  |  | 7656.52 |  |  | 8197 |  |  |  | 965 | [10 empty] | 93.60 |  |  |  | 93.60 | [5 empty] | 90.57 |  |  | 93.57 |  |  |  | 5.57 |  | 5.52 | [8 empty] | 0.88 |  |  |  |  | 0.00
1999 |  |  |  | 7269.17 |  |  | 7659 |  |  |  | 965 | [10 empty] | 87.40 |  |  |  | 87.40 | [5 empty] | 85.99 |  |  | 87.43 |  |  |  | 1.52 |  | 1.35 | [8 empty] | 11.25 |  |  |  |  | 0.00
2000 |  |  |  | 8432.24 |  |  | 8600 |  |  |  | 965 | [10 empty] | 97.91 |  |  |  | 97.91 | [5 empty] | 99.48 |  |  | 97.91 |  |  |  | 1.89 |  | 1.89 | [8 empty] | 0.20 |  |  |  |  | 0.00
2001 |  |  |  | 7940.17 |  |  | 8130 |  |  |  | 965 | [10 empty] | 92.78 |  |  |  | 92.78 | [5 empty] | 93.93 |  |  | 92.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.22 |  |  |  |  | 0.00
2002 |  |  |  | 8432.65 |  |  | 8611 |  |  |  | 979 | [10 empty] | 98.27 |  |  |  | 98.27 | [5 empty] | 99.63 |  |  | 98.30 |  |  |  | 1.73 |  | 1.73 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 7608.44 |  |  | 7748 |  |  |  | 979 | [10 empty] | 88.41 |  |  |  | 88.41 | [5 empty] | 88.72 |  |  | 88.45 |  |  |  | 3.57 |  | 3.28 | [8 empty] | 8.31 |  |  |  |  | 0.00
2004 |  |  |  | 8747.28 |  |  | 8784 |  |  |  | 979 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.72 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 8037.20 |  |  | 7969 |  |  |  | 985 | [10 empty] | 91.00 |  |  |  | 91.00 | [5 empty] | 93.15 |  |  | 90.97 |  |  |  | 1.85 |  | 1.72 | [8 empty] | 7.28 |  |  |  |  | 0.00
2006 |  |  |  | 8974.52 |  |  | 8705 |  |  |  | 1025 | [10 empty] | 99.38 |  |  |  | 99.38 | [5 empty] | 99.95 |  |  | 99.37 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 7797.31 |  |  | 7602 |  |  |  | 1025 | [10 empty] | 86.79 |  |  |  | 86.79 | [5 empty] | 86.84 |  |  | 86.78 |  |  |  | 7.00 |  | 6.53 | [8 empty] | 6.68 |  |  |  |  | 0.00
2008 |  |  |  | 9162.73 |  |  | 8784 |  |  |  | 1025 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.77 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 7703.70 |  |  | 7649 |  |  |  | 1040 | [10 empty] | 87.53 |  |  |  | 87.53 | [5 empty] | 84.56 |  |  | 87.32 |  |  |  | 3.16 |  | 2.85 | [8 empty] | 9.62 |  |  |  |  | 0.00
2010 |  |  |  | 8994.71 |  |  | 8676 |  |  |  | 1040 | [10 empty] | 99.04 |  |  |  | 99.04 | [5 empty] | 98.73 |  |  | 99.04 |  |  |  | 0.96 |  | 0.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8217.05 |  |  | 7953 |  |  |  | 1040 | [10 empty] | 90.80 |  |  |  | 90.80 | [5 empty] | 90.19 |  |  | 90.79 |  |  |  | 0.93 |  | 0.85 | [8 empty] | 8.34 |  |  |  |  | 0.00
2012 |  |  |  | 8963.07 |  |  | 8649 |  |  |  | 1040 | [10 empty] | 98.50 |  |  |  | 99.33 | [5 empty] | 98.11 |  |  | 98.46 |  |  |  | 0.37 |  | 0.36 | [8 empty] | 0.30 |  |  |  |  | 0.83
2013 |  |  |  | 8288.93 |  |  | 8025 |  |  |  | 1041 | [10 empty] | 91.62 |  |  |  | 91.62 | [5 empty] | 90.89 |  |  | 91.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.38 |  |  |  |  | 0.00
2014 |  |  |  | 8971.54 |  |  | 8669 |  |  |  | 1040 | [10 empty] | 98.96 |  |  |  | 98.96 | [5 empty] | 98.48 |  |  | 98.96 |  |  |  | 1.04 |  | 1.04 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 7588.92 |  |  | 7440 |  |  |  | 1040 | [10 empty] | 84.92 |  |  |  | 84.92 | [5 empty] | 83.30 |  |  | 84.93 |  |  |  | 6.45 |  | 5.85 | [8 empty] | 9.22 |  |  |  |  | 0.00
2016 |  |  |  | 9069.20 |  |  | 8784 |  |  |  | 1040 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6933.65 |  |  | 6789 |  |  |  | 1040 | [10 empty] | 77.51 |  |  |  | 77.51 | [5 empty] | 76.11 |  |  | 77.50 |  |  |  | 2.02 |  | 1.59 | [8 empty] | 20.90 |  |  |  |  | 0.00
2018 |  |  |  | 8328.02 |  |  | 8098 |  |  |  | 1030 | [10 empty] | 92.44 |  |  |  | 92.44 | [5 empty] | 92.30 |  |  | 92.44 |  |  |  | 7.56 |  | 7.56 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 8342.71 |  |  | 8054 |  |  |  | 1030 | [10 empty] | 91.95 |  |  |  | 91.95 | [5 empty] | 92.46 |  |  | 91.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.05 |  |  |  |  | 0.00
2020 |  |  |  | 9108.82 |  |  | 8783 |  |  |  | 1030 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.68 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1976 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1013
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 942
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 209
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 9
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 4
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
P. |  | Fire | [39 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 0
Z. |  | Other | [39 empty] | 9
Subtotal | [37 empty] | 1153 |  |  |  | 1036 | [11 empty] | 6
Total | [22 empty] | 0 | [14 empty] | 2195
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1976 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 17
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
14. |  |  | Safety Systems | [34 empty] | 466
15. |  |  | Reactor Cooling Systems | [34 empty] | 28
16. |  |  | Steam generation systems | [34 empty] | 58
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 81
32. |  |  | Feedwater and Main Steam System | [34 empty] | 48
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 21
41. |  |  | Main Generator Systems | [34 empty] | 248
42. |  |  | Electrical Power Supply Systems | [34 empty] | 50
Total | [37 empty] | 1026

## LASALLE-1
2020 Operating Experience
US-373 | [8 empty] | LASALLE-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 (Mark 2) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-09-10
Thermal power | [12 empty] | : |  |  | 3546 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-09-04
Gross electrical power | [12 empty] | : |  |  | 1207 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-01-01
Reference unit power (net) | [12 empty] | : |  |  | 1137 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.1
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.41
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.65
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Pond (closed-cycle)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 44 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9535.89 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.98 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.02 %
Load Factor (LF) | [18 empty] | : | 95.48 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 94.97 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 442 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 818.11 | 246.69 |  |  |  | 870.56 |  | 842.11 | [8 empty] | 861.80 |  |  | 823.56 | [6 empty] | 825.19 |  | 839.16 |  |  |  | 825.59 |  |  | 867.54 |  |  | 844.26 | [9 empty] | 871.34 |  |  | 9535.89
EAF [%] |  |  |  |  | 100.00 | 36.60 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.98
UCF [%] |  |  |  |  | 100.00 | 36.60 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.98
LF [%] |  |  |  |  | 96.71 | 31.17 |  |  |  | 102.91 |  | 102.87 | [8 empty] | 101.88 |  |  | 100.60 | [6 empty] | 97.55 |  | 99.20 |  |  |  | 100.85 |  |  | 102.55 |  |  | 103.13 | [9 empty] | 103.00 |  |  | 95.48
OF [%] |  |  |  |  | 100.00 | 36.64 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.97
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 63.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.02
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 263086.78 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.99 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.12 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.89 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.78 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.44 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 5206.21 |  |  | 6052 |  |  |  | 1078 | [10 empty] | 69.43 |  |  |  | 69.43 | [5 empty] | 54.99 |  |  | 68.91 |  |  |  | 16.31 |  | 13.53 | [8 empty] | 17.04 |  |  |  |  | 0.00
1985 |  |  |  | 4827.46 |  |  | 5581 |  |  |  | 1036 | [10 empty] | 63.69 |  |  |  | 64.26 | [5 empty] | 53.19 |  |  | 63.71 |  |  |  | 19.25 |  | 15.32 | [8 empty] | 20.42 |  |  |  |  | 0.57
1986 |  |  |  | 2100.75 |  |  | 2331 |  |  |  | 1036 | [10 empty] | 25.78 |  |  |  | 25.78 | [5 empty] | 23.15 |  |  | 26.61 |  |  |  | 2.65 |  | 0.70 | [8 empty] | 73.52 |  |  |  |  | 0.00
1987 |  |  |  | 4108.12 |  |  | 5455 |  |  |  | 1036 | [10 empty] | 61.89 |  |  |  | 61.89 | [5 empty] | 45.27 |  |  | 62.27 |  |  |  | 38.11 |  | 38.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 5453.67 |  |  | 5818 |  |  |  | 1036 | [10 empty] | 65.86 |  |  |  | 65.86 | [5 empty] | 59.93 |  |  | 66.23 |  |  |  | 2.49 |  | 1.68 | [8 empty] | 32.45 |  |  |  |  | 0.00
1989 |  |  |  | 6180.58 |  |  | 6103 |  |  |  | 1036 | [10 empty] | 69.67 |  |  |  | 69.67 | [5 empty] | 68.10 |  |  | 69.67 |  |  |  | 1.37 |  | 0.97 | [8 empty] | 29.36 |  |  |  |  | 0.00
1990 |  |  |  | 8637.38 |  |  | 8329 |  |  |  | 1036 | [10 empty] | 95.02 |  |  |  | 95.02 | [5 empty] | 95.17 |  |  | 95.08 |  |  |  | 1.85 |  | 1.79 | [8 empty] | 3.19 |  |  |  |  | 0.00
1991 |  |  |  | 6841.44 |  |  | 6627 |  |  |  | 1036 | [10 empty] | 75.39 |  |  |  | 75.39 | [5 empty] | 75.38 |  |  | 75.65 |  |  |  | 2.23 |  | 1.72 | [8 empty] | 22.89 |  |  |  |  | 0.00
1992 |  |  |  | 6469.28 |  |  | 6528 |  |  |  | 1036 | [10 empty] | 74.04 |  |  |  | 74.04 | [5 empty] | 71.09 |  |  | 74.32 |  |  |  | 1.44 |  | 1.08 | [8 empty] | 24.87 |  |  |  |  | 0.00
1993 |  |  |  | 7207.51 |  |  | 7102 |  |  |  | 1036 | [10 empty] | 80.97 |  |  |  | 80.97 | [5 empty] | 79.42 |  |  | 81.07 |  |  |  | 11.79 |  | 10.82 | [8 empty] | 8.21 |  |  |  |  | 0.00
1994 |  |  |  | 4945.32 |  |  | 5095 |  |  |  | 1036 | [10 empty] | 57.78 |  |  |  | 57.78 | [5 empty] | 54.49 |  |  | 58.16 |  |  |  | 16.78 |  | 11.65 | [8 empty] | 30.57 |  |  |  |  | 0.00
1995 |  |  |  | 8239.56 |  |  | 8226 |  |  |  | 1036 | [10 empty] | 93.88 |  |  |  | 93.88 | [5 empty] | 90.79 |  |  | 93.90 |  |  |  | 6.12 |  | 6.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 3300.36 |  |  | 3349 |  |  |  | 1036 | [10 empty] | 37.48 |  |  |  | 37.48 | [5 empty] | 36.27 |  |  | 38.13 |  |  |  | 30.53 |  | 16.47 | [8 empty] | 46.05 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1036 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1998 |  |  |  | 3336.67 |  |  | 3174 |  |  |  | 1036 | [10 empty] | 36.27 |  |  |  | 36.27 | [5 empty] | 36.77 |  |  | 36.23 |  |  |  | 63.06 |  | 61.91 | [8 empty] | 1.82 |  |  |  |  | 0.00
1999 |  |  |  | 8013.68 |  |  | 7963 |  |  |  | 1036 | [10 empty] | 90.81 |  |  |  | 90.81 | [5 empty] | 88.30 |  |  | 90.90 |  |  |  | 0.75 |  | 0.69 | [8 empty] | 8.50 |  |  |  |  | 0.00
2000 |  |  |  | 9745.39 |  |  | 8784 |  |  |  | 1114 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.81 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 9850.36 |  |  | 8708 |  |  |  | 1111 | [10 empty] | 99.42 |  |  |  | 99.42 | [5 empty] | 101.01 |  |  | 99.41 |  |  |  | 0.58 |  | 0.58 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 8927.60 |  |  | 7945 |  |  |  | 1111 | [10 empty] | 90.57 |  |  |  | 90.57 | [5 empty] | 91.73 |  |  | 90.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.43 |  |  |  |  | 0.00
2003 |  |  |  | 9739.03 |  |  | 8716 |  |  |  | 1111 | [10 empty] | 99.50 |  |  |  | 99.50 | [5 empty] | 100.07 |  |  | 99.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.50 |  |  |  |  | 0.00
2004 |  |  |  | 9051.53 |  |  | 8059 |  |  |  | 1111 | [10 empty] | 91.50 |  |  |  | 91.50 | [5 empty] | 92.75 |  |  | 91.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.50 |  |  |  |  | 0.00
2005 |  |  |  | 9811.96 |  |  | 8760 |  |  |  | 1146 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.73 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 9092.07 |  |  | 8129 |  |  |  | 1118 | [10 empty] | 92.81 |  |  |  | 92.81 | [5 empty] | 92.84 |  |  | 92.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.19 |  |  |  |  | 0.00
2007 |  |  |  | 9664.63 |  |  | 8760 |  |  |  | 1118 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.68 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8883.77 |  |  | 8103 |  |  |  | 1118 | [10 empty] | 92.26 |  |  |  | 92.26 | [5 empty] | 90.46 |  |  | 92.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.74 |  |  |  |  | 0.00
2009 |  |  |  | 9700.71 |  |  | 8580 |  |  |  | 1118 | [10 empty] | 97.95 |  |  |  | 97.95 | [5 empty] | 99.05 |  |  | 97.95 |  |  |  | 1.10 |  | 1.09 | [8 empty] | 0.96 |  |  |  |  | 0.00
2010 |  |  |  | 9207.03 |  |  | 8119 |  |  |  | 1118 | [10 empty] | 92.69 |  |  |  | 92.69 | [5 empty] | 94.01 |  |  | 92.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.31 |  |  |  |  | 0.00
2011 |  |  |  | 9851.68 |  |  | 8529 |  |  |  | 1118 | [10 empty] | 97.37 |  |  |  | 97.37 | [5 empty] | 100.59 |  |  | 97.36 |  |  |  | 2.63 |  | 2.63 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 9471.23 |  |  | 8213 |  |  |  | 1137 | [10 empty] | 93.60 |  |  |  | 93.60 | [5 empty] | 95.09 |  |  | 93.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.40 |  |  |  |  | 0.00
2013 |  |  |  | 9774.52 |  |  | 8465 |  |  |  | 1137 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.13 |  |  | 96.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 9267.74 |  |  | 8092 |  |  |  | 1137 | [10 empty] | 92.37 |  |  |  | 92.37 | [5 empty] | 93.05 |  |  | 92.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.63 |  |  |  |  | 0.00
2015 |  |  |  | 10153.40 |  |  | 8760 |  |  |  | 1137 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.94 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 9054.09 |  |  | 8019 |  |  |  | 1137 | [10 empty] | 91.29 |  |  |  | 91.29 | [5 empty] | 90.66 |  |  | 91.29 |  |  |  | 2.29 |  | 2.14 | [8 empty] | 6.56 |  |  |  |  | 0.00
2017 |  |  |  | 9856.32 |  |  | 8541 |  |  |  | 1137 | [10 empty] | 97.51 |  |  |  | 97.51 | [5 empty] | 98.96 |  |  | 97.50 |  |  |  | 2.49 |  | 2.49 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 9347.13 |  |  | 8117 |  |  |  | 1137 | [10 empty] | 92.83 |  |  |  | 92.83 | [5 empty] | 93.85 |  |  | 92.66 |  |  |  | 0.88 |  | 0.83 | [8 empty] | 6.34 |  |  |  |  | 0.00
2019 |  |  |  | 10026.81 |  |  | 8680 |  |  |  | 1137 | [10 empty] | 99.10 |  |  |  | 99.10 | [5 empty] | 100.67 |  |  | 99.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.90 |  |  |  |  | 0.00
2020 |  |  |  | 9535.89 |  |  | 8342 |  |  |  | 1137 | [10 empty] | 94.98 |  |  |  | 94.98 | [5 empty] | 95.48 |  |  | 94.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.02 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 351
B. |  | Refuelling without maintenance | [20 empty] | 441 | [14 empty] | 12
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 833
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 313
E. |  | Testing of plant systems or components | [35 empty] | 42 |  |  |  | 3
H. |  | Nuclear regulatory requirements | [39 empty] | 145
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 9
L. |  | Human factor related | [39 empty] | 26
Z. |  | Other | [39 empty] | 4
Subtotal | [22 empty] | 441 | [14 empty] | 1200 |  |  |  | 529 | [11 empty] | 9
Total | [22 empty] | 441 | [14 empty] | 1738
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 29
12. |  |  | Reactor I&C Systems | [34 empty] | 25
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 34
15. |  |  | Reactor Cooling Systems | [34 empty] | 101
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 76
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 11
35. |  |  | All other I&C Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 12
42. |  |  | Electrical Power Supply Systems | [34 empty] | 33
Total | [37 empty] | 356
Highlights (2020)
Refueling Outage 18

## LASALLE-2
2020 Operating Experience
US-374 | [8 empty] | LASALLE-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 (Mark 2) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-09-10
Thermal power | [12 empty] | : |  |  | 3546 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-04-20
Gross electrical power | [12 empty] | : |  |  | 1207 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-10-19
Reference unit power (net) | [12 empty] | : |  |  | 1140 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.1
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.41
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.65
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Pond (closed-cycle)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 44 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10159.8 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.46 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 873.40 | 817.34 |  |  |  | 868.79 |  | 841.41 | [8 empty] | 857.28 |  |  | 822.32 | [6 empty] | 836.36 |  | 842.31 |  |  |  | 824.28 |  |  | 864.89 |  |  | 841.68 | [9 empty] | 869.73 |  |  | 10159.80
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 102.98 | 103.01 |  |  |  | 102.43 |  | 102.51 | [8 empty] | 101.08 |  |  | 100.18 | [6 empty] | 98.61 |  | 99.31 |  |  |  | 100.42 |  |  | 101.97 |  |  | 102.54 | [9 empty] | 102.54 |  |  | 101.46
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 282402.49 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.72 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.68 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.88 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.69 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.42 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.89 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.02 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 2735.73 |  |  | 4058 |  |  |  | 1039 | [10 empty] | 86.57 |  |  |  | 86.57 | [5 empty] | 77.10 |  |  | 86.68 |  |  |  | 13.43 |  | 13.43 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 3476.96 |  |  | 3698 |  |  |  | 1036 | [10 empty] | 41.81 |  |  |  | 41.81 | [5 empty] | 38.31 |  |  | 42.21 |  |  |  | 30.40 |  | 18.26 | [8 empty] | 39.93 |  |  |  |  | 0.00
1986 |  |  |  | 5727.77 |  |  | 6533 |  |  |  | 1036 | [10 empty] | 74.58 |  |  |  | 75.00 | [5 empty] | 63.11 |  |  | 74.58 |  |  |  | 24.61 |  | 24.49 | [8 empty] | 0.51 |  |  |  |  | 0.43
1987 |  |  |  | 4573.28 |  |  | 4699 |  |  |  | 1036 | [10 empty] | 53.13 |  |  |  | 53.13 | [5 empty] | 50.39 |  |  | 53.64 |  |  |  | 1.67 |  | 0.90 | [8 empty] | 45.97 |  |  |  |  | 0.00
1988 |  |  |  | 5662.76 |  |  | 6593 |  |  |  | 1036 | [10 empty] | 75.07 |  |  |  | 75.07 | [5 empty] | 62.23 |  |  | 75.06 |  |  |  | 4.26 |  | 3.34 | [8 empty] | 21.59 |  |  |  |  | 0.00
1989 |  |  |  | 6506.76 |  |  | 6591 |  |  |  | 1036 | [10 empty] | 75.13 |  |  |  | 75.13 | [5 empty] | 71.70 |  |  | 75.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.87 |  |  |  |  | 0.00
1990 |  |  |  | 6216.77 |  |  | 6162 |  |  |  | 1036 | [10 empty] | 70.01 |  |  |  | 70.01 | [5 empty] | 68.50 |  |  | 70.34 |  |  |  | 7.34 |  | 5.55 | [8 empty] | 24.45 |  |  |  |  | 0.00
1991 |  |  |  | 8712.41 |  |  | 8357 |  |  |  | 1036 | [10 empty] | 95.35 |  |  |  | 95.35 | [5 empty] | 96.00 |  |  | 95.40 |  |  |  | 4.65 |  | 4.65 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 5797.87 |  |  | 5850 |  |  |  | 1036 | [10 empty] | 66.28 |  |  |  | 66.28 | [5 empty] | 63.71 |  |  | 66.60 |  |  |  | 8.49 |  | 6.15 | [8 empty] | 27.57 |  |  |  |  | 0.00
1993 |  |  |  | 5859.19 |  |  | 5825 |  |  |  | 1036 | [10 empty] | 66.12 |  |  |  | 66.12 | [5 empty] | 64.56 |  |  | 66.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.88 |  |  |  |  | 0.00
1994 |  |  |  | 8428.87 |  |  | 8101 |  |  |  | 1036 | [10 empty] | 92.44 |  |  |  | 92.44 | [5 empty] | 92.88 |  |  | 92.48 |  |  |  | 4.45 |  | 4.31 | [8 empty] | 3.26 |  |  |  |  | 0.00
1995 |  |  |  | 5905.70 |  |  | 5855 |  |  |  | 1036 | [10 empty] | 66.49 |  |  |  | 66.49 | [5 empty] | 65.07 |  |  | 66.84 |  |  |  | 3.18 |  | 2.18 | [8 empty] | 31.33 |  |  |  |  | 0.00
1996 |  |  |  | 5642.33 |  |  | 5649 |  |  |  | 1036 | [10 empty] | 64.50 |  |  |  | 64.50 | [5 empty] | 62.00 |  |  | 64.31 |  |  |  | 10.53 |  | 7.59 | [8 empty] | 27.92 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1036 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1998 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1036 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 6632.33 |  |  | 6231 |  |  |  | 1036 | [10 empty] | 71.11 |  |  |  | 71.11 | [5 empty] | 73.08 |  |  | 71.13 |  |  |  | 28.89 |  | 28.89 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 9040.45 |  |  | 8229 |  |  |  | 1114 | [10 empty] | 93.08 |  |  |  | 93.08 | [5 empty] | 95.97 |  |  | 93.68 |  |  |  | 0.81 |  | 0.76 | [8 empty] | 6.17 |  |  |  |  | 0.00
2001 |  |  |  | 9683.43 |  |  | 8515 |  |  |  | 1111 | [10 empty] | 97.18 |  |  |  | 97.18 | [5 empty] | 99.30 |  |  | 97.20 |  |  |  | 2.82 |  | 2.82 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 8995.59 |  |  | 8078 |  |  |  | 1111 | [10 empty] | 92.09 |  |  |  | 92.09 | [5 empty] | 92.43 |  |  | 92.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.91 |  |  |  |  | 0.00
2003 |  |  |  | 8709.05 |  |  | 7762 |  |  |  | 1111 | [10 empty] | 88.43 |  |  |  | 88.43 | [5 empty] | 89.49 |  |  | 88.61 |  |  |  | 3.07 |  | 2.80 | [8 empty] | 8.77 |  |  |  |  | 0.00
2004 |  |  |  | 9940.43 |  |  | 8764 |  |  |  | 1111 | [10 empty] | 99.77 |  |  |  | 99.77 | [5 empty] | 101.86 |  |  | 99.77 |  |  |  | 0.23 |  | 0.23 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 8901.22 |  |  | 7857 |  |  |  | 1147 | [10 empty] | 89.71 |  |  |  | 89.71 | [5 empty] | 88.58 |  |  | 89.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.29 |  |  |  |  | 0.00
2006 |  |  |  | 10015.75 |  |  | 8760 |  |  |  | 1120 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.08 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 9315.51 |  |  | 8287 |  |  |  | 1120 | [10 empty] | 94.61 |  |  |  | 94.61 | [5 empty] | 94.95 |  |  | 94.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.39 |  |  |  |  | 0.00
2008 |  |  |  | 9964.59 |  |  | 8784 |  |  |  | 1120 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.29 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 9108.04 |  |  | 8058 |  |  |  | 1120 | [10 empty] | 92.01 |  |  |  | 92.01 | [5 empty] | 92.83 |  |  | 91.99 |  |  |  | 2.07 |  | 1.95 | [8 empty] | 6.04 |  |  |  |  | 0.00
2010 |  |  |  | 9925.54 |  |  | 8760 |  |  |  | 1120 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.17 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 9404.75 |  |  | 8238 |  |  |  | 1140 | [10 empty] | 94.14 |  |  |  | 94.14 | [5 empty] | 94.44 |  |  | 94.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.86 |  |  |  |  | 0.00
2012 |  |  |  | 10123.73 |  |  | 8784 |  |  |  | 1140 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.10 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 8985.77 |  |  | 7962 |  |  |  | 1140 | [10 empty] | 92.90 |  |  |  | 92.90 | [5 empty] | 89.97 |  |  | 90.88 |  |  |  | 1.43 |  | 1.34 | [8 empty] | 5.76 |  |  |  |  | 0.00
2014 |  |  |  | 9487.27 |  |  | 8228 |  |  |  | 1140 | [10 empty] | 93.93 |  |  |  | 93.93 | [5 empty] | 95.00 |  |  | 93.93 |  |  |  | 3.52 |  | 3.43 | [8 empty] | 2.64 |  |  |  |  | 0.00
2015 |  |  |  | 8530.63 |  |  | 7955 |  |  |  | 1140 | [10 empty] | 90.81 |  |  |  | 90.81 | [5 empty] | 85.42 |  |  | 90.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.19 |  |  |  |  | 0.00
2016 |  |  |  | 10090.77 |  |  | 8784 |  |  |  | 1140 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.77 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 9052.14 |  |  | 7877 |  |  |  | 1140 | [10 empty] | 89.92 |  |  |  | 89.92 | [5 empty] | 90.64 |  |  | 89.92 |  |  |  | 0.77 |  | 0.70 | [8 empty] | 9.38 |  |  |  |  | 0.00
2018 |  |  |  | 10053.26 |  |  | 8687 |  |  |  | 1140 | [10 empty] | 99.19 |  |  |  | 99.19 | [5 empty] | 100.67 |  |  | 99.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.81 |  |  |  |  | 0.00
2019 |  |  |  | 9408.48 |  |  | 8290 |  |  |  | 1140 | [10 empty] | 94.64 |  |  |  | 94.64 | [5 empty] | 94.21 |  |  | 94.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.36 |  |  |  |  | 0.00
2020 |  |  |  | 10159.80 |  |  | 8783 |  |  |  | 1140 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.46 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 205
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 940
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 145
E. |  | Testing of plant systems or components | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 312
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 6
Z. |  | Other | [39 empty] | 49
Subtotal | [37 empty] | 1086 |  |  |  | 572 | [11 empty] | 6
Total | [22 empty] | 0 | [14 empty] | 1664
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 50
12. |  |  | Reactor I&C Systems | [34 empty] | 46
15. |  |  | Reactor Cooling Systems | [34 empty] | 20
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 39
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 15
35. |  |  | All other I&C Systems | [34 empty] | 9
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 17
Total | [37 empty] | 208

## LIMERICK-1
2020 Operating Experience
US-352 | [8 empty] | LIMERICK-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 2) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-06-19
Thermal power | [12 empty] | : |  |  | 3515 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-04-13
Gross electrical power | [12 empty] | : |  |  | 1194 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-02-01
Reference unit power (net) | [12 empty] | : |  |  | 1134 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.1
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 282
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.38
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.57 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.65
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9133.2 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.29 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.3 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.24 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.3 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.47 %
Load Factor (LF) | [18 empty] | : | 91.69 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 94.3 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 501 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 837.88 | 704.76 |  |  |  | 569.59 |  | 472.15 | [8 empty] | 862.23 |  |  | 824.20 | [6 empty] | 842.06 |  | 845.29 |  |  |  | 785.94 |  |  | 863.90 |  |  | 696.97 | [9 empty] | 828.22 |  |  | 9133.19
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 87.13 |  | 58.82 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 84.91 | [9 empty] | 100.00 |  |  | 94.30
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 87.13 |  | 58.82 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 84.91 | [9 empty] | 100.00 |  |  | 94.30
LF [%] |  |  |  |  | 99.31 | 89.29 |  |  |  | 67.51 |  | 57.83 | [8 empty] | 102.20 |  |  | 100.95 | [6 empty] | 99.81 |  | 100.19 |  |  |  | 96.26 |  |  | 102.39 |  |  | 85.36 | [9 empty] | 98.17 |  |  | 91.69
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 86.96 |  | 58.89 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 85.00 | [9 empty] | 100.00 |  |  | 94.30
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 15.09 | [9 empty] | 0.00 |  |  | 1.29
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 15.09 | [9 empty] | 0.00 |  |  | 1.24
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 12.87 |  | 41.18 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.47
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 346368.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.74 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.63 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.63 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.63 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.75 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.78 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.24 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 7210.57 |  |  | 7022 |  |  |  | 1055 | [10 empty] | 82.79 |  |  |  | 82.79 | [5 empty] | 80.99 |  |  | 82.76 |  |  |  | 3.46 |  | 2.97 | [8 empty] | 14.25 |  |  |  |  | 0.00
1987 |  |  |  | 5341.32 |  |  | 5924 |  |  |  | 1055 | [10 empty] | 67.66 |  |  |  | 67.66 | [5 empty] | 57.80 |  |  | 67.63 |  |  |  | 4.11 |  | 2.90 | [8 empty] | 29.44 |  |  |  |  | 0.00
1988 |  |  |  | 6674.75 |  |  | 8470 |  |  |  | 1055 | [10 empty] | 96.43 |  |  |  | 96.43 | [5 empty] | 72.03 |  |  | 96.43 |  |  |  | 3.57 |  | 3.57 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 5244.25 |  |  | 5638 |  |  |  | 1055 | [10 empty] | 69.36 |  |  |  | 69.36 | [5 empty] | 56.74 |  |  | 64.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.64 |  |  |  |  | 0.00
1990 |  |  |  | 5633.12 |  |  | 5724 |  |  |  | 1055 | [10 empty] | 65.34 |  |  |  | 65.34 | [5 empty] | 60.95 |  |  | 65.34 |  |  |  | 6.61 |  | 4.62 | [8 empty] | 30.03 |  |  |  |  | 0.00
1991 |  |  |  | 8133.85 |  |  | 8043 |  |  |  | 1055 | [10 empty] | 91.83 |  |  |  | 91.83 | [5 empty] | 88.01 |  |  | 91.82 |  |  |  | 8.17 |  | 8.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 6239.64 |  |  | 6115 |  |  |  | 1055 | [10 empty] | 69.63 |  |  |  | 69.63 | [5 empty] | 67.33 |  |  | 69.62 |  |  |  | 0.10 |  | 0.07 | [8 empty] | 30.31 |  |  |  |  | 0.00
1993 |  |  |  | 8745.47 |  |  | 8626 |  |  |  | 1055 | [10 empty] | 98.48 |  |  |  | 98.48 | [5 empty] | 94.63 |  |  | 98.47 |  |  |  | 1.52 |  | 1.52 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 7858.02 |  |  | 7840 |  |  |  | 1055 | [10 empty] | 89.52 |  |  |  | 89.52 | [5 empty] | 85.03 |  |  | 89.50 |  |  |  | 0.86 |  | 0.78 | [8 empty] | 9.70 |  |  |  |  | 0.00
1995 |  |  |  | 8147.47 |  |  | 7973 |  |  |  | 1055 | [10 empty] | 91.06 |  |  |  | 91.06 | [5 empty] | 88.16 |  |  | 91.02 |  |  |  | 7.90 |  | 7.81 | [8 empty] | 1.13 |  |  |  |  | 0.00
1996 |  |  |  | 8141.62 |  |  | 7758 |  |  |  | 1096 | [10 empty] | 88.83 |  |  |  | 88.83 | [5 empty] | 84.51 |  |  | 88.32 |  |  |  | 3.15 |  | 2.89 | [8 empty] | 8.28 |  |  |  |  | 0.00
1997 |  |  |  | 9227.48 |  |  | 8534 |  |  |  | 1105 | [10 empty] | 97.54 |  |  |  | 97.54 | [5 empty] | 95.33 |  |  | 97.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.46 |  |  |  |  | 0.00
1998 |  |  |  | 7449.12 |  |  | 7061 |  |  |  | 1112 | [10 empty] | 81.62 |  |  |  | 81.62 | [5 empty] | 76.45 |  |  | 80.61 |  |  |  | 8.24 |  | 7.33 | [8 empty] | 11.04 |  |  |  |  | 0.00
1999 |  |  |  | 9744.01 |  |  | 8588 |  |  |  | 1134 | [10 empty] | 98.05 |  |  |  | 98.05 | [5 empty] | 98.09 |  |  | 98.04 |  |  |  | 1.95 |  | 1.95 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 8988.10 |  |  | 7982 |  |  |  | 1143 | [10 empty] | 90.94 |  |  |  | 90.94 | [5 empty] | 89.82 |  |  | 90.87 |  |  |  | 1.04 |  | 0.96 | [8 empty] | 8.10 |  |  |  |  | 0.00
2001 |  |  |  | 10133.10 |  |  | 8735 |  |  |  | 1143 | [10 empty] | 99.73 |  |  |  | 99.73 | [5 empty] | 101.20 |  |  | 99.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.27 |  |  |  |  | 0.00
2002 |  |  |  | 9286.82 |  |  | 8244 |  |  |  | 1134 | [10 empty] | 94.07 |  |  |  | 94.07 | [5 empty] | 93.49 |  |  | 94.11 |  |  |  | 1.20 |  | 1.14 | [8 empty] | 4.78 |  |  |  |  | 0.00
2003 |  |  |  | 10057.46 |  |  | 8672 |  |  |  | 1134 | [10 empty] | 99.00 |  |  |  | 99.00 | [5 empty] | 101.24 |  |  | 99.00 |  |  |  | 1.00 |  | 1.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 9539.06 |  |  | 8345 |  |  |  | 1134 | [10 empty] | 95.01 |  |  |  | 95.01 | [5 empty] | 95.76 |  |  | 95.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.99 |  |  |  |  | 0.00
2005 |  |  |  | 9926.94 |  |  | 8642 |  |  |  | 1134 | [10 empty] | 98.67 |  |  |  | 98.67 | [5 empty] | 99.92 |  |  | 98.64 |  |  |  | 0.45 |  | 0.45 | [8 empty] | 0.89 |  |  |  |  | 0.00
2006 |  |  |  | 9320.36 |  |  | 8224 |  |  |  | 1134 | [10 empty] | 93.90 |  |  |  | 93.90 | [5 empty] | 93.82 |  |  | 93.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.10 |  |  |  |  | 0.00
2007 |  |  |  | 9994.36 |  |  | 8744 |  |  |  | 1134 | [10 empty] | 99.82 |  |  |  | 99.82 | [5 empty] | 100.61 |  |  | 99.82 |  |  |  | 0.18 |  | 0.18 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 9342.51 |  |  | 8251 |  |  |  | 1134 | [10 empty] | 93.94 |  |  |  | 93.94 | [5 empty] | 93.79 |  |  | 93.93 |  |  |  | 0.63 |  | 0.59 | [8 empty] | 5.47 |  |  |  |  | 0.00
2009 |  |  |  | 10019.44 |  |  | 8760 |  |  |  | 1130 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.22 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 9046.94 |  |  | 8129 |  |  |  | 1130 | [10 empty] | 92.81 |  |  |  | 92.81 | [5 empty] | 91.39 |  |  | 92.80 |  |  |  | 1.02 |  | 0.96 | [8 empty] | 6.23 |  |  |  |  | 0.00
2011 |  |  |  | 9550.19 |  |  | 8435 |  |  |  | 1130 | [10 empty] | 96.29 |  |  |  | 96.29 | [5 empty] | 96.48 |  |  | 96.29 |  |  |  | 0.88 |  | 0.85 | [8 empty] | 2.86 |  |  |  |  | 0.00
2012 |  |  |  | 8599.50 |  |  | 7637 |  |  |  | 1130 | [10 empty] | 86.99 |  |  |  | 86.99 | [5 empty] | 86.64 |  |  | 86.94 |  |  |  | 2.80 |  | 2.51 | [8 empty] | 10.50 |  |  |  |  | 0.00
2013 |  |  |  | 10147.12 |  |  | 8760 |  |  |  | 1130 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.50 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 9112.31 |  |  | 7926 |  |  |  | 1130 | [10 empty] | 90.48 |  |  |  | 90.48 | [5 empty] | 92.05 |  |  | 90.48 |  |  |  | 3.50 |  | 3.28 | [8 empty] | 6.24 |  |  |  |  | 0.00
2015 |  |  |  | 10037.82 |  |  | 8718 |  |  |  | 1130 | [10 empty] | 99.52 |  |  |  | 99.52 | [5 empty] | 101.40 |  |  | 99.52 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 9294.59 |  |  | 8132 |  |  |  | 1130 | [10 empty] | 92.58 |  |  |  | 92.58 | [5 empty] | 93.64 |  |  | 92.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.42 |  |  |  |  | 0.00
2017 |  |  |  | 10023.55 |  |  | 8760 |  |  |  | 1130 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.26 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 9228.95 |  |  | 8197 |  |  |  | 1099 | [10 empty] | 93.57 |  |  |  | 93.57 | [5 empty] | 95.86 |  |  | 93.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.43 |  |  |  |  | 0.00
2019 |  |  |  | 10112.18 |  |  | 8760 |  |  |  | 1134 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.80 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9133.19 |  |  | 8283 |  |  |  | 1134 | [10 empty] | 94.30 |  |  |  | 94.30 | [5 empty] | 91.69 |  |  | 94.30 |  |  |  | 1.29 |  | 1.24 | [8 empty] | 4.47 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 132
B. |  | Refuelling without maintenance | [20 empty] | 784 | [14 empty] | 22
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 577
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 177
E. |  | Testing of plant systems or components | [35 empty] | 9 |  |  |  | 9
Z. |  | Other | [24 empty] | 109 | [10 empty] | 75 |  |  |  | 29
Subtotal | [22 empty] | 784 |  |  |  | 109 | [10 empty] | 860 |  |  |  | 170
Total | [22 empty] | 893 | [14 empty] | 1030
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 8
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 27
31. |  |  | Turbine and auxiliaries | [34 empty] | 46
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 10
41. |  |  | Main Generator Systems | [34 empty] | 8
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [37 empty] | 144
Highlights (2020)
Rx Scram, MSIV failed closed

## LIMERICK-2
2020 Operating Experience
US-353 | [8 empty] | LIMERICK-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXELCORP (Exelon Corporation )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 2) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-06-19
Thermal power | [12 empty] | : |  |  | 3515 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1989-09-01
Gross electrical power | [12 empty] | : |  |  | 1194 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-01-08
Reference unit power (net) | [12 empty] | : |  |  | 1134 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.1
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 282
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.38
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.57 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.65
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10211.57 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 102.51 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 881.04 | 824.59 |  |  |  | 874.46 |  | 846.85 | [8 empty] | 866.62 |  |  | 813.31 | [6 empty] | 845.80 |  | 848.59 |  |  |  | 828.81 |  |  | 867.01 |  |  | 844.73 | [9 empty] | 869.76 |  |  | 10211.57
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 104.43 | 104.48 |  |  |  | 103.65 |  | 103.72 | [8 empty] | 102.72 |  |  | 99.61 | [6 empty] | 100.25 |  | 100.58 |  |  |  | 101.51 |  |  | 102.76 |  |  | 103.46 | [9 empty] | 103.09 |  |  | 102.51
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 270690.78 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.39 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 93.75 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.77 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 4.9 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 93.21 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 93.79 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 7232.60 |  |  | 7174 |  |  |  | 1055 | [10 empty] | 81.81 |  |  |  | 81.81 | [5 empty] | 79.79 |  |  | 83.50 |  |  |  | 13.12 |  | 12.35 | [8 empty] | 5.84 |  |  |  |  | 0.00
1991 |  |  |  | 7146.91 |  |  | 6919 |  |  |  | 1055 | [10 empty] | 77.82 |  |  |  | 77.82 | [5 empty] | 77.33 |  |  | 78.98 |  |  |  | 0.55 |  | 0.43 | [8 empty] | 21.74 |  |  |  |  | 0.00
1992 |  |  |  | 8489.18 |  |  | 8557 |  |  |  | 1055 | [10 empty] | 97.42 |  |  |  | 97.42 | [5 empty] | 91.61 |  |  | 97.42 |  |  |  | 2.58 |  | 2.58 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 7468.72 |  |  | 7289 |  |  |  | 1055 | [10 empty] | 82.26 |  |  |  | 82.26 | [5 empty] | 80.81 |  |  | 83.21 |  |  |  | 2.60 |  | 2.20 | [8 empty] | 15.54 |  |  |  |  | 0.00
1994 |  |  |  | 8571.51 |  |  | 8657 |  |  |  | 1055 | [10 empty] | 98.78 |  |  |  | 98.78 | [5 empty] | 92.75 |  |  | 98.82 |  |  |  | 1.22 |  | 1.22 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 8401.43 |  |  | 7984 |  |  |  | 1110 | [10 empty] | 91.17 |  |  |  | 91.17 | [5 empty] | 86.41 |  |  | 91.14 |  |  |  | 2.66 |  | 2.49 | [8 empty] | 6.34 |  |  |  |  | 0.00
1996 |  |  |  | 9001.10 |  |  | 8346 |  |  |  | 1115 | [10 empty] | 95.08 |  |  |  | 95.72 | [5 empty] | 91.90 |  |  | 95.01 |  |  |  | 4.28 |  | 4.28 | [8 empty] | 0.00 |  |  |  |  | 0.64
1997 |  |  |  | 8307.46 |  |  | 7840 |  |  |  | 1115 | [10 empty] | 89.33 |  |  |  | 89.33 | [5 empty] | 85.05 |  |  | 89.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.67 |  |  |  |  | 0.00
1998 |  |  |  | 9257.88 |  |  | 8346 |  |  |  | 1115 | [10 empty] | 95.30 |  |  |  | 95.30 | [5 empty] | 94.78 |  |  | 95.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.70 |  |  |  |  | 0.00
1999 |  |  |  | 8560.96 |  |  | 7726 |  |  |  | 1135 | [10 empty] | 88.42 |  |  |  | 88.42 | [5 empty] | 86.06 |  |  | 88.20 |  |  |  | 1.25 |  | 1.12 | [8 empty] | 10.46 |  |  |  |  | 0.00
2000 |  |  |  | 9940.73 |  |  | 8661 |  |  |  | 1145 | [10 empty] | 98.64 |  |  |  | 98.64 | [5 empty] | 98.76 |  |  | 98.60 |  |  |  | 1.36 |  | 1.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 9243.35 |  |  | 8230 |  |  |  | 1143 | [10 empty] | 93.93 |  |  |  | 93.93 | [5 empty] | 92.32 |  |  | 93.95 |  |  |  | 1.60 |  | 1.53 | [8 empty] | 4.55 |  |  |  |  | 0.00
2002 |  |  |  | 10009.52 |  |  | 8672 |  |  |  | 1134 | [10 empty] | 98.99 |  |  |  | 98.99 | [5 empty] | 100.76 |  |  | 99.00 |  |  |  | 1.01 |  | 1.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 9387.12 |  |  | 8252 |  |  |  | 1134 | [10 empty] | 94.21 |  |  |  | 94.21 | [5 empty] | 94.50 |  |  | 94.20 |  |  |  | 0.37 |  | 0.35 | [8 empty] | 5.44 |  |  |  |  | 0.00
2004 |  |  |  | 9952.00 |  |  | 8734 |  |  |  | 1134 | [10 empty] | 99.43 |  |  |  | 99.43 | [5 empty] | 99.91 |  |  | 99.43 |  |  |  | 0.57 |  | 0.57 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 9124.68 |  |  | 8085 |  |  |  | 1134 | [10 empty] | 92.31 |  |  |  | 92.31 | [5 empty] | 91.85 |  |  | 92.29 |  |  |  | 0.77 |  | 0.71 | [8 empty] | 6.98 |  |  |  |  | 0.00
2006 |  |  |  | 10015.11 |  |  | 8710 |  |  |  | 1134 | [10 empty] | 99.43 |  |  |  | 99.43 | [5 empty] | 100.82 |  |  | 99.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.57 |  |  |  |  | 0.00
2007 |  |  |  | 9059.17 |  |  | 8007 |  |  |  | 1134 | [10 empty] | 91.42 |  |  |  | 91.42 | [5 empty] | 91.20 |  |  | 91.40 |  |  |  | 0.77 |  | 0.71 | [8 empty] | 7.87 |  |  |  |  | 0.00
2008 |  |  |  | 9712.13 |  |  | 8517 |  |  |  | 1134 | [10 empty] | 96.97 |  |  |  | 96.97 | [5 empty] | 97.50 |  |  | 96.96 |  |  |  | 3.03 |  | 3.03 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 9311.40 |  |  | 8241 |  |  |  | 1134 | [10 empty] | 94.09 |  |  |  | 94.09 | [5 empty] | 93.73 |  |  | 94.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.91 |  |  |  |  | 0.00
2010 |  |  |  | 9879.13 |  |  | 8727 |  |  |  | 1134 | [10 empty] | 99.63 |  |  |  | 99.63 | [5 empty] | 99.45 |  |  | 99.62 |  |  |  | 0.37 |  | 0.37 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8956.99 |  |  | 7917 |  |  |  | 1134 | [10 empty] | 90.40 |  |  |  | 90.40 | [5 empty] | 90.17 |  |  | 90.38 |  |  |  | 2.29 |  | 2.12 | [8 empty] | 7.48 |  |  |  |  | 0.00
2012 |  |  |  | 9595.26 |  |  | 8392 |  |  |  | 1134 | [10 empty] | 95.55 |  |  |  | 95.55 | [5 empty] | 96.33 |  |  | 95.54 |  |  |  | 2.23 |  | 2.18 | [8 empty] | 2.26 |  |  |  |  | 0.00
2013 |  |  |  | 9437.56 |  |  | 8143 |  |  |  | 1134 | [10 empty] | 92.96 |  |  |  | 92.96 | [5 empty] | 94.99 |  |  | 92.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.04 |  |  |  |  | 0.00
2014 |  |  |  | 10003.11 |  |  | 8607 |  |  |  | 1134 | [10 empty] | 98.25 |  |  |  | 98.25 | [5 empty] | 100.70 |  |  | 98.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.75 |  |  |  |  | 0.00
2015 |  |  |  | 8933.00 |  |  | 7982 |  |  |  | 1134 | [10 empty] | 91.11 |  |  |  | 91.11 | [5 empty] | 89.92 |  |  | 91.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.89 |  |  |  |  | 0.00
2016 |  |  |  | 10144.92 |  |  | 8744 |  |  |  | 1134 | [10 empty] | 99.55 |  |  |  | 99.55 | [5 empty] | 101.85 |  |  | 99.54 |  |  |  | 0.45 |  | 0.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 8574.81 |  |  | 7552 |  |  |  | 1134 | [10 empty] | 86.21 |  |  |  | 86.21 | [5 empty] | 86.32 |  |  | 86.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.79 |  |  |  |  | 0.00
2018 |  |  |  | 10173.71 |  |  | 8760 |  |  |  | 1134 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.41 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 9274.51 |  |  | 8170 |  |  |  | 1134 | [10 empty] | 93.29 |  |  |  | 93.29 | [5 empty] | 93.36 |  |  | 93.26 |  |  |  | 1.16 |  | 1.10 | [8 empty] | 5.62 |  |  |  |  | 0.00
2020 |  |  |  | 10211.57 |  |  | 8783 |  |  |  | 1134 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.51 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1990 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 102
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 355
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 71
E. |  | Testing of plant systems or components | [35 empty] | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 9
Z. |  | Other | [39 empty] | 5
Subtotal | [37 empty] | 426 |  |  |  | 116 | [11 empty] | 2
Total | [22 empty] | 0 | [14 empty] | 544
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1990 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 4
12. |  |  | Reactor I&C Systems | [34 empty] | 4
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 53
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 10
42. |  |  | Electrical Power Supply Systems | [34 empty] | 11
Total | [37 empty] | 113

## MCGUIRE-1
2020 Operating Experience
US-369 | [8 empty] | MCGUIRE-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Owner | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (ICECND) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-04-01
Thermal power | [12 empty] | : |  |  | 3411 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-09-12
Gross electrical power | [12 empty] | : |  |  | 1215 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-12-01
Reference unit power (net) | [12 empty] | : |  |  | 1158 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.204
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 37 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.83
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 25 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9434.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.23 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.23 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.77 %
Load Factor (LF) | [18 empty] | : | 92.75 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.22 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 771 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 888.90 | 832.02 |  |  |  | 886.38 |  | 857.60 | [8 empty] | 883.54 |  |  | 853.71 | [6 empty] | 870.72 |  | 855.27 |  |  |  | 499.85 |  |  | 257.91 |  |  | 859.25 | [9 empty] | 888.97 |  |  | 9434.12
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 60.56 |  |  | 34.65 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.23
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 60.56 |  |  | 34.65 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.23
LF [%] |  |  |  |  | 103.17 | 103.23 |  |  |  | 102.88 |  | 102.86 | [8 empty] | 102.55 |  |  | 102.39 | [6 empty] | 101.06 |  | 99.27 |  |  |  | 59.95 |  |  | 29.94 |  |  | 103.06 | [9 empty] | 103.18 |  |  | 92.75
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 60.56 |  |  | 34.68 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.22
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 39.44 |  |  | 65.35 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.77
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 364558.66 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.33 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.83 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.75 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.06 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.18 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.91 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.24 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.66 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 19.10 |  |  | 45 |  |  |  | 1146 | [10 empty] | 10.20 |  |  |  | 10.20 | [5 empty] | 2.18 |  |  | 6.05 |  |  |  | 89.80 |  | 89.80 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 4302.30 |  |  | 7043 |  |  |  | 1180 | [10 empty] | 81.62 |  |  |  | 81.62 | [5 empty] | 41.62 |  |  | 80.40 |  |  |  | 14.80 |  | 14.18 | [8 empty] | 4.20 |  |  |  |  | 0.00
1983 |  |  |  | 4650.00 |  |  | 4852 |  |  |  | 1180 | [10 empty] | 57.26 |  |  |  | 57.26 | [5 empty] | 44.98 |  |  | 55.39 |  |  |  | 16.60 |  | 11.39 | [8 empty] | 31.34 |  |  |  |  | 0.00
1984 |  |  |  | 6434.27 |  |  | 6011 |  |  |  | 1180 | [10 empty] | 69.33 |  |  |  | 78.14 | [5 empty] | 62.08 |  |  | 68.43 |  |  |  | 4.14 |  | 3.38 | [8 empty] | 18.48 |  |  |  |  | 8.81
1985 |  |  |  | 6780.08 |  |  | 6747 |  |  |  | 1180 | [10 empty] | 77.10 |  |  |  | 77.10 | [5 empty] | 65.59 |  |  | 77.02 |  |  |  | 8.75 |  | 7.39 | [8 empty] | 15.51 |  |  |  |  | 0.00
1986 |  |  |  | 5181.08 |  |  | 4912 |  |  |  | 1150 | [10 empty] | 56.16 |  |  |  | 56.16 | [5 empty] | 51.43 |  |  | 56.07 |  |  |  | 27.72 |  | 21.54 | [8 empty] | 22.29 |  |  |  |  | 0.00
1987 |  |  |  | 7352.88 |  |  | 6713 |  |  |  | 1150 | [10 empty] | 76.70 |  |  |  | 76.70 | [5 empty] | 72.99 |  |  | 76.63 |  |  |  | 4.75 |  | 3.82 | [8 empty] | 19.48 |  |  |  |  | 0.00
1988 |  |  |  | 7406.41 |  |  | 6763 |  |  |  | 1129 | [10 empty] | 77.04 |  |  |  | 77.04 | [5 empty] | 74.68 |  |  | 76.99 |  |  |  | 1.35 |  | 1.06 | [8 empty] | 21.90 |  |  |  |  | 0.00
1989 |  |  |  | 7807.23 |  |  | 7187 |  |  |  | 1129 | [10 empty] | 84.49 |  |  |  | 84.49 | [5 empty] | 78.94 |  |  | 82.04 |  |  |  | 15.49 |  | 15.48 | [8 empty] | 0.03 |  |  |  |  | 0.00
1990 |  |  |  | 4755.31 |  |  | 4718 |  |  |  | 1129 | [10 empty] | 56.90 |  |  |  | 56.90 | [5 empty] | 48.08 |  |  | 53.86 |  |  |  | 13.38 |  | 8.79 | [8 empty] | 34.30 |  |  |  |  | 0.00
1991 |  |  |  | 6851.08 |  |  | 6259 |  |  |  | 1129 | [10 empty] | 71.45 |  |  |  | 71.45 | [5 empty] | 69.27 |  |  | 71.45 |  |  |  | 9.09 |  | 7.15 | [8 empty] | 21.40 |  |  |  |  | 0.00
1992 |  |  |  | 7485.28 |  |  | 6839 |  |  |  | 1129 | [10 empty] | 77.89 |  |  |  | 77.89 | [5 empty] | 75.48 |  |  | 77.86 |  |  |  | 22.11 |  | 22.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 5537.09 |  |  | 5095 |  |  |  | 1129 | [10 empty] | 58.18 |  |  |  | 58.18 | [5 empty] | 55.99 |  |  | 58.16 |  |  |  | 23.34 |  | 17.72 | [8 empty] | 24.10 |  |  |  |  | 0.00
1994 |  |  |  | 6877.25 |  |  | 6291 |  |  |  | 1129 | [10 empty] | 71.86 |  |  |  | 71.86 | [5 empty] | 69.54 |  |  | 71.82 |  |  |  | 16.20 |  | 13.89 | [8 empty] | 14.25 |  |  |  |  | 0.00
1995 |  |  |  | 8860.20 |  |  | 8017 |  |  |  | 1129 | [10 empty] | 91.58 |  |  |  | 91.58 | [5 empty] | 89.59 |  |  | 91.52 |  |  |  | 3.72 |  | 3.54 | [8 empty] | 4.89 |  |  |  |  | 0.00
1996 |  |  |  | 8558.29 |  |  | 7858 |  |  |  | 1129 | [10 empty] | 89.50 |  |  |  | 89.50 | [5 empty] | 86.30 |  |  | 89.46 |  |  |  | 3.79 |  | 3.53 | [8 empty] | 6.97 |  |  |  |  | 0.00
1997 |  |  |  | 7011.25 |  |  | 6361 |  |  |  | 1129 | [10 empty] | 72.68 |  |  |  | 72.68 | [5 empty] | 70.89 |  |  | 72.61 |  |  |  | 1.83 |  | 1.36 | [8 empty] | 25.96 |  |  |  |  | 0.00
1998 |  |  |  | 8822.61 |  |  | 7889 |  |  |  | 1119 | [10 empty] | 89.99 |  |  |  | 89.99 | [5 empty] | 89.98 |  |  | 90.06 |  |  |  | 0.73 |  | 0.66 | [8 empty] | 9.35 |  |  |  |  | 0.00
1999 |  |  |  | 8593.31 |  |  | 7584 |  |  |  | 1100 | [10 empty] | 86.58 |  |  |  | 86.58 | [5 empty] | 89.18 |  |  | 86.58 |  |  |  | 2.15 |  | 1.91 | [8 empty] | 11.51 |  |  |  |  | 0.00
2000 |  |  |  | 9995.02 |  |  | 8741 |  |  |  | 1100 | [10 empty] | 99.52 |  |  |  | 99.52 | [5 empty] | 103.44 |  |  | 99.51 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 8684.94 |  |  | 7708 |  |  |  | 1100 | [10 empty] | 88.00 |  |  |  | 88.00 | [5 empty] | 90.13 |  |  | 87.99 |  |  |  | 1.70 |  | 1.53 | [8 empty] | 10.47 |  |  |  |  | 0.00
2002 |  |  |  | 9100.83 |  |  | 8042 |  |  |  | 1100 | [10 empty] | 91.83 |  |  |  | 91.83 | [5 empty] | 94.45 |  |  | 91.80 |  |  |  | 1.04 |  | 1.87 | [8 empty] | 6.30 |  |  |  |  | 0.00
2003 |  |  |  | 9912.47 |  |  | 8760 |  |  |  | 1100 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.87 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 8238.51 |  |  | 7321 |  |  |  | 1100 | [10 empty] | 83.37 |  |  |  | 83.37 | [5 empty] | 85.26 |  |  | 83.34 |  |  |  | 7.74 |  | 6.99 | [8 empty] | 9.63 |  |  |  |  | 0.00
2005 |  |  |  | 8968.59 |  |  | 7963 |  |  |  | 1100 | [10 empty] | 90.91 |  |  |  | 90.91 | [5 empty] | 93.07 |  |  | 90.90 |  |  |  | 0.51 |  | 0.47 | [8 empty] | 8.62 |  |  |  |  | 0.00
2006 |  |  |  | 9967.23 |  |  | 8760 |  |  |  | 1100 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.44 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 7656.08 |  |  | 6852 |  |  |  | 1100 | [10 empty] | 78.24 |  |  |  | 78.24 | [5 empty] | 79.45 |  |  | 78.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.76 |  |  |  |  | 0.00
2008 |  |  |  | 8364.40 |  |  | 7412 |  |  |  | 1100 | [10 empty] | 84.38 |  |  |  | 84.38 | [5 empty] | 86.57 |  |  | 84.38 |  |  |  | 1.09 |  | 0.93 | [8 empty] | 14.68 |  |  |  |  | 0.00
2009 |  |  |  | 9999.08 |  |  | 8760 |  |  |  | 1100 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.77 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 8835.73 |  |  | 7778 |  |  |  | 1100 | [10 empty] | 88.81 |  |  |  | 88.81 | [5 empty] | 91.70 |  |  | 88.79 |  |  |  | 1.01 |  | 0.91 | [8 empty] | 10.29 |  |  |  |  | 0.00
2011 |  |  |  | 9081.86 |  |  | 7979 |  |  |  | 1129 | [10 empty] | 91.17 |  |  |  | 91.17 | [5 empty] | 93.63 |  |  | 91.08 |  |  |  | 1.28 |  | 1.19 | [8 empty] | 7.64 |  |  |  |  | 0.00
2012 |  |  |  | 10114.04 |  |  | 8784 |  |  |  | 1129 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.99 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 8780.45 |  |  | 7740 |  |  |  | 1158 | [10 empty] | 88.65 |  |  |  | 88.65 | [5 empty] | 86.55 |  |  | 88.35 |  |  |  | 1.46 |  | 1.31 | [8 empty] | 10.04 |  |  |  |  | 0.00
2014 |  |  |  | 8227.61 |  |  | 7194 |  |  |  | 1158 | [10 empty] | 82.13 |  |  |  | 82.13 | [5 empty] | 81.11 |  |  | 82.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.87 |  |  |  |  | 0.00
2015 |  |  |  | 10188.92 |  |  | 8603 |  |  |  | 1160 | [10 empty] | 98.21 |  |  |  | 98.21 | [5 empty] | 100.27 |  |  | 98.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.79 |  |  |  |  | 0.00
2016 |  |  |  | 9515.88 |  |  | 8085 |  |  |  | 1160 | [10 empty] | 91.77 |  |  |  | 91.77 | [5 empty] | 93.39 |  |  | 92.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.23 |  |  |  |  | 0.00
2017 |  |  |  | 9646.27 |  |  | 8196 |  |  |  | 1158 | [10 empty] | 93.55 |  |  |  | 93.55 | [5 empty] | 95.09 |  |  | 93.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.45 |  |  |  |  | 0.00
2018 |  |  |  | 10359.25 |  |  | 8730 |  |  |  | 1158 | [10 empty] | 99.66 |  |  |  | 99.66 | [5 empty] | 102.12 |  |  | 99.66 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 9271.86 |  |  | 8022 |  |  |  | 1158 | [10 empty] | 91.59 |  |  |  | 91.59 | [5 empty] | 91.40 |  |  | 91.58 |  |  |  | 1.75 |  | 1.63 | [8 empty] | 6.78 |  |  |  |  | 0.00
2020 |  |  |  | 9434.12 |  |  | 8013 |  |  |  | 1158 | [10 empty] | 91.23 |  |  |  | 91.23 | [5 empty] | 92.75 |  |  | 91.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.77 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 401
B. |  | Refuelling without maintenance | [20 empty] | 770 | [14 empty] | 20
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 829
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 107 |  |  |  | 0
E. |  | Testing of plant systems or components | [35 empty] | 14 |  |  |  | 1
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 6
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [35 empty] | 9 |  |  |  | 3 | [11 empty] | 20
Subtotal | [22 empty] | 770 | [14 empty] | 981 |  |  |  | 416 | [11 empty] | 20
Total | [22 empty] | 770 | [14 empty] | 1417
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 30
12. |  |  | Reactor I&C Systems | [34 empty] | 16
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 16
14. |  |  | Safety Systems | [34 empty] | 21
15. |  |  | Reactor Cooling Systems | [34 empty] | 58
16. |  |  | Steam generation systems | [34 empty] | 60
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 39
32. |  |  | Feedwater and Main Steam System | [34 empty] | 125
34. |  |  | Miscellaneous Systems | [34 empty] | 20
41. |  |  | Main Generator Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 17
Total | [37 empty] | 408
Highlights (2020)
Refueling Outage 27

## MCGUIRE-2
2020 Operating Experience
US-370 | [8 empty] | MCGUIRE-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Owner | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (ICECND) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-04-01
Thermal power | [12 empty] | : |  |  | 3411 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-05-23
Gross electrical power | [12 empty] | : |  |  | 1215 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-03-01
Reference unit power (net) | [12 empty] | : |  |  | 1158 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.2
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 39 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.4 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.83
| Active core height/length [m] | [13 empty] | : |  |  | 3.7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 25 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9612.83 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.6 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.6 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.4 %
Load Factor (LF) | [18 empty] | : | 94.5 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.59 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 563 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 882.83 | 822.63 |  |  |  | 532.15 |  | 464.85 | [8 empty] | 873.01 |  |  | 851.76 | [6 empty] | 870.98 |  | 864.34 |  |  |  | 839.86 |  |  | 876.11 |  |  | 851.94 | [9 empty] | 882.38 |  |  | 9612.83
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 65.05 |  | 58.02 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.60
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 65.05 |  | 58.02 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.60
LF [%] |  |  |  |  | 102.47 | 102.07 |  |  |  | 61.77 |  | 55.75 | [8 empty] | 101.33 |  |  | 102.16 | [6 empty] | 101.09 |  | 100.32 |  |  |  | 100.73 |  |  | 101.69 |  |  | 102.18 | [9 empty] | 102.42 |  |  | 94.50
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 64.92 |  | 58.06 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.59
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 34.95 |  | 41.98 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.40
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 323735.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.66 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.43 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.57 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.84 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 6557.80 |  |  | 6086 |  |  |  | 1171 | [10 empty] | 82.97 |  |  |  | 82.97 | [5 empty] | 75.67 |  |  | 82.87 |  |  |  | 16.04 |  | 15.85 | [8 empty] | 1.18 |  |  |  |  | 0.00
1985 |  |  |  | 5609.29 |  |  | 5171 |  |  |  | 1180 | [10 empty] | 61.05 |  |  |  | 61.05 | [5 empty] | 54.27 |  |  | 59.03 |  |  |  | 18.66 |  | 14.01 | [8 empty] | 24.95 |  |  |  |  | 0.00
1986 |  |  |  | 6216.62 |  |  | 5601 |  |  |  | 1150 | [10 empty] | 64.53 |  |  |  | 64.53 | [5 empty] | 61.71 |  |  | 63.94 |  |  |  | 10.88 |  | 7.88 | [8 empty] | 27.59 |  |  |  |  | 0.00
1987 |  |  |  | 7577.35 |  |  | 6954 |  |  |  | 1150 | [10 empty] | 80.16 |  |  |  | 80.16 | [5 empty] | 75.22 |  |  | 79.38 |  |  |  | 2.75 |  | 2.26 | [8 empty] | 17.58 |  |  |  |  | 0.00
1988 |  |  |  | 8058.02 |  |  | 7229 |  |  |  | 1129 | [10 empty] | 82.34 |  |  |  | 82.34 | [5 empty] | 81.25 |  |  | 82.30 |  |  |  | 1.02 |  | 0.84 | [8 empty] | 16.82 |  |  |  |  | 0.00
1989 |  |  |  | 7418.33 |  |  | 6867 |  |  |  | 1129 | [10 empty] | 78.42 |  |  |  | 78.42 | [5 empty] | 75.01 |  |  | 78.39 |  |  |  | 0.89 |  | 0.71 | [8 empty] | 20.87 |  |  |  |  | 0.00
1990 |  |  |  | 6496.16 |  |  | 5873 |  |  |  | 1129 | [10 empty] | 69.52 |  |  |  | 69.52 | [5 empty] | 65.68 |  |  | 67.04 |  |  |  | 1.22 |  | 0.86 | [8 empty] | 29.62 |  |  |  |  | 0.00
1991 |  |  |  | 9515.97 |  |  | 8548 |  |  |  | 1129 | [10 empty] | 97.60 |  |  |  | 97.60 | [5 empty] | 96.22 |  |  | 97.58 |  |  |  | 2.40 |  | 2.40 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 6785.04 |  |  | 6141 |  |  |  | 1129 | [10 empty] | 69.96 |  |  |  | 69.96 | [5 empty] | 68.42 |  |  | 69.91 |  |  |  | 3.64 |  | 2.64 | [8 empty] | 27.40 |  |  |  |  | 0.00
1993 |  |  |  | 6821.09 |  |  | 6378 |  |  |  | 1129 | [10 empty] | 72.82 |  |  |  | 72.82 | [5 empty] | 68.97 |  |  | 72.81 |  |  |  | 2.95 |  | 2.21 | [8 empty] | 24.97 |  |  |  |  | 0.00
1994 |  |  |  | 8659.96 |  |  | 7708 |  |  |  | 1129 | [10 empty] | 88.01 |  |  |  | 88.01 | [5 empty] | 87.56 |  |  | 87.99 |  |  |  | 1.83 |  | 1.64 | [8 empty] | 10.34 |  |  |  |  | 0.00
1995 |  |  |  | 9090.01 |  |  | 8144 |  |  |  | 1129 | [10 empty] | 93.01 |  |  |  | 93.01 | [5 empty] | 91.91 |  |  | 92.97 |  |  |  | 4.07 |  | 3.95 | [8 empty] | 3.04 |  |  |  |  | 0.00
1996 |  |  |  | 7265.11 |  |  | 6543 |  |  |  | 1129 | [10 empty] | 74.57 |  |  |  | 74.57 | [5 empty] | 73.26 |  |  | 74.49 |  |  |  | 16.44 |  | 14.67 | [8 empty] | 10.76 |  |  |  |  | 0.00
1997 |  |  |  | 6648.44 |  |  | 6214 |  |  |  | 1129 | [10 empty] | 70.97 |  |  |  | 70.97 | [5 empty] | 67.22 |  |  | 70.94 |  |  |  | 10.12 |  | 7.99 | [8 empty] | 21.04 |  |  |  |  | 0.00
1998 |  |  |  | 9928.27 |  |  | 8715 |  |  |  | 1119 | [10 empty] | 99.49 |  |  |  | 99.49 | [5 empty] | 101.26 |  |  | 99.49 |  |  |  | 0.51 |  | 0.51 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 8596.72 |  |  | 7927 |  |  |  | 1100 | [10 empty] | 90.51 |  |  |  | 90.51 | [5 empty] | 89.21 |  |  | 90.49 |  |  |  | 0.40 |  | 0.36 | [8 empty] | 9.13 |  |  |  |  | 0.00
2000 |  |  |  | 8452.37 |  |  | 7757 |  |  |  | 1100 | [10 empty] | 88.32 |  |  |  | 88.32 | [5 empty] | 87.48 |  |  | 88.31 |  |  |  | 0.46 |  | 0.41 | [8 empty] | 11.27 |  |  |  |  | 0.00
2001 |  |  |  | 9878.04 |  |  | 8698 |  |  |  | 1100 | [10 empty] | 99.30 |  |  |  | 99.30 | [5 empty] | 102.51 |  |  | 99.29 |  |  |  | 0.70 |  | 0.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 8913.51 |  |  | 7940 |  |  |  | 1100 | [10 empty] | 90.65 |  |  |  | 90.65 | [5 empty] | 92.50 |  |  | 90.64 |  |  |  | 0.54 |  | 1.94 | [8 empty] | 7.41 |  |  |  |  | 0.00
2003 |  |  |  | 9027.81 |  |  | 8024 |  |  |  | 1100 | [10 empty] | 91.61 |  |  |  | 91.61 | [5 empty] | 93.69 |  |  | 91.60 |  |  |  | 0.00 |  | 0.52 | [8 empty] | 7.86 |  |  |  |  | 0.00
2004 |  |  |  | 9994.02 |  |  | 8784 |  |  |  | 1100 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.43 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 8545.57 |  |  | 7589 |  |  |  | 1100 | [10 empty] | 86.66 |  |  |  | 86.66 | [5 empty] | 88.67 |  |  | 86.62 |  |  |  | 3.20 |  | 2.87 | [8 empty] | 10.47 |  |  |  |  | 0.00
2006 |  |  |  | 8430.33 |  |  | 7418 |  |  |  | 1100 | [10 empty] | 84.70 |  |  |  | 84.70 | [5 empty] | 87.49 |  |  | 84.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.30 |  |  |  |  | 0.00
2007 |  |  |  | 9967.57 |  |  | 8760 |  |  |  | 1100 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.44 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8713.27 |  |  | 7651 |  |  |  | 1100 | [10 empty] | 87.11 |  |  |  | 87.11 | [5 empty] | 90.18 |  |  | 87.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.89 |  |  |  |  | 0.00
2009 |  |  |  | 9015.67 |  |  | 7907 |  |  |  | 1100 | [10 empty] | 90.27 |  |  |  | 90.27 | [5 empty] | 93.56 |  |  | 90.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.73 |  |  |  |  | 0.00
2010 |  |  |  | 10014.70 |  |  | 8760 |  |  |  | 1100 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.93 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8773.24 |  |  | 7705 |  |  |  | 1129 | [10 empty] | 88.22 |  |  |  | 88.22 | [5 empty] | 89.27 |  |  | 87.96 |  |  |  | 1.75 |  | 1.57 | [8 empty] | 10.21 |  |  |  |  | 0.00
2012 |  |  |  | 7878.65 |  |  | 6923 |  |  |  | 1129 | [10 empty] | 78.83 |  |  |  | 78.83 | [5 empty] | 79.44 |  |  | 78.81 |  |  |  | 0.34 |  | 0.27 | [8 empty] | 20.90 |  |  |  |  | 0.00
2013 |  |  |  | 10117.09 |  |  | 8760 |  |  |  | 1158 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.72 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 9362.49 |  |  | 7956 |  |  |  | 1158 | [10 empty] | 90.82 |  |  |  | 90.82 | [5 empty] | 92.30 |  |  | 90.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.18 |  |  |  |  | 0.00
2015 |  |  |  | 9347.08 |  |  | 8079 |  |  |  | 1158 | [10 empty] | 92.22 |  |  |  | 92.22 | [5 empty] | 92.14 |  |  | 92.23 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 7.60 |  |  |  |  | 0.00
2016 |  |  |  | 10368.41 |  |  | 8784 |  |  |  | 1158 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.93 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 9149.27 |  |  | 7878 |  |  |  | 1158 | [10 empty] | 89.94 |  |  |  | 89.94 | [5 empty] | 90.19 |  |  | 89.93 |  |  |  | 3.79 |  | 3.55 | [8 empty] | 6.52 |  |  |  |  | 0.00
2018 |  |  |  | 9502.82 |  |  | 8076 |  |  |  | 1158 | [10 empty] | 92.20 |  |  |  | 92.20 | [5 empty] | 93.68 |  |  | 92.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.80 |  |  |  |  | 0.00
2019 |  |  |  | 10316.39 |  |  | 8760 |  |  |  | 1158 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.70 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9612.83 |  |  | 8221 |  |  |  | 1158 | [10 empty] | 93.60 |  |  |  | 93.60 | [5 empty] | 94.50 |  |  | 93.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.40 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 197
B. |  | Refuelling without maintenance | [20 empty] | 562 | [14 empty] | 15
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 845
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 70 |  |  |  | 0
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 8
L. |  | Human factor related | [39 empty] | 3
Z. |  | Other | [35 empty] | 0 |  |  |  | 3
Subtotal | [22 empty] | 562 | [14 empty] | 930 |  |  |  | 211
Total | [22 empty] | 562 | [14 empty] | 1141
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 18
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 15
14. |  |  | Safety Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [34 empty] | 60
16. |  |  | Steam generation systems | [34 empty] | 10
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 6
32. |  |  | Feedwater and Main Steam System | [34 empty] | 31
34. |  |  | Miscellaneous Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 34
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [37 empty] | 209
Highlights (2020)
End of Cycle 26 Refueling Outage.

## MILLSTONE-2
2020 Operating Experience
US-336 | [8 empty] | MILLSTONE-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DOMINION (Dominion Energy)
Owner | [7 empty] | : | DOMINRES (Dominion Resources, Inc.)
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1969-11-01
Thermal power | [12 empty] | : |  |  | 2700 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-11-09
Gross electrical power | [12 empty] | : |  |  | 918 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-12-26
Reference unit power (net) | [12 empty] | : |  |  | 869 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 312.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.483
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.45 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.73
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 49 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6690.5 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.22 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.22 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.78 %
Load Factor (LF) | [18 empty] | : | 87.65 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 88.21 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1036 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 641.85 | 605.22 |  |  |  | 647.18 |  | 472.82 | [8 empty] | 0.00 |  |  | 500.58 | [6 empty] | 643.98 |  | 638.01 |  |  |  | 621.51 |  |  | 645.51 |  |  | 625.00 | [9 empty] | 648.85 |  |  | 6690.50
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 76.25 | [8 empty] | 0.00 |  |  | 83.34 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.22
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 76.25 | [8 empty] | 0.00 |  |  | 83.34 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.22
LF [%] |  |  |  |  | 99.27 | 100.07 |  |  |  | 100.10 |  | 75.57 | [8 empty] | 0.00 |  |  | 80.01 | [6 empty] | 99.60 |  | 98.68 |  |  |  | 99.33 |  |  | 99.84 |  |  | 99.89 | [9 empty] | 100.36 |  |  | 87.65
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 76.25 | [8 empty] | 0.00 |  |  | 83.33 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.21
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 23.75 | [8 empty] | 100.00 |  |  | 16.66 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 11.78
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 215982.05 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 15.45 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.36 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 73.13 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.51 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.17 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.59 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.83 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 134.70 |  |  | 623 |  |  |  | 851 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1976 |  |  |  | 4543.20 |  |  | 6815 |  |  |  | 780 | [10 empty] | 66.37 |  |  |  | 66.37 | [5 empty] | 66.31 |  |  | 77.58 |  |  |  | 31.06 |  | 29.91 | [8 empty] | 3.72 |  |  |  |  | 0.00
1977 |  |  |  | 4345.70 |  |  | 5756 |  |  |  | 790 | [10 empty] | 62.88 |  |  |  | 62.88 | [5 empty] | 62.80 |  |  | 65.71 |  |  |  | 19.40 |  | 15.13 | [8 empty] | 21.99 |  |  |  |  | 0.00
1978 |  |  |  | 4507.20 |  |  | 5756 |  |  |  | 802 | [10 empty] | 64.12 |  |  |  | 64.12 | [5 empty] | 64.15 |  |  | 65.71 |  |  |  | 23.99 |  | 20.24 | [8 empty] | 15.64 |  |  |  |  | 0.00
1979 |  |  |  | 4370.90 |  |  | 5385 |  |  |  | 837 | [10 empty] | 59.58 |  |  |  | 59.58 | [5 empty] | 59.61 |  |  | 61.47 |  |  |  | 23.78 |  | 18.59 | [8 empty] | 21.82 |  |  |  |  | 0.00
1980 |  |  |  | 4884.30 |  |  | 5947 |  |  |  | 864 | [10 empty] | 68.17 |  |  |  | 80.81 | [5 empty] | 64.36 |  |  | 67.70 |  |  |  | 2.03 |  | 1.68 | [8 empty] | 17.51 |  |  |  |  | 12.65
1981 |  |  |  | 6091.70 |  |  | 7229 |  |  |  | 864 | [10 empty] | 82.71 |  |  |  | 82.71 | [5 empty] | 80.49 |  |  | 82.52 |  |  |  | 10.74 |  | 9.95 | [8 empty] | 7.33 |  |  |  |  | 0.00
1982 |  |  |  | 5015.60 |  |  | 6183 |  |  |  | 864 | [10 empty] | 70.48 |  |  |  | 70.48 | [5 empty] | 66.27 |  |  | 70.58 |  |  |  | 11.29 |  | 8.97 | [8 empty] | 20.55 |  |  |  |  | 0.00
1983 |  |  |  | 2474.40 |  |  | 2993 |  |  |  | 861 | [10 empty] | 34.07 |  |  |  | 34.07 | [5 empty] | 32.81 |  |  | 34.17 |  |  |  | 13.92 |  | 5.51 | [8 empty] | 60.42 |  |  |  |  | 0.00
1984 |  |  |  | 6608.34 |  |  | 8209 |  |  |  | 860 | [10 empty] | 93.40 |  |  |  | 93.40 | [5 empty] | 87.48 |  |  | 93.45 |  |  |  | 3.79 |  | 3.68 | [8 empty] | 2.92 |  |  |  |  | 0.00
1985 |  |  |  | 3515.65 |  |  | 4322 |  |  |  | 841 | [10 empty] | 47.66 |  |  |  | 59.35 | [5 empty] | 47.72 |  |  | 49.34 |  |  |  | 2.23 |  | 1.35 | [8 empty] | 39.29 |  |  |  |  | 11.69
1986 |  |  |  | 5164.85 |  |  | 6352 |  |  |  | 857 | [10 empty] | 72.50 |  |  |  | 72.50 | [5 empty] | 68.80 |  |  | 72.51 |  |  |  | 2.59 |  | 1.93 | [8 empty] | 25.58 |  |  |  |  | 0.00
1987 |  |  |  | 6892.53 |  |  | 8177 |  |  |  | 857 | [10 empty] | 93.29 |  |  |  | 93.29 | [5 empty] | 91.81 |  |  | 93.34 |  |  |  | 6.47 |  | 6.45 | [8 empty] | 0.26 |  |  |  |  | 0.00
1988 |  |  |  | 5735.94 |  |  | 6810 |  |  |  | 860 | [10 empty] | 77.24 |  |  |  | 77.24 | [5 empty] | 75.89 |  |  | 77.53 |  |  |  | 3.29 |  | 2.63 | [8 empty] | 20.13 |  |  |  |  | 0.00
1989 |  |  |  | 4763.57 |  |  | 5705 |  |  |  | 863 | [10 empty] | 66.85 |  |  |  | 66.85 | [5 empty] | 62.95 |  |  | 65.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.15 |  |  |  |  | 0.00
1990 |  |  |  | 5309.94 |  |  | 6389 |  |  |  | 863 | [10 empty] | 72.84 |  |  |  | 72.84 | [5 empty] | 70.24 |  |  | 72.93 |  |  |  | 2.54 |  | 1.90 | [8 empty] | 25.26 |  |  |  |  | 0.00
1991 |  |  |  | 3948.13 |  |  | 4820 |  |  |  | 863 | [10 empty] | 55.28 |  |  |  | 55.28 | [5 empty] | 52.22 |  |  | 55.02 |  |  |  | 44.49 |  | 44.31 | [8 empty] | 0.41 |  |  |  |  | 0.00
1992 |  |  |  | 2725.02 |  |  | 3187 |  |  |  | 870 | [10 empty] | 36.12 |  |  |  | 36.12 | [5 empty] | 35.64 |  |  | 36.28 |  |  |  | 11.45 |  | 4.67 | [8 empty] | 59.21 |  |  |  |  | 0.00
1993 |  |  |  | 6295.91 |  |  | 7431 |  |  |  | 873 | [10 empty] | 84.79 |  |  |  | 84.79 | [5 empty] | 82.33 |  |  | 84.83 |  |  |  | 11.85 |  | 11.39 | [8 empty] | 3.81 |  |  |  |  | 0.00
1994 |  |  |  | 3676.45 |  |  | 4289 |  |  |  | 873 | [10 empty] | 49.02 |  |  |  | 49.02 | [5 empty] | 48.07 |  |  | 48.96 |  |  |  | 34.50 |  | 25.82 | [8 empty] | 25.16 |  |  |  |  | 0.00
1995 |  |  |  | 2740.54 |  |  | 3273 |  |  |  | 873 | [10 empty] | 37.39 |  |  |  | 37.39 | [5 empty] | 35.84 |  |  | 37.36 |  |  |  | 8.62 |  | 3.53 | [8 empty] | 59.09 |  |  |  |  | 0.00
1996 |  |  |  | 1046.48 |  |  | 1222 |  |  |  | 871 | [10 empty] | 13.73 |  |  |  | 13.73 | [5 empty] | 13.68 |  |  | 13.91 |  |  |  | 85.90 |  | 83.63 | [8 empty] | 2.65 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 871 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 0.00 |  |  | 0 |  |  |  | 871 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 4433.22 |  |  | 5310 |  |  |  | 870 | [10 empty] | 60.63 |  |  |  | 60.63 | [5 empty] | 58.17 |  |  | 60.62 |  |  |  | 39.37 |  | 39.37 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 6268.50 |  |  | 7353 |  |  |  | 873 | [10 empty] | 83.70 |  |  |  | 83.70 | [5 empty] | 81.77 |  |  | 83.71 |  |  |  | 6.03 |  | 5.38 | [8 empty] | 10.93 |  |  |  |  | 0.00
2001 |  |  |  | 7284.02 |  |  | 8587 |  |  |  | 869 | [10 empty] | 98.04 |  |  |  | 98.04 | [5 empty] | 95.44 |  |  | 98.03 |  |  |  | 1.96 |  | 1.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 6209.31 |  |  | 7285 |  |  |  | 871 | [10 empty] | 83.20 |  |  |  | 83.20 | [5 empty] | 81.47 |  |  | 83.16 |  |  |  | 4.90 |  | 4.29 | [8 empty] | 12.51 |  |  |  |  | 0.00
2003 |  |  |  | 6109.80 |  |  | 7083 |  |  |  | 866 | [10 empty] | 80.88 |  |  |  | 80.88 | [5 empty] | 80.19 |  |  | 80.86 |  |  |  | 7.18 |  | 6.25 | [8 empty] | 12.87 |  |  |  |  | 0.00
2004 |  |  |  | 7596.04 |  |  | 8677 |  |  |  | 877 | [10 empty] | 98.81 |  |  |  | 98.81 | [5 empty] | 98.71 |  |  | 98.78 |  |  |  | 1.19 |  | 1.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 6843.02 |  |  | 7812 |  |  |  | 866 | [10 empty] | 89.19 |  |  |  | 89.19 | [5 empty] | 90.19 |  |  | 89.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.81 |  |  |  |  | 0.00
2006 |  |  |  | 6519.46 |  |  | 7453 |  |  |  | 882 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 84.38 |  |  | 85.08 |  |  |  | 3.42 |  | 3.02 | [8 empty] | 11.88 |  |  |  |  | 0.00
2007 |  |  |  | 7686.76 |  |  | 8760 |  |  |  | 877 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 6619.59 |  |  | 7596 |  |  |  | 877 | [10 empty] | 86.50 |  |  |  | 88.17 | [5 empty] | 85.93 |  |  | 86.48 |  |  |  | 0.97 |  | 0.86 | [8 empty] | 10.97 |  |  |  |  | 1.67
2009 |  |  |  | 6239.17 |  |  | 7196 |  |  |  | 877 | [10 empty] | 82.18 |  |  |  | 82.18 | [5 empty] | 81.21 |  |  | 82.15 |  |  |  | 17.82 |  | 17.82 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 7414.57 |  |  | 8547 |  |  |  | 869 | [10 empty] | 97.56 |  |  |  | 98.22 | [5 empty] | 97.40 |  |  | 97.57 |  |  |  | 1.29 |  | 1.28 | [8 empty] | 0.50 |  |  |  |  | 0.67
2011 |  |  |  | 6601.01 |  |  | 7620 |  |  |  | 869 | [10 empty] | 87.17 |  |  |  | 87.17 | [5 empty] | 86.71 |  |  | 86.99 |  |  |  | 5.00 |  | 4.59 | [8 empty] | 8.24 |  |  |  |  | 0.00
2012 |  |  |  | 6342.84 |  |  | 7363 |  |  |  | 869 | [10 empty] | 83.85 |  |  |  | 83.85 | [5 empty] | 83.09 |  |  | 83.82 |  |  |  | 3.66 |  | 3.18 | [8 empty] | 12.97 |  |  |  |  | 0.00
2013 |  |  |  | 7578.99 |  |  | 8711 |  |  |  | 869 | [10 empty] | 99.44 |  |  |  | 99.44 | [5 empty] | 99.55 |  |  | 99.43 |  |  |  | 0.56 |  | 0.56 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 6518.71 |  |  | 7534 |  |  |  | 869 | [10 empty] | 86.75 |  |  |  | 86.75 | [5 empty] | 85.63 |  |  | 86.00 |  |  |  | 1.84 |  | 1.62 | [8 empty] | 11.62 |  |  |  |  | 0.00
2015 |  |  |  | 6775.63 |  |  | 7860 |  |  |  | 869 | [10 empty] | 89.72 |  |  |  | 89.72 | [5 empty] | 89.01 |  |  | 89.73 |  |  |  | 0.94 |  | 0.85 | [8 empty] | 9.43 |  |  |  |  | 0.00
2016 |  |  |  | 7469.89 |  |  | 8725 |  |  |  | 869 | [10 empty] | 99.33 |  |  |  | 99.33 | [5 empty] | 97.86 |  |  | 99.33 |  |  |  | 0.54 |  | 0.54 | [8 empty] | 0.13 |  |  |  |  | 0.00
2017 |  |  |  | 6798.76 |  |  | 7953 |  |  |  | 869 | [10 empty] | 90.79 |  |  |  | 90.79 | [5 empty] | 89.31 |  |  | 90.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.21 |  |  |  |  | 0.00
2018 |  |  |  | 6163.60 |  |  | 7251 |  |  |  | 869 | [10 empty] | 82.77 |  |  |  | 82.77 | [5 empty] | 80.97 |  |  | 82.77 |  |  |  | 8.14 |  | 7.34 | [8 empty] | 9.89 |  |  |  |  | 0.00
2019 |  |  |  | 7257.73 |  |  | 8637 |  |  |  | 869 | [10 empty] | 98.61 |  |  |  | 98.61 | [5 empty] | 95.34 |  |  | 98.60 |  |  |  | 1.39 |  | 1.39 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 6690.50 |  |  | 7748 |  |  |  | 869 | [10 empty] | 88.22 |  |  |  | 88.22 | [5 empty] | 87.65 |  |  | 88.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.78 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1975 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 481
B. |  | Refuelling without maintenance | [20 empty] | 1035 | [14 empty] | 23
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1095
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 38
E. |  | Testing of plant systems or components | [35 empty] | 7 |  |  |  | 162
H. |  | Nuclear regulatory requirements | [39 empty] | 490
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 21
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 28
Z. |  | Other | [35 empty] | 19 |  |  |  | 5
Subtotal | [22 empty] | 1035 | [14 empty] | 1182 |  |  |  | 1159 | [11 empty] | 29
Total | [22 empty] | 1035 | [14 empty] | 2370
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1975 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 50
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 98
16. |  |  | Steam generation systems | [34 empty] | 74
31. |  |  | Turbine and auxiliaries | [34 empty] | 65
32. |  |  | Feedwater and Main Steam System | [34 empty] | 80
33. |  |  | Circulating Water System | [34 empty] | 12
34. |  |  | Miscellaneous Systems | [34 empty] | 176
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 70
Total | [37 empty] | 656
Highlights (2020)
Refueling Outage 26 (2R26).

## MILLSTONE-3
2020 Operating Experience
US-423 | [8 empty] | MILLSTONE-3 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DOMINION (Dominion Energy)
Owner | [7 empty] | : | DOMINRES (Dominion Resources, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYSUB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-08-09
Thermal power | [12 empty] | : |  |  | 3650 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-02-12
Gross electrical power | [12 empty] | : |  |  | 1280 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-04-23
Reference unit power (net) | [12 empty] | : |  |  | 1210 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.17
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.4 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.7
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 580 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9024.35 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.54 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.13 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.12 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.13 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.75 %
Load Factor (LF) | [18 empty] | : | 84.91 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 84.68 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1346 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 914.02 | 855.64 |  |  |  | 912.71 |  | 512.34 | [8 empty] | 912.17 |  |  | 880.06 | [6 empty] | 900.07 |  | 873.85 |  |  |  | 871.18 |  |  | 18.50 |  |  | 510.41 | [9 empty] | 863.40 |  |  | 9024.35
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 67.59 | [8 empty] | 94.49 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 2.92 |  |  | 61.27 | [9 empty] | 95.82 |  |  | 85.13
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 67.59 | [8 empty] | 94.49 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 2.92 |  |  | 61.27 | [9 empty] | 95.82 |  |  | 85.13
LF [%] |  |  |  |  | 101.53 | 101.60 |  |  |  | 101.38 |  | 58.81 | [8 empty] | 101.33 |  |  | 101.02 | [6 empty] | 99.98 |  | 97.07 |  |  |  | 100.00 |  |  | 2.06 |  |  | 58.59 | [9 empty] | 95.91 |  |  | 84.91
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 61.94 | [8 empty] | 94.49 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 2.96 |  |  | 61.39 | [9 empty] | 95.83 |  |  | 84.68
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 32.41 | [8 empty] | 5.51 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.54
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 32.41 | [8 empty] | 5.51 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.12
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 97.08 |  |  | 38.73 | [9 empty] | 4.18 |  |  | 11.75
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 251278.31 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 11.55 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.04 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 10.58 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.06 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.36 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 79.83 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.56 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | Data not provided
1987 |  |  |  | 6748.20 |  |  | 6235 |  |  |  | 1142 | [10 empty] | 71.36 |  |  |  | 71.36 | [5 empty] | 67.46 |  |  | 71.18 |  |  |  | 5.40 |  | 4.07 | [8 empty] | 24.56 |  |  |  |  | 0.00
1988 |  |  |  | 7683.62 |  |  | 6954 |  |  |  | 1142 | [10 empty] | 79.50 |  |  |  | 79.50 | [5 empty] | 76.60 |  |  | 79.17 |  |  |  | 11.03 |  | 9.85 | [8 empty] | 10.65 |  |  |  |  | 0.00
1989 |  |  |  | 7082.60 |  |  | 6636 |  |  |  | 1142 | [10 empty] | 75.89 |  |  |  | 75.89 | [5 empty] | 70.80 |  |  | 75.75 |  |  |  | 9.03 |  | 7.54 | [8 empty] | 16.57 |  |  |  |  | 0.00
1990 |  |  |  | 8218.24 |  |  | 7798 |  |  |  | 1137 | [10 empty] | 89.18 |  |  |  | 89.18 | [5 empty] | 82.51 |  |  | 89.02 |  |  |  | 10.63 |  | 10.60 | [8 empty] | 0.22 |  |  |  |  | 0.00
1991 |  |  |  | 2876.71 |  |  | 2850 |  |  |  | 1137 | [10 empty] | 33.57 |  |  |  | 33.57 | [5 empty] | 28.88 |  |  | 32.53 |  |  |  | 58.17 |  | 46.68 | [8 empty] | 19.76 |  |  |  |  | 0.00
1992 |  |  |  | 6593.81 |  |  | 6311 |  |  |  | 1137 | [10 empty] | 72.11 |  |  |  | 72.11 | [5 empty] | 66.02 |  |  | 71.85 |  |  |  | 23.89 |  | 22.64 | [8 empty] | 5.25 |  |  |  |  | 0.00
1993 |  |  |  | 6502.83 |  |  | 6106 |  |  |  | 1137 | [10 empty] | 70.15 |  |  |  | 70.15 | [5 empty] | 65.29 |  |  | 69.70 |  |  |  | 4.20 |  | 3.08 | [8 empty] | 26.77 |  |  |  |  | 0.00
1994 |  |  |  | 9416.15 |  |  | 8426 |  |  |  | 1137 | [10 empty] | 96.26 |  |  |  | 96.26 | [5 empty] | 94.54 |  |  | 96.19 |  |  |  | 3.74 |  | 3.74 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 7993.62 |  |  | 7083 |  |  |  | 1137 | [10 empty] | 81.20 |  |  |  | 81.20 | [5 empty] | 80.26 |  |  | 80.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.80 |  |  |  |  | 0.00
1996 |  |  |  | 2476.71 |  |  | 2156 |  |  |  | 1137 | [10 empty] | 25.68 |  |  |  | 25.68 | [5 empty] | 24.80 |  |  | 24.54 |  |  |  | 74.32 |  | 74.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1137 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 3392.06 |  |  | 3402 |  |  |  | 1137 | [10 empty] | 38.87 |  |  |  | 38.87 | [5 empty] | 34.06 |  |  | 38.84 |  |  |  | 61.01 |  | 60.83 | [8 empty] | 0.30 |  |  |  |  | 0.00
1999 |  |  |  | 8307.55 |  |  | 7329 |  |  |  | 1139 | [10 empty] | 83.67 |  |  |  | 83.67 | [5 empty] | 83.21 |  |  | 83.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.33 |  |  |  |  | 0.00
2000 |  |  |  | 10125.72 |  |  | 8784 |  |  |  | 1151 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.09 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 8169.69 |  |  | 7392 |  |  |  | 1136 | [10 empty] | 84.33 |  |  |  | 84.33 | [5 empty] | 81.35 |  |  | 84.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.67 |  |  |  |  | 0.00
2002 |  |  |  | 8746.21 |  |  | 7803 |  |  |  | 1130 | [10 empty] | 88.96 |  |  |  | 88.96 | [5 empty] | 88.12 |  |  | 89.08 |  |  |  | 2.70 |  | 2.47 | [8 empty] | 8.57 |  |  |  |  | 0.00
2003 |  |  |  | 10005.70 |  |  | 8729 |  |  |  | 1130 | [10 empty] | 99.65 |  |  |  | 99.65 | [5 empty] | 101.08 |  |  | 99.65 |  |  |  | 0.35 |  | 0.35 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 8983.70 |  |  | 7905 |  |  |  | 1148 | [10 empty] | 90.06 |  |  |  | 90.06 | [5 empty] | 89.91 |  |  | 89.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.94 |  |  |  |  | 0.00
2005 |  |  |  | 8766.99 |  |  | 7677 |  |  |  | 1131 | [10 empty] | 87.65 |  |  |  | 88.04 | [5 empty] | 88.49 |  |  | 87.64 |  |  |  | 4.98 |  | 4.61 | [8 empty] | 7.34 |  |  |  |  | 0.40
2006 |  |  |  | 10111.10 |  |  | 8760 |  |  |  | 1155 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.93 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 8699.38 |  |  | 7694 |  |  |  | 1145 | [10 empty] | 87.74 |  |  |  | 87.74 | [5 empty] | 86.73 |  |  | 87.83 |  |  |  | 0.62 |  | 0.55 | [8 empty] | 11.71 |  |  |  |  | 0.00
2008 |  |  |  | 8850.30 |  |  | 7739 |  |  |  | 1145 | [10 empty] | 88.12 |  |  |  | 88.12 | [5 empty] | 88.00 |  |  | 88.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.88 |  |  |  |  | 0.00
2009 |  |  |  | 10418.22 |  |  | 8470 |  |  |  | 1137 | [10 empty] | 96.68 |  |  |  | 96.68 | [5 empty] | 104.60 |  |  | 96.69 |  |  |  | 3.32 |  | 3.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 9335.74 |  |  | 7623 |  |  |  | 1233 | [10 empty] | 88.05 |  |  |  | 88.05 | [5 empty] | 86.43 |  |  | 87.02 |  |  |  | 2.61 |  | 2.36 | [8 empty] | 9.59 |  |  |  |  | 0.00
2011 |  |  |  | 9365.73 |  |  | 7674 |  |  |  | 1233 | [10 empty] | 87.61 |  |  |  | 87.61 | [5 empty] | 86.71 |  |  | 87.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.39 |  |  |  |  | 0.00
2012 |  |  |  | 10776.49 |  |  | 8784 |  |  |  | 1218 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.73 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 9542.43 |  |  | 7803 |  |  |  | 1210 | [10 empty] | 89.01 |  |  |  | 89.01 | [5 empty] | 89.92 |  |  | 89.07 |  |  |  | 1.41 |  | 1.28 | [8 empty] | 9.71 |  |  |  |  | 0.00
2014 |  |  |  | 9360.53 |  |  | 7676 |  |  |  | 1218 | [10 empty] | 89.99 |  |  |  | 89.99 | [5 empty] | 87.73 |  |  | 87.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.01 |  |  |  |  | 0.00
2015 |  |  |  | 10677.97 |  |  | 8760 |  |  |  | 1229 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.18 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 9140.32 |  |  | 7539 |  |  |  | 1229 | [10 empty] | 85.83 |  |  |  | 85.83 | [5 empty] | 84.67 |  |  | 85.83 |  |  |  | 5.47 |  | 4.96 | [8 empty] | 9.21 |  |  |  |  | 0.00
2017 |  |  |  | 9740.29 |  |  | 7972 |  |  |  | 1229 | [10 empty] | 91.00 |  |  |  | 91.00 | [5 empty] | 90.47 |  |  | 91.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.00 |  |  |  |  | 0.00
2018 |  |  |  | 10758.28 |  |  | 8760 |  |  |  | 1210 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.50 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 9516.62 |  |  | 7834 |  |  |  | 1210 | [10 empty] | 89.45 |  |  |  | 89.45 | [5 empty] | 89.78 |  |  | 89.43 |  |  |  | 1.63 |  | 1.48 | [8 empty] | 9.06 |  |  |  |  | 0.00
2020 |  |  |  | 9024.35 |  |  | 7438 |  |  |  | 1210 | [10 empty] | 85.13 |  |  |  | 85.13 | [5 empty] | 84.91 |  |  | 84.68 |  |  |  | 3.54 |  | 3.12 | [8 empty] | 11.75 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 413
B. |  | Refuelling without maintenance | [20 empty] | 1280 | [14 empty] | 38
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 661
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 45
E. |  | Testing of plant systems or components | [35 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 258
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 5
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 22
Z. |  | Other | [24 empty] | 305 | [14 empty] | 259
Subtotal | [22 empty] | 1280 |  |  |  | 305 | [10 empty] | 746 |  |  |  | 935 | [11 empty] | 28
Total | [22 empty] | 1585 | [14 empty] | 1709
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 16
14. |  |  | Safety Systems | [34 empty] | 327
15. |  |  | Reactor Cooling Systems | [34 empty] | 43
16. |  |  | Steam generation systems | [34 empty] | 26
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 12
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
33. |  |  | Circulating Water System | [34 empty] | 18
34. |  |  | Miscellaneous Systems | [34 empty] | 115
41. |  |  | Main Generator Systems | [34 empty] | 21
42. |  |  | Electrical Power Supply Systems | [34 empty] | 11
Total | [37 empty] | 623
Highlights (2020)
Refueling Outage 20.

## MONTICELLO
2020 Operating Experience
US-263 | [8 empty] | MONTICELLO | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NSP (Northern States Power Co. (subsidiary of Xcel Energy))
Owner | [7 empty] | : | XCEL (Xcel Energy)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-3 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-06-19
Thermal power | [12 empty] | : |  |  | 2004 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1971-03-05
Gross electrical power | [12 empty] | : |  |  | 691 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1971-06-30
Reference unit power (net) | [12 empty] | : |  |  | 628 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.17
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 285
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.394
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 75 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 27000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.96 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.78
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 484 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 39 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 121 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5593.31 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.4 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 489.49 | 456.93 |  |  |  | 483.71 |  | 468.63 | [8 empty] | 473.91 |  |  | 444.35 | [6 empty] | 445.85 |  | 465.95 |  |  |  | 457.07 |  |  | 445.78 |  |  | 474.41 | [9 empty] | 487.26 |  |  | 5593.31
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 104.76 | 104.54 |  |  |  | 103.53 |  | 103.64 | [8 empty] | 101.43 |  |  | 98.27 | [6 empty] | 95.42 |  | 99.72 |  |  |  | 101.09 |  |  | 95.41 |  |  | 104.92 | [9 empty] | 104.29 |  |  | 101.40
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 204006.83 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.83 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.51 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.94 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.92 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1971 |  |  |  | 1465.90 |  |  | 3357 |  |  |  | 564 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 50.25 |  |  | 59.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1972 |  |  |  | 3717.90 |  |  | 6975 |  |  |  | 580 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 72.98 |  |  | 79.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 3271.60 |  |  | 6242 |  |  |  | 580 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 64.39 |  |  | 71.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1974 |  |  |  | 2925.20 |  |  | 6567 |  |  |  | 538 | [10 empty] | 74.98 |  |  |  | 74.98 | [5 empty] | 62.07 |  |  | 74.97 |  |  |  | 8.03 |  | 6.55 | [8 empty] | 18.47 |  |  |  |  | 0.00
1975 |  |  |  | 2881.40 |  |  | 6322 |  |  |  | 538 | [10 empty] | 61.05 |  |  |  | 61.05 | [5 empty] | 61.14 |  |  | 72.17 |  |  |  | 5.95 |  | 3.86 | [8 empty] | 35.09 |  |  |  |  | 0.00
1976 |  |  |  | 3986.20 |  |  | 8033 |  |  |  | 537 | [10 empty] | 84.30 |  |  |  | 84.30 | [5 empty] | 84.51 |  |  | 91.45 |  |  |  | 2.80 |  | 2.43 | [8 empty] | 13.27 |  |  |  |  | 0.00
1977 |  |  |  | 3570.70 |  |  | 7001 |  |  |  | 536 | [10 empty] | 75.95 |  |  |  | 75.95 | [5 empty] | 76.05 |  |  | 79.92 |  |  |  | 0.77 |  | 0.59 | [8 empty] | 23.46 |  |  |  |  | 0.00
1978 |  |  |  | 3856.20 |  |  | 7638 |  |  |  | 536 | [10 empty] | 81.70 |  |  |  | 81.70 | [5 empty] | 82.13 |  |  | 87.19 |  |  |  | 5.75 |  | 4.98 | [8 empty] | 13.32 |  |  |  |  | 0.00
1979 |  |  |  | 4399.70 |  |  | 8549 |  |  |  | 536 | [10 empty] | 93.41 |  |  |  | 93.41 | [5 empty] | 93.70 |  |  | 97.59 |  |  |  | 3.13 |  | 3.02 | [8 empty] | 3.57 |  |  |  |  | 0.00
1980 |  |  |  | 3455.50 |  |  | 6876 |  |  |  | 536 | [10 empty] | 78.22 |  |  |  | 79.04 | [5 empty] | 73.39 |  |  | 78.28 |  |  |  | 7.46 |  | 6.37 | [8 empty] | 14.59 |  |  |  |  | 0.81
1981 |  |  |  | 3262.30 |  |  | 6362 |  |  |  | 536 | [10 empty] | 72.34 |  |  |  | 72.34 | [5 empty] | 69.48 |  |  | 72.63 |  |  |  | 2.11 |  | 1.56 | [8 empty] | 26.11 |  |  |  |  | 0.00
1982 |  |  |  | 2425.10 |  |  | 5543 |  |  |  | 525 | [10 empty] | 62.22 |  |  |  | 62.22 | [5 empty] | 52.73 |  |  | 63.28 |  |  |  | 1.82 |  | 1.15 | [8 empty] | 36.63 |  |  |  |  | 0.00
1983 |  |  |  | 4147.70 |  |  | 8438 |  |  |  | 525 | [10 empty] | 96.29 |  |  |  | 96.29 | [5 empty] | 90.19 |  |  | 96.32 |  |  |  | 0.22 |  | 0.21 | [8 empty] | 3.50 |  |  |  |  | 0.00
1984 |  |  |  | 279.13 |  |  | 808 |  |  |  | 525 | [10 empty] | 9.21 |  |  |  | 9.21 | [5 empty] | 6.05 |  |  | 9.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 90.79 |  |  |  |  | 0.00
1985 |  |  |  | 4286.99 |  |  | 8028 |  |  |  | 536 | [10 empty] | 91.63 |  |  |  | 91.63 | [5 empty] | 91.30 |  |  | 91.64 |  |  |  | 0.58 |  | 0.54 | [8 empty] | 7.84 |  |  |  |  | 0.00
1986 |  |  |  | 3379.91 |  |  | 6926 |  |  |  | 536 | [10 empty] | 78.77 |  |  |  | 78.77 | [5 empty] | 71.98 |  |  | 79.06 |  |  |  | 0.81 |  | 0.65 | [8 empty] | 20.59 |  |  |  |  | 0.00
1987 |  |  |  | 3535.62 |  |  | 7051 |  |  |  | 536 | [10 empty] | 80.23 |  |  |  | 80.23 | [5 empty] | 75.30 |  |  | 80.49 |  |  |  | 2.07 |  | 1.70 | [8 empty] | 18.07 |  |  |  |  | 0.00
1988 |  |  |  | 4573.58 |  |  | 8759 |  |  |  | 536 | [10 empty] | 99.71 |  |  |  | 99.71 | [5 empty] | 97.14 |  |  | 99.72 |  |  |  | 0.29 |  | 0.29 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 2650.40 |  |  | 6578 |  |  |  | 536 | [10 empty] | 74.73 |  |  |  | 74.73 | [5 empty] | 56.45 |  |  | 75.09 |  |  |  | 1.95 |  | 1.49 | [8 empty] | 23.79 |  |  |  |  | 0.00
1990 |  |  |  | 4505.93 |  |  | 8414 |  |  |  | 536 | [10 empty] | 96.00 |  |  |  | 96.00 | [5 empty] | 95.97 |  |  | 96.05 |  |  |  | 2.54 |  | 2.50 | [8 empty] | 1.49 |  |  |  |  | 0.00
1991 |  |  |  | 3596.53 |  |  | 6996 |  |  |  | 536 | [10 empty] | 79.56 |  |  |  | 79.56 | [5 empty] | 76.60 |  |  | 79.86 |  |  |  | 3.15 |  | 2.58 | [8 empty] | 17.85 |  |  |  |  | 0.00
1992 |  |  |  | 4453.67 |  |  | 8527 |  |  |  | 536 | [10 empty] | 97.04 |  |  |  | 97.04 | [5 empty] | 94.59 |  |  | 97.07 |  |  |  | 1.03 |  | 1.01 | [8 empty] | 1.95 |  |  |  |  | 0.00
1993 |  |  |  | 3864.38 |  |  | 7322 |  |  |  | 536 | [10 empty] | 83.37 |  |  |  | 83.37 | [5 empty] | 82.30 |  |  | 83.58 |  |  |  | 1.49 |  | 1.26 | [8 empty] | 15.36 |  |  |  |  | 0.00
1994 |  |  |  | 3956.18 |  |  | 7508 |  |  |  | 536 | [10 empty] | 85.55 |  |  |  | 85.55 | [5 empty] | 84.26 |  |  | 85.71 |  |  |  | 2.88 |  | 2.54 | [8 empty] | 11.91 |  |  |  |  | 0.00
1995 |  |  |  | 4756.26 |  |  | 8760 |  |  |  | 536 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.30 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 3872.94 |  |  | 7443 |  |  |  | 541 | [10 empty] | 84.76 |  |  |  | 84.76 | [5 empty] | 81.37 |  |  | 84.73 |  |  |  | 3.99 |  | 3.52 | [8 empty] | 11.72 |  |  |  |  | 0.00
1997 |  |  |  | 3661.60 |  |  | 6609 |  |  |  | 544 | [10 empty] | 75.23 |  |  |  | 75.23 | [5 empty] | 76.84 |  |  | 75.45 |  |  |  | 24.77 |  | 24.77 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 4118.93 |  |  | 7659 |  |  |  | 553 | [10 empty] | 87.68 |  |  |  | 87.68 | [5 empty] | 84.91 |  |  | 87.43 |  |  |  | 2.70 |  | 2.43 | [8 empty] | 9.89 |  |  |  |  | 0.00
1999 |  |  |  | 4649.34 |  |  | 8092 |  |  |  | 578 | [10 empty] | 92.38 |  |  |  | 92.38 | [5 empty] | 91.82 |  |  | 92.37 |  |  |  | 7.62 |  | 7.62 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 4251.42 |  |  | 7332 |  |  |  | 578 | [10 empty] | 83.49 |  |  |  | 83.49 | [5 empty] | 83.74 |  |  | 83.47 |  |  |  | 1.85 |  | 1.57 | [8 empty] | 14.94 |  |  |  |  | 0.00
2001 |  |  |  | 3880.58 |  |  | 6774 |  |  |  | 578 | [10 empty] | 76.90 |  |  |  | 76.90 | [5 empty] | 76.64 |  |  | 77.33 |  |  |  | 12.66 |  | 11.14 | [8 empty] | 11.96 |  |  |  |  | 0.00
2002 |  |  |  | 5015.56 |  |  | 8620 |  |  |  | 578 | [10 empty] | 98.35 |  |  |  | 98.35 | [5 empty] | 99.06 |  |  | 98.40 |  |  |  | 1.65 |  | 1.65 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 4592.46 |  |  | 7969 |  |  |  | 578 | [10 empty] | 90.70 |  |  |  | 90.70 | [5 empty] | 90.70 |  |  | 90.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.30 |  |  |  |  | 0.00
2004 |  |  |  | 5034.88 |  |  | 8689 |  |  |  | 578 | [10 empty] | 98.94 |  |  |  | 98.94 | [5 empty] | 99.17 |  |  | 98.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.06 |  |  |  |  | 0.00
2005 |  |  |  | 4474.92 |  |  | 7826 |  |  |  | 569 | [10 empty] | 89.35 |  |  |  | 89.35 | [5 empty] | 89.77 |  |  | 89.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.65 |  |  |  |  | 0.00
2006 |  |  |  | 5072.59 |  |  | 8760 |  |  |  | 572 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.23 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 4192.27 |  |  | 7327 |  |  |  | 572 | [10 empty] | 83.66 |  |  |  | 83.66 | [5 empty] | 83.67 |  |  | 83.64 |  |  |  | 4.35 |  | 3.81 | [8 empty] | 12.53 |  |  |  |  | 0.00
2008 |  |  |  | 4878.02 |  |  | 8398 |  |  |  | 572 | [10 empty] | 95.61 |  |  |  | 95.61 | [5 empty] | 97.09 |  |  | 95.61 |  |  |  | 4.39 |  | 4.39 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 4144.69 |  |  | 7421 |  |  |  | 572 | [10 empty] | 84.73 |  |  |  | 84.73 | [5 empty] | 82.72 |  |  | 84.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.27 |  |  |  |  | 0.00
2010 |  |  |  | 4695.11 |  |  | 8504 |  |  |  | 572 | [10 empty] | 97.08 |  |  |  | 97.08 | [5 empty] | 93.70 |  |  | 97.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.92 |  |  |  |  | 0.00
2011 |  |  |  | 3358.49 |  |  | 6045 |  |  |  | 572 | [10 empty] | 69.04 |  |  |  | 69.04 | [5 empty] | 67.03 |  |  | 69.01 |  |  |  | 11.16 |  | 8.67 | [8 empty] | 22.29 |  |  |  |  | 0.00
2012 |  |  |  | 4890.37 |  |  | 8552 |  |  |  | 578 | [10 empty] | 97.36 |  |  |  | 97.36 | [5 empty] | 96.32 |  |  | 97.36 |  |  |  | 2.64 |  | 2.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 2998.28 |  |  | 5419 |  |  |  | 578 | [10 empty] | 61.87 |  |  |  | 61.87 | [5 empty] | 59.21 |  |  | 61.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 38.13 |  |  |  |  | 0.00
2014 |  |  |  | 4323.97 |  |  | 8304 |  |  |  | 647 | [10 empty] | 94.79 |  |  |  | 94.79 | [5 empty] | 76.29 |  |  | 94.79 |  |  |  | 5.21 |  | 5.21 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 4663.53 |  |  | 7407 |  |  |  | 647 | [10 empty] | 84.55 |  |  |  | 84.55 | [5 empty] | 82.28 |  |  | 84.55 |  |  |  | 2.39 |  | 2.07 | [8 empty] | 13.38 |  |  |  |  | 0.00
2016 |  |  |  | 5597.76 |  |  | 8784 |  |  |  | 647 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.50 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 5159.59 |  |  | 8051 |  |  |  | 647 | [10 empty] | 91.91 |  |  |  | 91.91 | [5 empty] | 91.03 |  |  | 91.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.09 |  |  |  |  | 0.00
2018 |  |  |  | 5618.02 |  |  | 8691 |  |  |  | 628 | [10 empty] | 99.21 |  |  |  | 99.21 | [5 empty] | 102.12 |  |  | 99.21 |  |  |  | 0.79 |  | 0.79 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 4964.57 |  |  | 8023 |  |  |  | 628 | [10 empty] | 91.59 |  |  |  | 91.59 | [5 empty] | 90.24 |  |  | 91.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.41 |  |  |  |  | 0.00
2020 |  |  |  | 5593.31 |  |  | 8783 |  |  |  | 628 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.40 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1971 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 215
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 924
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 92
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 22
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 7
Z. |  | Other | [35 empty] | 1 |  |  |  | 44
Subtotal | [37 empty] | 1019 |  |  |  | 294 | [11 empty] | 1
Total | [22 empty] | 0 | [14 empty] | 1314
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1971 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 8
12. |  |  | Reactor I&C Systems | [34 empty] | 19
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 18
14. |  |  | Safety Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [34 empty] | 22
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 35
32. |  |  | Feedwater and Main Steam System | [34 empty] | 45
33. |  |  | Circulating Water System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 37
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 12
42. |  |  | Electrical Power Supply Systems | [34 empty] | 26
Total | [37 empty] | 246

## NINE MILE POINT-1
2020 Operating Experience
US-220 | [8 empty] | NINE MILE POINT-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXE/EDF (Exelon Nuclear, Électricité de France)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-2 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1965-04-12
Thermal power | [12 empty] | : |  |  | 1850 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1969-11-09
Gross electrical power | [12 empty] | : |  |  | 642 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1969-12-01
Reference unit power (net) | [12 empty] | : |  |  | 613 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 51 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.13
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 285
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.436
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 34 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 26000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.79
| Active core height/length [m] | [13 empty] | : |  |  | 3.7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 532 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 129 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 5 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5473 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.64 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 470.59 | 440.35 |  |  |  | 470.68 |  | 453.50 | [8 empty] | 469.56 |  |  | 446.94 | [6 empty] | 448.80 |  | 446.63 |  |  |  | 439.13 |  |  | 461.48 |  |  | 454.77 | [9 empty] | 470.59 |  |  | 5473.00
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 103.18 | 103.21 |  |  |  | 103.20 |  | 102.75 | [8 empty] | 102.96 |  |  | 101.26 | [6 empty] | 98.41 |  | 97.93 |  |  |  | 99.50 |  |  | 101.18 |  |  | 103.04 | [9 empty] | 103.18 |  |  | 101.64
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 201733.9 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.91 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.14 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.91 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.96 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.93 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.75 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1969 |  |  |  | Data not provided
1970 |  |  |  | 1581.00 |  |  | 3443 |  |  |  | 525 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 34.38 |  |  | 39.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1971 |  |  |  | 3033.10 |  |  | 5963 |  |  |  | 592 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 58.49 |  |  | 68.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1972 |  |  |  | 3344.80 |  |  | 6101 |  |  |  | 630 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 60.44 |  |  | 69.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 3494.20 |  |  | 6682 |  |  |  | 610 | [10 empty] | 76.41 |  |  |  | 76.41 | [5 empty] | 65.39 |  |  | 76.28 |  |  |  | 7.94 |  | 6.59 | [8 empty] | 17.00 |  |  |  |  | 0.00
1974 |  |  |  | 3278.70 |  |  | 6177 |  |  |  | 610 | [10 empty] | 70.50 |  |  |  | 70.50 | [5 empty] | 61.36 |  |  | 70.51 |  |  |  | 4.91 |  | 3.64 | [8 empty] | 25.86 |  |  |  |  | 0.00
1975 |  |  |  | 3044.90 |  |  | 6235 |  |  |  | 610 | [10 empty] | 57.03 |  |  |  | 57.03 | [5 empty] | 56.98 |  |  | 71.18 |  |  |  | 17.76 |  | 12.32 | [8 empty] | 30.66 |  |  |  |  | 0.00
1976 |  |  |  | 4112.80 |  |  | 7724 |  |  |  | 610 | [10 empty] | 76.79 |  |  |  | 76.79 | [5 empty] | 76.76 |  |  | 87.93 |  |  |  | 18.88 |  | 17.88 | [8 empty] | 5.33 |  |  |  |  | 0.00
1977 |  |  |  | 2956.80 |  |  | 5171 |  |  |  | 610 | [10 empty] | 55.39 |  |  |  | 55.39 | [5 empty] | 55.33 |  |  | 59.03 |  |  |  | 2.16 |  | 1.22 | [8 empty] | 43.39 |  |  |  |  | 0.00
1978 |  |  |  | 4467.40 |  |  | 8329 |  |  |  | 610 | [10 empty] | 83.60 |  |  |  | 83.60 | [5 empty] | 83.60 |  |  | 95.08 |  |  |  | 4.41 |  | 3.86 | [8 empty] | 12.54 |  |  |  |  | 0.00
1979 |  |  |  | 3005.40 |  |  | 5785 |  |  |  | 610 | [10 empty] | 56.24 |  |  |  | 56.24 | [5 empty] | 56.24 |  |  | 66.04 |  |  |  | 5.91 |  | 3.53 | [8 empty] | 40.23 |  |  |  |  | 0.00
1980 |  |  |  | 4537.30 |  |  | 8097 |  |  |  | 610 | [10 empty] | 92.16 |  |  |  | 92.16 | [5 empty] | 84.68 |  |  | 92.18 |  |  |  | 4.77 |  | 4.61 | [8 empty] | 3.22 |  |  |  |  | 0.00
1981 |  |  |  | 3270.30 |  |  | 5780 |  |  |  | 610 | [10 empty] | 65.61 |  |  |  | 65.61 | [5 empty] | 61.20 |  |  | 65.98 |  |  |  | 1.79 |  | 1.20 | [8 empty] | 33.19 |  |  |  |  | 0.00
1982 |  |  |  | 1134.80 |  |  | 1872 |  |  |  | 610 | [10 empty] | 21.47 |  |  |  | 21.47 | [5 empty] | 21.24 |  |  | 21.37 |  |  |  | 78.19 |  | 76.99 | [8 empty] | 1.54 |  |  |  |  | 0.00
1983 |  |  |  | 2802.00 |  |  | 4925 |  |  |  | 610 | [10 empty] | 56.21 |  |  |  | 56.21 | [5 empty] | 52.44 |  |  | 56.22 |  |  |  | 43.79 |  | 43.79 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 3635.23 |  |  | 6316 |  |  |  | 610 | [10 empty] | 71.61 |  |  |  | 71.61 | [5 empty] | 67.84 |  |  | 71.90 |  |  |  | 3.95 |  | 2.94 | [8 empty] | 25.45 |  |  |  |  | 0.00
1985 |  |  |  | 4932.30 |  |  | 8441 |  |  |  | 610 | [10 empty] | 96.37 |  |  |  | 96.37 | [5 empty] | 92.30 |  |  | 96.36 |  |  |  | 3.63 |  | 3.63 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 3146.88 |  |  | 5722 |  |  |  | 610 | [10 empty] | 64.95 |  |  |  | 64.95 | [5 empty] | 58.89 |  |  | 65.32 |  |  |  | 8.55 |  | 6.07 | [8 empty] | 28.98 |  |  |  |  | 0.00
1987 |  |  |  | 4615.17 |  |  | 8130 |  |  |  | 610 | [10 empty] | 92.81 |  |  |  | 92.81 | [5 empty] | 86.37 |  |  | 92.81 |  |  |  | 7.19 |  | 7.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 0.00 |  |  | 0 |  |  |  | 610 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 5.87 | [8 empty] | 94.13 |  |  |  |  | 0.00
1989 |  |  |  | 0.00 |  |  | 0 |  |  |  | 610 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1990 |  |  |  | 1316.68 |  |  | 3043 |  |  |  | 612 | [10 empty] | 34.24 |  |  |  | 34.24 | [5 empty] | 24.56 |  |  | 34.74 |  |  |  | 65.54 |  | 65.11 | [8 empty] | 0.66 |  |  |  |  | 0.00
1991 |  |  |  | 3873.51 |  |  | 6853 |  |  |  | 615 | [10 empty] | 78.22 |  |  |  | 78.22 | [5 empty] | 71.90 |  |  | 78.23 |  |  |  | 9.02 |  | 7.75 | [8 empty] | 14.03 |  |  |  |  | 0.00
1992 |  |  |  | 2930.09 |  |  | 5052 |  |  |  | 615 | [10 empty] | 57.41 |  |  |  | 57.41 | [5 empty] | 54.24 |  |  | 57.51 |  |  |  | 42.54 |  | 42.51 | [8 empty] | 0.08 |  |  |  |  | 0.00
1993 |  |  |  | 4353.36 |  |  | 7370 |  |  |  | 615 | [10 empty] | 84.08 |  |  |  | 84.08 | [5 empty] | 80.81 |  |  | 84.13 |  |  |  | 0.72 |  | 0.61 | [8 empty] | 15.31 |  |  |  |  | 0.00
1994 |  |  |  | 4917.95 |  |  | 8390 |  |  |  | 565 | [10 empty] | 95.42 |  |  |  | 95.42 | [5 empty] | 99.36 |  |  | 95.78 |  |  |  | 4.58 |  | 4.58 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 4127.64 |  |  | 7381 |  |  |  | 565 | [10 empty] | 82.86 |  |  |  | 82.86 | [5 empty] | 83.40 |  |  | 84.26 |  |  |  | 1.76 |  | 1.48 | [8 empty] | 15.66 |  |  |  |  | 0.00
1996 |  |  |  | 4676.17 |  |  | 8133 |  |  |  | 565 | [10 empty] | 91.98 |  |  |  | 91.98 | [5 empty] | 94.22 |  |  | 92.59 |  |  |  | 6.65 |  | 6.55 | [8 empty] | 1.47 |  |  |  |  | 0.00
1997 |  |  |  | 2698.57 |  |  | 4620 |  |  |  | 565 | [10 empty] | 51.77 |  |  |  | 51.77 | [5 empty] | 54.52 |  |  | 52.74 |  |  |  | 36.61 |  | 29.90 | [8 empty] | 18.33 |  |  |  |  | 0.00
1998 |  |  |  | 4845.98 |  |  | 8085 |  |  |  | 565 | [10 empty] | 92.31 |  |  |  | 92.31 | [5 empty] | 97.91 |  |  | 92.29 |  |  |  | 7.69 |  | 7.69 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 3564.86 |  |  | 6162 |  |  |  | 565 | [10 empty] | 68.37 |  |  |  | 68.37 | [5 empty] | 72.03 |  |  | 70.34 |  |  |  | 12.16 |  | 9.47 | [8 empty] | 22.17 |  |  |  |  | 0.00
2000 |  |  |  | 4681.85 |  |  | 8060 |  |  |  | 565 | [10 empty] | 91.00 |  |  |  | 91.00 | [5 empty] | 94.34 |  |  | 91.76 |  |  |  | 1.53 |  | 1.41 | [8 empty] | 7.58 |  |  |  |  | 0.00
2001 |  |  |  | 4378.01 |  |  | 7376 |  |  |  | 565 | [10 empty] | 83.52 |  |  |  | 83.52 | [5 empty] | 88.46 |  |  | 84.20 |  |  |  | 2.47 |  | 2.12 | [8 empty] | 14.36 |  |  |  |  | 0.00
2002 |  |  |  | 4904.56 |  |  | 8194 |  |  |  | 565 | [10 empty] | 92.90 |  |  |  | 92.90 | [5 empty] | 99.09 |  |  | 93.54 |  |  |  | 6.14 |  | 6.07 | [8 empty] | 1.03 |  |  |  |  | 0.00
2003 |  |  |  | 4361.37 |  |  | 7373 |  |  |  | 565 | [10 empty] | 83.61 |  |  |  | 83.61 | [5 empty] | 88.12 |  |  | 84.17 |  |  |  | 3.65 |  | 3.17 | [8 empty] | 13.22 |  |  |  |  | 0.00
2004 |  |  |  | 4988.21 |  |  | 8258 |  |  |  | 565 | [10 empty] | 93.46 |  |  |  | 93.46 | [5 empty] | 100.51 |  |  | 94.01 |  |  |  | 1.22 |  | 1.15 | [8 empty] | 5.39 |  |  |  |  | 0.00
2005 |  |  |  | 4589.79 |  |  | 7667 |  |  |  | 621 | [10 empty] | 87.55 |  |  |  | 87.55 | [5 empty] | 84.36 |  |  | 87.51 |  |  |  | 1.49 |  | 1.33 | [8 empty] | 11.12 |  |  |  |  | 0.00
2006 |  |  |  | 5346.94 |  |  | 8713 |  |  |  | 621 | [10 empty] | 99.47 |  |  |  | 99.47 | [5 empty] | 98.29 |  |  | 99.46 |  |  |  | 0.53 |  | 0.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 4762.88 |  |  | 7910 |  |  |  | 621 | [10 empty] | 90.31 |  |  |  | 90.31 | [5 empty] | 87.55 |  |  | 90.30 |  |  |  | 1.59 |  | 1.46 | [8 empty] | 8.23 |  |  |  |  | 0.00
2008 |  |  |  | 5341.42 |  |  | 8707 |  |  |  | 621 | [10 empty] | 99.13 |  |  |  | 99.13 | [5 empty] | 97.92 |  |  | 99.12 |  |  |  | 0.87 |  | 0.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 4992.58 |  |  | 8216 |  |  |  | 621 | [10 empty] | 93.81 |  |  |  | 93.81 | [5 empty] | 91.78 |  |  | 93.79 |  |  |  | 0.87 |  | 0.82 | [8 empty] | 5.37 |  |  |  |  | 0.00
2010 |  |  |  | 5294.08 |  |  | 8677 |  |  |  | 621 | [10 empty] | 99.06 |  |  |  | 99.06 | [5 empty] | 97.32 |  |  | 99.05 |  |  |  | 0.94 |  | 0.94 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 4595.11 |  |  | 7671 |  |  |  | 621 | [10 empty] | 87.59 |  |  |  | 87.59 | [5 empty] | 84.47 |  |  | 87.57 |  |  |  | 4.71 |  | 4.33 | [8 empty] | 8.08 |  |  |  |  | 0.00
2012 |  |  |  | 4798.45 |  |  | 7951 |  |  |  | 621 | [10 empty] | 90.57 |  |  |  | 90.57 | [5 empty] | 87.97 |  |  | 90.52 |  |  |  | 8.49 |  | 8.40 | [8 empty] | 1.02 |  |  |  |  | 0.00
2013 |  |  |  | 4868.75 |  |  | 7933 |  |  |  | 621 | [10 empty] | 90.56 |  |  |  | 90.56 | [5 empty] | 89.49 |  |  | 90.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.44 |  |  |  |  | 0.00
2014 |  |  |  | 5400.06 |  |  | 8760 |  |  |  | 621 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.27 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 4903.16 |  |  | 8039 |  |  |  | 613 | [10 empty] | 91.66 |  |  |  | 91.66 | [5 empty] | 91.31 |  |  | 91.77 |  |  |  | 1.10 |  | 1.02 | [8 empty] | 7.32 |  |  |  |  | 0.00
2016 |  |  |  | 5342.98 |  |  | 8721 |  |  |  | 613 | [10 empty] | 99.28 |  |  |  | 99.28 | [5 empty] | 99.23 |  |  | 99.28 |  |  |  | 0.72 |  | 0.72 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 4885.28 |  |  | 8290 |  |  |  | 613 | [10 empty] | 94.64 |  |  |  | 94.64 | [5 empty] | 90.98 |  |  | 94.63 |  |  |  | 0.70 |  | 0.67 | [8 empty] | 4.69 |  |  |  |  | 0.00
2018 |  |  |  | 5313.34 |  |  | 8684 |  |  |  | 613 | [10 empty] | 99.20 |  |  |  | 99.20 | [5 empty] | 98.95 |  |  | 99.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.80 |  |  |  |  | 0.00
2019 |  |  |  | 4574.14 |  |  | 7646 |  |  |  | 613 | [10 empty] | 87.30 |  |  |  | 87.30 | [5 empty] | 85.18 |  |  | 87.28 |  |  |  | 1.94 |  | 1.73 | [8 empty] | 10.98 |  |  |  |  | 0.00
2020 |  |  |  | 5473.00 |  |  | 8783 |  |  |  | 613 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.64 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1969 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 588
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1031
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 111
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 8
L. |  | Human factor related | [39 empty] | 23
Z. |  | Other | [35 empty] | 4 |  |  |  | 107
Subtotal | [37 empty] | 1150 |  |  |  | 727
Total | [22 empty] | 0 | [14 empty] | 1877
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1969 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 29
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 23
14. |  |  | Safety Systems | [34 empty] | 96
15. |  |  | Reactor Cooling Systems | [34 empty] | 257
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [34 empty] | 72
32. |  |  | Feedwater and Main Steam System | [34 empty] | 47
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 14
42. |  |  | Electrical Power Supply Systems | [34 empty] | 25
Total | [37 empty] | 593

## NINE MILE POINT-2
2020 Operating Experience
US-410 | [8 empty] | NINE MILE POINT-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXE/EDF (Exelon Nuclear, Électricité de France)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-5 (Mark 2) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-08-01
Thermal power | [12 empty] | : |  |  | 3988 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-08-08
Gross electrical power | [12 empty] | : |  |  | 1320 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-03-11
Reference unit power (net) | [12 empty] | : |  |  | 1277 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.17
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.316
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 26 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 32300 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.78
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.68 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10167.61 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.31 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.75 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.22 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.75 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.03 %
Load Factor (LF) | [18 empty] | : | 90.64 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.75 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 725 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 957.50 | 842.76 |  |  |  | 97.10 |  | 770.32 | [8 empty] | 953.76 |  |  | 914.22 | [6 empty] | 935.08 |  | 937.88 |  |  |  | 916.92 |  |  | 953.60 |  |  | 927.46 | [9 empty] | 961.00 |  |  | 10167.61
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 11.44 |  | 90.93 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.75
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 11.44 |  | 90.93 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.75
LF [%] |  |  |  |  | 100.78 | 94.82 |  |  |  | 10.22 |  | 83.78 | [8 empty] | 100.39 |  |  | 99.43 | [6 empty] | 98.42 |  | 98.72 |  |  |  | 99.73 |  |  | 100.37 |  |  | 100.87 | [9 empty] | 101.15 |  |  | 90.64
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 11.29 |  | 90.97 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.75
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 55.69 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.31
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 14.37 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.22
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 74.19 |  | 9.07 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.03
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 333525.19 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.11 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.19 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.73 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.19 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.08 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.09 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.18 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 2540.56 |  |  | 2800 |  |  |  | 1040 | [10 empty] | 49.12 |  |  |  | 49.12 | [5 empty] | 33.61 |  |  | 38.64 |  |  |  | 17.46 |  | 10.39 | [8 empty] | 40.48 |  |  |  |  | 0.00
1989 |  |  |  | 4288.28 |  |  | 4824 |  |  |  | 1068 | [10 empty] | 56.45 |  |  |  | 56.45 | [5 empty] | 45.81 |  |  | 55.07 |  |  |  | 20.46 |  | 14.52 | [8 empty] | 29.03 |  |  |  |  | 0.00
1990 |  |  |  | 4140.41 |  |  | 4697 |  |  |  | 1082 | [10 empty] | 54.42 |  |  |  | 54.42 | [5 empty] | 43.66 |  |  | 53.62 |  |  |  | 20.59 |  | 14.11 | [8 empty] | 31.47 |  |  |  |  | 0.00
1991 |  |  |  | 6562.93 |  |  | 6484 |  |  |  | 1092 | [10 empty] | 75.10 |  |  |  | 75.10 | [5 empty] | 68.57 |  |  | 74.02 |  |  |  | 18.31 |  | 16.83 | [8 empty] | 8.07 |  |  |  |  | 0.00
1992 |  |  |  | 5144.97 |  |  | 5169 |  |  |  | 1075 | [10 empty] | 61.85 |  |  |  | 61.85 | [5 empty] | 54.48 |  |  | 58.85 |  |  |  | 12.58 |  | 8.90 | [8 empty] | 29.26 |  |  |  |  | 0.00
1993 |  |  |  | 7191.09 |  |  | 7195 |  |  |  | 1048 | [10 empty] | 82.22 |  |  |  | 82.22 | [5 empty] | 78.28 |  |  | 82.13 |  |  |  | 2.06 |  | 1.73 | [8 empty] | 16.05 |  |  |  |  | 0.00
1994 |  |  |  | 8355.90 |  |  | 8243 |  |  |  | 994 | [10 empty] | 93.93 |  |  |  | 93.93 | [5 empty] | 95.96 |  |  | 94.10 |  |  |  | 6.07 |  | 6.07 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 7253.68 |  |  | 6848 |  |  |  | 1061 | [10 empty] | 78.91 |  |  |  | 78.91 | [5 empty] | 77.99 |  |  | 78.17 |  |  |  | 7.60 |  | 6.49 | [8 empty] | 14.59 |  |  |  |  | 0.00
1996 |  |  |  | 8698.50 |  |  | 7811 |  |  |  | 1106 | [10 empty] | 89.75 |  |  |  | 89.75 | [5 empty] | 89.50 |  |  | 88.92 |  |  |  | 1.23 |  | 1.12 | [8 empty] | 9.13 |  |  |  |  | 0.00
1997 |  |  |  | 8877.99 |  |  | 8279 |  |  |  | 1105 | [10 empty] | 94.93 |  |  |  | 94.93 | [5 empty] | 91.72 |  |  | 94.51 |  |  |  | 3.22 |  | 3.16 | [8 empty] | 1.91 |  |  |  |  | 0.00
1998 |  |  |  | 7307.16 |  |  | 7028 |  |  |  | 1105 | [10 empty] | 80.84 |  |  |  | 80.84 | [5 empty] | 75.49 |  |  | 80.23 |  |  |  | 2.37 |  | 1.96 | [8 empty] | 17.20 |  |  |  |  | 0.00
1999 |  |  |  | 8782.30 |  |  | 7810 |  |  |  | 1128 | [10 empty] | 89.06 |  |  |  | 89.06 | [5 empty] | 88.86 |  |  | 89.16 |  |  |  | 10.94 |  | 10.94 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 8001.52 |  |  | 7204 |  |  |  | 1123 | [10 empty] | 81.73 |  |  |  | 81.73 | [5 empty] | 81.11 |  |  | 82.01 |  |  |  | 3.35 |  | 2.83 | [8 empty] | 15.43 |  |  |  |  | 0.00
2001 |  |  |  | 8858.85 |  |  | 7964 |  |  |  | 1119 | [10 empty] | 90.66 |  |  |  | 90.66 | [5 empty] | 90.37 |  |  | 90.91 |  |  |  | 4.01 |  | 3.78 | [8 empty] | 5.56 |  |  |  |  | 0.00
2002 |  |  |  | 8417.50 |  |  | 7473 |  |  |  | 1119 | [10 empty] | 85.14 |  |  |  | 85.14 | [5 empty] | 85.87 |  |  | 85.31 |  |  |  | 6.47 |  | 5.89 | [8 empty] | 8.97 |  |  |  |  | 0.00
2003 |  |  |  | 9566.87 |  |  | 8448 |  |  |  | 1119 | [10 empty] | 96.40 |  |  |  | 96.40 | [5 empty] | 97.60 |  |  | 96.44 |  |  |  | 3.60 |  | 3.60 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 8643.48 |  |  | 7788 |  |  |  | 1119 | [10 empty] | 88.52 |  |  |  | 88.52 | [5 empty] | 87.94 |  |  | 88.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.48 |  |  |  |  | 0.00
2005 |  |  |  | 9961.02 |  |  | 8760 |  |  |  | 1135 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.17 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 9081.58 |  |  | 8100 |  |  |  | 1135 | [10 empty] | 92.48 |  |  |  | 92.48 | [5 empty] | 91.34 |  |  | 92.47 |  |  |  | 0.69 |  | 0.64 | [8 empty] | 6.88 |  |  |  |  | 0.00
2007 |  |  |  | 9201.14 |  |  | 8286 |  |  |  | 1140 | [10 empty] | 94.60 |  |  |  | 94.60 | [5 empty] | 92.14 |  |  | 94.59 |  |  |  | 2.00 |  | 1.93 | [8 empty] | 3.46 |  |  |  |  | 0.00
2008 |  |  |  | 9082.39 |  |  | 8063 |  |  |  | 1140 | [10 empty] | 91.81 |  |  |  | 91.81 | [5 empty] | 90.70 |  |  | 91.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.19 |  |  |  |  | 0.00
2009 |  |  |  | 9921.92 |  |  | 8760 |  |  |  | 1142 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.18 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 8944.98 |  |  | 7934 |  |  |  | 1143 | [10 empty] | 90.61 |  |  |  | 90.61 | [5 empty] | 89.34 |  |  | 90.57 |  |  |  | 0.95 |  | 0.87 | [8 empty] | 8.52 |  |  |  |  | 0.00
2011 |  |  |  | 9568.30 |  |  | 8450 |  |  |  | 1119 | [10 empty] | 96.40 |  |  |  | 96.40 | [5 empty] | 97.61 |  |  | 96.46 |  |  |  | 3.60 |  | 3.60 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 8418.34 |  |  | 7119 |  |  |  | 1276 | [10 empty] | 81.94 |  |  |  | 81.94 | [5 empty] | 80.26 |  |  | 81.05 |  |  |  | 1.34 |  | 1.11 | [8 empty] | 16.95 |  |  |  |  | 0.00
2013 |  |  |  | 10942.30 |  |  | 8622 |  |  |  | 1277 | [10 empty] | 98.42 |  |  |  | 98.42 | [5 empty] | 97.81 |  |  | 98.41 |  |  |  | 1.58 |  | 1.58 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 9822.73 |  |  | 7755 |  |  |  | 1276 | [10 empty] | 88.53 |  |  |  | 88.53 | [5 empty] | 87.88 |  |  | 88.53 |  |  |  | 1.76 |  | 1.59 | [8 empty] | 9.88 |  |  |  |  | 0.00
2015 |  |  |  | 11072.56 |  |  | 8647 |  |  |  | 1277 | [10 empty] | 98.72 |  |  |  | 98.72 | [5 empty] | 98.98 |  |  | 98.71 |  |  |  | 1.28 |  | 1.28 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 10123.11 |  |  | 7935 |  |  |  | 1277 | [10 empty] | 90.34 |  |  |  | 90.34 | [5 empty] | 90.25 |  |  | 90.33 |  |  |  | 3.01 |  | 2.80 | [8 empty] | 6.86 |  |  |  |  | 0.00
2017 |  |  |  | 11122.23 |  |  | 8695 |  |  |  | 1277 | [10 empty] | 99.26 |  |  |  | 99.26 | [5 empty] | 99.43 |  |  | 99.26 |  |  |  | 0.74 |  | 0.74 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 10094.77 |  |  | 7988 |  |  |  | 1277 | [10 empty] | 91.80 |  |  |  | 91.80 | [5 empty] | 90.24 |  |  | 91.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.20 |  |  |  |  | 0.00
2019 |  |  |  | 10993.81 |  |  | 8760 |  |  |  | 1277 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 10167.61 |  |  | 8059 |  |  |  | 1277 | [10 empty] | 91.75 |  |  |  | 91.75 | [5 empty] | 90.64 |  |  | 91.75 |  |  |  | 1.31 |  | 1.22 | [8 empty] | 7.03 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 305
B. |  | Refuelling without maintenance | [20 empty] | 617 | [14 empty] | 19
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 600
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 213
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 3
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 18
Z. |  | Other | [24 empty] | 107 | [14 empty] | 20
Subtotal | [22 empty] | 617 |  |  |  | 107 | [10 empty] | 834 |  |  |  | 346 | [11 empty] | 4
Total | [22 empty] | 724 | [14 empty] | 1184
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 8
12. |  |  | Reactor I&C Systems | [34 empty] | 25
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 47
16. |  |  | Steam generation systems | [34 empty] | 9
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 27
32. |  |  | Feedwater and Main Steam System | [34 empty] | 47
33. |  |  | Circulating Water System | [34 empty] | 10
34. |  |  | Miscellaneous Systems | [34 empty] | 18
35. |  |  | All other I&C Systems | [34 empty] | 33
41. |  |  | Main Generator Systems | [34 empty] | 22
42. |  |  | Electrical Power Supply Systems | [34 empty] | 48
Total | [37 empty] | 313
Highlights (2020)
EHC Leak led to manual scram. Site then commenced refueling outage (previously scheduled to begin 3/9)

## NORTH ANNA-1
2020 Operating Experience
US-338 | [8 empty] | NORTH ANNA-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DOMINION (Dominion Energy)
Owner | [7 empty] | : | VEPCO (Virginia Electric Power Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYSUB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-02-19
Thermal power | [12 empty] | : |  |  | 2940 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-04-17
Gross electrical power | [12 empty] | : |  |  | 990 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1978-06-06
Reference unit power (net) | [12 empty] | : |  |  | 948 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.316
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 39000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.82
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.59 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 32 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8468.83 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.7 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 728.83 | 681.50 |  |  |  | 711.34 |  | 701.88 | [8 empty] | 721.96 |  |  | 671.79 | [6 empty] | 700.10 |  | 704.22 |  |  |  | 690.01 |  |  | 722.20 |  |  | 705.45 | [9 empty] | 729.57 |  |  | 8468.83
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 103.33 | 103.29 |  |  |  | 100.86 |  | 102.83 | [8 empty] | 102.36 |  |  | 98.42 | [6 empty] | 99.26 |  | 99.84 |  |  |  | 101.09 |  |  | 102.39 |  |  | 103.35 | [9 empty] | 103.44 |  |  | 101.70
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 328010.46 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.31 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.65 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.84 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.18 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.98 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.23 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.54 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1978 |  |  |  | 3971.50 |  |  | 5420 |  |  |  | 896 | [10 empty] | 81.39 |  |  |  | 81.39 | [5 empty] | 79.45 |  |  | 92.85 |  |  |  | 13.69 |  | 12.91 | [8 empty] | 5.70 |  |  |  |  | 0.00
1979 |  |  |  | 4188.70 |  |  | 5399 |  |  |  | 898 | [10 empty] | 53.25 |  |  |  | 53.25 | [5 empty] | 53.25 |  |  | 61.63 |  |  |  | 21.68 |  | 14.74 | [8 empty] | 32.02 |  |  |  |  | 0.00
1980 |  |  |  | 5631.00 |  |  | 7589 |  |  |  | 878 | [10 empty] | 87.25 |  |  |  | 87.25 | [5 empty] | 73.01 |  |  | 86.40 |  |  |  | 6.30 |  | 5.87 | [8 empty] | 6.89 |  |  |  |  | 0.00
1981 |  |  |  | 4637.90 |  |  | 5703 |  |  |  | 860 | [10 empty] | 65.62 |  |  |  | 65.62 | [5 empty] | 61.56 |  |  | 65.10 |  |  |  | 0.38 |  | 0.25 | [8 empty] | 34.13 |  |  |  |  | 0.00
1982 |  |  |  | 2397.90 |  |  | 3027 |  |  |  | 865 | [10 empty] | 34.73 |  |  |  | 34.73 | [5 empty] | 31.65 |  |  | 34.55 |  |  |  | 22.49 |  | 10.08 | [8 empty] | 55.19 |  |  |  |  | 0.00
1983 |  |  |  | 5310.40 |  |  | 6277 |  |  |  | 872 | [10 empty] | 71.62 |  |  |  | 71.62 | [5 empty] | 69.52 |  |  | 71.66 |  |  |  | 23.75 |  | 22.30 | [8 empty] | 6.08 |  |  |  |  | 0.00
1984 |  |  |  | 3784.80 |  |  | 4425 |  |  |  | 883 | [10 empty] | 50.31 |  |  |  | 50.31 | [5 empty] | 48.80 |  |  | 50.38 |  |  |  | 19.28 |  | 12.01 | [8 empty] | 37.68 |  |  |  |  | 0.00
1985 |  |  |  | 5798.93 |  |  | 6820 |  |  |  | 892 | [10 empty] | 77.88 |  |  |  | 77.88 | [5 empty] | 74.21 |  |  | 77.85 |  |  |  | 5.14 |  | 4.22 | [8 empty] | 17.90 |  |  |  |  | 0.00
1986 |  |  |  | 6310.74 |  |  | 7327 |  |  |  | 893 | [10 empty] | 83.70 |  |  |  | 83.70 | [5 empty] | 80.67 |  |  | 83.64 |  |  |  | 16.10 |  | 16.06 | [8 empty] | 0.24 |  |  |  |  | 0.00
1987 |  |  |  | 3568.91 |  |  | 4523 |  |  |  | 913 | [10 empty] | 52.09 |  |  |  | 52.09 | [5 empty] | 44.61 |  |  | 51.63 |  |  |  | 35.37 |  | 28.50 | [8 empty] | 19.41 |  |  |  |  | 0.00
1988 |  |  |  | 6897.30 |  |  | 7760 |  |  |  | 915 | [10 empty] | 88.61 |  |  |  | 88.61 | [5 empty] | 85.82 |  |  | 88.34 |  |  |  | 10.25 |  | 10.12 | [8 empty] | 1.26 |  |  |  |  | 0.00
1989 |  |  |  | 4303.32 |  |  | 4978 |  |  |  | 915 | [10 empty] | 57.80 |  |  |  | 57.80 | [5 empty] | 53.69 |  |  | 56.83 |  |  |  | 9.68 |  | 6.20 | [8 empty] | 36.01 |  |  |  |  | 0.00
1990 |  |  |  | 7233.54 |  |  | 8726 |  |  |  | 912 | [10 empty] | 99.62 |  |  |  | 99.62 | [5 empty] | 90.54 |  |  | 99.61 |  |  |  | 0.38 |  | 0.38 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 5625.82 |  |  | 6549 |  |  |  | 911 | [10 empty] | 75.16 |  |  |  | 75.16 | [5 empty] | 70.50 |  |  | 74.76 |  |  |  | 11.49 |  | 9.75 | [8 empty] | 15.08 |  |  |  |  | 0.00
1992 |  |  |  | 5358.08 |  |  | 7225 |  |  |  | 858 | [10 empty] | 81.53 |  |  |  | 81.53 | [5 empty] | 71.07 |  |  | 82.25 |  |  |  | 3.04 |  | 2.56 | [8 empty] | 15.91 |  |  |  |  | 0.00
1993 |  |  |  | 5692.65 |  |  | 6444 |  |  |  | 890 | [10 empty] | 73.49 |  |  |  | 73.49 | [5 empty] | 72.99 |  |  | 73.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.51 |  |  |  |  | 0.00
1994 |  |  |  | 6795.70 |  |  | 8012 |  |  |  | 900 | [10 empty] | 91.55 |  |  |  | 91.55 | [5 empty] | 86.20 |  |  | 91.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.45 |  |  |  |  | 0.00
1995 |  |  |  | 7839.17 |  |  | 8733 |  |  |  | 896 | [10 empty] | 99.70 |  |  |  | 99.70 | [5 empty] | 99.82 |  |  | 99.69 |  |  |  | 0.30 |  | 0.30 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 6945.50 |  |  | 7985 |  |  |  | 893 | [10 empty] | 90.96 |  |  |  | 90.96 | [5 empty] | 88.54 |  |  | 90.90 |  |  |  | 0.84 |  | 0.77 | [8 empty] | 8.27 |  |  |  |  | 0.00
1997 |  |  |  | 7157.53 |  |  | 7992 |  |  |  | 893 | [10 empty] | 91.26 |  |  |  | 91.26 | [5 empty] | 91.50 |  |  | 91.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.74 |  |  |  |  | 0.00
1998 |  |  |  | 7217.05 |  |  | 8091 |  |  |  | 893 | [10 empty] | 92.39 |  |  |  | 92.39 | [5 empty] | 92.26 |  |  | 92.36 |  |  |  | 0.71 |  | 0.66 | [8 empty] | 6.95 |  |  |  |  | 0.00
1999 |  |  |  | 8124.46 |  |  | 8760 |  |  |  | 893 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.86 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 7213.08 |  |  | 7997 |  |  |  | 893 | [10 empty] | 91.06 |  |  |  | 91.06 | [5 empty] | 91.96 |  |  | 91.04 |  |  |  | 1.45 |  | 1.34 | [8 empty] | 7.59 |  |  |  |  | 0.00
2001 |  |  |  | 7120.79 |  |  | 8010 |  |  |  | 925 | [10 empty] | 91.46 |  |  |  | 91.46 | [5 empty] | 87.88 |  |  | 91.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.54 |  |  |  |  | 0.00
2002 |  |  |  | 8164.34 |  |  | 8760 |  |  |  | 925 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 6519.92 |  |  | 7200 |  |  |  | 925 | [10 empty] | 82.21 |  |  |  | 82.21 | [5 empty] | 80.46 |  |  | 82.19 |  |  |  | 3.41 |  | 2.90 | [8 empty] | 14.89 |  |  |  |  | 0.00
2004 |  |  |  | 7418.35 |  |  | 8023 |  |  |  | 925 | [10 empty] | 91.35 |  |  |  | 91.35 | [5 empty] | 91.30 |  |  | 91.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.65 |  |  |  |  | 0.00
2005 |  |  |  | 8091.86 |  |  | 8744 |  |  |  | 925 | [10 empty] | 99.82 |  |  |  | 99.82 | [5 empty] | 99.85 |  |  | 99.81 |  |  |  | 0.18 |  | 0.18 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 7142.74 |  |  | 7861 |  |  |  | 924 | [10 empty] | 89.77 |  |  |  | 89.77 | [5 empty] | 88.24 |  |  | 89.74 |  |  |  | 1.01 |  | 0.91 | [8 empty] | 9.32 |  |  |  |  | 0.00
2007 |  |  |  | 7215.14 |  |  | 7854 |  |  |  | 903 | [10 empty] | 89.45 |  |  |  | 89.45 | [5 empty] | 91.21 |  |  | 89.66 |  |  |  | 0.32 |  | 0.28 | [8 empty] | 10.27 |  |  |  |  | 0.00
2008 |  |  |  | 7986.83 |  |  | 8784 |  |  |  | 903 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.69 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 7302.50 |  |  | 8017 |  |  |  | 903 | [10 empty] | 91.53 |  |  |  | 91.53 | [5 empty] | 92.32 |  |  | 91.52 |  |  |  | 1.70 |  | 1.58 | [8 empty] | 6.88 |  |  |  |  | 0.00
2010 |  |  |  | 6779.93 |  |  | 7496 |  |  |  | 903 | [10 empty] | 85.60 |  |  |  | 85.60 | [5 empty] | 85.71 |  |  | 85.57 |  |  |  | 1.40 |  | 1.21 | [8 empty] | 13.18 |  |  |  |  | 0.00
2011 |  |  |  | 6243.13 |  |  | 6746 |  |  |  | 920 | [10 empty] | 77.45 |  |  |  | 100.00 | [5 empty] | 77.47 |  |  | 77.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 22.55
2012 |  |  |  | 7170.90 |  |  | 7531 |  |  |  | 943 | [10 empty] | 86.00 |  |  |  | 86.00 | [5 empty] | 87.27 |  |  | 85.74 |  |  |  | 0.23 |  | 0.20 | [8 empty] | 13.81 |  |  |  |  | 0.00
2013 |  |  |  | 7672.82 |  |  | 7922 |  |  |  | 943 | [10 empty] | 90.44 |  |  |  | 90.44 | [5 empty] | 92.87 |  |  | 90.42 |  |  |  | 0.65 |  | 0.59 | [8 empty] | 8.97 |  |  |  |  | 0.00
2014 |  |  |  | 8279.47 |  |  | 8546 |  |  |  | 943 | [10 empty] | 97.56 |  |  |  | 97.56 | [5 empty] | 100.23 |  |  | 97.56 |  |  |  | 2.44 |  | 2.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 7789.98 |  |  | 8141 |  |  |  | 948 | [10 empty] | 92.96 |  |  |  | 92.96 | [5 empty] | 93.80 |  |  | 92.93 |  |  |  | 1.54 |  | 1.46 | [8 empty] | 5.58 |  |  |  |  | 0.00
2016 |  |  |  | 7629.40 |  |  | 7925 |  |  |  | 948 | [10 empty] | 90.22 |  |  |  | 90.22 | [5 empty] | 91.62 |  |  | 90.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.78 |  |  |  |  | 0.00
2017 |  |  |  | 8492.34 |  |  | 8760 |  |  |  | 948 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.26 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 7568.38 |  |  | 7893 |  |  |  | 948 | [10 empty] | 90.10 |  |  |  | 90.10 | [5 empty] | 91.14 |  |  | 90.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.90 |  |  |  |  | 0.00
2019 |  |  |  | 7850.41 |  |  | 8159 |  |  |  | 948 | [10 empty] | 93.16 |  |  |  | 93.16 | [5 empty] | 94.53 |  |  | 93.14 |  |  |  | 0.46 |  | 0.43 | [8 empty] | 6.40 |  |  |  |  | 0.00
2020 |  |  |  | 8468.83 |  |  | 8783 |  |  |  | 948 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.70 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1978 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 314
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 882
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 85
E. |  | Testing of plant systems or components | [35 empty] | 6 |  |  |  | 4
L. |  | Human factor related | [39 empty] | 4
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 47
Z. |  | Other | [35 empty] | 0 |  |  |  | 2
Subtotal | [37 empty] | 973 |  |  |  | 324 | [11 empty] | 47
Total | [22 empty] | 0 | [14 empty] | 1344
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1978 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 11
12. |  |  | Reactor I&C Systems | [34 empty] | 3
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 15
15. |  |  | Reactor Cooling Systems | [34 empty] | 41
16. |  |  | Steam generation systems | [34 empty] | 85
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 41
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 18
41. |  |  | Main Generator Systems | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 66
Total | [37 empty] | 318

## NORTH ANNA-2
2020 Operating Experience
US-339 | [8 empty] | NORTH ANNA-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DOMINION (Dominion Energy)
Owner | [7 empty] | : | VEPCO (Virginia Electric Power Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYSUB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-02-19
Thermal power | [12 empty] | : |  |  | 2940 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-08-25
Gross electrical power | [12 empty] | : |  |  | 1011 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-12-14
Reference unit power (net) | [12 empty] | : |  |  | 944 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.316
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 39000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.82
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.59 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 32 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7331.07 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.53 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.54 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.27 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.54 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.18 %
Load Factor (LF) | [18 empty] | : | 88.41 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 87.53 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1095 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 724.78 | 670.95 |  |  |  | 723.24 |  | 483.46 | [8 empty] | 685.08 |  |  | 688.23 | [6 empty] | 700.96 |  | 700.02 |  |  |  | 248.90 |  |  | 275.64 |  |  | 702.73 | [9 empty] | 727.09 |  |  | 7331.07
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 72.26 | [8 empty] | 96.53 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 39.81 |  |  | 41.49 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.54
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 72.26 | [8 empty] | 96.53 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 39.81 |  |  | 41.49 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.54
LF [%] |  |  |  |  | 103.20 | 102.12 |  |  |  | 102.98 |  | 71.13 | [8 empty] | 97.54 |  |  | 101.26 | [6 empty] | 99.80 |  | 99.67 |  |  |  | 36.62 |  |  | 39.25 |  |  | 103.39 | [9 empty] | 103.52 |  |  | 88.41
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 72.22 | [8 empty] | 96.51 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 39.86 |  |  | 41.53 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.53
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 27.74 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.53
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 27.74 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.27
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.47 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 60.19 |  |  | 58.51 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.18
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 274030.07 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.44 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.88 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.12 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.54 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.34 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.67 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 1082.50 |  |  | 1701 |  |  |  | 897 | [10 empty] | 97.50 |  |  |  | 97.50 | [5 empty] | 90.12 |  |  | 95.37 |  |  |  | 2.50 |  | 2.50 | [8 empty] | 0.00 |  |  |  |  | 0.00
1981 |  |  |  | 5652.70 |  |  | 6813 |  |  |  | 883 | [10 empty] | 78.35 |  |  |  | 78.35 | [5 empty] | 73.08 |  |  | 77.77 |  |  |  | 19.06 |  | 18.46 | [8 empty] | 3.19 |  |  |  |  | 0.00
1982 |  |  |  | 4047.20 |  |  | 4990 |  |  |  | 890 | [10 empty] | 57.35 |  |  |  | 57.35 | [5 empty] | 51.91 |  |  | 56.96 |  |  |  | 22.01 |  | 16.18 | [8 empty] | 26.47 |  |  |  |  | 0.00
1983 |  |  |  | 5802.50 |  |  | 7052 |  |  |  | 890 | [10 empty] | 80.75 |  |  |  | 80.75 | [5 empty] | 74.43 |  |  | 80.50 |  |  |  | 4.16 |  | 3.51 | [8 empty] | 15.74 |  |  |  |  | 0.00
1984 |  |  |  | 4717.19 |  |  | 5896 |  |  |  | 890 | [10 empty] | 67.14 |  |  |  | 67.14 | [5 empty] | 60.34 |  |  | 67.12 |  |  |  | 5.29 |  | 3.75 | [8 empty] | 29.11 |  |  |  |  | 0.00
1985 |  |  |  | 6813.59 |  |  | 8252 |  |  |  | 892 | [10 empty] | 94.22 |  |  |  | 94.22 | [5 empty] | 87.17 |  |  | 94.20 |  |  |  | 5.78 |  | 5.78 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 6022.05 |  |  | 7208 |  |  |  | 893 | [10 empty] | 82.25 |  |  |  | 82.25 | [5 empty] | 76.98 |  |  | 82.28 |  |  |  | 6.38 |  | 5.60 | [8 empty] | 12.15 |  |  |  |  | 0.00
1987 |  |  |  | 5653.45 |  |  | 6783 |  |  |  | 905 | [10 empty] | 77.42 |  |  |  | 77.42 | [5 empty] | 71.24 |  |  | 77.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.58 |  |  |  |  | 0.00
1988 |  |  |  | 7883.98 |  |  | 8708 |  |  |  | 915 | [10 empty] | 99.15 |  |  |  | 99.15 | [5 empty] | 98.09 |  |  | 99.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.85 |  |  |  |  | 0.00
1989 |  |  |  | 5896.51 |  |  | 6887 |  |  |  | 915 | [10 empty] | 80.17 |  |  |  | 80.17 | [5 empty] | 73.56 |  |  | 78.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.83 |  |  |  |  | 0.00
1990 |  |  |  | 5976.65 |  |  | 6982 |  |  |  | 910 | [10 empty] | 80.01 |  |  |  | 80.01 | [5 empty] | 74.93 |  |  | 79.70 |  |  |  | 19.96 |  | 19.95 | [8 empty] | 0.03 |  |  |  |  | 0.00
1991 |  |  |  | 7684.26 |  |  | 8539 |  |  |  | 909 | [10 empty] | 97.52 |  |  |  | 97.52 | [5 empty] | 96.50 |  |  | 97.48 |  |  |  | 2.48 |  | 2.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 6324.75 |  |  | 7237 |  |  |  | 909 | [10 empty] | 82.63 |  |  |  | 82.63 | [5 empty] | 79.21 |  |  | 82.39 |  |  |  | 0.94 |  | 0.78 | [8 empty] | 16.59 |  |  |  |  | 0.00
1993 |  |  |  | 6225.22 |  |  | 7303 |  |  |  | 909 | [10 empty] | 83.60 |  |  |  | 83.60 | [5 empty] | 78.18 |  |  | 83.37 |  |  |  | 3.16 |  | 2.73 | [8 empty] | 13.68 |  |  |  |  | 0.00
1994 |  |  |  | 7490.27 |  |  | 8517 |  |  |  | 887 | [10 empty] | 97.19 |  |  |  | 97.19 | [5 empty] | 96.40 |  |  | 97.23 |  |  |  | 2.81 |  | 2.81 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 6031.67 |  |  | 7086 |  |  |  | 892 | [10 empty] | 80.82 |  |  |  | 80.82 | [5 empty] | 77.19 |  |  | 80.89 |  |  |  | 0.42 |  | 0.34 | [8 empty] | 18.84 |  |  |  |  | 0.00
1996 |  |  |  | 6121.54 |  |  | 6859 |  |  |  | 897 | [10 empty] | 78.13 |  |  |  | 78.13 | [5 empty] | 77.69 |  |  | 78.09 |  |  |  | 13.48 |  | 12.17 | [8 empty] | 9.70 |  |  |  |  | 0.00
1997 |  |  |  | 7834.79 |  |  | 8738 |  |  |  | 897 | [10 empty] | 99.75 |  |  |  | 99.75 | [5 empty] | 99.71 |  |  | 99.75 |  |  |  | 0.25 |  | 0.25 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 7086.10 |  |  | 8049 |  |  |  | 897 | [10 empty] | 91.91 |  |  |  | 92.15 | [5 empty] | 90.18 |  |  | 91.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.85 |  |  |  |  | 0.23
1999 |  |  |  | 7185.14 |  |  | 8034 |  |  |  | 897 | [10 empty] | 91.73 |  |  |  | 91.73 | [5 empty] | 91.44 |  |  | 91.71 |  |  |  | 0.49 |  | 0.45 | [8 empty] | 7.82 |  |  |  |  | 0.00
2000 |  |  |  | 8018.85 |  |  | 8729 |  |  |  | 897 | [10 empty] | 99.38 |  |  |  | 99.38 | [5 empty] | 101.77 |  |  | 99.37 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 5975.80 |  |  | 6776 |  |  |  | 917 | [10 empty] | 77.40 |  |  |  | 77.40 | [5 empty] | 74.39 |  |  | 77.35 |  |  |  | 1.24 |  | 0.97 | [8 empty] | 21.63 |  |  |  |  | 0.00
2002 |  |  |  | 5509.69 |  |  | 6000 |  |  |  | 917 | [10 empty] | 68.48 |  |  |  | 68.48 | [5 empty] | 68.59 |  |  | 68.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.52 |  |  |  |  | 0.00
2003 |  |  |  | 7262.75 |  |  | 7950 |  |  |  | 917 | [10 empty] | 90.77 |  |  |  | 90.77 | [5 empty] | 90.41 |  |  | 90.75 |  |  |  | 0.26 |  | 0.24 | [8 empty] | 9.00 |  |  |  |  | 0.00
2004 |  |  |  | 7388.14 |  |  | 8077 |  |  |  | 917 | [10 empty] | 91.97 |  |  |  | 91.97 | [5 empty] | 91.72 |  |  | 91.95 |  |  |  | 0.28 |  | 0.26 | [8 empty] | 7.78 |  |  |  |  | 0.00
2005 |  |  |  | 7293.54 |  |  | 8034 |  |  |  | 917 | [10 empty] | 91.72 |  |  |  | 92.14 | [5 empty] | 90.80 |  |  | 91.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.86 |  |  |  |  | 0.42
2006 |  |  |  | 7950.42 |  |  | 8732 |  |  |  | 910 | [10 empty] | 99.68 |  |  |  | 99.68 | [5 empty] | 99.73 |  |  | 99.68 |  |  |  | 0.32 |  | 0.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 6771.79 |  |  | 7524 |  |  |  | 903 | [10 empty] | 85.81 |  |  |  | 85.81 | [5 empty] | 85.61 |  |  | 85.89 |  |  |  | 4.66 |  | 4.20 | [8 empty] | 9.99 |  |  |  |  | 0.00
2008 |  |  |  | 6446.59 |  |  | 7132 |  |  |  | 903 | [10 empty] | 81.21 |  |  |  | 81.21 | [5 empty] | 81.27 |  |  | 81.19 |  |  |  | 2.84 |  | 2.37 | [8 empty] | 16.42 |  |  |  |  | 0.00
2009 |  |  |  | 7900.11 |  |  | 8688 |  |  |  | 903 | [10 empty] | 99.18 |  |  |  | 99.18 | [5 empty] | 99.87 |  |  | 99.18 |  |  |  | 0.82 |  | 0.82 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 6619.53 |  |  | 7093 |  |  |  | 943 | [10 empty] | 81.56 |  |  |  | 81.56 | [5 empty] | 81.27 |  |  | 80.97 |  |  |  | 9.72 |  | 8.78 | [8 empty] | 9.66 |  |  |  |  | 0.00
2011 |  |  |  | 6275.39 |  |  | 6570 |  |  |  | 943 | [10 empty] | 74.77 |  |  |  | 100.00 | [5 empty] | 75.97 |  |  | 75.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 25.23
2012 |  |  |  | 8162.29 |  |  | 8474 |  |  |  | 943 | [10 empty] | 96.48 |  |  |  | 96.48 | [5 empty] | 98.54 |  |  | 96.47 |  |  |  | 3.52 |  | 3.52 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 7332.46 |  |  | 7642 |  |  |  | 943 | [10 empty] | 87.24 |  |  |  | 87.24 | [5 empty] | 88.75 |  |  | 87.23 |  |  |  | 4.24 |  | 3.86 | [8 empty] | 8.90 |  |  |  |  | 0.00
2014 |  |  |  | 7609.18 |  |  | 7913 |  |  |  | 943 | [10 empty] | 90.33 |  |  |  | 90.33 | [5 empty] | 92.11 |  |  | 90.33 |  |  |  | 0.41 |  | 0.37 | [8 empty] | 9.31 |  |  |  |  | 0.00
2015 |  |  |  | 8480.65 |  |  | 8760 |  |  |  | 943 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.66 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 7491.97 |  |  | 7835 |  |  |  | 943 | [10 empty] | 89.18 |  |  |  | 89.18 | [5 empty] | 90.45 |  |  | 89.20 |  |  |  | 1.30 |  | 1.18 | [8 empty] | 9.64 |  |  |  |  | 0.00
2017 |  |  |  | 7633.75 |  |  | 7937 |  |  |  | 944 | [10 empty] | 90.62 |  |  |  | 90.62 | [5 empty] | 92.31 |  |  | 90.61 |  |  |  | 0.70 |  | 0.64 | [8 empty] | 8.75 |  |  |  |  | 0.00
2018 |  |  |  | 8428.87 |  |  | 8732 |  |  |  | 944 | [10 empty] | 99.68 |  |  |  | 99.68 | [5 empty] | 101.93 |  |  | 99.68 |  |  |  | 0.32 |  | 0.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7474.13 |  |  | 7828 |  |  |  | 944 | [10 empty] | 89.38 |  |  |  | 89.38 | [5 empty] | 90.38 |  |  | 89.36 |  |  |  | 0.46 |  | 0.41 | [8 empty] | 10.21 |  |  |  |  | 0.00
2020 |  |  |  | 7331.07 |  |  | 7689 |  |  |  | 944 | [10 empty] | 87.54 |  |  |  | 87.54 | [5 empty] | 88.41 |  |  | 87.53 |  |  |  | 2.53 |  | 2.27 | [8 empty] | 10.18 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1980 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 213
B. |  | Refuelling without maintenance | [20 empty] | 869 | [14 empty] | 22
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 745
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 26 | [14 empty] | 54
E. |  | Testing of plant systems or components | [35 empty] | 2
L. |  | Human factor related | [39 empty] | 10
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 62
Z. |  | Other | [24 empty] | 200 | [14 empty] | 50
Subtotal | [22 empty] | 895 |  |  |  | 200 | [10 empty] | 823 |  |  |  | 273 | [11 empty] | 62
Total | [22 empty] | 1095 | [14 empty] | 1158
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1980 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 4
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 16
15. |  |  | Reactor Cooling Systems | [34 empty] | 26
16. |  |  | Steam generation systems | [34 empty] | 72
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
32. |  |  | Feedwater and Main Steam System | [34 empty] | 19
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 41
42. |  |  | Electrical Power Supply Systems | [34 empty] | 58
Total | [37 empty] | 260
Highlights (2020)
2-RC-P-1A Seal Injection piping repaired

## OCONEE-1
2020 Operating Experience
US-269 | [8 empty] | OCONEE-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Owner | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Reactor Supplier | [7 empty] | : | B&W (BABCOCK & WILCOX CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / B&W LLP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-11-06
Thermal power | [12 empty] | : |  |  | 2568 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-05-06
Gross electrical power | [12 empty] | : |  |  | 891 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-07-15
Reference unit power (net) | [12 empty] | : |  |  | 847 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.513
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 34 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 30000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.27 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.33
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6859.97 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.19 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.19 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.81 %
Load Factor (LF) | [18 empty] | : | 92.2 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.2 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 773 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 643.92 | 602.40 |  |  |  | 643.74 |  | 623.80 | [8 empty] | 642.88 |  |  | 619.67 | [6 empty] | 635.63 |  | 629.69 |  |  |  | 608.54 |  |  | 317.32 |  |  | 244.32 | [9 empty] | 648.07 |  |  | 6859.97
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 51.34 |  |  | 42.85 | [9 empty] | 100.00 |  |  | 91.19
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 51.34 |  |  | 42.85 | [9 empty] | 100.00 |  |  | 91.19
LF [%] |  |  |  |  | 102.18 | 102.19 |  |  |  | 102.15 |  | 102.29 | [8 empty] | 102.02 |  |  | 101.61 | [6 empty] | 100.87 |  | 99.92 |  |  |  | 99.79 |  |  | 50.35 |  |  | 40.06 | [9 empty] | 102.84 |  |  | 92.20
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 51.34 |  |  | 43.06 | [9 empty] | 100.00 |  |  | 91.20
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 48.66 |  |  | 57.15 | [9 empty] | 0.00 |  |  | 8.81
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 289009.61 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.3 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.65 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.6 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.53 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.34 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.22 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.3 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 2200.00 |  |  | 4226 |  |  |  | 721 | [10 empty] | 70.52 |  |  |  | 70.52 | [5 empty] | 67.32 |  |  | 75.86 |  |  |  | 11.34 |  | 9.02 | [8 empty] | 20.46 |  |  |  |  | 0.00
1974 |  |  |  | 4230.30 |  |  | 5141 |  |  |  | 920 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 52.49 |  |  | 58.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1975 |  |  |  | 5299.30 |  |  | 6672 |  |  |  | 871 | [10 empty] | 69.51 |  |  |  | 69.51 | [5 empty] | 69.45 |  |  | 76.16 |  |  |  | 27.02 |  | 25.73 | [8 empty] | 4.75 |  |  |  |  | 0.00
1976 |  |  |  | 4003.50 |  |  | 5029 |  |  |  | 871 | [10 empty] | 52.38 |  |  |  | 52.38 | [5 empty] | 52.33 |  |  | 57.25 |  |  |  | 25.57 |  | 18.00 | [8 empty] | 29.62 |  |  |  |  | 0.00
1977 |  |  |  | 3949.00 |  |  | 5455 |  |  |  | 860 | [10 empty] | 52.47 |  |  |  | 52.47 | [5 empty] | 52.42 |  |  | 62.27 |  |  |  | 30.19 |  | 22.69 | [8 empty] | 24.84 |  |  |  |  | 0.00
1978 |  |  |  | 5054.40 |  |  | 6299 |  |  |  | 860 | [10 empty] | 67.07 |  |  |  | 67.07 | [5 empty] | 67.09 |  |  | 71.91 |  |  |  | 20.04 |  | 16.81 | [8 empty] | 16.12 |  |  |  |  | 0.00
1979 |  |  |  | 5003.10 |  |  | 6220 |  |  |  | 860 | [10 empty] | 66.41 |  |  |  | 66.41 | [5 empty] | 66.41 |  |  | 71.00 |  |  |  | 22.11 |  | 18.86 | [8 empty] | 14.73 |  |  |  |  | 0.00
1980 |  |  |  | 5118.30 |  |  | 6634 |  |  |  | 860 | [10 empty] | 76.23 |  |  |  | 86.33 | [5 empty] | 67.75 |  |  | 75.52 |  |  |  | 8.70 |  | 8.22 | [8 empty] | 5.45 |  |  |  |  | 10.10
1981 |  |  |  | 3023.20 |  |  | 3657 |  |  |  | 860 | [10 empty] | 42.94 |  |  |  | 42.94 | [5 empty] | 40.13 |  |  | 41.75 |  |  |  | 13.04 |  | 6.44 | [8 empty] | 50.62 |  |  |  |  | 0.00
1982 |  |  |  | 5152.80 |  |  | 6335 |  |  |  | 860 | [10 empty] | 73.50 |  |  |  | 73.50 | [5 empty] | 68.40 |  |  | 72.32 |  |  |  | 24.78 |  | 24.22 | [8 empty] | 2.29 |  |  |  |  | 0.00
1983 |  |  |  | 5672.00 |  |  | 6804 |  |  |  | 860 | [10 empty] | 78.43 |  |  |  | 78.43 | [5 empty] | 75.29 |  |  | 77.67 |  |  |  | 0.46 |  | 0.37 | [8 empty] | 21.20 |  |  |  |  | 0.00
1984 |  |  |  | 6173.71 |  |  | 7312 |  |  |  | 860 | [10 empty] | 83.55 |  |  |  | 83.55 | [5 empty] | 81.73 |  |  | 83.24 |  |  |  | 2.07 |  | 1.76 | [8 empty] | 14.68 |  |  |  |  | 0.00
1985 |  |  |  | 7065.96 |  |  | 8424 |  |  |  | 860 | [10 empty] | 96.25 |  |  |  | 96.25 | [5 empty] | 93.79 |  |  | 96.16 |  |  |  | 3.75 |  | 3.75 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 4793.94 |  |  | 5870 |  |  |  | 860 | [10 empty] | 70.22 |  |  |  | 70.22 | [5 empty] | 63.63 |  |  | 67.01 |  |  |  | 13.19 |  | 10.67 | [8 empty] | 19.11 |  |  |  |  | 0.00
1987 |  |  |  | 5031.13 |  |  | 6693 |  |  |  | 860 | [10 empty] | 76.82 |  |  |  | 76.82 | [5 empty] | 66.78 |  |  | 76.40 |  |  |  | 4.83 |  | 3.90 | [8 empty] | 19.28 |  |  |  |  | 0.00
1988 |  |  |  | 7192.19 |  |  | 8742 |  |  |  | 846 | [10 empty] | 99.53 |  |  |  | 99.53 | [5 empty] | 96.78 |  |  | 99.52 |  |  |  | 0.47 |  | 0.47 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 5943.13 |  |  | 7264 |  |  |  | 846 | [10 empty] | 82.95 |  |  |  | 82.95 | [5 empty] | 80.19 |  |  | 82.92 |  |  |  | 3.54 |  | 3.04 | [8 empty] | 14.01 |  |  |  |  | 0.00
1990 |  |  |  | 6454.83 |  |  | 7751 |  |  |  | 846 | [10 empty] | 88.49 |  |  |  | 88.49 | [5 empty] | 87.10 |  |  | 88.48 |  |  |  | 0.24 |  | 0.22 | [8 empty] | 11.29 |  |  |  |  | 0.00
1991 |  |  |  | 6022.45 |  |  | 7245 |  |  |  | 846 | [10 empty] | 82.73 |  |  |  | 82.73 | [5 empty] | 81.26 |  |  | 82.71 |  |  |  | 2.59 |  | 2.20 | [8 empty] | 15.07 |  |  |  |  | 0.00
1992 |  |  |  | 6277.69 |  |  | 7494 |  |  |  | 846 | [10 empty] | 85.31 |  |  |  | 85.31 | [5 empty] | 84.48 |  |  | 85.31 |  |  |  | 7.36 |  | 6.77 | [8 empty] | 7.91 |  |  |  |  | 0.00
1993 |  |  |  | 6525.05 |  |  | 7833 |  |  |  | 846 | [10 empty] | 89.42 |  |  |  | 89.42 | [5 empty] | 88.05 |  |  | 89.42 |  |  |  | 2.19 |  | 2.00 | [8 empty] | 8.58 |  |  |  |  | 0.00
1994 |  |  |  | 6088.71 |  |  | 7302 |  |  |  | 846 | [10 empty] | 83.39 |  |  |  | 83.39 | [5 empty] | 82.16 |  |  | 83.36 |  |  |  | 0.46 |  | 0.39 | [8 empty] | 16.22 |  |  |  |  | 0.00
1995 |  |  |  | 6360.47 |  |  | 7537 |  |  |  | 846 | [10 empty] | 86.07 |  |  |  | 86.07 | [5 empty] | 85.83 |  |  | 86.04 |  |  |  | 3.88 |  | 3.47 | [8 empty] | 10.46 |  |  |  |  | 0.00
1996 |  |  |  | 5566.97 |  |  | 6606 |  |  |  | 846 | [10 empty] | 75.23 |  |  |  | 75.23 | [5 empty] | 74.91 |  |  | 75.20 |  |  |  | 0.60 |  | 0.46 | [8 empty] | 24.32 |  |  |  |  | 0.00
1997 |  |  |  | 3194.22 |  |  | 4482 |  |  |  | 846 | [10 empty] | 51.28 |  |  |  | 51.28 | [5 empty] | 43.10 |  |  | 51.16 |  |  |  | 25.69 |  | 17.73 | [8 empty] | 30.99 |  |  |  |  | 0.00
1998 |  |  |  | 5996.40 |  |  | 7255 |  |  |  | 846 | [10 empty] | 82.83 |  |  |  | 82.83 | [5 empty] | 80.91 |  |  | 82.82 |  |  |  | 17.17 |  | 17.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 6212.59 |  |  | 7383 |  |  |  | 846 | [10 empty] | 85.11 |  |  |  | 85.11 | [5 empty] | 83.83 |  |  | 84.28 |  |  |  | 3.81 |  | 3.37 | [8 empty] | 11.52 |  |  |  |  | 0.00
2000 |  |  |  | 6312.68 |  |  | 7445 |  |  |  | 846 | [10 empty] | 84.76 |  |  |  | 84.76 | [5 empty] | 84.95 |  |  | 84.76 |  |  |  | 5.13 |  | 4.59 | [8 empty] | 10.66 |  |  |  |  | 0.00
2001 |  |  |  | 6962.62 |  |  | 8210 |  |  |  | 846 | [10 empty] | 94.03 |  |  |  | 94.03 | [5 empty] | 93.95 |  |  | 93.72 |  |  |  | 5.71 |  | 5.70 | [8 empty] | 0.28 |  |  |  |  | 0.00
2002 |  |  |  | 6607.46 |  |  | 7788 |  |  |  | 846 | [10 empty] | 88.93 |  |  |  | 88.93 | [5 empty] | 89.16 |  |  | 88.90 |  |  |  | 1.09 |  | 0.98 | [8 empty] | 10.09 |  |  |  |  | 0.00
2003 |  |  |  | 5258.63 |  |  | 6288 |  |  |  | 846 | [10 empty] | 71.77 |  |  |  | 71.77 | [5 empty] | 70.96 |  |  | 71.78 |  |  |  | 7.75 |  | 6.03 | [8 empty] | 22.20 |  |  |  |  | 0.00
2004 |  |  |  | 7260.23 |  |  | 8549 |  |  |  | 846 | [10 empty] | 97.33 |  |  |  | 97.33 | [5 empty] | 97.70 |  |  | 97.32 |  |  |  | 2.07 |  | 2.06 | [8 empty] | 0.61 |  |  |  |  | 0.00
2005 |  |  |  | 6728.57 |  |  | 7879 |  |  |  | 846 | [10 empty] | 89.96 |  |  |  | 89.96 | [5 empty] | 90.78 |  |  | 89.93 |  |  |  | 0.00 |  | 1.27 | [8 empty] | 8.77 |  |  |  |  | 0.00
2006 |  |  |  | 5819.36 |  |  | 6884 |  |  |  | 846 | [10 empty] | 78.62 |  |  |  | 78.62 | [5 empty] | 78.52 |  |  | 78.58 |  |  |  | 0.68 |  | 0.53 | [8 empty] | 20.85 |  |  |  |  | 0.00
2007 |  |  |  | 7335.72 |  |  | 8562 |  |  |  | 846 | [10 empty] | 97.74 |  |  |  | 97.74 | [5 empty] | 98.98 |  |  | 97.74 |  |  |  | 2.26 |  | 2.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 6222.80 |  |  | 7564 |  |  |  | 846 | [10 empty] | 86.12 |  |  |  | 86.12 | [5 empty] | 83.74 |  |  | 86.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.88 |  |  |  |  | 0.00
2009 |  |  |  | 6316.65 |  |  | 7393 |  |  |  | 846 | [10 empty] | 84.41 |  |  |  | 84.41 | [5 empty] | 85.23 |  |  | 84.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.59 |  |  |  |  | 0.00
2010 |  |  |  | 7433.77 |  |  | 8695 |  |  |  | 846 | [10 empty] | 99.27 |  |  |  | 99.27 | [5 empty] | 100.31 |  |  | 99.26 |  |  |  | 0.73 |  | 0.73 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 5876.33 |  |  | 6917 |  |  |  | 846 | [10 empty] | 78.98 |  |  |  | 78.98 | [5 empty] | 79.29 |  |  | 78.96 |  |  |  | 2.70 |  | 2.19 | [8 empty] | 18.82 |  |  |  |  | 0.00
2012 |  |  |  | 6701.97 |  |  | 7902 |  |  |  | 846 | [10 empty] | 89.98 |  |  |  | 89.98 | [5 empty] | 90.19 |  |  | 89.96 |  |  |  | 0.77 |  | 0.70 | [8 empty] | 9.32 |  |  |  |  | 0.00
2013 |  |  |  | 7075.28 |  |  | 8260 |  |  |  | 846 | [10 empty] | 94.29 |  |  |  | 94.29 | [5 empty] | 95.46 |  |  | 94.28 |  |  |  | 5.71 |  | 5.71 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 6718.01 |  |  | 7880 |  |  |  | 846 | [10 empty] | 89.95 |  |  |  | 89.95 | [5 empty] | 90.65 |  |  | 89.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.05 |  |  |  |  | 0.00
2015 |  |  |  | 7436.93 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.35 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6472.06 |  |  | 7669 |  |  |  | 846 | [10 empty] | 87.31 |  |  |  | 87.31 | [5 empty] | 87.09 |  |  | 87.31 |  |  |  | 6.98 |  | 6.55 | [8 empty] | 6.13 |  |  |  |  | 0.00
2017 |  |  |  | 7356.78 |  |  | 8583 |  |  |  | 847 | [10 empty] | 97.98 |  |  |  | 97.98 | [5 empty] | 99.15 |  |  | 97.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.02 |  |  |  |  | 0.00
2018 |  |  |  | 6745.64 |  |  | 7918 |  |  |  | 847 | [10 empty] | 90.39 |  |  |  | 90.39 | [5 empty] | 90.91 |  |  | 90.39 |  |  |  | 2.68 |  | 2.49 | [8 empty] | 7.12 |  |  |  |  | 0.00
2019 |  |  |  | 7498.64 |  |  | 8760 |  |  |  | 847 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 6859.97 |  |  | 8011 |  |  |  | 847 | [10 empty] | 91.19 |  |  |  | 91.19 | [5 empty] | 92.20 |  |  | 91.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.81 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1973 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 449
B. |  | Refuelling without maintenance | [20 empty] | 774 | [14 empty] | 16
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 814
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 123
E. |  | Testing of plant systems or components | [35 empty] | 17 |  |  |  | 3
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 29
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 1
P. |  | Fire | [39 empty] | 12
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 774 | [14 empty] | 971 |  |  |  | 495 | [11 empty] | 0
Total | [22 empty] | 774 | [14 empty] | 1466
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1973 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 34
12. |  |  | Reactor I&C Systems | [34 empty] | 48
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 40
15. |  |  | Reactor Cooling Systems | [34 empty] | 96
16. |  |  | Steam generation systems | [34 empty] | 125
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 37
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
34. |  |  | Miscellaneous Systems | [34 empty] | 30
41. |  |  | Main Generator Systems | [34 empty] | 13
42. |  |  | Electrical Power Supply Systems | [34 empty] | 31
Total | [37 empty] | 477
Highlights (2020)
Refueling Outage 31 (1EOC31)

## OCONEE-2
2020 Operating Experience
US-270 | [8 empty] | OCONEE-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Owner | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Reactor Supplier | [7 empty] | : | B&W (BABCOCK & WILCOX CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / B&W LLP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-11-06
Thermal power | [12 empty] | : |  |  | 2568 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-12-05
Gross electrical power | [12 empty] | : |  |  | 891 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-09-09
Reference unit power (net) | [12 empty] | : |  |  | 848 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.513
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 34 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 30000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.27 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.33
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19.06 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7670.16 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 102.97 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 653.78 | 613.79 |  |  |  | 655.18 |  | 633.22 | [8 empty] | 651.95 |  |  | 629.94 | [6 empty] | 646.19 |  | 640.43 |  |  |  | 618.70 |  |  | 645.72 |  |  | 628.54 | [9 empty] | 652.72 |  |  | 7670.16
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 103.62 | 104.00 |  |  |  | 103.85 |  | 103.71 | [8 empty] | 103.34 |  |  | 103.17 | [6 empty] | 102.42 |  | 101.51 |  |  |  | 101.33 |  |  | 102.35 |  |  | 102.95 | [9 empty] | 103.46 |  |  | 102.97
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 291632.43 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.79 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.72 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.08 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.17 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.08 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 2115.50 |  |  | 2786 |  |  |  | 920 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 54.57 |  |  | 61.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1975 |  |  |  | 4970.60 |  |  | 6398 |  |  |  | 871 | [10 empty] | 65.21 |  |  |  | 65.21 | [5 empty] | 65.15 |  |  | 73.04 |  |  |  | 29.64 |  | 27.47 | [8 empty] | 7.32 |  |  |  |  | 0.00
1976 |  |  |  | 4232.60 |  |  | 5483 |  |  |  | 871 | [10 empty] | 55.38 |  |  |  | 55.38 | [5 empty] | 55.32 |  |  | 62.42 |  |  |  | 32.45 |  | 26.61 | [8 empty] | 18.02 |  |  |  |  | 0.00
1977 |  |  |  | 3830.00 |  |  | 5315 |  |  |  | 860 | [10 empty] | 50.88 |  |  |  | 50.88 | [5 empty] | 50.84 |  |  | 60.67 |  |  |  | 30.19 |  | 22.00 | [8 empty] | 27.12 |  |  |  |  | 0.00
1978 |  |  |  | 4786.20 |  |  | 6155 |  |  |  | 860 | [10 empty] | 63.54 |  |  |  | 63.54 | [5 empty] | 63.53 |  |  | 70.26 |  |  |  | 25.09 |  | 21.28 | [8 empty] | 15.17 |  |  |  |  | 0.00
1979 |  |  |  | 5968.20 |  |  | 7532 |  |  |  | 860 | [10 empty] | 79.22 |  |  |  | 79.22 | [5 empty] | 79.22 |  |  | 85.98 |  |  |  | 13.54 |  | 12.41 | [8 empty] | 8.37 |  |  |  |  | 0.00
1980 |  |  |  | 3882.00 |  |  | 5397 |  |  |  | 860 | [10 empty] | 62.03 |  |  |  | 69.65 | [5 empty] | 51.39 |  |  | 61.44 |  |  |  | 0.20 |  | 0.14 | [8 empty] | 30.21 |  |  |  |  | 7.62
1981 |  |  |  | 5198.90 |  |  | 7050 |  |  |  | 860 | [10 empty] | 81.03 |  |  |  | 81.03 | [5 empty] | 69.01 |  |  | 80.48 |  |  |  | 15.40 |  | 14.75 | [8 empty] | 4.22 |  |  |  |  | 0.00
1982 |  |  |  | 3447.70 |  |  | 4580 |  |  |  | 860 | [10 empty] | 53.48 |  |  |  | 53.48 | [5 empty] | 45.76 |  |  | 52.28 |  |  |  | 17.17 |  | 11.09 | [8 empty] | 35.44 |  |  |  |  | 0.00
1983 |  |  |  | 5147.00 |  |  | 6348 |  |  |  | 860 | [10 empty] | 73.25 |  |  |  | 73.25 | [5 empty] | 68.32 |  |  | 72.47 |  |  |  | 8.09 |  | 6.45 | [8 empty] | 20.30 |  |  |  |  | 0.00
1984 |  |  |  | 7297.96 |  |  | 8784 |  |  |  | 860 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 96.61 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 5059.95 |  |  | 6654 |  |  |  | 860 | [10 empty] | 76.28 |  |  |  | 76.28 | [5 empty] | 67.17 |  |  | 75.96 |  |  |  | 4.92 |  | 3.95 | [8 empty] | 19.77 |  |  |  |  | 0.00
1986 |  |  |  | 5803.10 |  |  | 7169 |  |  |  | 860 | [10 empty] | 81.37 |  |  |  | 81.37 | [5 empty] | 77.03 |  |  | 81.84 |  |  |  | 1.33 |  | 1.10 | [8 empty] | 17.53 |  |  |  |  | 0.00
1987 |  |  |  | 6228.69 |  |  | 8565 |  |  |  | 860 | [10 empty] | 98.02 |  |  |  | 98.02 | [5 empty] | 82.68 |  |  | 97.77 |  |  |  | 1.98 |  | 1.98 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 5539.98 |  |  | 6880 |  |  |  | 846 | [10 empty] | 78.35 |  |  |  | 78.35 | [5 empty] | 74.55 |  |  | 78.32 |  |  |  | 1.01 |  | 0.80 | [8 empty] | 20.85 |  |  |  |  | 0.00
1989 |  |  |  | 6013.10 |  |  | 7272 |  |  |  | 846 | [10 empty] | 83.06 |  |  |  | 83.06 | [5 empty] | 81.14 |  |  | 83.01 |  |  |  | 4.79 |  | 4.18 | [8 empty] | 12.76 |  |  |  |  | 0.00
1990 |  |  |  | 6269.36 |  |  | 7469 |  |  |  | 846 | [10 empty] | 85.26 |  |  |  | 85.26 | [5 empty] | 84.60 |  |  | 85.26 |  |  |  | 2.95 |  | 2.59 | [8 empty] | 12.15 |  |  |  |  | 0.00
1991 |  |  |  | 7427.94 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.23 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 5946.93 |  |  | 7103 |  |  |  | 846 | [10 empty] | 80.89 |  |  |  | 80.89 | [5 empty] | 80.03 |  |  | 80.86 |  |  |  | 4.00 |  | 3.37 | [8 empty] | 15.74 |  |  |  |  | 0.00
1993 |  |  |  | 6236.28 |  |  | 7352 |  |  |  | 846 | [10 empty] | 83.95 |  |  |  | 83.95 | [5 empty] | 84.15 |  |  | 83.93 |  |  |  | 0.66 |  | 0.56 | [8 empty] | 15.49 |  |  |  |  | 0.00
1994 |  |  |  | 6148.50 |  |  | 7292 |  |  |  | 846 | [10 empty] | 83.33 |  |  |  | 83.33 | [5 empty] | 82.96 |  |  | 83.24 |  |  |  | 5.53 |  | 4.87 | [8 empty] | 11.79 |  |  |  |  | 0.00
1995 |  |  |  | 6973.94 |  |  | 8263 |  |  |  | 846 | [10 empty] | 94.35 |  |  |  | 94.35 | [5 empty] | 94.10 |  |  | 94.33 |  |  |  | 5.65 |  | 5.65 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 4431.97 |  |  | 5304 |  |  |  | 846 | [10 empty] | 60.42 |  |  |  | 60.42 | [5 empty] | 59.64 |  |  | 60.38 |  |  |  | 32.36 |  | 28.90 | [8 empty] | 10.68 |  |  |  |  | 0.00
1997 |  |  |  | 5876.79 |  |  | 6974 |  |  |  | 846 | [10 empty] | 79.67 |  |  |  | 79.67 | [5 empty] | 79.30 |  |  | 79.61 |  |  |  | 20.33 |  | 20.33 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 5654.70 |  |  | 6776 |  |  |  | 846 | [10 empty] | 77.39 |  |  |  | 77.39 | [5 empty] | 76.30 |  |  | 77.35 |  |  |  | 4.49 |  | 3.64 | [8 empty] | 18.97 |  |  |  |  | 0.00
1999 |  |  |  | 6257.60 |  |  | 7374 |  |  |  | 846 | [10 empty] | 84.20 |  |  |  | 84.20 | [5 empty] | 84.44 |  |  | 84.18 |  |  |  | 4.67 |  | 4.13 | [8 empty] | 11.67 |  |  |  |  | 0.00
2000 |  |  |  | 7499.52 |  |  | 8784 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.92 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 6688.42 |  |  | 7836 |  |  |  | 846 | [10 empty] | 89.45 |  |  |  | 89.45 | [5 empty] | 90.25 |  |  | 89.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.55 |  |  |  |  | 0.00
2002 |  |  |  | 6611.11 |  |  | 7743 |  |  |  | 846 | [10 empty] | 88.40 |  |  |  | 88.40 | [5 empty] | 89.20 |  |  | 88.38 |  |  |  | 3.37 |  | 3.08 | [8 empty] | 8.52 |  |  |  |  | 0.00
2003 |  |  |  | 7568.72 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.13 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 5676.11 |  |  | 6652 |  |  |  | 846 | [10 empty] | 75.76 |  |  |  | 75.76 | [5 empty] | 76.38 |  |  | 75.73 |  |  |  | 3.40 |  | 2.67 | [8 empty] | 21.57 |  |  |  |  | 0.00
2005 |  |  |  | 6672.33 |  |  | 7808 |  |  |  | 846 | [10 empty] | 89.14 |  |  |  | 89.14 | [5 empty] | 90.03 |  |  | 89.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.86 |  |  |  |  | 0.00
2006 |  |  |  | 7391.88 |  |  | 8552 |  |  |  | 846 | [10 empty] | 97.65 |  |  |  | 97.65 | [5 empty] | 99.74 |  |  | 97.63 |  |  |  | 1.36 |  | 1.35 | [8 empty] | 1.01 |  |  |  |  | 0.00
2007 |  |  |  | 6768.99 |  |  | 7878 |  |  |  | 846 | [10 empty] | 89.95 |  |  |  | 89.95 | [5 empty] | 91.34 |  |  | 89.93 |  |  |  | 1.13 |  | 1.03 | [8 empty] | 9.02 |  |  |  |  | 0.00
2008 |  |  |  | 6392.52 |  |  | 7470 |  |  |  | 846 | [10 empty] | 85.06 |  |  |  | 85.06 | [5 empty] | 86.02 |  |  | 85.04 |  |  |  | 1.88 |  | 1.63 | [8 empty] | 13.31 |  |  |  |  | 0.00
2009 |  |  |  | 7606.99 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.65 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 6734.26 |  |  | 7829 |  |  |  | 846 | [10 empty] | 89.41 |  |  |  | 89.41 | [5 empty] | 90.87 |  |  | 89.37 |  |  |  | 1.05 |  | 0.95 | [8 empty] | 9.65 |  |  |  |  | 0.00
2011 |  |  |  | 6858.68 |  |  | 8097 |  |  |  | 846 | [10 empty] | 92.45 |  |  |  | 92.45 | [5 empty] | 92.55 |  |  | 92.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.55 |  |  |  |  | 0.00
2012 |  |  |  | 7537.01 |  |  | 8756 |  |  |  | 846 | [10 empty] | 99.69 |  |  |  | 99.69 | [5 empty] | 101.42 |  |  | 99.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.31 |  |  |  |  | 0.00
2013 |  |  |  | 6396.65 |  |  | 7455 |  |  |  | 846 | [10 empty] | 85.11 |  |  |  | 85.11 | [5 empty] | 86.30 |  |  | 85.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.89 |  |  |  |  | 0.00
2014 |  |  |  | 7539.58 |  |  | 8711 |  |  |  | 846 | [10 empty] | 99.44 |  |  |  | 99.44 | [5 empty] | 101.74 |  |  | 99.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.56 |  |  |  |  | 0.00
2015 |  |  |  | 6949.48 |  |  | 8082 |  |  |  | 848 | [10 empty] | 92.28 |  |  |  | 92.28 | [5 empty] | 93.55 |  |  | 92.26 |  |  |  | 0.57 |  | 0.52 | [8 empty] | 7.19 |  |  |  |  | 0.00
2016 |  |  |  | 7609.83 |  |  | 8784 |  |  |  | 848 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.16 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6869.61 |  |  | 8045 |  |  |  | 848 | [10 empty] | 91.83 |  |  |  | 91.83 | [5 empty] | 92.48 |  |  | 91.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.17 |  |  |  |  | 0.00
2018 |  |  |  | 7581.17 |  |  | 8760 |  |  |  | 848 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 6798.42 |  |  | 7955 |  |  |  | 848 | [10 empty] | 90.82 |  |  |  | 90.82 | [5 empty] | 91.52 |  |  | 90.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.18 |  |  |  |  | 0.00
2020 |  |  |  | 7670.16 |  |  | 8783 |  |  |  | 848 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.97 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 418
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 785
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 52
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 3
H. |  | Nuclear regulatory requirements | [39 empty] | 22
L. |  | Human factor related | [39 empty] | 1
Z. |  | Other | [39 empty] | 0
Subtotal | [37 empty] | 841 |  |  |  | 444
Total | [22 empty] | 0 | [14 empty] | 1285
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 31
12. |  |  | Reactor I&C Systems | [34 empty] | 46
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 34
15. |  |  | Reactor Cooling Systems | [34 empty] | 79
16. |  |  | Steam generation systems | [34 empty] | 84
31. |  |  | Turbine and auxiliaries | [34 empty] | 113
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 13
Total | [37 empty] | 423

## OCONEE-3
2020 Operating Experience
US-287 | [8 empty] | OCONEE-3 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Owner | [7 empty] | : | DUKEENER (Duke Energy Corp.)
Reactor Supplier | [7 empty] | : | B&W (BABCOCK & WILCOX CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / B&W LLP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-11-06
Thermal power | [12 empty] | : |  |  | 2568 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-09-18
Gross electrical power | [12 empty] | : |  |  | 900 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-12-16
Reference unit power (net) | [12 empty] | : |  |  | 859 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.513
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 34 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 30000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.27 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.33
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19.06 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7012.14 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.09 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.09 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.91 %
Load Factor (LF) | [18 empty] | : | 92.93 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.07 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 697 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 649.94 | 608.53 |  |  |  | 644.19 |  | 190.34 | [8 empty] | 447.31 |  |  | 631.26 | [6 empty] | 647.41 |  | 641.29 |  |  |  | 619.95 |  |  | 647.29 |  |  | 630.90 | [9 empty] | 653.72 |  |  | 7012.14
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 32.97 | [8 empty] | 71.42 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.09
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 32.97 | [8 empty] | 71.42 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.09
LF [%] |  |  |  |  | 101.70 | 101.78 |  |  |  | 100.80 |  | 30.78 | [8 empty] | 69.99 |  |  | 102.07 | [6 empty] | 101.30 |  | 100.34 |  |  |  | 100.24 |  |  | 101.28 |  |  | 102.01 | [9 empty] | 102.29 |  |  | 92.93
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 32.92 | [8 empty] | 71.37 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.07
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 67.03 | [8 empty] | 28.58 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.91
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 290063.61 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.33 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.52 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.66 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.76 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.58 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.94 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.24 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | Data not provided
1975 |  |  |  | 5037.40 |  |  | 6761 |  |  |  | 871 | [10 empty] | 66.09 |  |  |  | 66.09 | [5 empty] | 66.02 |  |  | 77.18 |  |  |  | 22.28 |  | 18.95 | [8 empty] | 14.96 |  |  |  |  | 0.00
1976 |  |  |  | 4758.00 |  |  | 6072 |  |  |  | 871 | [10 empty] | 62.25 |  |  |  | 62.25 | [5 empty] | 62.19 |  |  | 69.13 |  |  |  | 22.10 |  | 17.66 | [8 empty] | 20.09 |  |  |  |  | 0.00
1977 |  |  |  | 5268.70 |  |  | 6545 |  |  |  | 860 | [10 empty] | 69.90 |  |  |  | 69.90 | [5 empty] | 69.94 |  |  | 74.71 |  |  |  | 19.50 |  | 16.94 | [8 empty] | 13.16 |  |  |  |  | 0.00
1978 |  |  |  | 6064.30 |  |  | 7444 |  |  |  | 860 | [10 empty] | 80.47 |  |  |  | 80.47 | [5 empty] | 80.50 |  |  | 84.98 |  |  |  | 8.17 |  | 7.16 | [8 empty] | 12.37 |  |  |  |  | 0.00
1979 |  |  |  | 3278.90 |  |  | 4038 |  |  |  | 860 | [10 empty] | 43.53 |  |  |  | 43.53 | [5 empty] | 43.52 |  |  | 46.10 |  |  |  | 47.13 |  | 38.81 | [8 empty] | 17.67 |  |  |  |  | 0.00
1980 |  |  |  | 5224.60 |  |  | 6414 |  |  |  | 860 | [10 empty] | 73.84 |  |  |  | 84.77 | [5 empty] | 69.16 |  |  | 73.02 |  |  |  | 8.74 |  | 8.12 | [8 empty] | 7.12 |  |  |  |  | 10.93
1981 |  |  |  | 5641.40 |  |  | 6835 |  |  |  | 860 | [10 empty] | 78.63 |  |  |  | 78.63 | [5 empty] | 74.88 |  |  | 78.03 |  |  |  | 2.19 |  | 1.76 | [8 empty] | 19.61 |  |  |  |  | 0.00
1982 |  |  |  | 2128.40 |  |  | 2826 |  |  |  | 860 | [10 empty] | 33.51 |  |  |  | 33.51 | [5 empty] | 28.25 |  |  | 32.26 |  |  |  | 40.34 |  | 22.65 | [8 empty] | 43.84 |  |  |  |  | 0.00
1983 |  |  |  | 7099.10 |  |  | 8436 |  |  |  | 860 | [10 empty] | 96.52 |  |  |  | 96.52 | [5 empty] | 94.23 |  |  | 96.30 |  |  |  | 3.48 |  | 3.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 5355.51 |  |  | 6474 |  |  |  | 860 | [10 empty] | 74.15 |  |  |  | 74.15 | [5 empty] | 70.89 |  |  | 73.70 |  |  |  | 5.77 |  | 4.54 | [8 empty] | 21.31 |  |  |  |  | 0.00
1985 |  |  |  | 4860.76 |  |  | 6071 |  |  |  | 860 | [10 empty] | 69.67 |  |  |  | 69.67 | [5 empty] | 64.52 |  |  | 69.30 |  |  |  | 16.59 |  | 13.85 | [8 empty] | 16.47 |  |  |  |  | 0.00
1986 |  |  |  | 6064.31 |  |  | 7781 |  |  |  | 860 | [10 empty] | 89.99 |  |  |  | 89.99 | [5 empty] | 80.50 |  |  | 88.82 |  |  |  | 7.45 |  | 7.24 | [8 empty] | 2.77 |  |  |  |  | 0.00
1987 |  |  |  | 5094.42 |  |  | 6068 |  |  |  | 860 | [10 empty] | 69.81 |  |  |  | 69.81 | [5 empty] | 67.62 |  |  | 69.27 |  |  |  | 3.48 |  | 2.52 | [8 empty] | 27.67 |  |  |  |  | 0.00
1988 |  |  |  | 5965.75 |  |  | 7190 |  |  |  | 846 | [10 empty] | 81.87 |  |  |  | 81.87 | [5 empty] | 80.28 |  |  | 81.85 |  |  |  | 7.09 |  | 6.24 | [8 empty] | 11.88 |  |  |  |  | 0.00
1989 |  |  |  | 6337.39 |  |  | 7585 |  |  |  | 846 | [10 empty] | 86.61 |  |  |  | 86.61 | [5 empty] | 85.51 |  |  | 86.59 |  |  |  | 2.39 |  | 2.12 | [8 empty] | 11.27 |  |  |  |  | 0.00
1990 |  |  |  | 7427.84 |  |  | 8712 |  |  |  | 846 | [10 empty] | 99.45 |  |  |  | 99.45 | [5 empty] | 100.23 |  |  | 99.45 |  |  |  | 0.55 |  | 0.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 5594.62 |  |  | 6691 |  |  |  | 846 | [10 empty] | 86.59 |  |  |  | 86.59 | [5 empty] | 75.49 |  |  | 76.38 |  |  |  | 9.61 |  | 9.20 | [8 empty] | 4.21 |  |  |  |  | 0.00
1992 |  |  |  | 5448.23 |  |  | 6634 |  |  |  | 846 | [10 empty] | 75.52 |  |  |  | 75.52 | [5 empty] | 73.31 |  |  | 75.52 |  |  |  | 7.37 |  | 6.01 | [8 empty] | 18.47 |  |  |  |  | 0.00
1993 |  |  |  | 7393.76 |  |  | 8647 |  |  |  | 846 | [10 empty] | 98.72 |  |  |  | 98.72 | [5 empty] | 99.77 |  |  | 98.71 |  |  |  | 0.20 |  | 0.19 | [8 empty] | 1.08 |  |  |  |  | 0.00
1994 |  |  |  | 5670.82 |  |  | 6781 |  |  |  | 846 | [10 empty] | 77.47 |  |  |  | 77.47 | [5 empty] | 76.52 |  |  | 77.41 |  |  |  | 8.35 |  | 7.05 | [8 empty] | 15.48 |  |  |  |  | 0.00
1995 |  |  |  | 6467.84 |  |  | 7625 |  |  |  | 846 | [10 empty] | 87.09 |  |  |  | 87.09 | [5 empty] | 87.27 |  |  | 87.04 |  |  |  | 3.09 |  | 2.77 | [8 empty] | 10.14 |  |  |  |  | 0.00
1996 |  |  |  | 5454.03 |  |  | 6429 |  |  |  | 846 | [10 empty] | 73.22 |  |  |  | 73.22 | [5 empty] | 73.39 |  |  | 73.19 |  |  |  | 3.45 |  | 2.62 | [8 empty] | 24.16 |  |  |  |  | 0.00
1997 |  |  |  | 4652.64 |  |  | 5633 |  |  |  | 846 | [10 empty] | 64.65 |  |  |  | 64.65 | [5 empty] | 62.78 |  |  | 64.30 |  |  |  | 19.58 |  | 15.74 | [8 empty] | 19.61 |  |  |  |  | 0.00
1998 |  |  |  | 5786.35 |  |  | 7026 |  |  |  | 846 | [10 empty] | 80.06 |  |  |  | 80.06 | [5 empty] | 78.08 |  |  | 80.21 |  |  |  | 7.91 |  | 6.88 | [8 empty] | 13.06 |  |  |  |  | 0.00
1999 |  |  |  | 7369.54 |  |  | 8676 |  |  |  | 846 | [10 empty] | 99.05 |  |  |  | 99.05 | [5 empty] | 99.44 |  |  | 99.04 |  |  |  | 0.40 |  | 0.40 | [8 empty] | 0.56 |  |  |  |  | 0.00
2000 |  |  |  | 6577.84 |  |  | 7729 |  |  |  | 846 | [10 empty] | 88.02 |  |  |  | 88.02 | [5 empty] | 88.52 |  |  | 87.99 |  |  |  | 1.51 |  | 1.35 | [8 empty] | 10.63 |  |  |  |  | 0.00
2001 |  |  |  | 5398.55 |  |  | 6355 |  |  |  | 846 | [10 empty] | 72.57 |  |  |  | 72.57 | [5 empty] | 72.85 |  |  | 72.55 |  |  |  | 21.17 |  | 19.48 | [8 empty] | 7.95 |  |  |  |  | 0.00
2002 |  |  |  | 7465.52 |  |  | 8688 |  |  |  | 846 | [10 empty] | 99.18 |  |  |  | 99.18 | [5 empty] | 100.74 |  |  | 99.18 |  |  |  | 0.82 |  | 0.82 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 6318.01 |  |  | 7467 |  |  |  | 846 | [10 empty] | 85.25 |  |  |  | 85.25 | [5 empty] | 85.25 |  |  | 85.24 |  |  |  | 5.72 |  | 5.17 | [8 empty] | 9.58 |  |  |  |  | 0.00
2004 |  |  |  | 5747.05 |  |  | 6698 |  |  |  | 846 | [10 empty] | 76.27 |  |  |  | 76.27 | [5 empty] | 77.34 |  |  | 76.25 |  |  |  | 1.01 |  | 0.78 | [8 empty] | 22.95 |  |  |  |  | 0.00
2005 |  |  |  | 7236.99 |  |  | 8395 |  |  |  | 846 | [10 empty] | 95.87 |  |  |  | 95.87 | [5 empty] | 97.64 |  |  | 95.82 |  |  |  | 3.62 |  | 3.60 | [8 empty] | 0.53 |  |  |  |  | 0.00
2006 |  |  |  | 6716.23 |  |  | 7804 |  |  |  | 846 | [10 empty] | 89.11 |  |  |  | 89.11 | [5 empty] | 90.63 |  |  | 89.09 |  |  |  | 0.69 |  | 0.62 | [8 empty] | 10.27 |  |  |  |  | 0.00
2007 |  |  |  | 6461.88 |  |  | 7498 |  |  |  | 846 | [10 empty] | 85.60 |  |  |  | 85.60 | [5 empty] | 87.19 |  |  | 85.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.40 |  |  |  |  | 0.00
2008 |  |  |  | 7575.11 |  |  | 8717 |  |  |  | 846 | [10 empty] | 99.24 |  |  |  | 99.24 | [5 empty] | 101.94 |  |  | 99.24 |  |  |  | 0.76 |  | 0.76 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 6974.69 |  |  | 8041 |  |  |  | 846 | [10 empty] | 91.81 |  |  |  | 91.81 | [5 empty] | 94.11 |  |  | 91.79 |  |  |  | 0.96 |  | 0.89 | [8 empty] | 7.31 |  |  |  |  | 0.00
2010 |  |  |  | 6778.51 |  |  | 7889 |  |  |  | 846 | [10 empty] | 90.08 |  |  |  | 90.08 | [5 empty] | 91.47 |  |  | 90.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.92 |  |  |  |  | 0.00
2011 |  |  |  | 7602.37 |  |  | 8730 |  |  |  | 846 | [10 empty] | 99.66 |  |  |  | 99.66 | [5 empty] | 102.58 |  |  | 99.66 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 6411.91 |  |  | 7469 |  |  |  | 846 | [10 empty] | 85.05 |  |  |  | 85.05 | [5 empty] | 86.28 |  |  | 85.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.95 |  |  |  |  | 0.00
2013 |  |  |  | 7553.22 |  |  | 8700 |  |  |  | 846 | [10 empty] | 99.31 |  |  |  | 99.31 | [5 empty] | 101.91 |  |  | 99.30 |  |  |  | 0.69 |  | 0.69 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 6935.79 |  |  | 8022 |  |  |  | 846 | [10 empty] | 91.57 |  |  |  | 91.57 | [5 empty] | 93.59 |  |  | 91.58 |  |  |  | 0.30 |  | 0.28 | [8 empty] | 8.15 |  |  |  |  | 0.00
2015 |  |  |  | 7553.32 |  |  | 8701 |  |  |  | 859 | [10 empty] | 99.33 |  |  |  | 99.33 | [5 empty] | 100.38 |  |  | 99.33 |  |  |  | 0.67 |  | 0.67 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 7095.22 |  |  | 8216 |  |  |  | 859 | [10 empty] | 93.53 |  |  |  | 93.53 | [5 empty] | 94.03 |  |  | 93.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.47 |  |  |  |  | 0.00
2017 |  |  |  | 7572.35 |  |  | 8730 |  |  |  | 859 | [10 empty] | 99.66 |  |  |  | 99.66 | [5 empty] | 100.63 |  |  | 99.66 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 6967.44 |  |  | 8083 |  |  |  | 859 | [10 empty] | 92.26 |  |  |  | 92.26 | [5 empty] | 92.59 |  |  | 92.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.74 |  |  |  |  | 0.00
2019 |  |  |  | 7587.62 |  |  | 8760 |  |  |  | 859 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.83 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7012.14 |  |  | 8087 |  |  |  | 859 | [10 empty] | 92.09 |  |  |  | 92.09 | [5 empty] | 92.93 |  |  | 92.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.91 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 390
B. |  | Refuelling without maintenance | [20 empty] | 695 | [14 empty] | 15
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 779
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 93 |  |  |  | 0
E. |  | Testing of plant systems or components | [35 empty] | 9 |  |  |  | 4
H. |  | Nuclear regulatory requirements | [39 empty] | 81
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 3
Z. |  | Other | [35 empty] | 0 |  |  |  | 11
Subtotal | [22 empty] | 695 | [14 empty] | 896 |  |  |  | 489 | [11 empty] | 0
Total | [22 empty] | 695 | [14 empty] | 1385
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 69
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 27
14. |  |  | Safety Systems | [34 empty] | 19
15. |  |  | Reactor Cooling Systems | [34 empty] | 53
16. |  |  | Steam generation systems | [34 empty] | 101
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 53
32. |  |  | Feedwater and Main Steam System | [34 empty] | 23
34. |  |  | Miscellaneous Systems | [34 empty] | 28
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [37 empty] | 400
Highlights (2020)
Refueling Outage 30 (3EOC30)

## PALISADES
2020 Operating Experience
US-255 | [8 empty] | PALISADES | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Owner | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-03-14
Thermal power | [12 empty] | : |  |  | 2565 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1971-12-31
Gross electrical power | [12 empty] | : |  |  | 850 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1971-12-31
Reference unit power (net) | [12 empty] | : |  |  | 805 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 14.48
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.387
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 28 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33205 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.47 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.18
| Active core height/length [m] | [13 empty] | : |  |  | 3.34 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 204 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 25.73 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 5995.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.85 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.85 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 14.15 %
Load Factor (LF) | [18 empty] | : | 84.78 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 85.84 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1244 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 607.20 | 567.65 |  |  |  | 606.48 |  | 585.43 | [8 empty] | 600.02 |  |  | 570.88 | [6 empty] | 583.76 |  | 512.27 |  |  |  | 0.00 |  |  | 170.46 |  |  | 584.08 | [9 empty] | 606.90 |  |  | 5995.12
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 94.76 |  |  |  | 0.00 |  |  | 34.92 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.85
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 94.76 |  |  |  | 0.00 |  |  | 34.92 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.85
LF [%] |  |  |  |  | 101.38 | 101.31 |  |  |  | 101.26 |  | 101.01 | [8 empty] | 100.18 |  |  | 98.50 | [6 empty] | 97.47 |  | 85.53 |  |  |  | 0.00 |  |  | 28.46 |  |  | 100.77 | [9 empty] | 101.33 |  |  | 84.78
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 94.76 |  |  |  | 0.00 |  |  | 34.95 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.84
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 5.24 |  |  |  | 100.00 |  |  | 65.08 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 14.15
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 227256.66 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 14.04 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.05 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 12.21 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.99 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.61 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.74 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 70.78 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1971 |  |  |  | Data not provided
1972 |  |  |  | 1899.10 |  |  | 4990 |  |  |  | 400 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 54.05 |  |  | 56.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 2411.30 |  |  | 3829 |  |  |  | 700 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 39.32 |  |  | 43.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1974 |  |  |  | 93.30 |  |  | 317 |  |  |  | 722 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 1.48 |  |  | 3.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1975 |  |  |  | 2427.80 |  |  | 5649 |  |  |  | 684 | [10 empty] | 40.52 |  |  |  | 40.52 | [5 empty] | 40.52 |  |  | 64.49 |  |  |  | 58.12 |  | 56.23 | [8 empty] | 3.24 |  |  |  |  | 0.00
1976 |  |  |  | 2846.90 |  |  | 4847 |  |  |  | 684 | [10 empty] | 47.43 |  |  |  | 47.43 | [5 empty] | 47.38 |  |  | 55.18 |  |  |  | 24.68 |  | 15.54 | [8 empty] | 37.02 |  |  |  |  | 0.00
1977 |  |  |  | 5084.60 |  |  | 8004 |  |  |  | 635 | [10 empty] | 90.15 |  |  |  | 90.15 | [5 empty] | 91.41 |  |  | 91.37 |  |  |  | 6.50 |  | 6.27 | [8 empty] | 3.58 |  |  |  |  | 0.00
1978 |  |  |  | 2624.20 |  |  | 4346 |  |  |  | 635 | [10 empty] | 46.03 |  |  |  | 46.03 | [5 empty] | 47.18 |  |  | 49.61 |  |  |  | 29.67 |  | 19.42 | [8 empty] | 34.54 |  |  |  |  | 0.00
1979 |  |  |  | 3433.40 |  |  | 5241 |  |  |  | 635 | [10 empty] | 58.73 |  |  |  | 58.73 | [5 empty] | 61.72 |  |  | 59.83 |  |  |  | 13.81 |  | 9.41 | [8 empty] | 31.86 |  |  |  |  | 0.00
1980 |  |  |  | 2379.10 |  |  | 3764 |  |  |  | 635 | [10 empty] | 39.70 |  |  |  | 80.04 | [5 empty] | 42.65 |  |  | 42.85 |  |  |  | 7.37 |  | 6.37 | [8 empty] | 13.59 |  |  |  |  | 40.33
1981 |  |  |  | 3462.70 |  |  | 5009 |  |  |  | 635 | [10 empty] | 55.75 |  |  |  | 55.75 | [5 empty] | 62.25 |  |  | 57.18 |  |  |  | 15.28 |  | 10.06 | [8 empty] | 34.19 |  |  |  |  | 0.00
1982 |  |  |  | 3345.00 |  |  | 4788 |  |  |  | 635 | [10 empty] | 49.29 |  |  |  | 49.29 | [5 empty] | 60.13 |  |  | 54.66 |  |  |  | 50.71 |  | 50.71 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 3770.00 |  |  | 5282 |  |  |  | 635 | [10 empty] | 60.12 |  |  |  | 60.12 | [5 empty] | 67.77 |  |  | 60.30 |  |  |  | 2.01 |  | 1.23 | [8 empty] | 38.65 |  |  |  |  | 0.00
1984 |  |  |  | 811.55 |  |  | 1334 |  |  |  | 635 | [10 empty] | 10.02 |  |  |  | 10.02 | [5 empty] | 14.55 |  |  | 15.19 |  |  |  | 76.28 |  | 32.22 | [8 empty] | 57.76 |  |  |  |  | 0.00
1985 |  |  |  | 5301.80 |  |  | 7342 |  |  |  | 658 | [10 empty] | 82.02 |  |  |  | 82.02 | [5 empty] | 91.85 |  |  | 83.81 |  |  |  | 9.29 |  | 8.40 | [8 empty] | 9.59 |  |  |  |  | 0.00
1986 |  |  |  | 841.24 |  |  | 1323 |  |  |  | 730 | [10 empty] | 14.86 |  |  |  | 14.86 | [5 empty] | 13.16 |  |  | 15.10 |  |  |  | 82.12 |  | 68.28 | [8 empty] | 16.86 |  |  |  |  | 0.00
1987 |  |  |  | 2634.43 |  |  | 3980 |  |  |  | 730 | [10 empty] | 45.16 |  |  |  | 45.16 | [5 empty] | 41.20 |  |  | 45.43 |  |  |  | 48.82 |  | 43.07 | [8 empty] | 11.77 |  |  |  |  | 0.00
1988 |  |  |  | 3435.22 |  |  | 4853 |  |  |  | 730 | [10 empty] | 53.68 |  |  |  | 53.68 | [5 empty] | 53.57 |  |  | 55.25 |  |  |  | 21.29 |  | 14.52 | [8 empty] | 31.80 |  |  |  |  | 0.00
1989 |  |  |  | 3637.78 |  |  | 6019 |  |  |  | 730 | [10 empty] | 67.36 |  |  |  | 67.36 | [5 empty] | 56.89 |  |  | 68.71 |  |  |  | 19.70 |  | 16.53 | [8 empty] | 16.11 |  |  |  |  | 0.00
1990 |  |  |  | 3008.09 |  |  | 5073 |  |  |  | 730 | [10 empty] | 56.09 |  |  |  | 56.09 | [5 empty] | 47.04 |  |  | 57.91 |  |  |  | 5.78 |  | 3.44 | [8 empty] | 40.47 |  |  |  |  | 0.00
1991 |  |  |  | 4873.84 |  |  | 6693 |  |  |  | 730 | [10 empty] | 75.38 |  |  |  | 75.38 | [5 empty] | 76.22 |  |  | 76.40 |  |  |  | 4.76 |  | 3.76 | [8 empty] | 20.85 |  |  |  |  | 0.00
1992 |  |  |  | 4865.07 |  |  | 6293 |  |  |  | 730 | [10 empty] | 70.47 |  |  |  | 70.47 | [5 empty] | 75.87 |  |  | 71.64 |  |  |  | 29.46 |  | 29.43 | [8 empty] | 0.10 |  |  |  |  | 0.00
1993 |  |  |  | 3545.65 |  |  | 4595 |  |  |  | 730 | [10 empty] | 50.37 |  |  |  | 50.37 | [5 empty] | 55.45 |  |  | 52.45 |  |  |  | 9.14 |  | 5.06 | [8 empty] | 44.57 |  |  |  |  | 0.00
1994 |  |  |  | 4513.83 |  |  | 5860 |  |  |  | 730 | [10 empty] | 65.47 |  |  |  | 65.47 | [5 empty] | 70.59 |  |  | 66.89 |  |  |  | 34.53 |  | 34.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 4663.52 |  |  | 6491 |  |  |  | 730 | [10 empty] | 73.02 |  |  |  | 73.02 | [5 empty] | 72.93 |  |  | 74.10 |  |  |  | 26.06 |  | 25.73 | [8 empty] | 1.25 |  |  |  |  | 0.00
1996 |  |  |  | 5314.34 |  |  | 7068 |  |  |  | 730 | [10 empty] | 79.66 |  |  |  | 79.66 | [5 empty] | 82.88 |  |  | 80.46 |  |  |  | 5.42 |  | 4.56 | [8 empty] | 15.78 |  |  |  |  | 0.00
1997 |  |  |  | 5803.46 |  |  | 7714 |  |  |  | 730 | [10 empty] | 87.60 |  |  |  | 87.60 | [5 empty] | 90.75 |  |  | 88.06 |  |  |  | 12.40 |  | 12.40 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 5390.58 |  |  | 7142 |  |  |  | 730 | [10 empty] | 81.12 |  |  |  | 81.12 | [5 empty] | 84.30 |  |  | 81.53 |  |  |  | 6.40 |  | 5.55 | [8 empty] | 13.33 |  |  |  |  | 0.00
1999 |  |  |  | 5128.36 |  |  | 6910 |  |  |  | 730 | [10 empty] | 78.37 |  |  |  | 78.37 | [5 empty] | 80.20 |  |  | 78.88 |  |  |  | 2.57 |  | 2.06 | [8 empty] | 19.57 |  |  |  |  | 0.00
2000 |  |  |  | 5748.02 |  |  | 7672 |  |  |  | 730 | [10 empty] | 86.84 |  |  |  | 86.84 | [5 empty] | 89.64 |  |  | 87.34 |  |  |  | 13.16 |  | 13.16 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 2355.63 |  |  | 3118 |  |  |  | 730 | [10 empty] | 35.15 |  |  |  | 35.15 | [5 empty] | 36.84 |  |  | 35.59 |  |  |  | 60.37 |  | 53.56 | [8 empty] | 11.29 |  |  |  |  | 0.00
2002 |  |  |  | 6369.37 |  |  | 8187 |  |  |  | 730 | [10 empty] | 93.21 |  |  |  | 94.23 | [5 empty] | 99.60 |  |  | 93.46 |  |  |  | 5.77 |  | 5.77 | [8 empty] | 0.00 |  |  |  |  | 1.02
2003 |  |  |  | 6158.15 |  |  | 7914 |  |  |  | 730 | [10 empty] | 89.96 |  |  |  | 89.96 | [5 empty] | 96.30 |  |  | 90.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.04 |  |  |  |  | 0.00
2004 |  |  |  | 5346.14 |  |  | 7164 |  |  |  | 730 | [10 empty] | 81.08 |  |  |  | 81.08 | [5 empty] | 83.37 |  |  | 81.56 |  |  |  | 2.69 |  | 2.24 | [8 empty] | 16.67 |  |  |  |  | 0.00
2005 |  |  |  | 6645.84 |  |  | 8443 |  |  |  | 767 | [10 empty] | 96.38 |  |  |  | 96.38 | [5 empty] | 98.90 |  |  | 96.37 |  |  |  | 3.35 |  | 3.34 | [8 empty] | 0.27 |  |  |  |  | 0.00
2006 |  |  |  | 5917.11 |  |  | 7498 |  |  |  | 778 | [10 empty] | 85.62 |  |  |  | 85.62 | [5 empty] | 86.81 |  |  | 85.58 |  |  |  | 2.29 |  | 2.01 | [8 empty] | 12.37 |  |  |  |  | 0.00
2007 |  |  |  | 5826.02 |  |  | 7427 |  |  |  | 778 | [10 empty] | 84.81 |  |  |  | 84.81 | [5 empty] | 85.48 |  |  | 84.78 |  |  |  | 4.20 |  | 3.72 | [8 empty] | 11.47 |  |  |  |  | 0.00
2008 |  |  |  | 6837.23 |  |  | 8599 |  |  |  | 778 | [10 empty] | 97.91 |  |  |  | 97.91 | [5 empty] | 100.05 |  |  | 97.89 |  |  |  | 2.09 |  | 2.09 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 6118.71 |  |  | 7695 |  |  |  | 778 | [10 empty] | 87.87 |  |  |  | 87.87 | [5 empty] | 89.78 |  |  | 87.84 |  |  |  | 1.09 |  | 0.97 | [8 empty] | 11.16 |  |  |  |  | 0.00
2010 |  |  |  | 6240.66 |  |  | 7915 |  |  |  | 778 | [10 empty] | 90.38 |  |  |  | 90.38 | [5 empty] | 91.57 |  |  | 90.35 |  |  |  | 2.56 |  | 2.37 | [8 empty] | 7.24 |  |  |  |  | 0.00
2011 |  |  |  | 6641.01 |  |  | 8407 |  |  |  | 793 | [10 empty] | 96.07 |  |  |  | 96.07 | [5 empty] | 95.60 |  |  | 95.97 |  |  |  | 3.93 |  | 3.93 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 5178.21 |  |  | 6702 |  |  |  | 793 | [10 empty] | 76.35 |  |  |  | 76.35 | [5 empty] | 74.34 |  |  | 76.30 |  |  |  | 15.01 |  | 13.48 | [8 empty] | 10.17 |  |  |  |  | 0.00
2013 |  |  |  | 6041.70 |  |  | 7567 |  |  |  | 793 | [10 empty] | 86.38 |  |  |  | 86.38 | [5 empty] | 86.96 |  |  | 86.37 |  |  |  | 13.62 |  | 13.62 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 5830.36 |  |  | 7286 |  |  |  | 793 | [10 empty] | 83.17 |  |  |  | 83.17 | [5 empty] | 83.93 |  |  | 83.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.83 |  |  |  |  | 0.00
2015 |  |  |  | 6318.52 |  |  | 7948 |  |  |  | 805 | [10 empty] | 90.87 |  |  |  | 90.87 | [5 empty] | 89.60 |  |  | 90.73 |  |  |  | 0.62 |  | 0.57 | [8 empty] | 8.56 |  |  |  |  | 0.00
2016 |  |  |  | 7041.29 |  |  | 8784 |  |  |  | 805 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.58 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6097.50 |  |  | 7969 |  |  |  | 805 | [10 empty] | 90.96 |  |  |  | 90.96 | [5 empty] | 86.47 |  |  | 90.97 |  |  |  | 1.64 |  | 1.52 | [8 empty] | 7.52 |  |  |  |  | 0.00
2018 |  |  |  | 5455.94 |  |  | 6863 |  |  |  | 805 | [10 empty] | 79.10 |  |  |  | 79.10 | [5 empty] | 77.37 |  |  | 78.34 |  |  |  | 4.72 |  | 3.92 | [8 empty] | 16.98 |  |  |  |  | 0.00
2019 |  |  |  | 6864.36 |  |  | 8585 |  |  |  | 805 | [10 empty] | 98.02 |  |  |  | 98.02 | [5 empty] | 97.34 |  |  | 98.00 |  |  |  | 0.98 |  | 0.97 | [8 empty] | 1.01 |  |  |  |  | 0.00
2020 |  |  |  | 5995.12 |  |  | 7540 |  |  |  | 805 | [10 empty] | 85.85 |  |  |  | 85.85 | [5 empty] | 84.78 |  |  | 85.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.15 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1971 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1282
B. |  | Refuelling without maintenance | [20 empty] | 1243 | [14 empty] | 25
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 995
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 126
E. |  | Testing of plant systems or components | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 84
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 9
P. |  | Fire | [39 empty] | 1
Z. |  | Other | [39 empty] | 19
Subtotal | [22 empty] | 1243 | [14 empty] | 1147 |  |  |  | 1395 | [11 empty] | 5
Total | [22 empty] | 1243 | [14 empty] | 2547
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1971 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 133
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 108
14. |  |  | Safety Systems | [34 empty] | 107
15. |  |  | Reactor Cooling Systems | [34 empty] | 132
16. |  |  | Steam generation systems | [34 empty] | 323
31. |  |  | Turbine and auxiliaries | [34 empty] | 103
32. |  |  | Feedwater and Main Steam System | [34 empty] | 79
33. |  |  | Circulating Water System | [34 empty] | 26
34. |  |  | Miscellaneous Systems | [34 empty] | 19
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 46
42. |  |  | Electrical Power Supply Systems | [34 empty] | 213
Total | [37 empty] | 1289
Highlights (2020)
Refueling Outage 27. On 8/30/2020 at 09:00, Palisades manually shutdown the reactor to commence the planned 1R27 refueling outage.

## PALO VERDE-1
2020 Operating Experience
US-528 | [8 empty] | PALO VERDE-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | APS (ARIZONA PUBLIC SERVICE CO.)
Owner | [7 empty] | : | APS (ARIZONA PUBLIC SERVICE CO.)
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE80 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-05-25
Thermal power | [12 empty] | : |  |  | 3990 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-06-10
Gross electrical power | [12 empty] | : |  |  | 1414 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-01-28
Reference unit power (net) | [12 empty] | : |  |  | 1311 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.45
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.14 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 76 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9818.48 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.93 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.93 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.07 %
Load Factor (LF) | [18 empty] | : | 85.26 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 84.93 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1324 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 995.02 | 927.99 |  |  |  | 991.35 |  | 960.89 | [8 empty] | 989.13 |  |  | 953.86 | [6 empty] | 977.45 |  | 972.94 |  |  |  | 949.34 |  |  | 269.85 |  |  | 0.00 | [9 empty] | 830.65 |  |  | 9818.48
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 29.03 |  |  | 0.00 | [9 empty] | 89.77 |  |  | 84.93
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 29.03 |  |  | 0.00 | [9 empty] | 89.77 |  |  | 84.93
LF [%] |  |  |  |  | 102.01 | 101.70 |  |  |  | 101.64 |  | 101.80 | [8 empty] | 101.41 |  |  | 101.05 | [6 empty] | 100.21 |  | 99.75 |  |  |  | 100.57 |  |  | 27.67 |  |  | 0.00 | [9 empty] | 85.16 |  |  | 85.26
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 29.03 |  |  | 0.00 | [9 empty] | 89.78 |  |  | 84.93
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 70.97 |  |  | 100.00 | [9 empty] | 10.23 |  |  | 15.07
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 340830.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.68 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.16 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.66 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.77 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.14 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.23 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 6264.75 |  |  | 5349 |  |  |  | 1221 | [10 empty] | 63.26 |  |  |  | 63.26 | [5 empty] | 62.16 |  |  | 64.51 |  |  |  | 36.74 |  | 36.74 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 5268.27 |  |  | 4500 |  |  |  | 1221 | [10 empty] | 50.89 |  |  |  | 50.89 | [5 empty] | 49.26 |  |  | 51.38 |  |  |  | 32.44 |  | 24.43 | [8 empty] | 24.67 |  |  |  |  | 0.00
1988 |  |  |  | 6668.69 |  |  | 5585 |  |  |  | 1221 | [10 empty] | 62.81 |  |  |  | 62.81 | [5 empty] | 62.18 |  |  | 63.58 |  |  |  | 35.00 |  | 33.82 | [8 empty] | 3.37 |  |  |  |  | 0.00
1989 |  |  |  | 1796.57 |  |  | 1522 |  |  |  | 1221 | [10 empty] | 14.06 |  |  |  | 14.06 | [5 empty] | 16.80 |  |  | 17.37 |  |  |  | 40.50 |  | 9.57 | [8 empty] | 76.37 |  |  |  |  | 0.00
1990 |  |  |  | 4719.46 |  |  | 3925 |  |  |  | 1221 | [10 empty] | 42.61 |  |  |  | 42.61 | [5 empty] | 44.12 |  |  | 44.81 |  |  |  | 9.64 |  | 4.55 | [8 empty] | 52.84 |  |  |  |  | 0.00
1991 |  |  |  | 9312.14 |  |  | 7567 |  |  |  | 1221 | [10 empty] | 85.85 |  |  |  | 87.09 | [5 empty] | 87.06 |  |  | 86.38 |  |  |  | 1.56 |  | 1.38 | [8 empty] | 11.53 |  |  |  |  | 1.25
1992 |  |  |  | 7118.80 |  |  | 6010 |  |  |  | 1221 | [10 empty] | 67.16 |  |  |  | 67.16 | [5 empty] | 66.37 |  |  | 68.42 |  |  |  | 6.70 |  | 4.82 | [8 empty] | 28.02 |  |  |  |  | 0.00
1993 |  |  |  | 7514.76 |  |  | 6665 |  |  |  | 1221 | [10 empty] | 76.06 |  |  |  | 76.06 | [5 empty] | 70.26 |  |  | 76.08 |  |  |  | 1.41 |  | 1.09 | [8 empty] | 22.85 |  |  |  |  | 0.00
1994 |  |  |  | 9772.54 |  |  | 8656 |  |  |  | 1221 | [10 empty] | 98.78 |  |  |  | 98.78 | [5 empty] | 91.37 |  |  | 98.81 |  |  |  | 1.22 |  | 1.22 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 8526.82 |  |  | 7244 |  |  |  | 1224 | [10 empty] | 82.10 |  |  |  | 82.10 | [5 empty] | 79.52 |  |  | 82.69 |  |  |  | 2.15 |  | 1.80 | [8 empty] | 16.10 |  |  |  |  | 0.00
1996 |  |  |  | 8713.00 |  |  | 7246 |  |  |  | 1227 | [10 empty] | 81.97 |  |  |  | 84.39 | [5 empty] | 80.84 |  |  | 82.49 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 15.60 |  |  |  |  | 2.42
1997 |  |  |  | 10737.71 |  |  | 8658 |  |  |  | 1244 | [10 empty] | 98.82 |  |  |  | 98.82 | [5 empty] | 98.47 |  |  | 98.82 |  |  |  | 1.18 |  | 1.18 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 9575.01 |  |  | 7819 |  |  |  | 1243 | [10 empty] | 89.04 |  |  |  | 89.04 | [5 empty] | 87.94 |  |  | 89.26 |  |  |  | 0.76 |  | 0.68 | [8 empty] | 10.28 |  |  |  |  | 0.00
1999 |  |  |  | 9653.94 |  |  | 7774 |  |  |  | 1243 | [10 empty] | 88.76 |  |  |  | 88.76 | [5 empty] | 88.66 |  |  | 88.74 |  |  |  | 0.76 |  | 0.68 | [8 empty] | 10.56 |  |  |  |  | 0.00
2000 |  |  |  | 10966.60 |  |  | 8770 |  |  |  | 1243 | [10 empty] | 99.84 |  |  |  | 99.84 | [5 empty] | 100.44 |  |  | 99.84 |  |  |  | 0.16 |  | 0.16 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 9559.58 |  |  | 7712 |  |  |  | 1243 | [10 empty] | 88.04 |  |  |  | 88.04 | [5 empty] | 87.79 |  |  | 88.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.96 |  |  |  |  | 0.00
2002 |  |  |  | 9705.03 |  |  | 7890 |  |  |  | 1243 | [10 empty] | 90.14 |  |  |  | 90.14 | [5 empty] | 89.13 |  |  | 90.07 |  |  |  | 0.90 |  | 0.82 | [8 empty] | 9.04 |  |  |  |  | 0.00
2003 |  |  |  | 10587.11 |  |  | 8604 |  |  |  | 1243 | [10 empty] | 98.24 |  |  |  | 98.24 | [5 empty] | 97.23 |  |  | 98.22 |  |  |  | 1.76 |  | 1.76 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 9235.80 |  |  | 7669 |  |  |  | 1243 | [10 empty] | 87.33 |  |  |  | 88.53 | [5 empty] | 84.59 |  |  | 87.31 |  |  |  | 1.33 |  | 1.19 | [8 empty] | 10.28 |  |  |  |  | 1.20
2005 |  |  |  | 7212.30 |  |  | 6194 |  |  |  | 1243 | [10 empty] | 70.73 |  |  |  | 70.73 | [5 empty] | 66.24 |  |  | 70.71 |  |  |  | 3.95 |  | 2.91 | [8 empty] | 26.36 |  |  |  |  | 0.00
2006 |  |  |  | 4868.23 |  |  | 5292 |  |  |  | 1314 | [10 empty] | 60.44 |  |  |  | 60.44 | [5 empty] | 42.29 |  |  | 60.41 |  |  |  | 12.90 |  | 8.95 | [8 empty] | 30.61 |  |  |  |  | 0.00
2007 |  |  |  | 8844.90 |  |  | 6834 |  |  |  | 1311 | [10 empty] | 78.04 |  |  |  | 78.04 | [5 empty] | 77.02 |  |  | 78.01 |  |  |  | 2.23 |  | 1.78 | [8 empty] | 20.18 |  |  |  |  | 0.00
2008 |  |  |  | 9953.15 |  |  | 7616 |  |  |  | 1311 | [10 empty] | 86.71 |  |  |  | 86.71 | [5 empty] | 86.43 |  |  | 86.70 |  |  |  | 0.88 |  | 0.77 | [8 empty] | 12.52 |  |  |  |  | 0.00
2009 |  |  |  | 11589.72 |  |  | 8707 |  |  |  | 1311 | [10 empty] | 99.40 |  |  |  | 99.40 | [5 empty] | 100.92 |  |  | 99.39 |  |  |  | 0.60 |  | 0.60 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 9307.97 |  |  | 7217 |  |  |  | 1311 | [10 empty] | 82.41 |  |  |  | 82.41 | [5 empty] | 81.05 |  |  | 82.39 |  |  |  | 4.46 |  | 3.85 | [8 empty] | 13.74 |  |  |  |  | 0.00
2011 |  |  |  | 9525.07 |  |  | 7400 |  |  |  | 1311 | [10 empty] | 84.50 |  |  |  | 84.50 | [5 empty] | 82.94 |  |  | 84.47 |  |  |  | 1.69 |  | 1.46 | [8 empty] | 14.05 |  |  |  |  | 0.00
2012 |  |  |  | 11482.17 |  |  | 8784 |  |  |  | 1311 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.71 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 10481.92 |  |  | 8044 |  |  |  | 1311 | [10 empty] | 91.83 |  |  |  | 91.83 | [5 empty] | 91.27 |  |  | 91.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.17 |  |  |  |  | 0.00
2014 |  |  |  | 10350.31 |  |  | 7943 |  |  |  | 1311 | [10 empty] | 90.68 |  |  |  | 90.68 | [5 empty] | 90.13 |  |  | 90.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.32 |  |  |  |  | 0.00
2015 |  |  |  | 11600.88 |  |  | 8760 |  |  |  | 1311 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.01 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 10068.74 |  |  | 7763 |  |  |  | 1311 | [10 empty] | 88.37 |  |  |  | 88.37 | [5 empty] | 87.43 |  |  | 88.38 |  |  |  | 1.67 |  | 1.50 | [8 empty] | 10.13 |  |  |  |  | 0.00
2017 |  |  |  | 10477.95 |  |  | 8012 |  |  |  | 1311 | [10 empty] | 91.46 |  |  |  | 91.46 | [5 empty] | 91.24 |  |  | 91.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.54 |  |  |  |  | 0.00
2018 |  |  |  | 11220.88 |  |  | 8655 |  |  |  | 1311 | [10 empty] | 98.80 |  |  |  | 98.80 | [5 empty] | 97.71 |  |  | 98.80 |  |  |  | 1.20 |  | 1.20 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 10515.17 |  |  | 7956 |  |  |  | 1311 | [10 empty] | 90.83 |  |  |  | 90.83 | [5 empty] | 91.56 |  |  | 90.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.17 |  |  |  |  | 0.00
2020 |  |  |  | 9818.48 |  |  | 7460 |  |  |  | 1311 | [10 empty] | 84.93 |  |  |  | 84.93 | [5 empty] | 85.26 |  |  | 84.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.07 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 405
B. |  | Refuelling without maintenance | [20 empty] | 1324 | [14 empty] | 38
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1010
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 138
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 8
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 5
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 8
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 2
Z. |  | Other | [39 empty] | 14
Subtotal | [22 empty] | 1324 | [14 empty] | 1189 |  |  |  | 434 | [11 empty] | 12
Total | [22 empty] | 1324 | [14 empty] | 1635
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 74
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 61
16. |  |  | Steam generation systems | [34 empty] | 34
31. |  |  | Turbine and auxiliaries | [34 empty] | 5
32. |  |  | Feedwater and Main Steam System | [34 empty] | 89
33. |  |  | Circulating Water System | [34 empty] | 24
34. |  |  | Miscellaneous Systems | [34 empty] | 38
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 11
42. |  |  | Electrical Power Supply Systems | [34 empty] | 58
Total | [37 empty] | 412
Highlights (2020)
Refueling Outage 22

## PALO VERDE-2
2020 Operating Experience
US-529 | [8 empty] | PALO VERDE-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | APS (ARIZONA PUBLIC SERVICE CO.)
Owner | [7 empty] | : | APS (ARIZONA PUBLIC SERVICE CO.)
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE80 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-06-01
Thermal power | [12 empty] | : |  |  | 3990 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-05-20
Gross electrical power | [12 empty] | : |  |  | 1414 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-09-19
Reference unit power (net) | [12 empty] | : |  |  | 1314 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.45
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.21 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 76 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10466.37 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.26 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.11 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.26 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.62 %
Load Factor (LF) | [18 empty] | : | 90.68 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.27 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 855 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 997.55 | 932.02 |  |  |  | 824.25 |  | 88.82 | [8 empty] | 801.30 |  |  | 954.48 | [6 empty] | 980.91 |  | 978.85 |  |  |  | 953.10 |  |  | 992.46 |  |  | 965.80 | [9 empty] | 996.83 |  |  | 10466.37
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 86.85 |  | 9.98 | [8 empty] | 85.30 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.26
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 86.85 |  | 9.98 | [8 empty] | 85.30 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.26
LF [%] |  |  |  |  | 102.04 | 101.91 |  |  |  | 84.31 |  | 9.39 | [8 empty] | 81.97 |  |  | 100.89 | [6 empty] | 100.34 |  | 100.13 |  |  |  | 100.74 |  |  | 101.52 |  |  | 102.08 | [9 empty] | 101.97 |  |  | 90.68
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 86.83 |  | 10.00 | [8 empty] | 85.35 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.27
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 13.15 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.11
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 90.02 | [8 empty] | 14.70 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.62
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 341064.94 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.33 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.46 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.06 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.53 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.41 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.26 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.07 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.48 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | Data not provided
1987 |  |  |  | 8190.04 |  |  | 6860 |  |  |  | 1221 | [10 empty] | 77.59 |  |  |  | 77.59 | [5 empty] | 76.57 |  |  | 78.31 |  |  |  | 6.73 |  | 5.60 | [8 empty] | 16.81 |  |  |  |  | 0.00
1988 |  |  |  | 6747.17 |  |  | 5613 |  |  |  | 1221 | [10 empty] | 62.56 |  |  |  | 62.56 | [5 empty] | 62.91 |  |  | 63.90 |  |  |  | 3.50 |  | 2.27 | [8 empty] | 35.17 |  |  |  |  | 0.00
1989 |  |  |  | 4698.76 |  |  | 4003 |  |  |  | 1221 | [10 empty] | 44.31 |  |  |  | 44.31 | [5 empty] | 43.93 |  |  | 45.70 |  |  |  | 25.08 |  | 14.83 | [8 empty] | 40.86 |  |  |  |  | 0.00
1990 |  |  |  | 6242.22 |  |  | 5276 |  |  |  | 1221 | [10 empty] | 58.63 |  |  |  | 58.63 | [5 empty] | 58.36 |  |  | 60.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 41.37 |  |  |  |  | 0.00
1991 |  |  |  | 8265.19 |  |  | 6690 |  |  |  | 1221 | [10 empty] | 76.27 |  |  |  | 76.27 | [5 empty] | 77.27 |  |  | 76.37 |  |  |  | 3.69 |  | 2.92 | [8 empty] | 20.81 |  |  |  |  | 0.00
1992 |  |  |  | 10104.51 |  |  | 8341 |  |  |  | 1221 | [10 empty] | 94.85 |  |  |  | 94.85 | [5 empty] | 94.21 |  |  | 94.96 |  |  |  | 2.94 |  | 2.87 | [8 empty] | 2.27 |  |  |  |  | 0.00
1993 |  |  |  | 5125.31 |  |  | 4621 |  |  |  | 1221 | [10 empty] | 50.91 |  |  |  | 50.91 | [5 empty] | 47.92 |  |  | 52.75 |  |  |  | 3.50 |  | 1.84 | [8 empty] | 47.25 |  |  |  |  | 0.00
1994 |  |  |  | 6573.86 |  |  | 5919 |  |  |  | 1221 | [10 empty] | 66.82 |  |  |  | 66.82 | [5 empty] | 61.46 |  |  | 67.57 |  |  |  | 5.45 |  | 3.85 | [8 empty] | 29.33 |  |  |  |  | 0.00
1995 |  |  |  | 9070.86 |  |  | 7420 |  |  |  | 1224 | [10 empty] | 84.16 |  |  |  | 84.16 | [5 empty] | 84.60 |  |  | 84.70 |  |  |  | 0.53 |  | 0.45 | [8 empty] | 15.39 |  |  |  |  | 0.00
1996 |  |  |  | 9346.14 |  |  | 7548 |  |  |  | 1227 | [10 empty] | 85.46 |  |  |  | 85.46 | [5 empty] | 86.72 |  |  | 85.93 |  |  |  | 0.73 |  | 0.62 | [8 empty] | 13.92 |  |  |  |  | 0.00
1997 |  |  |  | 9322.67 |  |  | 7661 |  |  |  | 1244 | [10 empty] | 87.22 |  |  |  | 87.22 | [5 empty] | 85.49 |  |  | 87.44 |  |  |  | 2.65 |  | 2.38 | [8 empty] | 10.40 |  |  |  |  | 0.00
1998 |  |  |  | 11084.83 |  |  | 8760 |  |  |  | 1243 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.80 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 9797.35 |  |  | 7857 |  |  |  | 1243 | [10 empty] | 89.71 |  |  |  | 89.71 | [5 empty] | 89.98 |  |  | 89.69 |  |  |  | 0.45 |  | 0.41 | [8 empty] | 9.89 |  |  |  |  | 0.00
2000 |  |  |  | 9525.26 |  |  | 7743 |  |  |  | 1243 | [10 empty] | 88.17 |  |  |  | 88.17 | [5 empty] | 87.24 |  |  | 88.15 |  |  |  | 1.24 |  | 1.11 | [8 empty] | 10.73 |  |  |  |  | 0.00
2001 |  |  |  | 10083.52 |  |  | 8002 |  |  |  | 1243 | [10 empty] | 91.36 |  |  |  | 91.36 | [5 empty] | 92.61 |  |  | 91.35 |  |  |  | 8.64 |  | 8.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 10019.17 |  |  | 7981 |  |  |  | 1243 | [10 empty] | 91.12 |  |  |  | 91.12 | [5 empty] | 92.01 |  |  | 91.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.88 |  |  |  |  | 0.00
2003 |  |  |  | 8444.41 |  |  | 6809 |  |  |  | 1243 | [10 empty] | 77.74 |  |  |  | 77.74 | [5 empty] | 77.55 |  |  | 77.73 |  |  |  | 0.78 |  | 0.61 | [8 empty] | 21.65 |  |  |  |  | 0.00
2004 |  |  |  | 10662.06 |  |  | 8138 |  |  |  | 1335 | [10 empty] | 92.60 |  |  |  | 94.90 | [5 empty] | 91.96 |  |  | 92.65 |  |  |  | 5.10 |  | 5.10 | [8 empty] | 0.00 |  |  |  |  | 2.30
2005 |  |  |  | 9427.24 |  |  | 7284 |  |  |  | 1335 | [10 empty] | 83.18 |  |  |  | 83.18 | [5 empty] | 80.61 |  |  | 83.15 |  |  |  | 3.96 |  | 3.43 | [8 empty] | 13.39 |  |  |  |  | 0.00
2006 |  |  |  | 9808.17 |  |  | 7535 |  |  |  | 1314 | [10 empty] | 86.05 |  |  |  | 86.05 | [5 empty] | 85.21 |  |  | 86.02 |  |  |  | 1.76 |  | 1.55 | [8 empty] | 12.41 |  |  |  |  | 0.00
2007 |  |  |  | 10957.60 |  |  | 8384 |  |  |  | 1314 | [10 empty] | 95.71 |  |  |  | 95.71 | [5 empty] | 95.20 |  |  | 95.71 |  |  |  | 4.29 |  | 4.29 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8624.08 |  |  | 6577 |  |  |  | 1314 | [10 empty] | 74.88 |  |  |  | 74.88 | [5 empty] | 74.72 |  |  | 74.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.12 |  |  |  |  | 0.00
2009 |  |  |  | 9521.55 |  |  | 7254 |  |  |  | 1314 | [10 empty] | 82.82 |  |  |  | 82.82 | [5 empty] | 82.72 |  |  | 82.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.18 |  |  |  |  | 0.00
2010 |  |  |  | 11652.97 |  |  | 8760 |  |  |  | 1314 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.24 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 10421.32 |  |  | 7921 |  |  |  | 1314 | [10 empty] | 90.43 |  |  |  | 90.43 | [5 empty] | 90.54 |  |  | 90.42 |  |  |  | 0.00 |  | 0.10 | [8 empty] | 9.47 |  |  |  |  | 0.00
2012 |  |  |  | 10358.07 |  |  | 7957 |  |  |  | 1314 | [10 empty] | 90.59 |  |  |  | 90.59 | [5 empty] | 89.74 |  |  | 90.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.41 |  |  |  |  | 0.00
2013 |  |  |  | 11235.03 |  |  | 8488 |  |  |  | 1314 | [10 empty] | 96.90 |  |  |  | 96.90 | [5 empty] | 97.61 |  |  | 96.89 |  |  |  | 3.10 |  | 3.10 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 10394.10 |  |  | 7904 |  |  |  | 1314 | [10 empty] | 90.22 |  |  |  | 90.22 | [5 empty] | 90.30 |  |  | 90.23 |  |  |  | 2.00 |  | 1.84 | [8 empty] | 7.94 |  |  |  |  | 0.00
2015 |  |  |  | 10410.84 |  |  | 7883 |  |  |  | 1314 | [10 empty] | 89.98 |  |  |  | 89.98 | [5 empty] | 90.45 |  |  | 89.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.02 |  |  |  |  | 0.00
2016 |  |  |  | 11696.95 |  |  | 8784 |  |  |  | 1314 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.34 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 10588.60 |  |  | 8011 |  |  |  | 1314 | [10 empty] | 91.44 |  |  |  | 91.44 | [5 empty] | 91.99 |  |  | 91.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.56 |  |  |  |  | 0.00
2018 |  |  |  | 9458.03 |  |  | 7216 |  |  |  | 1314 | [10 empty] | 82.38 |  |  |  | 82.38 | [5 empty] | 82.17 |  |  | 82.37 |  |  |  | 1.14 |  | 0.95 | [8 empty] | 16.68 |  |  |  |  | 0.00
2019 |  |  |  | 11434.51 |  |  | 8670 |  |  |  | 1314 | [10 empty] | 98.98 |  |  |  | 98.98 | [5 empty] | 99.34 |  |  | 98.97 |  |  |  | 1.02 |  | 1.02 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 10466.37 |  |  | 7929 |  |  |  | 1314 | [10 empty] | 90.26 |  |  |  | 90.26 | [5 empty] | 90.68 |  |  | 90.27 |  |  |  | 0.00 |  | 1.11 | [8 empty] | 8.62 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 141
B. |  | Refuelling without maintenance | [20 empty] | 758 | [14 empty] | 22
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 910
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 163
E. |  | Testing of plant systems or components | [35 empty] | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 21
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 10
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Z. |  | Other | [31 empty] | 98 |  |  |  | 77 |  |  |  | 6 | [11 empty] | 3
Subtotal | [22 empty] | 758 | [10 empty] | 98 |  |  |  | 1172 |  |  |  | 178 | [11 empty] | 9
Total | [22 empty] | 856 | [14 empty] | 1359
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 22
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 20
15. |  |  | Reactor Cooling Systems | [34 empty] | 15
16. |  |  | Steam generation systems | [34 empty] | 21
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
34. |  |  | Miscellaneous Systems | [34 empty] | 32
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [37 empty] | 169
Highlights (2020)
Unplanned automatic RX trip due to Auxiliary Feedwater Pumps (AFAS1 & AFAS2) actuated on low SG level following trip of both Main Feedwater Pumps (MFWPs) during restoration of power to MFWP lube oil control panel.

## PALO VERDE-3
2020 Operating Experience
US-530 | [8 empty] | PALO VERDE-3 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | APS (ARIZONA PUBLIC SERVICE CO.)
Owner | [7 empty] | : | APS (ARIZONA PUBLIC SERVICE CO.)
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE80 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-06-01
Thermal power | [12 empty] | : |  |  | 3990 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-11-28
Gross electrical power | [12 empty] | : |  |  | 1414 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-01-08
Reference unit power (net) | [12 empty] | : |  |  | 1312 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.45
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.37 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 76 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 11267.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.24 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.76 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.24 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.76 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 97.77 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 97.76 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 197 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 983.42 | 631.60 |  |  |  | 980.59 |  | 949.59 | [8 empty] | 978.83 |  |  | 943.22 | [6 empty] | 970.70 |  | 969.28 |  |  |  | 943.86 |  |  | 980.86 |  |  | 949.80 | [9 empty] | 985.82 |  |  | 11267.58
EAF [%] |  |  |  |  | 100.00 | 71.70 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.76
UCF [%] |  |  |  |  | 100.00 | 71.70 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.76
LF [%] |  |  |  |  | 100.75 | 69.17 |  |  |  | 100.46 |  | 100.52 | [8 empty] | 100.28 |  |  | 99.85 | [6 empty] | 99.44 |  | 99.30 |  |  |  | 99.92 |  |  | 100.48 |  |  | 100.55 | [9 empty] | 100.99 |  |  | 97.77
OF [%] |  |  |  |  | 100.00 | 71.70 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.76
FLR [%] |  |  |  |  | 0.00 | 28.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.24
UCL [%] |  |  |  |  | 0.00 | 28.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.24
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 314934.65 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.96 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.73 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.48 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.79 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.73 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.2 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.29 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 10035.48 |  |  | 8177 |  |  |  | 1221 | [10 empty] | 94.92 |  |  |  | 94.92 | [5 empty] | 95.39 |  |  | 94.90 |  |  |  | 5.08 |  | 5.08 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 1327.99 |  |  | 1096 |  |  |  | 1221 | [10 empty] | 9.01 |  |  |  | 9.01 | [5 empty] | 12.42 |  |  | 12.51 |  |  |  | 40.97 |  | 6.25 | [8 empty] | 84.74 |  |  |  |  | 0.00
1990 |  |  |  | 9636.01 |  |  | 8048 |  |  |  | 1221 | [10 empty] | 91.58 |  |  |  | 91.58 | [5 empty] | 90.09 |  |  | 91.87 |  |  |  | 8.36 |  | 8.35 | [8 empty] | 0.07 |  |  |  |  | 0.00
1991 |  |  |  | 7518.45 |  |  | 6272 |  |  |  | 1221 | [10 empty] | 70.78 |  |  |  | 75.30 | [5 empty] | 70.29 |  |  | 71.60 |  |  |  | 2.63 |  | 2.03 | [8 empty] | 22.67 |  |  |  |  | 4.52
1992 |  |  |  | 8386.20 |  |  | 6923 |  |  |  | 1221 | [10 empty] | 78.72 |  |  |  | 78.72 | [5 empty] | 78.19 |  |  | 78.81 |  |  |  | 3.48 |  | 2.84 | [8 empty] | 18.44 |  |  |  |  | 0.00
1993 |  |  |  | 9393.90 |  |  | 7898 |  |  |  | 1221 | [10 empty] | 90.12 |  |  |  | 90.12 | [5 empty] | 87.83 |  |  | 90.16 |  |  |  | 2.69 |  | 2.49 | [8 empty] | 7.39 |  |  |  |  | 0.00
1994 |  |  |  | 6824.49 |  |  | 5920 |  |  |  | 1221 | [10 empty] | 66.35 |  |  |  | 66.35 | [5 empty] | 63.80 |  |  | 67.58 |  |  |  | 1.29 |  | 0.87 | [8 empty] | 32.78 |  |  |  |  | 0.00
1995 |  |  |  | 9386.83 |  |  | 7628 |  |  |  | 1225 | [10 empty] | 86.63 |  |  |  | 86.63 | [5 empty] | 87.44 |  |  | 87.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.37 |  |  |  |  | 0.00
1996 |  |  |  | 10789.60 |  |  | 8699 |  |  |  | 1230 | [10 empty] | 99.04 |  |  |  | 99.52 | [5 empty] | 99.86 |  |  | 99.03 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.00 |  |  |  |  | 0.48
1997 |  |  |  | 9456.06 |  |  | 7820 |  |  |  | 1247 | [10 empty] | 89.13 |  |  |  | 89.13 | [5 empty] | 86.50 |  |  | 89.26 |  |  |  | 0.38 |  | 0.34 | [8 empty] | 10.54 |  |  |  |  | 0.00
1998 |  |  |  | 9600.91 |  |  | 7835 |  |  |  | 1247 | [10 empty] | 89.26 |  |  |  | 89.26 | [5 empty] | 87.89 |  |  | 89.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.74 |  |  |  |  | 0.00
1999 |  |  |  | 10956.48 |  |  | 8760 |  |  |  | 1247 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.30 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 9888.71 |  |  | 7898 |  |  |  | 1247 | [10 empty] | 89.94 |  |  |  | 89.94 | [5 empty] | 90.28 |  |  | 89.91 |  |  |  | 1.59 |  | 1.46 | [8 empty] | 8.61 |  |  |  |  | 0.00
2001 |  |  |  | 9170.39 |  |  | 7439 |  |  |  | 1247 | [10 empty] | 84.96 |  |  |  | 84.96 | [5 empty] | 83.95 |  |  | 84.92 |  |  |  | 1.60 |  | 1.38 | [8 empty] | 13.65 |  |  |  |  | 0.00
2002 |  |  |  | 11137.71 |  |  | 8760 |  |  |  | 1247 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.96 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 9554.71 |  |  | 7712 |  |  |  | 1247 | [10 empty] | 88.05 |  |  |  | 88.05 | [5 empty] | 87.47 |  |  | 88.04 |  |  |  | 2.18 |  | 1.96 | [8 empty] | 9.99 |  |  |  |  | 0.00
2004 |  |  |  | 8223.32 |  |  | 6729 |  |  |  | 1247 | [10 empty] | 76.65 |  |  |  | 78.41 | [5 empty] | 75.07 |  |  | 76.61 |  |  |  | 4.32 |  | 3.54 | [8 empty] | 18.06 |  |  |  |  | 1.76
2005 |  |  |  | 9163.97 |  |  | 7471 |  |  |  | 1247 | [10 empty] | 85.31 |  |  |  | 85.31 | [5 empty] | 83.89 |  |  | 85.29 |  |  |  | 2.88 |  | 2.53 | [8 empty] | 12.16 |  |  |  |  | 0.00
2006 |  |  |  | 9335.83 |  |  | 7625 |  |  |  | 1247 | [10 empty] | 87.07 |  |  |  | 87.07 | [5 empty] | 85.46 |  |  | 87.04 |  |  |  | 1.70 |  | 1.51 | [8 empty] | 11.43 |  |  |  |  | 0.00
2007 |  |  |  | 6993.69 |  |  | 5903 |  |  |  | 1247 | [10 empty] | 67.42 |  |  |  | 67.42 | [5 empty] | 64.02 |  |  | 67.39 |  |  |  | 7.47 |  | 5.45 | [8 empty] | 27.13 |  |  |  |  | 0.00
2008 |  |  |  | 10673.28 |  |  | 8197 |  |  |  | 1317 | [10 empty] | 93.32 |  |  |  | 93.32 | [5 empty] | 92.26 |  |  | 93.32 |  |  |  | 1.90 |  | 1.81 | [8 empty] | 4.87 |  |  |  |  | 0.00
2009 |  |  |  | 9562.61 |  |  | 7310 |  |  |  | 1317 | [10 empty] | 83.46 |  |  |  | 83.46 | [5 empty] | 82.89 |  |  | 83.45 |  |  |  | 2.11 |  | 1.80 | [8 empty] | 14.74 |  |  |  |  | 0.00
2010 |  |  |  | 10238.99 |  |  | 7801 |  |  |  | 1317 | [10 empty] | 89.06 |  |  |  | 89.06 | [5 empty] | 88.75 |  |  | 89.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.94 |  |  |  |  | 0.00
2011 |  |  |  | 11331.50 |  |  | 8657 |  |  |  | 1312 | [10 empty] | 98.84 |  |  |  | 98.84 | [5 empty] | 98.59 |  |  | 98.82 |  |  |  | 1.16 |  | 1.16 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 10093.67 |  |  | 7797 |  |  |  | 1312 | [10 empty] | 88.78 |  |  |  | 88.78 | [5 empty] | 87.58 |  |  | 88.76 |  |  |  | 2.82 |  | 2.58 | [8 empty] | 8.64 |  |  |  |  | 0.00
2013 |  |  |  | 9714.13 |  |  | 7506 |  |  |  | 1312 | [10 empty] | 85.68 |  |  |  | 85.68 | [5 empty] | 84.52 |  |  | 85.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.32 |  |  |  |  | 0.00
2014 |  |  |  | 11579.13 |  |  | 8760 |  |  |  | 1312 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.75 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 10502.98 |  |  | 8037 |  |  |  | 1312 | [10 empty] | 91.74 |  |  |  | 91.74 | [5 empty] | 91.38 |  |  | 91.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.26 |  |  |  |  | 0.00
2016 |  |  |  | 10477.43 |  |  | 8001 |  |  |  | 1312 | [10 empty] | 91.09 |  |  |  | 91.09 | [5 empty] | 90.91 |  |  | 91.09 |  |  |  | 1.04 |  | 0.96 | [8 empty] | 7.95 |  |  |  |  | 0.00
2017 |  |  |  | 11273.58 |  |  | 8626 |  |  |  | 1312 | [10 empty] | 98.63 |  |  |  | 98.63 | [5 empty] | 98.09 |  |  | 98.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.37 |  |  |  |  | 0.00
2018 |  |  |  | 10427.45 |  |  | 7983 |  |  |  | 1312 | [10 empty] | 91.13 |  |  |  | 91.13 | [5 empty] | 90.73 |  |  | 91.13 |  |  |  | 1.04 |  | 0.96 | [8 empty] | 7.91 |  |  |  |  | 0.00
2019 |  |  |  | 9969.69 |  |  | 7619 |  |  |  | 1312 | [10 empty] | 86.99 |  |  |  | 86.99 | [5 empty] | 86.74 |  |  | 86.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.01 |  |  |  |  | 0.00
2020 |  |  |  | 11267.58 |  |  | 8587 |  |  |  | 1312 | [10 empty] | 97.76 |  |  |  | 97.76 | [5 empty] | 97.77 |  |  | 97.76 |  |  |  | 2.24 |  | 2.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 123
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 940
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 86
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 6
H. |  | Nuclear regulatory requirements | [39 empty] | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 25
Z. |  | Other | [24 empty] | 197 | [14 empty] | 7 | [11 empty] | 0
Subtotal | [26 empty] | 197 | [10 empty] | 1030 |  |  |  | 140 | [11 empty] | 30
Total | [22 empty] | 197 | [14 empty] | 1200
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 10
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 18
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 27
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
34. |  |  | Miscellaneous Systems | [34 empty] | 20
41. |  |  | Main Generator Systems | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 45
Total | [37 empty] | 152
Highlights (2020)
Unplanned manual reactor shutdown due to degradation of the 1B RCP seal.

## PEACH BOTTOM-2
2020 Operating Experience
US-277 | [8 empty] | PEACH BOTTOM-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXE/PSEG (EXELON Corp. (50%) PSEG Power (50%))
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-01-31
Thermal power | [12 empty] | : |  |  | 3951 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-02-18
Gross electrical power | [12 empty] | : |  |  | 1412 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-07-05
Reference unit power (net) | [12 empty] | : |  |  | 1300 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.1
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.16
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 48000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.57 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.65
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.37 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10211.82 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.34 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.34 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.66 %
Load Factor (LF) | [18 empty] | : | 89.43 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.34 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 673 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1001.34 | 936.51 |  |  |  | 995.18 |  | 964.53 | [8 empty] | 973.20 |  |  | 925.39 | [6 empty] | 929.81 |  | 882.02 |  |  |  | 771.62 |  |  | 412.70 |  |  | 448.92 | [9 empty] | 970.59 |  |  | 10211.82
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 58.06 |  |  | 49.90 | [9 empty] | 100.00 |  |  | 92.34
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 58.06 |  |  | 49.90 | [9 empty] | 100.00 |  |  | 92.34
LF [%] |  |  |  |  | 103.53 | 103.50 |  |  |  | 102.89 |  | 103.05 | [8 empty] | 100.62 |  |  | 98.87 | [6 empty] | 96.13 |  | 91.19 |  |  |  | 82.44 |  |  | 42.67 |  |  | 47.96 | [9 empty] | 100.35 |  |  | 89.43
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 58.06 |  |  | 50.00 | [9 empty] | 100.00 |  |  | 92.34
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 41.94 |  |  | 50.10 | [9 empty] | 0.00 |  |  | 7.66
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 358577.73 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.45 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.86 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.72 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.41 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.42 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 4982.70 |  |  | 6162 |  |  |  | 1053 | [10 empty] | 90.55 |  |  |  | 90.55 | [5 empty] | 78.92 |  |  | 90.58 |  |  |  | 7.84 |  | 7.70 | [8 empty] | 1.75 |  |  |  |  | 0.00
1975 |  |  |  | 5082.50 |  |  | 6638 |  |  |  | 1051 | [10 empty] | 55.26 |  |  |  | 55.26 | [5 empty] | 55.20 |  |  | 75.78 |  |  |  | 22.93 |  | 16.44 | [8 empty] | 28.31 |  |  |  |  | 0.00
1976 |  |  |  | 5580.40 |  |  | 5998 |  |  |  | 1051 | [10 empty] | 60.51 |  |  |  | 60.51 | [5 empty] | 60.45 |  |  | 68.28 |  |  |  | 13.21 |  | 9.21 | [8 empty] | 30.28 |  |  |  |  | 0.00
1977 |  |  |  | 4051.60 |  |  | 4836 |  |  |  | 1051 | [10 empty] | 44.04 |  |  |  | 44.04 | [5 empty] | 44.01 |  |  | 55.21 |  |  |  | 23.10 |  | 13.23 | [8 empty] | 42.73 |  |  |  |  | 0.00
1978 |  |  |  | 6793.60 |  |  | 7299 |  |  |  | 1051 | [10 empty] | 73.79 |  |  |  | 73.79 | [5 empty] | 73.79 |  |  | 83.32 |  |  |  | 7.88 |  | 6.31 | [8 empty] | 19.89 |  |  |  |  | 0.00
1979 |  |  |  | 8574.40 |  |  | 8295 |  |  |  | 1051 | [10 empty] | 92.91 |  |  |  | 92.91 | [5 empty] | 93.13 |  |  | 94.69 |  |  |  | 0.92 |  | 0.86 | [8 empty] | 6.23 |  |  |  |  | 0.00
1980 |  |  |  | 4372.60 |  |  | 4529 |  |  |  | 1051 | [10 empty] | 49.95 |  |  |  | 49.95 | [5 empty] | 47.36 |  |  | 51.56 |  |  |  | 4.19 |  | 2.18 | [8 empty] | 47.87 |  |  |  |  | 0.00
1981 |  |  |  | 6635.30 |  |  | 6938 |  |  |  | 1051 | [10 empty] | 78.53 |  |  |  | 78.53 | [5 empty] | 72.07 |  |  | 79.20 |  |  |  | 19.56 |  | 19.10 | [8 empty] | 2.37 |  |  |  |  | 0.00
1982 |  |  |  | 4816.80 |  |  | 5089 |  |  |  | 1051 | [10 empty] | 56.46 |  |  |  | 56.46 | [5 empty] | 52.32 |  |  | 58.09 |  |  |  | 3.36 |  | 1.96 | [8 empty] | 41.57 |  |  |  |  | 0.00
1983 |  |  |  | 4481.10 |  |  | 4461 |  |  |  | 1051 | [10 empty] | 49.03 |  |  |  | 49.56 | [5 empty] | 48.67 |  |  | 50.92 |  |  |  | 11.53 |  | 6.46 | [8 empty] | 43.98 |  |  |  |  | 0.53
1984 |  |  |  | 2465.82 |  |  | 2544 |  |  |  | 1051 | [10 empty] | 28.85 |  |  |  | 28.85 | [5 empty] | 26.71 |  |  | 28.96 |  |  |  | 4.54 |  | 1.37 | [8 empty] | 69.77 |  |  |  |  | 0.00
1985 |  |  |  | 2378.20 |  |  | 2570 |  |  |  | 1051 | [10 empty] | 28.67 |  |  |  | 28.67 | [5 empty] | 25.83 |  |  | 29.34 |  |  |  | 24.48 |  | 9.30 | [8 empty] | 62.03 |  |  |  |  | 0.00
1986 |  |  |  | 6896.57 |  |  | 7010 |  |  |  | 1051 | [10 empty] | 79.76 |  |  |  | 79.76 | [5 empty] | 74.91 |  |  | 80.02 |  |  |  | 18.80 |  | 18.46 | [8 empty] | 1.77 |  |  |  |  | 0.00
1987 |  |  |  | 1599.91 |  |  | 1724 |  |  |  | 1051 | [10 empty] | 16.48 |  |  |  | 16.48 | [5 empty] | 17.38 |  |  | 19.68 |  |  |  | 48.28 |  | 15.39 | [8 empty] | 68.13 |  |  |  |  | 0.00
1988 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1051 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1989 |  |  |  | 3880.86 |  |  | 4735 |  |  |  | 1051 | [10 empty] | 52.26 |  |  |  | 52.26 | [5 empty] | 42.15 |  |  | 54.05 |  |  |  | 12.44 |  | 7.42 | [8 empty] | 40.32 |  |  |  |  | 0.00
1990 |  |  |  | 6699.80 |  |  | 6977 |  |  |  | 1055 | [10 empty] | 78.92 |  |  |  | 78.92 | [5 empty] | 72.49 |  |  | 79.65 |  |  |  | 8.26 |  | 7.11 | [8 empty] | 13.97 |  |  |  |  | 0.00
1991 |  |  |  | 5120.97 |  |  | 5277 |  |  |  | 1055 | [10 empty] | 58.82 |  |  |  | 58.82 | [5 empty] | 55.41 |  |  | 60.24 |  |  |  | 18.91 |  | 13.72 | [8 empty] | 27.46 |  |  |  |  | 0.00
1992 |  |  |  | 5677.94 |  |  | 5811 |  |  |  | 1055 | [10 empty] | 64.94 |  |  |  | 64.94 | [5 empty] | 61.27 |  |  | 66.15 |  |  |  | 13.16 |  | 9.84 | [8 empty] | 25.23 |  |  |  |  | 0.00
1993 |  |  |  | 7704.08 |  |  | 7571 |  |  |  | 1053 | [10 empty] | 85.92 |  |  |  | 85.92 | [5 empty] | 83.47 |  |  | 86.43 |  |  |  | 5.53 |  | 5.03 | [8 empty] | 9.05 |  |  |  |  | 0.00
1994 |  |  |  | 7450.65 |  |  | 7783 |  |  |  | 1055 | [10 empty] | 88.80 |  |  |  | 88.80 | [5 empty] | 80.60 |  |  | 88.85 |  |  |  | 1.59 |  | 1.43 | [8 empty] | 9.77 |  |  |  |  | 0.00
1995 |  |  |  | 9363.44 |  |  | 8598 |  |  |  | 1093 | [10 empty] | 98.15 |  |  |  | 98.15 | [5 empty] | 97.79 |  |  | 98.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.85 |  |  |  |  | 0.00
1996 |  |  |  | 7660.56 |  |  | 8176 |  |  |  | 1093 | [10 empty] | 93.09 |  |  |  | 93.09 | [5 empty] | 79.79 |  |  | 93.08 |  |  |  | 1.75 |  | 1.66 | [8 empty] | 5.25 |  |  |  |  | 0.00
1997 |  |  |  | 9570.35 |  |  | 8663 |  |  |  | 1093 | [10 empty] | 98.89 |  |  |  | 98.89 | [5 empty] | 99.95 |  |  | 98.89 |  |  |  | 0.43 |  | 0.42 | [8 empty] | 0.68 |  |  |  |  | 0.00
1998 |  |  |  | 7658.77 |  |  | 7923 |  |  |  | 1093 | [10 empty] | 90.45 |  |  |  | 90.45 | [5 empty] | 79.99 |  |  | 90.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.55 |  |  |  |  | 0.00
1999 |  |  |  | 9462.31 |  |  | 8635 |  |  |  | 1093 | [10 empty] | 98.58 |  |  |  | 98.58 | [5 empty] | 98.83 |  |  | 98.57 |  |  |  | 1.42 |  | 1.42 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 8523.01 |  |  | 8169 |  |  |  | 1093 | [10 empty] | 93.01 |  |  |  | 93.01 | [5 empty] | 88.77 |  |  | 93.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.99 |  |  |  |  | 0.00
2001 |  |  |  | 9369.24 |  |  | 8563 |  |  |  | 1093 | [10 empty] | 97.76 |  |  |  | 97.76 | [5 empty] | 97.85 |  |  | 97.75 |  |  |  | 2.24 |  | 2.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 8838.93 |  |  | 8149 |  |  |  | 1093 | [10 empty] | 93.03 |  |  |  | 93.03 | [5 empty] | 92.32 |  |  | 93.03 |  |  |  | 0.81 |  | 0.76 | [8 empty] | 6.21 |  |  |  |  | 0.00
2003 |  |  |  | 9265.77 |  |  | 8430 |  |  |  | 1112 | [10 empty] | 96.32 |  |  |  | 96.32 | [5 empty] | 94.86 |  |  | 96.23 |  |  |  | 3.68 |  | 3.68 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 8886.06 |  |  | 8066 |  |  |  | 1112 | [10 empty] | 91.85 |  |  |  | 91.85 | [5 empty] | 90.97 |  |  | 91.83 |  |  |  | 1.61 |  | 1.51 | [8 empty] | 6.65 |  |  |  |  | 0.00
2005 |  |  |  | 9615.14 |  |  | 8569 |  |  |  | 1112 | [10 empty] | 97.83 |  |  |  | 97.83 | [5 empty] | 98.70 |  |  | 97.81 |  |  |  | 0.40 |  | 0.40 | [8 empty] | 1.78 |  |  |  |  | 0.00
2006 |  |  |  | 9088.33 |  |  | 8172 |  |  |  | 1112 | [10 empty] | 93.30 |  |  |  | 93.30 | [5 empty] | 93.30 |  |  | 93.29 |  |  |  | 0.72 |  | 0.68 | [8 empty] | 6.02 |  |  |  |  | 0.00
2007 |  |  |  | 9867.90 |  |  | 8737 |  |  |  | 1112 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.57 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8750.03 |  |  | 7914 |  |  |  | 1112 | [10 empty] | 90.11 |  |  |  | 90.11 | [5 empty] | 89.58 |  |  | 90.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.89 |  |  |  |  | 0.00
2009 |  |  |  | 9941.74 |  |  | 8760 |  |  |  | 1112 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 9000.11 |  |  | 8139 |  |  |  | 1122 | [10 empty] | 92.99 |  |  |  | 92.99 | [5 empty] | 91.57 |  |  | 92.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.01 |  |  |  |  | 0.00
2011 |  |  |  | 9978.33 |  |  | 8760 |  |  |  | 1122 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.52 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 8671.08 |  |  | 7832 |  |  |  | 1125 | [10 empty] | 89.18 |  |  |  | 89.18 | [5 empty] | 87.94 |  |  | 89.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.82 |  |  |  |  | 0.00
2013 |  |  |  | 10103.52 |  |  | 8760 |  |  |  | 1125 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.51 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 8641.88 |  |  | 7685 |  |  |  | 1125 | [10 empty] | 87.74 |  |  |  | 87.74 | [5 empty] | 87.69 |  |  | 87.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.26 |  |  |  |  | 0.00
2015 |  |  |  | 10762.56 |  |  | 8692 |  |  |  | 1308 | [10 empty] | 99.29 |  |  |  | 99.29 | [5 empty] | 99.70 |  |  | 99.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.71 |  |  |  |  | 0.00
2016 |  |  |  | 10476.69 |  |  | 8322 |  |  |  | 1308 | [10 empty] | 94.74 |  |  |  | 94.74 | [5 empty] | 91.19 |  |  | 94.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.26 |  |  |  |  | 0.00
2017 |  |  |  | 11313.07 |  |  | 8760 |  |  |  | 1308 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.73 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 10784.58 |  |  | 8395 |  |  |  | 1308 | [10 empty] | 96.07 |  |  |  | 96.07 | [5 empty] | 94.12 |  |  | 95.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.93 |  |  |  |  | 0.00
2019 |  |  |  | 11534.21 |  |  | 8760 |  |  |  | 1300 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 10211.82 |  |  | 8111 |  |  |  | 1300 | [10 empty] | 92.34 |  |  |  | 92.34 | [5 empty] | 89.43 |  |  | 92.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.66 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 309
B. |  | Refuelling without maintenance | [20 empty] | 673 | [14 empty] | 22
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1045
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 187
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 0
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 116
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [35 empty] | 25 |  |  |  | 5 | [11 empty] | 1
Subtotal | [22 empty] | 673 | [14 empty] | 1284 |  |  |  | 435 | [11 empty] | 5
Total | [22 empty] | 673 | [14 empty] | 1724
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 0
12. |  |  | Reactor I&C Systems | [34 empty] | 19
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 12
14. |  |  | Safety Systems | [34 empty] | 40
15. |  |  | Reactor Cooling Systems | [34 empty] | 79
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 50
31. |  |  | Turbine and auxiliaries | [34 empty] | 39
32. |  |  | Feedwater and Main Steam System | [34 empty] | 23
34. |  |  | Miscellaneous Systems | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 51
Total | [37 empty] | 325
Highlights (2020)
2R23

## PEACH BOTTOM-3
2020 Operating Experience
US-278 | [8 empty] | PEACH BOTTOM-3 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXE/PSEG (EXELON Corp. (50%) PSEG Power (50%))
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-01-31
Thermal power | [12 empty] | : |  |  | 3951 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-09-01
Gross electrical power | [12 empty] | : |  |  | 1412 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-12-23
Reference unit power (net) | [12 empty] | : |  |  | 1331 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.1
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.16
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 48000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.75 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.65
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 11580.52 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 99.05 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1003.65 | 940.12 |  |  |  | 989.48 |  | 969.87 | [8 empty] | 994.63 |  |  | 930.52 | [6 empty] | 942.15 |  | 944.61 |  |  |  | 929.30 |  |  | 981.57 |  |  | 967.14 | [9 empty] | 987.48 |  |  | 11580.52
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 101.35 | 101.48 |  |  |  | 99.92 |  | 101.21 | [8 empty] | 100.44 |  |  | 97.10 | [6 empty] | 95.14 |  | 95.39 |  |  |  | 96.97 |  |  | 99.12 |  |  | 100.92 | [9 empty] | 99.72 |  |  | 99.05
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 355997.24 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.96 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.17 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.08 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.24 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.68 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.9 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.08 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.13 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 1095.30 |  |  | 1902 |  |  |  | 1073 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1975 |  |  |  | 5282.40 |  |  | 7520 |  |  |  | 1035 | [10 empty] | 58.19 |  |  |  | 58.19 | [5 empty] | 58.26 |  |  | 85.84 |  |  |  | 24.55 |  | 18.94 | [8 empty] | 22.87 |  |  |  |  | 0.00
1976 |  |  |  | 6056.80 |  |  | 6829 |  |  |  | 1035 | [10 empty] | 66.68 |  |  |  | 66.68 | [5 empty] | 66.62 |  |  | 77.74 |  |  |  | 18.98 |  | 15.62 | [8 empty] | 17.70 |  |  |  |  | 0.00
1977 |  |  |  | 4787.80 |  |  | 5450 |  |  |  | 1035 | [10 empty] | 52.84 |  |  |  | 52.84 | [5 empty] | 52.81 |  |  | 62.21 |  |  |  | 14.35 |  | 8.85 | [8 empty] | 38.30 |  |  |  |  | 0.00
1978 |  |  |  | 6973.60 |  |  | 7412 |  |  |  | 1035 | [10 empty] | 76.91 |  |  |  | 76.91 | [5 empty] | 76.92 |  |  | 84.61 |  |  |  | 6.53 |  | 5.37 | [8 empty] | 17.71 |  |  |  |  | 0.00
1979 |  |  |  | 6110.40 |  |  | 6500 |  |  |  | 1035 | [10 empty] | 67.21 |  |  |  | 67.21 | [5 empty] | 67.39 |  |  | 74.20 |  |  |  | 5.73 |  | 4.09 | [8 empty] | 28.71 |  |  |  |  | 0.00
1980 |  |  |  | 7233.40 |  |  | 7089 |  |  |  | 1035 | [10 empty] | 79.70 |  |  |  | 80.12 | [5 empty] | 79.56 |  |  | 80.70 |  |  |  | 11.47 |  | 10.38 | [8 empty] | 9.49 |  |  |  |  | 0.43
1981 |  |  |  | 3171.10 |  |  | 3201 |  |  |  | 1035 | [10 empty] | 33.00 |  |  |  | 33.00 | [5 empty] | 34.98 |  |  | 36.54 |  |  |  | 13.97 |  | 5.36 | [8 empty] | 61.64 |  |  |  |  | 0.00
1982 |  |  |  | 8532.30 |  |  | 8372 |  |  |  | 1035 | [10 empty] | 95.35 |  |  |  | 95.35 | [5 empty] | 94.11 |  |  | 95.57 |  |  |  | 4.65 |  | 4.65 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 2465.70 |  |  | 2714 |  |  |  | 1035 | [10 empty] | 27.14 |  |  |  | 27.50 | [5 empty] | 27.20 |  |  | 30.98 |  |  |  | 4.64 |  | 1.34 | [8 empty] | 71.16 |  |  |  |  | 0.36
1984 |  |  |  | 7445.52 |  |  | 7545 |  |  |  | 1035 | [10 empty] | 85.15 |  |  |  | 86.21 | [5 empty] | 81.90 |  |  | 85.89 |  |  |  | 13.79 |  | 13.79 | [8 empty] | 0.00 |  |  |  |  | 1.06
1985 |  |  |  | 3320.84 |  |  | 3988 |  |  |  | 1035 | [10 empty] | 45.11 |  |  |  | 45.11 | [5 empty] | 36.63 |  |  | 45.53 |  |  |  | 0.83 |  | 0.38 | [8 empty] | 54.51 |  |  |  |  | 0.00
1986 |  |  |  | 4858.84 |  |  | 5542 |  |  |  | 1035 | [10 empty] | 60.94 |  |  |  | 60.94 | [5 empty] | 53.59 |  |  | 63.26 |  |  |  | 20.95 |  | 16.15 | [8 empty] | 22.91 |  |  |  |  | 0.00
1987 |  |  |  | 1507.72 |  |  | 1658 |  |  |  | 1035 | [10 empty] | 14.41 |  |  |  | 14.41 | [5 empty] | 16.63 |  |  | 18.93 |  |  |  | 85.59 |  | 85.59 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1035 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1989 |  |  |  | 247.31 |  |  | 472 |  |  |  | 1035 | [10 empty] | 0.10 |  |  |  | 0.10 | [5 empty] | 2.73 |  |  | 5.39 |  |  |  | 47.89 |  | 0.09 | [8 empty] | 99.81 |  |  |  |  | 0.00
1990 |  |  |  | 7534.10 |  |  | 7684 |  |  |  | 1035 | [10 empty] | 87.08 |  |  |  | 87.08 | [5 empty] | 83.10 |  |  | 87.72 |  |  |  | 5.30 |  | 4.87 | [8 empty] | 8.05 |  |  |  |  | 0.00
1991 |  |  |  | 5118.92 |  |  | 5212 |  |  |  | 1035 | [10 empty] | 57.26 |  |  |  | 59.14 | [5 empty] | 56.46 |  |  | 59.50 |  |  |  | 13.61 |  | 9.32 | [8 empty] | 31.54 |  |  |  |  | 1.88
1992 |  |  |  | 7180.95 |  |  | 7391 |  |  |  | 1035 | [10 empty] | 83.65 |  |  |  | 83.65 | [5 empty] | 78.99 |  |  | 84.14 |  |  |  | 12.72 |  | 12.19 | [8 empty] | 4.16 |  |  |  |  | 0.00
1993 |  |  |  | 6314.03 |  |  | 6594 |  |  |  | 1035 | [10 empty] | 73.89 |  |  |  | 73.89 | [5 empty] | 69.64 |  |  | 75.27 |  |  |  | 7.25 |  | 5.77 | [8 empty] | 20.34 |  |  |  |  | 0.00
1994 |  |  |  | 8867.35 |  |  | 8588 |  |  |  | 1035 | [10 empty] | 97.93 |  |  |  | 97.93 | [5 empty] | 97.80 |  |  | 98.04 |  |  |  | 2.07 |  | 2.07 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 7172.49 |  |  | 7929 |  |  |  | 1049 | [10 empty] | 90.12 |  |  |  | 90.12 | [5 empty] | 78.01 |  |  | 90.51 |  |  |  | 3.20 |  | 2.98 | [8 empty] | 6.89 |  |  |  |  | 0.00
1996 |  |  |  | 9424.69 |  |  | 8627 |  |  |  | 1093 | [10 empty] | 98.21 |  |  |  | 98.21 | [5 empty] | 98.16 |  |  | 98.21 |  |  |  | 1.79 |  | 1.79 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 7566.58 |  |  | 7909 |  |  |  | 1093 | [10 empty] | 90.29 |  |  |  | 90.29 | [5 empty] | 79.03 |  |  | 90.29 |  |  |  | 1.75 |  | 1.61 | [8 empty] | 8.11 |  |  |  |  | 0.00
1998 |  |  |  | 8823.63 |  |  | 8172 |  |  |  | 1093 | [10 empty] | 93.30 |  |  |  | 93.30 | [5 empty] | 92.16 |  |  | 93.29 |  |  |  | 1.41 |  | 1.34 | [8 empty] | 5.36 |  |  |  |  | 0.00
1999 |  |  |  | 8558.61 |  |  | 8100 |  |  |  | 1093 | [10 empty] | 92.48 |  |  |  | 92.48 | [5 empty] | 89.39 |  |  | 92.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.52 |  |  |  |  | 0.00
2000 |  |  |  | 9556.78 |  |  | 8722 |  |  |  | 1093 | [10 empty] | 99.30 |  |  |  | 99.30 | [5 empty] | 99.54 |  |  | 99.29 |  |  |  | 0.70 |  | 0.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 8524.44 |  |  | 8153 |  |  |  | 1093 | [10 empty] | 93.09 |  |  |  | 93.09 | [5 empty] | 89.03 |  |  | 93.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.91 |  |  |  |  | 0.00
2002 |  |  |  | 9647.38 |  |  | 8740 |  |  |  | 1093 | [10 empty] | 99.78 |  |  |  | 99.78 | [5 empty] | 100.76 |  |  | 99.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.22 |  |  |  |  | 0.00
2003 |  |  |  | 8937.81 |  |  | 8089 |  |  |  | 1112 | [10 empty] | 92.38 |  |  |  | 92.38 | [5 empty] | 92.94 |  |  | 92.34 |  |  |  | 4.49 |  | 4.35 | [8 empty] | 3.27 |  |  |  |  | 0.00
2004 |  |  |  | 9989.10 |  |  | 8784 |  |  |  | 1112 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.27 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 8848.91 |  |  | 8105 |  |  |  | 1112 | [10 empty] | 92.55 |  |  |  | 92.55 | [5 empty] | 90.84 |  |  | 92.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.45 |  |  |  |  | 0.00
2006 |  |  |  | 9912.75 |  |  | 8760 |  |  |  | 1112 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 9030.82 |  |  | 8207 |  |  |  | 1112 | [10 empty] | 93.70 |  |  |  | 93.70 | [5 empty] | 92.71 |  |  | 93.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.30 |  |  |  |  | 0.00
2008 |  |  |  | 9830.48 |  |  | 8729 |  |  |  | 1112 | [10 empty] | 99.38 |  |  |  | 99.38 | [5 empty] | 100.64 |  |  | 99.37 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 8668.09 |  |  | 7888 |  |  |  | 1112 | [10 empty] | 90.09 |  |  |  | 90.09 | [5 empty] | 88.98 |  |  | 90.05 |  |  |  | 2.04 |  | 1.88 | [8 empty] | 8.04 |  |  |  |  | 0.00
2010 |  |  |  | 9759.27 |  |  | 8640 |  |  |  | 1112 | [10 empty] | 98.64 |  |  |  | 98.64 | [5 empty] | 100.19 |  |  | 98.63 |  |  |  | 1.36 |  | 1.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8873.28 |  |  | 7952 |  |  |  | 1122 | [10 empty] | 90.81 |  |  |  | 90.81 | [5 empty] | 90.95 |  |  | 90.78 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 8.89 |  |  |  |  | 0.00
2012 |  |  |  | 10148.35 |  |  | 8784 |  |  |  | 1138 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.52 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 8673.15 |  |  | 7656 |  |  |  | 1138 | [10 empty] | 87.40 |  |  |  | 87.40 | [5 empty] | 86.99 |  |  | 87.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.60 |  |  |  |  | 0.00
2014 |  |  |  | 10124.97 |  |  | 8757 |  |  |  | 1138 | [10 empty] | 99.96 |  |  |  | 99.96 | [5 empty] | 101.57 |  |  | 99.97 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 9101.27 |  |  | 8006 |  |  |  | 1308 | [10 empty] | 91.50 |  |  |  | 91.50 | [5 empty] | 90.15 |  |  | 91.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.50 |  |  |  |  | 0.00
2016 |  |  |  | 11406.74 |  |  | 8784 |  |  |  | 1309 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.20 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 10421.37 |  |  | 8378 |  |  |  | 1309 | [10 empty] | 95.64 |  |  |  | 95.64 | [5 empty] | 90.88 |  |  | 95.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.36 |  |  |  |  | 0.00
2018 |  |  |  | 10895.50 |  |  | 8384 |  |  |  | 1251 | [10 empty] | 95.70 |  |  |  | 95.70 | [5 empty] | 99.54 |  |  | 95.71 |  |  |  | 4.30 |  | 4.30 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 10761.63 |  |  | 8377 |  |  |  | 1331 | [10 empty] | 95.90 |  |  |  | 95.90 | [5 empty] | 92.30 |  |  | 95.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.10 |  |  |  |  | 0.00
2020 |  |  |  | 11580.51 |  |  | 8783 |  |  |  | 1331 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.05 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 292
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1107
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 66
E. |  | Testing of plant systems or components | [35 empty] | 13 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 148
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 8
L. |  | Human factor related | [39 empty] | 14
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 8
Z. |  | Other | [35 empty] | 18 |  |  |  | 0 | [11 empty] | 1
Subtotal | [37 empty] | 1204 |  |  |  | 455 | [11 empty] | 17
Total | [22 empty] | 0 | [14 empty] | 1676
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 20
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 35
15. |  |  | Reactor Cooling Systems | [34 empty] | 82
31. |  |  | Turbine and auxiliaries | [34 empty] | 38
32. |  |  | Feedwater and Main Steam System | [34 empty] | 50
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 15
42. |  |  | Electrical Power Supply Systems | [34 empty] | 54
Total | [37 empty] | 306

## PERRY-1
2020 Operating Experience
US-440 | [8 empty] | PERRY-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FENOC (FIRST ENERGY NUCLEAR OPERATING CO.)
Owner | [7 empty] | : | CEI (CLEVELAND ELECTRIC ILLUMINATING CO.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-6 (Mark 3) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-10-01
Thermal power | [12 empty] | : |  |  | 3758 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-12-19
Gross electrical power | [12 empty] | : |  |  | 1303 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-11-18
Reference unit power (net) | [12 empty] | : |  |  | 1240 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.31
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 285.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.105
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7614 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.65 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.78
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 748 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19.85 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 177 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10990.96 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 100.91 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 928.86 | 893.21 |  |  |  | 932.28 |  | 917.96 | [8 empty] | 941.61 |  |  | 891.45 | [6 empty] | 889.36 |  | 909.73 |  |  |  | 892.40 |  |  | 936.48 |  |  | 914.07 | [9 empty] | 943.56 |  |  | 10990.96
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 100.68 | 103.50 |  |  |  | 101.05 |  | 102.82 | [8 empty] | 102.06 |  |  | 99.85 | [6 empty] | 96.40 |  | 98.61 |  |  |  | 99.96 |  |  | 101.51 |  |  | 102.38 | [9 empty] | 102.28 |  |  | 100.91
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 293838.99 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.91 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.17 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.35 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.17 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.48 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.11 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.9 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | Data not provided
1988 |  |  |  | 7233.82 |  |  | 6664 |  |  |  | 1203 | [10 empty] | 76.34 |  |  |  | 76.34 | [5 empty] | 68.44 |  |  | 75.87 |  |  |  | 14.72 |  | 13.18 | [8 empty] | 10.48 |  |  |  |  | 0.00
1989 |  |  |  | 5357.58 |  |  | 4776 |  |  |  | 1141 | [10 empty] | 53.43 |  |  |  | 53.43 | [5 empty] | 53.60 |  |  | 54.52 |  |  |  | 0.80 |  | 0.43 | [8 empty] | 46.14 |  |  |  |  | 0.00
1990 |  |  |  | 6638.89 |  |  | 5723 |  |  |  | 1141 | [10 empty] | 65.27 |  |  |  | 65.27 | [5 empty] | 66.42 |  |  | 65.33 |  |  |  | 1.27 |  | 0.84 | [8 empty] | 33.89 |  |  |  |  | 0.00
1991 |  |  |  | 8975.67 |  |  | 7949 |  |  |  | 1166 | [10 empty] | 90.74 |  |  |  | 90.74 | [5 empty] | 87.87 |  |  | 90.74 |  |  |  | 8.38 |  | 8.30 | [8 empty] | 0.96 |  |  |  |  | 0.00
1992 |  |  |  | 7168.56 |  |  | 6383 |  |  |  | 1166 | [10 empty] | 72.62 |  |  |  | 72.62 | [5 empty] | 69.99 |  |  | 72.67 |  |  |  | 7.41 |  | 5.81 | [8 empty] | 21.57 |  |  |  |  | 0.00
1993 |  |  |  | 3973.21 |  |  | 3853 |  |  |  | 1166 | [10 empty] | 43.86 |  |  |  | 43.86 | [5 empty] | 38.90 |  |  | 43.98 |  |  |  | 37.99 |  | 26.87 | [8 empty] | 29.26 |  |  |  |  | 0.00
1994 |  |  |  | 4591.90 |  |  | 4151 |  |  |  | 1166 | [10 empty] | 47.28 |  |  |  | 47.28 | [5 empty] | 44.96 |  |  | 47.39 |  |  |  | 1.34 |  | 0.64 | [8 empty] | 52.07 |  |  |  |  | 0.00
1995 |  |  |  | 9112.12 |  |  | 8174 |  |  |  | 1166 | [10 empty] | 93.36 |  |  |  | 93.36 | [5 empty] | 89.21 |  |  | 93.31 |  |  |  | 6.64 |  | 6.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 7481.95 |  |  | 6673 |  |  |  | 1164 | [10 empty] | 75.92 |  |  |  | 75.92 | [5 empty] | 73.18 |  |  | 75.97 |  |  |  | 4.60 |  | 3.66 | [8 empty] | 20.42 |  |  |  |  | 0.00
1997 |  |  |  | 8151.83 |  |  | 7178 |  |  |  | 1160 | [10 empty] | 81.88 |  |  |  | 81.88 | [5 empty] | 80.22 |  |  | 81.94 |  |  |  | 7.35 |  | 6.50 | [8 empty] | 11.62 |  |  |  |  | 0.00
1998 |  |  |  | 10188.94 |  |  | 8684 |  |  |  | 1160 | [10 empty] | 99.14 |  |  |  | 99.14 | [5 empty] | 100.27 |  |  | 99.13 |  |  |  | 0.86 |  | 0.86 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 9124.91 |  |  | 7850 |  |  |  | 1160 | [10 empty] | 89.62 |  |  |  | 89.62 | [5 empty] | 89.80 |  |  | 89.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.38 |  |  |  |  | 0.00
2000 |  |  |  | 10085.68 |  |  | 8506 |  |  |  | 1191 | [10 empty] | 96.90 |  |  |  | 96.90 | [5 empty] | 96.35 |  |  | 96.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.10 |  |  |  |  | 0.00
2001 |  |  |  | 7781.77 |  |  | 6708 |  |  |  | 1241 | [10 empty] | 77.89 |  |  |  | 77.89 | [5 empty] | 71.84 |  |  | 76.58 |  |  |  | 14.30 |  | 12.99 | [8 empty] | 9.12 |  |  |  |  | 0.00
2002 |  |  |  | 9974.81 |  |  | 8196 |  |  |  | 1235 | [10 empty] | 93.56 |  |  |  | 93.56 | [5 empty] | 92.20 |  |  | 93.56 |  |  |  | 6.44 |  | 6.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 8553.20 |  |  | 7217 |  |  |  | 1235 | [10 empty] | 82.36 |  |  |  | 82.36 | [5 empty] | 79.06 |  |  | 82.39 |  |  |  | 2.38 |  | 2.00 | [8 empty] | 15.63 |  |  |  |  | 0.00
2004 |  |  |  | 10227.34 |  |  | 8378 |  |  |  | 1235 | [10 empty] | 95.41 |  |  |  | 95.41 | [5 empty] | 94.28 |  |  | 95.38 |  |  |  | 4.59 |  | 4.59 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 7667.52 |  |  | 6363 |  |  |  | 1235 | [10 empty] | 72.65 |  |  |  | 72.65 | [5 empty] | 70.87 |  |  | 72.63 |  |  |  | 8.93 |  | 7.12 | [8 empty] | 20.23 |  |  |  |  | 0.00
2006 |  |  |  | 10475.37 |  |  | 8521 |  |  |  | 1235 | [10 empty] | 97.27 |  |  |  | 97.27 | [5 empty] | 96.83 |  |  | 97.27 |  |  |  | 2.73 |  | 2.73 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 8058.25 |  |  | 6704 |  |  |  | 1245 | [10 empty] | 76.84 |  |  |  | 76.84 | [5 empty] | 73.89 |  |  | 76.53 |  |  |  | 12.74 |  | 11.22 | [8 empty] | 11.95 |  |  |  |  | 0.00
2008 |  |  |  | 10680.58 |  |  | 8580 |  |  |  | 1245 | [10 empty] | 97.68 |  |  |  | 97.68 | [5 empty] | 97.66 |  |  | 97.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.32 |  |  |  |  | 0.00
2009 |  |  |  | 7345.14 |  |  | 6284 |  |  |  | 1245 | [10 empty] | 71.77 |  |  |  | 71.77 | [5 empty] | 67.35 |  |  | 71.74 |  |  |  | 7.95 |  | 6.20 | [8 empty] | 22.03 |  |  |  |  | 0.00
2010 |  |  |  | 10619.71 |  |  | 8590 |  |  |  | 1240 | [10 empty] | 98.06 |  |  |  | 98.06 | [5 empty] | 97.77 |  |  | 98.06 |  |  |  | 1.94 |  | 1.94 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8569.09 |  |  | 7115 |  |  |  | 1240 | [10 empty] | 81.24 |  |  |  | 81.24 | [5 empty] | 78.89 |  |  | 81.22 |  |  |  | 5.41 |  | 4.64 | [8 empty] | 14.12 |  |  |  |  | 0.00
2012 |  |  |  | 10490.30 |  |  | 8607 |  |  |  | 1240 | [10 empty] | 98.00 |  |  |  | 98.00 | [5 empty] | 96.31 |  |  | 97.98 |  |  |  | 0.94 |  | 0.93 | [8 empty] | 1.07 |  |  |  |  | 0.00
2013 |  |  |  | 8448.62 |  |  | 6981 |  |  |  | 1256 | [10 empty] | 79.88 |  |  |  | 79.88 | [5 empty] | 77.10 |  |  | 79.68 |  |  |  | 1.84 |  | 1.50 | [8 empty] | 18.63 |  |  |  |  | 0.00
2014 |  |  |  | 10455.27 |  |  | 8490 |  |  |  | 1256 | [10 empty] | 96.92 |  |  |  | 96.92 | [5 empty] | 95.03 |  |  | 96.92 |  |  |  | 3.08 |  | 3.08 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 9482.84 |  |  | 7639 |  |  |  | 1256 | [10 empty] | 87.20 |  |  |  | 87.20 | [5 empty] | 86.19 |  |  | 87.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.80 |  |  |  |  | 0.00
2016 |  |  |  | 10420.29 |  |  | 8434 |  |  |  | 1256 | [10 empty] | 96.02 |  |  |  | 96.02 | [5 empty] | 94.45 |  |  | 96.02 |  |  |  | 1.84 |  | 1.80 | [8 empty] | 2.18 |  |  |  |  | 0.00
2017 |  |  |  | 9812.38 |  |  | 8054 |  |  |  | 1256 | [10 empty] | 91.92 |  |  |  | 91.92 | [5 empty] | 89.18 |  |  | 91.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.08 |  |  |  |  | 0.00
2018 |  |  |  | 10718.96 |  |  | 8760 |  |  |  | 1240 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.68 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 9173.10 |  |  | 7763 |  |  |  | 1240 | [10 empty] | 88.64 |  |  |  | 88.64 | [5 empty] | 84.45 |  |  | 88.62 |  |  |  | 3.79 |  | 3.49 | [8 empty] | 7.86 |  |  |  |  | 0.00
2020 |  |  |  | 10990.96 |  |  | 8783 |  |  |  | 1240 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.91 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 359
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 877
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 145
E. |  | Testing of plant systems or components | [35 empty] | 0
L. |  | Human factor related | [39 empty] | 11
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 1
Z. |  | Other | [39 empty] | 5
Subtotal | [37 empty] | 1022 |  |  |  | 376
Total | [22 empty] | 0 | [14 empty] | 1398
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 34
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 50
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 50
32. |  |  | Feedwater and Main Steam System | [34 empty] | 26
33. |  |  | Circulating Water System | [34 empty] | 10
34. |  |  | Miscellaneous Systems | [34 empty] | 85
35. |  |  | All other I&C Systems | [34 empty] | 18
41. |  |  | Main Generator Systems | [34 empty] | 24
42. |  |  | Electrical Power Supply Systems | [34 empty] | 62
Total | [37 empty] | 368

## POINT BEACH-1
2020 Operating Experience
US-266 | [8 empty] | POINT BEACH-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NEXTERA (NextEra Energy Resources, LLC )
Owner | [7 empty] | : | NEXTERA (NextEra Energy Resources, LLC )
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-07-19
Thermal power | [12 empty] | : |  |  | 1800 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1970-11-06
Gross electrical power | [12 empty] | : |  |  | 640 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1970-12-21
Reference unit power (net) | [12 empty] | : |  |  | 591 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 50 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 316
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.422
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 74 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.7 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4828.77 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.15 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.15 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.85 %
Load Factor (LF) | [18 empty] | : | 93.02 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.14 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 603 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 446.50 | 417.80 |  |  |  | 446.68 |  | 430.08 | [8 empty] | 447.86 |  |  | 431.99 | [6 empty] | 441.53 |  | 441.77 |  |  |  | 429.41 |  |  | 43.21 |  |  | 406.35 | [9 empty] | 445.59 |  |  | 4828.76
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 19.07 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.15
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 19.07 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.15
LF [%] |  |  |  |  | 101.55 | 101.57 |  |  |  | 101.59 |  | 101.07 | [8 empty] | 101.85 |  |  | 101.52 | [6 empty] | 100.41 |  | 100.47 |  |  |  | 100.91 |  |  | 9.83 |  |  | 95.49 | [9 empty] | 101.34 |  |  | 93.02
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 19.09 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.14
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 80.93 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.85
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 188639.27 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.36 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.59 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.99 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.31 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.28 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.91 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1970 |  |  |  | Data not provided
1971 |  |  |  | 3446.20 |  |  | 7699 |  |  |  | 524 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 75.08 |  |  | 87.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1972 |  |  |  | 3085.50 |  |  | 6349 |  |  |  | 524 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 67.04 |  |  | 72.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 2742.30 |  |  | 6867 |  |  |  | 497 | [10 empty] | 67.61 |  |  |  | 67.61 | [5 empty] | 62.99 |  |  | 78.39 |  |  |  | 15.83 |  | 12.72 | [8 empty] | 19.67 |  |  |  |  | 0.00
1974 |  |  |  | 3144.30 |  |  | 7136 |  |  |  | 497 | [10 empty] | 81.45 |  |  |  | 81.45 | [5 empty] | 72.22 |  |  | 81.46 |  |  |  | 4.61 |  | 3.93 | [8 empty] | 14.62 |  |  |  |  | 0.00
1975 |  |  |  | 2924.90 |  |  | 6297 |  |  |  | 480 | [10 empty] | 69.52 |  |  |  | 69.52 | [5 empty] | 69.56 |  |  | 71.88 |  |  |  | 17.11 |  | 14.35 | [8 empty] | 16.14 |  |  |  |  | 0.00
1976 |  |  |  | 3392.50 |  |  | 7239 |  |  |  | 492 | [10 empty] | 78.43 |  |  |  | 78.43 | [5 empty] | 78.50 |  |  | 82.41 |  |  |  | 0.08 |  | 0.06 | [8 empty] | 21.52 |  |  |  |  | 0.00
1977 |  |  |  | 3687.10 |  |  | 7733 |  |  |  | 495 | [10 empty] | 85.08 |  |  |  | 85.08 | [5 empty] | 85.03 |  |  | 88.28 |  |  |  | 3.92 |  | 3.47 | [8 empty] | 11.45 |  |  |  |  | 0.00
1978 |  |  |  | 3794.50 |  |  | 7864 |  |  |  | 495 | [10 empty] | 87.50 |  |  |  | 87.50 | [5 empty] | 87.51 |  |  | 89.77 |  |  |  | 2.83 |  | 2.55 | [8 empty] | 9.95 |  |  |  |  | 0.00
1979 |  |  |  | 3059.60 |  |  | 6455 |  |  |  | 495 | [10 empty] | 70.56 |  |  |  | 70.56 | [5 empty] | 70.56 |  |  | 73.69 |  |  |  | 12.40 |  | 9.99 | [8 empty] | 19.45 |  |  |  |  | 0.00
1980 |  |  |  | 2479.30 |  |  | 6739 |  |  |  | 495 | [10 empty] | 76.96 |  |  |  | 91.02 | [5 empty] | 57.02 |  |  | 76.72 |  |  |  | 0.40 |  | 0.37 | [8 empty] | 8.62 |  |  |  |  | 14.06
1981 |  |  |  | 2614.90 |  |  | 6834 |  |  |  | 495 | [10 empty] | 78.30 |  |  |  | 78.30 | [5 empty] | 60.30 |  |  | 78.01 |  |  |  | 0.22 |  | 0.18 | [8 empty] | 21.52 |  |  |  |  | 0.00
1982 |  |  |  | 2701.70 |  |  | 7134 |  |  |  | 495 | [10 empty] | 81.51 |  |  |  | 81.51 | [5 empty] | 62.31 |  |  | 81.44 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 18.34 |  |  |  |  | 0.00
1983 |  |  |  | 2384.90 |  |  | 6498 |  |  |  | 495 | [10 empty] | 74.26 |  |  |  | 74.26 | [5 empty] | 55.00 |  |  | 74.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.74 |  |  |  |  | 0.00
1984 |  |  |  | 3109.21 |  |  | 6379 |  |  |  | 485 | [10 empty] | 72.63 |  |  |  | 72.63 | [5 empty] | 72.98 |  |  | 72.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.37 |  |  |  |  | 0.00
1985 |  |  |  | 3354.18 |  |  | 6917 |  |  |  | 485 | [10 empty] | 78.65 |  |  |  | 78.65 | [5 empty] | 78.95 |  |  | 78.96 |  |  |  | 0.10 |  | 0.08 | [8 empty] | 21.27 |  |  |  |  | 0.00
1986 |  |  |  | 3770.07 |  |  | 7786 |  |  |  | 485 | [10 empty] | 88.73 |  |  |  | 88.73 | [5 empty] | 88.74 |  |  | 88.88 |  |  |  | 0.40 |  | 0.36 | [8 empty] | 10.92 |  |  |  |  | 0.00
1987 |  |  |  | 3567.09 |  |  | 7348 |  |  |  | 485 | [10 empty] | 83.64 |  |  |  | 83.64 | [5 empty] | 83.96 |  |  | 83.88 |  |  |  | 0.28 |  | 0.23 | [8 empty] | 16.12 |  |  |  |  | 0.00
1988 |  |  |  | 3830.95 |  |  | 7787 |  |  |  | 485 | [10 empty] | 88.48 |  |  |  | 88.48 | [5 empty] | 89.92 |  |  | 88.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.52 |  |  |  |  | 0.00
1989 |  |  |  | 3606.22 |  |  | 7706 |  |  |  | 485 | [10 empty] | 87.78 |  |  |  | 87.78 | [5 empty] | 84.88 |  |  | 87.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.22 |  |  |  |  | 0.00
1990 |  |  |  | 3531.73 |  |  | 7362 |  |  |  | 485 | [10 empty] | 83.80 |  |  |  | 83.80 | [5 empty] | 83.13 |  |  | 84.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.20 |  |  |  |  | 0.00
1991 |  |  |  | 3628.73 |  |  | 7524 |  |  |  | 485 | [10 empty] | 85.68 |  |  |  | 85.68 | [5 empty] | 85.41 |  |  | 85.89 |  |  |  | 1.33 |  | 1.16 | [8 empty] | 13.17 |  |  |  |  | 0.00
1992 |  |  |  | 3605.64 |  |  | 7409 |  |  |  | 485 | [10 empty] | 84.10 |  |  |  | 84.10 | [5 empty] | 84.63 |  |  | 84.35 |  |  |  | 0.66 |  | 0.56 | [8 empty] | 15.34 |  |  |  |  | 0.00
1993 |  |  |  | 3804.79 |  |  | 7799 |  |  |  | 485 | [10 empty] | 88.85 |  |  |  | 88.85 | [5 empty] | 89.55 |  |  | 89.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.15 |  |  |  |  | 0.00
1994 |  |  |  | 3905.06 |  |  | 8071 |  |  |  | 485 | [10 empty] | 92.04 |  |  |  | 92.04 | [5 empty] | 91.91 |  |  | 92.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.96 |  |  |  |  | 0.00
1995 |  |  |  | 3792.43 |  |  | 7768 |  |  |  | 485 | [10 empty] | 88.52 |  |  |  | 88.52 | [5 empty] | 89.26 |  |  | 88.68 |  |  |  | 1.28 |  | 1.15 | [8 empty] | 10.33 |  |  |  |  | 0.00
1996 |  |  |  | 4003.33 |  |  | 8173 |  |  |  | 485 | [10 empty] | 92.95 |  |  |  | 92.95 | [5 empty] | 93.97 |  |  | 93.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.05 |  |  |  |  | 0.00
1997 |  |  |  | 853.50 |  |  | 1872 |  |  |  | 485 | [10 empty] | 21.33 |  |  |  | 21.33 | [5 empty] | 20.09 |  |  | 21.37 |  |  |  | 78.67 |  | 78.67 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 2584.22 |  |  | 5489 |  |  |  | 485 | [10 empty] | 62.69 |  |  |  | 62.69 | [5 empty] | 60.83 |  |  | 62.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.31 |  |  |  |  | 0.00
1999 |  |  |  | 3489.33 |  |  | 7070 |  |  |  | 489 | [10 empty] | 80.02 |  |  |  | 80.02 | [5 empty] | 81.43 |  |  | 80.71 |  |  |  | 3.79 |  | 3.15 | [8 empty] | 16.83 |  |  |  |  | 0.00
2000 |  |  |  | 4134.62 |  |  | 8391 |  |  |  | 510 | [10 empty] | 95.59 |  |  |  | 96.10 | [5 empty] | 92.29 |  |  | 95.53 |  |  |  | 3.90 |  | 3.90 | [8 empty] | 0.00 |  |  |  |  | 0.51
2001 |  |  |  | 3702.10 |  |  | 7611 |  |  |  | 510 | [10 empty] | 87.04 |  |  |  | 87.04 | [5 empty] | 82.87 |  |  | 86.88 |  |  |  | 3.35 |  | 3.01 | [8 empty] | 9.95 |  |  |  |  | 0.00
2002 |  |  |  | 3975.79 |  |  | 7964 |  |  |  | 510 | [10 empty] | 91.01 |  |  |  | 91.01 | [5 empty] | 88.99 |  |  | 90.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.99 |  |  |  |  | 0.00
2003 |  |  |  | 4343.00 |  |  | 8538 |  |  |  | 516 | [10 empty] | 97.52 |  |  |  | 97.52 | [5 empty] | 96.18 |  |  | 97.47 |  |  |  | 2.48 |  | 2.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 3631.04 |  |  | 7186 |  |  |  | 516 | [10 empty] | 81.89 |  |  |  | 81.89 | [5 empty] | 80.11 |  |  | 81.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.11 |  |  |  |  | 0.00
2005 |  |  |  | 3641.04 |  |  | 7232 |  |  |  | 512 | [10 empty] | 82.58 |  |  |  | 82.58 | [5 empty] | 81.18 |  |  | 82.56 |  |  |  | 0.76 |  | 0.63 | [8 empty] | 16.79 |  |  |  |  | 0.00
2006 |  |  |  | 4465.63 |  |  | 8760 |  |  |  | 512 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.57 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 3822.30 |  |  | 7582 |  |  |  | 512 | [10 empty] | 86.57 |  |  |  | 86.57 | [5 empty] | 85.22 |  |  | 86.55 |  |  |  | 3.89 |  | 3.51 | [8 empty] | 9.92 |  |  |  |  | 0.00
2008 |  |  |  | 3737.01 |  |  | 7365 |  |  |  | 512 | [10 empty] | 83.87 |  |  |  | 83.87 | [5 empty] | 83.09 |  |  | 83.85 |  |  |  | 5.89 |  | 5.24 | [8 empty] | 10.89 |  |  |  |  | 0.00
2009 |  |  |  | 4385.38 |  |  | 8760 |  |  |  | 512 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.78 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 3956.14 |  |  | 7870 |  |  |  | 512 | [10 empty] | 89.89 |  |  |  | 89.89 | [5 empty] | 88.21 |  |  | 89.84 |  |  |  | 0.83 |  | 0.75 | [8 empty] | 9.36 |  |  |  |  | 0.00
2011 |  |  |  | 3525.04 |  |  | 6954 |  |  |  | 512 | [10 empty] | 79.39 |  |  |  | 79.39 | [5 empty] | 78.59 |  |  | 79.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.61 |  |  |  |  | 0.00
2012 |  |  |  | 5154.43 |  |  | 8737 |  |  |  | 591 | [10 empty] | 99.47 |  |  |  | 99.47 | [5 empty] | 99.29 |  |  | 99.46 |  |  |  | 0.53 |  | 0.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 4707.21 |  |  | 7981 |  |  |  | 591 | [10 empty] | 91.11 |  |  |  | 91.11 | [5 empty] | 90.91 |  |  | 91.10 |  |  |  | 0.40 |  | 0.36 | [8 empty] | 8.53 |  |  |  |  | 0.00
2014 |  |  |  | 4713.10 |  |  | 7956 |  |  |  | 591 | [10 empty] | 90.82 |  |  |  | 90.82 | [5 empty] | 91.04 |  |  | 90.82 |  |  |  | 0.49 |  | 0.45 | [8 empty] | 8.73 |  |  |  |  | 0.00
2015 |  |  |  | 5191.57 |  |  | 8671 |  |  |  | 591 | [10 empty] | 98.99 |  |  |  | 98.99 | [5 empty] | 100.28 |  |  | 98.98 |  |  |  | 1.01 |  | 1.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 4871.11 |  |  | 8196 |  |  |  | 591 | [10 empty] | 93.30 |  |  |  | 93.30 | [5 empty] | 93.83 |  |  | 93.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.70 |  |  |  |  | 0.00
2017 |  |  |  | 4842.86 |  |  | 8158 |  |  |  | 591 | [10 empty] | 93.13 |  |  |  | 93.13 | [5 empty] | 93.54 |  |  | 93.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.87 |  |  |  |  | 0.00
2018 |  |  |  | 5184.30 |  |  | 8675 |  |  |  | 591 | [10 empty] | 99.06 |  |  |  | 99.06 | [5 empty] | 100.14 |  |  | 99.03 |  |  |  | 0.94 |  | 0.94 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 4792.60 |  |  | 8098 |  |  |  | 591 | [10 empty] | 92.45 |  |  |  | 92.45 | [5 empty] | 92.57 |  |  | 92.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.55 |  |  |  |  | 0.00
2020 |  |  |  | 4828.77 |  |  | 8181 |  |  |  | 591 | [10 empty] | 93.15 |  |  |  | 93.15 | [5 empty] | 93.02 |  |  | 93.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.85 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1970 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 123
B. |  | Refuelling without maintenance | [20 empty] | 602 | [14 empty] | 12
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 963
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 45
E. |  | Testing of plant systems or components | [35 empty] | 2
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 25
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 138
Z. |  | Other | [35 empty] | 1 |  |  |  | 3
Subtotal | [22 empty] | 602 | [14 empty] | 1024 |  |  |  | 152 | [11 empty] | 139
Total | [22 empty] | 602 | [14 empty] | 1315
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1970 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 73
31. |  |  | Turbine and auxiliaries | [34 empty] | 15
32. |  |  | Feedwater and Main Steam System | [34 empty] | 21
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 146
41. |  |  | Main Generator Systems | [34 empty] | 8
42. |  |  | Electrical Power Supply Systems | [34 empty] | 13
Total | [37 empty] | 289
Highlights (2020)
Refueling Outage 39

## POINT BEACH-2
2020 Operating Experience
US-301 | [8 empty] | POINT BEACH-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NEXTERA (NextEra Energy Resources, LLC )
Owner | [7 empty] | : | NEXTERA (NextEra Energy Resources, LLC )
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-07-25
Thermal power | [12 empty] | : |  |  | 1800 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1972-08-02
Gross electrical power | [12 empty] | : |  |  | 640 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1972-10-01
Reference unit power (net) | [12 empty] | : |  |  | 591 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 316
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.422
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 74 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.44 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.55
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.7 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4942.57 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.87 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.87 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.13 %
Load Factor (LF) | [18 empty] | : | 95.21 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.85 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 540 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 450.08 | 420.65 |  |  |  | 174.97 |  | 346.62 | [8 empty] | 451.70 |  |  | 436.13 | [6 empty] | 445.69 |  | 445.70 |  |  |  | 434.48 |  |  | 447.30 |  |  | 438.07 | [9 empty] | 451.17 |  |  | 4942.57
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.94 |  | 85.17 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.87
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.94 |  | 85.17 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.87
LF [%] |  |  |  |  | 102.36 | 102.27 |  |  |  | 39.79 |  | 81.46 | [8 empty] | 102.73 |  |  | 102.49 | [6 empty] | 101.36 |  | 101.36 |  |  |  | 102.11 |  |  | 101.73 |  |  | 102.95 | [9 empty] | 102.61 |  |  | 95.21
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.80 |  | 85.14 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.85
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 58.06 |  | 14.83 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.13
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 137102 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.71 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.74 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.51 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.75 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.17 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.43 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1972 |  |  |  | 225.70 |  |  | 2987 |  |  |  | 288 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 84.78 |  |  | 81.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 2991.00 |  |  | 8192 |  |  |  | 497 | [10 empty] | 80.16 |  |  |  | 80.16 | [5 empty] | 68.70 |  |  | 93.52 |  |  |  | 16.63 |  | 15.99 | [8 empty] | 3.85 |  |  |  |  | 0.00
1974 |  |  |  | 3179.30 |  |  | 7100 |  |  |  | 497 | [10 empty] | 81.05 |  |  |  | 81.05 | [5 empty] | 73.02 |  |  | 81.05 |  |  |  | 1.22 |  | 1.00 | [8 empty] | 17.95 |  |  |  |  | 0.00
1975 |  |  |  | 3741.40 |  |  | 8224 |  |  |  | 485 | [10 empty] | 87.92 |  |  |  | 87.92 | [5 empty] | 88.06 |  |  | 93.88 |  |  |  | 3.19 |  | 2.89 | [8 empty] | 9.19 |  |  |  |  | 0.00
1976 |  |  |  | 3749.20 |  |  | 7959 |  |  |  | 491 | [10 empty] | 86.80 |  |  |  | 86.80 | [5 empty] | 86.93 |  |  | 90.61 |  |  |  | 0.78 |  | 0.68 | [8 empty] | 12.52 |  |  |  |  | 0.00
1977 |  |  |  | 3622.30 |  |  | 7496 |  |  |  | 495 | [10 empty] | 83.51 |  |  |  | 83.51 | [5 empty] | 83.54 |  |  | 85.57 |  |  |  | 0.54 |  | 0.45 | [8 empty] | 16.05 |  |  |  |  | 0.00
1978 |  |  |  | 3858.90 |  |  | 8039 |  |  |  | 495 | [10 empty] | 88.99 |  |  |  | 88.99 | [5 empty] | 88.99 |  |  | 91.77 |  |  |  | 0.64 |  | 0.58 | [8 empty] | 10.43 |  |  |  |  | 0.00
1979 |  |  |  | 3707.50 |  |  | 7728 |  |  |  | 495 | [10 empty] | 85.50 |  |  |  | 85.50 | [5 empty] | 85.50 |  |  | 88.22 |  |  |  | 0.52 |  | 0.44 | [8 empty] | 14.06 |  |  |  |  | 0.00
1980 |  |  |  | 3587.90 |  |  | 7569 |  |  |  | 495 | [10 empty] | 88.03 |  |  |  | 88.03 | [5 empty] | 82.52 |  |  | 86.17 |  |  |  | 3.86 |  | 3.54 | [8 empty] | 8.44 |  |  |  |  | 0.00
1981 |  |  |  | 3720.30 |  |  | 7757 |  |  |  | 495 | [10 empty] | 89.89 |  |  |  | 89.89 | [5 empty] | 85.80 |  |  | 88.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.11 |  |  |  |  | 0.00
1982 |  |  |  | 3605.40 |  |  | 7595 |  |  |  | 495 | [10 empty] | 88.22 |  |  |  | 88.22 | [5 empty] | 83.15 |  |  | 86.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.78 |  |  |  |  | 0.00
1983 |  |  |  | 3016.30 |  |  | 6245 |  |  |  | 495 | [10 empty] | 74.47 |  |  |  | 74.47 | [5 empty] | 69.56 |  |  | 71.29 |  |  |  | 0.49 |  | 0.37 | [8 empty] | 25.16 |  |  |  |  | 0.00
1984 |  |  |  | 3512.37 |  |  | 7405 |  |  |  | 495 | [10 empty] | 86.04 |  |  |  | 86.04 | [5 empty] | 80.78 |  |  | 84.30 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 13.91 |  |  |  |  | 0.00
1985 |  |  |  | 3603.08 |  |  | 7491 |  |  |  | 485 | [10 empty] | 86.84 |  |  |  | 86.84 | [5 empty] | 84.81 |  |  | 85.51 |  |  |  | 0.57 |  | 0.50 | [8 empty] | 12.66 |  |  |  |  | 0.00
1986 |  |  |  | 3417.55 |  |  | 7186 |  |  |  | 485 | [10 empty] | 82.12 |  |  |  | 82.12 | [5 empty] | 80.44 |  |  | 82.03 |  |  |  | 0.30 |  | 0.25 | [8 empty] | 17.64 |  |  |  |  | 0.00
1987 |  |  |  | 3606.15 |  |  | 7478 |  |  |  | 485 | [10 empty] | 85.50 |  |  |  | 85.90 | [5 empty] | 84.88 |  |  | 85.37 |  |  |  | 0.58 |  | 0.50 | [8 empty] | 13.60 |  |  |  |  | 0.39
1988 |  |  |  | 3718.68 |  |  | 7626 |  |  |  | 485 | [10 empty] | 88.02 |  |  |  | 88.02 | [5 empty] | 87.29 |  |  | 86.82 |  |  |  | 0.28 |  | 0.24 | [8 empty] | 11.74 |  |  |  |  | 0.00
1989 |  |  |  | 3485.10 |  |  | 7107 |  |  |  | 485 | [10 empty] | 82.87 |  |  |  | 82.87 | [5 empty] | 82.03 |  |  | 81.13 |  |  |  | 1.57 |  | 1.32 | [8 empty] | 15.81 |  |  |  |  | 0.00
1990 |  |  |  | 3793.46 |  |  | 7713 |  |  |  | 485 | [10 empty] | 89.14 |  |  |  | 89.14 | [5 empty] | 89.29 |  |  | 88.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.86 |  |  |  |  | 0.00
1991 |  |  |  | 3689.18 |  |  | 7569 |  |  |  | 485 | [10 empty] | 87.60 |  |  |  | 87.60 | [5 empty] | 86.83 |  |  | 86.40 |  |  |  | 0.61 |  | 0.54 | [8 empty] | 11.86 |  |  |  |  | 0.00
1992 |  |  |  | 3668.19 |  |  | 7492 |  |  |  | 485 | [10 empty] | 86.63 |  |  |  | 86.63 | [5 empty] | 86.10 |  |  | 85.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.37 |  |  |  |  | 0.00
1993 |  |  |  | 3844.50 |  |  | 7883 |  |  |  | 485 | [10 empty] | 90.91 |  |  |  | 90.91 | [5 empty] | 90.49 |  |  | 89.99 |  |  |  | 0.24 |  | 0.22 | [8 empty] | 8.87 |  |  |  |  | 0.00
1994 |  |  |  | 3752.30 |  |  | 7827 |  |  |  | 485 | [10 empty] | 90.34 |  |  |  | 90.34 | [5 empty] | 88.32 |  |  | 89.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.66 |  |  |  |  | 0.00
1995 |  |  |  | 3385.96 |  |  | 7158 |  |  |  | 485 | [10 empty] | 83.41 |  |  |  | 83.41 | [5 empty] | 79.70 |  |  | 81.71 |  |  |  | 0.17 |  | 0.15 | [8 empty] | 16.44 |  |  |  |  | 0.00
1996 |  |  |  | 2950.35 |  |  | 6653 |  |  |  | 485 | [10 empty] | 77.95 |  |  |  | 77.95 | [5 empty] | 69.25 |  |  | 75.74 |  |  |  | 0.25 |  | 0.20 | [8 empty] | 21.85 |  |  |  |  | 0.00
1997 |  |  |  | 825.49 |  |  | 1788 |  |  |  | 485 | [10 empty] | 21.45 |  |  |  | 21.45 | [5 empty] | 19.43 |  |  | 20.41 |  |  |  | 43.40 |  | 16.44 | [8 empty] | 62.11 |  |  |  |  | 0.00
1998 |  |  |  | 3123.75 |  |  | 6609 |  |  |  | 485 | [10 empty] | 75.46 |  |  |  | 75.46 | [5 empty] | 73.52 |  |  | 75.45 |  |  |  | 18.52 |  | 17.15 | [8 empty] | 7.40 |  |  |  |  | 0.00
1999 |  |  |  | 3578.50 |  |  | 7195 |  |  |  | 498 | [10 empty] | 82.57 |  |  |  | 82.57 | [5 empty] | 81.93 |  |  | 82.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.43 |  |  |  |  | 0.00
2000 |  |  |  | 3527.45 |  |  | 7094 |  |  |  | 512 | [10 empty] | 80.89 |  |  |  | 80.89 | [5 empty] | 78.43 |  |  | 80.76 |  |  |  | 0.81 |  | 0.66 | [8 empty] | 18.45 |  |  |  |  | 0.00
2001 |  |  |  | 4342.97 |  |  | 8631 |  |  |  | 512 | [10 empty] | 98.55 |  |  |  | 98.55 | [5 empty] | 96.83 |  |  | 98.53 |  |  |  | 1.45 |  | 1.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 4004.30 |  |  | 7934 |  |  |  | 512 | [10 empty] | 90.69 |  |  |  | 90.69 | [5 empty] | 89.28 |  |  | 90.57 |  |  |  | 0.89 |  | 0.81 | [8 empty] | 8.50 |  |  |  |  | 0.00
2003 |  |  |  | 3713.28 |  |  | 7469 |  |  |  | 518 | [10 empty] | 85.59 |  |  |  | 85.59 | [5 empty] | 81.91 |  |  | 85.26 |  |  |  | 2.00 |  | 1.75 | [8 empty] | 12.66 |  |  |  |  | 0.00
2004 |  |  |  | 4384.88 |  |  | 8559 |  |  |  | 518 | [10 empty] | 97.47 |  |  |  | 97.47 | [5 empty] | 96.37 |  |  | 97.44 |  |  |  | 2.53 |  | 2.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 3232.63 |  |  | 6355 |  |  |  | 514 | [10 empty] | 72.57 |  |  |  | 72.57 | [5 empty] | 71.79 |  |  | 72.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.43 |  |  |  |  | 0.00
2006 |  |  |  | 4094.78 |  |  | 7972 |  |  |  | 514 | [10 empty] | 91.03 |  |  |  | 91.03 | [5 empty] | 90.94 |  |  | 91.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.97 |  |  |  |  | 0.00
2007 |  |  |  | 4462.21 |  |  | 8760 |  |  |  | 514 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.10 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 4075.91 |  |  | 7904 |  |  |  | 514 | [10 empty] | 89.99 |  |  |  | 89.99 | [5 empty] | 90.28 |  |  | 89.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.01 |  |  |  |  | 0.00
2009 |  |  |  | 3782.45 |  |  | 7501 |  |  |  | 516 | [10 empty] | 85.69 |  |  |  | 85.69 | [5 empty] | 83.68 |  |  | 85.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.31 |  |  |  |  | 0.00
2010 |  |  |  | 4336.29 |  |  | 8495 |  |  |  | 515 | [10 empty] | 96.99 |  |  |  | 96.99 | [5 empty] | 96.12 |  |  | 96.97 |  |  |  | 3.01 |  | 3.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 3450.08 |  |  | 6098 |  |  |  | 586 | [10 empty] | 71.91 |  |  |  | 71.91 | [5 empty] | 70.75 |  |  | 69.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.09 |  |  |  |  | 0.00
2012 |  |  |  | 4633.79 |  |  | 7935 |  |  |  | 591 | [10 empty] | 90.36 |  |  |  | 90.36 | [5 empty] | 89.26 |  |  | 90.33 |  |  |  | 1.68 |  | 1.55 | [8 empty] | 8.09 |  |  |  |  | 0.00
2013 |  |  |  | 5237.69 |  |  | 8760 |  |  |  | 591 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.16 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 4742.28 |  |  | 7962 |  |  |  | 591 | [10 empty] | 90.89 |  |  |  | 90.89 | [5 empty] | 91.60 |  |  | 90.89 |  |  |  | 0.36 |  | 0.33 | [8 empty] | 8.78 |  |  |  |  | 0.00
2015 |  |  |  | 4819.90 |  |  | 8095 |  |  |  | 591 | [10 empty] | 92.40 |  |  |  | 92.40 | [5 empty] | 93.10 |  |  | 92.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.60 |  |  |  |  | 0.00
2016 |  |  |  | 5282.17 |  |  | 8784 |  |  |  | 591 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.75 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 4810.70 |  |  | 8113 |  |  |  | 591 | [10 empty] | 92.61 |  |  |  | 92.61 | [5 empty] | 92.92 |  |  | 92.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.39 |  |  |  |  | 0.00
2018 |  |  |  | 4948.38 |  |  | 8267 |  |  |  | 591 | [10 empty] | 94.49 |  |  |  | 94.49 | [5 empty] | 95.58 |  |  | 94.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.51 |  |  |  |  | 0.00
2019 |  |  |  | 5239.90 |  |  | 8760 |  |  |  | 591 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.21 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 4942.57 |  |  | 8244 |  |  |  | 591 | [10 empty] | 93.87 |  |  |  | 93.87 | [5 empty] | 95.21 |  |  | 93.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.13 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1972 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 89
B. |  | Refuelling without maintenance | [20 empty] | 539 | [14 empty] | 21
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 997
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 35
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 19
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 3
L. |  | Human factor related | [39 empty] | 5
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 14
Subtotal | [22 empty] | 539 | [14 empty] | 1056 |  |  |  | 130 | [11 empty] | 1
Total | [22 empty] | 539 | [14 empty] | 1187
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1972 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 4
12. |  |  | Reactor I&C Systems | [34 empty] | 43
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 27
16. |  |  | Steam generation systems | [34 empty] | 13
31. |  |  | Turbine and auxiliaries | [34 empty] | 9
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [37 empty] | 119
Highlights (2020)
Refueling Outage 37 (U2R37)

## PRAIRIE ISALND-1
2020 Operating Experience
US-282 | [8 empty] | PRAIRIE ISLAND-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NSP (Northern States Power Co. (subsidiary of Xcel Energy))
Owner | [7 empty] | : | XCEL (Xcel Energy)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-06-25
Thermal power | [12 empty] | : |  |  | 1677 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-12-04
Gross electrical power | [12 empty] | : |  |  | 566 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-12-16
Reference unit power (net) | [12 empty] | : |  |  | 522 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.291
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 51000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.45 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.06
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4337.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.21 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.02 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.12 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.02 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.86 %
Load Factor (LF) | [18 empty] | : | 94.6 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.12 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 692 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 414.86 | 388.29 |  |  |  | 407.86 |  | 387.48 | [8 empty] | 394.66 |  |  | 379.48 | [6 empty] | 393.34 |  | 328.61 |  |  |  | 206.32 |  |  | 221.78 |  |  | 401.77 | [9 empty] | 413.14 |  |  | 4337.58
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 73.62 |  |  |  | 59.86 |  |  | 59.18 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.02
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 73.62 |  |  |  | 59.86 |  |  | 59.18 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.02
LF [%] |  |  |  |  | 106.82 | 106.88 |  |  |  | 105.02 |  | 103.10 | [8 empty] | 101.62 |  |  | 100.97 | [6 empty] | 101.28 |  | 84.61 |  |  |  | 54.90 |  |  | 57.11 |  |  | 106.90 | [9 empty] | 106.38 |  |  | 94.60
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 86.83 |  |  |  | 59.86 |  |  | 59.14 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.12
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 15.20 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.21
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 13.19 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.12
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 13.19 |  |  |  | 40.14 |  |  | 40.82 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.86
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 188189.77 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.22 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.63 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.14 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.82 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.75 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 7.20 |  |  | 312 |  |  |  | 514 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1974 |  |  |  | 1452.20 |  |  | 3848 |  |  |  | 520 | [10 empty] | 43.95 |  |  |  | 43.95 | [5 empty] | 31.88 |  |  | 43.93 |  |  |  | 51.66 |  | 46.97 | [8 empty] | 9.08 |  |  |  |  | 0.00
1975 |  |  |  | 3694.20 |  |  | 7560 |  |  |  | 520 | [10 empty] | 81.18 |  |  |  | 81.18 | [5 empty] | 81.10 |  |  | 86.30 |  |  |  | 6.61 |  | 5.75 | [8 empty] | 13.07 |  |  |  |  | 0.00
1976 |  |  |  | 3268.70 |  |  | 6801 |  |  |  | 520 | [10 empty] | 71.55 |  |  |  | 71.55 | [5 empty] | 71.56 |  |  | 77.42 |  |  |  | 11.20 |  | 9.03 | [8 empty] | 19.43 |  |  |  |  | 0.00
1977 |  |  |  | 3714.50 |  |  | 7453 |  |  |  | 511 | [10 empty] | 82.93 |  |  |  | 82.93 | [5 empty] | 82.98 |  |  | 85.08 |  |  |  | 0.92 |  | 0.77 | [8 empty] | 16.29 |  |  |  |  | 0.00
1978 |  |  |  | 3810.70 |  |  | 8012 |  |  |  | 507 | [10 empty] | 85.86 |  |  |  | 85.86 | [5 empty] | 85.80 |  |  | 91.46 |  |  |  | 4.44 |  | 3.99 | [8 empty] | 10.14 |  |  |  |  | 0.00
1979 |  |  |  | 2910.90 |  |  | 6402 |  |  |  | 503 | [10 empty] | 65.84 |  |  |  | 65.84 | [5 empty] | 66.06 |  |  | 73.08 |  |  |  | 24.15 |  | 20.96 | [8 empty] | 13.20 |  |  |  |  | 0.00
1980 |  |  |  | 3105.70 |  |  | 6863 |  |  |  | 503 | [10 empty] | 77.80 |  |  |  | 77.80 | [5 empty] | 70.29 |  |  | 78.13 |  |  |  | 2.56 |  | 2.05 | [8 empty] | 20.15 |  |  |  |  | 0.00
1981 |  |  |  | 3838.60 |  |  | 7803 |  |  |  | 503 | [10 empty] | 88.87 |  |  |  | 88.87 | [5 empty] | 87.12 |  |  | 89.08 |  |  |  | 0.27 |  | 0.24 | [8 empty] | 10.88 |  |  |  |  | 0.00
1982 |  |  |  | 3918.00 |  |  | 7960 |  |  |  | 503 | [10 empty] | 90.90 |  |  |  | 90.90 | [5 empty] | 88.92 |  |  | 90.87 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 8.92 |  |  |  |  | 0.00
1983 |  |  |  | 3888.90 |  |  | 7621 |  |  |  | 503 | [10 empty] | 87.20 |  |  |  | 87.20 | [5 empty] | 88.26 |  |  | 87.00 |  |  |  | 4.99 |  | 4.58 | [8 empty] | 8.22 |  |  |  |  | 0.00
1984 |  |  |  | 4159.39 |  |  | 8285 |  |  |  | 503 | [10 empty] | 94.34 |  |  |  | 94.34 | [5 empty] | 94.14 |  |  | 94.32 |  |  |  | 4.95 |  | 4.91 | [8 empty] | 0.75 |  |  |  |  | 0.00
1985 |  |  |  | 3678.45 |  |  | 7333 |  |  |  | 503 | [10 empty] | 83.39 |  |  |  | 83.39 | [5 empty] | 83.48 |  |  | 83.71 |  |  |  | 0.60 |  | 0.51 | [8 empty] | 16.11 |  |  |  |  | 0.00
1986 |  |  |  | 3819.56 |  |  | 7870 |  |  |  | 503 | [10 empty] | 89.64 |  |  |  | 89.64 | [5 empty] | 86.68 |  |  | 89.84 |  |  |  | 0.31 |  | 0.28 | [8 empty] | 10.08 |  |  |  |  | 0.00
1987 |  |  |  | 3590.27 |  |  | 7232 |  |  |  | 503 | [10 empty] | 82.22 |  |  |  | 82.22 | [5 empty] | 81.48 |  |  | 82.56 |  |  |  | 4.08 |  | 3.50 | [8 empty] | 14.29 |  |  |  |  | 0.00
1988 |  |  |  | 3823.39 |  |  | 7800 |  |  |  | 503 | [10 empty] | 89.26 |  |  |  | 89.26 | [5 empty] | 86.53 |  |  | 88.80 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 10.65 |  |  |  |  | 0.00
1989 |  |  |  | 4392.28 |  |  | 8737 |  |  |  | 503 | [10 empty] | 99.75 |  |  |  | 99.75 | [5 empty] | 99.68 |  |  | 99.74 |  |  |  | 0.25 |  | 0.25 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 3829.68 |  |  | 7764 |  |  |  | 503 | [10 empty] | 81.66 |  |  |  | 81.66 | [5 empty] | 86.91 |  |  | 88.63 |  |  |  | 8.30 |  | 7.39 | [8 empty] | 10.94 |  |  |  |  | 0.00
1991 |  |  |  | 3987.08 |  |  | 7943 |  |  |  | 505 | [10 empty] | 90.51 |  |  |  | 90.51 | [5 empty] | 90.09 |  |  | 90.67 |  |  |  | 1.27 |  | 1.16 | [8 empty] | 8.33 |  |  |  |  | 0.00
1992 |  |  |  | 3497.78 |  |  | 6844 |  |  |  | 503 | [10 empty] | 77.44 |  |  |  | 77.44 | [5 empty] | 79.16 |  |  | 77.91 |  |  |  | 4.38 |  | 3.55 | [8 empty] | 19.01 |  |  |  |  | 0.00
1993 |  |  |  | 4377.99 |  |  | 8480 |  |  |  | 505 | [10 empty] | 96.83 |  |  |  | 96.83 | [5 empty] | 98.86 |  |  | 96.80 |  |  |  | 0.18 |  | 0.17 | [8 empty] | 3.00 |  |  |  |  | 0.00
1994 |  |  |  | 3718.20 |  |  | 7258 |  |  |  | 513 | [10 empty] | 82.84 |  |  |  | 82.84 | [5 empty] | 82.74 |  |  | 82.85 |  |  |  | 2.23 |  | 1.89 | [8 empty] | 15.27 |  |  |  |  | 0.00
1995 |  |  |  | 4519.04 |  |  | 8752 |  |  |  | 513 | [10 empty] | 99.91 |  |  |  | 99.91 | [5 empty] | 100.56 |  |  | 99.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.09 |  |  |  |  | 0.00
1996 |  |  |  | 3741.65 |  |  | 7327 |  |  |  | 513 | [10 empty] | 92.18 |  |  |  | 92.86 | [5 empty] | 83.03 |  |  | 83.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.14 |  |  |  |  | 0.68
1997 |  |  |  | 3522.80 |  |  | 6965 |  |  |  | 513 | [10 empty] | 79.53 |  |  |  | 79.53 | [5 empty] | 78.39 |  |  | 79.51 |  |  |  | 4.83 |  | 4.04 | [8 empty] | 16.43 |  |  |  |  | 0.00
1998 |  |  |  | 4209.16 |  |  | 7948 |  |  |  | 514 | [10 empty] | 90.78 |  |  |  | 90.78 | [5 empty] | 93.46 |  |  | 90.73 |  |  |  | 8.98 |  | 8.96 | [8 empty] | 0.27 |  |  |  |  | 0.00
1999 |  |  |  | 4068.78 |  |  | 7643 |  |  |  | 522 | [10 empty] | 87.17 |  |  |  | 87.17 | [5 empty] | 88.98 |  |  | 87.25 |  |  |  | 2.02 |  | 1.80 | [8 empty] | 11.02 |  |  |  |  | 0.00
2000 |  |  |  | 4536.51 |  |  | 8499 |  |  |  | 522 | [10 empty] | 96.74 |  |  |  | 96.74 | [5 empty] | 98.94 |  |  | 96.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.26 |  |  |  |  | 0.00
2001 |  |  |  | 3641.74 |  |  | 6890 |  |  |  | 522 | [10 empty] | 78.77 |  |  |  | 78.77 | [5 empty] | 79.64 |  |  | 78.65 |  |  |  | 12.28 |  | 11.02 | [8 empty] | 10.21 |  |  |  |  | 0.00
2002 |  |  |  | 4373.23 |  |  | 8268 |  |  |  | 522 | [10 empty] | 94.36 |  |  |  | 94.36 | [5 empty] | 95.64 |  |  | 94.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.64 |  |  |  |  | 0.00
2003 |  |  |  | 4596.35 |  |  | 8619 |  |  |  | 522 | [10 empty] | 98.38 |  |  |  | 98.38 | [5 empty] | 100.96 |  |  | 98.39 |  |  |  | 1.62 |  | 1.62 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 3602.14 |  |  | 7017 |  |  |  | 522 | [10 empty] | 79.89 |  |  |  | 79.89 | [5 empty] | 78.56 |  |  | 79.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.11 |  |  |  |  | 0.00
2005 |  |  |  | 4518.40 |  |  | 8465 |  |  |  | 522 | [10 empty] | 96.66 |  |  |  | 96.66 | [5 empty] | 98.80 |  |  | 96.62 |  |  |  | 0.44 |  | 0.43 | [8 empty] | 2.91 |  |  |  |  | 0.00
2006 |  |  |  | 4103.24 |  |  | 7785 |  |  |  | 523 | [10 empty] | 88.88 |  |  |  | 88.88 | [5 empty] | 89.56 |  |  | 88.87 |  |  |  | 0.57 |  | 0.51 | [8 empty] | 10.62 |  |  |  |  | 0.00
2007 |  |  |  | 4457.09 |  |  | 8472 |  |  |  | 551 | [10 empty] | 96.72 |  |  |  | 96.72 | [5 empty] | 92.34 |  |  | 96.71 |  |  |  | 0.98 |  | 0.96 | [8 empty] | 2.32 |  |  |  |  | 0.00
2008 |  |  |  | 4059.45 |  |  | 7780 |  |  |  | 551 | [10 empty] | 88.58 |  |  |  | 88.58 | [5 empty] | 83.87 |  |  | 88.57 |  |  |  | 0.83 |  | 0.74 | [8 empty] | 10.67 |  |  |  |  | 0.00
2009 |  |  |  | 3600.15 |  |  | 6923 |  |  |  | 551 | [10 empty] | 79.04 |  |  |  | 79.04 | [5 empty] | 74.59 |  |  | 79.03 |  |  |  | 1.20 |  | 0.96 | [8 empty] | 20.00 |  |  |  |  | 0.00
2010 |  |  |  | 4654.86 |  |  | 8760 |  |  |  | 560 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 96.04 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 4128.39 |  |  | 7717 |  |  |  | 521 | [10 empty] | 87.69 |  |  |  | 87.69 | [5 empty] | 87.22 |  |  | 88.09 |  |  |  | 0.39 |  | 0.34 | [8 empty] | 11.96 |  |  |  |  | 0.00
2012 |  |  |  | 3705.98 |  |  | 6961 |  |  |  | 522 | [10 empty] | 79.26 |  |  |  | 79.26 | [5 empty] | 80.82 |  |  | 79.25 |  |  |  | 1.99 |  | 1.61 | [8 empty] | 19.13 |  |  |  |  | 0.00
2013 |  |  |  | 4654.69 |  |  | 8732 |  |  |  | 522 | [10 empty] | 99.68 |  |  |  | 99.68 | [5 empty] | 101.78 |  |  | 99.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.32 |  |  |  |  | 0.00
2014 |  |  |  | 3812.46 |  |  | 7264 |  |  |  | 522 | [10 empty] | 82.92 |  |  |  | 82.92 | [5 empty] | 83.37 |  |  | 82.92 |  |  |  | 5.28 |  | 4.62 | [8 empty] | 12.45 |  |  |  |  | 0.00
2015 |  |  |  | 3991.22 |  |  | 7539 |  |  |  | 522 | [10 empty] | 86.06 |  |  |  | 86.06 | [5 empty] | 87.28 |  |  | 86.06 |  |  |  | 13.94 |  | 13.94 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 4207.70 |  |  | 7903 |  |  |  | 522 | [10 empty] | 89.97 |  |  |  | 89.97 | [5 empty] | 91.77 |  |  | 89.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.03 |  |  |  |  | 0.00
2017 |  |  |  | 4565.00 |  |  | 8689 |  |  |  | 522 | [10 empty] | 99.18 |  |  |  | 99.18 | [5 empty] | 99.83 |  |  | 99.19 |  |  |  | 0.54 |  | 0.54 | [8 empty] | 0.28 |  |  |  |  | 0.00
2018 |  |  |  | 4190.47 |  |  | 7916 |  |  |  | 522 | [10 empty] | 90.36 |  |  |  | 90.36 | [5 empty] | 91.64 |  |  | 90.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.64 |  |  |  |  | 0.00
2019 |  |  |  | 4772.56 |  |  | 8760 |  |  |  | 522 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 104.37 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 4337.58 |  |  | 8092 |  |  |  | 522 | [10 empty] | 91.02 |  |  |  | 91.02 | [5 empty] | 94.60 |  |  | 92.12 |  |  |  | 1.21 |  | 1.12 | [8 empty] | 7.86 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1973 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 267
B. |  | Refuelling without maintenance | [20 empty] | 593 | [14 empty] | 13
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 683
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 68
E. |  | Testing of plant systems or components | [35 empty] | 5 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 3
L. |  | Human factor related | [39 empty] | 1
P. |  | Fire | [39 empty] | 20
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 0
Z. |  | Other | [24 empty] | 98 | [14 empty] | 2 | [11 empty] | 1
Subtotal | [22 empty] | 593 |  |  |  | 98 | [10 empty] | 770 |  |  |  | 294 | [11 empty] | 1
Total | [22 empty] | 691 | [14 empty] | 1065
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1973 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 12
12. |  |  | Reactor I&C Systems | [34 empty] | 42
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 31
16. |  |  | Steam generation systems | [34 empty] | 30
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 97
32. |  |  | Feedwater and Main Steam System | [34 empty] | 29
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 16
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [37 empty] | 290
Highlights (2020)
Automatic reactor scram on a spurious Power Range Negative Rate trip signal during surveillance testing of PRNIs.

## PRAIRIE ISALND-2
2020 Operating Experience
US-306 | [8 empty] | PRAIRIE ISLAND-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NSP (Northern States Power Co. (subsidiary of Xcel Energy))
Owner | [7 empty] | : | XCEL (Xcel Energy)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1969-06-25
Thermal power | [12 empty] | : |  |  | 1677 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-12-21
Gross electrical power | [12 empty] | : |  |  | 560 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-12-21
Reference unit power (net) | [12 empty] | : |  |  | 519 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.291
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 51000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.45 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.06
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 4746.4 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 104.11 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 415.77 | 388.16 |  |  |  | 412.98 |  | 392.20 | [8 empty] | 392.84 |  |  | 372.00 | [6 empty] | 393.31 |  | 396.86 |  |  |  | 359.77 |  |  | 408.72 |  |  | 398.96 | [9 empty] | 414.82 |  |  | 4746.40
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 107.68 | 107.46 |  |  |  | 106.95 |  | 104.96 | [8 empty] | 101.74 |  |  | 99.55 | [6 empty] | 101.86 |  | 102.78 |  |  |  | 96.28 |  |  | 105.85 |  |  | 106.77 | [9 empty] | 107.43 |  |  | 104.11
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 185005.28 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.31 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.23 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.02 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.25 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.32 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.8 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 7.40 |  |  | 104 |  |  |  | 513 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1975 |  |  |  | 3176.20 |  |  | 7035 |  |  |  | 520 | [10 empty] | 69.91 |  |  |  | 69.91 | [5 empty] | 69.92 |  |  | 80.53 |  |  |  | 22.79 |  | 20.63 | [8 empty] | 9.46 |  |  |  |  | 0.00
1976 |  |  |  | 2660.60 |  |  | 6657 |  |  |  | 520 | [10 empty] | 58.24 |  |  |  | 58.24 | [5 empty] | 58.25 |  |  | 75.79 |  |  |  | 16.48 |  | 11.50 | [8 empty] | 30.27 |  |  |  |  | 0.00
1977 |  |  |  | 3882.30 |  |  | 7807 |  |  |  | 511 | [10 empty] | 86.68 |  |  |  | 86.68 | [5 empty] | 86.73 |  |  | 89.12 |  |  |  | 1.79 |  | 1.58 | [8 empty] | 11.74 |  |  |  |  | 0.00
1978 |  |  |  | 3924.40 |  |  | 8126 |  |  |  | 507 | [10 empty] | 88.16 |  |  |  | 88.16 | [5 empty] | 88.36 |  |  | 92.76 |  |  |  | 2.09 |  | 1.88 | [8 empty] | 9.96 |  |  |  |  | 0.00
1979 |  |  |  | 4193.00 |  |  | 8661 |  |  |  | 500 | [10 empty] | 94.61 |  |  |  | 94.61 | [5 empty] | 95.73 |  |  | 98.87 |  |  |  | 3.46 |  | 3.39 | [8 empty] | 2.00 |  |  |  |  | 0.00
1980 |  |  |  | 3468.70 |  |  | 7167 |  |  |  | 500 | [10 empty] | 81.41 |  |  |  | 81.54 | [5 empty] | 78.98 |  |  | 81.59 |  |  |  | 0.24 |  | 0.20 | [8 empty] | 18.26 |  |  |  |  | 0.13
1981 |  |  |  | 3092.90 |  |  | 6292 |  |  |  | 500 | [10 empty] | 71.40 |  |  |  | 71.40 | [5 empty] | 70.61 |  |  | 71.83 |  |  |  | 15.28 |  | 12.88 | [8 empty] | 15.72 |  |  |  |  | 0.00
1982 |  |  |  | 3857.70 |  |  | 7844 |  |  |  | 500 | [10 empty] | 89.85 |  |  |  | 89.99 | [5 empty] | 88.08 |  |  | 89.54 |  |  |  | 0.26 |  | 0.24 | [8 empty] | 9.77 |  |  |  |  | 0.15
1983 |  |  |  | 3716.30 |  |  | 7574 |  |  |  | 500 | [10 empty] | 86.51 |  |  |  | 86.51 | [5 empty] | 84.85 |  |  | 86.46 |  |  |  | 2.88 |  | 2.56 | [8 empty] | 10.93 |  |  |  |  | 0.00
1984 |  |  |  | 3905.96 |  |  | 7830 |  |  |  | 500 | [10 empty] | 89.16 |  |  |  | 89.16 | [5 empty] | 88.93 |  |  | 89.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.84 |  |  |  |  | 0.00
1985 |  |  |  | 3612.47 |  |  | 7378 |  |  |  | 500 | [10 empty] | 92.95 |  |  |  | 92.95 | [5 empty] | 82.48 |  |  | 84.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.05 |  |  |  |  | 0.00
1986 |  |  |  | 3853.98 |  |  | 7930 |  |  |  | 500 | [10 empty] | 90.55 |  |  |  | 90.55 | [5 empty] | 87.99 |  |  | 90.53 |  |  |  | 0.55 |  | 0.50 | [8 empty] | 8.95 |  |  |  |  | 0.00
1987 |  |  |  | 4462.19 |  |  | 8760 |  |  |  | 500 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.88 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 3886.16 |  |  | 7773 |  |  |  | 500 | [10 empty] | 88.24 |  |  |  | 88.24 | [5 empty] | 88.48 |  |  | 88.49 |  |  |  | 1.19 |  | 1.07 | [8 empty] | 10.70 |  |  |  |  | 0.00
1989 |  |  |  | 3887.19 |  |  | 7798 |  |  |  | 500 | [10 empty] | 96.86 |  |  |  | 96.86 | [5 empty] | 88.75 |  |  | 89.02 |  |  |  | 2.30 |  | 2.28 | [8 empty] | 0.86 |  |  |  |  | 0.00
1990 |  |  |  | 3803.70 |  |  | 7602 |  |  |  | 500 | [10 empty] | 83.31 |  |  |  | 83.31 | [5 empty] | 86.84 |  |  | 86.78 |  |  |  | 8.79 |  | 8.03 | [8 empty] | 8.65 |  |  |  |  | 0.00
1991 |  |  |  | 4480.40 |  |  | 8760 |  |  |  | 502 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.82 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 3223.51 |  |  | 6516 |  |  |  | 500 | [10 empty] | 73.51 |  |  |  | 73.51 | [5 empty] | 73.40 |  |  | 74.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.49 |  |  |  |  | 0.00
1993 |  |  |  | 3746.24 |  |  | 7338 |  |  |  | 503 | [10 empty] | 83.53 |  |  |  | 83.53 | [5 empty] | 85.02 |  |  | 83.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.47 |  |  |  |  | 0.00
1994 |  |  |  | 4552.96 |  |  | 8734 |  |  |  | 512 | [10 empty] | 99.71 |  |  |  | 99.71 | [5 empty] | 101.51 |  |  | 99.70 |  |  |  | 0.23 |  | 0.23 | [8 empty] | 0.06 |  |  |  |  | 0.00
1995 |  |  |  | 3968.17 |  |  | 7666 |  |  |  | 512 | [10 empty] | 87.51 |  |  |  | 87.51 | [5 empty] | 88.47 |  |  | 87.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.49 |  |  |  |  | 0.00
1996 |  |  |  | 4485.11 |  |  | 8653 |  |  |  | 512 | [10 empty] | 98.55 |  |  |  | 99.20 | [5 empty] | 99.73 |  |  | 98.51 |  |  |  | 0.80 |  | 0.80 | [8 empty] | 0.00 |  |  |  |  | 0.65
1997 |  |  |  | 3642.86 |  |  | 7180 |  |  |  | 512 | [10 empty] | 82.00 |  |  |  | 82.00 | [5 empty] | 81.22 |  |  | 81.96 |  |  |  | 7.91 |  | 7.05 | [8 empty] | 10.95 |  |  |  |  | 0.00
1998 |  |  |  | 3333.71 |  |  | 6555 |  |  |  | 512 | [10 empty] | 74.84 |  |  |  | 74.84 | [5 empty] | 74.33 |  |  | 74.83 |  |  |  | 12.44 |  | 10.64 | [8 empty] | 14.52 |  |  |  |  | 0.00
1999 |  |  |  | 4597.44 |  |  | 8690 |  |  |  | 522 | [10 empty] | 99.21 |  |  |  | 99.21 | [5 empty] | 100.48 |  |  | 99.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.79 |  |  |  |  | 0.00
2000 |  |  |  | 4182.26 |  |  | 7820 |  |  |  | 522 | [10 empty] | 89.03 |  |  |  | 89.03 | [5 empty] | 91.21 |  |  | 89.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.97 |  |  |  |  | 0.00
2001 |  |  |  | 4270.96 |  |  | 8031 |  |  |  | 522 | [10 empty] | 91.67 |  |  |  | 91.67 | [5 empty] | 93.40 |  |  | 91.68 |  |  |  | 8.33 |  | 8.33 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 4296.03 |  |  | 8082 |  |  |  | 522 | [10 empty] | 92.43 |  |  |  | 92.43 | [5 empty] | 93.95 |  |  | 92.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.57 |  |  |  |  | 0.00
2003 |  |  |  | 4240.97 |  |  | 8058 |  |  |  | 522 | [10 empty] | 91.97 |  |  |  | 91.97 | [5 empty] | 92.75 |  |  | 91.99 |  |  |  | 0.55 |  | 0.51 | [8 empty] | 7.52 |  |  |  |  | 0.00
2004 |  |  |  | 4660.26 |  |  | 8737 |  |  |  | 522 | [10 empty] | 99.47 |  |  |  | 99.47 | [5 empty] | 101.64 |  |  | 99.46 |  |  |  | 0.53 |  | 0.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 3848.63 |  |  | 7296 |  |  |  | 522 | [10 empty] | 83.30 |  |  |  | 83.30 | [5 empty] | 84.16 |  |  | 83.28 |  |  |  | 7.72 |  | 6.97 | [8 empty] | 9.73 |  |  |  |  | 0.00
2006 |  |  |  | 4012.40 |  |  | 7665 |  |  |  | 522 | [10 empty] | 87.52 |  |  |  | 87.52 | [5 empty] | 87.75 |  |  | 87.50 |  |  |  | 4.53 |  | 4.15 | [8 empty] | 8.33 |  |  |  |  | 0.00
2007 |  |  |  | 4456.64 |  |  | 8488 |  |  |  | 545 | [10 empty] | 96.91 |  |  |  | 96.91 | [5 empty] | 93.35 |  |  | 96.89 |  |  |  | 0.82 |  | 0.81 | [8 empty] | 2.28 |  |  |  |  | 0.00
2008 |  |  |  | 4059.36 |  |  | 7768 |  |  |  | 545 | [10 empty] | 88.45 |  |  |  | 88.45 | [5 empty] | 84.79 |  |  | 88.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.55 |  |  |  |  | 0.00
2009 |  |  |  | 4653.35 |  |  | 8760 |  |  |  | 545 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.47 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 4128.07 |  |  | 7817 |  |  |  | 554 | [10 empty] | 89.30 |  |  |  | 89.30 | [5 empty] | 86.11 |  |  | 89.24 |  |  |  | 0.35 |  | 0.31 | [8 empty] | 10.39 |  |  |  |  | 0.00
2011 |  |  |  | 4477.65 |  |  | 8354 |  |  |  | 519 | [10 empty] | 95.07 |  |  |  | 95.07 | [5 empty] | 98.49 |  |  | 95.37 |  |  |  | 4.93 |  | 4.93 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 3354.75 |  |  | 6453 |  |  |  | 518 | [10 empty] | 73.49 |  |  |  | 73.49 | [5 empty] | 73.73 |  |  | 73.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.51 |  |  |  |  | 0.00
2013 |  |  |  | 3069.71 |  |  | 6311 |  |  |  | 519 | [10 empty] | 72.11 |  |  |  | 72.11 | [5 empty] | 67.51 |  |  | 72.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.89 |  |  |  |  | 0.00
2014 |  |  |  | 4570.74 |  |  | 8556 |  |  |  | 518 | [10 empty] | 97.67 |  |  |  | 97.67 | [5 empty] | 100.73 |  |  | 97.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.33 |  |  |  |  | 0.00
2015 |  |  |  | 3386.74 |  |  | 6531 |  |  |  | 518 | [10 empty] | 74.56 |  |  |  | 74.56 | [5 empty] | 74.64 |  |  | 74.55 |  |  |  | 13.40 |  | 11.54 | [8 empty] | 13.91 |  |  |  |  | 0.00
2016 |  |  |  | 4066.08 |  |  | 7500 |  |  |  | 518 | [10 empty] | 85.38 |  |  |  | 85.38 | [5 empty] | 89.36 |  |  | 85.38 |  |  |  | 14.62 |  | 14.62 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 4179.73 |  |  | 7767 |  |  |  | 519 | [10 empty] | 88.68 |  |  |  | 88.68 | [5 empty] | 91.93 |  |  | 88.66 |  |  |  | 0.91 |  | 0.82 | [8 empty] | 10.50 |  |  |  |  | 0.00
2018 |  |  |  | 4792.83 |  |  | 8760 |  |  |  | 519 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.42 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 4367.41 |  |  | 8183 |  |  |  | 519 | [10 empty] | 93.42 |  |  |  | 93.42 | [5 empty] | 96.06 |  |  | 93.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.58 |  |  |  |  | 0.00
2020 |  |  |  | 4746.40 |  |  | 8783 |  |  |  | 519 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 104.11 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1974 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 216
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 650
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 70
E. |  | Testing of plant systems or components | [35 empty] | 4
H. |  | Nuclear regulatory requirements | [39 empty] | 11
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 11
Z. |  | Other | [39 empty] | 2 | [11 empty] | 1
Subtotal | [37 empty] | 724 |  |  |  | 230 | [11 empty] | 12
Total | [22 empty] | 0 | [14 empty] | 966
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1974 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 0
12. |  |  | Reactor I&C Systems | [34 empty] | 33
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 37
16. |  |  | Steam generation systems | [34 empty] | 5
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 11
31. |  |  | Turbine and auxiliaries | [34 empty] | 64
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
33. |  |  | Circulating Water System | [34 empty] | 13
34. |  |  | Miscellaneous Systems | [34 empty] | 4
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 41
42. |  |  | Electrical Power Supply Systems | [34 empty] | 23
Total | [37 empty] | 241

## QUAD CITIES-1
2020 Operating Experience
US-254 | [8 empty] | QUAD CITIES-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXE/MIDA (Exelon (75%), MidAmerican Energy (25%) )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-3 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-02-15
Thermal power | [12 empty] | : |  |  | 2957 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1972-04-12
Gross electrical power | [12 empty] | : |  |  | 940 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-02-18
Reference unit power (net) | [12 empty] | : |  |  | 908 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.1
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.43
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 35 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.55 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.57
| Active core height/length [m] | [13 empty] | : |  |  | 3.6 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 724 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 43.96 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 177 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8075.97 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.25 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 696.58 | 649.83 |  |  |  | 687.06 |  | 670.04 | [8 empty] | 681.68 |  |  | 653.42 | [6 empty] | 666.31 |  | 667.81 |  |  |  | 657.82 |  |  | 687.21 |  |  | 666.48 | [9 empty] | 691.74 |  |  | 8075.97
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 103.11 | 102.83 |  |  |  | 101.70 |  | 102.49 | [8 empty] | 100.91 |  |  | 99.95 | [6 empty] | 98.63 |  | 98.85 |  |  |  | 100.62 |  |  | 101.72 |  |  | 101.94 | [9 empty] | 102.40 |  |  | 101.25
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 277926.16 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.77 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.08 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.32 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.6 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.68 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.28 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 4908.50 |  |  | 7382 |  |  |  | 800 | [10 empty] | 86.81 |  |  |  | 86.81 | [5 empty] | 69.05 |  |  | 82.79 |  |  |  | 4.33 |  | 3.93 | [8 empty] | 9.26 |  |  |  |  | 0.00
1974 |  |  |  | 3464.10 |  |  | 5365 |  |  |  | 800 | [10 empty] | 61.37 |  |  |  | 61.37 | [5 empty] | 49.43 |  |  | 61.24 |  |  |  | 17.84 |  | 13.33 | [8 empty] | 25.31 |  |  |  |  | 0.00
1975 |  |  |  | 4413.40 |  |  | 7531 |  |  |  | 800 | [10 empty] | 61.04 |  |  |  | 61.04 | [5 empty] | 62.98 |  |  | 85.97 |  |  |  | 38.96 |  | 38.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
1976 |  |  |  | 3401.70 |  |  | 5699 |  |  |  | 769 | [10 empty] | 50.44 |  |  |  | 50.44 | [5 empty] | 50.36 |  |  | 64.88 |  |  |  | 14.61 |  | 8.63 | [8 empty] | 40.92 |  |  |  |  | 0.00
1977 |  |  |  | 3527.40 |  |  | 6176 |  |  |  | 769 | [10 empty] | 52.42 |  |  |  | 52.42 | [5 empty] | 52.36 |  |  | 70.50 |  |  |  | 21.19 |  | 14.10 | [8 empty] | 33.49 |  |  |  |  | 0.00
1978 |  |  |  | 4782.00 |  |  | 8315 |  |  |  | 769 | [10 empty] | 71.04 |  |  |  | 71.04 | [5 empty] | 70.99 |  |  | 94.92 |  |  |  | 11.08 |  | 8.85 | [8 empty] | 20.11 |  |  |  |  | 0.00
1979 |  |  |  | 4786.50 |  |  | 7096 |  |  |  | 769 | [10 empty] | 71.05 |  |  |  | 71.05 | [5 empty] | 71.05 |  |  | 81.00 |  |  |  | 9.44 |  | 7.41 | [8 empty] | 21.54 |  |  |  |  | 0.00
1980 |  |  |  | 3468.80 |  |  | 5840 |  |  |  | 769 | [10 empty] | 66.68 |  |  |  | 67.43 | [5 empty] | 51.35 |  |  | 66.48 |  |  |  | 2.92 |  | 2.03 | [8 empty] | 30.54 |  |  |  |  | 0.75
1981 |  |  |  | 5726.80 |  |  | 8244 |  |  |  | 769 | [10 empty] | 94.33 |  |  |  | 94.33 | [5 empty] | 85.01 |  |  | 94.11 |  |  |  | 2.05 |  | 1.97 | [8 empty] | 3.70 |  |  |  |  | 0.00
1982 |  |  |  | 3258.00 |  |  | 5951 |  |  |  | 769 | [10 empty] | 68.48 |  |  |  | 68.48 | [5 empty] | 48.36 |  |  | 67.93 |  |  |  | 1.18 |  | 0.82 | [8 empty] | 30.70 |  |  |  |  | 0.00
1983 |  |  |  | 5776.40 |  |  | 8258 |  |  |  | 769 | [10 empty] | 94.65 |  |  |  | 94.65 | [5 empty] | 85.75 |  |  | 94.27 |  |  |  | 1.00 |  | 0.96 | [8 empty] | 4.39 |  |  |  |  | 0.00
1984 |  |  |  | 3358.48 |  |  | 4687 |  |  |  | 769 | [10 empty] | 53.37 |  |  |  | 53.37 | [5 empty] | 49.72 |  |  | 53.36 |  |  |  | 2.65 |  | 1.45 | [8 empty] | 45.17 |  |  |  |  | 0.00
1985 |  |  |  | 6072.32 |  |  | 8242 |  |  |  | 769 | [10 empty] | 94.11 |  |  |  | 94.11 | [5 empty] | 90.14 |  |  | 94.09 |  |  |  | 3.80 |  | 3.72 | [8 empty] | 2.17 |  |  |  |  | 0.00
1986 |  |  |  | 4426.18 |  |  | 6035 |  |  |  | 769 | [10 empty] | 68.92 |  |  |  | 68.92 | [5 empty] | 65.71 |  |  | 68.89 |  |  |  | 3.37 |  | 2.40 | [8 empty] | 28.67 |  |  |  |  | 0.00
1987 |  |  |  | 4456.09 |  |  | 6141 |  |  |  | 769 | [10 empty] | 70.11 |  |  |  | 70.11 | [5 empty] | 66.15 |  |  | 70.10 |  |  |  | 0.71 |  | 0.50 | [8 empty] | 29.38 |  |  |  |  | 0.00
1988 |  |  |  | 5661.98 |  |  | 8199 |  |  |  | 769 | [10 empty] | 93.36 |  |  |  | 93.36 | [5 empty] | 83.82 |  |  | 93.34 |  |  |  | 4.22 |  | 4.11 | [8 empty] | 2.53 |  |  |  |  | 0.00
1989 |  |  |  | 4280.44 |  |  | 6428 |  |  |  | 769 | [10 empty] | 73.43 |  |  |  | 73.43 | [5 empty] | 63.54 |  |  | 73.38 |  |  |  | 6.13 |  | 4.79 | [8 empty] | 21.78 |  |  |  |  | 0.00
1990 |  |  |  | 5345.56 |  |  | 7276 |  |  |  | 769 | [10 empty] | 83.08 |  |  |  | 83.08 | [5 empty] | 79.35 |  |  | 83.06 |  |  |  | 1.48 |  | 1.24 | [8 empty] | 15.67 |  |  |  |  | 0.00
1991 |  |  |  | 3549.53 |  |  | 4882 |  |  |  | 769 | [10 empty] | 55.79 |  |  |  | 56.61 | [5 empty] | 52.69 |  |  | 55.73 |  |  |  | 16.08 |  | 10.84 | [8 empty] | 32.55 |  |  |  |  | 0.82
1992 |  |  |  | 4166.14 |  |  | 6158 |  |  |  | 769 | [10 empty] | 70.12 |  |  |  | 70.12 | [5 empty] | 61.68 |  |  | 70.10 |  |  |  | 7.88 |  | 6.00 | [8 empty] | 23.88 |  |  |  |  | 0.00
1993 |  |  |  | 5042.49 |  |  | 6902 |  |  |  | 769 | [10 empty] | 78.81 |  |  |  | 78.81 | [5 empty] | 74.85 |  |  | 78.79 |  |  |  | 15.10 |  | 14.02 | [8 empty] | 7.17 |  |  |  |  | 0.00
1994 |  |  |  | 1670.17 |  |  | 2526 |  |  |  | 769 | [10 empty] | 28.87 |  |  |  | 28.87 | [5 empty] | 24.79 |  |  | 28.84 |  |  |  | 46.41 |  | 25.00 | [8 empty] | 46.13 |  |  |  |  | 0.00
1995 |  |  |  | 5886.21 |  |  | 7934 |  |  |  | 769 | [10 empty] | 90.59 |  |  |  | 90.59 | [5 empty] | 87.38 |  |  | 90.57 |  |  |  | 9.41 |  | 9.41 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 2680.59 |  |  | 3769 |  |  |  | 769 | [10 empty] | 42.94 |  |  |  | 42.94 | [5 empty] | 39.68 |  |  | 42.91 |  |  |  | 2.98 |  | 1.32 | [8 empty] | 55.74 |  |  |  |  | 0.00
1997 |  |  |  | 5565.46 |  |  | 7764 |  |  |  | 769 | [10 empty] | 88.69 |  |  |  | 88.69 | [5 empty] | 82.62 |  |  | 88.63 |  |  |  | 11.31 |  | 11.31 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 3142.88 |  |  | 4299 |  |  |  | 769 | [10 empty] | 49.12 |  |  |  | 49.12 | [5 empty] | 46.65 |  |  | 49.08 |  |  |  | 41.59 |  | 34.98 | [8 empty] | 15.90 |  |  |  |  | 0.00
1999 |  |  |  | 6337.59 |  |  | 8210 |  |  |  | 769 | [10 empty] | 93.72 |  |  |  | 93.72 | [5 empty] | 94.08 |  |  | 93.72 |  |  |  | 0.55 |  | 0.52 | [8 empty] | 5.75 |  |  |  |  | 0.00
2000 |  |  |  | 6168.07 |  |  | 8242 |  |  |  | 769 | [10 empty] | 93.83 |  |  |  | 93.83 | [5 empty] | 91.31 |  |  | 93.83 |  |  |  | 0.56 |  | 0.52 | [8 empty] | 5.65 |  |  |  |  | 0.00
2001 |  |  |  | 6710.87 |  |  | 8691 |  |  |  | 769 | [10 empty] | 99.22 |  |  |  | 99.22 | [5 empty] | 99.62 |  |  | 99.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.78 |  |  |  |  | 0.00
2002 |  |  |  | 5709.52 |  |  | 7564 |  |  |  | 855 | [10 empty] | 86.60 |  |  |  | 86.60 | [5 empty] | 83.96 |  |  | 86.35 |  |  |  | 7.61 |  | 7.14 | [8 empty] | 6.26 |  |  |  |  | 0.00
2003 |  |  |  | 6810.25 |  |  | 8013 |  |  |  | 855 | [10 empty] | 92.41 |  |  |  | 92.41 | [5 empty] | 90.93 |  |  | 91.47 |  |  |  | 4.96 |  | 4.82 | [8 empty] | 2.77 |  |  |  |  | 0.00
2004 |  |  |  | 6502.77 |  |  | 8784 |  |  |  | 855 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 86.58 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 6281.05 |  |  | 7875 |  |  |  | 864 | [10 empty] | 89.92 |  |  |  | 89.92 | [5 empty] | 82.98 |  |  | 89.89 |  |  |  | 0.69 |  | 0.62 | [8 empty] | 9.46 |  |  |  |  | 0.00
2006 |  |  |  | 6747.25 |  |  | 8161 |  |  |  | 867 | [10 empty] | 93.18 |  |  |  | 93.18 | [5 empty] | 88.84 |  |  | 93.16 |  |  |  | 1.77 |  | 1.68 | [8 empty] | 5.14 |  |  |  |  | 0.00
2007 |  |  |  | 6951.04 |  |  | 8212 |  |  |  | 867 | [10 empty] | 93.75 |  |  |  | 93.75 | [5 empty] | 91.52 |  |  | 93.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.25 |  |  |  |  | 0.00
2008 |  |  |  | 7490.09 |  |  | 8784 |  |  |  | 867 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.35 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 6230.78 |  |  | 7879 |  |  |  | 867 | [10 empty] | 89.96 |  |  |  | 89.96 | [5 empty] | 82.04 |  |  | 89.94 |  |  |  | 0.98 |  | 2.53 | [8 empty] | 7.52 |  |  |  |  | 0.00
2010 |  |  |  | 7646.11 |  |  | 8698 |  |  |  | 882 | [10 empty] | 99.31 |  |  |  | 99.31 | [5 empty] | 98.96 |  |  | 99.29 |  |  |  | 0.69 |  | 0.69 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 7109.23 |  |  | 7898 |  |  |  | 882 | [10 empty] | 90.18 |  |  |  | 90.18 | [5 empty] | 92.01 |  |  | 90.16 |  |  |  | 1.13 |  | 1.03 | [8 empty] | 8.79 |  |  |  |  | 0.00
2012 |  |  |  | 8130.41 |  |  | 8784 |  |  |  | 908 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.94 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 7505.99 |  |  | 8073 |  |  |  | 908 | [10 empty] | 92.16 |  |  |  | 92.16 | [5 empty] | 94.36 |  |  | 92.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.84 |  |  |  |  | 0.00
2014 |  |  |  | 8168.26 |  |  | 8760 |  |  |  | 908 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.69 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 7519.60 |  |  | 8170 |  |  |  | 908 | [10 empty] | 93.26 |  |  |  | 93.26 | [5 empty] | 94.54 |  |  | 93.26 |  |  |  | 0.87 |  | 0.82 | [8 empty] | 5.91 |  |  |  |  | 0.00
2016 |  |  |  | 8104.18 |  |  | 8784 |  |  |  | 908 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.61 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7498.16 |  |  | 8305 |  |  |  | 908 | [10 empty] | 94.81 |  |  |  | 94.81 | [5 empty] | 94.27 |  |  | 94.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.19 |  |  |  |  | 0.00
2018 |  |  |  | 8051.91 |  |  | 8668 |  |  |  | 908 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.23 |  |  | 98.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7421.05 |  |  | 8101 |  |  |  | 908 | [10 empty] | 92.49 |  |  |  | 92.49 | [5 empty] | 93.30 |  |  | 92.48 |  |  |  | 1.95 |  | 1.84 | [8 empty] | 5.67 |  |  |  |  | 0.00
2020 |  |  |  | 8075.97 |  |  | 8783 |  |  |  | 908 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.25 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1973 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 264
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 917
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 124 |  |  |  | 61
E. |  | Testing of plant systems or components | [35 empty] | 7 |  |  |  | 6
H. |  | Nuclear regulatory requirements | [39 empty] | 6
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 54
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
P. |  | Fire | [39 empty] | 7
Z. |  | Other | [35 empty] | 3 |  |  |  | 7 | [11 empty] | 2
Subtotal | [37 empty] | 1051 |  |  |  | 405 | [11 empty] | 15
Total | [22 empty] | 0 | [14 empty] | 1471
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1973 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 18
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 78
31. |  |  | Turbine and auxiliaries | [34 empty] | 72
32. |  |  | Feedwater and Main Steam System | [34 empty] | 19
34. |  |  | Miscellaneous Systems | [34 empty] | 23
41. |  |  | Main Generator Systems | [34 empty] | 16
42. |  |  | Electrical Power Supply Systems | [34 empty] | 32
Total | [37 empty] | 272

## QUAD CITIES-2
2020 Operating Experience
US-265 | [8 empty] | QUAD CITIES-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EXELON (Exelon Generation Co., LLC)
Owner | [7 empty] | : | EXE/MIDA (Exelon (75%), MidAmerican Energy (25%) )
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-3 (Mark 1) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-02-15
Thermal power | [12 empty] | : |  |  | 2957 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1972-05-23
Gross electrical power | [12 empty] | : |  |  | 940 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-03-10
Reference unit power (net) | [12 empty] | : |  |  | 911 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.1
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.43
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 35 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.55 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.57
| Active core height/length [m] | [13 empty] | : |  |  | 3.6 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 724 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 43.96 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 177 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7636.48 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.37 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.37 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.63 %
Load Factor (LF) | [18 empty] | : | 95.43 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 95.36 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 408 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 692.91 | 649.52 |  |  |  | 594.47 |  | 299.58 | [8 empty] | 685.80 |  |  | 646.57 | [6 empty] | 668.26 |  | 674.15 |  |  |  | 665.51 |  |  | 690.07 |  |  | 673.79 | [9 empty] | 695.84 |  |  | 7636.48
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.55 |  | 50.13 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.37
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.55 |  | 50.13 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.37
LF [%] |  |  |  |  | 102.23 | 102.44 |  |  |  | 87.71 |  | 45.67 | [8 empty] | 101.18 |  |  | 98.58 | [6 empty] | 98.59 |  | 99.46 |  |  |  | 101.46 |  |  | 101.81 |  |  | 102.72 | [9 empty] | 102.66 |  |  | 95.43
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.41 |  | 50.14 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.36
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 6.45 |  | 49.87 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.63
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 274008.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.39 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.06 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.6 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.61 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.8 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.38 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.54 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.07 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 5208.90 |  |  | 7405 |  |  |  | 800 | [10 empty] | 86.42 |  |  |  | 86.42 | [5 empty] | 74.76 |  |  | 84.94 |  |  |  | 4.05 |  | 3.64 | [8 empty] | 9.94 |  |  |  |  | 0.00
1974 |  |  |  | 4643.80 |  |  | 7232 |  |  |  | 800 | [10 empty] | 82.56 |  |  |  | 82.56 | [5 empty] | 66.26 |  |  | 82.56 |  |  |  | 11.84 |  | 11.08 | [8 empty] | 6.36 |  |  |  |  | 0.00
1975 |  |  |  | 2490.90 |  |  | 4555 |  |  |  | 798 | [10 empty] | 35.73 |  |  |  | 35.73 | [5 empty] | 35.63 |  |  | 52.00 |  |  |  | 31.66 |  | 16.55 | [8 empty] | 47.72 |  |  |  |  | 0.00
1976 |  |  |  | 4320.00 |  |  | 7143 |  |  |  | 769 | [10 empty] | 64.02 |  |  |  | 64.02 | [5 empty] | 63.95 |  |  | 81.32 |  |  |  | 9.71 |  | 6.88 | [8 empty] | 29.10 |  |  |  |  | 0.00
1977 |  |  |  | 4369.30 |  |  | 7118 |  |  |  | 769 | [10 empty] | 64.92 |  |  |  | 64.92 | [5 empty] | 64.86 |  |  | 81.26 |  |  |  | 12.32 |  | 9.12 | [8 empty] | 25.96 |  |  |  |  | 0.00
1978 |  |  |  | 4429.10 |  |  | 7022 |  |  |  | 769 | [10 empty] | 65.74 |  |  |  | 65.74 | [5 empty] | 65.75 |  |  | 80.16 |  |  |  | 6.60 |  | 4.64 | [8 empty] | 29.62 |  |  |  |  | 0.00
1979 |  |  |  | 3993.60 |  |  | 7686 |  |  |  | 769 | [10 empty] | 59.28 |  |  |  | 59.28 | [5 empty] | 59.28 |  |  | 87.74 |  |  |  | 13.92 |  | 9.59 | [8 empty] | 31.13 |  |  |  |  | 0.00
1980 |  |  |  | 3651.60 |  |  | 5486 |  |  |  | 769 | [10 empty] | 62.47 |  |  |  | 62.79 | [5 empty] | 54.06 |  |  | 62.45 |  |  |  | 8.26 |  | 5.65 | [8 empty] | 31.56 |  |  |  |  | 0.32
1981 |  |  |  | 3770.70 |  |  | 5957 |  |  |  | 769 | [10 empty] | 68.07 |  |  |  | 68.07 | [5 empty] | 55.97 |  |  | 68.00 |  |  |  | 1.08 |  | 0.74 | [8 empty] | 31.19 |  |  |  |  | 0.00
1982 |  |  |  | 5062.30 |  |  | 7343 |  |  |  | 769 | [10 empty] | 83.98 |  |  |  | 83.98 | [5 empty] | 75.15 |  |  | 83.82 |  |  |  | 14.50 |  | 14.24 | [8 empty] | 1.78 |  |  |  |  | 0.00
1983 |  |  |  | 3158.50 |  |  | 5620 |  |  |  | 769 | [10 empty] | 64.18 |  |  |  | 64.18 | [5 empty] | 46.89 |  |  | 64.16 |  |  |  | 0.50 |  | 0.32 | [8 empty] | 35.50 |  |  |  |  | 0.00
1984 |  |  |  | 4984.45 |  |  | 6837 |  |  |  | 769 | [10 empty] | 77.87 |  |  |  | 77.87 | [5 empty] | 73.79 |  |  | 77.83 |  |  |  | 10.15 |  | 8.79 | [8 empty] | 13.34 |  |  |  |  | 0.00
1985 |  |  |  | 4560.69 |  |  | 6247 |  |  |  | 769 | [10 empty] | 71.33 |  |  |  | 71.33 | [5 empty] | 67.70 |  |  | 71.31 |  |  |  | 2.97 |  | 2.19 | [8 empty] | 26.49 |  |  |  |  | 0.00
1986 |  |  |  | 4727.96 |  |  | 6399 |  |  |  | 769 | [10 empty] | 74.24 |  |  |  | 74.24 | [5 empty] | 70.18 |  |  | 73.05 |  |  |  | 0.88 |  | 0.66 | [8 empty] | 25.10 |  |  |  |  | 0.00
1987 |  |  |  | 4952.99 |  |  | 6832 |  |  |  | 769 | [10 empty] | 78.06 |  |  |  | 78.06 | [5 empty] | 73.53 |  |  | 77.99 |  |  |  | 17.05 |  | 16.05 | [8 empty] | 5.90 |  |  |  |  | 0.00
1988 |  |  |  | 4178.87 |  |  | 6193 |  |  |  | 769 | [10 empty] | 70.55 |  |  |  | 70.55 | [5 empty] | 61.86 |  |  | 70.50 |  |  |  | 10.03 |  | 7.86 | [8 empty] | 21.59 |  |  |  |  | 0.00
1989 |  |  |  | 5743.07 |  |  | 8363 |  |  |  | 769 | [10 empty] | 95.51 |  |  |  | 95.51 | [5 empty] | 85.25 |  |  | 95.47 |  |  |  | 3.85 |  | 3.82 | [8 empty] | 0.67 |  |  |  |  | 0.00
1990 |  |  |  | 4373.60 |  |  | 6186 |  |  |  | 769 | [10 empty] | 70.38 |  |  |  | 70.38 | [5 empty] | 64.92 |  |  | 70.62 |  |  |  | 27.74 |  | 27.02 | [8 empty] | 2.60 |  |  |  |  | 0.00
1991 |  |  |  | 5285.18 |  |  | 7731 |  |  |  | 769 | [10 empty] | 88.26 |  |  |  | 88.26 | [5 empty] | 78.46 |  |  | 88.25 |  |  |  | 11.74 |  | 11.74 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 3464.19 |  |  | 5621 |  |  |  | 769 | [10 empty] | 63.99 |  |  |  | 63.99 | [5 empty] | 51.28 |  |  | 63.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.01 |  |  |  |  | 0.00
1993 |  |  |  | 3111.82 |  |  | 4538 |  |  |  | 769 | [10 empty] | 51.84 |  |  |  | 51.84 | [5 empty] | 46.19 |  |  | 51.80 |  |  |  | 26.46 |  | 18.65 | [8 empty] | 29.51 |  |  |  |  | 0.00
1994 |  |  |  | 4013.35 |  |  | 5745 |  |  |  | 769 | [10 empty] | 65.66 |  |  |  | 65.66 | [5 empty] | 59.58 |  |  | 65.58 |  |  |  | 34.26 |  | 34.21 | [8 empty] | 0.13 |  |  |  |  | 0.00
1995 |  |  |  | 2496.98 |  |  | 3966 |  |  |  | 769 | [10 empty] | 45.33 |  |  |  | 45.33 | [5 empty] | 37.07 |  |  | 45.27 |  |  |  | 22.14 |  | 12.89 | [8 empty] | 41.78 |  |  |  |  | 0.00
1996 |  |  |  | 4666.84 |  |  | 6348 |  |  |  | 769 | [10 empty] | 72.31 |  |  |  | 98.78 | [5 empty] | 69.09 |  |  | 72.27 |  |  |  | 1.22 |  | 1.22 | [8 empty] | 0.00 |  |  |  |  | 26.47
1997 |  |  |  | 2627.74 |  |  | 3718 |  |  |  | 769 | [10 empty] | 42.34 |  |  |  | 42.34 | [5 empty] | 39.01 |  |  | 42.44 |  |  |  | 38.44 |  | 26.44 | [8 empty] | 31.22 |  |  |  |  | 0.00
1998 |  |  |  | 3819.59 |  |  | 5095 |  |  |  | 769 | [10 empty] | 58.20 |  |  |  | 59.00 | [5 empty] | 56.70 |  |  | 58.16 |  |  |  | 2.12 |  | 1.28 | [8 empty] | 39.73 |  |  |  |  | 0.79
1999 |  |  |  | 6596.69 |  |  | 8537 |  |  |  | 769 | [10 empty] | 97.47 |  |  |  | 97.47 | [5 empty] | 97.93 |  |  | 97.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.53 |  |  |  |  | 0.00
2000 |  |  |  | 6220.62 |  |  | 8156 |  |  |  | 769 | [10 empty] | 92.87 |  |  |  | 92.87 | [5 empty] | 92.09 |  |  | 92.85 |  |  |  | 1.21 |  | 1.14 | [8 empty] | 5.99 |  |  |  |  | 0.00
2001 |  |  |  | 6273.82 |  |  | 8058 |  |  |  | 769 | [10 empty] | 91.92 |  |  |  | 91.92 | [5 empty] | 93.13 |  |  | 91.99 |  |  |  | 7.30 |  | 7.24 | [8 empty] | 0.84 |  |  |  |  | 0.00
2002 |  |  |  | 6556.83 |  |  | 7852 |  |  |  | 855 | [10 empty] | 90.37 |  |  |  | 90.37 | [5 empty] | 89.77 |  |  | 89.63 |  |  |  | 3.56 |  | 3.33 | [8 empty] | 6.30 |  |  |  |  | 0.00
2003 |  |  |  | 6975.11 |  |  | 8181 |  |  |  | 855 | [10 empty] | 94.01 |  |  |  | 94.01 | [5 empty] | 93.13 |  |  | 93.39 |  |  |  | 5.99 |  | 5.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 6179.39 |  |  | 7955 |  |  |  | 855 | [10 empty] | 90.48 |  |  |  | 90.48 | [5 empty] | 82.28 |  |  | 90.56 |  |  |  | 0.32 |  | 0.29 | [8 empty] | 9.23 |  |  |  |  | 0.00
2005 |  |  |  | 7036.91 |  |  | 8533 |  |  |  | 864 | [10 empty] | 97.42 |  |  |  | 97.42 | [5 empty] | 92.96 |  |  | 97.40 |  |  |  | 0.44 |  | 0.43 | [8 empty] | 2.15 |  |  |  |  | 0.00
2006 |  |  |  | 6611.02 |  |  | 8000 |  |  |  | 867 | [10 empty] | 91.34 |  |  |  | 91.34 | [5 empty] | 87.05 |  |  | 91.32 |  |  |  | 1.84 |  | 1.71 | [8 empty] | 6.94 |  |  |  |  | 0.00
2007 |  |  |  | 7505.84 |  |  | 8720 |  |  |  | 867 | [10 empty] | 99.55 |  |  |  | 99.55 | [5 empty] | 98.83 |  |  | 99.54 |  |  |  | 0.45 |  | 0.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 6734.60 |  |  | 7852 |  |  |  | 867 | [10 empty] | 89.40 |  |  |  | 89.40 | [5 empty] | 88.43 |  |  | 89.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.60 |  |  |  |  | 0.00
2009 |  |  |  | 6909.37 |  |  | 8760 |  |  |  | 867 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 90.97 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 7150.14 |  |  | 7849 |  |  |  | 892 | [10 empty] | 89.90 |  |  |  | 89.90 | [5 empty] | 91.51 |  |  | 89.60 |  |  |  | 0.88 |  | 1.93 | [8 empty] | 8.17 |  |  |  |  | 0.00
2011 |  |  |  | 8092.34 |  |  | 8743 |  |  |  | 892 | [10 empty] | 99.81 |  |  |  | 99.81 | [5 empty] | 103.56 |  |  | 99.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.19 |  |  |  |  | 0.00
2012 |  |  |  | 7375.56 |  |  | 8004 |  |  |  | 911 | [10 empty] | 91.14 |  |  |  | 91.14 | [5 empty] | 92.17 |  |  | 91.12 |  |  |  | 0.67 |  | 0.61 | [8 empty] | 8.25 |  |  |  |  | 0.00
2013 |  |  |  | 8051.85 |  |  | 8723 |  |  |  | 911 | [10 empty] | 99.58 |  |  |  | 99.58 | [5 empty] | 100.88 |  |  | 99.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.42 |  |  |  |  | 0.00
2014 |  |  |  | 7220.77 |  |  | 7886 |  |  |  | 911 | [10 empty] | 90.03 |  |  |  | 90.03 | [5 empty] | 90.48 |  |  | 90.02 |  |  |  | 1.84 |  | 1.69 | [8 empty] | 8.28 |  |  |  |  | 0.00
2015 |  |  |  | 8042.55 |  |  | 8760 |  |  |  | 911 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.78 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 7550.87 |  |  | 8336 |  |  |  | 911 | [10 empty] | 94.90 |  |  |  | 94.90 | [5 empty] | 94.36 |  |  | 94.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.10 |  |  |  |  | 0.00
2017 |  |  |  | 7903.72 |  |  | 8604 |  |  |  | 911 | [10 empty] | 98.22 |  |  |  | 98.22 | [5 empty] | 99.04 |  |  | 98.22 |  |  |  | 1.78 |  | 1.78 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 7424.55 |  |  | 8282 |  |  |  | 911 | [10 empty] | 94.68 |  |  |  | 94.68 | [5 empty] | 93.04 |  |  | 94.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.32 |  |  |  |  | 0.00
2019 |  |  |  | 8029.05 |  |  | 8760 |  |  |  | 911 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.61 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7636.48 |  |  | 8376 |  |  |  | 911 | [10 empty] | 95.37 |  |  |  | 95.37 | [5 empty] | 95.43 |  |  | 95.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.63 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1973 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 400
B. |  | Refuelling without maintenance | [20 empty] | 407 | [14 empty] | 19
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 868
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 111
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 8
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 12
L. |  | Human factor related | [39 empty] | 11
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
P. |  | Fire | [39 empty] | 6
Z. |  | Other | [35 empty] | 74 |  |  |  | 35 | [11 empty] | 49
Subtotal | [22 empty] | 407 | [14 empty] | 1075 |  |  |  | 461 | [11 empty] | 62
Total | [22 empty] | 407 | [14 empty] | 1598
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1973 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 21
12. |  |  | Reactor I&C Systems | [34 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [34 empty] | 57
16. |  |  | Steam generation systems | [34 empty] | 9
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 6
31. |  |  | Turbine and auxiliaries | [34 empty] | 72
32. |  |  | Feedwater and Main Steam System | [34 empty] | 40
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 72
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 27
42. |  |  | Electrical Power Supply Systems | [34 empty] | 65
Total | [37 empty] | 405
Highlights (2020)
Refueling Outage 30.

## RIVER BEND-1
2020 Operating Experience
US-458 | [8 empty] | RIVER BEND-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Owner | [7 empty] | : | ENTGS (ENTERGY GULF STATES, INC.)
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-6 (Mark 3) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-03-25
Thermal power | [12 empty] | : |  |  | 3091 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-12-03
Gross electrical power | [12 empty] | : |  |  | 1016 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-06-16
Reference unit power (net) | [12 empty] | : |  |  | 967 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.56
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 288
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.105
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 29600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.29 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.78
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 624 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.86 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 145 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7988.37 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.54 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.4 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.6 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.4 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 94.05 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 96.39 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 317 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 707.06 | 674.07 |  |  |  | 725.43 |  | 674.27 | [8 empty] | 724.23 |  |  | 681.32 | [6 empty] | 667.70 |  | 586.01 |  |  |  | 663.11 |  |  | 709.06 |  |  | 460.14 | [9 empty] | 715.96 |  |  | 7988.37
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 86.59 |  |  |  | 100.00 |  |  | 99.23 |  |  | 70.72 | [9 empty] | 100.00 |  |  | 96.40
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 86.59 |  |  |  | 100.00 |  |  | 99.23 |  |  | 70.72 | [9 empty] | 100.00 |  |  | 96.40
LF [%] |  |  |  |  | 98.28 | 100.15 |  |  |  | 100.83 |  | 96.84 | [8 empty] | 100.66 |  |  | 97.86 | [6 empty] | 92.81 |  | 81.45 |  |  |  | 95.24 |  |  | 98.56 |  |  | 66.09 | [9 empty] | 99.51 |  |  | 94.05
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 86.56 |  |  |  | 100.00 |  |  | 99.19 |  |  | 70.83 | [9 empty] | 100.00 |  |  | 96.39
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 13.41 |  |  |  | 0.00 |  |  | 0.00 |  |  | 29.27 | [9 empty] | 0.00 |  |  | 3.54
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 13.41 |  |  |  | 0.00 |  |  | 0.77 |  |  | 29.27 | [9 empty] | 0.00 |  |  | 3.60
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 195107.14 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.77 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.76 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.21 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.93 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.86 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.17 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.64 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 2995.44 |  |  | 4221 |  |  |  | 936 | [10 empty] | 51.92 |  |  |  | 51.92 | [5 empty] | 47.08 |  |  | 51.73 |  |  |  | 18.86 |  | 12.07 | [8 empty] | 36.01 |  |  |  |  | 0.00
1987 |  |  |  | 4964.44 |  |  | 5836 |  |  |  | 936 | [10 empty] | 66.65 |  |  |  | 66.65 | [5 empty] | 60.55 |  |  | 66.62 |  |  |  | 5.69 |  | 4.02 | [8 empty] | 29.33 |  |  |  |  | 0.00
1988 |  |  |  | 7248.98 |  |  | 8149 |  |  |  | 936 | [10 empty] | 92.80 |  |  |  | 92.80 | [5 empty] | 88.17 |  |  | 92.77 |  |  |  | 4.26 |  | 4.13 | [8 empty] | 3.06 |  |  |  |  | 0.00
1989 |  |  |  | 4785.01 |  |  | 5853 |  |  |  | 936 | [10 empty] | 66.88 |  |  |  | 66.88 | [5 empty] | 58.36 |  |  | 66.82 |  |  |  | 11.31 |  | 8.53 | [8 empty] | 24.60 |  |  |  |  | 0.00
1990 |  |  |  | 5592.55 |  |  | 6642 |  |  |  | 936 | [10 empty] | 75.83 |  |  |  | 75.83 | [5 empty] | 68.21 |  |  | 75.82 |  |  |  | 2.27 |  | 1.76 | [8 empty] | 22.41 |  |  |  |  | 0.00
1991 |  |  |  | 6687.20 |  |  | 7507 |  |  |  | 936 | [10 empty] | 85.72 |  |  |  | 85.72 | [5 empty] | 81.56 |  |  | 85.70 |  |  |  | 11.54 |  | 11.19 | [8 empty] | 3.09 |  |  |  |  | 0.00
1992 |  |  |  | 2762.68 |  |  | 3210 |  |  |  | 936 | [10 empty] | 36.54 |  |  |  | 36.54 | [5 empty] | 33.60 |  |  | 36.54 |  |  |  | 25.78 |  | 12.69 | [8 empty] | 50.76 |  |  |  |  | 0.00
1993 |  |  |  | 5257.87 |  |  | 6076 |  |  |  | 936 | [10 empty] | 69.37 |  |  |  | 69.37 | [5 empty] | 64.13 |  |  | 69.36 |  |  |  | 28.70 |  | 27.92 | [8 empty] | 2.71 |  |  |  |  | 0.00
1994 |  |  |  | 4886.23 |  |  | 5455 |  |  |  | 936 | [10 empty] | 62.34 |  |  |  | 62.34 | [5 empty] | 59.59 |  |  | 62.27 |  |  |  | 19.70 |  | 15.30 | [8 empty] | 22.36 |  |  |  |  | 0.00
1995 |  |  |  | 7930.81 |  |  | 8704 |  |  |  | 936 | [10 empty] | 99.37 |  |  |  | 99.37 | [5 empty] | 96.72 |  |  | 99.36 |  |  |  | 0.63 |  | 0.63 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 6860.33 |  |  | 7391 |  |  |  | 936 | [10 empty] | 84.20 |  |  |  | 84.20 | [5 empty] | 83.44 |  |  | 84.14 |  |  |  | 5.65 |  | 5.04 | [8 empty] | 10.76 |  |  |  |  | 0.00
1997 |  |  |  | 6822.66 |  |  | 7427 |  |  |  | 936 | [10 empty] | 84.82 |  |  |  | 84.82 | [5 empty] | 83.21 |  |  | 84.78 |  |  |  | 5.08 |  | 4.54 | [8 empty] | 10.64 |  |  |  |  | 0.00
1998 |  |  |  | 7833.50 |  |  | 8404 |  |  |  | 936 | [10 empty] | 95.94 |  |  |  | 95.94 | [5 empty] | 95.54 |  |  | 95.94 |  |  |  | 4.06 |  | 4.06 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 5704.78 |  |  | 6476 |  |  |  | 936 | [10 empty] | 74.01 |  |  |  | 74.01 | [5 empty] | 69.58 |  |  | 73.93 |  |  |  | 16.83 |  | 14.98 | [8 empty] | 11.02 |  |  |  |  | 0.00
2000 |  |  |  | 7352.74 |  |  | 7795 |  |  |  | 936 | [10 empty] | 88.76 |  |  |  | 88.76 | [5 empty] | 89.43 |  |  | 88.74 |  |  |  | 1.65 |  | 1.49 | [8 empty] | 9.76 |  |  |  |  | 0.00
2001 |  |  |  | 7811.78 |  |  | 8120 |  |  |  | 936 | [10 empty] | 92.36 |  |  |  | 92.36 | [5 empty] | 95.27 |  |  | 92.69 |  |  |  | 0.77 |  | 0.72 | [8 empty] | 6.92 |  |  |  |  | 0.00
2002 |  |  |  | 8472.43 |  |  | 8579 |  |  |  | 966 | [10 empty] | 97.92 |  |  |  | 97.92 | [5 empty] | 100.12 |  |  | 97.93 |  |  |  | 1.03 |  | 1.01 | [8 empty] | 1.06 |  |  |  |  | 0.00
2003 |  |  |  | 7653.23 |  |  | 8050 |  |  |  | 966 | [10 empty] | 91.81 |  |  |  | 91.81 | [5 empty] | 90.44 |  |  | 91.89 |  |  |  | 1.24 |  | 1.16 | [8 empty] | 7.03 |  |  |  |  | 0.00
2004 |  |  |  | 7427.37 |  |  | 7758 |  |  |  | 966 | [10 empty] | 88.20 |  |  |  | 88.20 | [5 empty] | 87.53 |  |  | 88.32 |  |  |  | 3.27 |  | 2.98 | [8 empty] | 8.83 |  |  |  |  | 0.00
2005 |  |  |  | 7822.48 |  |  | 8162 |  |  |  | 978 | [10 empty] | 93.21 |  |  |  | 93.21 | [5 empty] | 91.30 |  |  | 93.16 |  |  |  | 2.03 |  | 1.93 | [8 empty] | 4.86 |  |  |  |  | 0.00
2006 |  |  |  | 7478.26 |  |  | 7921 |  |  |  | 966 | [10 empty] | 90.44 |  |  |  | 90.44 | [5 empty] | 88.37 |  |  | 90.42 |  |  |  | 1.71 |  | 1.58 | [8 empty] | 7.98 |  |  |  |  | 0.00
2007 |  |  |  | 7184.57 |  |  | 7916 |  |  |  | 970 | [10 empty] | 90.46 |  |  |  | 90.46 | [5 empty] | 84.55 |  |  | 90.37 |  |  |  | 9.54 |  | 9.54 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 6366.63 |  |  | 6771 |  |  |  | 970 | [10 empty] | 77.09 |  |  |  | 82.99 | [5 empty] | 74.72 |  |  | 77.08 |  |  |  | 1.74 |  | 1.47 | [8 empty] | 15.54 |  |  |  |  | 5.90
2009 |  |  |  | 7833.37 |  |  | 8085 |  |  |  | 978 | [10 empty] | 92.39 |  |  |  | 92.39 | [5 empty] | 91.43 |  |  | 92.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.61 |  |  |  |  | 0.00
2010 |  |  |  | 8363.16 |  |  | 8642 |  |  |  | 974 | [10 empty] | 98.67 |  |  |  | 98.67 | [5 empty] | 98.02 |  |  | 98.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.33 |  |  |  |  | 0.00
2011 |  |  |  | 7696.44 |  |  | 7988 |  |  |  | 967 | [10 empty] | 91.15 |  |  |  | 91.15 | [5 empty] | 90.86 |  |  | 91.19 |  |  |  | 1.21 |  | 1.12 | [8 empty] | 7.73 |  |  |  |  | 0.00
2012 |  |  |  | 7819.86 |  |  | 8172 |  |  |  | 967 | [10 empty] | 93.06 |  |  |  | 93.06 | [5 empty] | 92.06 |  |  | 93.03 |  |  |  | 5.19 |  | 5.09 | [8 empty] | 1.85 |  |  |  |  | 0.00
2013 |  |  |  | 7599.84 |  |  | 7898 |  |  |  | 967 | [10 empty] | 90.16 |  |  |  | 90.16 | [5 empty] | 89.71 |  |  | 90.15 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 9.76 |  |  |  |  | 0.00
2014 |  |  |  | 8197.47 |  |  | 8525 |  |  |  | 967 | [10 empty] | 97.31 |  |  |  | 97.31 | [5 empty] | 96.77 |  |  | 97.32 |  |  |  | 2.69 |  | 2.69 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6934.81 |  |  | 7556 |  |  |  | 967 | [10 empty] | 86.24 |  |  |  | 86.24 | [5 empty] | 81.87 |  |  | 86.26 |  |  |  | 4.42 |  | 3.99 | [8 empty] | 9.77 |  |  |  |  | 0.00
2016 |  |  |  | 7108.86 |  |  | 7501 |  |  |  | 967 | [10 empty] | 85.39 |  |  |  | 85.39 | [5 empty] | 83.69 |  |  | 85.39 |  |  |  | 11.23 |  | 10.80 | [8 empty] | 3.81 |  |  |  |  | 0.00
2017 |  |  |  | 7047.56 |  |  | 7586 |  |  |  | 967 | [10 empty] | 86.61 |  |  |  | 86.61 | [5 empty] | 83.20 |  |  | 86.60 |  |  |  | 2.39 |  | 2.12 | [8 empty] | 11.27 |  |  |  |  | 0.00
2018 |  |  |  | 7045.93 |  |  | 7650 |  |  |  | 967 | [10 empty] | 87.34 |  |  |  | 87.34 | [5 empty] | 83.18 |  |  | 87.33 |  |  |  | 6.53 |  | 6.10 | [8 empty] | 6.56 |  |  |  |  | 0.00
2019 |  |  |  | 6574.77 |  |  | 7448 |  |  |  | 967 | [10 empty] | 85.04 |  |  |  | 85.04 | [5 empty] | 77.62 |  |  | 85.02 |  |  |  | 3.17 |  | 2.78 | [8 empty] | 12.17 |  |  |  |  | 0.00
2020 |  |  |  | 7988.37 |  |  | 8467 |  |  |  | 967 | [10 empty] | 96.40 |  |  |  | 96.40 | [5 empty] | 94.05 |  |  | 96.39 |  |  |  | 3.54 |  | 3.60 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1986 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 359
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 712
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 152
E. |  | Testing of plant systems or components | [35 empty] | 9 |  |  |  | 15
L. |  | Human factor related | [39 empty] | 17
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 15
P. |  | Fire | [39 empty] | 0
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 10
Z. |  | Other | [24 empty] | 311 | [6 empty] | 6 |  |  |  | 8 |  |  |  | 95 | [11 empty] | 0
Subtotal | [26 empty] | 311 | [6 empty] | 6 |  |  |  | 891 |  |  |  | 486 | [11 empty] | 15
Total | [22 empty] | 317 | [14 empty] | 1392
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1986 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 35
12. |  |  | Reactor I&C Systems | [34 empty] | 59
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 71
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 14
31. |  |  | Turbine and auxiliaries | [34 empty] | 67
32. |  |  | Feedwater and Main Steam System | [34 empty] | 67
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 15
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 43
42. |  |  | Electrical Power Supply Systems | [34 empty] | 33
Total | [37 empty] | 423
Highlights (2020)
Shutdown due to loss of Make-Up Water flow.

## ROBINSON-2
2020 Operating Experience
US-261 | [8 empty] | ROBINSON-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PROGRESS (Progress Energy)
Owner | [7 empty] | : | PROG_E_C (PROGRESS ENERGY Carolinas, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-04-13
Thermal power | [12 empty] | : |  |  | 2339 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1970-09-26
Gross electrical power | [12 empty] | : |  |  | 780 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1971-03-07
Reference unit power (net) | [12 empty] | : |  |  | 741 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 50 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.71
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.295
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 30000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.4
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 43.96 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 45 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6124.63 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.08 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.08 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.92 %
Load Factor (LF) | [18 empty] | : | 94.1 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.09 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 783 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 587.24 | 549.66 |  |  |  | 585.38 |  | 564.64 | [8 empty] | 579.28 |  |  | 558.50 | [6 empty] | 569.63 |  | 570.45 |  |  |  | 555.98 |  |  | 530.42 |  |  | 86.39 | [9 empty] | 387.05 |  |  | 6124.63
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 20.25 | [9 empty] | 71.87 |  |  | 91.08
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 20.25 | [9 empty] | 71.87 |  |  | 91.08
LF [%] |  |  |  |  | 106.52 | 106.58 |  |  |  | 106.18 |  | 105.83 | [8 empty] | 105.07 |  |  | 104.68 | [6 empty] | 103.32 |  | 103.47 |  |  |  | 104.21 |  |  | 96.21 |  |  | 16.19 | [9 empty] | 70.21 |  |  | 94.10
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 20.42 | [9 empty] | 71.91 |  |  | 91.09
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 79.75 | [9 empty] | 28.13 |  |  | 8.92
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 245151.54 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.72 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.83 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.88 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.29 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 79.37 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.16 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1971 |  |  |  | 2538.60 |  |  | 4078 |  |  |  | 739 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 43.07 |  |  | 48.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1972 |  |  |  | 5082.40 |  |  | 7487 |  |  |  | 739 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 78.29 |  |  | 85.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 3765.50 |  |  | 6591 |  |  |  | 715 | [10 empty] | 75.70 |  |  |  | 75.70 | [5 empty] | 60.12 |  |  | 75.24 |  |  |  | 9.44 |  | 7.89 | [8 empty] | 16.41 |  |  |  |  | 0.00
1974 |  |  |  | 4813.10 |  |  | 7297 |  |  |  | 700 | [10 empty] | 83.30 |  |  |  | 83.30 | [5 empty] | 78.49 |  |  | 83.30 |  |  |  | 3.03 |  | 2.60 | [8 empty] | 14.10 |  |  |  |  | 0.00
1975 |  |  |  | 4170.90 |  |  | 6316 |  |  |  | 665 | [10 empty] | 71.05 |  |  |  | 71.05 | [5 empty] | 71.60 |  |  | 72.10 |  |  |  | 13.68 |  | 11.26 | [8 empty] | 17.69 |  |  |  |  | 0.00
1976 |  |  |  | 4874.20 |  |  | 7435 |  |  |  | 667 | [10 empty] | 82.54 |  |  |  | 82.54 | [5 empty] | 83.19 |  |  | 84.64 |  |  |  | 3.46 |  | 2.95 | [8 empty] | 14.50 |  |  |  |  | 0.00
1977 |  |  |  | 4130.20 |  |  | 7462 |  |  |  | 665 | [10 empty] | 70.81 |  |  |  | 70.81 | [5 empty] | 70.90 |  |  | 85.18 |  |  |  | 23.86 |  | 22.18 | [8 empty] | 7.01 |  |  |  |  | 0.00
1978 |  |  |  | 3980.00 |  |  | 6307 |  |  |  | 665 | [10 empty] | 68.21 |  |  |  | 68.21 | [5 empty] | 68.32 |  |  | 72.00 |  |  |  | 9.62 |  | 7.26 | [8 empty] | 24.53 |  |  |  |  | 0.00
1979 |  |  |  | 4005.10 |  |  | 6172 |  |  |  | 665 | [10 empty] | 68.72 |  |  |  | 68.72 | [5 empty] | 68.75 |  |  | 70.46 |  |  |  | 5.18 |  | 3.75 | [8 empty] | 27.53 |  |  |  |  | 0.00
1980 |  |  |  | 3210.90 |  |  | 5464 |  |  |  | 665 | [10 empty] | 61.85 |  |  |  | 61.85 | [5 empty] | 54.97 |  |  | 62.20 |  |  |  | 21.08 |  | 16.52 | [8 empty] | 21.63 |  |  |  |  | 0.00
1981 |  |  |  | 3510.80 |  |  | 6391 |  |  |  | 665 | [10 empty] | 73.41 |  |  |  | 81.06 | [5 empty] | 60.27 |  |  | 72.96 |  |  |  | 18.94 |  | 18.94 | [8 empty] | 0.00 |  |  |  |  | 7.65
1982 |  |  |  | 2268.40 |  |  | 4278 |  |  |  | 665 | [10 empty] | 47.89 |  |  |  | 47.89 | [5 empty] | 38.94 |  |  | 48.84 |  |  |  | 7.11 |  | 3.66 | [8 empty] | 48.44 |  |  |  |  | 0.00
1983 |  |  |  | 3347.50 |  |  | 6609 |  |  |  | 665 | [10 empty] | 75.54 |  |  |  | 75.54 | [5 empty] | 57.46 |  |  | 75.45 |  |  |  | 17.74 |  | 16.30 | [8 empty] | 8.16 |  |  |  |  | 0.00
1984 |  |  |  | 224.28 |  |  | 615 |  |  |  | 665 | [10 empty] | 6.97 |  |  |  | 6.97 | [5 empty] | 3.84 |  |  | 7.00 |  |  |  | 17.70 |  | 1.50 | [8 empty] | 91.53 |  |  |  |  | 0.00
1985 |  |  |  | 5239.91 |  |  | 7697 |  |  |  | 665 | [10 empty] | 87.64 |  |  |  | 87.64 | [5 empty] | 89.95 |  |  | 87.87 |  |  |  | 9.76 |  | 9.48 | [8 empty] | 2.89 |  |  |  |  | 0.00
1986 |  |  |  | 4799.60 |  |  | 7028 |  |  |  | 665 | [10 empty] | 79.72 |  |  |  | 79.72 | [5 empty] | 82.39 |  |  | 80.23 |  |  |  | 20.23 |  | 20.22 | [8 empty] | 0.06 |  |  |  |  | 0.00
1987 |  |  |  | 4235.47 |  |  | 6224 |  |  |  | 665 | [10 empty] | 70.31 |  |  |  | 70.31 | [5 empty] | 72.71 |  |  | 71.05 |  |  |  | 9.25 |  | 7.17 | [8 empty] | 22.52 |  |  |  |  | 0.00
1988 |  |  |  | 3182.43 |  |  | 5717 |  |  |  | 665 | [10 empty] | 64.23 |  |  |  | 64.23 | [5 empty] | 54.48 |  |  | 65.08 |  |  |  | 25.18 |  | 21.62 | [8 empty] | 14.15 |  |  |  |  | 0.00
1989 |  |  |  | 2790.53 |  |  | 4107 |  |  |  | 665 | [10 empty] | 45.49 |  |  |  | 45.49 | [5 empty] | 47.90 |  |  | 46.88 |  |  |  | 46.11 |  | 38.93 | [8 empty] | 15.58 |  |  |  |  | 0.00
1990 |  |  |  | 3319.19 |  |  | 5614 |  |  |  | 665 | [10 empty] | 63.15 |  |  |  | 63.15 | [5 empty] | 56.98 |  |  | 64.09 |  |  |  | 1.77 |  | 1.14 | [8 empty] | 35.71 |  |  |  |  | 0.00
1991 |  |  |  | 4792.24 |  |  | 7048 |  |  |  | 672 | [10 empty] | 80.15 |  |  |  | 80.15 | [5 empty] | 81.34 |  |  | 80.46 |  |  |  | 1.30 |  | 1.05 | [8 empty] | 18.79 |  |  |  |  | 0.00
1992 |  |  |  | 4062.91 |  |  | 5812 |  |  |  | 683 | [10 empty] | 66.17 |  |  |  | 66.17 | [5 empty] | 67.72 |  |  | 66.17 |  |  |  | 12.75 |  | 9.67 | [8 empty] | 24.17 |  |  |  |  | 0.00
1993 |  |  |  | 4193.27 |  |  | 6137 |  |  |  | 683 | [10 empty] | 70.07 |  |  |  | 70.07 | [5 empty] | 70.09 |  |  | 70.06 |  |  |  | 14.94 |  | 12.31 | [8 empty] | 17.63 |  |  |  |  | 0.00
1994 |  |  |  | 4655.06 |  |  | 6845 |  |  |  | 683 | [10 empty] | 78.20 |  |  |  | 78.20 | [5 empty] | 77.80 |  |  | 78.14 |  |  |  | 21.80 |  | 21.80 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 5033.83 |  |  | 7356 |  |  |  | 683 | [10 empty] | 84.01 |  |  |  | 84.01 | [5 empty] | 84.13 |  |  | 83.97 |  |  |  | 1.64 |  | 1.40 | [8 empty] | 14.59 |  |  |  |  | 0.00
1996 |  |  |  | 5460.10 |  |  | 7745 |  |  |  | 683 | [10 empty] | 88.19 |  |  |  | 88.19 | [5 empty] | 91.01 |  |  | 88.17 |  |  |  | 0.21 |  | 0.18 | [8 empty] | 11.62 |  |  |  |  | 0.00
1997 |  |  |  | 6197.59 |  |  | 8662 |  |  |  | 683 | [10 empty] | 98.89 |  |  |  | 98.89 | [5 empty] | 103.59 |  |  | 98.88 |  |  |  | 1.11 |  | 1.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 5505.56 |  |  | 7751 |  |  |  | 683 | [10 empty] | 88.50 |  |  |  | 88.50 | [5 empty] | 92.02 |  |  | 88.48 |  |  |  | 0.99 |  | 0.88 | [8 empty] | 10.62 |  |  |  |  | 0.00
1999 |  |  |  | 5684.48 |  |  | 8009 |  |  |  | 683 | [10 empty] | 91.45 |  |  |  | 91.45 | [5 empty] | 95.01 |  |  | 91.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.55 |  |  |  |  | 0.00
2000 |  |  |  | 6237.08 |  |  | 8750 |  |  |  | 683 | [10 empty] | 99.62 |  |  |  | 99.62 | [5 empty] | 103.96 |  |  | 99.61 |  |  |  | 0.38 |  | 0.38 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 5515.04 |  |  | 7919 |  |  |  | 683 | [10 empty] | 90.41 |  |  |  | 90.41 | [5 empty] | 92.18 |  |  | 90.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.59 |  |  |  |  | 0.00
2002 |  |  |  | 5606.11 |  |  | 7960 |  |  |  | 683 | [10 empty] | 90.88 |  |  |  | 90.88 | [5 empty] | 93.70 |  |  | 90.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.12 |  |  |  |  | 0.00
2003 |  |  |  | 6439.90 |  |  | 8760 |  |  |  | 710 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.54 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 5742.21 |  |  | 7811 |  |  |  | 710 | [10 empty] | 88.94 |  |  |  | 88.94 | [5 empty] | 92.07 |  |  | 88.92 |  |  |  | 0.60 |  | 0.54 | [8 empty] | 10.52 |  |  |  |  | 0.00
2005 |  |  |  | 5770.14 |  |  | 7839 |  |  |  | 710 | [10 empty] | 89.50 |  |  |  | 89.50 | [5 empty] | 92.77 |  |  | 89.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.50 |  |  |  |  | 0.00
2006 |  |  |  | 6442.70 |  |  | 8705 |  |  |  | 710 | [10 empty] | 99.38 |  |  |  | 99.38 | [5 empty] | 103.59 |  |  | 99.37 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 5737.92 |  |  | 7825 |  |  |  | 710 | [10 empty] | 89.34 |  |  |  | 89.34 | [5 empty] | 92.26 |  |  | 89.33 |  |  |  | 0.62 |  | 0.56 | [8 empty] | 10.10 |  |  |  |  | 0.00
2008 |  |  |  | 5429.26 |  |  | 7380 |  |  |  | 710 | [10 empty] | 84.03 |  |  |  | 84.03 | [5 empty] | 87.05 |  |  | 84.02 |  |  |  | 4.50 |  | 3.96 | [8 empty] | 12.01 |  |  |  |  | 0.00
2009 |  |  |  | 6473.19 |  |  | 8667 |  |  |  | 710 | [10 empty] | 98.95 |  |  |  | 98.95 | [5 empty] | 104.08 |  |  | 98.94 |  |  |  | 0.52 |  | 0.52 | [8 empty] | 0.54 |  |  |  |  | 0.00
2010 |  |  |  | 3598.36 |  |  | 4902 |  |  |  | 724 | [10 empty] | 56.85 |  |  |  | 56.85 | [5 empty] | 56.74 |  |  | 55.96 |  |  |  | 23.96 |  | 17.91 | [8 empty] | 25.24 |  |  |  |  | 0.00
2011 |  |  |  | 6363.80 |  |  | 8677 |  |  |  | 724 | [10 empty] | 99.06 |  |  |  | 99.06 | [5 empty] | 100.34 |  |  | 99.05 |  |  |  | 0.94 |  | 0.94 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 5388.11 |  |  | 7165 |  |  |  | 741 | [10 empty] | 81.90 |  |  |  | 81.90 | [5 empty] | 83.25 |  |  | 81.57 |  |  |  | 0.93 |  | 0.77 | [8 empty] | 17.33 |  |  |  |  | 0.00
2013 |  |  |  | 5696.46 |  |  | 7446 |  |  |  | 741 | [10 empty] | 85.00 |  |  |  | 85.00 | [5 empty] | 87.75 |  |  | 84.99 |  |  |  | 0.70 |  | 0.60 | [8 empty] | 14.40 |  |  |  |  | 0.00
2014 |  |  |  | 6159.41 |  |  | 7975 |  |  |  | 741 | [10 empty] | 91.03 |  |  |  | 91.03 | [5 empty] | 94.89 |  |  | 91.04 |  |  |  | 0.66 |  | 0.60 | [8 empty] | 8.37 |  |  |  |  | 0.00
2015 |  |  |  | 5723.72 |  |  | 7413 |  |  |  | 741 | [10 empty] | 84.62 |  |  |  | 84.62 | [5 empty] | 88.18 |  |  | 84.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.38 |  |  |  |  | 0.00
2016 |  |  |  | 6432.19 |  |  | 8441 |  |  |  | 741 | [10 empty] | 96.09 |  |  |  | 96.73 | [5 empty] | 98.82 |  |  | 96.10 |  |  |  | 3.27 |  | 3.27 | [8 empty] | 0.00 |  |  |  |  | 0.64
2017 |  |  |  | 5930.08 |  |  | 7752 |  |  |  | 741 | [10 empty] | 88.48 |  |  |  | 88.48 | [5 empty] | 91.36 |  |  | 88.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.52 |  |  |  |  | 0.00
2018 |  |  |  | 5278.14 |  |  | 7009 |  |  |  | 741 | [10 empty] | 80.01 |  |  |  | 80.01 | [5 empty] | 81.31 |  |  | 80.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.99 |  |  |  |  | 0.00
2019 |  |  |  | 6376.32 |  |  | 8207 |  |  |  | 741 | [10 empty] | 93.70 |  |  |  | 93.70 | [5 empty] | 98.23 |  |  | 93.69 |  |  |  | 6.30 |  | 6.30 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 6124.63 |  |  | 8001 |  |  |  | 741 | [10 empty] | 91.08 |  |  |  | 91.08 | [5 empty] | 94.10 |  |  | 91.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.92 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1971 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 445
B. |  | Refuelling without maintenance | [20 empty] | 784 | [14 empty] | 16
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1076
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 56
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 0
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 95
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 49
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 28
Subtotal | [22 empty] | 784 | [14 empty] | 1149 |  |  |  | 617 | [11 empty] | 2
Total | [22 empty] | 784 | [14 empty] | 1768
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1971 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 0
12. |  |  | Reactor I&C Systems | [34 empty] | 50
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 45
15. |  |  | Reactor Cooling Systems | [34 empty] | 70
16. |  |  | Steam generation systems | [34 empty] | 104
31. |  |  | Turbine and auxiliaries | [34 empty] | 85
32. |  |  | Feedwater and Main Steam System | [34 empty] | 34
34. |  |  | Miscellaneous Systems | [34 empty] | 73
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 12
42. |  |  | Electrical Power Supply Systems | [34 empty] | 88
Total | [37 empty] | 563
Highlights (2020)
Refueling Outage 32

## SALEM-1
2020 Operating Experience
US-272 | [8 empty] | SALEM-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PSEG (PSEG Nuclear, LLC)
Owner | [7 empty] | : | PSEGPOWR (PSEG Power, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-09-25
Thermal power | [12 empty] | : |  |  | 3459 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-12-25
Gross electrical power | [12 empty] | : |  |  | 1254 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-06-30
Reference unit power (net) | [12 empty] | : |  |  | 1169 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.4 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.85 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7142.17 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 10.22 %
Energy Availability Factor (EAF) | [18 empty] | : | 70.87 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 8.07 %
Unit Capability Factor (UCF) | [18 empty] | : | 70.87 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.05 %
Load Factor (LF) | [18 empty] | : | 69.55 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 70.87 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2559 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 877.80 | 700.41 |  |  |  | 127.05 |  | 846.23 | [8 empty] | 874.32 |  |  | 834.52 | [6 empty] | 841.53 |  | 844.24 |  |  |  | 831.95 |  |  | 48.27 |  |  | -2.89 | [9 empty] | 318.73 |  |  | 7142.17
EAF [%] |  |  |  |  | 100.00 | 85.72 |  |  |  | 18.06 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 6.45 |  |  | 0.00 | [9 empty] | 41.74 |  |  | 70.87
UCF [%] |  |  |  |  | 100.00 | 85.72 |  |  |  | 18.06 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 6.45 |  |  | 0.00 | [9 empty] | 41.74 |  |  | 70.87
LF [%] |  |  |  |  | 100.93 | 86.09 |  |  |  | 14.61 |  | 100.54 | [8 empty] | 100.53 |  |  | 99.15 | [6 empty] | 96.76 |  | 97.07 |  |  |  | 98.84 |  |  | 5.55 |  |  | -0.34 | [9 empty] | 36.65 |  |  | 69.55
OF [%] |  |  |  |  | 100.00 | 85.78 |  |  |  | 17.88 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 6.45 |  |  | 0.00 | [9 empty] | 41.80 |  |  | 70.87
FLR [%] |  |  |  |  | 0.00 | 14.28 |  |  |  | 81.94 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.22
UCL [%] |  |  |  |  | 0.00 | 14.28 |  |  |  | 81.94 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.07
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 93.55 |  |  | 100.00 | [9 empty] | 58.26 |  |  | 21.05
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 307296.94 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 16.54 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.03 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 14.51 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 73.19 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.3 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.58 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.16 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.03 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 3398.20 |  |  | 2432 |  |  |  | 1079 | [10 empty] | 42.77 |  |  |  | 42.77 | [5 empty] | 42.79 |  |  | 54.53 |  |  |  | 56.99 |  | 56.66 | [8 empty] | 0.57 |  |  |  |  | 0.00
1978 |  |  |  | 4537.00 |  |  | 4862 |  |  |  | 1079 | [10 empty] | 48.00 |  |  |  | 48.00 | [5 empty] | 48.00 |  |  | 55.50 |  |  |  | 51.90 |  | 51.80 | [8 empty] | 0.20 |  |  |  |  | 0.00
1979 |  |  |  | 2084.30 |  |  | 2231 |  |  |  | 1079 | [10 empty] | 22.05 |  |  |  | 22.05 | [5 empty] | 22.05 |  |  | 25.47 |  |  |  | 65.71 |  | 42.25 | [8 empty] | 35.70 |  |  |  |  | 0.00
1980 |  |  |  | 5689.80 |  |  | 6075 |  |  |  | 1079 | [10 empty] | 69.47 |  |  |  | 74.22 | [5 empty] | 60.03 |  |  | 69.16 |  |  |  | 5.09 |  | 3.98 | [8 empty] | 21.81 |  |  |  |  | 4.74
1981 |  |  |  | 6191.30 |  |  | 6839 |  |  |  | 1079 | [10 empty] | 78.47 |  |  |  | 78.47 | [5 empty] | 65.50 |  |  | 78.07 |  |  |  | 21.53 |  | 21.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 4107.40 |  |  | 4192 |  |  |  | 1079 | [10 empty] | 46.96 |  |  |  | 46.96 | [5 empty] | 43.46 |  |  | 47.85 |  |  |  | 6.50 |  | 3.27 | [8 empty] | 49.78 |  |  |  |  | 0.00
1983 |  |  |  | 5408.80 |  |  | 5127 |  |  |  | 1079 | [10 empty] | 57.61 |  |  |  | 57.61 | [5 empty] | 57.22 |  |  | 58.53 |  |  |  | 42.39 |  | 42.39 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 2160.15 |  |  | 2378 |  |  |  | 1079 | [10 empty] | 27.08 |  |  |  | 27.08 | [5 empty] | 22.79 |  |  | 27.07 |  |  |  | 61.84 |  | 43.88 | [8 empty] | 29.05 |  |  |  |  | 0.00
1985 |  |  |  | 9007.51 |  |  | 8345 |  |  |  | 1079 | [10 empty] | 95.16 |  |  |  | 95.16 | [5 empty] | 95.30 |  |  | 95.26 |  |  |  | 4.84 |  | 4.84 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 7084.01 |  |  | 6921 |  |  |  | 1083 | [10 empty] | 78.61 |  |  |  | 78.61 | [5 empty] | 74.63 |  |  | 79.01 |  |  |  | 9.85 |  | 8.59 | [8 empty] | 12.81 |  |  |  |  | 0.00
1987 |  |  |  | 6216.61 |  |  | 6362 |  |  |  | 1106 | [10 empty] | 72.64 |  |  |  | 73.08 | [5 empty] | 64.16 |  |  | 72.63 |  |  |  | 2.96 |  | 2.23 | [8 empty] | 24.69 |  |  |  |  | 0.44
1988 |  |  |  | 7418.56 |  |  | 6841 |  |  |  | 1106 | [10 empty] | 77.92 |  |  |  | 77.92 | [5 empty] | 76.36 |  |  | 77.88 |  |  |  | 3.06 |  | 2.46 | [8 empty] | 19.62 |  |  |  |  | 0.00
1989 |  |  |  | 6213.35 |  |  | 6059 |  |  |  | 1106 | [10 empty] | 69.18 |  |  |  | 69.18 | [5 empty] | 64.13 |  |  | 69.17 |  |  |  | 10.69 |  | 8.28 | [8 empty] | 22.53 |  |  |  |  | 0.00
1990 |  |  |  | 5999.21 |  |  | 5868 |  |  |  | 1106 | [10 empty] | 67.01 |  |  |  | 67.01 | [5 empty] | 61.92 |  |  | 66.99 |  |  |  | 32.99 |  | 32.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 6810.28 |  |  | 6479 |  |  |  | 1106 | [10 empty] | 73.96 |  |  |  | 73.96 | [5 empty] | 70.29 |  |  | 73.96 |  |  |  | 4.23 |  | 3.26 | [8 empty] | 22.77 |  |  |  |  | 0.00
1992 |  |  |  | 5307.84 |  |  | 5090 |  |  |  | 1106 | [10 empty] | 57.99 |  |  |  | 57.99 | [5 empty] | 54.63 |  |  | 57.95 |  |  |  | 24.21 |  | 18.52 | [8 empty] | 23.49 |  |  |  |  | 0.00
1993 |  |  |  | 5870.60 |  |  | 5746 |  |  |  | 1106 | [10 empty] | 65.61 |  |  |  | 65.61 | [5 empty] | 60.59 |  |  | 65.59 |  |  |  | 12.61 |  | 9.46 | [8 empty] | 24.93 |  |  |  |  | 0.00
1994 |  |  |  | 5779.31 |  |  | 5865 |  |  |  | 1106 | [10 empty] | 67.04 |  |  |  | 67.04 | [5 empty] | 59.65 |  |  | 66.95 |  |  |  | 25.86 |  | 23.38 | [8 empty] | 9.58 |  |  |  |  | 0.00
1995 |  |  |  | 2554.43 |  |  | 2632 |  |  |  | 1106 | [10 empty] | 30.07 |  |  |  | 30.07 | [5 empty] | 26.37 |  |  | 30.05 |  |  |  | 59.80 |  | 44.73 | [8 empty] | 25.21 |  |  |  |  | 0.00
1996 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1106 | [10 empty] | 0.01 |  |  |  | 0.01 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 99.98 |  | 66.94 | [8 empty] | 33.05 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1106 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 6475.62 |  |  | 6199 |  |  |  | 1106 | [10 empty] | 70.76 |  |  |  | 70.76 | [5 empty] | 66.84 |  |  | 70.76 |  |  |  | 29.24 |  | 29.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 8009.17 |  |  | 7663 |  |  |  | 1106 | [10 empty] | 87.48 |  |  |  | 87.48 | [5 empty] | 82.67 |  |  | 87.48 |  |  |  | 2.21 |  | 1.97 | [8 empty] | 10.55 |  |  |  |  | 0.00
2000 |  |  |  | 8952.64 |  |  | 8328 |  |  |  | 1106 | [10 empty] | 94.81 |  |  |  | 94.81 | [5 empty] | 92.15 |  |  | 94.81 |  |  |  | 4.84 |  | 4.83 | [8 empty] | 0.36 |  |  |  |  | 0.00
2001 |  |  |  | 7709.42 |  |  | 7116 |  |  |  | 1096 | [10 empty] | 80.94 |  |  |  | 80.94 | [5 empty] | 80.83 |  |  | 81.23 |  |  |  | 8.04 |  | 7.07 | [8 empty] | 11.99 |  |  |  |  | 0.00
2002 |  |  |  | 8620.57 |  |  | 7855 |  |  |  | 1096 | [10 empty] | 89.53 |  |  |  | 89.53 | [5 empty] | 89.79 |  |  | 89.67 |  |  |  | 3.23 |  | 2.99 | [8 empty] | 7.49 |  |  |  |  | 0.00
2003 |  |  |  | 9096.68 |  |  | 8401 |  |  |  | 1096 | [10 empty] | 95.85 |  |  |  | 95.85 | [5 empty] | 94.75 |  |  | 95.90 |  |  |  | 4.15 |  | 4.15 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 7452.71 |  |  | 6766 |  |  |  | 1159 | [10 empty] | 77.61 |  |  |  | 77.61 | [5 empty] | 75.24 |  |  | 77.03 |  |  |  | 5.21 |  | 4.27 | [8 empty] | 18.13 |  |  |  |  | 0.00
2005 |  |  |  | 9440.58 |  |  | 8105 |  |  |  | 1111 | [10 empty] | 92.52 |  |  |  | 92.52 | [5 empty] | 97.00 |  |  | 92.52 |  |  |  | 0.60 |  | 0.56 | [8 empty] | 6.92 |  |  |  |  | 0.00
2006 |  |  |  | 10228.09 |  |  | 8725 |  |  |  | 1174 | [10 empty] | 99.60 |  |  |  | 99.60 | [5 empty] | 99.45 |  |  | 99.60 |  |  |  | 0.40 |  | 0.40 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 9158.51 |  |  | 8013 |  |  |  | 1174 | [10 empty] | 91.51 |  |  |  | 91.51 | [5 empty] | 89.05 |  |  | 91.47 |  |  |  | 2.15 |  | 2.01 | [8 empty] | 6.48 |  |  |  |  | 0.00
2008 |  |  |  | 9333.79 |  |  | 8053 |  |  |  | 1174 | [10 empty] | 91.69 |  |  |  | 91.69 | [5 empty] | 90.51 |  |  | 91.68 |  |  |  | 0.17 |  | 0.16 | [8 empty] | 8.15 |  |  |  |  | 0.00
2009 |  |  |  | 10221.76 |  |  | 8735 |  |  |  | 1174 | [10 empty] | 99.72 |  |  |  | 99.72 | [5 empty] | 99.39 |  |  | 99.71 |  |  |  | 0.28 |  | 0.28 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 8776.60 |  |  | 7653 |  |  |  | 1174 | [10 empty] | 87.37 |  |  |  | 87.37 | [5 empty] | 85.34 |  |  | 87.36 |  |  |  | 6.06 |  | 5.63 | [8 empty] | 6.99 |  |  |  |  | 0.00
2011 |  |  |  | 8835.77 |  |  | 7847 |  |  |  | 1174 | [10 empty] | 89.61 |  |  |  | 91.30 | [5 empty] | 85.92 |  |  | 89.58 |  |  |  | 0.46 |  | 0.43 | [8 empty] | 8.28 |  |  |  |  | 1.69
2012 |  |  |  | 9896.78 |  |  | 8472 |  |  |  | 1168 | [10 empty] | 96.48 |  |  |  | 96.48 | [5 empty] | 96.46 |  |  | 96.45 |  |  |  | 3.52 |  | 3.52 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 9124.16 |  |  | 7692 |  |  |  | 1168 | [10 empty] | 87.80 |  |  |  | 87.80 | [5 empty] | 89.17 |  |  | 87.80 |  |  |  | 0.58 |  | 0.52 | [8 empty] | 11.68 |  |  |  |  | 0.00
2014 |  |  |  | 8891.48 |  |  | 7657 |  |  |  | 1168 | [10 empty] | 87.40 |  |  |  | 87.40 | [5 empty] | 86.90 |  |  | 87.41 |  |  |  | 3.51 |  | 3.17 | [8 empty] | 9.42 |  |  |  |  | 0.00
2015 |  |  |  | 9778.02 |  |  | 8593 |  |  |  | 1169 | [10 empty] | 98.09 |  |  |  | 98.09 | [5 empty] | 95.48 |  |  | 98.09 |  |  |  | 1.91 |  | 1.91 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 7002.31 |  |  | 6214 |  |  |  | 1169 | [10 empty] | 70.74 |  |  |  | 70.74 | [5 empty] | 68.19 |  |  | 70.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.26 |  |  |  |  | 0.00
2017 |  |  |  | 9275.70 |  |  | 7964 |  |  |  | 1169 | [10 empty] | 90.92 |  |  |  | 90.92 | [5 empty] | 90.58 |  |  | 90.91 |  |  |  | 0.67 |  | 0.62 | [8 empty] | 8.47 |  |  |  |  | 0.00
2018 |  |  |  | 10204.37 |  |  | 8760 |  |  |  | 1169 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.65 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7990.30 |  |  | 7153 |  |  |  | 1169 | [10 empty] | 81.66 |  |  |  | 81.66 | [5 empty] | 78.03 |  |  | 81.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.34 |  |  |  |  | 0.00
2020 |  |  |  | 7142.17 |  |  | 6225 |  |  |  | 1169 | [10 empty] | 70.87 |  |  |  | 70.87 | [5 empty] | 69.55 |  |  | 70.87 |  |  |  | 10.22 |  | 8.07 | [8 empty] | 21.05 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1977 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1048
B. |  | Refuelling without maintenance | [20 empty] | 1849 | [14 empty] | 43
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 953
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 75
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 113
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 7
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 7
Z. |  | Other | [24 empty] | 709 | [10 empty] | 10 |  |  |  | 97
Subtotal | [22 empty] | 1849 |  |  |  | 709 | [10 empty] | 1082 |  |  |  | 1266 | [11 empty] | 8
Total | [22 empty] | 2558 | [14 empty] | 2356
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1977 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 709 | [14 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 69
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 88
15. |  |  | Reactor Cooling Systems | [34 empty] | 68
16. |  |  | Steam generation systems | [34 empty] | 432
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 183
32. |  |  | Feedwater and Main Steam System | [34 empty] | 89
33. |  |  | Circulating Water System | [34 empty] | 46
34. |  |  | Miscellaneous Systems | [34 empty] | 67
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 85
42. |  |  | Electrical Power Supply Systems | [34 empty] | 49
Total | [22 empty] | 709 | [14 empty] | 1210
Highlights (2020)
1R27 Refueling Outage

## SALEM-2
2020 Operating Experience
US-311 | [8 empty] | SALEM-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PSEG (PSEG Nuclear, LLC)
Owner | [7 empty] | : | PSEGPOWR (PSEG Power, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-09-25
Thermal power | [12 empty] | : |  |  | 3459 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-06-03
Gross electrical power | [12 empty] | : |  |  | 1200 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-10-13
Reference unit power (net) | [12 empty] | : |  |  | 1158 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.4 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.85 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9003.39 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.05 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.41 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.96 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.41 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.63 %
Load Factor (LF) | [18 empty] | : | 88.51 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.4 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 843 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 866.14 | 811.75 |  |  |  | 860.25 |  | 251.85 | [8 empty] | 326.74 |  |  | 824.23 | [6 empty] | 841.90 |  | 818.08 |  |  |  | 827.18 |  |  | 865.22 |  |  | 841.21 | [9 empty] | 868.85 |  |  | 9003.39
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 33.34 | [8 empty] | 51.30 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.41
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 33.34 | [8 empty] | 51.30 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.41
LF [%] |  |  |  |  | 100.53 | 100.72 |  |  |  | 99.85 |  | 30.21 | [8 empty] | 37.92 |  |  | 98.86 | [6 empty] | 97.72 |  | 94.95 |  |  |  | 99.21 |  |  | 100.43 |  |  | 100.89 | [9 empty] | 100.85 |  |  | 88.51
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 33.33 | [8 empty] | 51.34 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.40
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.15 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.05
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.38 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.96
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 66.66 | [8 empty] | 37.32 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.63
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 378149.53 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 14.37 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.98 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.22 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.99 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.79 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.9 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 75.38 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 3009.57 |  |  | 3253 |  |  |  | 1105 | [10 empty] | 96.27 |  |  |  | 96.27 | [5 empty] | 76.89 |  |  | 94.59 |  |  |  | 3.73 |  | 3.73 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 7941.70 |  |  | 8517 |  |  |  | 1106 | [10 empty] | 97.54 |  |  |  | 97.54 | [5 empty] | 81.97 |  |  | 97.23 |  |  |  | 2.46 |  | 2.46 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 775.20 |  |  | 1078 |  |  |  | 1106 | [10 empty] | 12.65 |  |  |  | 12.65 | [5 empty] | 8.00 |  |  | 12.31 |  |  |  | 73.49 |  | 35.06 | [8 empty] | 52.29 |  |  |  |  | 0.00
1984 |  |  |  | 3225.70 |  |  | 3192 |  |  |  | 1106 | [10 empty] | 36.40 |  |  |  | 36.40 | [5 empty] | 33.20 |  |  | 36.34 |  |  |  | 56.61 |  | 47.48 | [8 empty] | 16.12 |  |  |  |  | 0.00
1985 |  |  |  | 5033.76 |  |  | 4923 |  |  |  | 1106 | [10 empty] | 56.22 |  |  |  | 56.22 | [5 empty] | 51.96 |  |  | 56.20 |  |  |  | 41.70 |  | 40.21 | [8 empty] | 3.56 |  |  |  |  | 0.00
1986 |  |  |  | 5317.72 |  |  | 5388 |  |  |  | 1106 | [10 empty] | 61.59 |  |  |  | 61.59 | [5 empty] | 54.89 |  |  | 61.51 |  |  |  | 20.69 |  | 16.06 | [8 empty] | 22.35 |  |  |  |  | 0.00
1987 |  |  |  | 6176.55 |  |  | 6338 |  |  |  | 1106 | [10 empty] | 72.42 |  |  |  | 72.42 | [5 empty] | 63.75 |  |  | 72.35 |  |  |  | 9.33 |  | 7.45 | [8 empty] | 20.12 |  |  |  |  | 0.00
1988 |  |  |  | 5982.17 |  |  | 5838 |  |  |  | 1106 | [10 empty] | 66.50 |  |  |  | 66.50 | [5 empty] | 61.58 |  |  | 66.46 |  |  |  | 33.47 |  | 33.45 | [8 empty] | 0.05 |  |  |  |  | 0.00
1989 |  |  |  | 7824.60 |  |  | 7419 |  |  |  | 1106 | [10 empty] | 84.74 |  |  |  | 84.74 | [5 empty] | 80.76 |  |  | 84.69 |  |  |  | 9.76 |  | 9.17 | [8 empty] | 6.10 |  |  |  |  | 0.00
1990 |  |  |  | 5446.10 |  |  | 5163 |  |  |  | 1106 | [10 empty] | 72.16 |  |  |  | 72.16 | [5 empty] | 56.21 |  |  | 58.94 |  |  |  | 5.68 |  | 4.35 | [8 empty] | 23.49 |  |  |  |  | 0.00
1991 |  |  |  | 7662.34 |  |  | 7188 |  |  |  | 1106 | [10 empty] | 82.05 |  |  |  | 82.05 | [5 empty] | 79.09 |  |  | 82.05 |  |  |  | 15.40 |  | 14.93 | [8 empty] | 3.01 |  |  |  |  | 0.00
1992 |  |  |  | 4744.64 |  |  | 4657 |  |  |  | 1106 | [10 empty] | 53.05 |  |  |  | 53.05 | [5 empty] | 48.84 |  |  | 53.02 |  |  |  | 16.80 |  | 10.71 | [8 empty] | 36.24 |  |  |  |  | 0.00
1993 |  |  |  | 5575.50 |  |  | 5328 |  |  |  | 1106 | [10 empty] | 60.87 |  |  |  | 60.87 | [5 empty] | 57.55 |  |  | 60.82 |  |  |  | 20.37 |  | 15.57 | [8 empty] | 23.56 |  |  |  |  | 0.00
1994 |  |  |  | 5606.78 |  |  | 6076 |  |  |  | 1106 | [10 empty] | 69.43 |  |  |  | 69.43 | [5 empty] | 57.87 |  |  | 69.36 |  |  |  | 5.75 |  | 4.24 | [8 empty] | 26.34 |  |  |  |  | 0.00
1995 |  |  |  | 2071.74 |  |  | 2261 |  |  |  | 1106 | [10 empty] | 25.83 |  |  |  | 25.83 | [5 empty] | 21.38 |  |  | 25.81 |  |  |  | 65.33 |  | 48.69 | [8 empty] | 25.48 |  |  |  |  | 0.00
1996 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1106 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 91.53 | [8 empty] | 8.47 |  |  |  |  | 0.00
1997 |  |  |  | 2564.28 |  |  | 2834 |  |  |  | 1106 | [10 empty] | 32.37 |  |  |  | 32.37 | [5 empty] | 26.47 |  |  | 32.35 |  |  |  | 67.63 |  | 67.63 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 7797.25 |  |  | 7287 |  |  |  | 1106 | [10 empty] | 83.18 |  |  |  | 83.18 | [5 empty] | 80.48 |  |  | 83.18 |  |  |  | 15.42 |  | 15.17 | [8 empty] | 1.64 |  |  |  |  | 0.00
1999 |  |  |  | 7949.39 |  |  | 7431 |  |  |  | 1106 | [10 empty] | 84.83 |  |  |  | 84.83 | [5 empty] | 82.05 |  |  | 84.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.17 |  |  |  |  | 0.00
2000 |  |  |  | 8381.72 |  |  | 7819 |  |  |  | 1106 | [10 empty] | 89.01 |  |  |  | 89.01 | [5 empty] | 86.28 |  |  | 89.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.99 |  |  |  |  | 0.00
2001 |  |  |  | 9517.60 |  |  | 8736 |  |  |  | 1092 | [10 empty] | 99.72 |  |  |  | 99.72 | [5 empty] | 99.97 |  |  | 99.73 |  |  |  | 0.28 |  | 0.28 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 8367.43 |  |  | 7620 |  |  |  | 1092 | [10 empty] | 86.77 |  |  |  | 86.77 | [5 empty] | 87.47 |  |  | 86.99 |  |  |  | 1.68 |  | 1.49 | [8 empty] | 11.74 |  |  |  |  | 0.00
2003 |  |  |  | 8095.61 |  |  | 7355 |  |  |  | 1116 | [10 empty] | 83.73 |  |  |  | 83.73 | [5 empty] | 84.47 |  |  | 83.96 |  |  |  | 3.24 |  | 2.80 | [8 empty] | 13.47 |  |  |  |  | 0.00
2004 |  |  |  | 8799.76 |  |  | 7945 |  |  |  | 1116 | [10 empty] | 90.34 |  |  |  | 90.34 | [5 empty] | 89.77 |  |  | 90.45 |  |  |  | 9.60 |  | 9.59 | [8 empty] | 0.07 |  |  |  |  | 0.00
2005 |  |  |  | 8886.03 |  |  | 7897 |  |  |  | 1129 | [10 empty] | 90.15 |  |  |  | 90.15 | [5 empty] | 89.84 |  |  | 90.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.85 |  |  |  |  | 0.00
2006 |  |  |  | 9147.38 |  |  | 8220 |  |  |  | 1130 | [10 empty] | 93.86 |  |  |  | 93.86 | [5 empty] | 92.41 |  |  | 93.84 |  |  |  | 0.29 |  | 0.28 | [8 empty] | 5.87 |  |  |  |  | 0.00
2007 |  |  |  | 9669.39 |  |  | 8506 |  |  |  | 1130 | [10 empty] | 97.12 |  |  |  | 97.12 | [5 empty] | 97.68 |  |  | 97.10 |  |  |  | 2.88 |  | 2.88 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8222.00 |  |  | 7285 |  |  |  | 1156 | [10 empty] | 82.82 |  |  |  | 82.82 | [5 empty] | 81.58 |  |  | 82.93 |  |  |  | 1.50 |  | 1.26 | [8 empty] | 15.92 |  |  |  |  | 0.00
2009 |  |  |  | 9427.50 |  |  | 8069 |  |  |  | 1158 | [10 empty] | 92.15 |  |  |  | 92.15 | [5 empty] | 92.94 |  |  | 92.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.85 |  |  |  |  | 0.00
2010 |  |  |  | 9954.77 |  |  | 8620 |  |  |  | 1158 | [10 empty] | 98.41 |  |  |  | 98.41 | [5 empty] | 98.13 |  |  | 98.40 |  |  |  | 1.59 |  | 1.59 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 9162.79 |  |  | 7863 |  |  |  | 1158 | [10 empty] | 89.78 |  |  |  | 89.78 | [5 empty] | 90.33 |  |  | 89.76 |  |  |  | 2.62 |  | 2.41 | [8 empty] | 7.81 |  |  |  |  | 0.00
2012 |  |  |  | 8758.57 |  |  | 7813 |  |  |  | 1158 | [10 empty] | 89.19 |  |  |  | 89.19 | [5 empty] | 86.11 |  |  | 88.95 |  |  |  | 1.49 |  | 1.35 | [8 empty] | 9.46 |  |  |  |  | 0.00
2013 |  |  |  | 10262.83 |  |  | 8760 |  |  |  | 1158 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.16 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 7490.46 |  |  | 6488 |  |  |  | 1158 | [10 empty] | 74.06 |  |  |  | 74.06 | [5 empty] | 73.84 |  |  | 74.06 |  |  |  | 0.74 |  | 18.14 | [8 empty] | 7.80 |  |  |  |  | 0.00
2015 |  |  |  | 8892.07 |  |  | 7710 |  |  |  | 1158 | [10 empty] | 88.02 |  |  |  | 88.02 | [5 empty] | 87.66 |  |  | 88.01 |  |  |  | 1.13 |  | 1.00 | [8 empty] | 10.98 |  |  |  |  | 0.00
2016 |  |  |  | 8773.17 |  |  | 7661 |  |  |  | 1158 | [10 empty] | 87.22 |  |  |  | 87.22 | [5 empty] | 86.25 |  |  | 87.22 |  |  |  | 12.78 |  | 12.78 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 8774.68 |  |  | 7617 |  |  |  | 1158 | [10 empty] | 86.96 |  |  |  | 86.96 | [5 empty] | 86.50 |  |  | 86.95 |  |  |  | 0.45 |  | 0.40 | [8 empty] | 12.64 |  |  |  |  | 0.00
2018 |  |  |  | 8761.52 |  |  | 7844 |  |  |  | 1158 | [10 empty] | 89.75 |  |  |  | 89.75 | [5 empty] | 86.37 |  |  | 89.54 |  |  |  | 1.54 |  | 1.40 | [8 empty] | 8.85 |  |  |  |  | 0.00
2019 |  |  |  | 9999.01 |  |  | 8649 |  |  |  | 1158 | [10 empty] | 98.75 |  |  |  | 99.13 | [5 empty] | 98.57 |  |  | 98.73 |  |  |  | 0.87 |  | 0.87 | [8 empty] | 0.00 |  |  |  |  | 0.38
2020 |  |  |  | 9003.39 |  |  | 7941 |  |  |  | 1158 | [10 empty] | 90.41 |  |  |  | 90.41 | [5 empty] | 88.51 |  |  | 90.40 |  |  |  | 1.05 |  | 0.96 | [8 empty] | 8.63 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 902
B. |  | Refuelling without maintenance | [20 empty] | 758 | [14 empty] | 19
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 848
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 80
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 219
L. |  | Human factor related | [39 empty] | 6
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 5
Z. |  | Other | [24 empty] | 85 | [10 empty] | 3 |  |  |  | 22
Subtotal | [22 empty] | 758 |  |  |  | 85 | [10 empty] | 950 |  |  |  | 1149 | [11 empty] | 5
Total | [22 empty] | 843 | [14 empty] | 2104
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 203
12. |  |  | Reactor I&C Systems | [34 empty] | 47
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 40
15. |  |  | Reactor Cooling Systems | [34 empty] | 104
16. |  |  | Steam generation systems | [34 empty] | 150
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 79
32. |  |  | Feedwater and Main Steam System | [34 empty] | 99
33. |  |  | Circulating Water System | [34 empty] | 15
34. |  |  | Miscellaneous Systems | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 208
42. |  |  | Electrical Power Supply Systems | [34 empty] | 164
Total | [37 empty] | 1127
Highlights (2020)
Refueling Outage 24 (2R24)

## SEABROOK-1
2020 Operating Experience
US-443 | [8 empty] | SEABROOK-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NEXTERA (NextEra Energy Resources, LLC )
Owner | [7 empty] | : | NEXTERA (NextEra Energy Resources, LLC )
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-07-07
Thermal power | [12 empty] | : |  |  | 3648 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-05-29
Gross electrical power | [12 empty] | : |  |  | 1296 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-08-19
Reference unit power (net) | [12 empty] | : |  |  | 1246 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.37
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.14
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.18 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 57 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9865.2 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.72 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.96 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.67 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.96 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.36 %
Load Factor (LF) | [18 empty] | : | 90.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.63 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 823 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 928.05 | 868.31 |  |  |  | 917.65 |  | 56.21 | [8 empty] | 855.39 |  |  | 732.89 | [6 empty] | 927.49 |  | 926.70 |  |  |  | 896.51 |  |  | 928.34 |  |  | 899.42 | [9 empty] | 928.23 |  |  | 9865.20
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 10.16 | [8 empty] | 92.21 |  |  | 99.86 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.96
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 10.16 | [8 empty] | 92.21 |  |  | 99.86 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.96
LF [%] |  |  |  |  | 100.11 | 100.13 |  |  |  | 98.99 |  | 6.27 | [8 empty] | 92.27 |  |  | 81.69 | [6 empty] | 100.05 |  | 99.97 |  |  |  | 99.93 |  |  | 100.14 |  |  | 100.26 | [9 empty] | 100.13 |  |  | 90.14
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 10.14 | [8 empty] | 92.20 |  |  | 83.75 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.63
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.79 |  |  | 0.14 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.72
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.79 |  |  | 0.14 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.67
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 89.84 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.36
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 280516.3 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.56 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.86 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.95 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.72 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.42 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.09 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.69 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 4094.00 |  |  | 4125 |  |  |  | 1151 | [10 empty] | 84.94 |  |  |  | 84.94 | [5 empty] | 82.11 |  |  | 84.94 |  |  |  | 15.06 |  | 15.06 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 6814.38 |  |  | 6394 |  |  |  | 1150 | [10 empty] | 73.00 |  |  |  | 73.00 | [5 empty] | 67.64 |  |  | 72.99 |  |  |  | 6.00 |  | 4.66 | [8 empty] | 22.34 |  |  |  |  | 0.00
1992 |  |  |  | 7868.44 |  |  | 7056 |  |  |  | 1150 | [10 empty] | 80.26 |  |  |  | 80.26 | [5 empty] | 77.89 |  |  | 80.33 |  |  |  | 1.29 |  | 1.05 | [8 empty] | 18.69 |  |  |  |  | 0.00
1993 |  |  |  | 9046.81 |  |  | 8094 |  |  |  | 1150 | [10 empty] | 92.39 |  |  |  | 92.39 | [5 empty] | 89.80 |  |  | 92.40 |  |  |  | 7.61 |  | 7.61 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 6203.50 |  |  | 5466 |  |  |  | 1150 | [10 empty] | 62.28 |  |  |  | 62.28 | [5 empty] | 61.58 |  |  | 62.40 |  |  |  | 9.22 |  | 6.33 | [8 empty] | 31.39 |  |  |  |  | 0.00
1995 |  |  |  | 8380.64 |  |  | 7465 |  |  |  | 1150 | [10 empty] | 85.18 |  |  |  | 85.18 | [5 empty] | 83.14 |  |  | 85.22 |  |  |  | 5.01 |  | 4.49 | [8 empty] | 10.32 |  |  |  |  | 0.00
1996 |  |  |  | 9844.19 |  |  | 8690 |  |  |  | 1158 | [10 empty] | 98.96 |  |  |  | 98.96 | [5 empty] | 96.78 |  |  | 98.93 |  |  |  | 1.04 |  | 1.04 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 7945.70 |  |  | 6929 |  |  |  | 1158 | [10 empty] | 79.18 |  |  |  | 79.18 | [5 empty] | 78.33 |  |  | 79.10 |  |  |  | 8.32 |  | 7.18 | [8 empty] | 13.64 |  |  |  |  | 0.00
1998 |  |  |  | 8388.43 |  |  | 7294 |  |  |  | 1158 | [10 empty] | 83.33 |  |  |  | 83.33 | [5 empty] | 82.69 |  |  | 83.26 |  |  |  | 16.67 |  | 16.67 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 8685.71 |  |  | 7564 |  |  |  | 1156 | [10 empty] | 86.33 |  |  |  | 86.33 | [5 empty] | 85.77 |  |  | 86.35 |  |  |  | 0.62 |  | 0.54 | [8 empty] | 13.13 |  |  |  |  | 0.00
2000 |  |  |  | 7921.49 |  |  | 6910 |  |  |  | 1155 | [10 empty] | 78.66 |  |  |  | 78.66 | [5 empty] | 78.08 |  |  | 78.67 |  |  |  | 2.05 |  | 1.64 | [8 empty] | 19.69 |  |  |  |  | 0.00
2001 |  |  |  | 8692.24 |  |  | 7703 |  |  |  | 1155 | [10 empty] | 87.89 |  |  |  | 90.59 | [5 empty] | 85.91 |  |  | 87.93 |  |  |  | 1.82 |  | 1.68 | [8 empty] | 7.73 |  |  |  |  | 2.70
2002 |  |  |  | 9293.37 |  |  | 8083 |  |  |  | 1155 | [10 empty] | 92.24 |  |  |  | 92.24 | [5 empty] | 91.85 |  |  | 92.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.76 |  |  |  |  | 0.00
2003 |  |  |  | 9275.43 |  |  | 8121 |  |  |  | 1155 | [10 empty] | 92.68 |  |  |  | 92.68 | [5 empty] | 91.67 |  |  | 92.71 |  |  |  | 0.48 |  | 0.45 | [8 empty] | 6.88 |  |  |  |  | 0.00
2004 |  |  |  | 10176.97 |  |  | 8784 |  |  |  | 1155 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.31 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 9455.21 |  |  | 7928 |  |  |  | 1159 | [10 empty] | 90.52 |  |  |  | 90.52 | [5 empty] | 93.12 |  |  | 90.49 |  |  |  | 0.72 |  | 0.65 | [8 empty] | 8.83 |  |  |  |  | 0.00
2006 |  |  |  | 9397.40 |  |  | 7718 |  |  |  | 1244 | [10 empty] | 87.94 |  |  |  | 87.94 | [5 empty] | 87.58 |  |  | 88.11 |  |  |  | 1.02 |  | 0.90 | [8 empty] | 11.16 |  |  |  |  | 0.00
2007 |  |  |  | 10763.88 |  |  | 8669 |  |  |  | 1245 | [10 empty] | 99.00 |  |  |  | 99.00 | [5 empty] | 98.70 |  |  | 98.96 |  |  |  | 1.00 |  | 1.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 9349.64 |  |  | 7596 |  |  |  | 1245 | [10 empty] | 86.49 |  |  |  | 86.49 | [5 empty] | 85.49 |  |  | 86.48 |  |  |  | 3.62 |  | 3.25 | [8 empty] | 10.26 |  |  |  |  | 0.00
2009 |  |  |  | 8816.67 |  |  | 7326 |  |  |  | 1245 | [10 empty] | 83.65 |  |  |  | 83.65 | [5 empty] | 80.84 |  |  | 83.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.35 |  |  |  |  | 0.00
2010 |  |  |  | 10910.05 |  |  | 8760 |  |  |  | 1247 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.87 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8361.74 |  |  | 6959 |  |  |  | 1247 | [10 empty] | 79.46 |  |  |  | 79.46 | [5 empty] | 76.55 |  |  | 79.44 |  |  |  | 7.19 |  | 6.15 | [8 empty] | 14.38 |  |  |  |  | 0.00
2012 |  |  |  | 8188.86 |  |  | 7689 |  |  |  | 1246 | [10 empty] | 87.55 |  |  |  | 87.55 | [5 empty] | 74.82 |  |  | 87.53 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 12.30 |  |  |  |  | 0.00
2013 |  |  |  | 10926.11 |  |  | 8760 |  |  |  | 1246 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.09 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 10167.58 |  |  | 8190 |  |  |  | 1246 | [10 empty] | 93.49 |  |  |  | 93.49 | [5 empty] | 93.15 |  |  | 93.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.51 |  |  |  |  | 0.00
2015 |  |  |  | 9483.63 |  |  | 7705 |  |  |  | 1246 | [10 empty] | 87.96 |  |  |  | 87.96 | [5 empty] | 86.89 |  |  | 87.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.04 |  |  |  |  | 0.00
2016 |  |  |  | 10760.55 |  |  | 8667 |  |  |  | 1246 | [10 empty] | 98.67 |  |  |  | 98.67 | [5 empty] | 98.32 |  |  | 98.67 |  |  |  | 1.33 |  | 1.33 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 9990.27 |  |  | 8033 |  |  |  | 1246 | [10 empty] | 91.70 |  |  |  | 91.70 | [5 empty] | 91.53 |  |  | 91.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.30 |  |  |  |  | 0.00
2018 |  |  |  | 10061.27 |  |  | 8093 |  |  |  | 1246 | [10 empty] | 92.38 |  |  |  | 92.38 | [5 empty] | 92.18 |  |  | 92.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.62 |  |  |  |  | 0.00
2019 |  |  |  | 10906.28 |  |  | 8760 |  |  |  | 1246 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.92 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9865.20 |  |  | 7961 |  |  |  | 1246 | [10 empty] | 91.96 |  |  |  | 91.96 | [5 empty] | 90.14 |  |  | 90.63 |  |  |  | 0.72 |  | 0.67 | [8 empty] | 7.36 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1990 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 215
B. |  | Refuelling without maintenance | [20 empty] | 647 | [14 empty] | 21
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 731
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 22
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 8
Z. |  | Other | [24 empty] | 175 | [10 empty] | 0 |  |  |  | 8
Subtotal | [22 empty] | 647 |  |  |  | 175 | [10 empty] | 775 |  |  |  | 227 | [11 empty] | 8
Total | [22 empty] | 822 | [14 empty] | 1010
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1990 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 4
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 57
15. |  |  | Reactor Cooling Systems | [34 empty] | 28
16. |  |  | Steam generation systems | [34 empty] | 0
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 26
32. |  |  | Feedwater and Main Steam System | [34 empty] | 30
35. |  |  | All other I&C Systems | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 30
42. |  |  | Electrical Power Supply Systems | [34 empty] | 26
Total | [37 empty] | 218
Highlights (2020)
Refueling Outage 20.

## SEQUOYAH-1
2020 Operating Experience
US-327 | [8 empty] | SEQUOYAH-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVA (Tennessee Valley Authority)
Owner | [7 empty] | : | TVA (Tennessee Valley Authority)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (ICECND) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-05-27
Thermal power | [12 empty] | : |  |  | 3455 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-07-22
Gross electrical power | [12 empty] | : |  |  | 1221 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-07-01
Reference unit power (net) | [12 empty] | : |  |  | 1152 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.82
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.84
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 37 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.85
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.85 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9846.77 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.99 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.22 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.98 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.22 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.79 %
Load Factor (LF) | [18 empty] | : | 97.31 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 98.21 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 157 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 764.14 | 807.95 |  |  |  | 862.76 |  | 834.78 | [8 empty] | 745.49 |  |  | 822.29 | [6 empty] | 822.34 |  | 814.81 |  |  |  | 814.78 |  |  | 856.71 |  |  | 835.53 | [9 empty] | 865.19 |  |  | 9846.77
EAF [%] |  |  |  |  | 90.63 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 88.38 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.22
UCF [%] |  |  |  |  | 90.63 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 88.38 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.22
LF [%] |  |  |  |  | 89.16 | 100.77 |  |  |  | 100.66 |  | 100.64 | [8 empty] | 86.98 |  |  | 99.14 | [6 empty] | 95.95 |  | 95.07 |  |  |  | 98.23 |  |  | 99.96 |  |  | 100.73 | [9 empty] | 100.94 |  |  | 97.31
OF [%] |  |  |  |  | 90.59 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 88.44 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.21
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.62 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.99
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.62 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.98
PUF [%] |  |  |  |  | 9.37 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.79
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 343361.7 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 14.69 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.06 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.27 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.1 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.63 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.11 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.79 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 4806.21 |  |  | 4984 |  |  |  | 1128 | [10 empty] | 62.10 |  |  |  | 62.10 | [5 empty] | 50.72 |  |  | 60.86 |  |  |  | 17.60 |  | 13.26 | [8 empty] | 24.64 |  |  |  |  | 0.00
1982 |  |  |  | 4909.70 |  |  | 4626 |  |  |  | 1128 | [10 empty] | 53.36 |  |  |  | 53.36 | [5 empty] | 49.69 |  |  | 52.81 |  |  |  | 23.05 |  | 15.99 | [8 empty] | 30.65 |  |  |  |  | 0.00
1983 |  |  |  | 7340.90 |  |  | 6791 |  |  |  | 1139 | [10 empty] | 78.25 |  |  |  | 78.25 | [5 empty] | 73.57 |  |  | 77.52 |  |  |  | 17.49 |  | 16.58 | [8 empty] | 5.17 |  |  |  |  | 0.00
1984 |  |  |  | 6104.70 |  |  | 5992 |  |  |  | 1148 | [10 empty] | 69.06 |  |  |  | 69.06 | [5 empty] | 60.54 |  |  | 68.21 |  |  |  | 18.75 |  | 15.94 | [8 empty] | 15.00 |  |  |  |  | 0.00
1985 |  |  |  | 4076.07 |  |  | 3760 |  |  |  | 1148 | [10 empty] | 44.68 |  |  |  | 44.68 | [5 empty] | 40.53 |  |  | 42.92 |  |  |  | 17.01 |  | 9.16 | [8 empty] | 46.16 |  |  |  |  | 0.00
1986 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1148 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1148 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 127.69 |  |  | 282 |  |  |  | 1148 | [10 empty] | 6.35 |  |  |  | 6.35 | [5 empty] | 1.27 |  |  | 3.21 |  |  |  | 93.58 |  | 92.57 | [8 empty] | 1.09 |  |  |  |  | 0.00
1989 |  |  |  | 9550.60 |  |  | 8624 |  |  |  | 1148 | [10 empty] | 98.52 |  |  |  | 98.52 | [5 empty] | 94.97 |  |  | 98.45 |  |  |  | 1.48 |  | 1.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 6840.68 |  |  | 6406 |  |  |  | 1148 | [10 empty] | 73.99 |  |  |  | 73.99 | [5 empty] | 68.02 |  |  | 73.13 |  |  |  | 7.02 |  | 5.59 | [8 empty] | 20.42 |  |  |  |  | 0.00
1991 |  |  |  | 7270.13 |  |  | 6774 |  |  |  | 1122 | [10 empty] | 77.56 |  |  |  | 77.56 | [5 empty] | 73.97 |  |  | 77.33 |  |  |  | 2.14 |  | 1.70 | [8 empty] | 20.74 |  |  |  |  | 0.00
1992 |  |  |  | 8402.49 |  |  | 7734 |  |  |  | 1122 | [10 empty] | 88.20 |  |  |  | 88.20 | [5 empty] | 85.26 |  |  | 88.05 |  |  |  | 11.80 |  | 11.80 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 1290.51 |  |  | 1219 |  |  |  | 1122 | [10 empty] | 14.77 |  |  |  | 14.77 | [5 empty] | 13.13 |  |  | 13.92 |  |  |  | 85.23 |  | 85.23 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 6111.64 |  |  | 5774 |  |  |  | 1111 | [10 empty] | 65.97 |  |  |  | 65.97 | [5 empty] | 62.80 |  |  | 65.91 |  |  |  | 5.91 |  | 4.14 | [8 empty] | 29.89 |  |  |  |  | 0.00
1995 |  |  |  | 6829.49 |  |  | 6620 |  |  |  | 1111 | [10 empty] | 75.64 |  |  |  | 75.64 | [5 empty] | 70.17 |  |  | 75.57 |  |  |  | 8.20 |  | 6.76 | [8 empty] | 17.60 |  |  |  |  | 0.00
1996 |  |  |  | 9293.49 |  |  | 8344 |  |  |  | 1112 | [10 empty] | 95.07 |  |  |  | 95.07 | [5 empty] | 95.10 |  |  | 94.99 |  |  |  | 1.05 |  | 1.01 | [8 empty] | 3.92 |  |  |  |  | 0.00
1997 |  |  |  | 8324.30 |  |  | 7486 |  |  |  | 1117 | [10 empty] | 85.54 |  |  |  | 85.54 | [5 empty] | 85.07 |  |  | 85.46 |  |  |  | 0.44 |  | 0.37 | [8 empty] | 14.09 |  |  |  |  | 0.00
1998 |  |  |  | 8905.68 |  |  | 7966 |  |  |  | 1118 | [10 empty] | 91.02 |  |  |  | 91.02 | [5 empty] | 90.91 |  |  | 90.94 |  |  |  | 1.08 |  | 0.99 | [8 empty] | 7.99 |  |  |  |  | 0.00
1999 |  |  |  | 9986.98 |  |  | 8760 |  |  |  | 1122 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.61 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 7720.48 |  |  | 6988 |  |  |  | 1122 | [10 empty] | 79.53 |  |  |  | 79.53 | [5 empty] | 78.34 |  |  | 79.55 |  |  |  | 14.83 |  | 13.85 | [8 empty] | 6.63 |  |  |  |  | 0.00
2001 |  |  |  | 9018.99 |  |  | 7988 |  |  |  | 1122 | [10 empty] | 91.21 |  |  |  | 91.21 | [5 empty] | 91.76 |  |  | 91.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.79 |  |  |  |  | 0.00
2002 |  |  |  | 9953.53 |  |  | 8760 |  |  |  | 1125 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.07 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 7351.13 |  |  | 6443 |  |  |  | 1125 | [10 empty] | 73.61 |  |  |  | 73.61 | [5 empty] | 74.59 |  |  | 73.55 |  |  |  | 1.46 |  | 1.09 | [8 empty] | 25.30 |  |  |  |  | 0.00
2004 |  |  |  | 9290.48 |  |  | 8027 |  |  |  | 1148 | [10 empty] | 91.39 |  |  |  | 91.39 | [5 empty] | 92.13 |  |  | 91.38 |  |  |  | 1.42 |  | 1.32 | [8 empty] | 7.30 |  |  |  |  | 0.00
2005 |  |  |  | 10076.53 |  |  | 8658 |  |  |  | 1150 | [10 empty] | 98.84 |  |  |  | 98.84 | [5 empty] | 100.01 |  |  | 98.82 |  |  |  | 1.16 |  | 1.16 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 9086.03 |  |  | 7915 |  |  |  | 1150 | [10 empty] | 90.37 |  |  |  | 90.37 | [5 empty] | 90.19 |  |  | 90.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.63 |  |  |  |  | 0.00
2007 |  |  |  | 8758.29 |  |  | 7668 |  |  |  | 1148 | [10 empty] | 87.52 |  |  |  | 87.52 | [5 empty] | 87.09 |  |  | 87.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.48 |  |  |  |  | 0.00
2008 |  |  |  | 10164.80 |  |  | 8738 |  |  |  | 1148 | [10 empty] | 99.49 |  |  |  | 99.49 | [5 empty] | 100.80 |  |  | 99.48 |  |  |  | 0.51 |  | 0.51 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 8962.17 |  |  | 7820 |  |  |  | 1148 | [10 empty] | 89.29 |  |  |  | 89.29 | [5 empty] | 89.12 |  |  | 89.27 |  |  |  | 2.49 |  | 2.28 | [8 empty] | 8.42 |  |  |  |  | 0.00
2010 |  |  |  | 8464.09 |  |  | 7524 |  |  |  | 1152 | [10 empty] | 85.95 |  |  |  | 85.95 | [5 empty] | 83.87 |  |  | 85.89 |  |  |  | 1.83 |  | 1.60 | [8 empty] | 12.45 |  |  |  |  | 0.00
2011 |  |  |  | 9888.54 |  |  | 8636 |  |  |  | 1152 | [10 empty] | 98.61 |  |  |  | 98.61 | [5 empty] | 97.99 |  |  | 98.58 |  |  |  | 1.39 |  | 1.39 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 8945.17 |  |  | 7907 |  |  |  | 1152 | [10 empty] | 90.04 |  |  |  | 90.04 | [5 empty] | 88.40 |  |  | 90.02 |  |  |  | 0.49 |  | 0.45 | [8 empty] | 9.52 |  |  |  |  | 0.00
2013 |  |  |  | 8805.63 |  |  | 7834 |  |  |  | 1152 | [10 empty] | 89.43 |  |  |  | 89.43 | [5 empty] | 87.25 |  |  | 89.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.57 |  |  |  |  | 0.00
2014 |  |  |  | 10051.76 |  |  | 8760 |  |  |  | 1152 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.61 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 7771.73 |  |  | 7196 |  |  |  | 1152 | [10 empty] | 82.15 |  |  |  | 82.15 | [5 empty] | 77.01 |  |  | 82.15 |  |  |  | 9.05 |  | 8.17 | [8 empty] | 9.68 |  |  |  |  | 0.00
2016 |  |  |  | 7673.62 |  |  | 6783 |  |  |  | 1152 | [10 empty] | 77.22 |  |  |  | 77.22 | [5 empty] | 75.83 |  |  | 77.22 |  |  |  | 14.35 |  | 12.94 | [8 empty] | 9.84 |  |  |  |  | 0.00
2017 |  |  |  | 9378.86 |  |  | 8420 |  |  |  | 1152 | [10 empty] | 96.11 |  |  |  | 96.11 | [5 empty] | 92.94 |  |  | 96.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.89 |  |  |  |  | 0.00
2018 |  |  |  | 8916.87 |  |  | 7858 |  |  |  | 1152 | [10 empty] | 89.70 |  |  |  | 91.23 | [5 empty] | 88.36 |  |  | 89.70 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 8.46 |  |  |  |  | 1.53
2019 |  |  |  | 8189.64 |  |  | 7523 |  |  |  | 1152 | [10 empty] | 85.90 |  |  |  | 85.90 | [5 empty] | 81.15 |  |  | 85.88 |  |  |  | 1.58 |  | 1.38 | [8 empty] | 12.72 |  |  |  |  | 0.00
2020 |  |  |  | 9846.77 |  |  | 8627 |  |  |  | 1152 | [10 empty] | 98.22 |  |  |  | 98.22 | [5 empty] | 97.31 |  |  | 98.21 |  |  |  | 0.99 |  | 0.98 | [8 empty] | 0.79 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1981 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 507
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 773
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 70 | [14 empty] | 46
E. |  | Testing of plant systems or components | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 231
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 18
P. |  | Fire | [39 empty] | 3
Z. |  | Other | [24 empty] | 86 | [10 empty] | 35 |  |  |  | 415
Subtotal | [22 empty] | 70 |  |  |  | 86 | [10 empty] | 855 |  |  |  | 1174 | [11 empty] | 3
Total | [22 empty] | 156 | [14 empty] | 2032
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1981 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 18
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 28
15. |  |  | Reactor Cooling Systems | [34 empty] | 42
16. |  |  | Steam generation systems | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 35
32. |  |  | Feedwater and Main Steam System | [34 empty] | 222
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 112
42. |  |  | Electrical Power Supply Systems | [34 empty] | 30
Total | [37 empty] | 508
Highlights (2020)
EHC Turbine Control Maintenance

## SEQUOYAH-2
2020 Operating Experience
US-328 | [8 empty] | SEQUOYAH-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVA (Tennessee Valley Authority)
Owner | [7 empty] | : | TVA (Tennessee Valley Authority)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (ICECND) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-05-27
Thermal power | [12 empty] | : |  |  | 3455 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-12-23
Gross electrical power | [12 empty] | : |  |  | 1200 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1982-06-01
Reference unit power (net) | [12 empty] | : |  |  | 1139 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.82
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.84
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 37 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.85
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.85 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9252.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.33 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.24 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.31 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.24 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.45 %
Load Factor (LF) | [18 empty] | : | 92.48 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.24 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 594 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 859.17 | 804.82 |  |  |  | 831.40 |  | 222.56 | [8 empty] | 693.35 |  |  | 820.23 | [6 empty] | 833.45 |  | 829.67 |  |  |  | 811.25 |  |  | 853.02 |  |  | 832.31 | [9 empty] | 861.20 |  |  | 9252.42
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 33.30 | [8 empty] | 84.76 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.24
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 33.30 | [8 empty] | 84.76 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.24
LF [%] |  |  |  |  | 101.39 | 101.52 |  |  |  | 98.11 |  | 27.14 | [8 empty] | 81.82 |  |  | 100.02 | [6 empty] | 98.35 |  | 97.91 |  |  |  | 98.92 |  |  | 100.66 |  |  | 101.49 | [9 empty] | 101.63 |  |  | 92.48
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 33.33 | [8 empty] | 84.81 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.24
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.17 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.33
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.69 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.31
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 66.70 | [8 empty] | 11.55 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.45
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 306250.64 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 12.32 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.4 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.4 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.31 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.23 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.34 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1982 |  |  |  | 5207.56 |  |  | 5881 |  |  |  | 1145 | [10 empty] | 75.00 |  |  |  | 75.00 | [5 empty] | 66.75 |  |  | 74.05 |  |  |  | 17.32 |  | 15.71 | [8 empty] | 9.29 |  |  |  |  | 0.00
1983 |  |  |  | 6691.40 |  |  | 6346 |  |  |  | 1133 | [10 empty] | 72.76 |  |  |  | 72.76 | [5 empty] | 67.42 |  |  | 72.44 |  |  |  | 3.72 |  | 2.81 | [8 empty] | 24.42 |  |  |  |  | 0.00
1984 |  |  |  | 6403.27 |  |  | 6112 |  |  |  | 1148 | [10 empty] | 69.82 |  |  |  | 69.82 | [5 empty] | 63.50 |  |  | 69.58 |  |  |  | 7.23 |  | 5.44 | [8 empty] | 24.74 |  |  |  |  | 0.00
1985 |  |  |  | 5624.97 |  |  | 5223 |  |  |  | 1148 | [10 empty] | 59.80 |  |  |  | 59.80 | [5 empty] | 55.93 |  |  | 59.62 |  |  |  | 40.16 |  | 40.13 | [8 empty] | 0.07 |  |  |  |  | 0.00
1986 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1148 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1148 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 3934.70 |  |  | 5097 |  |  |  | 1148 | [10 empty] | 59.44 |  |  |  | 59.44 | [5 empty] | 39.02 |  |  | 58.03 |  |  |  | 40.55 |  | 40.55 | [8 empty] | 0.02 |  |  |  |  | 0.00
1989 |  |  |  | 6067.70 |  |  | 6103 |  |  |  | 1148 | [10 empty] | 70.71 |  |  |  | 70.71 | [5 empty] | 60.34 |  |  | 69.67 |  |  |  | 5.97 |  | 4.49 | [8 empty] | 24.80 |  |  |  |  | 0.00
1990 |  |  |  | 7185.46 |  |  | 6864 |  |  |  | 1148 | [10 empty] | 79.14 |  |  |  | 79.14 | [5 empty] | 71.45 |  |  | 78.36 |  |  |  | 1.29 |  | 1.03 | [8 empty] | 19.83 |  |  |  |  | 0.00
1991 |  |  |  | 9318.89 |  |  | 8482 |  |  |  | 1122 | [10 empty] | 96.88 |  |  |  | 96.88 | [5 empty] | 94.81 |  |  | 96.83 |  |  |  | 3.12 |  | 3.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 7276.08 |  |  | 7031 |  |  |  | 1122 | [10 empty] | 80.35 |  |  |  | 80.35 | [5 empty] | 73.83 |  |  | 80.04 |  |  |  | 2.69 |  | 2.22 | [8 empty] | 17.43 |  |  |  |  | 0.00
1993 |  |  |  | 2094.36 |  |  | 2213 |  |  |  | 1122 | [10 empty] | 26.32 |  |  |  | 26.32 | [5 empty] | 21.31 |  |  | 25.26 |  |  |  | 73.68 |  | 73.68 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 5849.36 |  |  | 5415 |  |  |  | 1106 | [10 empty] | 61.85 |  |  |  | 61.85 | [5 empty] | 60.37 |  |  | 61.82 |  |  |  | 2.18 |  | 1.38 | [8 empty] | 36.77 |  |  |  |  | 0.00
1995 |  |  |  | 8887.69 |  |  | 8064 |  |  |  | 1106 | [10 empty] | 92.15 |  |  |  | 92.15 | [5 empty] | 91.73 |  |  | 92.05 |  |  |  | 7.85 |  | 7.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 7682.50 |  |  | 6894 |  |  |  | 1108 | [10 empty] | 78.59 |  |  |  | 78.59 | [5 empty] | 78.88 |  |  | 78.48 |  |  |  | 8.62 |  | 7.42 | [8 empty] | 13.99 |  |  |  |  | 0.00
1997 |  |  |  | 8725.64 |  |  | 8001 |  |  |  | 1117 | [10 empty] | 91.45 |  |  |  | 91.45 | [5 empty] | 89.17 |  |  | 91.34 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 8.27 |  |  |  |  | 0.00
1998 |  |  |  | 9799.59 |  |  | 8656 |  |  |  | 1117 | [10 empty] | 98.84 |  |  |  | 98.84 | [5 empty] | 100.15 |  |  | 98.81 |  |  |  | 1.16 |  | 1.16 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 8978.97 |  |  | 8203 |  |  |  | 1117 | [10 empty] | 93.65 |  |  |  | 93.65 | [5 empty] | 91.76 |  |  | 93.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.35 |  |  |  |  | 0.00
2000 |  |  |  | 9058.27 |  |  | 8158 |  |  |  | 1117 | [10 empty] | 92.88 |  |  |  | 92.88 | [5 empty] | 92.32 |  |  | 92.87 |  |  |  | 0.88 |  | 0.82 | [8 empty] | 6.30 |  |  |  |  | 0.00
2001 |  |  |  | 9939.87 |  |  | 8760 |  |  |  | 1117 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.58 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 8542.04 |  |  | 7640 |  |  |  | 1126 | [10 empty] | 87.28 |  |  |  | 87.28 | [5 empty] | 87.14 |  |  | 87.21 |  |  |  | 3.20 |  | 2.88 | [8 empty] | 9.83 |  |  |  |  | 0.00
2003 |  |  |  | 8258.27 |  |  | 7401 |  |  |  | 1126 | [10 empty] | 84.64 |  |  |  | 84.64 | [5 empty] | 83.72 |  |  | 84.49 |  |  |  | 7.37 |  | 6.74 | [8 empty] | 8.63 |  |  |  |  | 0.00
2004 |  |  |  | 9464.89 |  |  | 8353 |  |  |  | 1124 | [10 empty] | 95.08 |  |  |  | 95.08 | [5 empty] | 95.86 |  |  | 95.09 |  |  |  | 2.19 |  | 2.13 | [8 empty] | 2.78 |  |  |  |  | 0.00
2005 |  |  |  | 8922.57 |  |  | 7867 |  |  |  | 1127 | [10 empty] | 89.83 |  |  |  | 89.83 | [5 empty] | 90.37 |  |  | 89.80 |  |  |  | 0.77 |  | 0.70 | [8 empty] | 9.47 |  |  |  |  | 0.00
2006 |  |  |  | 8914.65 |  |  | 7931 |  |  |  | 1127 | [10 empty] | 90.56 |  |  |  | 90.56 | [5 empty] | 90.30 |  |  | 90.54 |  |  |  | 1.42 |  | 1.31 | [8 empty] | 8.13 |  |  |  |  | 0.00
2007 |  |  |  | 9892.40 |  |  | 8692 |  |  |  | 1126 | [10 empty] | 99.23 |  |  |  | 99.23 | [5 empty] | 100.29 |  |  | 99.22 |  |  |  | 0.77 |  | 0.77 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8752.56 |  |  | 7749 |  |  |  | 1126 | [10 empty] | 88.23 |  |  |  | 88.23 | [5 empty] | 88.49 |  |  | 88.22 |  |  |  | 2.89 |  | 2.62 | [8 empty] | 9.14 |  |  |  |  | 0.00
2009 |  |  |  | 8792.36 |  |  | 7837 |  |  |  | 1126 | [10 empty] | 89.49 |  |  |  | 89.49 | [5 empty] | 89.14 |  |  | 89.46 |  |  |  | 2.46 |  | 2.26 | [8 empty] | 8.25 |  |  |  |  | 0.00
2010 |  |  |  | 9536.67 |  |  | 8573 |  |  |  | 1126 | [10 empty] | 97.89 |  |  |  | 97.89 | [5 empty] | 96.68 |  |  | 97.87 |  |  |  | 2.11 |  | 2.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8799.53 |  |  | 8016 |  |  |  | 1126 | [10 empty] | 91.52 |  |  |  | 91.52 | [5 empty] | 89.21 |  |  | 91.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.48 |  |  |  |  | 0.00
2012 |  |  |  | 7640.46 |  |  | 6866 |  |  |  | 1125 | [10 empty] | 78.18 |  |  |  | 78.18 | [5 empty] | 77.32 |  |  | 78.16 |  |  |  | 0.64 |  | 0.51 | [8 empty] | 21.31 |  |  |  |  | 0.00
2013 |  |  |  | 9661.10 |  |  | 8519 |  |  |  | 1126 | [10 empty] | 97.25 |  |  |  | 97.25 | [5 empty] | 97.93 |  |  | 97.24 |  |  |  | 1.18 |  | 1.16 | [8 empty] | 1.59 |  |  |  |  | 0.00
2014 |  |  |  | 8840.63 |  |  | 7867 |  |  |  | 1125 | [10 empty] | 89.81 |  |  |  | 89.81 | [5 empty] | 89.71 |  |  | 89.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.19 |  |  |  |  | 0.00
2015 |  |  |  | 8739.59 |  |  | 7849 |  |  |  | 1125 | [10 empty] | 89.60 |  |  |  | 89.60 | [5 empty] | 88.68 |  |  | 89.60 |  |  |  | 2.11 |  | 1.93 | [8 empty] | 8.47 |  |  |  |  | 0.00
2016 |  |  |  | 9595.60 |  |  | 8526 |  |  |  | 1125 | [10 empty] | 97.06 |  |  |  | 97.06 | [5 empty] | 97.10 |  |  | 97.06 |  |  |  | 2.94 |  | 2.94 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 8848.02 |  |  | 7824 |  |  |  | 1125 | [10 empty] | 89.32 |  |  |  | 89.32 | [5 empty] | 89.78 |  |  | 89.32 |  |  |  | 1.08 |  | 0.98 | [8 empty] | 9.71 |  |  |  |  | 0.00
2018 |  |  |  | 8786.87 |  |  | 7909 |  |  |  | 1139 | [10 empty] | 90.28 |  |  |  | 90.28 | [5 empty] | 88.07 |  |  | 90.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.72 |  |  |  |  | 0.00
2019 |  |  |  | 9874.98 |  |  | 8711 |  |  |  | 1139 | [10 empty] | 99.45 |  |  |  | 99.45 | [5 empty] | 98.97 |  |  | 99.44 |  |  |  | 0.55 |  | 0.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9252.42 |  |  | 8190 |  |  |  | 1139 | [10 empty] | 93.24 |  |  |  | 93.24 | [5 empty] | 92.48 |  |  | 93.24 |  |  |  | 0.33 |  | 0.31 | [8 empty] | 6.45 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1982 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 367
B. |  | Refuelling without maintenance | [20 empty] | 566 | [14 empty] | 15
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 690
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 28
E. |  | Testing of plant systems or components | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 309
L. |  | Human factor related | [39 empty] | 20
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 0
Z. |  | Other | [24 empty] | 27 | [14 empty] | 291
Subtotal | [22 empty] | 566 |  |  |  | 27 | [10 empty] | 734 |  |  |  | 987
Total | [22 empty] | 593 | [14 empty] | 1721
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1982 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 37
16. |  |  | Steam generation systems | [34 empty] | 19
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 46
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 198
42. |  |  | Electrical Power Supply Systems | [34 empty] | 19
Total | [37 empty] | 366
Highlights (2020)
Refueling Outage 23

## SOUTH TEXAS-1
2020 Operating Experience
US-498 | [8 empty] | SOUTH TEXAS-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | STP (STP Nuclear Operating Co.)
Owner | [7 empty] | : | NRGENERG (NRG Energy, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-12-22
Thermal power | [12 empty] | : |  |  | 3853 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-03-30
Gross electrical power | [12 empty] | : |  |  | 1354 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-08-25
Reference unit power (net) | [12 empty] | : |  |  | 1280 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 330
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.397
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 16.7 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.55
| Active core height/length [m] | [13 empty] | : |  |  | 4.27 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Pond (closed-cycle)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.03 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10409.82 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.69 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.69 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.31 %
Load Factor (LF) | [18 empty] | : | 92.59 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.68 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 819 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 988.11 | 924.40 |  |  |  | 403.84 |  | 318.64 | [8 empty] | 988.26 |  |  | 950.01 | [6 empty] | 978.11 |  | 968.47 |  |  |  | 946.23 |  |  | 985.99 |  |  | 955.75 | [9 empty] | 1002.02 |  |  | 10409.82
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.80 |  | 46.53 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.69
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.80 |  | 46.53 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.69
LF [%] |  |  |  |  | 103.76 | 103.76 |  |  |  | 42.41 |  | 34.57 | [8 empty] | 103.77 |  |  | 103.08 | [6 empty] | 102.71 |  | 101.70 |  |  |  | 102.67 |  |  | 103.54 |  |  | 103.71 | [9 empty] | 105.22 |  |  | 92.59
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 41.67 |  | 46.53 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.68
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 58.20 |  | 53.47 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.31
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 293660.92 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.96 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.36 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.31 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.36 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.33 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.89 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.24 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 2791.49 |  |  | 2404 |  |  |  | 1250 | [10 empty] | 80.04 |  |  |  | 80.04 | [5 empty] | 74.87 |  |  | 79.55 |  |  |  | 7.84 |  | 6.81 | [8 empty] | 13.15 |  |  |  |  | 0.00
1989 |  |  |  | 6307.67 |  |  | 5524 |  |  |  | 1250 | [10 empty] | 63.09 |  |  |  | 63.09 | [5 empty] | 57.60 |  |  | 63.06 |  |  |  | 8.17 |  | 5.62 | [8 empty] | 31.29 |  |  |  |  | 0.00
1990 |  |  |  | 6072.87 |  |  | 5198 |  |  |  | 1251 | [10 empty] | 59.38 |  |  |  | 59.38 | [5 empty] | 55.42 |  |  | 59.34 |  |  |  | 23.62 |  | 18.37 | [8 empty] | 22.25 |  |  |  |  | 0.00
1991 |  |  |  | 7239.78 |  |  | 6069 |  |  |  | 1251 | [10 empty] | 69.29 |  |  |  | 69.29 | [5 empty] | 66.06 |  |  | 69.28 |  |  |  | 11.39 |  | 8.90 | [8 empty] | 21.80 |  |  |  |  | 0.00
1992 |  |  |  | 7265.14 |  |  | 6033 |  |  |  | 1251 | [10 empty] | 68.69 |  |  |  | 68.69 | [5 empty] | 66.11 |  |  | 68.68 |  |  |  | 14.83 |  | 11.96 | [8 empty] | 19.34 |  |  |  |  | 0.00
1993 |  |  |  | 666.03 |  |  | 676 |  |  |  | 1251 | [10 empty] | 7.73 |  |  |  | 7.73 | [5 empty] | 6.08 |  |  | 7.72 |  |  |  | 92.27 |  | 92.27 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 8251.41 |  |  | 6842 |  |  |  | 1251 | [10 empty] | 78.15 |  |  |  | 78.15 | [5 empty] | 75.30 |  |  | 78.11 |  |  |  | 21.80 |  | 21.79 | [8 empty] | 0.06 |  |  |  |  | 0.00
1995 |  |  |  | 9301.77 |  |  | 7570 |  |  |  | 1251 | [10 empty] | 86.46 |  |  |  | 86.46 | [5 empty] | 84.88 |  |  | 86.42 |  |  |  | 2.38 |  | 2.11 | [8 empty] | 11.43 |  |  |  |  | 0.00
1996 |  |  |  | 10226.80 |  |  | 8213 |  |  |  | 1251 | [10 empty] | 93.53 |  |  |  | 93.53 | [5 empty] | 93.07 |  |  | 93.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.47 |  |  |  |  | 0.00
1997 |  |  |  | 9873.23 |  |  | 8019 |  |  |  | 1251 | [10 empty] | 91.61 |  |  |  | 91.61 | [5 empty] | 90.09 |  |  | 91.54 |  |  |  | 1.57 |  | 1.46 | [8 empty] | 6.93 |  |  |  |  | 0.00
1998 |  |  |  | 10859.94 |  |  | 8739 |  |  |  | 1250 | [10 empty] | 99.77 |  |  |  | 99.77 | [5 empty] | 99.11 |  |  | 99.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.23 |  |  |  |  | 0.00
1999 |  |  |  | 9645.37 |  |  | 7857 |  |  |  | 1250 | [10 empty] | 89.72 |  |  |  | 89.72 | [5 empty] | 88.09 |  |  | 89.69 |  |  |  | 1.38 |  | 1.26 | [8 empty] | 9.02 |  |  |  |  | 0.00
2000 |  |  |  | 8591.90 |  |  | 6905 |  |  |  | 1250 | [10 empty] | 78.64 |  |  |  | 78.64 | [5 empty] | 78.25 |  |  | 78.61 |  |  |  | 1.22 |  | 0.97 | [8 empty] | 20.39 |  |  |  |  | 0.00
2001 |  |  |  | 10338.16 |  |  | 8240 |  |  |  | 1250 | [10 empty] | 94.07 |  |  |  | 94.07 | [5 empty] | 94.41 |  |  | 94.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.93 |  |  |  |  | 0.00
2002 |  |  |  | 10867.94 |  |  | 8573 |  |  |  | 1250 | [10 empty] | 97.85 |  |  |  | 97.85 | [5 empty] | 99.01 |  |  | 97.87 |  |  |  | 2.15 |  | 2.15 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 6858.78 |  |  | 5433 |  |  |  | 1250 | [10 empty] | 62.26 |  |  |  | 62.26 | [5 empty] | 62.64 |  |  | 62.02 |  |  |  | 33.18 |  | 30.92 | [8 empty] | 6.82 |  |  |  |  | 0.00
2004 |  |  |  | 11103.58 |  |  | 8712 |  |  |  | 1250 | [10 empty] | 99.17 |  |  |  | 99.17 | [5 empty] | 101.13 |  |  | 99.18 |  |  |  | 0.83 |  | 0.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 9901.85 |  |  | 7845 |  |  |  | 1280 | [10 empty] | 89.57 |  |  |  | 89.57 | [5 empty] | 88.30 |  |  | 89.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.43 |  |  |  |  | 0.00
2006 |  |  |  | 10144.55 |  |  | 7942 |  |  |  | 1280 | [10 empty] | 90.67 |  |  |  | 90.67 | [5 empty] | 90.47 |  |  | 90.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.33 |  |  |  |  | 0.00
2007 |  |  |  | 11804.80 |  |  | 8760 |  |  |  | 1280 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 10800.56 |  |  | 8108 |  |  |  | 1280 | [10 empty] | 92.31 |  |  |  | 92.31 | [5 empty] | 96.06 |  |  | 92.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.69 |  |  |  |  | 0.00
2009 |  |  |  | 10052.23 |  |  | 7582 |  |  |  | 1280 | [10 empty] | 86.56 |  |  |  | 86.56 | [5 empty] | 89.65 |  |  | 86.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.44 |  |  |  |  | 0.00
2010 |  |  |  | 11304.11 |  |  | 8588 |  |  |  | 1280 | [10 empty] | 98.05 |  |  |  | 98.05 | [5 empty] | 100.81 |  |  | 98.04 |  |  |  | 1.95 |  | 1.95 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 10616.20 |  |  | 7909 |  |  |  | 1280 | [10 empty] | 90.52 |  |  |  | 90.52 | [5 empty] | 94.68 |  |  | 90.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.48 |  |  |  |  | 0.00
2012 |  |  |  | 10520.66 |  |  | 7891 |  |  |  | 1280 | [10 empty] | 89.85 |  |  |  | 89.85 | [5 empty] | 93.57 |  |  | 89.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.15 |  |  |  |  | 0.00
2013 |  |  |  | 11019.47 |  |  | 8247 |  |  |  | 1280 | [10 empty] | 94.14 |  |  |  | 94.14 | [5 empty] | 98.26 |  |  | 94.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.86 |  |  |  |  | 0.00
2014 |  |  |  | 9075.07 |  |  | 6894 |  |  |  | 1280 | [10 empty] | 78.70 |  |  |  | 78.70 | [5 empty] | 80.93 |  |  | 78.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.30 |  |  |  |  | 0.00
2015 |  |  |  | 9331.90 |  |  | 7140 |  |  |  | 1280 | [10 empty] | 81.51 |  |  |  | 81.51 | [5 empty] | 83.23 |  |  | 81.51 |  |  |  | 1.22 |  | 1.01 | [8 empty] | 17.49 |  |  |  |  | 0.00
2016 |  |  |  | 11288.14 |  |  | 8599 |  |  |  | 1280 | [10 empty] | 97.89 |  |  |  | 97.89 | [5 empty] | 100.40 |  |  | 97.89 |  |  |  | 2.11 |  | 2.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 10109.92 |  |  | 7715 |  |  |  | 1280 | [10 empty] | 88.08 |  |  |  | 88.08 | [5 empty] | 90.16 |  |  | 88.07 |  |  |  | 0.51 |  | 0.45 | [8 empty] | 11.47 |  |  |  |  | 0.00
2018 |  |  |  | 10306.36 |  |  | 7881 |  |  |  | 1280 | [10 empty] | 90.20 |  |  |  | 90.20 | [5 empty] | 91.92 |  |  | 89.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.80 |  |  |  |  | 0.00
2019 |  |  |  | 11515.33 |  |  | 8760 |  |  |  | 1280 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.70 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 10409.82 |  |  | 7965 |  |  |  | 1280 | [10 empty] | 90.69 |  |  |  | 90.69 | [5 empty] | 92.59 |  |  | 90.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.31 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1988 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 508
B. |  | Refuelling without maintenance | [20 empty] | 818 | [14 empty] | 25
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 726
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 65 |  |  |  | 30
E. |  | Testing of plant systems or components | [35 empty] | 4
H. |  | Nuclear regulatory requirements | [39 empty] | 12
L. |  | Human factor related | [39 empty] | 12
Z. |  | Other | [35 empty] | 0
Subtotal | [22 empty] | 818 | [14 empty] | 820 |  |  |  | 562
Total | [22 empty] | 818 | [14 empty] | 1382
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1988 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 291
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 99
31. |  |  | Turbine and auxiliaries | [34 empty] | 15
32. |  |  | Feedwater and Main Steam System | [34 empty] | 17
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 54
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 508
Highlights (2020)
Refueling Outage 22 (1RE22)

## SOUTH TEXAS-2
2020 Operating Experience
US-499 | [8 empty] | SOUTH TEXAS-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | STP (STP Nuclear Operating Co.)
Owner | [7 empty] | : | NRGENERG (NRG Energy, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-12-22
Thermal power | [12 empty] | : |  |  | 3853 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1989-04-11
Gross electrical power | [12 empty] | : |  |  | 1354 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-06-19
Reference unit power (net) | [12 empty] | : |  |  | 1280 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 330
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.397
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 16.7 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.55
| Active core height/length [m] | [13 empty] | : |  |  | 4.27 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Pond (closed-cycle)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.03 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 11548.94 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 102.72 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 993.02 | 930.50 |  |  |  | 983.01 |  | 948.97 | [8 empty] | 977.15 |  |  | 937.51 | [6 empty] | 963.39 |  | 956.56 |  |  |  | 933.39 |  |  | 977.05 |  |  | 954.76 | [9 empty] | 993.63 |  |  | 11548.94
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 104.27 | 104.45 |  |  |  | 103.22 |  | 102.97 | [8 empty] | 102.61 |  |  | 101.73 | [6 empty] | 101.16 |  | 100.45 |  |  |  | 101.28 |  |  | 102.60 |  |  | 103.60 | [9 empty] | 104.34 |  |  | 102.72
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 297025.52 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.06 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.28 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.32 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.61 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.22 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 3026.67 |  |  | 2845 |  |  |  | 1250 | [10 empty] | 57.92 |  |  |  | 57.92 | [5 empty] | 48.32 |  |  | 57.89 |  |  |  | 22.68 |  | 16.99 | [8 empty] | 25.09 |  |  |  |  | 0.00
1990 |  |  |  | 6452.17 |  |  | 5494 |  |  |  | 1251 | [10 empty] | 62.76 |  |  |  | 62.76 | [5 empty] | 58.88 |  |  | 62.72 |  |  |  | 21.61 |  | 17.31 | [8 empty] | 19.93 |  |  |  |  | 0.00
1991 |  |  |  | 7267.99 |  |  | 6134 |  |  |  | 1251 | [10 empty] | 70.03 |  |  |  | 70.03 | [5 empty] | 66.32 |  |  | 70.02 |  |  |  | 9.37 |  | 7.24 | [8 empty] | 22.73 |  |  |  |  | 0.00
1992 |  |  |  | 10340.97 |  |  | 8548 |  |  |  | 1251 | [10 empty] | 97.32 |  |  |  | 97.32 | [5 empty] | 94.10 |  |  | 97.31 |  |  |  | 2.68 |  | 2.68 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 690.30 |  |  | 702 |  |  |  | 1251 | [10 empty] | 8.00 |  |  |  | 8.00 | [5 empty] | 6.30 |  |  | 8.01 |  |  |  | 51.35 |  | 8.45 | [8 empty] | 83.55 |  |  |  |  | 0.00
1994 |  |  |  | 5990.98 |  |  | 5098 |  |  |  | 1251 | [10 empty] | 58.23 |  |  |  | 58.23 | [5 empty] | 54.67 |  |  | 58.20 |  |  |  | 41.72 |  | 41.68 | [8 empty] | 0.09 |  |  |  |  | 0.00
1995 |  |  |  | 9923.09 |  |  | 7985 |  |  |  | 1251 | [10 empty] | 91.19 |  |  |  | 91.19 | [5 empty] | 90.55 |  |  | 91.15 |  |  |  | 1.69 |  | 1.56 | [8 empty] | 7.25 |  |  |  |  | 0.00
1996 |  |  |  | 10457.93 |  |  | 8373 |  |  |  | 1251 | [10 empty] | 95.34 |  |  |  | 95.34 | [5 empty] | 95.17 |  |  | 95.32 |  |  |  | 0.68 |  | 0.65 | [8 empty] | 4.01 |  |  |  |  | 0.00
1997 |  |  |  | 9972.90 |  |  | 8093 |  |  |  | 1251 | [10 empty] | 92.44 |  |  |  | 92.44 | [5 empty] | 91.00 |  |  | 92.39 |  |  |  | 2.88 |  | 2.74 | [8 empty] | 4.82 |  |  |  |  | 0.00
1998 |  |  |  | 9983.91 |  |  | 8096 |  |  |  | 1250 | [10 empty] | 92.46 |  |  |  | 92.46 | [5 empty] | 91.11 |  |  | 92.42 |  |  |  | 1.33 |  | 1.25 | [8 empty] | 6.29 |  |  |  |  | 0.00
1999 |  |  |  | 9799.26 |  |  | 8034 |  |  |  | 1250 | [10 empty] | 91.73 |  |  |  | 91.73 | [5 empty] | 89.49 |  |  | 91.71 |  |  |  | 0.99 |  | 0.91 | [8 empty] | 7.36 |  |  |  |  | 0.00
2000 |  |  |  | 10557.22 |  |  | 8449 |  |  |  | 1250 | [10 empty] | 96.20 |  |  |  | 96.20 | [5 empty] | 96.15 |  |  | 96.19 |  |  |  | 2.08 |  | 2.04 | [8 empty] | 1.75 |  |  |  |  | 0.00
2001 |  |  |  | 9537.56 |  |  | 7751 |  |  |  | 1250 | [10 empty] | 88.52 |  |  |  | 88.52 | [5 empty] | 87.10 |  |  | 88.48 |  |  |  | 4.44 |  | 4.12 | [8 empty] | 7.36 |  |  |  |  | 0.00
2002 |  |  |  | 8219.85 |  |  | 6663 |  |  |  | 1250 | [10 empty] | 75.89 |  |  |  | 75.89 | [5 empty] | 75.07 |  |  | 76.06 |  |  |  | 7.57 |  | 6.22 | [8 empty] | 17.89 |  |  |  |  | 0.00
2003 |  |  |  | 8920.21 |  |  | 7112 |  |  |  | 1250 | [10 empty] | 81.07 |  |  |  | 81.07 | [5 empty] | 81.46 |  |  | 81.19 |  |  |  | 18.93 |  | 18.93 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 10304.10 |  |  | 8121 |  |  |  | 1250 | [10 empty] | 92.28 |  |  |  | 92.28 | [5 empty] | 93.84 |  |  | 92.45 |  |  |  | 0.50 |  | 0.46 | [8 empty] | 7.26 |  |  |  |  | 0.00
2005 |  |  |  | 9937.18 |  |  | 7866 |  |  |  | 1280 | [10 empty] | 89.81 |  |  |  | 89.81 | [5 empty] | 88.62 |  |  | 89.79 |  |  |  | 2.18 |  | 2.00 | [8 empty] | 8.19 |  |  |  |  | 0.00
2006 |  |  |  | 11225.96 |  |  | 8760 |  |  |  | 1280 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.12 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 10373.70 |  |  | 7943 |  |  |  | 1280 | [10 empty] | 90.68 |  |  |  | 90.68 | [5 empty] | 92.52 |  |  | 90.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.32 |  |  |  |  | 0.00
2008 |  |  |  | 10739.07 |  |  | 8047 |  |  |  | 1280 | [10 empty] | 91.61 |  |  |  | 91.61 | [5 empty] | 95.51 |  |  | 91.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.39 |  |  |  |  | 0.00
2009 |  |  |  | 11303.91 |  |  | 8498 |  |  |  | 1280 | [10 empty] | 97.01 |  |  |  | 97.01 | [5 empty] | 100.81 |  |  | 97.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.99 |  |  |  |  | 0.00
2010 |  |  |  | 9822.67 |  |  | 7371 |  |  |  | 1280 | [10 empty] | 84.16 |  |  |  | 84.16 | [5 empty] | 87.60 |  |  | 84.14 |  |  |  | 6.86 |  | 6.20 | [8 empty] | 9.63 |  |  |  |  | 0.00
2011 |  |  |  | 9823.15 |  |  | 7408 |  |  |  | 1280 | [10 empty] | 84.59 |  |  |  | 84.59 | [5 empty] | 87.61 |  |  | 84.57 |  |  |  | 9.61 |  | 9.00 | [8 empty] | 6.42 |  |  |  |  | 0.00
2012 |  |  |  | 8122.51 |  |  | 6073 |  |  |  | 1280 | [10 empty] | 69.15 |  |  |  | 69.15 | [5 empty] | 72.24 |  |  | 69.14 |  |  |  | 30.85 |  | 30.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 7046.84 |  |  | 5338 |  |  |  | 1280 | [10 empty] | 60.95 |  |  |  | 60.95 | [5 empty] | 62.84 |  |  | 60.93 |  |  |  | 32.55 |  | 29.42 | [8 empty] | 9.64 |  |  |  |  | 0.00
2014 |  |  |  | 11628.69 |  |  | 8760 |  |  |  | 1280 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.71 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 10154.98 |  |  | 7767 |  |  |  | 1280 | [10 empty] | 88.67 |  |  |  | 88.67 | [5 empty] | 90.57 |  |  | 88.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.33 |  |  |  |  | 0.00
2016 |  |  |  | 10452.92 |  |  | 8024 |  |  |  | 1280 | [10 empty] | 91.35 |  |  |  | 91.35 | [5 empty] | 92.97 |  |  | 91.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.65 |  |  |  |  | 0.00
2017 |  |  |  | 11502.22 |  |  | 8760 |  |  |  | 1280 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.58 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 10434.48 |  |  | 7964 |  |  |  | 1280 | [10 empty] | 91.12 |  |  |  | 91.12 | [5 empty] | 93.06 |  |  | 90.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.88 |  |  |  |  | 0.00
2019 |  |  |  | 10518.90 |  |  | 8007 |  |  |  | 1280 | [10 empty] | 91.42 |  |  |  | 91.42 | [5 empty] | 93.81 |  |  | 91.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.58 |  |  |  |  | 0.00
2020 |  |  |  | 11548.94 |  |  | 8783 |  |  |  | 1280 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.72 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 550
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 759
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 60
E. |  | Testing of plant systems or components | [35 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 2
L. |  | Human factor related | [39 empty] | 6
Z. |  | Other | [39 empty] | 5
Subtotal | [37 empty] | 821 |  |  |  | 563
Total | [22 empty] | 0 | [14 empty] | 1384
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 4
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
14. |  |  | Safety Systems | [34 empty] | 130
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 10
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 73
32. |  |  | Feedwater and Main Steam System | [34 empty] | 34
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 138
42. |  |  | Electrical Power Supply Systems | [34 empty] | 124
Total | [37 empty] | 548

## ST. LUCIE-1
2020 Operating Experience
US-335 | [8 empty] | ST. LUCIE-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FPL (Florida Power & Light Co.)
Owner | [7 empty] | : | FPL (Florida Power & Light Co.)
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-07-01
Thermal power | [12 empty] | : |  |  | 3020 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-05-07
Gross electrical power | [12 empty] | : |  |  | 1045 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-12-21
Reference unit power (net) | [12 empty] | : |  |  | 981 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 314
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.45 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 3.47 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 217 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8726.84 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 101.27 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 747.53 | 696.47 |  |  |  | 744.82 |  | 720.77 | [8 empty] | 742.08 |  |  | 715.81 | [6 empty] | 725.79 |  | 732.52 |  |  |  | 697.79 |  |  | 735.15 |  |  | 719.76 | [9 empty] | 748.35 |  |  | 8726.84
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 102.42 | 102.01 |  |  |  | 102.05 |  | 102.05 | [8 empty] | 101.67 |  |  | 101.34 | [6 empty] | 99.44 |  | 100.36 |  |  |  | 98.79 |  |  | 100.72 |  |  | 101.90 | [9 empty] | 102.53 |  |  | 101.27
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 308662.38 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.02 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.85 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.21 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.2 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.39 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | 317.20 |  |  | 919 |  |  |  | 814 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1977 |  |  |  | 5343.70 |  |  | 7414 |  |  |  | 779 | [10 empty] | 78.39 |  |  |  | 78.39 | [5 empty] | 78.31 |  |  | 84.63 |  |  |  | 16.10 |  | 15.04 | [8 empty] | 6.57 |  |  |  |  | 0.00
1978 |  |  |  | 5009.70 |  |  | 6674 |  |  |  | 777 | [10 empty] | 73.65 |  |  |  | 73.65 | [5 empty] | 73.60 |  |  | 76.19 |  |  |  | 3.45 |  | 2.64 | [8 empty] | 23.71 |  |  |  |  | 0.00
1979 |  |  |  | 4889.60 |  |  | 6469 |  |  |  | 777 | [10 empty] | 71.70 |  |  |  | 71.70 | [5 empty] | 71.84 |  |  | 73.85 |  |  |  | 3.60 |  | 2.67 | [8 empty] | 25.63 |  |  |  |  | 0.00
1980 |  |  |  | 5201.90 |  |  | 6797 |  |  |  | 777 | [10 empty] | 75.98 |  |  |  | 75.98 | [5 empty] | 76.22 |  |  | 77.38 |  |  |  | 7.26 |  | 5.95 | [8 empty] | 18.07 |  |  |  |  | 0.00
1981 |  |  |  | 4954.70 |  |  | 6364 |  |  |  | 777 | [10 empty] | 70.48 |  |  |  | 70.48 | [5 empty] | 72.79 |  |  | 72.65 |  |  |  | 5.05 |  | 3.75 | [8 empty] | 25.77 |  |  |  |  | 0.00
1982 |  |  |  | 6784.60 |  |  | 8227 |  |  |  | 803 | [10 empty] | 94.15 |  |  |  | 94.15 | [5 empty] | 96.45 |  |  | 93.92 |  |  |  | 0.55 |  | 0.52 | [8 empty] | 5.33 |  |  |  |  | 0.00
1983 |  |  |  | 1099.50 |  |  | 1350 |  |  |  | 820 | [10 empty] | 15.40 |  |  |  | 15.40 | [5 empty] | 15.31 |  |  | 15.41 |  |  |  | 1.15 |  | 0.18 | [8 empty] | 84.43 |  |  |  |  | 0.00
1984 |  |  |  | 4243.28 |  |  | 5154 |  |  |  | 822 | [10 empty] | 58.64 |  |  |  | 60.77 | [5 empty] | 58.77 |  |  | 58.67 |  |  |  | 3.05 |  | 1.91 | [8 empty] | 37.31 |  |  |  |  | 2.13
1985 |  |  |  | 5868.61 |  |  | 7067 |  |  |  | 825 | [10 empty] | 80.39 |  |  |  | 80.39 | [5 empty] | 81.13 |  |  | 80.67 |  |  |  | 1.45 |  | 1.18 | [8 empty] | 18.43 |  |  |  |  | 0.00
1986 |  |  |  | 7052.03 |  |  | 8351 |  |  |  | 829 | [10 empty] | 95.70 |  |  |  | 95.70 | [5 empty] | 97.10 |  |  | 95.33 |  |  |  | 0.50 |  | 0.48 | [8 empty] | 3.82 |  |  |  |  | 0.00
1987 |  |  |  | 5719.18 |  |  | 6812 |  |  |  | 839 | [10 empty] | 77.80 |  |  |  | 77.80 | [5 empty] | 77.82 |  |  | 77.76 |  |  |  | 4.35 |  | 3.54 | [8 empty] | 18.66 |  |  |  |  | 0.00
1988 |  |  |  | 6256.01 |  |  | 7407 |  |  |  | 839 | [10 empty] | 84.36 |  |  |  | 84.36 | [5 empty] | 84.89 |  |  | 84.32 |  |  |  | 1.56 |  | 1.34 | [8 empty] | 14.31 |  |  |  |  | 0.00
1989 |  |  |  | 6947.34 |  |  | 8257 |  |  |  | 839 | [10 empty] | 94.28 |  |  |  | 94.28 | [5 empty] | 94.53 |  |  | 94.26 |  |  |  | 0.53 |  | 0.51 | [8 empty] | 5.22 |  |  |  |  | 0.00
1990 |  |  |  | 4503.49 |  |  | 5463 |  |  |  | 839 | [10 empty] | 64.29 |  |  |  | 64.29 | [5 empty] | 61.27 |  |  | 62.36 |  |  |  | 33.77 |  | 32.79 | [8 empty] | 2.92 |  |  |  |  | 0.00
1991 |  |  |  | 5793.30 |  |  | 7089 |  |  |  | 839 | [10 empty] | 80.95 |  |  |  | 80.95 | [5 empty] | 78.82 |  |  | 80.92 |  |  |  | 1.16 |  | 0.95 | [8 empty] | 18.11 |  |  |  |  | 0.00
1992 |  |  |  | 7142.17 |  |  | 8479 |  |  |  | 839 | [10 empty] | 96.54 |  |  |  | 96.54 | [5 empty] | 96.91 |  |  | 96.53 |  |  |  | 3.46 |  | 3.46 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 5440.51 |  |  | 6678 |  |  |  | 839 | [10 empty] | 76.24 |  |  |  | 76.60 | [5 empty] | 74.02 |  |  | 76.23 |  |  |  | 1.61 |  | 1.26 | [8 empty] | 22.15 |  |  |  |  | 0.35
1994 |  |  |  | 6183.59 |  |  | 7600 |  |  |  | 839 | [10 empty] | 86.84 |  |  |  | 86.84 | [5 empty] | 84.13 |  |  | 86.76 |  |  |  | 5.03 |  | 4.60 | [8 empty] | 8.56 |  |  |  |  | 0.00
1995 |  |  |  | 5519.42 |  |  | 6662 |  |  |  | 839 | [10 empty] | 76.16 |  |  |  | 76.16 | [5 empty] | 75.10 |  |  | 76.05 |  |  |  | 21.82 |  | 21.26 | [8 empty] | 2.58 |  |  |  |  | 0.00
1996 |  |  |  | 5222.04 |  |  | 6472 |  |  |  | 839 | [10 empty] | 73.76 |  |  |  | 73.76 | [5 empty] | 70.86 |  |  | 73.68 |  |  |  | 2.99 |  | 2.28 | [8 empty] | 23.96 |  |  |  |  | 0.00
1997 |  |  |  | 5717.75 |  |  | 6842 |  |  |  | 839 | [10 empty] | 78.14 |  |  |  | 78.14 | [5 empty] | 77.80 |  |  | 78.11 |  |  |  | 2.33 |  | 1.86 | [8 empty] | 20.00 |  |  |  |  | 0.00
1998 |  |  |  | 7035.48 |  |  | 8393 |  |  |  | 839 | [10 empty] | 95.82 |  |  |  | 95.82 | [5 empty] | 95.73 |  |  | 95.81 |  |  |  | 0.48 |  | 0.46 | [8 empty] | 3.72 |  |  |  |  | 0.00
1999 |  |  |  | 6532.73 |  |  | 7752 |  |  |  | 839 | [10 empty] | 88.50 |  |  |  | 89.87 | [5 empty] | 88.89 |  |  | 88.49 |  |  |  | 1.99 |  | 1.83 | [8 empty] | 8.30 |  |  |  |  | 1.37
2000 |  |  |  | 7513.70 |  |  | 8784 |  |  |  | 839 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.95 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 6709.77 |  |  | 7915 |  |  |  | 839 | [10 empty] | 90.37 |  |  |  | 90.37 | [5 empty] | 91.29 |  |  | 90.35 |  |  |  | 1.92 |  | 1.77 | [8 empty] | 7.86 |  |  |  |  | 0.00
2002 |  |  |  | 6919.40 |  |  | 8163 |  |  |  | 839 | [10 empty] | 93.20 |  |  |  | 93.20 | [5 empty] | 94.15 |  |  | 93.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.80 |  |  |  |  | 0.00
2003 |  |  |  | 7504.81 |  |  | 8760 |  |  |  | 839 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.11 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 6324.30 |  |  | 7518 |  |  |  | 839 | [10 empty] | 85.62 |  |  |  | 90.45 | [5 empty] | 85.81 |  |  | 85.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.55 |  |  |  |  | 4.83
2005 |  |  |  | 6088.09 |  |  | 7217 |  |  |  | 839 | [10 empty] | 82.40 |  |  |  | 82.40 | [5 empty] | 82.84 |  |  | 82.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.60 |  |  |  |  | 0.00
2006 |  |  |  | 7463.29 |  |  | 8760 |  |  |  | 839 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.55 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 6235.76 |  |  | 7417 |  |  |  | 839 | [10 empty] | 84.68 |  |  |  | 84.68 | [5 empty] | 84.84 |  |  | 84.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.32 |  |  |  |  | 0.00
2008 |  |  |  | 6673.04 |  |  | 7872 |  |  |  | 839 | [10 empty] | 89.63 |  |  |  | 89.63 | [5 empty] | 90.55 |  |  | 89.62 |  |  |  | 1.62 |  | 1.47 | [8 empty] | 8.90 |  |  |  |  | 0.00
2009 |  |  |  | 7369.21 |  |  | 8760 |  |  |  | 839 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.27 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 5302.68 |  |  | 6813 |  |  |  | 839 | [10 empty] | 77.79 |  |  |  | 77.79 | [5 empty] | 72.15 |  |  | 77.77 |  |  |  | 3.63 |  | 2.93 | [8 empty] | 19.28 |  |  |  |  | 0.00
2011 |  |  |  | 6240.99 |  |  | 7719 |  |  |  | 839 | [10 empty] | 88.13 |  |  |  | 88.13 | [5 empty] | 84.92 |  |  | 88.12 |  |  |  | 2.67 |  | 2.42 | [8 empty] | 9.45 |  |  |  |  | 0.00
2012 |  |  |  | 4912.62 |  |  | 5821 |  |  |  | 982 | [10 empty] | 69.71 |  |  |  | 69.71 | [5 empty] | 59.09 |  |  | 66.27 |  |  |  | 1.83 |  | 1.30 | [8 empty] | 29.00 |  |  |  |  | 0.00
2013 |  |  |  | 6980.44 |  |  | 7104 |  |  |  | 982 | [10 empty] | 81.09 |  |  |  | 81.09 | [5 empty] | 81.14 |  |  | 81.09 |  |  |  | 6.68 |  | 5.80 | [8 empty] | 13.11 |  |  |  |  | 0.00
2014 |  |  |  | 8721.17 |  |  | 8760 |  |  |  | 982 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.38 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 7833.25 |  |  | 7927 |  |  |  | 982 | [10 empty] | 90.48 |  |  |  | 90.48 | [5 empty] | 91.06 |  |  | 90.49 |  |  |  | 0.65 |  | 0.59 | [8 empty] | 8.92 |  |  |  |  | 0.00
2016 |  |  |  | 6918.93 |  |  | 7059 |  |  |  | 982 | [10 empty] | 80.36 |  |  |  | 80.36 | [5 empty] | 80.21 |  |  | 80.36 |  |  |  | 8.42 |  | 7.39 | [8 empty] | 12.25 |  |  |  |  | 0.00
2017 |  |  |  | 8512.14 |  |  | 8554 |  |  |  | 981 | [10 empty] | 97.64 |  |  |  | 98.00 | [5 empty] | 99.05 |  |  | 97.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.00 |  |  |  |  | 0.35
2018 |  |  |  | 7914.55 |  |  | 7986 |  |  |  | 981 | [10 empty] | 91.17 |  |  |  | 91.17 | [5 empty] | 92.10 |  |  | 91.16 |  |  |  | 0.42 |  | 0.38 | [8 empty] | 8.45 |  |  |  |  | 0.00
2019 |  |  |  | 6098.13 |  |  | 6182 |  |  |  | 981 | [10 empty] | 70.59 |  |  |  | 70.59 | [5 empty] | 70.96 |  |  | 70.57 |  |  |  | 21.67 |  | 19.53 | [8 empty] | 9.89 |  |  |  |  | 0.00
2020 |  |  |  | 8726.84 |  |  | 8783 |  |  |  | 981 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.27 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1976 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 356
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1052
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 77
E. |  | Testing of plant systems or components | [35 empty] | 3
L. |  | Human factor related | [39 empty] | 19
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 23
Z. |  | Other | [35 empty] | 0 |  |  |  | 3
Subtotal | [37 empty] | 1132 |  |  |  | 378 | [11 empty] | 23
Total | [22 empty] | 0 | [14 empty] | 1533
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1976 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 109
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 107
16. |  |  | Steam generation systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 14
32. |  |  | Feedwater and Main Steam System | [34 empty] | 22
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 47
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [37 empty] | 376

## ST. LUCIE-2
2020 Operating Experience
US-389 | [8 empty] | ST. LUCIE-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FPL (Florida Power & Light Co.)
Owner | [7 empty] | : | FPL (Florida Power & Light Co.)
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-06-02
Thermal power | [12 empty] | : |  |  | 3020 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-06-13
Gross electrical power | [12 empty] | : |  |  | 1050 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-08-08
Reference unit power (net) | [12 empty] | : |  |  | 987 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 314
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 35 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 36000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.45 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 3.47 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 217 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 91 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8073.53 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.48 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.48 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.52 %
Load Factor (LF) | [18 empty] | : | 93.12 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.47 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 749 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 757.93 | 380.45 |  |  |  | 288.00 |  | 732.59 | [8 empty] | 753.54 |  |  | 726.80 | [6 empty] | 745.67 |  | 744.04 |  |  |  | 720.60 |  |  | 745.59 |  |  | 719.96 | [9 empty] | 758.36 |  |  | 8073.53
EAF [%] |  |  |  |  | 100.00 | 55.17 |  |  |  | 41.36 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.48
UCF [%] |  |  |  |  | 100.00 | 55.17 |  |  |  | 41.36 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.48
LF [%] |  |  |  |  | 103.21 | 55.38 |  |  |  | 39.22 |  | 103.09 | [8 empty] | 102.62 |  |  | 102.27 | [6 empty] | 101.54 |  | 101.32 |  |  |  | 101.40 |  |  | 101.53 |  |  | 101.31 | [9 empty] | 103.27 |  |  | 93.12
OF [%] |  |  |  |  | 100.00 | 55.17 |  |  |  | 41.26 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.47
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 44.83 |  |  |  | 58.64 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.52
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 188540.34 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.47 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.46 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.27 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.82 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.91 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.36 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.27 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 2575.80 |  |  | 3598 |  |  |  | 808 | [10 empty] | 89.40 |  |  |  | 89.40 | [5 empty] | 87.03 |  |  | 89.27 |  |  |  | 10.60 |  | 10.60 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 5564.83 |  |  | 7067 |  |  |  | 786 | [10 empty] | 79.49 |  |  |  | 82.85 | [5 empty] | 80.60 |  |  | 80.45 |  |  |  | 6.88 |  | 6.13 | [8 empty] | 11.02 |  |  |  |  | 3.36
1985 |  |  |  | 6108.63 |  |  | 7368 |  |  |  | 824 | [10 empty] | 83.89 |  |  |  | 83.89 | [5 empty] | 84.58 |  |  | 84.11 |  |  |  | 13.57 |  | 13.18 | [8 empty] | 2.94 |  |  |  |  | 0.00
1986 |  |  |  | 6151.23 |  |  | 7253 |  |  |  | 837 | [10 empty] | 82.80 |  |  |  | 82.80 | [5 empty] | 83.86 |  |  | 82.80 |  |  |  | 1.02 |  | 0.86 | [8 empty] | 16.35 |  |  |  |  | 0.00
1987 |  |  |  | 5950.18 |  |  | 7206 |  |  |  | 839 | [10 empty] | 82.30 |  |  |  | 82.30 | [5 empty] | 80.96 |  |  | 82.26 |  |  |  | 4.13 |  | 3.54 | [8 empty] | 14.16 |  |  |  |  | 0.00
1988 |  |  |  | 7407.10 |  |  | 8784 |  |  |  | 839 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 5443.45 |  |  | 6531 |  |  |  | 839 | [10 empty] | 74.59 |  |  |  | 74.59 | [5 empty] | 74.06 |  |  | 74.55 |  |  |  | 2.05 |  | 1.56 | [8 empty] | 23.85 |  |  |  |  | 0.00
1990 |  |  |  | 5341.48 |  |  | 6487 |  |  |  | 839 | [10 empty] | 74.08 |  |  |  | 74.08 | [5 empty] | 72.68 |  |  | 74.05 |  |  |  | 10.25 |  | 8.46 | [8 empty] | 17.47 |  |  |  |  | 0.00
1991 |  |  |  | 7428.74 |  |  | 8760 |  |  |  | 839 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.08 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 5431.15 |  |  | 6598 |  |  |  | 839 | [10 empty] | 75.15 |  |  |  | 75.15 | [5 empty] | 73.69 |  |  | 75.11 |  |  |  | 8.10 |  | 6.63 | [8 empty] | 18.23 |  |  |  |  | 0.00
1993 |  |  |  | 4719.91 |  |  | 6687 |  |  |  | 839 | [10 empty] | 76.36 |  |  |  | 76.36 | [5 empty] | 64.22 |  |  | 76.34 |  |  |  | 23.64 |  | 23.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 5607.44 |  |  | 6971 |  |  |  | 839 | [10 empty] | 79.62 |  |  |  | 79.62 | [5 empty] | 76.30 |  |  | 79.58 |  |  |  | 2.30 |  | 1.87 | [8 empty] | 18.50 |  |  |  |  | 0.00
1995 |  |  |  | 5295.95 |  |  | 6570 |  |  |  | 839 | [10 empty] | 75.05 |  |  |  | 75.05 | [5 empty] | 72.06 |  |  | 75.00 |  |  |  | 2.52 |  | 1.94 | [8 empty] | 23.01 |  |  |  |  | 0.00
1996 |  |  |  | 6984.80 |  |  | 8444 |  |  |  | 839 | [10 empty] | 96.16 |  |  |  | 96.16 | [5 empty] | 94.78 |  |  | 96.13 |  |  |  | 2.75 |  | 2.72 | [8 empty] | 1.12 |  |  |  |  | 0.00
1997 |  |  |  | 6498.92 |  |  | 7756 |  |  |  | 839 | [10 empty] | 88.55 |  |  |  | 88.55 | [5 empty] | 88.43 |  |  | 88.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.45 |  |  |  |  | 0.00
1998 |  |  |  | 6739.45 |  |  | 8009 |  |  |  | 839 | [10 empty] | 91.45 |  |  |  | 91.45 | [5 empty] | 91.70 |  |  | 91.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.55 |  |  |  |  | 0.00
1999 |  |  |  | 7212.98 |  |  | 8583 |  |  |  | 839 | [10 empty] | 97.99 |  |  |  | 97.99 | [5 empty] | 98.14 |  |  | 97.98 |  |  |  | 2.01 |  | 2.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 6804.33 |  |  | 8041 |  |  |  | 839 | [10 empty] | 91.56 |  |  |  | 91.56 | [5 empty] | 92.33 |  |  | 91.54 |  |  |  | 4.79 |  | 4.61 | [8 empty] | 3.83 |  |  |  |  | 0.00
2001 |  |  |  | 6707.49 |  |  | 7979 |  |  |  | 839 | [10 empty] | 91.11 |  |  |  | 91.11 | [5 empty] | 91.26 |  |  | 91.08 |  |  |  | 1.97 |  | 1.84 | [8 empty] | 7.05 |  |  |  |  | 0.00
2002 |  |  |  | 7424.99 |  |  | 8742 |  |  |  | 839 | [10 empty] | 99.80 |  |  |  | 99.80 | [5 empty] | 101.03 |  |  | 99.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.20 |  |  |  |  | 0.00
2003 |  |  |  | 5891.34 |  |  | 7120 |  |  |  | 839 | [10 empty] | 81.31 |  |  |  | 81.31 | [5 empty] | 80.16 |  |  | 81.28 |  |  |  | 6.03 |  | 5.22 | [8 empty] | 13.47 |  |  |  |  | 0.00
2004 |  |  |  | 6781.43 |  |  | 8059 |  |  |  | 839 | [10 empty] | 91.77 |  |  |  | 98.17 | [5 empty] | 92.02 |  |  | 91.75 |  |  |  | 1.83 |  | 1.83 | [8 empty] | 0.00 |  |  |  |  | 6.40
2005 |  |  |  | 6283.15 |  |  | 7602 |  |  |  | 839 | [10 empty] | 86.81 |  |  |  | 87.89 | [5 empty] | 85.49 |  |  | 86.78 |  |  |  | 0.97 |  | 0.86 | [8 empty] | 11.26 |  |  |  |  | 1.08
2006 |  |  |  | 6048.25 |  |  | 7434 |  |  |  | 839 | [10 empty] | 84.88 |  |  |  | 84.88 | [5 empty] | 82.29 |  |  | 84.86 |  |  |  | 1.70 |  | 1.47 | [8 empty] | 13.65 |  |  |  |  | 0.00
2007 |  |  |  | 5170.45 |  |  | 6232 |  |  |  | 839 | [10 empty] | 71.16 |  |  |  | 71.16 | [5 empty] | 70.35 |  |  | 71.14 |  |  |  | 4.71 |  | 3.52 | [8 empty] | 25.32 |  |  |  |  | 0.00
2008 |  |  |  | 7087.29 |  |  | 8361 |  |  |  | 839 | [10 empty] | 95.19 |  |  |  | 95.19 | [5 empty] | 96.17 |  |  | 95.18 |  |  |  | 3.83 |  | 3.79 | [8 empty] | 1.02 |  |  |  |  | 0.00
2009 |  |  |  | 5906.55 |  |  | 6721 |  |  |  | 839 | [10 empty] | 76.75 |  |  |  | 76.75 | [5 empty] | 80.37 |  |  | 76.72 |  |  |  | 5.72 |  | 4.66 | [8 empty] | 18.59 |  |  |  |  | 0.00
2010 |  |  |  | 7331.25 |  |  | 8589 |  |  |  | 839 | [10 empty] | 98.05 |  |  |  | 98.05 | [5 empty] | 99.75 |  |  | 98.05 |  |  |  | 1.95 |  | 1.95 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 4279.08 |  |  | 5674 |  |  |  | 839 | [10 empty] | 64.78 |  |  |  | 64.78 | [5 empty] | 58.22 |  |  | 64.77 |  |  |  | 1.30 |  | 0.86 | [8 empty] | 34.36 |  |  |  |  | 0.00
2012 |  |  |  | 5096.77 |  |  | 6101 |  |  |  | 839 | [10 empty] | 69.47 |  |  |  | 69.47 | [5 empty] | 69.16 |  |  | 69.46 |  |  |  | 0.78 |  | 0.54 | [8 empty] | 29.99 |  |  |  |  | 0.00
2013 |  |  |  | 8641.77 |  |  | 8583 |  |  |  | 987 | [10 empty] | 98.28 |  |  |  | 99.05 | [5 empty] | 99.94 |  |  | 97.97 |  |  |  | 0.95 |  | 0.95 | [8 empty] | 0.00 |  |  |  |  | 0.77
2014 |  |  |  | 7096.40 |  |  | 7121 |  |  |  | 987 | [10 empty] | 81.30 |  |  |  | 81.30 | [5 empty] | 82.08 |  |  | 81.29 |  |  |  | 5.23 |  | 9.51 | [8 empty] | 9.19 |  |  |  |  | 0.00
2015 |  |  |  | 7242.01 |  |  | 7272 |  |  |  | 987 | [10 empty] | 83.01 |  |  |  | 83.01 | [5 empty] | 83.76 |  |  | 83.01 |  |  |  | 4.42 |  | 3.84 | [8 empty] | 13.15 |  |  |  |  | 0.00
2016 |  |  |  | 8669.53 |  |  | 8604 |  |  |  | 987 | [10 empty] | 97.95 |  |  |  | 100.00 | [5 empty] | 100.00 |  |  | 97.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 2.05
2017 |  |  |  | 7915.78 |  |  | 7904 |  |  |  | 987 | [10 empty] | 90.23 |  |  |  | 90.23 | [5 empty] | 91.55 |  |  | 90.23 |  |  |  | 0.89 |  | 0.81 | [8 empty] | 8.96 |  |  |  |  | 0.00
2018 |  |  |  | 7652.59 |  |  | 7723 |  |  |  | 987 | [10 empty] | 88.16 |  |  |  | 88.16 | [5 empty] | 88.51 |  |  | 88.16 |  |  |  | 1.68 |  | 1.51 | [8 empty] | 10.33 |  |  |  |  | 0.00
2019 |  |  |  | 8876.97 |  |  | 8760 |  |  |  | 987 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.67 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 8073.53 |  |  | 8035 |  |  |  | 987 | [10 empty] | 91.48 |  |  |  | 91.48 | [5 empty] | 93.12 |  |  | 91.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.52 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 260
B. |  | Refuelling without maintenance | [20 empty] | 748 | [14 empty] | 20
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 841
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 35
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 33
P. |  | Fire | [39 empty] | 2
Z. |  | Other | [35 empty] | 0 |  |  |  | 11
Subtotal | [22 empty] | 748 | [14 empty] | 897 |  |  |  | 288 | [11 empty] | 33
Total | [22 empty] | 748 | [14 empty] | 1218
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 0
12. |  |  | Reactor I&C Systems | [34 empty] | 29
14. |  |  | Safety Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 105
16. |  |  | Steam generation systems | [34 empty] | 19
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 37
32. |  |  | Feedwater and Main Steam System | [34 empty] | 47
33. |  |  | Circulating Water System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 11
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [37 empty] | 289
Highlights (2020)
Refueling Outage 25

## SUMMER-1
2020 Operating Experience
US-395 | [8 empty] | SUMMER-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SCE&G (SOUTH CAROLINA ELECTRIC & GAS CO.)
Owner | [7 empty] | : | SCE&G (SOUTH CAROLINA ELECTRIC & GAS CO.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-03-21
Thermal power | [12 empty] | : |  |  | 2900 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-11-16
Gross electrical power | [12 empty] | : |  |  | 1006 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-01-01
Reference unit power (net) | [12 empty] | : |  |  | 973 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 43.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 38900 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 8.33
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.83 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7727.52 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.73 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.11 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.67 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.11 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.22 %
Load Factor (LF) | [18 empty] | : | 90.41 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.1 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 782 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 739.62 | 692.04 |  |  |  | 738.14 |  | 221.85 | [8 empty] | 436.99 |  |  | 711.80 | [6 empty] | 719.80 |  | 698.50 |  |  |  | 575.28 |  |  | 736.73 |  |  | 716.32 | [9 empty] | 740.45 |  |  | 7727.52
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 33.05 | [8 empty] | 67.80 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 91.80 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.11
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 33.05 | [8 empty] | 67.80 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 91.80 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.11
LF [%] |  |  |  |  | 102.17 | 102.19 |  |  |  | 101.97 |  | 31.67 | [8 empty] | 60.37 |  |  | 101.60 | [6 empty] | 99.43 |  | 96.49 |  |  |  | 82.12 |  |  | 101.77 |  |  | 102.25 | [9 empty] | 102.28 |  |  | 90.41
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 33.06 | [8 empty] | 67.74 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 91.81 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.10
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 8.20 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.73
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 8.20 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.67
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 66.95 | [8 empty] | 32.20 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.22
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 489464.19 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.28 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.07 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.01 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.07 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.92 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.51 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.85 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 4208.59 |  |  | 5362 |  |  |  | 900 | [10 empty] | 61.26 |  |  |  | 61.26 | [5 empty] | 53.24 |  |  | 61.04 |  |  |  | 10.76 |  | 7.38 | [8 empty] | 31.36 |  |  |  |  | 0.00
1985 |  |  |  | 5235.09 |  |  | 6272 |  |  |  | 885 | [10 empty] | 71.64 |  |  |  | 71.64 | [5 empty] | 67.53 |  |  | 71.60 |  |  |  | 6.13 |  | 4.68 | [8 empty] | 23.68 |  |  |  |  | 0.00
1986 |  |  |  | 7160.64 |  |  | 8346 |  |  |  | 885 | [10 empty] | 95.33 |  |  |  | 95.33 | [5 empty] | 92.36 |  |  | 95.27 |  |  |  | 4.67 |  | 4.67 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 5168.12 |  |  | 6135 |  |  |  | 885 | [10 empty] | 70.07 |  |  |  | 70.07 | [5 empty] | 66.66 |  |  | 70.03 |  |  |  | 5.44 |  | 4.03 | [8 empty] | 25.90 |  |  |  |  | 0.00
1988 |  |  |  | 5068.16 |  |  | 5952 |  |  |  | 885 | [10 empty] | 67.79 |  |  |  | 67.79 | [5 empty] | 65.20 |  |  | 67.76 |  |  |  | 5.40 |  | 3.87 | [8 empty] | 28.34 |  |  |  |  | 0.00
1989 |  |  |  | 5412.76 |  |  | 7073 |  |  |  | 885 | [10 empty] | 80.79 |  |  |  | 80.79 | [5 empty] | 69.82 |  |  | 80.74 |  |  |  | 19.04 |  | 18.99 | [8 empty] | 0.21 |  |  |  |  | 0.00
1990 |  |  |  | 6117.27 |  |  | 7261 |  |  |  | 885 | [10 empty] | 82.90 |  |  |  | 82.90 | [5 empty] | 78.91 |  |  | 82.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.10 |  |  |  |  | 0.00
1991 |  |  |  | 5346.13 |  |  | 7065 |  |  |  | 885 | [10 empty] | 80.65 |  |  |  | 80.65 | [5 empty] | 68.96 |  |  | 80.65 |  |  |  | 0.72 |  | 0.58 | [8 empty] | 18.77 |  |  |  |  | 0.00
1992 |  |  |  | 7515.20 |  |  | 8532 |  |  |  | 885 | [10 empty] | 97.14 |  |  |  | 97.14 | [5 empty] | 96.67 |  |  | 97.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.86 |  |  |  |  | 0.00
1993 |  |  |  | 6109.46 |  |  | 7258 |  |  |  | 885 | [10 empty] | 82.87 |  |  |  | 82.87 | [5 empty] | 78.81 |  |  | 82.85 |  |  |  | 1.44 |  | 1.21 | [8 empty] | 15.92 |  |  |  |  | 0.00
1994 |  |  |  | 4456.04 |  |  | 6022 |  |  |  | 885 | [10 empty] | 68.77 |  |  |  | 68.77 | [5 empty] | 57.48 |  |  | 68.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.23 |  |  |  |  | 0.00
1995 |  |  |  | 7561.35 |  |  | 8478 |  |  |  | 885 | [10 empty] | 96.80 |  |  |  | 96.80 | [5 empty] | 97.53 |  |  | 96.78 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 3.17 |  |  |  |  | 0.00
1996 |  |  |  | 7155.13 |  |  | 7829 |  |  |  | 923 | [10 empty] | 89.60 |  |  |  | 89.60 | [5 empty] | 88.24 |  |  | 89.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.40 |  |  |  |  | 0.00
1997 |  |  |  | 7267.91 |  |  | 7805 |  |  |  | 948 | [10 empty] | 89.87 |  |  |  | 89.87 | [5 empty] | 87.49 |  |  | 89.10 |  |  |  | 1.52 |  | 1.39 | [8 empty] | 8.75 |  |  |  |  | 0.00
1998 |  |  |  | 8188.92 |  |  | 8638 |  |  |  | 953 | [10 empty] | 98.71 |  |  |  | 98.71 | [5 empty] | 98.07 |  |  | 98.61 |  |  |  | 1.29 |  | 1.29 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 7376.30 |  |  | 7779 |  |  |  | 954 | [10 empty] | 88.85 |  |  |  | 88.85 | [5 empty] | 88.26 |  |  | 88.80 |  |  |  | 0.74 |  | 0.66 | [8 empty] | 10.49 |  |  |  |  | 0.00
2000 |  |  |  | 6358.81 |  |  | 6688 |  |  |  | 966 | [10 empty] | 76.23 |  |  |  | 76.23 | [5 empty] | 75.02 |  |  | 76.14 |  |  |  | 0.46 |  | 0.35 | [8 empty] | 23.42 |  |  |  |  | 0.00
2001 |  |  |  | 6757.53 |  |  | 7095 |  |  |  | 966 | [10 empty] | 81.02 |  |  |  | 81.02 | [5 empty] | 79.86 |  |  | 80.99 |  |  |  | 0.87 |  | 0.71 | [8 empty] | 18.27 |  |  |  |  | 0.00
2002 |  |  |  | 7379.52 |  |  | 7645 |  |  |  | 966 | [10 empty] | 87.28 |  |  |  | 87.28 | [5 empty] | 87.21 |  |  | 87.27 |  |  |  | 0.52 |  | 0.46 | [8 empty] | 12.26 |  |  |  |  | 0.00
2003 |  |  |  | 7352.06 |  |  | 7564 |  |  |  | 966 | [10 empty] | 86.37 |  |  |  | 86.37 | [5 empty] | 86.88 |  |  | 86.35 |  |  |  | 1.14 |  | 1.00 | [8 empty] | 12.64 |  |  |  |  | 0.00
2004 |  |  |  | 8243.34 |  |  | 8413 |  |  |  | 966 | [10 empty] | 95.80 |  |  |  | 95.80 | [5 empty] | 97.15 |  |  | 95.78 |  |  |  | 4.20 |  | 4.20 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 7469.40 |  |  | 7746 |  |  |  | 966 | [10 empty] | 88.44 |  |  |  | 88.44 | [5 empty] | 88.26 |  |  | 88.41 |  |  |  | 0.69 |  | 0.61 | [8 empty] | 10.95 |  |  |  |  | 0.00
2006 |  |  |  | 7521.40 |  |  | 7783 |  |  |  | 966 | [10 empty] | 88.86 |  |  |  | 88.86 | [5 empty] | 88.88 |  |  | 88.85 |  |  |  | 0.29 |  | 0.26 | [8 empty] | 10.88 |  |  |  |  | 0.00
2007 |  |  |  | 8479.04 |  |  | 8719 |  |  |  | 966 | [10 empty] | 99.53 |  |  |  | 99.53 | [5 empty] | 100.20 |  |  | 99.53 |  |  |  | 0.47 |  | 0.47 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 7178.10 |  |  | 7404 |  |  |  | 966 | [10 empty] | 84.31 |  |  |  | 84.31 | [5 empty] | 84.59 |  |  | 84.29 |  |  |  | 2.57 |  | 2.23 | [8 empty] | 13.47 |  |  |  |  | 0.00
2009 |  |  |  | 6872.04 |  |  | 7150 |  |  |  | 966 | [10 empty] | 81.64 |  |  |  | 81.64 | [5 empty] | 81.21 |  |  | 81.62 |  |  |  | 3.94 |  | 3.35 | [8 empty] | 15.01 |  |  |  |  | 0.00
2010 |  |  |  | 8487.08 |  |  | 8681 |  |  |  | 966 | [10 empty] | 99.11 |  |  |  | 99.11 | [5 empty] | 100.29 |  |  | 99.10 |  |  |  | 0.20 |  | 0.20 | [8 empty] | 0.69 |  |  |  |  | 0.00
2011 |  |  |  | 7426.23 |  |  | 7622 |  |  |  | 966 | [10 empty] | 87.02 |  |  |  | 87.02 | [5 empty] | 87.76 |  |  | 87.01 |  |  |  | 0.66 |  | 0.58 | [8 empty] | 12.40 |  |  |  |  | 0.00
2012 |  |  |  | 7281.60 |  |  | 7456 |  |  |  | 971 | [10 empty] | 84.89 |  |  |  | 84.89 | [5 empty] | 85.37 |  |  | 84.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.11 |  |  |  |  | 0.00
2013 |  |  |  | 8369.88 |  |  | 8501 |  |  |  | 971 | [10 empty] | 97.05 |  |  |  | 97.05 | [5 empty] | 98.39 |  |  | 97.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.95 |  |  |  |  | 0.00
2014 |  |  |  | 6914.78 |  |  | 7078 |  |  |  | 971 | [10 empty] | 80.80 |  |  |  | 80.80 | [5 empty] | 81.29 |  |  | 80.80 |  |  |  | 4.41 |  | 3.72 | [8 empty] | 15.48 |  |  |  |  | 0.00
2015 |  |  |  | 7115.39 |  |  | 7301 |  |  |  | 971 | [10 empty] | 83.35 |  |  |  | 83.35 | [5 empty] | 83.65 |  |  | 83.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.65 |  |  |  |  | 0.00
2016 |  |  |  | 8658.36 |  |  | 8784 |  |  |  | 971 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6913.29 |  |  | 7079 |  |  |  | 973 | [10 empty] | 80.85 |  |  |  | 80.85 | [5 empty] | 81.11 |  |  | 80.81 |  |  |  | 5.01 |  | 4.27 | [8 empty] | 14.89 |  |  |  |  | 0.00
2018 |  |  |  | 7366.39 |  |  | 7540 |  |  |  | 973 | [10 empty] | 86.17 |  |  |  | 86.17 | [5 empty] | 86.42 |  |  | 86.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.83 |  |  |  |  | 0.00
2019 |  |  |  | 8248.44 |  |  | 8402 |  |  |  | 973 | [10 empty] | 95.92 |  |  |  | 95.92 | [5 empty] | 96.77 |  |  | 95.91 |  |  |  | 4.08 |  | 4.08 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7727.52 |  |  | 8002 |  |  |  | 973 | [10 empty] | 91.11 |  |  |  | 91.11 | [5 empty] | 90.41 |  |  | 91.10 |  |  |  | 0.73 |  | 0.67 | [8 empty] | 8.22 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1984 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 136
B. |  | Refuelling without maintenance | [20 empty] | 722 | [14 empty] | 20
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 964
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 131
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 1
Z. |  | Other | [24 empty] | 59 | [14 empty] | 27
Subtotal | [22 empty] | 722 |  |  |  | 59 | [10 empty] | 1117 |  |  |  | 172 | [11 empty] | 1
Total | [22 empty] | 781 | [14 empty] | 1290
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1984 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 16
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 27
16. |  |  | Steam generation systems | [34 empty] | 18
31. |  |  | Turbine and auxiliaries | [34 empty] | 9
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 19
42. |  |  | Electrical Power Supply Systems | [34 empty] | 16
Total | [37 empty] | 138
Highlights (2020)
Refueling Outage 25.

## SURRY-1
2020 Operating Experience
US-280 | [8 empty] | SURRY-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DOMINION (Dominion Energy)
Owner | [7 empty] | : | DOMINRES (Dominion Resources, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYSUB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-06-25
Thermal power | [12 empty] | : |  |  | 2587 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1972-07-04
Gross electrical power | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1972-12-22
Reference unit power (net) | [12 empty] | : |  |  | 838 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.422
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 38 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 48000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.035 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.59
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 21.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 32 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 7551.07 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 102.58 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.99 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 649.12 | 604.98 |  |  |  | 642.76 |  | 618.34 | [8 empty] | 643.12 |  |  | 608.69 | [6 empty] | 619.65 |  | 621.71 |  |  |  | 612.40 |  |  | 658.80 |  |  | 623.33 | [9 empty] | 648.17 |  |  | 7551.07
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 104.11 | 103.73 |  |  |  | 103.09 |  | 102.48 | [8 empty] | 103.15 |  |  | 100.88 | [6 empty] | 99.39 |  | 99.72 |  |  |  | 101.50 |  |  | 105.67 |  |  | 103.31 | [9 empty] | 103.96 |  |  | 102.58
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.99
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 268417.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 8.71 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.27 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.56 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.31 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.13 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.5 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.84 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1972 |  |  |  | 407.60 |  |  | 1048 |  |  |  | 794 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 3479.70 |  |  | 5377 |  |  |  | 788 | [10 empty] | 61.88 |  |  |  | 61.88 | [5 empty] | 50.41 |  |  | 61.38 |  |  |  | 27.15 |  | 23.06 | [8 empty] | 15.06 |  |  |  |  | 0.00
1974 |  |  |  | 3318.10 |  |  | 4800 |  |  |  | 788 | [10 empty] | 54.81 |  |  |  | 54.81 | [5 empty] | 48.07 |  |  | 54.79 |  |  |  | 32.59 |  | 26.50 | [8 empty] | 18.69 |  |  |  |  | 0.00
1975 |  |  |  | 3858.40 |  |  | 5343 |  |  |  | 788 | [10 empty] | 56.10 |  |  |  | 56.10 | [5 empty] | 56.05 |  |  | 61.16 |  |  |  | 18.03 |  | 12.34 | [8 empty] | 31.56 |  |  |  |  | 0.00
1976 |  |  |  | 4396.80 |  |  | 6010 |  |  |  | 788 | [10 empty] | 63.58 |  |  |  | 63.58 | [5 empty] | 63.52 |  |  | 68.42 |  |  |  | 18.17 |  | 14.12 | [8 empty] | 22.31 |  |  |  |  | 0.00
1977 |  |  |  | 5023.90 |  |  | 6661 |  |  |  | 776 | [10 empty] | 74.03 |  |  |  | 74.03 | [5 empty] | 73.91 |  |  | 76.04 |  |  |  | 3.67 |  | 2.82 | [8 empty] | 23.15 |  |  |  |  | 0.00
1978 |  |  |  | 4704.20 |  |  | 6291 |  |  |  | 775 | [10 empty] | 69.27 |  |  |  | 69.27 | [5 empty] | 69.29 |  |  | 71.82 |  |  |  | 8.43 |  | 6.38 | [8 empty] | 24.35 |  |  |  |  | 0.00
1979 |  |  |  | 2255.10 |  |  | 3045 |  |  |  | 775 | [10 empty] | 33.22 |  |  |  | 33.22 | [5 empty] | 33.22 |  |  | 34.76 |  |  |  | 66.59 |  | 66.20 | [8 empty] | 0.59 |  |  |  |  | 0.00
1980 |  |  |  | 2472.60 |  |  | 3762 |  |  |  | 775 | [10 empty] | 42.17 |  |  |  | 42.17 | [5 empty] | 36.32 |  |  | 42.83 |  |  |  | 40.05 |  | 28.17 | [8 empty] | 29.66 |  |  |  |  | 0.00
1981 |  |  |  | 2377.40 |  |  | 3403 |  |  |  | 775 | [10 empty] | 39.05 |  |  |  | 39.05 | [5 empty] | 35.02 |  |  | 38.85 |  |  |  | 11.43 |  | 5.04 | [8 empty] | 55.91 |  |  |  |  | 0.00
1982 |  |  |  | 5483.10 |  |  | 7776 |  |  |  | 775 | [10 empty] | 89.22 |  |  |  | 89.22 | [5 empty] | 80.76 |  |  | 88.77 |  |  |  | 7.28 |  | 7.01 | [8 empty] | 3.77 |  |  |  |  | 0.00
1983 |  |  |  | 3517.10 |  |  | 5010 |  |  |  | 775 | [10 empty] | 56.29 |  |  |  | 56.41 | [5 empty] | 51.81 |  |  | 57.19 |  |  |  | 3.64 |  | 2.13 | [8 empty] | 41.45 |  |  |  |  | 0.13
1984 |  |  |  | 3334.11 |  |  | 5138 |  |  |  | 775 | [10 empty] | 58.15 |  |  |  | 58.15 | [5 empty] | 48.98 |  |  | 58.49 |  |  |  | 4.21 |  | 2.56 | [8 empty] | 39.30 |  |  |  |  | 0.00
1985 |  |  |  | 5618.28 |  |  | 7827 |  |  |  | 779 | [10 empty] | 89.33 |  |  |  | 89.33 | [5 empty] | 82.28 |  |  | 89.35 |  |  |  | 10.30 |  | 10.26 | [8 empty] | 0.41 |  |  |  |  | 0.00
1986 |  |  |  | 4488.63 |  |  | 6013 |  |  |  | 781 | [10 empty] | 68.08 |  |  |  | 68.08 | [5 empty] | 65.61 |  |  | 68.64 |  |  |  | 3.77 |  | 2.67 | [8 empty] | 29.25 |  |  |  |  | 0.00
1987 |  |  |  | 4633.40 |  |  | 6113 |  |  |  | 781 | [10 empty] | 70.14 |  |  |  | 70.14 | [5 empty] | 67.72 |  |  | 69.78 |  |  |  | 16.11 |  | 13.47 | [8 empty] | 16.39 |  |  |  |  | 0.00
1988 |  |  |  | 2685.03 |  |  | 3632 |  |  |  | 781 | [10 empty] | 18.73 |  |  |  | 18.73 | [5 empty] | 39.14 |  |  | 41.35 |  |  |  | 73.97 |  | 53.22 | [8 empty] | 28.06 |  |  |  |  | 0.00
1989 |  |  |  | 3170.53 |  |  | 4217 |  |  |  | 781 | [10 empty] | 46.83 |  |  |  | 46.83 | [5 empty] | 46.34 |  |  | 48.14 |  |  |  | 53.17 |  | 53.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 4772.20 |  |  | 6655 |  |  |  | 781 | [10 empty] | 74.91 |  |  |  | 74.91 | [5 empty] | 69.75 |  |  | 75.97 |  |  |  | 4.53 |  | 3.55 | [8 empty] | 21.54 |  |  |  |  | 0.00
1991 |  |  |  | 6590.94 |  |  | 8760 |  |  |  | 781 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 96.34 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 5223.79 |  |  | 7033 |  |  |  | 781 | [10 empty] | 79.61 |  |  |  | 79.61 | [5 empty] | 76.15 |  |  | 80.07 |  |  |  | 3.23 |  | 2.66 | [8 empty] | 17.74 |  |  |  |  | 0.00
1993 |  |  |  | 6229.24 |  |  | 8402 |  |  |  | 781 | [10 empty] | 95.89 |  |  |  | 95.89 | [5 empty] | 91.05 |  |  | 95.91 |  |  |  | 1.52 |  | 1.48 | [8 empty] | 2.64 |  |  |  |  | 0.00
1994 |  |  |  | 4881.92 |  |  | 6560 |  |  |  | 781 | [10 empty] | 74.30 |  |  |  | 74.30 | [5 empty] | 71.36 |  |  | 74.89 |  |  |  | 0.41 |  | 0.30 | [8 empty] | 25.39 |  |  |  |  | 0.00
1995 |  |  |  | 5746.95 |  |  | 7505 |  |  |  | 784 | [10 empty] | 85.42 |  |  |  | 85.42 | [5 empty] | 83.64 |  |  | 85.67 |  |  |  | 2.81 |  | 2.47 | [8 empty] | 12.11 |  |  |  |  | 0.00
1996 |  |  |  | 7137.78 |  |  | 8784 |  |  |  | 801 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.45 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 5640.47 |  |  | 7067 |  |  |  | 801 | [10 empty] | 80.74 |  |  |  | 80.74 | [5 empty] | 80.39 |  |  | 80.67 |  |  |  | 3.86 |  | 3.24 | [8 empty] | 16.02 |  |  |  |  | 0.00
1998 |  |  |  | 5752.38 |  |  | 7170 |  |  |  | 801 | [10 empty] | 81.87 |  |  |  | 81.87 | [5 empty] | 81.98 |  |  | 81.85 |  |  |  | 6.87 |  | 6.04 | [8 empty] | 12.09 |  |  |  |  | 0.00
1999 |  |  |  | 7116.20 |  |  | 8760 |  |  |  | 801 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.42 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 6548.43 |  |  | 8188 |  |  |  | 801 | [10 empty] | 93.23 |  |  |  | 93.23 | [5 empty] | 93.07 |  |  | 93.21 |  |  |  | 0.34 |  | 0.32 | [8 empty] | 6.45 |  |  |  |  | 0.00
2001 |  |  |  | 5941.63 |  |  | 7380 |  |  |  | 810 | [10 empty] | 84.27 |  |  |  | 84.27 | [5 empty] | 83.74 |  |  | 84.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.73 |  |  |  |  | 0.00
2002 |  |  |  | 7149.46 |  |  | 8760 |  |  |  | 810 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 5419.78 |  |  | 6741 |  |  |  | 810 | [10 empty] | 76.97 |  |  |  | 76.97 | [5 empty] | 76.38 |  |  | 76.95 |  |  |  | 6.27 |  | 5.15 | [8 empty] | 17.88 |  |  |  |  | 0.00
2004 |  |  |  | 6457.13 |  |  | 7943 |  |  |  | 810 | [10 empty] | 90.45 |  |  |  | 90.45 | [5 empty] | 90.75 |  |  | 90.43 |  |  |  | 0.36 |  | 0.33 | [8 empty] | 9.22 |  |  |  |  | 0.00
2005 |  |  |  | 6746.56 |  |  | 8376 |  |  |  | 810 | [10 empty] | 95.63 |  |  |  | 95.63 | [5 empty] | 95.08 |  |  | 95.62 |  |  |  | 4.37 |  | 4.37 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 6311.00 |  |  | 7931 |  |  |  | 799 | [10 empty] | 90.56 |  |  |  | 90.56 | [5 empty] | 90.17 |  |  | 90.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.44 |  |  |  |  | 0.00
2007 |  |  |  | 6195.20 |  |  | 7720 |  |  |  | 799 | [10 empty] | 88.15 |  |  |  | 88.15 | [5 empty] | 88.51 |  |  | 88.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.85 |  |  |  |  | 0.00
2008 |  |  |  | 6890.50 |  |  | 8560 |  |  |  | 799 | [10 empty] | 97.46 |  |  |  | 97.46 | [5 empty] | 98.18 |  |  | 97.45 |  |  |  | 0.31 |  | 0.31 | [8 empty] | 2.23 |  |  |  |  | 0.00
2009 |  |  |  | 6597.35 |  |  | 8214 |  |  |  | 799 | [10 empty] | 93.78 |  |  |  | 93.78 | [5 empty] | 94.26 |  |  | 93.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.22 |  |  |  |  | 0.00
2010 |  |  |  | 6206.40 |  |  | 7724 |  |  |  | 839 | [10 empty] | 88.25 |  |  |  | 88.25 | [5 empty] | 88.30 |  |  | 88.17 |  |  |  | 1.06 |  | 0.95 | [8 empty] | 10.80 |  |  |  |  | 0.00
2011 |  |  |  | 7423.81 |  |  | 8590 |  |  |  | 839 | [10 empty] | 98.07 |  |  |  | 100.00 | [5 empty] | 101.01 |  |  | 98.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 1.93
2012 |  |  |  | 6839.54 |  |  | 8019 |  |  |  | 838 | [10 empty] | 91.30 |  |  |  | 91.30 | [5 empty] | 92.92 |  |  | 91.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.70 |  |  |  |  | 0.00
2013 |  |  |  | 6836.37 |  |  | 7980 |  |  |  | 838 | [10 empty] | 91.09 |  |  |  | 91.09 | [5 empty] | 93.12 |  |  | 91.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.91 |  |  |  |  | 0.00
2014 |  |  |  | 7570.57 |  |  | 8760 |  |  |  | 838 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.13 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 5669.30 |  |  | 6701 |  |  |  | 838 | [10 empty] | 76.50 |  |  |  | 76.50 | [5 empty] | 77.23 |  |  | 76.50 |  |  |  | 11.35 |  | 9.80 | [8 empty] | 13.70 |  |  |  |  | 0.00
2016 |  |  |  | 7111.17 |  |  | 8294 |  |  |  | 838 | [10 empty] | 94.42 |  |  |  | 94.42 | [5 empty] | 96.61 |  |  | 94.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.58 |  |  |  |  | 0.00
2017 |  |  |  | 7513.73 |  |  | 8720 |  |  |  | 838 | [10 empty] | 99.54 |  |  |  | 99.54 | [5 empty] | 102.35 |  |  | 99.54 |  |  |  | 0.46 |  | 0.46 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 6561.75 |  |  | 7671 |  |  |  | 838 | [10 empty] | 87.56 |  |  |  | 87.56 | [5 empty] | 89.39 |  |  | 87.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.44 |  |  |  |  | 0.00
2019 |  |  |  | 6642.08 |  |  | 7754 |  |  |  | 838 | [10 empty] | 88.53 |  |  |  | 88.53 | [5 empty] | 90.48 |  |  | 88.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.47 |  |  |  |  | 0.00
2020 |  |  |  | 7551.07 |  |  | 8783 |  |  |  | 838 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.58 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1972 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 463
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 794
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 334
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 154
L. |  | Human factor related | [39 empty] | 15
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 5
Z. |  | Other | [39 empty] | 95
Subtotal | [37 empty] | 1130 |  |  |  | 728 | [11 empty] | 5
Total | [22 empty] | 0 | [14 empty] | 1863
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1972 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 0
12. |  |  | Reactor I&C Systems | [34 empty] | 26
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 164
16. |  |  | Steam generation systems | [34 empty] | 45
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 18
32. |  |  | Feedwater and Main Steam System | [34 empty] | 71
34. |  |  | Miscellaneous Systems | [34 empty] | 39
41. |  |  | Main Generator Systems | [34 empty] | 24
42. |  |  | Electrical Power Supply Systems | [34 empty] | 71
Total | [37 empty] | 469

## SURRY-2
2020 Operating Experience
US-281 | [8 empty] | SURRY-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DOMINION (Dominion Energy)
Owner | [7 empty] | : | DOMINRES (Dominion Resources, Inc.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYSUB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-06-25
Thermal power | [12 empty] | : |  |  | 2587 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-03-10
Gross electrical power | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-05-01
Reference unit power (net) | [12 empty] | : |  |  | 838 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.422
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 38 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 48000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.035 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.59
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 21.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 32 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6789.08 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.25 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.25 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.75 %
Load Factor (LF) | [18 empty] | : | 92.23 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.23 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 770 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 648.76 | 603.18 |  |  |  | 645.30 |  | 572.85 | [8 empty] | 32.06 |  |  | 524.15 | [6 empty] | 621.11 |  | 625.02 |  |  |  | 609.53 |  |  | 637.65 |  |  | 624.75 | [9 empty] | 644.71 |  |  | 6789.08
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 6.50 |  |  | 89.82 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.25
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 6.50 |  |  | 89.82 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.25
LF [%] |  |  |  |  | 104.06 | 103.42 |  |  |  | 103.50 |  | 94.94 | [8 empty] | 5.14 |  |  | 86.87 | [6 empty] | 99.62 |  | 100.25 |  |  |  | 101.02 |  |  | 102.27 |  |  | 103.54 | [9 empty] | 103.41 |  |  | 92.23
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 6.45 |  |  | 89.86 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.23
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 93.50 |  |  | 10.18 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.75
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 268157.65 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.19 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.75 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.27 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.81 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.93 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.74 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.06 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.01 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 3377.50 |  |  | 5392 |  |  |  | 790 | [10 empty] | 77.93 |  |  |  | 77.93 | [5 empty] | 66.14 |  |  | 77.09 |  |  |  | 5.82 |  | 4.82 | [8 empty] | 17.25 |  |  |  |  | 0.00
1974 |  |  |  | 2660.50 |  |  | 3854 |  |  |  | 788 | [10 empty] | 44.00 |  |  |  | 44.00 | [5 empty] | 38.54 |  |  | 44.00 |  |  |  | 36.59 |  | 25.39 | [8 empty] | 30.61 |  |  |  |  | 0.00
1975 |  |  |  | 5053.10 |  |  | 6967 |  |  |  | 788 | [10 empty] | 73.25 |  |  |  | 73.25 | [5 empty] | 73.20 |  |  | 79.53 |  |  |  | 11.31 |  | 9.35 | [8 empty] | 17.40 |  |  |  |  | 0.00
1976 |  |  |  | 3343.40 |  |  | 4585 |  |  |  | 788 | [10 empty] | 48.34 |  |  |  | 48.34 | [5 empty] | 48.30 |  |  | 52.20 |  |  |  | 43.48 |  | 37.19 | [8 empty] | 14.47 |  |  |  |  | 0.00
1977 |  |  |  | 4457.30 |  |  | 5980 |  |  |  | 776 | [10 empty] | 65.56 |  |  |  | 65.56 | [5 empty] | 65.57 |  |  | 68.26 |  |  |  | 27.45 |  | 24.81 | [8 empty] | 9.63 |  |  |  |  | 0.00
1978 |  |  |  | 5372.00 |  |  | 7244 |  |  |  | 775 | [10 empty] | 79.12 |  |  |  | 79.12 | [5 empty] | 79.13 |  |  | 82.69 |  |  |  | 4.04 |  | 3.33 | [8 empty] | 17.54 |  |  |  |  | 0.00
1979 |  |  |  | 611.50 |  |  | 818 |  |  |  | 775 | [10 empty] | 9.01 |  |  |  | 9.01 | [5 empty] | 9.01 |  |  | 9.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 90.99 |  |  |  |  | 0.00
1980 |  |  |  | 2241.60 |  |  | 3139 |  |  |  | 775 | [10 empty] | 35.97 |  |  |  | 35.97 | [5 empty] | 32.93 |  |  | 35.74 |  |  |  | 2.54 |  | 0.94 | [8 empty] | 63.09 |  |  |  |  | 0.00
1981 |  |  |  | 5150.30 |  |  | 6972 |  |  |  | 775 | [10 empty] | 79.57 |  |  |  | 82.36 | [5 empty] | 75.86 |  |  | 79.59 |  |  |  | 3.12 |  | 2.65 | [8 empty] | 14.99 |  |  |  |  | 2.78
1982 |  |  |  | 5492.20 |  |  | 7729 |  |  |  | 775 | [10 empty] | 88.72 |  |  |  | 88.72 | [5 empty] | 80.90 |  |  | 88.23 |  |  |  | 1.95 |  | 1.76 | [8 empty] | 9.52 |  |  |  |  | 0.00
1983 |  |  |  | 4086.10 |  |  | 5729 |  |  |  | 775 | [10 empty] | 64.98 |  |  |  | 64.98 | [5 empty] | 60.19 |  |  | 65.40 |  |  |  | 5.41 |  | 3.71 | [8 empty] | 31.31 |  |  |  |  | 0.00
1984 |  |  |  | 5209.38 |  |  | 7327 |  |  |  | 775 | [10 empty] | 83.31 |  |  |  | 83.31 | [5 empty] | 76.52 |  |  | 83.41 |  |  |  | 16.69 |  | 16.69 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 4072.44 |  |  | 5857 |  |  |  | 775 | [10 empty] | 65.77 |  |  |  | 65.77 | [5 empty] | 59.99 |  |  | 66.86 |  |  |  | 0.32 |  | 0.21 | [8 empty] | 34.02 |  |  |  |  | 0.00
1986 |  |  |  | 4498.94 |  |  | 6072 |  |  |  | 780 | [10 empty] | 68.71 |  |  |  | 68.71 | [5 empty] | 65.80 |  |  | 69.32 |  |  |  | 14.94 |  | 12.07 | [8 empty] | 19.23 |  |  |  |  | 0.00
1987 |  |  |  | 4790.95 |  |  | 6456 |  |  |  | 781 | [10 empty] | 73.60 |  |  |  | 73.60 | [5 empty] | 70.03 |  |  | 73.70 |  |  |  | 22.97 |  | 21.94 | [8 empty] | 4.45 |  |  |  |  | 0.00
1988 |  |  |  | 3570.90 |  |  | 4993 |  |  |  | 781 | [10 empty] | 56.55 |  |  |  | 56.55 | [5 empty] | 52.05 |  |  | 56.84 |  |  |  | 18.21 |  | 12.59 | [8 empty] | 30.86 |  |  |  |  | 0.00
1989 |  |  |  | 893.58 |  |  | 1355 |  |  |  | 781 | [10 empty] | 13.32 |  |  |  | 13.32 | [5 empty] | 13.06 |  |  | 15.47 |  |  |  | 48.28 |  | 12.44 | [8 empty] | 74.24 |  |  |  |  | 0.00
1990 |  |  |  | 5837.77 |  |  | 7919 |  |  |  | 781 | [10 empty] | 84.82 |  |  |  | 84.82 | [5 empty] | 85.33 |  |  | 90.40 |  |  |  | 15.18 |  | 15.18 | [8 empty] | 0.00 |  |  |  |  | 0.00
1991 |  |  |  | 3985.21 |  |  | 5886 |  |  |  | 781 | [10 empty] | 66.55 |  |  |  | 66.55 | [5 empty] | 58.25 |  |  | 67.19 |  |  |  | 17.38 |  | 14.00 | [8 empty] | 19.45 |  |  |  |  | 0.00
1992 |  |  |  | 6426.48 |  |  | 8470 |  |  |  | 781 | [10 empty] | 96.33 |  |  |  | 96.33 | [5 empty] | 93.68 |  |  | 96.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.67 |  |  |  |  | 0.00
1993 |  |  |  | 4541.66 |  |  | 6283 |  |  |  | 781 | [10 empty] | 71.02 |  |  |  | 71.02 | [5 empty] | 66.38 |  |  | 71.72 |  |  |  | 9.76 |  | 7.68 | [8 empty] | 21.30 |  |  |  |  | 0.00
1994 |  |  |  | 6260.97 |  |  | 8251 |  |  |  | 781 | [10 empty] | 94.05 |  |  |  | 94.05 | [5 empty] | 91.51 |  |  | 94.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.95 |  |  |  |  | 0.00
1995 |  |  |  | 5517.38 |  |  | 7087 |  |  |  | 787 | [10 empty] | 80.65 |  |  |  | 80.65 | [5 empty] | 79.96 |  |  | 80.90 |  |  |  | 7.47 |  | 6.51 | [8 empty] | 12.84 |  |  |  |  | 0.00
1996 |  |  |  | 6081.46 |  |  | 7539 |  |  |  | 801 | [10 empty] | 85.88 |  |  |  | 85.88 | [5 empty] | 86.43 |  |  | 85.83 |  |  |  | 1.69 |  | 1.48 | [8 empty] | 12.64 |  |  |  |  | 0.00
1997 |  |  |  | 6451.27 |  |  | 8034 |  |  |  | 801 | [10 empty] | 91.75 |  |  |  | 91.75 | [5 empty] | 91.94 |  |  | 91.71 |  |  |  | 1.33 |  | 1.23 | [8 empty] | 7.02 |  |  |  |  | 0.00
1998 |  |  |  | 7178.88 |  |  | 8760 |  |  |  | 801 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.31 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 5874.83 |  |  | 7493 |  |  |  | 801 | [10 empty] | 85.56 |  |  |  | 85.56 | [5 empty] | 83.73 |  |  | 85.54 |  |  |  | 3.20 |  | 2.83 | [8 empty] | 11.61 |  |  |  |  | 0.00
2000 |  |  |  | 6539.43 |  |  | 8022 |  |  |  | 801 | [10 empty] | 91.33 |  |  |  | 91.33 | [5 empty] | 92.94 |  |  | 91.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.67 |  |  |  |  | 0.00
2001 |  |  |  | 6720.74 |  |  | 8203 |  |  |  | 815 | [10 empty] | 93.68 |  |  |  | 93.68 | [5 empty] | 94.14 |  |  | 93.64 |  |  |  | 0.54 |  | 0.50 | [8 empty] | 5.82 |  |  |  |  | 0.00
2002 |  |  |  | 6523.67 |  |  | 7966 |  |  |  | 815 | [10 empty] | 90.97 |  |  |  | 90.97 | [5 empty] | 91.38 |  |  | 90.94 |  |  |  | 1.18 |  | 1.09 | [8 empty] | 7.95 |  |  |  |  | 0.00
2003 |  |  |  | 5612.12 |  |  | 6861 |  |  |  | 815 | [10 empty] | 78.33 |  |  |  | 78.33 | [5 empty] | 78.61 |  |  | 78.32 |  |  |  | 2.04 |  | 1.63 | [8 empty] | 20.03 |  |  |  |  | 0.00
2004 |  |  |  | 7051.74 |  |  | 8606 |  |  |  | 815 | [10 empty] | 97.98 |  |  |  | 97.98 | [5 empty] | 98.50 |  |  | 97.97 |  |  |  | 2.02 |  | 2.02 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 6488.55 |  |  | 8046 |  |  |  | 815 | [10 empty] | 91.86 |  |  |  | 91.86 | [5 empty] | 90.87 |  |  | 91.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.14 |  |  |  |  | 0.00
2006 |  |  |  | 6189.36 |  |  | 7705 |  |  |  | 799 | [10 empty] | 87.97 |  |  |  | 87.97 | [5 empty] | 88.43 |  |  | 87.96 |  |  |  | 1.32 |  | 1.17 | [8 empty] | 10.86 |  |  |  |  | 0.00
2007 |  |  |  | 7086.34 |  |  | 8760 |  |  |  | 799 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.24 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 6606.84 |  |  | 8205 |  |  |  | 799 | [10 empty] | 93.42 |  |  |  | 93.42 | [5 empty] | 94.14 |  |  | 93.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.58 |  |  |  |  | 0.00
2009 |  |  |  | 6412.30 |  |  | 8026 |  |  |  | 799 | [10 empty] | 91.63 |  |  |  | 91.63 | [5 empty] | 91.61 |  |  | 91.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.37 |  |  |  |  | 0.00
2010 |  |  |  | 6966.03 |  |  | 8646 |  |  |  | 799 | [10 empty] | 98.70 |  |  |  | 98.70 | [5 empty] | 99.53 |  |  | 98.70 |  |  |  | 1.30 |  | 1.30 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 5605.67 |  |  | 6771 |  |  |  | 839 | [10 empty] | 77.88 |  |  |  | 77.88 | [5 empty] | 78.12 |  |  | 77.29 |  |  |  | 6.89 |  | 5.76 | [8 empty] | 16.36 |  |  |  |  | 0.00
2012 |  |  |  | 6775.06 |  |  | 8001 |  |  |  | 838 | [10 empty] | 91.10 |  |  |  | 91.10 | [5 empty] | 92.04 |  |  | 91.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.90 |  |  |  |  | 0.00
2013 |  |  |  | 7568.22 |  |  | 8760 |  |  |  | 838 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 103.09 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 6761.76 |  |  | 7882 |  |  |  | 838 | [10 empty] | 89.96 |  |  |  | 89.96 | [5 empty] | 92.11 |  |  | 89.98 |  |  |  | 1.51 |  | 1.38 | [8 empty] | 8.66 |  |  |  |  | 0.00
2015 |  |  |  | 6120.41 |  |  | 7250 |  |  |  | 838 | [10 empty] | 82.77 |  |  |  | 82.77 | [5 empty] | 83.37 |  |  | 82.76 |  |  |  | 3.01 |  | 2.57 | [8 empty] | 14.66 |  |  |  |  | 0.00
2016 |  |  |  | 7499.35 |  |  | 8691 |  |  |  | 838 | [10 empty] | 98.94 |  |  |  | 98.94 | [5 empty] | 101.88 |  |  | 98.94 |  |  |  | 1.06 |  | 1.06 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6913.92 |  |  | 8057 |  |  |  | 838 | [10 empty] | 91.98 |  |  |  | 91.98 | [5 empty] | 94.18 |  |  | 91.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.02 |  |  |  |  | 0.00
2018 |  |  |  | 6657.38 |  |  | 7788 |  |  |  | 838 | [10 empty] | 88.90 |  |  |  | 88.90 | [5 empty] | 90.69 |  |  | 88.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.10 |  |  |  |  | 0.00
2019 |  |  |  | 7530.89 |  |  | 8760 |  |  |  | 838 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.59 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 6789.08 |  |  | 8014 |  |  |  | 838 | [10 empty] | 91.25 |  |  |  | 91.25 | [5 empty] | 92.23 |  |  | 91.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.75 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1973 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 438
B. |  | Refuelling without maintenance | [20 empty] | 769 | [14 empty] | 16
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1088
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 179
E. |  | Testing of plant systems or components | [35 empty] | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 19
L. |  | Human factor related | [39 empty] | 14
Z. |  | Other | [35 empty] | 4 |  |  |  | 0
Subtotal | [22 empty] | 769 | [14 empty] | 1289 |  |  |  | 471
Total | [22 empty] | 769 | [14 empty] | 1760
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1973 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 31
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 52
15. |  |  | Reactor Cooling Systems | [34 empty] | 25
16. |  |  | Steam generation systems | [34 empty] | 104
31. |  |  | Turbine and auxiliaries | [34 empty] | 90
32. |  |  | Feedwater and Main Steam System | [34 empty] | 94
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 15
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 22
Total | [37 empty] | 445
Highlights (2020)
Refueling Outage 29. 5/3/20, Breaker open 5/3/20 0022, Breaker closed 6/4/20 0119

## SUSQUEHANNA-1
2020 Operating Experience
US-387 | [8 empty] | SUSQUEHANNA-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PPL_SUSQ (PPL Susquehanna, LLC)
Owner | [7 empty] | : | PPL_CORP (PPL Corporation (former PENNSYLVANIA POWER & LIGHT CO. (PP&L)))
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 2) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-11-02
Thermal power | [12 empty] | : |  |  | 3952 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-11-16
Gross electrical power | [12 empty] | : |  |  | 1330 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-06-08
Reference unit power (net) | [12 empty] | : |  |  | 1257 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.19
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 304
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.372
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 36000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.57 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.69
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19.32 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9332.24 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.97 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.69 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.67 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.69 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.64 %
Load Factor (LF) | [18 empty] | : | 84.52 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 88.68 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 994 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 899.82 | 745.58 |  |  |  | 612.76 |  | 3.06 | [8 empty] | 563.72 |  |  | 897.54 | [6 empty] | 933.62 |  | 931.45 |  |  |  | 913.26 |  |  | 949.66 |  |  | 924.48 | [9 empty] | 957.28 |  |  | 9332.24
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 87.21 |  | 3.29 | [8 empty] | 75.98 |  |  | 96.78 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.69
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 87.21 |  | 3.29 | [8 empty] | 75.98 |  |  | 96.78 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.69
LF [%] |  |  |  |  | 96.22 | 85.22 |  |  |  | 65.52 |  | 0.34 | [8 empty] | 60.28 |  |  | 99.17 | [6 empty] | 99.83 |  | 99.60 |  |  |  | 100.91 |  |  | 101.55 |  |  | 102.15 | [9 empty] | 102.36 |  |  | 84.52
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 87.10 |  | 3.33 | [8 empty] | 72.85 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.68
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 83.56 | [8 empty] | 24.02 |  |  | 3.22 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.97
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 16.73 | [8 empty] | 24.02 |  |  | 3.22 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.67
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 12.79 |  | 79.97 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.64
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 333133.09 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.63 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.46 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.36 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.52 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.13 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.06 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.32 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 4472.80 |  |  | 4891 |  |  |  | 1034 | [10 empty] | 76.29 |  |  |  | 76.29 | [5 empty] | 66.58 |  |  | 73.31 |  |  |  | 11.82 |  | 10.23 | [8 empty] | 13.49 |  |  |  |  | 0.00
1984 |  |  |  | 6088.14 |  |  | 6377 |  |  |  | 1032 | [10 empty] | 72.02 |  |  |  | 74.45 | [5 empty] | 67.16 |  |  | 72.60 |  |  |  | 13.03 |  | 11.15 | [8 empty] | 14.40 |  |  |  |  | 2.43
1985 |  |  |  | 5286.43 |  |  | 5469 |  |  |  | 1032 | [10 empty] | 60.37 |  |  |  | 60.37 | [5 empty] | 58.48 |  |  | 62.43 |  |  |  | 6.06 |  | 3.89 | [8 empty] | 35.74 |  |  |  |  | 0.00
1986 |  |  |  | 5839.25 |  |  | 5992 |  |  |  | 1032 | [10 empty] | 66.81 |  |  |  | 66.81 | [5 empty] | 64.59 |  |  | 68.40 |  |  |  | 12.07 |  | 9.17 | [8 empty] | 24.02 |  |  |  |  | 0.00
1987 |  |  |  | 6132.87 |  |  | 6331 |  |  |  | 1032 | [10 empty] | 70.74 |  |  |  | 70.74 | [5 empty] | 67.84 |  |  | 72.27 |  |  |  | 10.27 |  | 8.10 | [8 empty] | 21.16 |  |  |  |  | 0.00
1988 |  |  |  | 8410.06 |  |  | 8206 |  |  |  | 1032 | [10 empty] | 93.06 |  |  |  | 93.06 | [5 empty] | 92.77 |  |  | 93.42 |  |  |  | 5.00 |  | 4.90 | [8 empty] | 2.04 |  |  |  |  | 0.00
1989 |  |  |  | 6483.95 |  |  | 6447 |  |  |  | 1032 | [10 empty] | 72.15 |  |  |  | 72.15 | [5 empty] | 71.72 |  |  | 73.60 |  |  |  | 8.90 |  | 7.04 | [8 empty] | 20.81 |  |  |  |  | 0.00
1990 |  |  |  | 6446.70 |  |  | 6528 |  |  |  | 1033 | [10 empty] | 73.14 |  |  |  | 73.14 | [5 empty] | 71.24 |  |  | 74.52 |  |  |  | 4.60 |  | 3.53 | [8 empty] | 23.33 |  |  |  |  | 0.00
1991 |  |  |  | 8821.60 |  |  | 8596 |  |  |  | 1035 | [10 empty] | 98.04 |  |  |  | 98.04 | [5 empty] | 97.21 |  |  | 98.13 |  |  |  | 1.96 |  | 1.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 6400.29 |  |  | 6568 |  |  |  | 1040 | [10 empty] | 73.60 |  |  |  | 73.60 | [5 empty] | 70.06 |  |  | 74.77 |  |  |  | 7.61 |  | 6.06 | [8 empty] | 20.34 |  |  |  |  | 0.00
1993 |  |  |  | 5232.40 |  |  | 5205 |  |  |  | 1040 | [10 empty] | 57.49 |  |  |  | 57.49 | [5 empty] | 57.43 |  |  | 59.42 |  |  |  | 19.76 |  | 14.15 | [8 empty] | 28.36 |  |  |  |  | 0.00
1994 |  |  |  | 8414.45 |  |  | 8249 |  |  |  | 1040 | [10 empty] | 94.18 |  |  |  | 94.18 | [5 empty] | 92.36 |  |  | 94.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.82 |  |  |  |  | 0.00
1995 |  |  |  | 7432.27 |  |  | 7126 |  |  |  | 1073 | [10 empty] | 81.11 |  |  |  | 81.11 | [5 empty] | 79.03 |  |  | 81.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.89 |  |  |  |  | 0.00
1996 |  |  |  | 7752.89 |  |  | 7434 |  |  |  | 1090 | [10 empty] | 84.68 |  |  |  | 84.68 | [5 empty] | 80.97 |  |  | 84.63 |  |  |  | 3.04 |  | 2.65 | [8 empty] | 12.67 |  |  |  |  | 0.00
1997 |  |  |  | 9085.32 |  |  | 8274 |  |  |  | 1090 | [10 empty] | 94.47 |  |  |  | 94.47 | [5 empty] | 95.15 |  |  | 94.45 |  |  |  | 5.53 |  | 5.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 7652.80 |  |  | 7015 |  |  |  | 1090 | [10 empty] | 81.47 |  |  |  | 81.47 | [5 empty] | 80.15 |  |  | 80.08 |  |  |  | 6.20 |  | 5.38 | [8 empty] | 13.15 |  |  |  |  | 0.00
1999 |  |  |  | 8814.47 |  |  | 8234 |  |  |  | 1090 | [10 empty] | 94.01 |  |  |  | 94.01 | [5 empty] | 92.31 |  |  | 94.00 |  |  |  | 5.99 |  | 5.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 8180.56 |  |  | 7598 |  |  |  | 1090 | [10 empty] | 86.52 |  |  |  | 86.52 | [5 empty] | 85.44 |  |  | 86.50 |  |  |  | 0.33 |  | 0.28 | [8 empty] | 13.19 |  |  |  |  | 0.00
2001 |  |  |  | 9412.96 |  |  | 8718 |  |  |  | 1090 | [10 empty] | 99.53 |  |  |  | 99.53 | [5 empty] | 98.58 |  |  | 99.52 |  |  |  | 0.23 |  | 0.23 | [8 empty] | 0.25 |  |  |  |  | 0.00
2002 |  |  |  | 8026.62 |  |  | 7493 |  |  |  | 1105 | [10 empty] | 85.67 |  |  |  | 85.67 | [5 empty] | 83.39 |  |  | 85.54 |  |  |  | 0.64 |  | 0.55 | [8 empty] | 13.78 |  |  |  |  | 0.00
2003 |  |  |  | 9359.91 |  |  | 8585 |  |  |  | 1105 | [10 empty] | 98.04 |  |  |  | 98.04 | [5 empty] | 96.70 |  |  | 98.00 |  |  |  | 1.79 |  | 1.79 | [8 empty] | 0.17 |  |  |  |  | 0.00
2004 |  |  |  | 8027.00 |  |  | 7359 |  |  |  | 1135 | [10 empty] | 84.08 |  |  |  | 84.08 | [5 empty] | 81.22 |  |  | 83.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.92 |  |  |  |  | 0.00
2005 |  |  |  | 9442.62 |  |  | 8357 |  |  |  | 1105 | [10 empty] | 95.41 |  |  |  | 95.41 | [5 empty] | 97.55 |  |  | 95.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.59 |  |  |  |  | 0.00
2006 |  |  |  | 8602.67 |  |  | 7639 |  |  |  | 1135 | [10 empty] | 87.24 |  |  |  | 87.24 | [5 empty] | 86.52 |  |  | 87.20 |  |  |  | 2.27 |  | 2.02 | [8 empty] | 10.73 |  |  |  |  | 0.00
2007 |  |  |  | 9456.33 |  |  | 8349 |  |  |  | 1149 | [10 empty] | 95.37 |  |  |  | 95.37 | [5 empty] | 93.95 |  |  | 95.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.63 |  |  |  |  | 0.00
2008 |  |  |  | 9005.70 |  |  | 7704 |  |  |  | 1149 | [10 empty] | 87.72 |  |  |  | 87.72 | [5 empty] | 89.23 |  |  | 87.70 |  |  |  | 0.33 |  | 0.29 | [8 empty] | 11.99 |  |  |  |  | 0.00
2009 |  |  |  | 10475.53 |  |  | 8760 |  |  |  | 1185 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.91 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 8294.36 |  |  | 6958 |  |  |  | 1239 | [10 empty] | 80.00 |  |  |  | 80.00 | [5 empty] | 77.82 |  |  | 79.43 |  |  |  | 7.48 |  | 6.47 | [8 empty] | 13.53 |  |  |  |  | 0.00
2011 |  |  |  | 9499.00 |  |  | 7588 |  |  |  | 1260 | [10 empty] | 86.83 |  |  |  | 86.83 | [5 empty] | 86.42 |  |  | 86.62 |  |  |  | 1.09 |  | 0.98 | [8 empty] | 12.19 |  |  |  |  | 0.00
2012 |  |  |  | 7814.86 |  |  | 6382 |  |  |  | 1257 | [10 empty] | 72.69 |  |  |  | 72.69 | [5 empty] | 70.78 |  |  | 72.65 |  |  |  | 4.77 |  | 3.64 | [8 empty] | 23.67 |  |  |  |  | 0.00
2013 |  |  |  | 9898.58 |  |  | 7860 |  |  |  | 1257 | [10 empty] | 89.73 |  |  |  | 89.73 | [5 empty] | 89.88 |  |  | 89.72 |  |  |  | 0.27 |  | 0.24 | [8 empty] | 10.02 |  |  |  |  | 0.00
2014 |  |  |  | 9150.78 |  |  | 7276 |  |  |  | 1257 | [10 empty] | 83.06 |  |  |  | 83.06 | [5 empty] | 83.10 |  |  | 83.06 |  |  |  | 1.94 |  | 6.11 | [8 empty] | 10.83 |  |  |  |  | 0.00
2015 |  |  |  | 10908.97 |  |  | 8584 |  |  |  | 1257 | [10 empty] | 97.99 |  |  |  | 97.99 | [5 empty] | 99.07 |  |  | 97.99 |  |  |  | 2.01 |  | 2.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 8749.66 |  |  | 7016 |  |  |  | 1257 | [10 empty] | 79.86 |  |  |  | 79.86 | [5 empty] | 79.24 |  |  | 79.87 |  |  |  | 6.81 |  | 5.83 | [8 empty] | 14.31 |  |  |  |  | 0.00
2017 |  |  |  | 11026.09 |  |  | 8711 |  |  |  | 1257 | [10 empty] | 99.44 |  |  |  | 99.44 | [5 empty] | 100.13 |  |  | 99.44 |  |  |  | 0.56 |  | 0.56 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 9582.31 |  |  | 7840 |  |  |  | 1257 | [10 empty] | 89.49 |  |  |  | 89.49 | [5 empty] | 87.02 |  |  | 89.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.51 |  |  |  |  | 0.00
2019 |  |  |  | 11105.06 |  |  | 8760 |  |  |  | 1257 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.85 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9332.24 |  |  | 7790 |  |  |  | 1257 | [10 empty] | 88.69 |  |  |  | 88.69 | [5 empty] | 84.52 |  |  | 88.68 |  |  |  | 3.97 |  | 3.67 | [8 empty] | 7.64 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1983 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 233
B. |  | Refuelling without maintenance | [20 empty] | 671 | [14 empty] | 18
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 772 |  |  |  | 10
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 123
E. |  | Testing of plant systems or components | [35 empty] | 43
H. |  | Nuclear regulatory requirements | [39 empty] | 20
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 28
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 11
Z. |  | Other | [24 empty] | 322 | [10 empty] | 52 |  |  |  | 28
Subtotal | [22 empty] | 671 |  |  |  | 322 | [10 empty] | 1019 |  |  |  | 319 | [11 empty] | 6
Total | [22 empty] | 993 | [14 empty] | 1344
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1983 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 8
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 39
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 6
31. |  |  | Turbine and auxiliaries | [34 empty] | 61
32. |  |  | Feedwater and Main Steam System | [34 empty] | 36
33. |  |  | Circulating Water System | [34 empty] | 12
34. |  |  | Miscellaneous Systems | [34 empty] | 34
35. |  |  | All other I&C Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 11
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [37 empty] | 263
Highlights (2020)
Refueling Outage 21. The Turbine was manually tripped at approximately 15% power to start the Refueling outage at 00:52 on 3/28/20.

## SUSQUEHANNA-2
2020 Operating Experience
US-388 | [8 empty] | SUSQUEHANNA-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PPL_SUSQ (PPL Susquehanna, LLC)
Owner | [7 empty] | : | PPL_CORP (PPL Corporation (former PENNSYLVANIA POWER & LIGHT CO. (PP&L)))
Reactor Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-4 (Mark 2) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-11-02
Thermal power | [12 empty] | : |  |  | 3952 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-07-03
Gross electrical power | [12 empty] | : |  |  | 1330 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-02-12
Reference unit power (net) | [12 empty] | : |  |  | 1257 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.19
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 287
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.372
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 24 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 36000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.57 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.69
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 764 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.32 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 185 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10658.66 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.14 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.86 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.14 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.86 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 96.53 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 98.85 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 101 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 932.74 | 736.96 |  |  |  | 923.48 |  | 892.39 | [8 empty] | 911.38 |  |  | 814.32 | [6 empty] | 915.31 |  | 918.42 |  |  |  | 884.97 |  |  | 908.74 |  |  | 904.07 | [9 empty] | 915.89 |  |  | 10658.67
EAF [%] |  |  |  |  | 100.00 | 87.91 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 97.82 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.86
UCF [%] |  |  |  |  | 100.00 | 87.91 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 97.82 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.86
LF [%] |  |  |  |  | 99.74 | 84.24 |  |  |  | 98.75 |  | 98.60 | [8 empty] | 97.45 |  |  | 89.98 | [6 empty] | 97.87 |  | 98.20 |  |  |  | 97.78 |  |  | 97.17 |  |  | 99.89 | [9 empty] | 97.93 |  |  | 96.53
OF [%] |  |  |  |  | 100.00 | 87.93 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 97.78 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.85
FLR [%] |  |  |  |  | 0.00 | 12.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.18 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.14
UCL [%] |  |  |  |  | 0.00 | 12.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.18 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.14
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 321201.03 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.62 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.65 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.43 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.66 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.9 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.44 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 7323.31 |  |  | 7463 |  |  |  | 1032 | [10 empty] | 90.18 |  |  |  | 90.61 | [5 empty] | 84.07 |  |  | 87.24 |  |  |  | 9.39 |  | 9.39 | [8 empty] | 0.00 |  |  |  |  | 0.43
1986 |  |  |  | 5458.36 |  |  | 5730 |  |  |  | 1032 | [10 empty] | 63.50 |  |  |  | 63.50 | [5 empty] | 60.38 |  |  | 65.41 |  |  |  | 16.73 |  | 12.76 | [8 empty] | 23.74 |  |  |  |  | 0.00
1987 |  |  |  | 8598.43 |  |  | 8431 |  |  |  | 1032 | [10 empty] | 96.03 |  |  |  | 96.03 | [5 empty] | 95.11 |  |  | 96.24 |  |  |  | 3.97 |  | 3.97 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 5915.25 |  |  | 5985 |  |  |  | 1034 | [10 empty] | 66.32 |  |  |  | 66.32 | [5 empty] | 65.13 |  |  | 68.14 |  |  |  | 0.20 |  | 0.13 | [8 empty] | 33.55 |  |  |  |  | 0.00
1989 |  |  |  | 6777.04 |  |  | 6745 |  |  |  | 1038 | [10 empty] | 76.89 |  |  |  | 76.89 | [5 empty] | 74.53 |  |  | 77.00 |  |  |  | 2.10 |  | 1.65 | [8 empty] | 21.46 |  |  |  |  | 0.00
1990 |  |  |  | 8290.70 |  |  | 8143 |  |  |  | 1038 | [10 empty] | 94.41 |  |  |  | 94.41 | [5 empty] | 91.14 |  |  | 92.96 |  |  |  | 5.18 |  | 5.16 | [8 empty] | 0.43 |  |  |  |  | 0.00
1991 |  |  |  | 7041.38 |  |  | 6955 |  |  |  | 1041 | [10 empty] | 78.37 |  |  |  | 78.37 | [5 empty] | 77.21 |  |  | 79.39 |  |  |  | 3.36 |  | 2.72 | [8 empty] | 18.91 |  |  |  |  | 0.00
1992 |  |  |  | 7186.16 |  |  | 7119 |  |  |  | 1044 | [10 empty] | 80.17 |  |  |  | 80.17 | [5 empty] | 78.36 |  |  | 81.05 |  |  |  | 2.41 |  | 1.98 | [8 empty] | 17.85 |  |  |  |  | 0.00
1993 |  |  |  | 8337.86 |  |  | 8094 |  |  |  | 1044 | [10 empty] | 92.30 |  |  |  | 92.30 | [5 empty] | 91.17 |  |  | 92.40 |  |  |  | 7.70 |  | 7.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 6909.84 |  |  | 6577 |  |  |  | 1073 | [10 empty] | 74.66 |  |  |  | 74.66 | [5 empty] | 73.49 |  |  | 75.08 |  |  |  | 0.85 |  | 0.64 | [8 empty] | 24.70 |  |  |  |  | 0.00
1995 |  |  |  | 8192.74 |  |  | 7691 |  |  |  | 1094 | [10 empty] | 87.83 |  |  |  | 87.83 | [5 empty] | 85.49 |  |  | 87.80 |  |  |  | 1.91 |  | 1.71 | [8 empty] | 10.46 |  |  |  |  | 0.00
1996 |  |  |  | 9127.17 |  |  | 8346 |  |  |  | 1094 | [10 empty] | 95.03 |  |  |  | 95.03 | [5 empty] | 94.98 |  |  | 95.01 |  |  |  | 4.97 |  | 4.97 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 7732.57 |  |  | 7211 |  |  |  | 1094 | [10 empty] | 82.36 |  |  |  | 82.36 | [5 empty] | 80.69 |  |  | 82.32 |  |  |  | 2.53 |  | 2.13 | [8 empty] | 15.50 |  |  |  |  | 0.00
1998 |  |  |  | 8820.75 |  |  | 8172 |  |  |  | 1094 | [10 empty] | 93.29 |  |  |  | 93.29 | [5 empty] | 92.04 |  |  | 93.29 |  |  |  | 5.18 |  | 5.09 | [8 empty] | 1.61 |  |  |  |  | 0.00
1999 |  |  |  | 7794.67 |  |  | 7268 |  |  |  | 1094 | [10 empty] | 83.00 |  |  |  | 83.00 | [5 empty] | 81.33 |  |  | 82.97 |  |  |  | 4.59 |  | 3.99 | [8 empty] | 13.01 |  |  |  |  | 0.00
2000 |  |  |  | 9347.19 |  |  | 8587 |  |  |  | 1094 | [10 empty] | 97.76 |  |  |  | 97.76 | [5 empty] | 97.27 |  |  | 97.76 |  |  |  | 2.24 |  | 2.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 8397.15 |  |  | 7693 |  |  |  | 1111 | [10 empty] | 87.93 |  |  |  | 87.93 | [5 empty] | 86.94 |  |  | 87.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.07 |  |  |  |  | 0.00
2002 |  |  |  | 9306.16 |  |  | 8439 |  |  |  | 1111 | [10 empty] | 96.35 |  |  |  | 96.35 | [5 empty] | 95.62 |  |  | 96.34 |  |  |  | 3.65 |  | 3.65 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 8654.66 |  |  | 7701 |  |  |  | 1140 | [10 empty] | 88.15 |  |  |  | 88.15 | [5 empty] | 87.23 |  |  | 87.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.85 |  |  |  |  | 0.00
2004 |  |  |  | 10057.13 |  |  | 8784 |  |  |  | 1140 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.43 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 8885.73 |  |  | 7900 |  |  |  | 1140 | [10 empty] | 90.20 |  |  |  | 90.20 | [5 empty] | 88.97 |  |  | 90.17 |  |  |  | 2.83 |  | 2.63 | [8 empty] | 7.17 |  |  |  |  | 0.00
2006 |  |  |  | 9270.90 |  |  | 8155 |  |  |  | 1140 | [10 empty] | 93.12 |  |  |  | 93.12 | [5 empty] | 92.84 |  |  | 93.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.88 |  |  |  |  | 0.00
2007 |  |  |  | 8781.57 |  |  | 7726 |  |  |  | 1140 | [10 empty] | 88.21 |  |  |  | 88.21 | [5 empty] | 87.94 |  |  | 88.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.79 |  |  |  |  | 0.00
2008 |  |  |  | 10091.45 |  |  | 8784 |  |  |  | 1140 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.78 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 9011.13 |  |  | 7775 |  |  |  | 1140 | [10 empty] | 88.78 |  |  |  | 88.78 | [5 empty] | 90.23 |  |  | 88.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.22 |  |  |  |  | 0.00
2010 |  |  |  | 10221.22 |  |  | 8686 |  |  |  | 1190 | [10 empty] | 99.19 |  |  |  | 99.19 | [5 empty] | 98.05 |  |  | 99.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.81 |  |  |  |  | 0.00
2011 |  |  |  | 7951.26 |  |  | 6600 |  |  |  | 1260 | [10 empty] | 76.06 |  |  |  | 76.06 | [5 empty] | 74.08 |  |  | 75.34 |  |  |  | 1.51 |  | 1.17 | [8 empty] | 22.77 |  |  |  |  | 0.00
2012 |  |  |  | 9194.97 |  |  | 7609 |  |  |  | 1257 | [10 empty] | 86.65 |  |  |  | 86.65 | [5 empty] | 83.28 |  |  | 86.62 |  |  |  | 9.37 |  | 8.96 | [8 empty] | 4.39 |  |  |  |  | 0.00
2013 |  |  |  | 9076.94 |  |  | 7256 |  |  |  | 1257 | [10 empty] | 82.83 |  |  |  | 82.83 | [5 empty] | 82.42 |  |  | 82.82 |  |  |  | 0.16 |  | 0.13 | [8 empty] | 17.04 |  |  |  |  | 0.00
2014 |  |  |  | 9710.29 |  |  | 7756 |  |  |  | 1257 | [10 empty] | 88.54 |  |  |  | 88.54 | [5 empty] | 88.18 |  |  | 88.54 |  |  |  | 4.77 |  | 5.94 | [8 empty] | 5.52 |  |  |  |  | 0.00
2015 |  |  |  | 9714.51 |  |  | 7685 |  |  |  | 1257 | [10 empty] | 87.73 |  |  |  | 87.73 | [5 empty] | 88.22 |  |  | 87.73 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 12.25 |  |  |  |  | 0.00
2016 |  |  |  | 10673.32 |  |  | 8523 |  |  |  | 1257 | [10 empty] | 97.03 |  |  |  | 97.03 | [5 empty] | 96.67 |  |  | 97.03 |  |  |  | 1.09 |  | 1.07 | [8 empty] | 1.90 |  |  |  |  | 0.00
2017 |  |  |  | 9784.47 |  |  | 7876 |  |  |  | 1257 | [10 empty] | 89.89 |  |  |  | 89.89 | [5 empty] | 88.86 |  |  | 89.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.11 |  |  |  |  | 0.00
2018 |  |  |  | 10945.59 |  |  | 8760 |  |  |  | 1257 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 99.40 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 9867.64 |  |  | 8059 |  |  |  | 1257 | [10 empty] | 92.01 |  |  |  | 92.01 | [5 empty] | 89.61 |  |  | 92.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.99 |  |  |  |  | 0.00
2020 |  |  |  | 10658.67 |  |  | 8683 |  |  |  | 1257 | [10 empty] | 98.86 |  |  |  | 98.86 | [5 empty] | 96.53 |  |  | 98.85 |  |  |  | 1.14 |  | 1.14 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 217
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 714
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 70
E. |  | Testing of plant systems or components | [35 empty] | 54
L. |  | Human factor related | [39 empty] | 4
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [24 empty] | 100 | [14 empty] | 10
Subtotal | [26 empty] | 100 | [10 empty] | 838 |  |  |  | 231 | [11 empty] | 1
Total | [22 empty] | 100 | [14 empty] | 1070
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 16
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 18
31. |  |  | Turbine and auxiliaries | [34 empty] | 38
32. |  |  | Feedwater and Main Steam System | [34 empty] | 38
34. |  |  | Miscellaneous Systems | [34 empty] | 30
41. |  |  | Main Generator Systems | [34 empty] | 21
42. |  |  | Electrical Power Supply Systems | [34 empty] | 37
Total | [37 empty] | 222
Highlights (2020)
Manual Scram on 02/14/20 due to degrading condenser pressure associated with Off-gas Recombiner performance. The generator was placed on line for continuous operation on 02/17/20.

## TURKEY POINT-3
2020 Operating Experience
US-250 | [8 empty] | TURKEY POINT-3 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FPL (Florida Power & Light Co.)
Owner | [7 empty] | : | FPL (Florida Power & Light Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-04-27
Thermal power | [12 empty] | : |  |  | 2644 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1972-11-02
Gross electrical power | [12 empty] | : |  |  | 829 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1972-12-14
Reference unit power (net) | [12 empty] | : |  |  | 837 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 338
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.41
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.13
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6556.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.85 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.01 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.79 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.01 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.21 %
Load Factor (LF) | [18 empty] | : | 89.18 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.03 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 788 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 649.34 | 605.96 |  |  |  | 578.71 |  | 84.58 | [8 empty] | 644.94 |  |  | 620.50 | [6 empty] | 641.21 |  | 487.57 |  |  |  | 620.01 |  |  | 646.84 |  |  | 526.64 | [9 empty] | 450.13 |  |  | 6556.42
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.55 |  | 18.75 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 90.72 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.01
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.55 |  | 18.75 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 90.72 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.01
LF [%] |  |  |  |  | 104.27 | 104.02 |  |  |  | 92.93 |  | 14.04 | [8 empty] | 103.57 |  |  | 102.96 | [6 empty] | 102.97 |  | 78.30 |  |  |  | 102.88 |  |  | 103.87 |  |  | 87.39 | [9 empty] | 72.28 |  |  | 89.18
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.41 |  | 18.75 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 79.30 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.03
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 9.28 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.85
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 9.28 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.79
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 6.45 |  | 81.25 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.21
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 234181.22 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.95 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.17 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.13 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.7 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.53 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.13 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.39 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1972 |  |  |  | 101.10 |  |  | 420 |  |  |  | 670 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 14.55 |  |  | 40.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | Data not provided
1974 |  |  |  | 3478.80 |  |  | 6090 |  |  |  | 666 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 59.63 |  |  | 69.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1975 |  |  |  | 4376.00 |  |  | 6948 |  |  |  | 666 | [10 empty] | 74.91 |  |  |  | 74.91 | [5 empty] | 75.01 |  |  | 79.32 |  |  |  | 5.56 |  | 4.41 | [8 empty] | 20.67 |  |  |  |  | 0.00
1976 |  |  |  | 4322.00 |  |  | 6665 |  |  |  | 666 | [10 empty] | 73.94 |  |  |  | 73.94 | [5 empty] | 73.88 |  |  | 75.88 |  |  |  | 0.56 |  | 0.42 | [8 empty] | 25.64 |  |  |  |  | 0.00
1977 |  |  |  | 4474.10 |  |  | 6994 |  |  |  | 666 | [10 empty] | 76.56 |  |  |  | 76.56 | [5 empty] | 76.69 |  |  | 79.84 |  |  |  | 4.46 |  | 3.58 | [8 empty] | 19.86 |  |  |  |  | 0.00
1978 |  |  |  | 4502.70 |  |  | 7087 |  |  |  | 666 | [10 empty] | 77.20 |  |  |  | 77.20 | [5 empty] | 77.18 |  |  | 80.90 |  |  |  | 2.53 |  | 2.00 | [8 empty] | 20.80 |  |  |  |  | 0.00
1979 |  |  |  | 2881.60 |  |  | 4509 |  |  |  | 666 | [10 empty] | 49.39 |  |  |  | 49.39 | [5 empty] | 49.39 |  |  | 51.47 |  |  |  | 3.82 |  | 1.96 | [8 empty] | 48.64 |  |  |  |  | 0.00
1980 |  |  |  | 4389.00 |  |  | 6812 |  |  |  | 657 | [10 empty] | 77.93 |  |  |  | 77.93 | [5 empty] | 76.05 |  |  | 77.55 |  |  |  | 0.97 |  | 0.77 | [8 empty] | 21.31 |  |  |  |  | 0.00
1981 |  |  |  | 933.20 |  |  | 1385 |  |  |  | 646 | [10 empty] | 13.23 |  |  |  | 13.23 | [5 empty] | 16.49 |  |  | 15.81 |  |  |  | 57.53 |  | 17.92 | [8 empty] | 68.84 |  |  |  |  | 0.00
1982 |  |  |  | 3771.40 |  |  | 5612 |  |  |  | 646 | [10 empty] | 64.25 |  |  |  | 64.25 | [5 empty] | 66.64 |  |  | 64.06 |  |  |  | 11.20 |  | 8.11 | [8 empty] | 27.64 |  |  |  |  | 0.00
1983 |  |  |  | 4331.00 |  |  | 6415 |  |  |  | 659 | [10 empty] | 73.35 |  |  |  | 73.35 | [5 empty] | 75.02 |  |  | 73.23 |  |  |  | 1.99 |  | 1.49 | [8 empty] | 25.16 |  |  |  |  | 0.00
1984 |  |  |  | 4784.19 |  |  | 7253 |  |  |  | 666 | [10 empty] | 82.62 |  |  |  | 82.62 | [5 empty] | 81.78 |  |  | 82.57 |  |  |  | 11.67 |  | 10.91 | [8 empty] | 6.47 |  |  |  |  | 0.00
1985 |  |  |  | 3420.99 |  |  | 5224 |  |  |  | 666 | [10 empty] | 59.70 |  |  |  | 60.99 | [5 empty] | 58.64 |  |  | 59.63 |  |  |  | 4.64 |  | 2.97 | [8 empty] | 36.04 |  |  |  |  | 1.29
1986 |  |  |  | 4513.06 |  |  | 6816 |  |  |  | 666 | [10 empty] | 77.87 |  |  |  | 77.87 | [5 empty] | 77.36 |  |  | 77.81 |  |  |  | 17.05 |  | 16.00 | [8 empty] | 6.13 |  |  |  |  | 0.00
1987 |  |  |  | 885.28 |  |  | 1566 |  |  |  | 666 | [10 empty] | 17.91 |  |  |  | 17.91 | [5 empty] | 15.17 |  |  | 17.88 |  |  |  | 63.55 |  | 31.22 | [8 empty] | 50.87 |  |  |  |  | 0.00
1988 |  |  |  | 3467.96 |  |  | 5320 |  |  |  | 666 | [10 empty] | 60.60 |  |  |  | 60.60 | [5 empty] | 59.28 |  |  | 60.56 |  |  |  | 39.29 |  | 39.22 | [8 empty] | 0.18 |  |  |  |  | 0.00
1989 |  |  |  | 3605.10 |  |  | 5696 |  |  |  | 666 | [10 empty] | 65.06 |  |  |  | 65.06 | [5 empty] | 61.79 |  |  | 65.02 |  |  |  | 14.66 |  | 11.18 | [8 empty] | 23.77 |  |  |  |  | 0.00
1990 |  |  |  | 3388.41 |  |  | 5200 |  |  |  | 666 | [10 empty] | 59.37 |  |  |  | 59.37 | [5 empty] | 58.08 |  |  | 59.36 |  |  |  | 4.04 |  | 2.50 | [8 empty] | 38.13 |  |  |  |  | 0.00
1991 |  |  |  | 1332.05 |  |  | 2155 |  |  |  | 666 | [10 empty] | 50.01 |  |  |  | 50.01 | [5 empty] | 22.83 |  |  | 24.60 |  |  |  | 0.59 |  | 0.30 | [8 empty] | 49.69 |  |  |  |  | 0.00
1992 |  |  |  | 3428.22 |  |  | 5896 |  |  |  | 666 | [10 empty] | 67.16 |  |  |  | 67.16 | [5 empty] | 58.60 |  |  | 67.12 |  |  |  | 5.96 |  | 4.26 | [8 empty] | 28.59 |  |  |  |  | 0.00
1993 |  |  |  | 5657.35 |  |  | 8421 |  |  |  | 666 | [10 empty] | 96.14 |  |  |  | 96.14 | [5 empty] | 96.97 |  |  | 96.13 |  |  |  | 1.78 |  | 1.75 | [8 empty] | 2.11 |  |  |  |  | 0.00
1994 |  |  |  | 4924.92 |  |  | 7513 |  |  |  | 666 | [10 empty] | 85.83 |  |  |  | 85.83 | [5 empty] | 84.42 |  |  | 85.76 |  |  |  | 1.93 |  | 1.69 | [8 empty] | 12.48 |  |  |  |  | 0.00
1995 |  |  |  | 5218.97 |  |  | 7846 |  |  |  | 666 | [10 empty] | 89.61 |  |  |  | 89.61 | [5 empty] | 89.46 |  |  | 89.57 |  |  |  | 0.82 |  | 0.74 | [8 empty] | 9.65 |  |  |  |  | 0.00
1996 |  |  |  | 5750.84 |  |  | 8490 |  |  |  | 673 | [10 empty] | 96.73 |  |  |  | 96.73 | [5 empty] | 97.27 |  |  | 96.65 |  |  |  | 3.27 |  | 3.27 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 5252.35 |  |  | 7570 |  |  |  | 693 | [10 empty] | 87.00 |  |  |  | 87.00 | [5 empty] | 86.52 |  |  | 86.42 |  |  |  | 1.37 |  | 1.21 | [8 empty] | 11.79 |  |  |  |  | 0.00
1998 |  |  |  | 5408.30 |  |  | 7757 |  |  |  | 693 | [10 empty] | 89.01 |  |  |  | 89.78 | [5 empty] | 89.09 |  |  | 88.55 |  |  |  | 1.08 |  | 0.98 | [8 empty] | 9.24 |  |  |  |  | 0.77
1999 |  |  |  | 6112.35 |  |  | 8684 |  |  |  | 693 | [10 empty] | 99.14 |  |  |  | 99.14 | [5 empty] | 100.69 |  |  | 99.13 |  |  |  | 0.86 |  | 0.86 | [8 empty] | 0.00 |  |  |  |  | 0.00
2000 |  |  |  | 5684.42 |  |  | 8122 |  |  |  | 693 | [10 empty] | 92.47 |  |  |  | 92.47 | [5 empty] | 93.38 |  |  | 92.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.53 |  |  |  |  | 0.00
2001 |  |  |  | 5526.02 |  |  | 7923 |  |  |  | 693 | [10 empty] | 90.46 |  |  |  | 90.46 | [5 empty] | 91.03 |  |  | 90.45 |  |  |  | 1.95 |  | 1.80 | [8 empty] | 7.74 |  |  |  |  | 0.00
2002 |  |  |  | 6215.43 |  |  | 8760 |  |  |  | 693 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.38 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 5445.57 |  |  | 7930 |  |  |  | 693 | [10 empty] | 90.56 |  |  |  | 90.56 | [5 empty] | 89.70 |  |  | 90.53 |  |  |  | 1.99 |  | 1.83 | [8 empty] | 7.61 |  |  |  |  | 0.00
2004 |  |  |  | 4734.02 |  |  | 6934 |  |  |  | 693 | [10 empty] | 78.96 |  |  |  | 78.96 | [5 empty] | 77.77 |  |  | 78.94 |  |  |  | 3.97 |  | 3.27 | [8 empty] | 17.77 |  |  |  |  | 0.00
2005 |  |  |  | 5798.91 |  |  | 8362 |  |  |  | 693 | [10 empty] | 95.47 |  |  |  | 96.41 | [5 empty] | 95.52 |  |  | 95.46 |  |  |  | 3.59 |  | 3.59 | [8 empty] | 0.00 |  |  |  |  | 0.94
2006 |  |  |  | 5581.94 |  |  | 7905 |  |  |  | 693 | [10 empty] | 90.25 |  |  |  | 90.25 | [5 empty] | 91.95 |  |  | 90.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.75 |  |  |  |  | 0.00
2007 |  |  |  | 6078.10 |  |  | 7320 |  |  |  | 693 | [10 empty] | 83.57 |  |  |  | 83.57 | [5 empty] | 100.12 |  |  | 83.56 |  |  |  | 5.06 |  | 4.45 | [8 empty] | 11.97 |  |  |  |  | 0.00
2008 |  |  |  | 6139.53 |  |  | 8617 |  |  |  | 693 | [10 empty] | 98.12 |  |  |  | 99.78 | [5 empty] | 100.86 |  |  | 98.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.22 |  |  |  |  | 1.66
2009 |  |  |  | 5249.30 |  |  | 7451 |  |  |  | 693 | [10 empty] | 85.06 |  |  |  | 85.06 | [5 empty] | 86.47 |  |  | 85.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.94 |  |  |  |  | 0.00
2010 |  |  |  | 5358.09 |  |  | 7594 |  |  |  | 693 | [10 empty] | 86.71 |  |  |  | 86.71 | [5 empty] | 88.26 |  |  | 86.69 |  |  |  | 1.19 |  | 1.04 | [8 empty] | 12.25 |  |  |  |  | 0.00
2011 |  |  |  | 5822.87 |  |  | 8291 |  |  |  | 693 | [10 empty] | 94.66 |  |  |  | 94.66 | [5 empty] | 95.92 |  |  | 94.65 |  |  |  | 2.25 |  | 2.18 | [8 empty] | 3.16 |  |  |  |  | 0.00
2012 |  |  |  | 2477.38 |  |  | 4121 |  |  |  | 802 | [10 empty] | 49.51 |  |  |  | 49.51 | [5 empty] | 38.67 |  |  | 46.91 |  |  |  | 0.88 |  | 0.44 | [8 empty] | 50.05 |  |  |  |  | 0.00
2013 |  |  |  | 6239.35 |  |  | 7945 |  |  |  | 802 | [10 empty] | 90.70 |  |  |  | 90.70 | [5 empty] | 88.80 |  |  | 90.69 |  |  |  | 9.30 |  | 9.30 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 5900.85 |  |  | 7726 |  |  |  | 802 | [10 empty] | 88.19 |  |  |  | 88.19 | [5 empty] | 83.99 |  |  | 88.20 |  |  |  | 0.78 |  | 0.69 | [8 empty] | 11.11 |  |  |  |  | 0.00
2015 |  |  |  | 6002.32 |  |  | 7552 |  |  |  | 802 | [10 empty] | 86.22 |  |  |  | 86.22 | [5 empty] | 85.44 |  |  | 86.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.78 |  |  |  |  | 0.00
2016 |  |  |  | 7174.17 |  |  | 8710 |  |  |  | 802 | [10 empty] | 99.15 |  |  |  | 99.15 | [5 empty] | 101.84 |  |  | 99.16 |  |  |  | 0.85 |  | 0.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6163.82 |  |  | 7531 |  |  |  | 802 | [10 empty] | 85.98 |  |  |  | 86.95 | [5 empty] | 87.73 |  |  | 85.97 |  |  |  | 3.60 |  | 3.25 | [8 empty] | 9.80 |  |  |  |  | 0.97
2018 |  |  |  | 6462.92 |  |  | 7811 |  |  |  | 837 | [10 empty] | 89.22 |  |  |  | 89.22 | [5 empty] | 90.49 |  |  | 89.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.78 |  |  |  |  | 0.00
2019 |  |  |  | 7533.69 |  |  | 8726 |  |  |  | 837 | [10 empty] | 99.62 |  |  |  | 100.00 | [5 empty] | 102.75 |  |  | 99.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.38
2020 |  |  |  | 6556.42 |  |  | 7996 |  |  |  | 837 | [10 empty] | 92.01 |  |  |  | 92.01 | [5 empty] | 89.18 |  |  | 91.03 |  |  |  | 0.85 |  | 0.79 | [8 empty] | 7.21 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1972 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 380
B. |  | Refuelling without maintenance | [20 empty] | 633 | [14 empty] | 13
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 893
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 250
E. |  | Testing of plant systems or components | [35 empty] | 7 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [35 empty] | 18 |  |  |  | 5
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 60
P. |  | Fire | [39 empty] | 2
Z. |  | Other | [24 empty] | 154 | [10 empty] | 146 |  |  |  | 17
Subtotal | [22 empty] | 633 |  |  |  | 154 | [10 empty] | 1329 |  |  |  | 405 | [11 empty] | 63
Total | [22 empty] | 787 | [14 empty] | 1797
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1972 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 39
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 43
14. |  |  | Safety Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 78
16. |  |  | Steam generation systems | [34 empty] | 21
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 40
32. |  |  | Feedwater and Main Steam System | [34 empty] | 31
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 43
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 60
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [37 empty] | 390
Highlights (2020)
Refueling Outage 31.

## TURKEY POINT-4
2020 Operating Experience
US-251 | [8 empty] | TURKEY POINT-4 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FPL (Florida Power & Light Co.)
Owner | [7 empty] | : | FPL (Florida Power & Light Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-04-27
Thermal power | [12 empty] | : |  |  | 2644 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-06-21
Gross electrical power | [12 empty] | : |  |  | 829 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-09-07
Reference unit power (net) | [12 empty] | : |  |  | 821 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 338
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.41
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.13
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 6062.56 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.6 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.54 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.03 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.54 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.43 %
Load Factor (LF) | [18 empty] | : | 84.07 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 83.54 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1446 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 630.57 | 585.37 |  |  |  | 622.61 |  | 600.45 | [8 empty] | 619.52 |  |  | 593.45 | [6 empty] | 305.60 |  | 608.84 |  |  |  | 587.64 |  |  | 22.84 |  |  | 229.54 | [9 empty] | 656.13 |  |  | 6062.56
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 52.45 |  | 100.00 |  |  |  | 100.00 |  |  | 6.45 |  |  | 45.01 | [9 empty] | 100.00 |  |  | 83.54
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 52.45 |  | 100.00 |  |  |  | 100.00 |  |  | 6.45 |  |  | 45.01 | [9 empty] | 100.00 |  |  | 83.54
LF [%] |  |  |  |  | 103.23 | 102.44 |  |  |  | 101.93 |  | 101.58 | [8 empty] | 101.42 |  |  | 100.39 | [6 empty] | 50.03 |  | 99.68 |  |  |  | 99.41 |  |  | 3.74 |  |  | 38.83 | [9 empty] | 107.42 |  |  | 84.07
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 52.42 |  | 100.00 |  |  |  | 100.00 |  |  | 6.45 |  |  | 45.14 | [9 empty] | 100.00 |  |  | 83.54
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 47.55 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.60
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 47.55 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.03
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 93.55 |  |  | 54.99 | [9 empty] | 0.00 |  |  | 12.43
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 233096.47 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.92 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.16 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.32 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.52 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.59 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.93 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | Data not provided
1974 |  |  |  | 4513.40 |  |  | 6759 |  |  |  | 728 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 70.77 |  |  | 77.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1975 |  |  |  | 3991.90 |  |  | 6172 |  |  |  | 666 | [10 empty] | 68.33 |  |  |  | 68.33 | [5 empty] | 68.42 |  |  | 70.46 |  |  |  | 0.88 |  | 0.60 | [8 empty] | 31.07 |  |  |  |  | 0.00
1976 |  |  |  | 3774.80 |  |  | 5825 |  |  |  | 666 | [10 empty] | 64.33 |  |  |  | 64.33 | [5 empty] | 64.52 |  |  | 66.31 |  |  |  | 6.81 |  | 4.70 | [8 empty] | 30.97 |  |  |  |  | 0.00
1977 |  |  |  | 3671.00 |  |  | 5578 |  |  |  | 666 | [10 empty] | 62.74 |  |  |  | 62.74 | [5 empty] | 62.92 |  |  | 63.68 |  |  |  | 3.32 |  | 2.15 | [8 empty] | 35.10 |  |  |  |  | 0.00
1978 |  |  |  | 3791.40 |  |  | 6693 |  |  |  | 666 | [10 empty] | 64.99 |  |  |  | 64.99 | [5 empty] | 64.99 |  |  | 76.40 |  |  |  | 4.78 |  | 3.26 | [8 empty] | 31.75 |  |  |  |  | 0.00
1979 |  |  |  | 3846.60 |  |  | 6361 |  |  |  | 666 | [10 empty] | 65.94 |  |  |  | 65.94 | [5 empty] | 65.93 |  |  | 72.61 |  |  |  | 7.34 |  | 5.22 | [8 empty] | 28.84 |  |  |  |  | 0.00
1980 |  |  |  | 3856.50 |  |  | 6093 |  |  |  | 657 | [10 empty] | 69.40 |  |  |  | 69.40 | [5 empty] | 66.82 |  |  | 69.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.60 |  |  |  |  | 0.00
1981 |  |  |  | 4507.20 |  |  | 6801 |  |  |  | 646 | [10 empty] | 77.32 |  |  |  | 77.32 | [5 empty] | 79.65 |  |  | 77.64 |  |  |  | 3.42 |  | 2.74 | [8 empty] | 19.94 |  |  |  |  | 0.00
1982 |  |  |  | 3847.20 |  |  | 5806 |  |  |  | 646 | [10 empty] | 66.35 |  |  |  | 66.35 | [5 empty] | 67.98 |  |  | 66.28 |  |  |  | 11.74 |  | 8.82 | [8 empty] | 24.83 |  |  |  |  | 0.00
1983 |  |  |  | 2978.90 |  |  | 4568 |  |  |  | 659 | [10 empty] | 52.44 |  |  |  | 52.44 | [5 empty] | 51.60 |  |  | 52.15 |  |  |  | 10.71 |  | 6.29 | [8 empty] | 41.26 |  |  |  |  | 0.00
1984 |  |  |  | 3084.14 |  |  | 4774 |  |  |  | 666 | [10 empty] | 54.43 |  |  |  | 54.43 | [5 empty] | 52.72 |  |  | 54.35 |  |  |  | 29.05 |  | 22.28 | [8 empty] | 23.29 |  |  |  |  | 0.00
1985 |  |  |  | 5177.93 |  |  | 7852 |  |  |  | 666 | [10 empty] | 89.68 |  |  |  | 89.81 | [5 empty] | 88.75 |  |  | 89.63 |  |  |  | 6.85 |  | 6.60 | [8 empty] | 3.59 |  |  |  |  | 0.13
1986 |  |  |  | 1744.00 |  |  | 2790 |  |  |  | 666 | [10 empty] | 31.88 |  |  |  | 31.88 | [5 empty] | 29.89 |  |  | 31.85 |  |  |  | 10.14 |  | 3.60 | [8 empty] | 64.53 |  |  |  |  | 0.00
1987 |  |  |  | 2657.55 |  |  | 4314 |  |  |  | 666 | [10 empty] | 49.31 |  |  |  | 49.31 | [5 empty] | 45.55 |  |  | 49.25 |  |  |  | 50.69 |  | 50.69 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 3267.74 |  |  | 4986 |  |  |  | 666 | [10 empty] | 56.80 |  |  |  | 56.80 | [5 empty] | 55.86 |  |  | 56.76 |  |  |  | 19.71 |  | 13.95 | [8 empty] | 29.25 |  |  |  |  | 0.00
1989 |  |  |  | 2107.57 |  |  | 3676 |  |  |  | 666 | [10 empty] | 42.00 |  |  |  | 42.00 | [5 empty] | 36.12 |  |  | 41.96 |  |  |  | 22.72 |  | 12.35 | [8 empty] | 45.65 |  |  |  |  | 0.00
1990 |  |  |  | 4384.92 |  |  | 6692 |  |  |  | 666 | [10 empty] | 76.42 |  |  |  | 76.42 | [5 empty] | 75.16 |  |  | 76.39 |  |  |  | 12.38 |  | 10.80 | [8 empty] | 12.79 |  |  |  |  | 0.00
1991 |  |  |  | 808.05 |  |  | 1335 |  |  |  | 666 | [10 empty] | 48.18 |  |  |  | 48.18 | [5 empty] | 13.85 |  |  | 15.24 |  |  |  | 0.59 |  | 0.29 | [8 empty] | 51.53 |  |  |  |  | 0.00
1992 |  |  |  | 4642.28 |  |  | 7139 |  |  |  | 666 | [10 empty] | 81.31 |  |  |  | 81.31 | [5 empty] | 79.35 |  |  | 81.27 |  |  |  | 13.23 |  | 12.40 | [8 empty] | 6.30 |  |  |  |  | 0.00
1993 |  |  |  | 4746.29 |  |  | 7277 |  |  |  | 666 | [10 empty] | 83.11 |  |  |  | 83.11 | [5 empty] | 81.35 |  |  | 83.07 |  |  |  | 2.03 |  | 1.72 | [8 empty] | 15.17 |  |  |  |  | 0.00
1994 |  |  |  | 4844.35 |  |  | 7437 |  |  |  | 666 | [10 empty] | 84.95 |  |  |  | 84.95 | [5 empty] | 83.03 |  |  | 84.90 |  |  |  | 3.83 |  | 3.38 | [8 empty] | 11.67 |  |  |  |  | 0.00
1995 |  |  |  | 5780.13 |  |  | 8629 |  |  |  | 666 | [10 empty] | 98.52 |  |  |  | 98.52 | [5 empty] | 99.07 |  |  | 98.50 |  |  |  | 1.48 |  | 1.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 5165.36 |  |  | 7771 |  |  |  | 673 | [10 empty] | 88.63 |  |  |  | 88.63 | [5 empty] | 87.37 |  |  | 88.47 |  |  |  | 0.33 |  | 0.29 | [8 empty] | 11.07 |  |  |  |  | 0.00
1997 |  |  |  | 5442.56 |  |  | 7809 |  |  |  | 693 | [10 empty] | 89.60 |  |  |  | 89.60 | [5 empty] | 89.65 |  |  | 89.14 |  |  |  | 1.04 |  | 0.94 | [8 empty] | 9.46 |  |  |  |  | 0.00
1998 |  |  |  | 6181.46 |  |  | 8760 |  |  |  | 693 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.82 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 5735.27 |  |  | 8185 |  |  |  | 693 | [10 empty] | 93.45 |  |  |  | 93.45 | [5 empty] | 94.47 |  |  | 93.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.55 |  |  |  |  | 0.00
2000 |  |  |  | 5591.38 |  |  | 8028 |  |  |  | 693 | [10 empty] | 91.41 |  |  |  | 91.41 | [5 empty] | 91.85 |  |  | 91.39 |  |  |  | 0.87 |  | 0.80 | [8 empty] | 7.79 |  |  |  |  | 0.00
2001 |  |  |  | 6105.26 |  |  | 8623 |  |  |  | 693 | [10 empty] | 98.44 |  |  |  | 98.44 | [5 empty] | 100.57 |  |  | 98.44 |  |  |  | 1.56 |  | 1.56 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 5854.08 |  |  | 8369 |  |  |  | 693 | [10 empty] | 95.55 |  |  |  | 95.55 | [5 empty] | 96.43 |  |  | 95.54 |  |  |  | 0.17 |  | 0.16 | [8 empty] | 4.28 |  |  |  |  | 0.00
2003 |  |  |  | 5562.48 |  |  | 8033 |  |  |  | 693 | [10 empty] | 91.71 |  |  |  | 91.71 | [5 empty] | 91.63 |  |  | 91.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.29 |  |  |  |  | 0.00
2004 |  |  |  | 6079.18 |  |  | 8662 |  |  |  | 693 | [10 empty] | 98.62 |  |  |  | 98.62 | [5 empty] | 99.87 |  |  | 98.61 |  |  |  | 1.38 |  | 1.38 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 4240.96 |  |  | 6243 |  |  |  | 693 | [10 empty] | 71.30 |  |  |  | 72.37 | [5 empty] | 69.86 |  |  | 71.27 |  |  |  | 12.25 |  | 10.11 | [8 empty] | 17.52 |  |  |  |  | 1.07
2006 |  |  |  | 5383.75 |  |  | 7669 |  |  |  | 693 | [10 empty] | 87.56 |  |  |  | 87.56 | [5 empty] | 88.68 |  |  | 87.55 |  |  |  | 1.07 |  | 0.95 | [8 empty] | 11.49 |  |  |  |  | 0.00
2007 |  |  |  | 5148.80 |  |  | 8552 |  |  |  | 693 | [10 empty] | 97.63 |  |  |  | 97.63 | [5 empty] | 84.81 |  |  | 97.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.37 |  |  |  |  | 0.00
2008 |  |  |  | 5234.90 |  |  | 7415 |  |  |  | 693 | [10 empty] | 84.43 |  |  |  | 85.15 | [5 empty] | 86.00 |  |  | 84.41 |  |  |  | 0.40 |  | 0.34 | [8 empty] | 14.50 |  |  |  |  | 0.72
2009 |  |  |  | 5435.35 |  |  | 7811 |  |  |  | 693 | [10 empty] | 89.18 |  |  |  | 89.18 | [5 empty] | 89.53 |  |  | 89.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.82 |  |  |  |  | 0.00
2010 |  |  |  | 5949.82 |  |  | 8397 |  |  |  | 693 | [10 empty] | 95.87 |  |  |  | 95.87 | [5 empty] | 98.01 |  |  | 95.86 |  |  |  | 4.13 |  | 4.13 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 5089.88 |  |  | 7202 |  |  |  | 693 | [10 empty] | 82.24 |  |  |  | 82.24 | [5 empty] | 83.84 |  |  | 82.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.76 |  |  |  |  | 0.00
2012 |  |  |  | 5235.36 |  |  | 7416 |  |  |  | 693 | [10 empty] | 84.44 |  |  |  | 84.44 | [5 empty] | 86.00 |  |  | 84.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.56 |  |  |  |  | 0.00
2013 |  |  |  | 4674.70 |  |  | 6156 |  |  |  | 802 | [10 empty] | 73.43 |  |  |  | 73.43 | [5 empty] | 68.84 |  |  | 70.27 |  |  |  | 0.65 |  | 0.48 | [8 empty] | 26.09 |  |  |  |  | 0.00
2014 |  |  |  | 6149.85 |  |  | 7828 |  |  |  | 802 | [10 empty] | 89.35 |  |  |  | 89.35 | [5 empty] | 87.54 |  |  | 89.36 |  |  |  | 2.41 |  | 2.20 | [8 empty] | 8.45 |  |  |  |  | 0.00
2015 |  |  |  | 7047.86 |  |  | 8623 |  |  |  | 802 | [10 empty] | 98.44 |  |  |  | 98.44 | [5 empty] | 100.32 |  |  | 98.44 |  |  |  | 0.61 |  | 0.61 | [8 empty] | 0.96 |  |  |  |  | 0.00
2016 |  |  |  | 6559.29 |  |  | 8022 |  |  |  | 802 | [10 empty] | 91.33 |  |  |  | 91.33 | [5 empty] | 93.11 |  |  | 91.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.67 |  |  |  |  | 0.00
2017 |  |  |  | 6554.48 |  |  | 7956 |  |  |  | 802 | [10 empty] | 90.82 |  |  |  | 90.82 | [5 empty] | 93.30 |  |  | 90.82 |  |  |  | 1.74 |  | 1.61 | [8 empty] | 7.57 |  |  |  |  | 0.00
2018 |  |  |  | 7292.15 |  |  | 8760 |  |  |  | 821 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.39 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 6608.74 |  |  | 8011 |  |  |  | 821 | [10 empty] | 91.46 |  |  |  | 91.46 | [5 empty] | 91.89 |  |  | 91.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.54 |  |  |  |  | 0.00
2020 |  |  |  | 6062.56 |  |  | 7338 |  |  |  | 821 | [10 empty] | 83.54 |  |  |  | 83.54 | [5 empty] | 84.07 |  |  | 83.54 |  |  |  | 4.60 |  | 4.03 | [8 empty] | 12.43 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1973 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 304
B. |  | Refuelling without maintenance | [20 empty] | 1092 | [14 empty] | 24
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1135
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 234 |  |  |  | 61
E. |  | Testing of plant systems or components | [35 empty] | 5 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 10
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 50
Z. |  | Other | [24 empty] | 354 | [14 empty] | 9
Subtotal | [22 empty] | 1092 |  |  |  | 354 | [10 empty] | 1398 |  |  |  | 385 | [11 empty] | 52
Total | [22 empty] | 1446 | [14 empty] | 1835
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1973 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 67
12. |  |  | Reactor I&C Systems | [34 empty] | 17
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 76
16. |  |  | Steam generation systems | [34 empty] | 80
31. |  |  | Turbine and auxiliaries | [34 empty] | 52
32. |  |  | Feedwater and Main Steam System | [34 empty] | 23
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 28
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 41
Total | [37 empty] | 398
Highlights (2020)
Cycle 32 Refueling Outage (PT432 RFO)

## VOGTLE-1
2020 Operating Experience
US-424 | [8 empty] | VOGTLE-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SOUTHERN (Southern Nuclear Operating Company, Inc.)
Owner | [7 empty] | : | GPCO (GEORGIA POWER CO.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-08-01
Thermal power | [12 empty] | : |  |  | 3626 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-03-27
Gross electrical power | [12 empty] | : |  |  | 1229 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-06-01
Reference unit power (net) | [12 empty] | : |  |  | 1150 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.82
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.365
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 36400 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.4 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.81
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9562.45 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.6 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.6 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.4 %
Load Factor (LF) | [18 empty] | : | 94.66 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.59 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 563 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 881.27 | 818.98 |  |  |  | 186.53 |  | 824.17 | [8 empty] | 874.68 |  |  | 839.82 | [6 empty] | 860.83 |  | 857.59 |  |  |  | 833.04 |  |  | 867.93 |  |  | 847.22 | [9 empty] | 870.39 |  |  | 9562.45
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 24.46 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.60
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 24.46 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.60
LF [%] |  |  |  |  | 103.00 | 102.32 |  |  |  | 21.80 |  | 99.54 | [8 empty] | 102.23 |  |  | 101.43 | [6 empty] | 100.61 |  | 100.23 |  |  |  | 100.61 |  |  | 101.44 |  |  | 102.32 | [9 empty] | 101.73 |  |  | 94.66
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 24.33 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.59
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 75.54 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.40
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 338695.08 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.61 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.47 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.04 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.82 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.48 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | Data not provided
1988 |  |  |  | 6799.71 |  |  | 6569 |  |  |  | 1079 | [10 empty] | 74.25 |  |  |  | 74.25 | [5 empty] | 71.74 |  |  | 74.78 |  |  |  | 12.68 |  | 10.78 | [8 empty] | 14.97 |  |  |  |  | 0.00
1989 |  |  |  | 8709.38 |  |  | 8275 |  |  |  | 1083 | [10 empty] | 94.19 |  |  |  | 94.19 | [5 empty] | 91.80 |  |  | 94.46 |  |  |  | 5.81 |  | 5.81 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | 7353.06 |  |  | 6980 |  |  |  | 1079 | [10 empty] | 78.39 |  |  |  | 78.39 | [5 empty] | 77.79 |  |  | 79.68 |  |  |  | 2.65 |  | 2.14 | [8 empty] | 19.48 |  |  |  |  | 0.00
1991 |  |  |  | 7501.74 |  |  | 7016 |  |  |  | 1100 | [10 empty] | 78.95 |  |  |  | 78.95 | [5 empty] | 77.85 |  |  | 80.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.05 |  |  |  |  | 0.00
1992 |  |  |  | 9383.53 |  |  | 8523 |  |  |  | 1105 | [10 empty] | 96.88 |  |  |  | 96.88 | [5 empty] | 96.67 |  |  | 97.03 |  |  |  | 3.12 |  | 3.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 8600.74 |  |  | 7577 |  |  |  | 1145 | [10 empty] | 86.29 |  |  |  | 86.29 | [5 empty] | 85.70 |  |  | 86.50 |  |  |  | 1.26 |  | 1.10 | [8 empty] | 12.61 |  |  |  |  | 0.00
1994 |  |  |  | 8817.16 |  |  | 7847 |  |  |  | 1168 | [10 empty] | 89.64 |  |  |  | 89.64 | [5 empty] | 86.14 |  |  | 89.58 |  |  |  | 0.62 |  | 0.56 | [8 empty] | 9.80 |  |  |  |  | 0.00
1995 |  |  |  | 9984.01 |  |  | 8621 |  |  |  | 1162 | [10 empty] | 98.43 |  |  |  | 99.18 | [5 empty] | 98.08 |  |  | 98.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.82 |  |  |  |  | 0.74
1996 |  |  |  | 8149.80 |  |  | 7162 |  |  |  | 1162 | [10 empty] | 81.55 |  |  |  | 81.55 | [5 empty] | 79.85 |  |  | 81.53 |  |  |  | 5.76 |  | 4.98 | [8 empty] | 13.47 |  |  |  |  | 0.00
1997 |  |  |  | 8270.11 |  |  | 7167 |  |  |  | 1162 | [10 empty] | 81.85 |  |  |  | 81.85 | [5 empty] | 81.25 |  |  | 81.82 |  |  |  | 4.29 |  | 3.67 | [8 empty] | 14.48 |  |  |  |  | 0.00
1998 |  |  |  | 10216.95 |  |  | 8738 |  |  |  | 1162 | [10 empty] | 99.75 |  |  |  | 99.75 | [5 empty] | 100.37 |  |  | 99.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.25 |  |  |  |  | 0.00
1999 |  |  |  | 9425.86 |  |  | 8108 |  |  |  | 1152 | [10 empty] | 92.59 |  |  |  | 92.59 | [5 empty] | 93.34 |  |  | 92.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.41 |  |  |  |  | 0.00
2000 |  |  |  | 9196.57 |  |  | 7963 |  |  |  | 1148 | [10 empty] | 90.66 |  |  |  | 90.66 | [5 empty] | 91.20 |  |  | 90.65 |  |  |  | 0.90 |  | 0.82 | [8 empty] | 8.52 |  |  |  |  | 0.00
2001 |  |  |  | 10144.38 |  |  | 8665 |  |  |  | 1148 | [10 empty] | 98.92 |  |  |  | 98.92 | [5 empty] | 100.87 |  |  | 98.92 |  |  |  | 1.08 |  | 1.08 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 8638.76 |  |  | 7469 |  |  |  | 1148 | [10 empty] | 85.29 |  |  |  | 85.29 | [5 empty] | 85.90 |  |  | 85.26 |  |  |  | 2.76 |  | 2.42 | [8 empty] | 12.29 |  |  |  |  | 0.00
2003 |  |  |  | 9411.48 |  |  | 8097 |  |  |  | 1152 | [10 empty] | 92.47 |  |  |  | 92.47 | [5 empty] | 93.26 |  |  | 92.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.53 |  |  |  |  | 0.00
2004 |  |  |  | 10162.27 |  |  | 8694 |  |  |  | 1152 | [10 empty] | 98.98 |  |  |  | 98.98 | [5 empty] | 100.43 |  |  | 98.98 |  |  |  | 0.83 |  | 0.83 | [8 empty] | 0.19 |  |  |  |  | 0.00
2005 |  |  |  | 9220.15 |  |  | 7964 |  |  |  | 1152 | [10 empty] | 90.95 |  |  |  | 90.95 | [5 empty] | 91.37 |  |  | 90.91 |  |  |  | 1.54 |  | 1.43 | [8 empty] | 7.63 |  |  |  |  | 0.00
2006 |  |  |  | 8671.05 |  |  | 7536 |  |  |  | 1152 | [10 empty] | 86.05 |  |  |  | 86.05 | [5 empty] | 85.92 |  |  | 86.03 |  |  |  | 2.27 |  | 2.00 | [8 empty] | 11.95 |  |  |  |  | 0.00
2007 |  |  |  | 9960.29 |  |  | 8760 |  |  |  | 1109 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.53 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 9050.43 |  |  | 7828 |  |  |  | 1109 | [10 empty] | 89.12 |  |  |  | 89.12 | [5 empty] | 92.91 |  |  | 89.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.88 |  |  |  |  | 0.00
2009 |  |  |  | 9135.00 |  |  | 7861 |  |  |  | 1150 | [10 empty] | 90.12 |  |  |  | 90.12 | [5 empty] | 90.68 |  |  | 89.74 |  |  |  | 1.10 |  | 1.00 | [8 empty] | 8.88 |  |  |  |  | 0.00
2010 |  |  |  | 10247.42 |  |  | 8760 |  |  |  | 1150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.72 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 9216.93 |  |  | 7954 |  |  |  | 1150 | [10 empty] | 90.82 |  |  |  | 90.82 | [5 empty] | 91.49 |  |  | 90.80 |  |  |  | 1.90 |  | 1.76 | [8 empty] | 7.42 |  |  |  |  | 0.00
2012 |  |  |  | 9216.97 |  |  | 7961 |  |  |  | 1150 | [10 empty] | 90.65 |  |  |  | 90.65 | [5 empty] | 91.24 |  |  | 90.63 |  |  |  | 0.67 |  | 0.62 | [8 empty] | 8.73 |  |  |  |  | 0.00
2013 |  |  |  | 10222.36 |  |  | 8760 |  |  |  | 1150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.46 |  |  | 99.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 8820.19 |  |  | 7752 |  |  |  | 1150 | [10 empty] | 88.50 |  |  |  | 88.50 | [5 empty] | 87.55 |  |  | 88.49 |  |  |  | 4.45 |  | 4.12 | [8 empty] | 7.39 |  |  |  |  | 0.00
2015 |  |  |  | 9215.78 |  |  | 7947 |  |  |  | 1150 | [10 empty] | 90.72 |  |  |  | 90.72 | [5 empty] | 91.48 |  |  | 90.72 |  |  |  | 0.45 |  | 0.41 | [8 empty] | 8.87 |  |  |  |  | 0.00
2016 |  |  |  | 10273.15 |  |  | 8784 |  |  |  | 1150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.70 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 9408.65 |  |  | 8109 |  |  |  | 1150 | [10 empty] | 92.57 |  |  |  | 92.57 | [5 empty] | 93.40 |  |  | 92.57 |  |  |  | 1.04 |  | 0.97 | [8 empty] | 6.47 |  |  |  |  | 0.00
2018 |  |  |  | 9627.22 |  |  | 8216 |  |  |  | 1150 | [10 empty] | 93.79 |  |  |  | 93.79 | [5 empty] | 95.57 |  |  | 93.79 |  |  |  | 0.51 |  | 0.48 | [8 empty] | 5.73 |  |  |  |  | 0.00
2019 |  |  |  | 10297.02 |  |  | 8760 |  |  |  | 1150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.21 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9562.45 |  |  | 8221 |  |  |  | 1150 | [10 empty] | 93.60 |  |  |  | 93.60 | [5 empty] | 94.66 |  |  | 93.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.40 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1987 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 114
B. |  | Refuelling without maintenance | [20 empty] | 562 | [14 empty] | 17
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 575
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 18
E. |  | Testing of plant systems or components | [35 empty] | 2 |  |  |  | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 6
L. |  | Human factor related | [39 empty] | 9
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [35 empty] | 2 |  |  |  | 0 | [11 empty] | 2
Subtotal | [22 empty] | 562 | [14 empty] | 614 |  |  |  | 129 | [11 empty] | 3
Total | [22 empty] | 562 | [14 empty] | 746
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1987 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 23
15. |  |  | Reactor Cooling Systems | [34 empty] | 24
16. |  |  | Steam generation systems | [34 empty] | 5
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 23
34. |  |  | Miscellaneous Systems | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 19
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 123
Highlights (2020)
Refueling Outage 22 (1R22).

## VOGTLE-2
2020 Operating Experience
US-425 | [8 empty] | VOGTLE-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SOUTHERN (Southern Nuclear Operating Company, Inc.)
Owner | [7 empty] | : | GPCO (GEORGIA POWER CO.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-08-01
Thermal power | [12 empty] | : |  |  | 3626 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1989-04-10
Gross electrical power | [12 empty] | : |  |  | 1229 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-05-20
Reference unit power (net) | [12 empty] | : |  |  | 1152 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.82
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.365
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 36400 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.4 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.81
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9295.37 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.83 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.09 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.62 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.09 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.29 %
Load Factor (LF) | [18 empty] | : | 91.86 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.08 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 871 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 888.23 | 830.42 |  |  |  | 878.45 |  | 852.62 | [8 empty] | 875.11 |  |  | 746.84 | [6 empty] | 861.21 |  | 416.76 |  |  |  | 517.87 |  |  | 882.05 |  |  | 653.00 | [9 empty] | 892.80 |  |  | 9295.37
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 90.72 | [6 empty] | 100.00 |  | 49.06 |  |  |  | 63.72 |  |  | 100.00 |  |  | 77.26 | [9 empty] | 100.00 |  |  | 90.09
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 90.72 | [6 empty] | 100.00 |  | 49.06 |  |  |  | 63.72 |  |  | 100.00 |  |  | 77.26 | [9 empty] | 100.00 |  |  | 90.09
LF [%] |  |  |  |  | 103.63 | 103.57 |  |  |  | 102.49 |  | 102.79 | [8 empty] | 102.10 |  |  | 90.04 | [6 empty] | 100.48 |  | 48.62 |  |  |  | 62.44 |  |  | 102.91 |  |  | 78.73 | [9 empty] | 104.17 |  |  | 91.86
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 90.69 | [6 empty] | 100.00 |  | 49.06 |  |  |  | 63.75 |  |  | 100.00 |  |  | 77.36 | [9 empty] | 100.00 |  |  | 90.08
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 9.28 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 22.74 | [9 empty] | 0.00 |  |  | 2.83
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 9.28 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 22.74 | [9 empty] | 0.00 |  |  | 2.62
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 50.94 |  |  |  | 36.28 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.29
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 285177 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.67 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.61 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.56 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.62 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.82 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.74 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.63 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 5547.17 |  |  | 5104 |  |  |  | 1110 | [10 empty] | 95.42 |  |  |  | 95.42 | [5 empty] | 96.38 |  |  | 95.60 |  |  |  | 2.29 |  | 2.24 | [8 empty] | 2.34 |  |  |  |  | 0.00
1990 |  |  |  | 6868.02 |  |  | 7125 |  |  |  | 1110 | [10 empty] | 81.06 |  |  |  | 81.06 | [5 empty] | 70.63 |  |  | 81.34 |  |  |  | 1.91 |  | 1.58 | [8 empty] | 17.36 |  |  |  |  | 0.00
1991 |  |  |  | 8897.44 |  |  | 8375 |  |  |  | 1097 | [10 empty] | 95.44 |  |  |  | 95.44 | [5 empty] | 92.59 |  |  | 95.61 |  |  |  | 2.20 |  | 2.15 | [8 empty] | 2.42 |  |  |  |  | 0.00
1992 |  |  |  | 7779.64 |  |  | 7175 |  |  |  | 1109 | [10 empty] | 80.79 |  |  |  | 80.79 | [5 empty] | 79.86 |  |  | 81.68 |  |  |  | 0.94 |  | 0.76 | [8 empty] | 18.45 |  |  |  |  | 0.00
1993 |  |  |  | 8680.90 |  |  | 7737 |  |  |  | 1140 | [10 empty] | 88.11 |  |  |  | 88.11 | [5 empty] | 86.88 |  |  | 88.32 |  |  |  | 0.38 |  | 0.34 | [8 empty] | 11.56 |  |  |  |  | 0.00
1994 |  |  |  | 9331.60 |  |  | 8062 |  |  |  | 1168 | [10 empty] | 92.12 |  |  |  | 92.12 | [5 empty] | 91.16 |  |  | 92.03 |  |  |  | 4.81 |  | 4.65 | [8 empty] | 3.23 |  |  |  |  | 0.00
1995 |  |  |  | 9165.65 |  |  | 7908 |  |  |  | 1162 | [10 empty] | 90.29 |  |  |  | 90.77 | [5 empty] | 90.04 |  |  | 90.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.23 |  |  |  |  | 0.48
1996 |  |  |  | 9037.64 |  |  | 7899 |  |  |  | 1162 | [10 empty] | 89.94 |  |  |  | 89.94 | [5 empty] | 88.54 |  |  | 89.92 |  |  |  | 0.59 |  | 0.54 | [8 empty] | 9.52 |  |  |  |  | 0.00
1997 |  |  |  | 10310.83 |  |  | 8760 |  |  |  | 1162 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.29 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 8388.61 |  |  | 7347 |  |  |  | 1162 | [10 empty] | 83.89 |  |  |  | 83.89 | [5 empty] | 82.38 |  |  | 83.87 |  |  |  | 4.82 |  | 4.25 | [8 empty] | 11.87 |  |  |  |  | 0.00
1999 |  |  |  | 9022.63 |  |  | 7833 |  |  |  | 1156 | [10 empty] | 89.47 |  |  |  | 89.47 | [5 empty] | 89.09 |  |  | 89.42 |  |  |  | 0.57 |  | 0.51 | [8 empty] | 10.02 |  |  |  |  | 0.00
2000 |  |  |  | 10337.82 |  |  | 8784 |  |  |  | 1149 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.39 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 9456.68 |  |  | 8112 |  |  |  | 1149 | [10 empty] | 92.61 |  |  |  | 92.61 | [5 empty] | 93.95 |  |  | 92.60 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 7.34 |  |  |  |  | 0.00
2002 |  |  |  | 8418.90 |  |  | 7328 |  |  |  | 1149 | [10 empty] | 83.66 |  |  |  | 83.66 | [5 empty] | 83.64 |  |  | 83.65 |  |  |  | 5.60 |  | 4.96 | [8 empty] | 11.38 |  |  |  |  | 0.00
2003 |  |  |  | 9736.64 |  |  | 8401 |  |  |  | 1149 | [10 empty] | 95.93 |  |  |  | 95.93 | [5 empty] | 96.74 |  |  | 95.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.07 |  |  |  |  | 0.00
2004 |  |  |  | 9168.69 |  |  | 7970 |  |  |  | 1149 | [10 empty] | 90.78 |  |  |  | 90.78 | [5 empty] | 90.84 |  |  | 90.73 |  |  |  | 0.60 |  | 0.55 | [8 empty] | 8.67 |  |  |  |  | 0.00
2005 |  |  |  | 8592.88 |  |  | 7464 |  |  |  | 1149 | [10 empty] | 85.24 |  |  |  | 85.24 | [5 empty] | 85.37 |  |  | 85.21 |  |  |  | 7.79 |  | 7.20 | [8 empty] | 7.56 |  |  |  |  | 0.00
2006 |  |  |  | 9276.10 |  |  | 8024 |  |  |  | 1149 | [10 empty] | 91.65 |  |  |  | 91.65 | [5 empty] | 92.16 |  |  | 91.60 |  |  |  | 8.35 |  | 8.35 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 8347.29 |  |  | 7323 |  |  |  | 1127 | [10 empty] | 83.31 |  |  |  | 83.31 | [5 empty] | 84.55 |  |  | 83.60 |  |  |  | 3.45 |  | 2.98 | [8 empty] | 13.71 |  |  |  |  | 0.00
2008 |  |  |  | 8727.13 |  |  | 7767 |  |  |  | 1127 | [10 empty] | 88.43 |  |  |  | 88.43 | [5 empty] | 88.16 |  |  | 88.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.57 |  |  |  |  | 0.00
2009 |  |  |  | 10150.93 |  |  | 8710 |  |  |  | 1152 | [10 empty] | 99.45 |  |  |  | 99.45 | [5 empty] | 100.59 |  |  | 99.43 |  |  |  | 0.55 |  | 0.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 9363.05 |  |  | 8011 |  |  |  | 1152 | [10 empty] | 91.46 |  |  |  | 91.46 | [5 empty] | 92.78 |  |  | 91.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.54 |  |  |  |  | 0.00
2011 |  |  |  | 9512.37 |  |  | 8163 |  |  |  | 1152 | [10 empty] | 93.20 |  |  |  | 93.20 | [5 empty] | 94.26 |  |  | 93.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.80 |  |  |  |  | 0.00
2012 |  |  |  | 10341.23 |  |  | 8784 |  |  |  | 1152 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.19 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 8860.32 |  |  | 7748 |  |  |  | 1152 | [10 empty] | 88.45 |  |  |  | 88.45 | [5 empty] | 87.79 |  |  | 88.44 |  |  |  | 3.14 |  | 2.86 | [8 empty] | 8.68 |  |  |  |  | 0.00
2014 |  |  |  | 9276.53 |  |  | 7984 |  |  |  | 1152 | [10 empty] | 91.13 |  |  |  | 91.13 | [5 empty] | 91.92 |  |  | 91.14 |  |  |  | 0.58 |  | 0.53 | [8 empty] | 8.34 |  |  |  |  | 0.00
2015 |  |  |  | 10144.14 |  |  | 8692 |  |  |  | 1152 | [10 empty] | 99.22 |  |  |  | 99.22 | [5 empty] | 100.52 |  |  | 99.22 |  |  |  | 0.78 |  | 0.78 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 9586.97 |  |  | 8220 |  |  |  | 1152 | [10 empty] | 93.57 |  |  |  | 93.57 | [5 empty] | 94.74 |  |  | 93.58 |  |  |  | 0.43 |  | 0.40 | [8 empty] | 6.03 |  |  |  |  | 0.00
2017 |  |  |  | 9767.38 |  |  | 8347 |  |  |  | 1152 | [10 empty] | 95.28 |  |  |  | 95.28 | [5 empty] | 96.79 |  |  | 95.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.72 |  |  |  |  | 0.00
2018 |  |  |  | 10331.91 |  |  | 8760 |  |  |  | 1152 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.38 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 9457.10 |  |  | 8076 |  |  |  | 1152 | [10 empty] | 92.21 |  |  |  | 92.21 | [5 empty] | 93.71 |  |  | 92.19 |  |  |  | 1.33 |  | 1.24 | [8 empty] | 6.54 |  |  |  |  | 0.00
2020 |  |  |  | 9295.37 |  |  | 7913 |  |  |  | 1152 | [10 empty] | 90.09 |  |  |  | 90.09 | [5 empty] | 91.86 |  |  | 90.08 |  |  |  | 2.83 |  | 2.62 | [8 empty] | 7.29 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1989 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 99
B. |  | Refuelling without maintenance | [20 empty] | 640 | [14 empty] | 20
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 523
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 49
E. |  | Testing of plant systems or components | [35 empty] | 1
L. |  | Human factor related | [39 empty] | 24
Z. |  | Other | [24 empty] | 231 | [10 empty] | 2 |  |  |  | 14 | [11 empty] | 1
Subtotal | [22 empty] | 640 |  |  |  | 231 | [10 empty] | 595 |  |  |  | 137 | [11 empty] | 1
Total | [22 empty] | 871 | [14 empty] | 733
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1989 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 24
16. |  |  | Steam generation systems | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 25
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 15
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [37 empty] | 102
Highlights (2020)
B Phase Main Step-Up transformer failure. Placed spare transformer in service.

## WATERFORD-3
2020 Operating Experience
US-382 | [8 empty] | WATERFORD-3 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ENTERGY (Entergy Nuclear Operations, Inc.)
Owner | [7 empty] | : | ENTLA (ENTERGY LOUISIANA, INC.)
Reactor Supplier | [7 empty] | : | CE (COMBUSTION ENGINEERING CO.)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CE 2LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-11-14
Thermal power | [12 empty] | : |  |  | 3716 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-03-18
Gross electrical power | [12 empty] | : |  |  | 1250 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-09-24
Reference unit power (net) | [12 empty] | : |  |  | 1168 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.309
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33450 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.45 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.05
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 217 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.52 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 41 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8961.22 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.72 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.42 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.55 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.42 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.03 %
Load Factor (LF) | [18 empty] | : | 87.34 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 88.42 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1017 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 880.61 | 823.35 |  |  |  | 881.61 |  | 850.98 | [8 empty] | 877.84 |  |  | 849.66 | [6 empty] | 876.17 |  | 874.04 |  |  |  | 619.65 |  |  | 0.00 |  |  | 661.86 | [9 empty] | 765.43 |  |  | 8961.22
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 83.32 |  |  | 0.00 |  |  | 90.25 | [9 empty] | 88.88 |  |  | 88.42
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 83.32 |  |  | 0.00 |  |  | 90.25 | [9 empty] | 88.88 |  |  | 88.42
LF [%] |  |  |  |  | 101.34 | 101.28 |  |  |  | 101.45 |  | 101.19 | [8 empty] | 101.02 |  |  | 101.03 | [6 empty] | 100.83 |  | 100.58 |  |  |  | 73.68 |  |  | 0.00 |  |  | 78.70 | [9 empty] | 88.08 |  |  | 87.34
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 83.33 |  |  | 0.00 |  |  | 90.42 | [9 empty] | 88.84 |  |  | 88.42
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 7.59 | [9 empty] | 11.12 |  |  | 1.72
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 7.41 | [9 empty] | 11.12 |  |  | 1.55
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 16.68 |  |  | 100.00 |  |  | 2.34 | [9 empty] | 0.00 |  |  | 10.03
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 330911.18 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.7 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.48 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.44 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.73 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.83 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.11 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.25 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.38 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 2773.07 |  |  | 3372 |  |  |  | 1099 | [10 empty] | 75.85 |  |  |  | 75.85 | [5 empty] | 69.71 |  |  | 75.51 |  |  |  | 23.80 |  | 23.69 | [8 empty] | 0.46 |  |  |  |  | 0.00
1986 |  |  |  | 7308.38 |  |  | 6921 |  |  |  | 1096 | [10 empty] | 79.47 |  |  |  | 79.47 | [5 empty] | 76.07 |  |  | 79.01 |  |  |  | 5.80 |  | 4.90 | [8 empty] | 15.64 |  |  |  |  | 0.00
1987 |  |  |  | 7434.08 |  |  | 7085 |  |  |  | 1075 | [10 empty] | 80.93 |  |  |  | 80.93 | [5 empty] | 78.94 |  |  | 80.88 |  |  |  | 9.29 |  | 8.29 | [8 empty] | 10.79 |  |  |  |  | 0.00
1988 |  |  |  | 6548.41 |  |  | 6468 |  |  |  | 1075 | [10 empty] | 73.70 |  |  |  | 73.70 | [5 empty] | 69.35 |  |  | 73.63 |  |  |  | 2.86 |  | 2.17 | [8 empty] | 24.13 |  |  |  |  | 0.00
1989 |  |  |  | 7609.43 |  |  | 7136 |  |  |  | 1075 | [10 empty] | 81.51 |  |  |  | 81.51 | [5 empty] | 80.81 |  |  | 81.46 |  |  |  | 2.84 |  | 2.38 | [8 empty] | 16.11 |  |  |  |  | 0.00
1990 |  |  |  | 8604.23 |  |  | 8079 |  |  |  | 1075 | [10 empty] | 92.25 |  |  |  | 92.25 | [5 empty] | 91.37 |  |  | 92.23 |  |  |  | 1.51 |  | 1.42 | [8 empty] | 6.34 |  |  |  |  | 0.00
1991 |  |  |  | 7274.94 |  |  | 6869 |  |  |  | 1075 | [10 empty] | 78.46 |  |  |  | 78.88 | [5 empty] | 77.25 |  |  | 78.41 |  |  |  | 1.26 |  | 1.00 | [8 empty] | 20.11 |  |  |  |  | 0.42
1992 |  |  |  | 7622.16 |  |  | 7213 |  |  |  | 1075 | [10 empty] | 82.14 |  |  |  | 82.14 | [5 empty] | 80.72 |  |  | 82.12 |  |  |  | 1.72 |  | 1.43 | [8 empty] | 16.43 |  |  |  |  | 0.00
1993 |  |  |  | 9138.83 |  |  | 8691 |  |  |  | 1075 | [10 empty] | 99.22 |  |  |  | 99.22 | [5 empty] | 97.05 |  |  | 99.21 |  |  |  | 0.78 |  | 0.78 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 7931.92 |  |  | 7555 |  |  |  | 1075 | [10 empty] | 86.28 |  |  |  | 86.28 | [5 empty] | 84.23 |  |  | 86.24 |  |  |  | 0.41 |  | 0.35 | [8 empty] | 13.37 |  |  |  |  | 0.00
1995 |  |  |  | 7763.45 |  |  | 7241 |  |  |  | 1075 | [10 empty] | 82.68 |  |  |  | 82.68 | [5 empty] | 82.44 |  |  | 82.66 |  |  |  | 6.01 |  | 5.29 | [8 empty] | 12.03 |  |  |  |  | 0.00
1996 |  |  |  | 8926.85 |  |  | 8237 |  |  |  | 1075 | [10 empty] | 93.81 |  |  |  | 93.81 | [5 empty] | 94.54 |  |  | 93.77 |  |  |  | 6.19 |  | 6.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 6720.68 |  |  | 6161 |  |  |  | 1075 | [10 empty] | 70.35 |  |  |  | 70.35 | [5 empty] | 71.37 |  |  | 70.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.65 |  |  |  |  | 0.00
1998 |  |  |  | 8620.78 |  |  | 7966 |  |  |  | 1075 | [10 empty] | 90.96 |  |  |  | 90.96 | [5 empty] | 91.54 |  |  | 90.94 |  |  |  | 8.54 |  | 8.50 | [8 empty] | 0.54 |  |  |  |  | 0.00
1999 |  |  |  | 7441.74 |  |  | 6905 |  |  |  | 1075 | [10 empty] | 78.87 |  |  |  | 78.87 | [5 empty] | 79.02 |  |  | 78.82 |  |  |  | 10.89 |  | 9.64 | [8 empty] | 11.50 |  |  |  |  | 0.00
2000 |  |  |  | 8477.38 |  |  | 7743 |  |  |  | 1075 | [10 empty] | 88.17 |  |  |  | 88.17 | [5 empty] | 89.78 |  |  | 88.15 |  |  |  | 0.61 |  | 0.55 | [8 empty] | 11.29 |  |  |  |  | 0.00
2001 |  |  |  | 9539.06 |  |  | 8718 |  |  |  | 1075 | [10 empty] | 99.52 |  |  |  | 99.52 | [5 empty] | 101.30 |  |  | 99.52 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 8847.93 |  |  | 8136 |  |  |  | 1075 | [10 empty] | 92.78 |  |  |  | 92.78 | [5 empty] | 93.96 |  |  | 92.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.22 |  |  |  |  | 0.00
2003 |  |  |  | 8503.13 |  |  | 7865 |  |  |  | 1075 | [10 empty] | 89.66 |  |  |  | 89.66 | [5 empty] | 90.30 |  |  | 89.78 |  |  |  | 1.25 |  | 1.13 | [8 empty] | 9.21 |  |  |  |  | 0.00
2004 |  |  |  | 9654.42 |  |  | 8771 |  |  |  | 1075 | [10 empty] | 99.86 |  |  |  | 99.86 | [5 empty] | 102.24 |  |  | 99.85 |  |  |  | 0.14 |  | 0.14 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 7913.75 |  |  | 6975 |  |  |  | 1089 | [10 empty] | 79.65 |  |  |  | 84.02 | [5 empty] | 82.95 |  |  | 79.61 |  |  |  | 0.85 |  | 0.72 | [8 empty] | 15.26 |  |  |  |  | 4.37
2006 |  |  |  | 9279.81 |  |  | 7996 |  |  |  | 1158 | [10 empty] | 91.30 |  |  |  | 91.30 | [5 empty] | 91.48 |  |  | 91.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.70 |  |  |  |  | 0.00
2007 |  |  |  | 9893.00 |  |  | 8423 |  |  |  | 1157 | [10 empty] | 96.18 |  |  |  | 96.18 | [5 empty] | 97.61 |  |  | 96.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.82 |  |  |  |  | 0.00
2008 |  |  |  | 9053.98 |  |  | 7703 |  |  |  | 1157 | [10 empty] | 87.73 |  |  |  | 90.27 | [5 empty] | 89.09 |  |  | 87.69 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 9.68 |  |  |  |  | 2.53
2009 |  |  |  | 8956.07 |  |  | 7648 |  |  |  | 1176 | [10 empty] | 87.52 |  |  |  | 87.52 | [5 empty] | 86.94 |  |  | 87.31 |  |  |  | 9.80 |  | 9.51 | [8 empty] | 2.97 |  |  |  |  | 0.00
2010 |  |  |  | 10276.18 |  |  | 8760 |  |  |  | 1168 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.43 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8942.35 |  |  | 7876 |  |  |  | 1168 | [10 empty] | 89.93 |  |  |  | 89.93 | [5 empty] | 87.40 |  |  | 89.91 |  |  |  | 0.18 |  | 0.17 | [8 empty] | 9.91 |  |  |  |  | 0.00
2012 |  |  |  | 7880.31 |  |  | 6820 |  |  |  | 1168 | [10 empty] | 77.68 |  |  |  | 79.22 | [5 empty] | 76.81 |  |  | 77.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.78 |  |  |  |  | 1.55
2013 |  |  |  | 9386.86 |  |  | 8176 |  |  |  | 1168 | [10 empty] | 93.33 |  |  |  | 93.33 | [5 empty] | 91.73 |  |  | 93.32 |  |  |  | 0.59 |  | 0.55 | [8 empty] | 6.12 |  |  |  |  | 0.00
2014 |  |  |  | 9166.31 |  |  | 7999 |  |  |  | 1168 | [10 empty] | 91.32 |  |  |  | 91.32 | [5 empty] | 89.59 |  |  | 91.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.68 |  |  |  |  | 0.00
2015 |  |  |  | 8405.17 |  |  | 7300 |  |  |  | 1168 | [10 empty] | 83.33 |  |  |  | 83.33 | [5 empty] | 82.15 |  |  | 83.33 |  |  |  | 2.54 |  | 2.17 | [8 empty] | 14.50 |  |  |  |  | 0.00
2016 |  |  |  | 10095.50 |  |  | 8622 |  |  |  | 1168 | [10 empty] | 98.16 |  |  |  | 98.16 | [5 empty] | 98.40 |  |  | 98.16 |  |  |  | 1.84 |  | 1.84 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 8401.72 |  |  | 7248 |  |  |  | 1168 | [10 empty] | 82.75 |  |  |  | 82.75 | [5 empty] | 82.11 |  |  | 82.74 |  |  |  | 4.54 |  | 3.94 | [8 empty] | 13.32 |  |  |  |  | 0.00
2018 |  |  |  | 10298.11 |  |  | 8760 |  |  |  | 1168 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.65 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7612.50 |  |  | 6528 |  |  |  | 1168 | [10 empty] | 74.54 |  |  |  | 74.54 | [5 empty] | 74.40 |  |  | 74.52 |  |  |  | 6.88 |  | 5.51 | [8 empty] | 19.95 |  |  |  |  | 0.00
2020 |  |  |  | 8961.22 |  |  | 7767 |  |  |  | 1168 | [10 empty] | 88.42 |  |  |  | 88.42 | [5 empty] | 87.34 |  |  | 88.42 |  |  |  | 1.72 |  | 1.55 | [8 empty] | 10.03 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 199
B. |  | Refuelling without maintenance | [20 empty] | 881 | [14 empty] | 25
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 764
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 77
E. |  | Testing of plant systems or components | [35 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 9
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 24
Z. |  | Other | [24 empty] | 136 | [14 empty] | 6
Subtotal | [22 empty] | 881 |  |  |  | 136 | [10 empty] | 867 |  |  |  | 214 | [11 empty] | 25
Total | [22 empty] | 1017 | [14 empty] | 1106
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 14
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 65
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 24
31. |  |  | Turbine and auxiliaries | [34 empty] | 40
32. |  |  | Feedwater and Main Steam System | [34 empty] | 21
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 11
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [37 empty] | 207
Highlights (2020)
Automatic reactor trip from 43% power during RF23 startup. An electrical fault in the motor generator system resulted in control rods dropping.

## WATTS BAR-1
2020 Operating Experience
US-390 | [8 empty] | WATTS BAR-1 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVA (Tennessee Valley Authority)
Owner | [7 empty] | : | TVA (Tennessee Valley Authority)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (ICECND) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-07-20
Thermal power | [12 empty] | : |  |  | 3459 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1996-02-06
Gross electrical power | [12 empty] | : |  |  | 1210 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1996-05-27
Reference unit power (net) | [12 empty] | : |  |  | 1157 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 24 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.71
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.105
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 32 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 36000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.85
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.88 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 9075.1 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.63 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.16 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.52 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.16 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.32 %
Load Factor (LF) | [18 empty] | : | 89.29 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.03 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 788 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 879.48 | 766.98 |  |  |  | 868.54 |  | 841.88 | [8 empty] | 198.40 |  |  | 647.33 | [6 empty] | 829.62 |  | 831.11 |  |  |  | 731.49 |  |  | 772.41 |  |  | 834.32 | [9 empty] | 873.53 |  |  | 9075.10
EAF [%] |  |  |  |  | 100.00 | 95.42 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 25.40 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 92.38 |  |  | 93.68 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.16
UCF [%] |  |  |  |  | 100.00 | 95.42 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 25.40 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 92.38 |  |  | 93.68 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.16
LF [%] |  |  |  |  | 102.17 | 95.25 |  |  |  | 100.90 |  | 101.06 | [8 empty] | 23.05 |  |  | 77.71 | [6 empty] | 96.38 |  | 96.55 |  |  |  | 87.81 |  |  | 89.73 |  |  | 100.15 | [9 empty] | 101.48 |  |  | 89.29
OF [%] |  |  |  |  | 100.00 | 95.40 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 25.40 |  |  | 86.39 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 92.36 |  |  | 93.68 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.03
FLR [%] |  |  |  |  | 0.00 | 4.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 7.62 |  |  | 6.32 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.63
UCL [%] |  |  |  |  | 0.00 | 4.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 7.62 |  |  | 6.32 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.52
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 74.60 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.32
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 198662.68 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.56 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.03 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.37 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.06 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.58 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.87 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.97 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1996 |  |  |  | 5544.23 |  |  | 5491 |  |  |  | 1109 | [10 empty] | 90.65 |  |  |  | 90.65 | [5 empty] | 88.78 |  |  | 91.16 |  |  |  | 0.21 |  | 0.19 | [8 empty] | 9.17 |  |  |  |  | 0.00
1997 |  |  |  | 7600.09 |  |  | 7269 |  |  |  | 1117 | [10 empty] | 82.27 |  |  |  | 82.27 | [5 empty] | 77.67 |  |  | 82.98 |  |  |  | 5.73 |  | 5.00 | [8 empty] | 12.73 |  |  |  |  | 0.00
1998 |  |  |  | 9680.98 |  |  | 8672 |  |  |  | 1117 | [10 empty] | 98.96 |  |  |  | 98.96 | [5 empty] | 98.93 |  |  | 99.00 |  |  |  | 1.04 |  | 1.04 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 8267.43 |  |  | 7606 |  |  |  | 1118 | [10 empty] | 86.84 |  |  |  | 86.84 | [5 empty] | 84.42 |  |  | 86.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.16 |  |  |  |  | 0.00
2000 |  |  |  | 9076.39 |  |  | 8124 |  |  |  | 1118 | [10 empty] | 92.50 |  |  |  | 92.50 | [5 empty] | 92.42 |  |  | 92.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.50 |  |  |  |  | 0.00
2001 |  |  |  | 9626.58 |  |  | 8419 |  |  |  | 1125 | [10 empty] | 96.13 |  |  |  | 96.13 | [5 empty] | 97.52 |  |  | 96.11 |  |  |  | 3.87 |  | 3.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 9079.35 |  |  | 7998 |  |  |  | 1125 | [10 empty] | 91.30 |  |  |  | 91.30 | [5 empty] | 92.13 |  |  | 91.30 |  |  |  | 2.10 |  | 1.95 | [8 empty] | 6.74 |  |  |  |  | 0.00
2003 |  |  |  | 8549.61 |  |  | 7551 |  |  |  | 1121 | [10 empty] | 86.16 |  |  |  | 86.16 | [5 empty] | 86.91 |  |  | 86.20 |  |  |  | 4.65 |  | 4.20 | [8 empty] | 9.64 |  |  |  |  | 0.00
2004 |  |  |  | 9856.92 |  |  | 8680 |  |  |  | 1121 | [10 empty] | 98.82 |  |  |  | 98.82 | [5 empty] | 100.10 |  |  | 98.82 |  |  |  | 1.18 |  | 1.18 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 8816.42 |  |  | 7841 |  |  |  | 1121 | [10 empty] | 89.52 |  |  |  | 89.52 | [5 empty] | 89.77 |  |  | 89.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.48 |  |  |  |  | 0.00
2006 |  |  |  | 6697.05 |  |  | 6099 |  |  |  | 1121 | [10 empty] | 69.66 |  |  |  | 69.66 | [5 empty] | 68.20 |  |  | 69.62 |  |  |  | 10.49 |  | 8.16 | [8 empty] | 22.18 |  |  |  |  | 0.00
2007 |  |  |  | 10049.69 |  |  | 8760 |  |  |  | 1123 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.16 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8112.31 |  |  | 7247 |  |  |  | 1123 | [10 empty] | 82.53 |  |  |  | 82.53 | [5 empty] | 82.24 |  |  | 82.50 |  |  |  | 6.44 |  | 5.68 | [8 empty] | 11.79 |  |  |  |  | 0.00
2009 |  |  |  | 9207.46 |  |  | 8055 |  |  |  | 1123 | [10 empty] | 91.96 |  |  |  | 91.96 | [5 empty] | 93.60 |  |  | 91.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.04 |  |  |  |  | 0.00
2010 |  |  |  | 9738.46 |  |  | 8544 |  |  |  | 1123 | [10 empty] | 97.55 |  |  |  | 97.55 | [5 empty] | 98.99 |  |  | 97.53 |  |  |  | 2.45 |  | 2.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 8230.98 |  |  | 7386 |  |  |  | 1123 | [10 empty] | 84.33 |  |  |  | 84.33 | [5 empty] | 83.67 |  |  | 84.32 |  |  |  | 0.93 |  | 0.79 | [8 empty] | 14.88 |  |  |  |  | 0.00
2012 |  |  |  | 8516.47 |  |  | 7557 |  |  |  | 1123 | [10 empty] | 86.04 |  |  |  | 86.04 | [5 empty] | 86.34 |  |  | 86.03 |  |  |  | 0.62 |  | 0.53 | [8 empty] | 13.42 |  |  |  |  | 0.00
2013 |  |  |  | 9967.80 |  |  | 8709 |  |  |  | 1123 | [10 empty] | 99.42 |  |  |  | 100.00 | [5 empty] | 101.31 |  |  | 99.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.58
2014 |  |  |  | 8789.69 |  |  | 7769 |  |  |  | 1123 | [10 empty] | 88.69 |  |  |  | 88.69 | [5 empty] | 89.35 |  |  | 88.69 |  |  |  | 0.51 |  | 0.45 | [8 empty] | 10.85 |  |  |  |  | 0.00
2015 |  |  |  | 8449.15 |  |  | 7609 |  |  |  | 1123 | [10 empty] | 86.86 |  |  |  | 86.86 | [5 empty] | 85.89 |  |  | 86.86 |  |  |  | 2.79 |  | 2.49 | [8 empty] | 10.65 |  |  |  |  | 0.00
2016 |  |  |  | 9441.96 |  |  | 8656 |  |  |  | 1123 | [10 empty] | 98.54 |  |  |  | 98.54 | [5 empty] | 95.72 |  |  | 98.54 |  |  |  | 1.46 |  | 1.46 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 8622.85 |  |  | 7529 |  |  |  | 1123 | [10 empty] | 85.94 |  |  |  | 85.94 | [5 empty] | 87.65 |  |  | 85.95 |  |  |  | 1.87 |  | 1.64 | [8 empty] | 12.41 |  |  |  |  | 0.00
2018 |  |  |  | 8840.45 |  |  | 7637 |  |  |  | 1157 | [10 empty] | 88.51 |  |  |  | 88.51 | [5 empty] | 87.22 |  |  | 87.18 |  |  |  | 1.24 |  | 1.11 | [8 empty] | 10.38 |  |  |  |  | 0.00
2019 |  |  |  | 8735.99 |  |  | 7514 |  |  |  | 1157 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 86.19 |  |  | 85.78 |  |  |  | 14.21 |  | 14.21 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 9075.10 |  |  | 7996 |  |  |  | 1157 | [10 empty] | 92.16 |  |  |  | 92.16 | [5 empty] | 89.29 |  |  | 91.03 |  |  |  | 1.63 |  | 1.52 | [8 empty] | 6.32 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1996 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 158
B. |  | Refuelling without maintenance | [20 empty] | 653 | [14 empty] | 27
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 612
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 60
E. |  | Testing of plant systems or components | [35 empty] | 29
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 16
P. |  | Fire | [39 empty] | 2
Z. |  | Other | [24 empty] | 134 | [10 empty] | 51 |  |  |  | 12
Subtotal | [22 empty] | 653 |  |  |  | 134 | [10 empty] | 779 |  |  |  | 188 | [11 empty] | 2
Total | [22 empty] | 787 | [14 empty] | 969
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1996 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 19
16. |  |  | Steam generation systems | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 56
32. |  |  | Feedwater and Main Steam System | [34 empty] | 38
33. |  |  | Circulating Water System | [34 empty] | 11
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 14
42. |  |  | Electrical Power Supply Systems | [34 empty] | 14
Total | [37 empty] | 166
Highlights (2020)
Repair U1 GV 1

## WATTS BAR-2
2020 Operating Experience
US-391 | [8 empty] | WATTS BAR-2 | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVA (Tennessee Valley Authority)
Owner | [7 empty] | : | TVA (Tennessee Valley Authority)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (ICECND) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-09-01
Thermal power | [12 empty] | : |  |  | 3411 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-06-03
Gross electrical power | [12 empty] | : |  |  | 1218 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-10-19
Reference unit power (net) | [12 empty] | : |  |  | 1164 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.71
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.05
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.85
| Active core height/length [m] | [13 empty] | : |  |  | 3.65 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.88 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 8513.91 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 6.33 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.31 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 6.17 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.31 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.52 %
Load Factor (LF) | [18 empty] | : | 83.27 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 85.93 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1236 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 883.57 | 826.11 |  |  |  | 806.75 |  | 843.95 | [8 empty] | 221.46 |  |  | 778.87 | [6 empty] | 825.24 |  | 831.68 |  |  |  | 819.94 |  |  | 626.70 |  |  | 243.17 | [9 empty] | 806.46 |  |  | 8513.91
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 96.46 |  | 100.00 | [8 empty] | 27.13 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 73.79 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.31
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 96.46 |  | 100.00 | [8 empty] | 27.13 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 73.79 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.31
LF [%] |  |  |  |  | 102.03 | 101.97 |  |  |  | 93.16 |  | 100.70 | [8 empty] | 25.57 |  |  | 92.93 | [6 empty] | 95.29 |  | 96.04 |  |  |  | 97.84 |  |  | 72.37 |  |  | 29.02 | [9 empty] | 93.12 |  |  | 83.27
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 96.37 |  | 100.00 | [8 empty] | 27.15 |  |  | 97.50 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 73.79 |  |  | 36.94 | [9 empty] | 100.00 |  |  | 85.93
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 72.87 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.33
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 72.87 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.17
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 3.54 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 26.21 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.52
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | -141918.54 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 12.77 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 12.09 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.55 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 5.36 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 79.6 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.17 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 2893.72 |  |  | 2593 |  |  |  | 1165 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.05 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 5026.65 |  |  | 4421 |  |  |  | 1165 | [10 empty] | 50.46 |  |  |  | 50.46 | [5 empty] | 49.25 |  |  | 50.47 |  |  |  | 43.34 |  | 38.59 | [8 empty] | 10.95 |  |  |  |  | 0.00
2018 |  |  |  | 9644.14 |  |  | 8397 |  |  |  | 1164 | [10 empty] | 95.97 |  |  |  | 95.97 | [5 empty] | 94.58 |  |  | 95.86 |  |  |  | 4.03 |  | 4.03 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 8944.95 |  |  | 7820 |  |  |  | 1164 | [10 empty] | 89.55 |  |  |  | 89.55 | [5 empty] | 87.72 |  |  | 89.27 |  |  |  | 1.72 |  | 1.57 | [8 empty] | 8.88 |  |  |  |  | 0.00
2020 |  |  |  | 8513.91 |  |  | 7548 |  |  |  | 1164 | [10 empty] | 91.31 |  |  |  | 91.31 | [5 empty] | 83.27 |  |  | 85.93 |  |  |  | 6.33 |  | 6.17 | [8 empty] | 2.52 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 2016 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 969
B. |  | Refuelling without maintenance | [20 empty] | 650 | [14 empty] | 156
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 422
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 26 | [14 empty] | 6
L. |  | Human factor related | [39 empty] | 15
Z. |  | Other | [24 empty] | 560 | [14 empty] | 134
Subtotal | [22 empty] | 676 |  |  |  | 560 | [10 empty] | 584 |  |  |  | 1118
Total | [22 empty] | 1236 | [14 empty] | 1702
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 2016 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 19
15. |  |  | Reactor Cooling Systems | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 108
32. |  |  | Feedwater and Main Steam System | [34 empty] | 710
34. |  |  | Miscellaneous Systems | [34 empty] | 47
Total | [37 empty] | 894
Highlights (2020)
Refueling Outage 3.

## WOLF CREEK
2020 Operating Experience
US-482 | [8 empty] | WOLF CREEK | [26 empty] | UNITED STATES OF AMERICA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | WCNOC (WOLF CREEK NUCLEAR OPERATING CORP.)
Owner | [7 empty] | : | KCP&L (Kansas City Power & Light Co.)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | GE (GENERAL ELECTRIC CO.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 4LP (DRYAMB) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-05-31
Thermal power | [12 empty] | : |  |  | 3565 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-06-12
Gross electrical power | [12 empty] | : |  |  | 1285 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-09-03
Reference unit power (net) | [12 empty] | : |  |  | 1200 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 6.3 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.86
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 22 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Pond (closed-cycle)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.85 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2020)
Net Energy Production | [18 empty] | : | 10582.48 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.45 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.55 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.45 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.55 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 100.4 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.53 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 41 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 911.52 | 791.95 |  |  |  | 911.47 |  | 882.42 | [8 empty] | 906.77 |  |  | 867.88 | [6 empty] | 889.61 |  | 892.89 |  |  |  | 871.48 |  |  | 908.72 |  |  | 840.65 | [9 empty] | 907.12 |  |  | 10582.48
EAF [%] |  |  |  |  | 100.00 | 94.27 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.55
UCF [%] |  |  |  |  | 100.00 | 94.27 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.55
LF [%] |  |  |  |  | 102.10 | 94.82 |  |  |  | 102.09 |  | 102.13 | [8 empty] | 101.57 |  |  | 100.45 | [6 empty] | 99.64 |  | 100.01 |  |  |  | 100.87 |  |  | 101.78 |  |  | 97.30 | [9 empty] | 101.60 |  |  | 100.40
OF [%] |  |  |  |  | 100.00 | 94.25 |  |  |  | 99.87 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.53
FLR [%] |  |  |  |  | 0.00 | 5.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.45
UCL [%] |  |  |  |  | 0.00 | 5.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.45
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 391653.71 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.83 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.85 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.42 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.9 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.68 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.5 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.85 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 3814.03 |  |  | 4350 |  |  |  | 1144 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 90.60 |  |  | 96.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 6966.06 |  |  | 6416 |  |  |  | 1128 | [10 empty] | 73.01 |  |  |  | 73.01 | [5 empty] | 70.50 |  |  | 73.24 |  |  |  | 9.92 |  | 8.04 | [8 empty] | 18.95 |  |  |  |  | 0.00
1987 |  |  |  | 6504.14 |  |  | 6009 |  |  |  | 1128 | [10 empty] | 68.59 |  |  |  | 68.59 | [5 empty] | 65.82 |  |  | 68.60 |  |  |  | 30.99 |  | 30.81 | [8 empty] | 0.61 |  |  |  |  | 0.00
1988 |  |  |  | 6676.39 |  |  | 5963 |  |  |  | 1128 | [10 empty] | 66.80 |  |  |  | 66.80 | [5 empty] | 67.38 |  |  | 67.88 |  |  |  | 10.14 |  | 7.54 | [8 empty] | 25.66 |  |  |  |  | 0.00
1989 |  |  |  | 9709.26 |  |  | 8618 |  |  |  | 1135 | [10 empty] | 98.35 |  |  |  | 98.35 | [5 empty] | 97.65 |  |  | 98.38 |  |  |  | 0.61 |  | 0.60 | [8 empty] | 1.05 |  |  |  |  | 0.00
1990 |  |  |  | 7889.14 |  |  | 7036 |  |  |  | 1135 | [10 empty] | 79.75 |  |  |  | 79.75 | [5 empty] | 79.35 |  |  | 80.32 |  |  |  | 1.78 |  | 1.44 | [8 empty] | 18.80 |  |  |  |  | 0.00
1991 |  |  |  | 5891.38 |  |  | 6288 |  |  |  | 1135 | [10 empty] | 70.99 |  |  |  | 70.99 | [5 empty] | 59.25 |  |  | 71.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.01 |  |  |  |  | 0.00
1992 |  |  |  | 8490.66 |  |  | 7538 |  |  |  | 1131 | [10 empty] | 85.38 |  |  |  | 85.38 | [5 empty] | 85.46 |  |  | 85.82 |  |  |  | 14.62 |  | 14.62 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 7908.61 |  |  | 7000 |  |  |  | 1132 | [10 empty] | 79.32 |  |  |  | 79.32 | [5 empty] | 79.74 |  |  | 79.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.68 |  |  |  |  | 0.00
1994 |  |  |  | 8545.97 |  |  | 7500 |  |  |  | 1149 | [10 empty] | 85.42 |  |  |  | 85.42 | [5 empty] | 84.89 |  |  | 85.62 |  |  |  | 0.79 |  | 0.68 | [8 empty] | 13.90 |  |  |  |  | 0.00
1995 |  |  |  | 10062.18 |  |  | 8625 |  |  |  | 1163 | [10 empty] | 98.47 |  |  |  | 98.47 | [5 empty] | 98.70 |  |  | 98.46 |  |  |  | 1.53 |  | 1.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 8233.68 |  |  | 7078 |  |  |  | 1165 | [10 empty] | 80.59 |  |  |  | 81.84 | [5 empty] | 80.41 |  |  | 80.58 |  |  |  | 0.68 |  | 0.56 | [8 empty] | 17.60 |  |  |  |  | 1.25
1997 |  |  |  | 8447.47 |  |  | 7255 |  |  |  | 1163 | [10 empty] | 82.80 |  |  |  | 82.80 | [5 empty] | 82.92 |  |  | 82.82 |  |  |  | 1.43 |  | 1.20 | [8 empty] | 16.00 |  |  |  |  | 0.00
1998 |  |  |  | 10400.72 |  |  | 8760 |  |  |  | 1163 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.09 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | 9156.62 |  |  | 7847 |  |  |  | 1163 | [10 empty] | 89.58 |  |  |  | 89.58 | [5 empty] | 89.88 |  |  | 89.58 |  |  |  | 0.32 |  | 0.28 | [8 empty] | 10.13 |  |  |  |  | 0.00
2000 |  |  |  | 9071.40 |  |  | 7795 |  |  |  | 1170 | [10 empty] | 88.75 |  |  |  | 88.75 | [5 empty] | 88.31 |  |  | 88.74 |  |  |  | 0.93 |  | 0.83 | [8 empty] | 10.41 |  |  |  |  | 0.00
2001 |  |  |  | 10346.66 |  |  | 8731 |  |  |  | 1170 | [10 empty] | 99.68 |  |  |  | 99.68 | [5 empty] | 100.95 |  |  | 99.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.32 |  |  |  |  | 0.00
2002 |  |  |  | 9041.70 |  |  | 7695 |  |  |  | 1165 | [10 empty] | 87.83 |  |  |  | 87.83 | [5 empty] | 88.44 |  |  | 87.84 |  |  |  | 2.51 |  | 2.26 | [8 empty] | 9.91 |  |  |  |  | 0.00
2003 |  |  |  | 8902.46 |  |  | 7594 |  |  |  | 1167 | [10 empty] | 86.70 |  |  |  | 86.70 | [5 empty] | 87.15 |  |  | 86.69 |  |  |  | 0.89 |  | 0.78 | [8 empty] | 12.52 |  |  |  |  | 0.00
2004 |  |  |  | 10132.74 |  |  | 8650 |  |  |  | 1166 | [10 empty] | 98.48 |  |  |  | 98.81 | [5 empty] | 98.93 |  |  | 98.47 |  |  |  | 1.19 |  | 1.19 | [8 empty] | 0.00 |  |  |  |  | 0.33
2005 |  |  |  | 8820.95 |  |  | 7528 |  |  |  | 1165 | [10 empty] | 85.97 |  |  |  | 85.97 | [5 empty] | 86.42 |  |  | 85.93 |  |  |  | 3.36 |  | 2.99 | [8 empty] | 11.04 |  |  |  |  | 0.00
2006 |  |  |  | 9350.27 |  |  | 7935 |  |  |  | 1166 | [10 empty] | 90.59 |  |  |  | 90.59 | [5 empty] | 91.54 |  |  | 90.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.41 |  |  |  |  | 0.00
2007 |  |  |  | 10369.14 |  |  | 8760 |  |  |  | 1166 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.52 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 8505.89 |  |  | 7271 |  |  |  | 1166 | [10 empty] | 82.78 |  |  |  | 82.78 | [5 empty] | 83.05 |  |  | 82.78 |  |  |  | 2.51 |  | 2.13 | [8 empty] | 15.09 |  |  |  |  | 0.00
2009 |  |  |  | 8768.55 |  |  | 7541 |  |  |  | 1160 | [10 empty] | 86.04 |  |  |  | 86.04 | [5 empty] | 86.29 |  |  | 86.08 |  |  |  | 2.52 |  | 2.22 | [8 empty] | 11.74 |  |  |  |  | 0.00
2010 |  |  |  | 9555.71 |  |  | 8163 |  |  |  | 1160 | [10 empty] | 93.20 |  |  |  | 93.20 | [5 empty] | 94.04 |  |  | 93.18 |  |  |  | 6.80 |  | 6.80 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 7350.65 |  |  | 6333 |  |  |  | 1195 | [10 empty] | 72.79 |  |  |  | 72.79 | [5 empty] | 71.08 |  |  | 72.29 |  |  |  | 1.26 |  | 0.93 | [8 empty] | 26.28 |  |  |  |  | 0.00
2012 |  |  |  | 8295.93 |  |  | 7014 |  |  |  | 1195 | [10 empty] | 79.86 |  |  |  | 79.86 | [5 empty] | 79.03 |  |  | 79.85 |  |  |  | 20.14 |  | 20.14 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 7175.89 |  |  | 6210 |  |  |  | 1195 | [10 empty] | 70.89 |  |  |  | 70.89 | [5 empty] | 68.54 |  |  | 70.88 |  |  |  | 11.95 |  | 9.62 | [8 empty] | 19.50 |  |  |  |  | 0.00
2014 |  |  |  | 8569.17 |  |  | 7161 |  |  |  | 1195 | [10 empty] | 81.74 |  |  |  | 81.74 | [5 empty] | 81.86 |  |  | 81.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.26 |  |  |  |  | 0.00
2015 |  |  |  | 8653.66 |  |  | 7194 |  |  |  | 1200 | [10 empty] | 82.18 |  |  |  | 82.18 | [5 empty] | 82.32 |  |  | 82.12 |  |  |  | 0.34 |  | 0.28 | [8 empty] | 17.54 |  |  |  |  | 0.00
2016 |  |  |  | 8251.51 |  |  | 6867 |  |  |  | 1200 | [10 empty] | 78.17 |  |  |  | 78.17 | [5 empty] | 78.28 |  |  | 78.18 |  |  |  | 4.82 |  | 3.96 | [8 empty] | 17.87 |  |  |  |  | 0.00
2017 |  |  |  | 10648.17 |  |  | 8760 |  |  |  | 1200 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.30 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 9176.04 |  |  | 7597 |  |  |  | 1200 | [10 empty] | 87.12 |  |  |  | 87.12 | [5 empty] | 87.29 |  |  | 86.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.88 |  |  |  |  | 0.00
2019 |  |  |  | 9255.42 |  |  | 7643 |  |  |  | 1200 | [10 empty] | 87.25 |  |  |  | 87.25 | [5 empty] | 88.05 |  |  | 87.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.75 |  |  |  |  | 0.00
2020 |  |  |  | 10582.48 |  |  | 8743 |  |  |  | 1200 | [10 empty] | 99.55 |  |  |  | 99.55 | [5 empty] | 100.40 |  |  | 99.53 |  |  |  | 0.45 |  | 0.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2020 | [14 empty] | 1985 to 2020
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 200
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 889 |  |  |  | 10
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 52
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 79
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
Z. |  | Other | [24 empty] | 40 | [14 empty] | 7
Subtotal | [26 empty] | 40 | [10 empty] | 941 |  |  |  | 299 | [11 empty] | 7
Total | [22 empty] | 40 | [14 empty] | 1247
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2020 | [14 empty] | 1985 to 2020
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 19
12. |  |  | Reactor I&C Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 29
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 49
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 59
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [37 empty] | 209
Highlights (2020)
Shutdown due to containment leakage rate exceeding acceptance criteria. Adjustment of a retaining ring and T-Ring were completed. Event Notification 54508 was made. LER is pending.