## BELARUSIAN-1
2021 Operating Experience
BY-1 | [8 empty] | BELARUSIAN-1 | [26 empty] | BELARUS
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BelNPP (Republican Unitary Enterprise "Belarusian Nuclear Power Plant")
Owner | [7 empty] | : | BelNPP (Republican Unitary Enterprise "Belarusian Nuclear Power Plant")
Reactor Supplier | [7 empty] | : | JSC ASE (JSC "Atomstroyexport")
Turbine Supplier | [7 empty] | : | JSC ASE (JSC "Atomstroyexport")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-491 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2013-11-08
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-11-03
Gross electrical power | [12 empty] | : |  |  | 1194 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-06-10
Reference unit power (net) | [12 empty] | : |  |  | 1110 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 55500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 4
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.73 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.87 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [13 empty] | : |  |  | 121 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 5
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 5422.11 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 40.71 %
Energy Availability Factor (EAF) | [18 empty] | : | 58.75 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 40.34 %
Unit Capability Factor (UCF) | [18 empty] | : | 58.75 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.91 %
Load Factor (LF) | [18 empty] | : | 58.32 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 59.66 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3505 hours
Annual Summary
[5 empty] | May | Jan |  |  |  | Feb |  | Mar | [8 empty] | Apr |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [23 empty] | 773.92 | [6 empty] | 295.24 |  | 0.00 |  |  |  | 0.00 |  |  | 701.75 |  |  | 725.43 | [9 empty] | 828.61 |  |  | 3324.96
EAF [%] | [23 empty] | 100.00 | [6 empty] | 37.23 |  | 0.00 |  |  |  | 0.00 |  |  | 84.27 |  |  | 90.16 | [9 empty] | 100.00 |  |  | 58.75
UCF [%] | [23 empty] | 100.00 | [6 empty] | 37.23 |  | 0.00 |  |  |  | 0.00 |  |  | 84.27 |  |  | 90.16 | [9 empty] | 100.00 |  |  | 58.75
LF [%] | [23 empty] | 96.84 | [6 empty] | 35.75 |  | 0.00 |  |  |  | 0.00 |  |  | 84.97 |  |  | 90.77 | [9 empty] | 100.34 |  |  | 58.32
OF [%] | [23 empty] | 100.00 | [6 empty] | 37.23 |  | 0.00 |  |  |  | 0.00 |  |  | 87.90 |  |  | 92.92 | [9 empty] | 100.00 |  |  | 59.66
FLR [%] | [23 empty] | 0.00 | [6 empty] | 62.77 |  | 100.00 |  |  |  | 100.00 |  |  | 12.55 |  |  | 7.28 | [9 empty] | 0.00 |  |  | 40.71
UCL [%] | [23 empty] | 0.00 | [6 empty] | 62.77 |  | 100.00 |  |  |  | 100.00 |  |  | 12.10 |  |  | 7.08 | [9 empty] | 0.00 |  |  | 40.34
PUF [%] | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 3.63 |  |  | 2.75 | [9 empty] | 0.00 |  |  | 0.91
XUF [%] | [23 empty] | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 5724.77 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 40.71 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 58.75 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 40.34 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 58.75 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0.91 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 58.32 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 59.66 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2021 |  |  |  | 5422.11 |  |  | 5255 |  |  |  | 1110 | [10 empty] | 58.75 |  |  |  | 58.75 | [5 empty] | 58.32 |  |  | 59.66 |  |  |  | 40.71 |  | 40.34 | [8 empty] | 0.91 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2021 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 2073 | [14 empty] | 3554
Subtotal | [26 empty] | 2073 | [14 empty] | 3554
Total | [22 empty] | 2073 | [14 empty] | 3554
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2021 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [19 empty] | 52 | [14 empty] | 52
41. |  |  | Main Generator Systems | [19 empty] | 2021 | [14 empty] | 2021
Total | [22 empty] | 2073 | [14 empty] | 2073
Highlights (2021)
1. Trial operation - until 10/06/2021 2. Commercial operation - 10/06/2021