## BROKDORF
2021 Operating Experience
DE-32 | [8 empty] | BROKDORF | [26 empty] | GERMANY
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | PElektra (PreussenElektra GmbH)
Owner | [7 empty] | : | PEL/VEN (1. (80%) PreussenElektra GmbH 2. (20%) Vattenfall GmbH)
Reactor Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / PWR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-01-01
Thermal power | [12 empty] | : |  |  | 3900 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-10-14
Gross electrical power | [12 empty] | : |  |  | 1480 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-12-22
Reference unit power (net) | [12 empty] | : |  |  | 1410 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.63
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 71 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 34000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.6 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.7
| Active core height/length [m] | [13 empty] | : |  |  | 3.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 11436.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.6 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.49 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.6 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.35 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.04 %
Load Factor (LF) | [18 empty] | : | 92.59 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.86 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 972.23 | 893.93 |  |  |  | 961.83 |  | 925.71 | [8 empty] | 968.95 |  |  | 973.31 | [6 empty] | 988.29 |  | 986.63 |  |  |  | 966.07 |  |  | 941.10 |  |  | 905.81 | [9 empty] | 952.72 |  |  | 11436.58
EAF [%] |  |  |  |  | 98.61 | 98.50 |  |  |  | 98.55 |  | 98.32 | [8 empty] | 98.32 |  |  | 97.30 | [6 empty] | 95.90 |  | 95.34 |  |  |  | 95.80 |  |  | 96.82 |  |  | 98.21 | [9 empty] | 98.38 |  |  | 97.49
UCF [%] |  |  |  |  | 99.95 | 99.96 |  |  |  | 99.96 |  | 99.97 | [8 empty] | 99.95 |  |  | 100.00 | [6 empty] | 99.63 |  | 98.65 |  |  |  | 98.32 |  |  | 98.58 |  |  | 98.57 | [9 empty] | 98.71 |  |  | 99.35
LF [%] |  |  |  |  | 92.68 | 94.34 |  |  |  | 91.81 |  | 91.19 | [8 empty] | 92.37 |  |  | 95.87 | [6 empty] | 94.21 |  | 94.05 |  |  |  | 95.16 |  |  | 89.59 |  |  | 89.23 | [9 empty] | 90.82 |  |  | 92.59
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.24 |  | 1.29 |  |  |  | 1.64 |  |  | 1.42 |  |  | 1.38 | [9 empty] | 1.23 |  |  | 0.60
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.24 |  | 1.29 |  |  |  | 1.64 |  |  | 1.42 |  |  | 1.38 | [9 empty] | 1.23 |  |  | 0.60
PUF [%] |  |  |  |  | 0.05 | 0.04 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.05 |  |  | 0.00 | [6 empty] | 0.12 |  | 0.06 |  |  |  | 0.04 |  |  | 0.00 |  |  | 0.05 | [9 empty] | 0.06 |  |  | 0.04
XUF [%] |  |  |  |  | 1.34 | 1.47 |  |  |  | 1.41 |  | 1.64 | [8 empty] | 1.64 |  |  | 2.70 | [6 empty] | 3.74 |  | 3.31 |  |  |  | 2.52 |  |  | 1.76 |  |  | 0.36 | [9 empty] | 0.33 |  |  | 1.86
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 364345.49 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.94 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.62 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.62 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.94 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.44 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.28 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.32 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 296.84 |  |  | 228 |  |  |  | 1307 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 9481.26 |  |  | 7477 |  |  |  | 1307 | [10 empty] | 85.18 |  |  |  | 85.18 | [5 empty] | 82.81 |  |  | 85.35 |  |  |  | 14.78 |  | 14.77 | [8 empty] | 0.06 |  |  |  |  | 0.00
1988 |  |  |  | 8581.77 |  |  | 7014 |  |  |  | 1326 | [10 empty] | 85.22 |  |  |  | 85.22 | [5 empty] | 73.68 |  |  | 79.85 |  |  |  | 4.26 |  | 3.79 | [8 empty] | 10.99 |  |  |  |  | 0.00
1989 |  |  |  | 8991.29 |  |  | 7134 |  |  |  | 1326 | [10 empty] | 79.99 |  |  |  | 79.99 | [5 empty] | 77.41 |  |  | 81.44 |  |  |  | 0.70 |  | 0.56 | [8 empty] | 19.44 |  |  |  |  | 0.00
1990 |  |  |  | 8337.23 |  |  | 6447 |  |  |  | 1326 | [10 empty] | 72.49 |  |  |  | 72.49 | [5 empty] | 71.78 |  |  | 73.60 |  |  |  | 13.76 |  | 11.56 | [8 empty] | 15.95 |  |  |  |  | 0.00
1991 |  |  |  | 9492.73 |  |  | 7542 |  |  |  | 1326 | [10 empty] | 85.66 |  |  |  | 85.66 | [5 empty] | 81.72 |  |  | 86.10 |  |  |  | 0.11 |  | 0.09 | [8 empty] | 14.25 |  |  |  |  | 0.00
1992 |  |  |  | 10788.03 |  |  | 8461 |  |  |  | 1326 | [10 empty] | 96.04 |  |  |  | 96.04 | [5 empty] | 92.62 |  |  | 96.32 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 3.94 |  |  |  |  | 0.00
1993 |  |  |  | 9447.12 |  |  | 7441 |  |  |  | 1326 | [10 empty] | 84.76 |  |  |  | 85.63 | [5 empty] | 81.33 |  |  | 84.94 |  |  |  | 6.56 |  | 6.01 | [8 empty] | 8.36 |  |  |  |  | 0.87
1994 |  |  |  | 10228.60 |  |  | 7793 |  |  |  | 1326 | [10 empty] | 88.71 |  |  |  | 88.71 | [5 empty] | 88.06 |  |  | 88.96 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 11.20 |  |  |  |  | 0.00
1995 |  |  |  | 9912.37 |  |  | 7833 |  |  |  | 1326 | [10 empty] | 86.57 |  |  |  | 86.57 | [5 empty] | 85.34 |  |  | 89.42 |  |  |  | 0.14 |  | 0.12 | [8 empty] | 13.30 |  |  |  |  | 0.00
1996 |  |  |  | 10555.39 |  |  | 8212 |  |  |  | 1326 | [10 empty] | 93.23 |  |  |  | 93.23 | [5 empty] | 90.62 |  |  | 93.49 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 6.73 |  |  |  |  | 0.00
1997 |  |  |  | 11249.32 |  |  | 8328 |  |  |  | 1326 | [10 empty] | 95.12 |  |  |  | 95.12 | [5 empty] | 96.85 |  |  | 95.07 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 4.85 |  |  |  |  | 0.00
1998 |  |  |  | 10752.32 |  |  | 7966 |  |  |  | 1326 | [10 empty] | 90.40 |  |  |  | 92.59 | [5 empty] | 92.57 |  |  | 90.94 |  |  |  | 0.23 |  | 0.22 | [8 empty] | 7.20 |  |  |  |  | 2.19
1999 |  |  |  | 11093.31 |  |  | 8177 |  |  |  | 1370 | [10 empty] | 93.31 |  |  |  | 93.31 | [5 empty] | 92.43 |  |  | 93.34 |  |  |  | 1.95 |  | 1.86 | [8 empty] | 4.83 |  |  |  |  | 0.00
2000 |  |  |  | 11335.07 |  |  | 8397 |  |  |  | 1370 | [10 empty] | 95.55 |  |  |  | 95.55 | [5 empty] | 94.19 |  |  | 95.59 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 4.43 |  |  |  |  | 0.00
2001 |  |  |  | 11215.40 |  |  | 8331 |  |  |  | 1370 | [10 empty] | 94.95 |  |  |  | 94.95 | [5 empty] | 93.45 |  |  | 95.10 |  |  |  | 0.55 |  | 0.53 | [8 empty] | 4.52 |  |  |  |  | 0.00
2002 |  |  |  | 11336.92 |  |  | 8405 |  |  |  | 1370 | [10 empty] | 95.78 |  |  |  | 95.78 | [5 empty] | 94.46 |  |  | 95.95 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 4.19 |  |  |  |  | 0.00
2003 |  |  |  | 10564.58 |  |  | 7903 |  |  |  | 1370 | [10 empty] | 90.11 |  |  |  | 90.11 | [5 empty] | 88.03 |  |  | 90.22 |  |  |  | 0.01 |  | 3.23 | [8 empty] | 6.67 |  |  |  |  | 0.00
2004 |  |  |  | 11040.81 |  |  | 8327 |  |  |  | 1370 | [10 empty] | 94.65 |  |  |  | 94.65 | [5 empty] | 91.75 |  |  | 94.80 |  |  |  | 0.03 |  | 0.67 | [8 empty] | 4.68 |  |  |  |  | 0.00
2005 |  |  |  | 11400.69 |  |  | 8433 |  |  |  | 1370 | [10 empty] | 95.86 |  |  |  | 96.12 | [5 empty] | 94.99 |  |  | 96.26 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 3.85 |  |  |  |  | 0.26
2006 |  |  |  | 11201.33 |  |  | 8307 |  |  |  | 1370 | [10 empty] | 93.72 |  |  |  | 94.67 | [5 empty] | 93.34 |  |  | 94.83 |  |  |  | 0.63 |  | 0.60 | [8 empty] | 4.73 |  |  |  |  | 0.95
2007 |  |  |  | 11425.65 |  |  | 8293 |  |  |  | 1370 | [10 empty] | 94.33 |  |  |  | 94.50 | [5 empty] | 95.19 |  |  | 94.66 |  |  |  | 0.05 |  | 0.34 | [8 empty] | 5.16 |  |  |  |  | 0.17
2008 |  |  |  | 11450.40 |  |  | 8320 |  |  |  | 1410 | [10 empty] | 94.13 |  |  |  | 94.57 | [5 empty] | 92.45 |  |  | 94.72 |  |  |  | 0.01 |  | 0.64 | [8 empty] | 4.79 |  |  |  |  | 0.44
2009 |  |  |  | 11459.42 |  |  | 8260 |  |  |  | 1410 | [10 empty] | 94.12 |  |  |  | 94.13 | [5 empty] | 92.78 |  |  | 94.29 |  |  |  | 0.02 |  | 0.79 | [8 empty] | 5.07 |  |  |  |  | 0.01
2010 |  |  |  | 11360.45 |  |  | 8201 |  |  |  | 1410 | [10 empty] | 93.30 |  |  |  | 93.42 | [5 empty] | 91.98 |  |  | 93.62 |  |  |  | 0.06 |  | 1.96 | [8 empty] | 4.62 |  |  |  |  | 0.13
2011 |  |  |  | 9701.26 |  |  | 7382 |  |  |  | 1410 | [10 empty] | 79.13 |  |  |  | 79.25 | [5 empty] | 78.54 |  |  | 84.27 |  |  |  | 11.99 |  | 14.57 | [8 empty] | 6.19 |  |  |  |  | 0.12
2012 |  |  |  | 10246.91 |  |  | 7369 |  |  |  | 1410 | [10 empty] | 83.65 |  |  |  | 83.65 | [5 empty] | 82.73 |  |  | 83.89 |  |  |  | 4.26 |  | 8.05 | [8 empty] | 8.30 |  |  |  |  | 0.00
2013 |  |  |  | 11146.17 |  |  | 8108 |  |  |  | 1410 | [10 empty] | 92.06 |  |  |  | 92.13 | [5 empty] | 90.24 |  |  | 92.56 |  |  |  | 0.19 |  | 0.44 | [8 empty] | 7.43 |  |  |  |  | 0.07
2014 |  |  |  | 10974.17 |  |  | 8136 |  |  |  | 1410 | [10 empty] | 92.76 |  |  |  | 92.76 | [5 empty] | 88.86 |  |  | 92.89 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 7.11 |  |  |  |  | 0.00
2015 |  |  |  | 10624.78 |  |  | 8210 |  |  |  | 1410 | [10 empty] | 92.83 |  |  |  | 92.91 | [5 empty] | 86.02 |  |  | 93.72 |  |  |  | 0.34 |  | 0.32 | [8 empty] | 6.78 |  |  |  |  | 0.08
2016 |  |  |  | 10958.01 |  |  | 8194 |  |  |  | 1410 | [10 empty] | 92.88 |  |  |  | 93.08 | [5 empty] | 88.47 |  |  | 93.28 |  |  |  | 0.19 |  | 0.76 | [8 empty] | 6.17 |  |  |  |  | 0.20
2017 |  |  |  | 5480.41 |  |  | 4527 |  |  |  | 1410 | [10 empty] | 48.15 |  |  |  | 48.23 | [5 empty] | 44.37 |  |  | 51.67 |  |  |  | 0.10 |  | 42.78 | [8 empty] | 8.99 |  |  |  |  | 0.08
2018 |  |  |  | 9838.25 |  |  | 7937 |  |  |  | 1410 | [10 empty] | 83.12 |  |  |  | 84.72 | [5 empty] | 79.65 |  |  | 90.61 |  |  |  | 1.82 |  | 1.58 | [8 empty] | 13.70 |  |  |  |  | 1.60
2019 |  |  |  | 9635.80 |  |  | 7682 |  |  |  | 1410 | [10 empty] | 81.41 |  |  |  | 82.34 | [5 empty] | 78.01 |  |  | 87.69 |  |  |  | 4.63 |  | 5.25 | [8 empty] | 12.42 |  |  |  |  | 0.93
2020 |  |  |  | 10015.11 |  |  | 7969 |  |  |  | 1410 | [10 empty] | 85.30 |  |  |  | 86.38 | [5 empty] | 80.86 |  |  | 90.72 |  |  |  | 0.29 |  | 3.38 | [8 empty] | 10.24 |  |  |  |  | 1.08
2021 |  |  |  | 11436.58 |  |  | 8760 |  |  |  | 1410 | [10 empty] | 97.49 |  |  |  | 99.35 | [5 empty] | 92.59 |  |  | 100.00 |  |  |  | 0.60 |  | 0.60 | [8 empty] | 0.04 |  |  |  |  | 1.86
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1986 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 229
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 561
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 5 |  |  |  | 6
E. |  | Testing of plant systems or components | [35 empty] | 0
H. |  | Nuclear regulatory requirements | [39 empty] | 35
L. |  | Human factor related | [39 empty] | 18
M. |  | Governmental requirements or court decisions | [31 empty] | 4 | [19 empty] | 0
Z. |  | Other | [39 empty] | 9 | [11 empty] | 2
Subtotal | [33 empty] | 4 |  |  |  | 566 |  |  |  | 297 | [11 empty] | 2
Total | [22 empty] | 4 | [14 empty] | 865
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1986 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 145
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
33. |  |  | Circulating Water System | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 55
42. |  |  | Electrical Power Supply Systems | [34 empty] | 16
Total | [37 empty] | 240

## EMSLAND
2021 Operating Experience
DE-33 | [8 empty] | EMSLAND | [26 empty] | GERMANY
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KLE (Kernkraftwerke Lippe-Ems GmbH)
Owner | [7 empty] | : | RWE/PEL (1. (75%) RWE Power AG 2. (25%) PreussenElektra GmbH)
Reactor Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / Konvoi | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-08-10
Thermal power | [12 empty] | : |  |  | 3850 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-04-19
Gross electrical power | [12 empty] | : |  |  | 1406 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-06-20
Reference unit power (net) | [12 empty] | : |  |  | 1335 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.62
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 32000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.6 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.05
| Active core height/length [m] | [13 empty] | : |  |  | 3.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 10779.48 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.85 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.37 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.63 %
Load Factor (LF) | [18 empty] | : | 92.17 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.51 %
Operating Factor (OF) | [18 empty] | : | 95.43 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 400 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1008.58 | 901.21 |  |  |  | 993.09 |  | 893.80 | [8 empty] | 454.88 |  |  | 942.67 | [6 empty] | 955.53 |  | 957.41 |  |  |  | 934.76 |  |  | 903.52 |  |  | 943.82 | [9 empty] | 890.22 |  |  | 10779.48
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.88 |  | 93.11 | [8 empty] | 46.20 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.85
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.21 | [8 empty] | 46.20 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.37
LF [%] |  |  |  |  | 101.54 | 100.46 |  |  |  | 100.12 |  | 92.99 | [8 empty] | 45.80 |  |  | 98.07 | [6 empty] | 96.20 |  | 96.39 |  |  |  | 97.25 |  |  | 90.84 |  |  | 98.19 | [9 empty] | 89.63 |  |  | 92.17
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.44 | [8 empty] | 46.77 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.43
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.79 | [8 empty] | 53.80 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.63
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.12 |  | 6.10 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.51
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 360769.02 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 93.33 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.58 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.54 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 5.88 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 92.97 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.21 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 93.7 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 5694.91 |  |  | 4516 |  |  |  | 1262 | [10 empty] | 96.27 |  |  |  | 96.27 | [5 empty] | 98.06 |  |  | 96.54 |  |  |  | 3.68 |  | 3.68 | [8 empty] | 0.05 |  |  |  |  | 0.00
1989 |  |  |  | 9857.21 |  |  | 7794 |  |  |  | 1242 | [10 empty] | 88.65 |  |  |  | 88.65 | [5 empty] | 90.60 |  |  | 88.97 |  |  |  | 1.23 |  | 1.10 | [8 empty] | 10.25 |  |  |  |  | 0.00
1990 |  |  |  | 10039.24 |  |  | 7956 |  |  |  | 1256 | [10 empty] | 90.37 |  |  |  | 90.37 | [5 empty] | 91.18 |  |  | 90.82 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 9.50 |  |  |  |  | 0.00
1991 |  |  |  | 9287.28 |  |  | 7304 |  |  |  | 1242 | [10 empty] | 81.99 |  |  |  | 81.99 | [5 empty] | 85.36 |  |  | 83.38 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 18.00 |  |  |  |  | 0.00
1992 |  |  |  | 10158.05 |  |  | 7933 |  |  |  | 1290 | [10 empty] | 90.16 |  |  |  | 90.16 | [5 empty] | 89.65 |  |  | 90.31 |  |  |  | 1.93 |  | 1.77 | [8 empty] | 8.07 |  |  |  |  | 0.00
1993 |  |  |  | 10477.10 |  |  | 8147 |  |  |  | 1290 | [10 empty] | 92.92 |  |  |  | 92.92 | [5 empty] | 92.71 |  |  | 93.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.08 |  |  |  |  | 0.00
1994 |  |  |  | 10526.69 |  |  | 8193 |  |  |  | 1290 | [10 empty] | 93.43 |  |  |  | 93.43 | [5 empty] | 93.15 |  |  | 93.53 |  |  |  | 0.56 |  | 0.53 | [8 empty] | 6.04 |  |  |  |  | 0.00
1995 |  |  |  | 10495.72 |  |  | 8168 |  |  |  | 1290 | [10 empty] | 93.09 |  |  |  | 93.09 | [5 empty] | 92.88 |  |  | 93.24 |  |  |  | 1.75 |  | 1.66 | [8 empty] | 5.25 |  |  |  |  | 0.00
1996 |  |  |  | 10557.29 |  |  | 8195 |  |  |  | 1290 | [10 empty] | 93.19 |  |  |  | 93.19 | [5 empty] | 93.17 |  |  | 93.29 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 6.77 |  |  |  |  | 0.00
1997 |  |  |  | 10650.19 |  |  | 8298 |  |  |  | 1290 | [10 empty] | 94.58 |  |  |  | 94.58 | [5 empty] | 94.25 |  |  | 94.73 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 5.37 |  |  |  |  | 0.00
1998 |  |  |  | 10794.75 |  |  | 8388 |  |  |  | 1290 | [10 empty] | 95.69 |  |  |  | 95.69 | [5 empty] | 95.53 |  |  | 95.75 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 4.21 |  |  |  |  | 0.00
1999 |  |  |  | 10729.18 |  |  | 8413 |  |  |  | 1290 | [10 empty] | 95.96 |  |  |  | 95.96 | [5 empty] | 94.95 |  |  | 96.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.04 |  |  |  |  | 0.00
2000 |  |  |  | 10801.99 |  |  | 8339 |  |  |  | 1329 | [10 empty] | 94.91 |  |  |  | 94.91 | [5 empty] | 94.14 |  |  | 94.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.09 |  |  |  |  | 0.00
2001 |  |  |  | 10933.15 |  |  | 8257 |  |  |  | 1329 | [10 empty] | 93.80 |  |  |  | 94.15 | [5 empty] | 93.91 |  |  | 94.26 |  |  |  | 0.30 |  | 0.29 | [8 empty] | 5.57 |  |  |  |  | 0.35
2002 |  |  |  | 11242.30 |  |  | 8497 |  |  |  | 1329 | [10 empty] | 96.86 |  |  |  | 96.86 | [5 empty] | 96.57 |  |  | 97.00 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 3.04 |  |  |  |  | 0.00
2003 |  |  |  | 11096.98 |  |  | 8401 |  |  |  | 1329 | [10 empty] | 95.84 |  |  |  | 95.84 | [5 empty] | 95.32 |  |  | 95.90 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 4.15 |  |  |  |  | 0.00
2004 |  |  |  | 11147.20 |  |  | 8456 |  |  |  | 1329 | [10 empty] | 96.08 |  |  |  | 96.08 | [5 empty] | 95.49 |  |  | 96.27 |  |  |  | 0.10 |  | 0.70 | [8 empty] | 3.23 |  |  |  |  | 0.00
2005 |  |  |  | 10887.83 |  |  | 8239 |  |  |  | 1329 | [10 empty] | 93.92 |  |  |  | 93.92 | [5 empty] | 93.51 |  |  | 94.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.08 |  |  |  |  | 0.00
2006 |  |  |  | 11147.60 |  |  | 8461 |  |  |  | 1329 | [10 empty] | 95.80 |  |  |  | 96.43 | [5 empty] | 95.75 |  |  | 96.59 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 3.55 |  |  |  |  | 0.63
2007 |  |  |  | 10989.22 |  |  | 8311 |  |  |  | 1329 | [10 empty] | 94.43 |  |  |  | 94.70 | [5 empty] | 94.38 |  |  | 94.86 |  |  |  | 0.16 |  | 0.88 | [8 empty] | 4.42 |  |  |  |  | 0.27
2008 |  |  |  | 10896.15 |  |  | 8211 |  |  |  | 1329 | [10 empty] | 93.37 |  |  |  | 93.45 | [5 empty] | 93.34 |  |  | 93.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.55 |  |  |  |  | 0.08
2009 |  |  |  | 10849.24 |  |  | 8194 |  |  |  | 1329 | [10 empty] | 93.25 |  |  |  | 93.27 | [5 empty] | 93.19 |  |  | 93.54 |  |  |  | 2.81 |  | 2.82 | [8 empty] | 3.92 |  |  |  |  | 0.02
2010 |  |  |  | 10977.96 |  |  | 8286 |  |  |  | 1329 | [10 empty] | 94.41 |  |  |  | 94.42 | [5 empty] | 94.30 |  |  | 94.59 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 5.50 |  |  |  |  | 0.01
2011 |  |  |  | 11055.52 |  |  | 8339 |  |  |  | 1329 | [10 empty] | 94.97 |  |  |  | 95.06 | [5 empty] | 94.96 |  |  | 95.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.94 |  |  |  |  | 0.08
2012 |  |  |  | 10847.66 |  |  | 8314 |  |  |  | 1329 | [10 empty] | 94.50 |  |  |  | 94.50 | [5 empty] | 92.92 |  |  | 94.65 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 5.44 |  |  |  |  | 0.00
2013 |  |  |  | 10912.11 |  |  | 8328 |  |  |  | 1329 | [10 empty] | 94.95 |  |  |  | 94.95 | [5 empty] | 93.73 |  |  | 95.07 |  |  |  | 0.41 |  | 0.39 | [8 empty] | 4.66 |  |  |  |  | 0.00
2014 |  |  |  | 10954.90 |  |  | 8341 |  |  |  | 1335 | [10 empty] | 95.14 |  |  |  | 95.14 | [5 empty] | 93.88 |  |  | 95.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.86 |  |  |  |  | 0.00
2015 |  |  |  | 10396.15 |  |  | 7980 |  |  |  | 1335 | [10 empty] | 90.60 |  |  |  | 90.60 | [5 empty] | 88.90 |  |  | 91.10 |  |  |  | 0.03 |  | 1.46 | [8 empty] | 7.94 |  |  |  |  | 0.00
2016 |  |  |  | 10539.68 |  |  | 8279 |  |  |  | 1335 | [10 empty] | 90.44 |  |  |  | 94.13 | [5 empty] | 89.88 |  |  | 94.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.86 |  |  |  |  | 3.70
2017 |  |  |  | 10751.53 |  |  | 8171 |  |  |  | 1335 | [10 empty] | 92.93 |  |  |  | 93.13 | [5 empty] | 91.94 |  |  | 93.28 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 6.87 |  |  |  |  | 0.20
2018 |  |  |  | 10915.03 |  |  | 8303 |  |  |  | 1335 | [10 empty] | 94.16 |  |  |  | 94.67 | [5 empty] | 93.33 |  |  | 94.78 |  |  |  | 0.03 |  | 0.51 | [8 empty] | 4.82 |  |  |  |  | 0.51
2019 |  |  |  | 10237.09 |  |  | 7814 |  |  |  | 1335 | [10 empty] | 88.70 |  |  |  | 89.12 | [5 empty] | 87.54 |  |  | 89.20 |  |  |  | 0.00 |  | 4.83 | [8 empty] | 6.05 |  |  |  |  | 0.42
2020 |  |  |  | 10836.45 |  |  | 8242 |  |  |  | 1335 | [10 empty] | 93.61 |  |  |  | 93.76 | [5 empty] | 92.41 |  |  | 93.83 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 6.18 |  |  |  |  | 0.15
2021 |  |  |  | 10779.48 |  |  | 8360 |  |  |  | 1335 | [10 empty] | 94.85 |  |  |  | 95.37 | [5 empty] | 92.17 |  |  | 95.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.63 |  |  |  |  | 0.51
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1988 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 42
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 399 | [14 empty] | 477
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 3
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 4
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 399 | [14 empty] | 484 |  |  |  | 46 | [11 empty] | 0
Total | [22 empty] | 399 | [14 empty] | 530
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1988 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 12
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 8
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 42

## GROHNDE
2021 Operating Experience
DE-27 | [8 empty] | GROHNDE | [26 empty] | GERMANY
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | PElektra (PreussenElektra GmbH)
Owner | [7 empty] | : | PEL/SBi (1. (83,3%) PreussenElektra GmbH 2. (16,7%) Stadtwerke Bielefeld)
Reactor Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / PWR | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-06-01
Thermal power | [12 empty] | : |  |  | 3900 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-09-05
Gross electrical power | [12 empty] | : |  |  | 1430 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-02-01
Reference unit power (net) | [12 empty] | : |  |  | 1360 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325.3
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.53
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 75 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 34000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.6 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 3.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 21.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 10492.41 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.08 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.41 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.07 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.49 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.44 %
Load Factor (LF) | [18 empty] | : | 88.07 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.08 %
Operating Factor (OF) | [18 empty] | : | 92.71 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 639 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 956.46 | 881.78 |  |  |  | 601.68 |  | 470.14 | [8 empty] | 949.01 |  |  | 913.61 | [6 empty] | 956.59 |  | 949.98 |  |  |  | 935.16 |  |  | 952.08 |  |  | 942.51 | [9 empty] | 983.42 |  |  | 10492.41
EAF [%] |  |  |  |  | 99.90 | 99.38 |  |  |  | 60.67 |  | 49.07 | [8 empty] | 96.66 |  |  | 94.39 | [6 empty] | 95.62 |  | 95.33 |  |  |  | 96.42 |  |  | 98.08 |  |  | 99.71 | [9 empty] | 99.79 |  |  | 90.41
UCF [%] |  |  |  |  | 99.90 | 99.84 |  |  |  | 61.08 |  | 49.77 | [8 empty] | 100.00 |  |  | 99.63 | [6 empty] | 99.97 |  | 100.00 |  |  |  | 99.96 |  |  | 99.96 |  |  | 99.71 | [9 empty] | 100.00 |  |  | 92.49
LF [%] |  |  |  |  | 94.53 | 96.48 |  |  |  | 59.54 |  | 48.01 | [8 empty] | 93.79 |  |  | 93.30 | [6 empty] | 94.54 |  | 93.89 |  |  |  | 95.50 |  |  | 93.97 |  |  | 96.25 | [9 empty] | 97.19 |  |  | 88.07
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 61.64 |  | 50.83 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.71
FLR [%] |  |  |  |  | 0.08 | 0.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.37 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.29 | [9 empty] | 0.00 |  |  | 0.08
UCL [%] |  |  |  |  | 0.08 | 0.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.37 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.29 | [9 empty] | 0.00 |  |  | 0.07
PUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 38.92 |  | 50.23 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.00 |  |  |  | 0.04 |  |  | 0.04 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.44
XUF [%] |  |  |  |  | 0.00 | 0.46 |  |  |  | 0.41 |  | 0.70 | [8 empty] | 3.34 |  |  | 5.24 | [6 empty] | 4.35 |  | 4.67 |  |  |  | 3.54 |  |  | 1.88 |  |  | 0.00 | [9 empty] | 0.21 |  |  | 2.08
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 386844.34 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.91 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.36 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.88 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.76 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.42 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.6 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.63 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 10871.05 |  |  | 8406 |  |  |  | 1300 | [10 empty] | 95.17 |  |  |  | 95.17 | [5 empty] | 94.97 |  |  | 95.58 |  |  |  | 4.60 |  | 4.59 | [8 empty] | 0.24 |  |  |  |  | 0.00
1986 |  |  |  | 10205.37 |  |  | 8120 |  |  |  | 1300 | [10 empty] | 89.70 |  |  |  | 89.70 | [5 empty] | 89.62 |  |  | 92.69 |  |  |  | 0.47 |  | 0.43 | [8 empty] | 9.87 |  |  |  |  | 0.00
1987 |  |  |  | 9648.48 |  |  | 7979 |  |  |  | 1300 | [10 empty] | 86.44 |  |  |  | 86.44 | [5 empty] | 84.72 |  |  | 91.08 |  |  |  | 0.51 |  | 0.44 | [8 empty] | 13.12 |  |  |  |  | 0.00
1988 |  |  |  | 10208.28 |  |  | 8104 |  |  |  | 1300 | [10 empty] | 90.83 |  |  |  | 90.83 | [5 empty] | 89.40 |  |  | 92.26 |  |  |  | 0.63 |  | 0.57 | [8 empty] | 8.60 |  |  |  |  | 0.00
1989 |  |  |  | 10279.44 |  |  | 8058 |  |  |  | 1300 | [10 empty] | 90.32 |  |  |  | 90.32 | [5 empty] | 90.27 |  |  | 91.99 |  |  |  | 0.94 |  | 0.86 | [8 empty] | 8.82 |  |  |  |  | 0.00
1990 |  |  |  | 10123.56 |  |  | 7872 |  |  |  | 1314 | [10 empty] | 88.13 |  |  |  | 88.13 | [5 empty] | 87.91 |  |  | 89.86 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 11.85 |  |  |  |  | 0.00
1991 |  |  |  | 9957.76 |  |  | 7603 |  |  |  | 1325 | [10 empty] | 86.43 |  |  |  | 86.43 | [5 empty] | 85.79 |  |  | 86.79 |  |  |  | 6.52 |  | 6.03 | [8 empty] | 7.54 |  |  |  |  | 0.00
1992 |  |  |  | 10424.29 |  |  | 7981 |  |  |  | 1325 | [10 empty] | 89.96 |  |  |  | 89.96 | [5 empty] | 89.56 |  |  | 90.86 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 9.91 |  |  |  |  | 0.00
1993 |  |  |  | 10680.11 |  |  | 8147 |  |  |  | 1325 | [10 empty] | 92.84 |  |  |  | 92.84 | [5 empty] | 92.01 |  |  | 93.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 7.15 |  |  |  |  | 0.00
1994 |  |  |  | 10266.46 |  |  | 8063 |  |  |  | 1325 | [10 empty] | 91.91 |  |  |  | 91.91 | [5 empty] | 88.45 |  |  | 92.04 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.09 |  |  |  |  | 0.00
1995 |  |  |  | 10771.16 |  |  | 7986 |  |  |  | 1349 | [10 empty] | 91.10 |  |  |  | 91.10 | [5 empty] | 91.12 |  |  | 91.16 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 8.83 |  |  |  |  | 0.00
1996 |  |  |  | 10589.85 |  |  | 7861 |  |  |  | 1360 | [10 empty] | 88.87 |  |  |  | 88.87 | [5 empty] | 88.65 |  |  | 89.49 |  |  |  | 1.23 |  | 1.10 | [8 empty] | 10.02 |  |  |  |  | 0.00
1997 |  |  |  | 11864.65 |  |  | 8760 |  |  |  | 1360 | [10 empty] | 99.96 |  |  |  | 99.96 | [5 empty] | 99.59 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.03 |  |  |  |  | 0.00
1998 |  |  |  | 11146.31 |  |  | 8301 |  |  |  | 1360 | [10 empty] | 94.52 |  |  |  | 94.52 | [5 empty] | 93.56 |  |  | 94.76 |  |  |  | 0.81 |  | 0.77 | [8 empty] | 4.71 |  |  |  |  | 0.00
1999 |  |  |  | 11212.15 |  |  | 8351 |  |  |  | 1360 | [10 empty] | 95.28 |  |  |  | 95.28 | [5 empty] | 94.11 |  |  | 95.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.72 |  |  |  |  | 0.00
2000 |  |  |  | 11055.88 |  |  | 8250 |  |  |  | 1360 | [10 empty] | 93.72 |  |  |  | 93.72 | [5 empty] | 92.55 |  |  | 93.92 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 6.17 |  |  |  |  | 0.00
2001 |  |  |  | 10926.65 |  |  | 8310 |  |  |  | 1360 | [10 empty] | 94.18 |  |  |  | 94.72 | [5 empty] | 91.72 |  |  | 94.86 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 5.22 |  |  |  |  | 0.54
2002 |  |  |  | 10791.89 |  |  | 8233 |  |  |  | 1360 | [10 empty] | 93.82 |  |  |  | 93.82 | [5 empty] | 90.58 |  |  | 93.98 |  |  |  | 1.90 |  | 1.81 | [8 empty] | 4.37 |  |  |  |  | 0.00
2003 |  |  |  | 10933.04 |  |  | 8343 |  |  |  | 1360 | [10 empty] | 95.00 |  |  |  | 95.00 | [5 empty] | 91.77 |  |  | 95.24 |  |  |  | 0.09 |  | 1.65 | [8 empty] | 3.35 |  |  |  |  | 0.00
2004 |  |  |  | 10695.42 |  |  | 8245 |  |  |  | 1360 | [10 empty] | 93.59 |  |  |  | 93.59 | [5 empty] | 89.53 |  |  | 93.86 |  |  |  | 0.97 |  | 0.92 | [8 empty] | 5.49 |  |  |  |  | 0.00
2005 |  |  |  | 10840.95 |  |  | 8364 |  |  |  | 1360 | [10 empty] | 94.49 |  |  |  | 95.15 | [5 empty] | 91.00 |  |  | 95.48 |  |  |  | 0.50 |  | 0.98 | [8 empty] | 3.87 |  |  |  |  | 0.66
2006 |  |  |  | 10995.69 |  |  | 8296 |  |  |  | 1360 | [10 empty] | 94.24 |  |  |  | 94.55 | [5 empty] | 92.30 |  |  | 94.70 |  |  |  | 0.01 |  | 0.88 | [8 empty] | 4.57 |  |  |  |  | 0.31
2007 |  |  |  | 10818.40 |  |  | 8270 |  |  |  | 1360 | [10 empty] | 93.63 |  |  |  | 94.07 | [5 empty] | 90.80 |  |  | 94.40 |  |  |  | 0.20 |  | 2.03 | [8 empty] | 3.91 |  |  |  |  | 0.43
2008 |  |  |  | 10545.95 |  |  | 8048 |  |  |  | 1360 | [10 empty] | 91.05 |  |  |  | 91.32 | [5 empty] | 88.28 |  |  | 91.62 |  |  |  | 0.11 |  | 1.23 | [8 empty] | 7.45 |  |  |  |  | 0.27
2009 |  |  |  | 10867.47 |  |  | 8288 |  |  |  | 1360 | [10 empty] | 92.00 |  |  |  | 94.36 | [5 empty] | 91.22 |  |  | 94.61 |  |  |  | 0.06 |  | 1.14 | [8 empty] | 4.50 |  |  |  |  | 2.36
2010 |  |  |  | 10782.44 |  |  | 8267 |  |  |  | 1360 | [10 empty] | 91.99 |  |  |  | 94.08 | [5 empty] | 90.51 |  |  | 94.37 |  |  |  | 0.17 |  | 1.12 | [8 empty] | 4.79 |  |  |  |  | 2.10
2011 |  |  |  | 9603.19 |  |  | 7341 |  |  |  | 1360 | [10 empty] | 81.91 |  |  |  | 83.40 | [5 empty] | 80.61 |  |  | 83.80 |  |  |  | 0.98 |  | 5.25 | [8 empty] | 11.36 |  |  |  |  | 1.49
2012 |  |  |  | 11008.61 |  |  | 8374 |  |  |  | 1360 | [10 empty] | 94.92 |  |  |  | 95.11 | [5 empty] | 92.15 |  |  | 95.33 |  |  |  | 0.10 |  | 0.49 | [8 empty] | 4.40 |  |  |  |  | 0.19
2013 |  |  |  | 10420.06 |  |  | 7847 |  |  |  | 1360 | [10 empty] | 89.39 |  |  |  | 89.39 | [5 empty] | 87.46 |  |  | 89.58 |  |  |  | 0.03 |  | 1.62 | [8 empty] | 9.00 |  |  |  |  | 0.00
2014 |  |  |  | 9481.18 |  |  | 7326 |  |  |  | 1360 | [10 empty] | 82.96 |  |  |  | 83.43 | [5 empty] | 79.58 |  |  | 83.63 |  |  |  | 1.28 |  | 12.37 | [8 empty] | 4.19 |  |  |  |  | 0.47
2015 |  |  |  | 9864.56 |  |  | 7792 |  |  |  | 1360 | [10 empty] | 86.32 |  |  |  | 88.43 | [5 empty] | 82.80 |  |  | 88.95 |  |  |  | 0.05 |  | 1.04 | [8 empty] | 10.53 |  |  |  |  | 2.12
2016 |  |  |  | 8415.91 |  |  | 6597 |  |  |  | 1360 | [10 empty] | 71.96 |  |  |  | 73.08 | [5 empty] | 70.45 |  |  | 75.10 |  |  |  | 7.85 |  | 22.31 | [8 empty] | 4.61 |  |  |  |  | 1.12
2017 |  |  |  | 9133.02 |  |  | 7540 |  |  |  | 1360 | [10 empty] | 78.68 |  |  |  | 82.15 | [5 empty] | 76.66 |  |  | 86.07 |  |  |  | 3.74 |  | 5.08 | [8 empty] | 12.77 |  |  |  |  | 3.47
2018 |  |  |  | 10339.24 |  |  | 8131 |  |  |  | 1360 | [10 empty] | 91.61 |  |  |  | 91.61 | [5 empty] | 86.79 |  |  | 92.82 |  |  |  | 0.38 |  | 1.92 | [8 empty] | 6.47 |  |  |  |  | 0.00
2019 |  |  |  | 10113.33 |  |  | 7889 |  |  |  | 1360 | [10 empty] | 87.65 |  |  |  | 89.82 | [5 empty] | 84.89 |  |  | 90.06 |  |  |  | 0.10 |  | 3.01 | [8 empty] | 7.16 |  |  |  |  | 2.18
2020 |  |  |  | 9909.60 |  |  | 7774 |  |  |  | 1360 | [10 empty] | 85.92 |  |  |  | 88.14 | [5 empty] | 82.95 |  |  | 88.50 |  |  |  | 0.24 |  | 6.76 | [8 empty] | 5.10 |  |  |  |  | 2.22
2021 |  |  |  | 10492.41 |  |  | 8121 |  |  |  | 1360 | [10 empty] | 90.41 |  |  |  | 92.49 | [5 empty] | 88.07 |  |  | 92.71 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 7.44 |  |  |  |  | 2.08
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1985 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 154
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 640 | [14 empty] | 495 |  |  |  | 3
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 11
L. |  | Human factor related | [39 empty] | 18
M. |  | Governmental requirements or court decisions | [51 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 10
Z. |  | Other | [39 empty] | 7
Subtotal | [22 empty] | 640 | [14 empty] | 516 |  |  |  | 182 | [11 empty] | 1
Total | [22 empty] | 640 | [14 empty] | 699
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1985 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 12
12. |  |  | Reactor I&C Systems | [34 empty] | 3
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 40
15. |  |  | Reactor Cooling Systems | [34 empty] | 35
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 46
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 154

## GUNDREMMINGEN-C
2021 Operating Experience
DE-28 | [8 empty] | GUNDREMMINGEN-C | [26 empty] | GERMANY
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | KGG (Kernkraftwerk Gundremmingen GmbH)
Owner | [7 empty] | : | RWE/PEL (1. (75%) RWE Power AG 2. (25%) PreussenElektra GmbH)
Reactor Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-72 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-07-20
Thermal power | [12 empty] | : |  |  | 3840 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-11-02
Gross electrical power | [12 empty] | : |  |  | 1344 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-01-18
Reference unit power (net) | [12 empty] | : |  |  | 1288 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.42
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 27500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 4.818 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.58
| Active core height/length [m] | [13 empty] | : |  |  | 3.71 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 784 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 193 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 10855.38 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.44 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.75 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.25 %
Load Factor (LF) | [18 empty] | : | 96.21 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.31 %
Operating Factor (OF) | [18 empty] | : | 99.95 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 957.71 | 865.53 |  |  |  | 956.14 |  | 924.91 | [8 empty] | 951.24 |  |  | 886.88 | [6 empty] | 934.52 |  | 937.03 |  |  |  | 903.66 |  |  | 936.33 |  |  | 848.49 | [9 empty] | 752.95 |  |  | 10855.38
EAF [%] |  |  |  |  | 99.53 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 98.02 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.37 |  |  | 98.71 |  |  | 92.71 | [9 empty] | 81.14 |  |  | 97.44
UCF [%] |  |  |  |  | 99.53 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 98.02 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.37 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.75
LF [%] |  |  |  |  | 99.94 | 100.00 |  |  |  | 99.91 |  | 99.74 | [8 empty] | 99.27 |  |  | 95.64 | [6 empty] | 97.52 |  | 97.78 |  |  |  | 97.44 |  |  | 97.58 |  |  | 91.50 | [9 empty] | 78.57 |  |  | 96.21
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.46 |  |  | 99.95
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.47 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.98 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.63 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.25
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 1.29 |  |  | 7.29 | [9 empty] | 18.86 |  |  | 2.31
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 344657.75 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.21 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.46 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.72 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.82 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.89 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.51 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.29 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 9149.56 |  |  | 7663 |  |  |  | 1244 | [10 empty] | 91.07 |  |  |  | 91.07 | [5 empty] | 89.78 |  |  | 93.25 |  |  |  | 8.02 |  | 7.94 | [8 empty] | 0.99 |  |  |  |  | 0.00
1986 |  |  |  | 8018.53 |  |  | 7945 |  |  |  | 1244 | [10 empty] | 84.68 |  |  |  | 84.68 | [5 empty] | 73.58 |  |  | 90.70 |  |  |  | 0.38 |  | 0.32 | [8 empty] | 15.00 |  |  |  |  | 0.00
1987 |  |  |  | 7333.18 |  |  | 7345 |  |  |  | 1248 | [10 empty] | 74.68 |  |  |  | 74.68 | [5 empty] | 67.08 |  |  | 83.85 |  |  |  | 7.43 |  | 5.99 | [8 empty] | 19.33 |  |  |  |  | 0.00
1988 |  |  |  | 7456.14 |  |  | 7887 |  |  |  | 1248 | [10 empty] | 88.28 |  |  |  | 88.28 | [5 empty] | 68.02 |  |  | 89.79 |  |  |  | 0.65 |  | 0.58 | [8 empty] | 11.14 |  |  |  |  | 0.00
1989 |  |  |  | 7884.50 |  |  | 7722 |  |  |  | 1248 | [10 empty] | 84.21 |  |  |  | 84.21 | [5 empty] | 72.12 |  |  | 88.15 |  |  |  | 0.14 |  | 0.12 | [8 empty] | 15.66 |  |  |  |  | 0.00
1990 |  |  |  | 8264.75 |  |  | 7519 |  |  |  | 1248 | [10 empty] | 80.23 |  |  |  | 80.23 | [5 empty] | 75.60 |  |  | 85.83 |  |  |  | 2.02 |  | 1.65 | [8 empty] | 18.12 |  |  |  |  | 0.00
1991 |  |  |  | 8341.34 |  |  | 7709 |  |  |  | 1248 | [10 empty] | 85.88 |  |  |  | 85.88 | [5 empty] | 76.30 |  |  | 88.00 |  |  |  | 1.39 |  | 1.21 | [8 empty] | 12.91 |  |  |  |  | 0.00
1992 |  |  |  | 9381.03 |  |  | 8784 |  |  |  | 1248 | [10 empty] | 98.92 |  |  |  | 98.92 | [5 empty] | 85.57 |  |  | 100.00 |  |  |  | 0.19 |  | 0.19 | [8 empty] | 0.89 |  |  |  |  | 0.00
1993 |  |  |  | 6689.16 |  |  | 7051 |  |  |  | 1248 | [10 empty] | 79.10 |  |  |  | 79.10 | [5 empty] | 61.19 |  |  | 80.49 |  |  |  | 0.12 |  | 0.09 | [8 empty] | 20.80 |  |  |  |  | 0.00
1994 |  |  |  | 7501.99 |  |  | 7147 |  |  |  | 1248 | [10 empty] | 80.67 |  |  |  | 81.11 | [5 empty] | 68.62 |  |  | 81.59 |  |  |  | 0.23 |  | 0.19 | [8 empty] | 18.70 |  |  |  |  | 0.44
1995 |  |  |  | 9376.72 |  |  | 7929 |  |  |  | 1288 | [10 empty] | 89.31 |  |  |  | 89.31 | [5 empty] | 83.11 |  |  | 90.51 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 10.51 |  |  |  |  | 0.00
1996 |  |  |  | 9508.99 |  |  | 8176 |  |  |  | 1288 | [10 empty] | 91.66 |  |  |  | 91.66 | [5 empty] | 84.05 |  |  | 93.08 |  |  |  | 0.54 |  | 0.49 | [8 empty] | 7.85 |  |  |  |  | 0.00
1997 |  |  |  | 9013.63 |  |  | 7861 |  |  |  | 1288 | [10 empty] | 88.68 |  |  |  | 89.10 | [5 empty] | 79.89 |  |  | 89.74 |  |  |  | 0.74 |  | 0.67 | [8 empty] | 10.23 |  |  |  |  | 0.42
1998 |  |  |  | 9629.47 |  |  | 8153 |  |  |  | 1288 | [10 empty] | 91.53 |  |  |  | 91.53 | [5 empty] | 85.35 |  |  | 93.07 |  |  |  | 0.80 |  | 0.74 | [8 empty] | 7.73 |  |  |  |  | 0.00
1999 |  |  |  | 8187.60 |  |  | 6942 |  |  |  | 1288 | [10 empty] | 77.04 |  |  |  | 77.04 | [5 empty] | 72.57 |  |  | 79.25 |  |  |  | 15.76 |  | 14.42 | [8 empty] | 8.55 |  |  |  |  | 0.00
2000 |  |  |  | 10176.83 |  |  | 8375 |  |  |  | 1288 | [10 empty] | 94.57 |  |  |  | 94.57 | [5 empty] | 89.95 |  |  | 95.34 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 5.35 |  |  |  |  | 0.00
2001 |  |  |  | 9838.39 |  |  | 8016 |  |  |  | 1288 | [10 empty] | 87.21 |  |  |  | 90.66 | [5 empty] | 87.20 |  |  | 91.51 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 9.17 |  |  |  |  | 3.45
2002 |  |  |  | 10335.84 |  |  | 8301 |  |  |  | 1288 | [10 empty] | 93.43 |  |  |  | 93.43 | [5 empty] | 91.61 |  |  | 94.76 |  |  |  | 1.50 |  | 1.43 | [8 empty] | 5.14 |  |  |  |  | 0.00
2003 |  |  |  | 9965.59 |  |  | 7931 |  |  |  | 1288 | [10 empty] | 89.16 |  |  |  | 89.16 | [5 empty] | 88.32 |  |  | 90.54 |  |  |  | 1.29 |  | 1.17 | [8 empty] | 9.67 |  |  |  |  | 0.00
2004 |  |  |  | 8470.48 |  |  | 6747 |  |  |  | 1288 | [10 empty] | 74.87 |  |  |  | 74.87 | [5 empty] | 74.87 |  |  | 76.81 |  |  |  | 20.75 |  | 19.60 | [8 empty] | 5.52 |  |  |  |  | 0.00
2005 |  |  |  | 10015.64 |  |  | 8158 |  |  |  | 1288 | [10 empty] | 89.22 |  |  |  | 92.56 | [5 empty] | 88.77 |  |  | 93.13 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 7.40 |  |  |  |  | 3.34
2006 |  |  |  | 10542.96 |  |  | 8289 |  |  |  | 1288 | [10 empty] | 93.74 |  |  |  | 93.94 | [5 empty] | 93.44 |  |  | 94.62 |  |  |  | 0.18 |  | 0.17 | [8 empty] | 5.89 |  |  |  |  | 0.19
2007 |  |  |  | 9888.31 |  |  | 7729 |  |  |  | 1288 | [10 empty] | 87.36 |  |  |  | 87.40 | [5 empty] | 87.64 |  |  | 88.23 |  |  |  | 2.95 |  | 2.66 | [8 empty] | 9.94 |  |  |  |  | 0.04
2008 |  |  |  | 9928.98 |  |  | 7737 |  |  |  | 1288 | [10 empty] | 87.34 |  |  |  | 87.49 | [5 empty] | 87.76 |  |  | 88.08 |  |  |  | 0.14 |  | 1.60 | [8 empty] | 10.91 |  |  |  |  | 0.15
2009 |  |  |  | 10275.18 |  |  | 8036 |  |  |  | 1288 | [10 empty] | 90.88 |  |  |  | 91.13 | [5 empty] | 91.07 |  |  | 91.74 |  |  |  | 0.34 |  | 1.46 | [8 empty] | 7.41 |  |  |  |  | 0.26
2010 |  |  |  | 10394.76 |  |  | 8125 |  |  |  | 1288 | [10 empty] | 91.74 |  |  |  | 92.10 | [5 empty] | 92.13 |  |  | 92.75 |  |  |  | 0.15 |  | 0.73 | [8 empty] | 7.17 |  |  |  |  | 0.35
2011 |  |  |  | 9454.97 |  |  | 7412 |  |  |  | 1288 | [10 empty] | 84.08 |  |  |  | 84.08 | [5 empty] | 83.80 |  |  | 84.61 |  |  |  | 4.24 |  | 5.38 | [8 empty] | 10.54 |  |  |  |  | 0.00
2012 |  |  |  | 10099.09 |  |  | 8057 |  |  |  | 1288 | [10 empty] | 91.07 |  |  |  | 91.07 | [5 empty] | 89.26 |  |  | 91.72 |  |  |  | 2.55 |  | 2.38 | [8 empty] | 6.55 |  |  |  |  | 0.00
2013 |  |  |  | 10015.72 |  |  | 7850 |  |  |  | 1288 | [10 empty] | 89.19 |  |  |  | 89.19 | [5 empty] | 88.77 |  |  | 89.61 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 10.74 |  |  |  |  | 0.00
2014 |  |  |  | 10031.13 |  |  | 7921 |  |  |  | 1288 | [10 empty] | 89.44 |  |  |  | 89.44 | [5 empty] | 88.91 |  |  | 90.42 |  |  |  | 3.34 |  | 4.06 | [8 empty] | 6.49 |  |  |  |  | 0.00
2015 |  |  |  | 9841.63 |  |  | 7900 |  |  |  | 1288 | [10 empty] | 89.49 |  |  |  | 89.49 | [5 empty] | 87.23 |  |  | 90.18 |  |  |  | 0.46 |  | 0.99 | [8 empty] | 9.52 |  |  |  |  | 0.00
2016 |  |  |  | 8918.29 |  |  | 7553 |  |  |  | 1288 | [10 empty] | 79.61 |  |  |  | 85.46 | [5 empty] | 78.83 |  |  | 85.99 |  |  |  | 0.05 |  | 1.41 | [8 empty] | 13.14 |  |  |  |  | 5.84
2017 |  |  |  | 9462.05 |  |  | 7696 |  |  |  | 1288 | [10 empty] | 85.93 |  |  |  | 85.93 | [5 empty] | 83.86 |  |  | 87.85 |  |  |  | 2.36 |  | 2.90 | [8 empty] | 11.18 |  |  |  |  | 0.00
2018 |  |  |  | 9874.20 |  |  | 7920 |  |  |  | 1288 | [10 empty] | 88.56 |  |  |  | 89.85 | [5 empty] | 87.51 |  |  | 90.41 |  |  |  | 0.00 |  | 2.26 | [8 empty] | 7.89 |  |  |  |  | 1.29
2019 |  |  |  | 9900.24 |  |  | 7809 |  |  |  | 1288 | [10 empty] | 88.41 |  |  |  | 88.54 | [5 empty] | 87.75 |  |  | 89.14 |  |  |  | 0.87 |  | 0.77 | [8 empty] | 10.69 |  |  |  |  | 0.13
2020 |  |  |  | 8710.13 |  |  | 6972 |  |  |  | 1288 | [10 empty] | 77.53 |  |  |  | 78.05 | [5 empty] | 76.99 |  |  | 79.37 |  |  |  | 6.45 |  | 7.20 | [8 empty] | 14.75 |  |  |  |  | 0.52
2021 |  |  |  | 10855.38 |  |  | 8756 |  |  |  | 1288 | [10 empty] | 97.44 |  |  |  | 99.75 | [5 empty] | 96.21 |  |  | 99.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.25 |  |  |  |  | 2.31
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1985 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 178
B. |  | Refuelling without maintenance | [35 empty] | 21
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 717
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 14
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 1
L. |  | Human factor related | [39 empty] | 4
M. |  | Governmental requirements or court decisions | [31 empty] | 10 | [19 empty] | 0
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 13
Subtotal | [33 empty] | 10 |  |  |  | 766 |  |  |  | 183 | [11 empty] | 0
Total | [22 empty] | 10 | [14 empty] | 949
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1985 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 40
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
14. |  |  | Safety Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 22
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 74
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 178

## ISAR-2
2021 Operating Experience
DE-31 | [8 empty] | ISAR-2 | [26 empty] | GERMANY
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PElektra (PreussenElektra GmbH)
Owner | [7 empty] | : | PEL/SwM (1. (75%) PreussenElektra GmbH 2. (25%) Stadtwerke München)
Reactor Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / Konvoi | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-09-15
Thermal power | [12 empty] | : |  |  | 3950 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-01-22
Gross electrical power | [12 empty] | : |  |  | 1485 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-04-09
Reference unit power (net) | [12 empty] | : |  |  | 1410 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 32000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.6 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 35
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 11421.16 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.1 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.62 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.43 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.62 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.95 %
Load Factor (LF) | [18 empty] | : | 92.47 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 94.79 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 456 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1051.39 | 946.19 |  |  |  | 1024.83 |  | 993.25 | [8 empty] | 1005.17 |  |  | 940.08 | [6 empty] | 1000.71 |  | 1014.06 |  |  |  | 785.41 |  |  | 597.05 |  |  | 1016.74 | [9 empty] | 1046.29 |  |  | 11421.16
EAF [%] |  |  |  |  | 99.98 | 100.00 |  |  |  | 100.00 |  | 99.98 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.97 |  | 100.00 |  |  |  | 79.16 |  |  | 56.97 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 94.62
UCF [%] |  |  |  |  | 99.98 | 100.00 |  |  |  | 100.00 |  | 99.98 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.97 |  | 100.00 |  |  |  | 79.16 |  |  | 56.97 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 94.62
LF [%] |  |  |  |  | 100.22 | 99.86 |  |  |  | 97.82 |  | 97.84 | [8 empty] | 95.82 |  |  | 92.60 | [6 empty] | 95.39 |  | 96.67 |  |  |  | 77.36 |  |  | 56.84 |  |  | 100.15 | [9 empty] | 99.74 |  |  | 92.47
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 80.00 |  |  | 58.12 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.79
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 1.89 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.10
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 5.04 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.43
PUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.00 |  | 0.02 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.02 |  | 0.00 |  |  |  | 20.84 |  |  | 37.99 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 4.95
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 368247.21 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.87 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.38 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.69 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.02 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.7 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.31 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 93.33 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 6023.00 |  |  | 6177 |  |  |  | 1323 | [10 empty] | 95.09 |  |  |  | 95.09 | [5 empty] | 69.65 |  |  | 93.58 |  |  |  | 4.81 |  | 4.81 | [8 empty] | 0.11 |  |  |  |  | 0.00
1989 |  |  |  | 7728.92 |  |  | 6876 |  |  |  | 1310 | [10 empty] | 73.41 |  |  |  | 73.41 | [5 empty] | 67.35 |  |  | 78.49 |  |  |  | 12.96 |  | 10.93 | [8 empty] | 15.65 |  |  |  |  | 0.00
1990 |  |  |  | 9271.36 |  |  | 7915 |  |  |  | 1310 | [10 empty] | 84.94 |  |  |  | 84.94 | [5 empty] | 80.79 |  |  | 90.35 |  |  |  | 0.58 |  | 0.49 | [8 empty] | 14.57 |  |  |  |  | 0.00
1991 |  |  |  | 9699.19 |  |  | 7732 |  |  |  | 1318 | [10 empty] | 87.78 |  |  |  | 87.78 | [5 empty] | 83.98 |  |  | 88.26 |  |  |  | 1.54 |  | 1.38 | [8 empty] | 10.84 |  |  |  |  | 0.00
1992 |  |  |  | 9843.49 |  |  | 7917 |  |  |  | 1320 | [10 empty] | 89.93 |  |  |  | 89.93 | [5 empty] | 84.90 |  |  | 90.13 |  |  |  | 0.36 |  | 0.32 | [8 empty] | 9.75 |  |  |  |  | 0.00
1993 |  |  |  | 10192.97 |  |  | 8052 |  |  |  | 1330 | [10 empty] | 88.08 |  |  |  | 91.26 | [5 empty] | 87.49 |  |  | 91.92 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 8.71 |  |  |  |  | 3.18
1994 |  |  |  | 10499.86 |  |  | 8209 |  |  |  | 1330 | [10 empty] | 93.14 |  |  |  | 93.14 | [5 empty] | 90.12 |  |  | 93.71 |  |  |  | 1.00 |  | 0.94 | [8 empty] | 5.92 |  |  |  |  | 0.00
1995 |  |  |  | 10040.31 |  |  | 7891 |  |  |  | 1332 | [10 empty] | 89.85 |  |  |  | 89.85 | [5 empty] | 86.01 |  |  | 90.08 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 9.99 |  |  |  |  | 0.00
1996 |  |  |  | 10265.10 |  |  | 7989 |  |  |  | 1338 | [10 empty] | 88.52 |  |  |  | 90.65 | [5 empty] | 87.29 |  |  | 90.95 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 9.27 |  |  |  |  | 2.13
1997 |  |  |  | 10906.39 |  |  | 8258 |  |  |  | 1365 | [10 empty] | 94.10 |  |  |  | 94.10 | [5 empty] | 91.21 |  |  | 94.27 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 5.88 |  |  |  |  | 0.00
1998 |  |  |  | 10758.10 |  |  | 8356 |  |  |  | 1365 | [10 empty] | 93.60 |  |  |  | 93.61 | [5 empty] | 89.97 |  |  | 95.39 |  |  |  | 1.65 |  | 1.57 | [8 empty] | 4.82 |  |  |  |  | 0.01
1999 |  |  |  | 11610.87 |  |  | 8465 |  |  |  | 1380 | [10 empty] | 96.51 |  |  |  | 96.51 | [5 empty] | 96.05 |  |  | 96.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.49 |  |  |  |  | 0.00
2000 |  |  |  | 11291.15 |  |  | 8311 |  |  |  | 1400 | [10 empty] | 94.50 |  |  |  | 94.50 | [5 empty] | 91.82 |  |  | 94.62 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 5.46 |  |  |  |  | 0.00
2001 |  |  |  | 11731.31 |  |  | 8506 |  |  |  | 1400 | [10 empty] | 97.14 |  |  |  | 97.14 | [5 empty] | 95.66 |  |  | 97.10 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 2.84 |  |  |  |  | 0.00
2002 |  |  |  | 11512.23 |  |  | 8350 |  |  |  | 1400 | [10 empty] | 95.10 |  |  |  | 95.10 | [5 empty] | 93.87 |  |  | 95.32 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 4.84 |  |  |  |  | 0.00
2003 |  |  |  | 11671.59 |  |  | 8491 |  |  |  | 1400 | [10 empty] | 95.93 |  |  |  | 96.67 | [5 empty] | 95.17 |  |  | 96.93 |  |  |  | 0.29 |  | 0.28 | [8 empty] | 3.05 |  |  |  |  | 0.75
2004 |  |  |  | 11595.28 |  |  | 8395 |  |  |  | 1400 | [10 empty] | 95.39 |  |  |  | 95.39 | [5 empty] | 94.29 |  |  | 95.57 |  |  |  | 0.05 |  | 0.57 | [8 empty] | 4.05 |  |  |  |  | 0.00
2005 |  |  |  | 11102.56 |  |  | 7976 |  |  |  | 1400 | [10 empty] | 90.52 |  |  |  | 90.87 | [5 empty] | 90.53 |  |  | 91.05 |  |  |  | 0.02 |  | 2.57 | [8 empty] | 6.55 |  |  |  |  | 0.35
2006 |  |  |  | 11755.26 |  |  | 8494 |  |  |  | 1400 | [10 empty] | 96.61 |  |  |  | 96.82 | [5 empty] | 95.85 |  |  | 96.96 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 3.18 |  |  |  |  | 0.20
2007 |  |  |  | 11377.49 |  |  | 8200 |  |  |  | 1400 | [10 empty] | 93.05 |  |  |  | 93.43 | [5 empty] | 92.76 |  |  | 93.60 |  |  |  | 0.00 |  | 1.48 | [8 empty] | 5.09 |  |  |  |  | 0.38
2008 |  |  |  | 11456.15 |  |  | 8217 |  |  |  | 1400 | [10 empty] | 93.15 |  |  |  | 93.33 | [5 empty] | 93.16 |  |  | 93.55 |  |  |  | 1.10 |  | 2.36 | [8 empty] | 4.31 |  |  |  |  | 0.18
2009 |  |  |  | 11484.85 |  |  | 8277 |  |  |  | 1410 | [10 empty] | 94.32 |  |  |  | 94.32 | [5 empty] | 93.37 |  |  | 94.49 |  |  |  | 0.00 |  | 1.65 | [8 empty] | 4.03 |  |  |  |  | 0.00
2010 |  |  |  | 11375.28 |  |  | 8162 |  |  |  | 1410 | [10 empty] | 92.99 |  |  |  | 92.99 | [5 empty] | 92.10 |  |  | 93.17 |  |  |  | 0.00 |  | 1.21 | [8 empty] | 5.81 |  |  |  |  | 0.00
2011 |  |  |  | 11655.84 |  |  | 8378 |  |  |  | 1410 | [10 empty] | 95.48 |  |  |  | 95.48 | [5 empty] | 94.37 |  |  | 95.64 |  |  |  | 0.00 |  | 0.67 | [8 empty] | 3.85 |  |  |  |  | 0.00
2012 |  |  |  | 11385.03 |  |  | 8299 |  |  |  | 1410 | [10 empty] | 94.31 |  |  |  | 94.31 | [5 empty] | 91.92 |  |  | 94.48 |  |  |  | 0.00 |  | 0.37 | [8 empty] | 5.32 |  |  |  |  | 0.00
2013 |  |  |  | 11402.06 |  |  | 8400 |  |  |  | 1410 | [10 empty] | 94.29 |  |  |  | 94.31 | [5 empty] | 92.31 |  |  | 95.89 |  |  |  | 1.63 |  | 1.84 | [8 empty] | 3.85 |  |  |  |  | 0.02
2014 |  |  |  | 10794.90 |  |  | 8350 |  |  |  | 1410 | [10 empty] | 90.48 |  |  |  | 90.55 | [5 empty] | 87.40 |  |  | 95.32 |  |  |  | 4.77 |  | 4.72 | [8 empty] | 4.73 |  |  |  |  | 0.07
2015 |  |  |  | 10505.19 |  |  | 7798 |  |  |  | 1410 | [10 empty] | 88.67 |  |  |  | 88.75 | [5 empty] | 85.05 |  |  | 89.02 |  |  |  | 0.00 |  | 4.16 | [8 empty] | 7.10 |  |  |  |  | 0.08
2016 |  |  |  | 11338.88 |  |  | 8420 |  |  |  | 1410 | [10 empty] | 93.97 |  |  |  | 95.68 | [5 empty] | 91.55 |  |  | 95.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.32 |  |  |  |  | 1.71
2017 |  |  |  | 10901.56 |  |  | 8019 |  |  |  | 1410 | [10 empty] | 90.50 |  |  |  | 91.15 | [5 empty] | 88.26 |  |  | 91.54 |  |  |  | 0.50 |  | 0.71 | [8 empty] | 8.14 |  |  |  |  | 0.64
2018 |  |  |  | 11477.22 |  |  | 8363 |  |  |  | 1410 | [10 empty] | 94.85 |  |  |  | 95.24 | [5 empty] | 92.92 |  |  | 95.47 |  |  |  | 0.24 |  | 0.97 | [8 empty] | 3.79 |  |  |  |  | 0.39
2019 |  |  |  | 11384.22 |  |  | 8405 |  |  |  | 1410 | [10 empty] | 95.28 |  |  |  | 95.77 | [5 empty] | 92.17 |  |  | 95.95 |  |  |  | 0.10 |  | 0.16 | [8 empty] | 4.07 |  |  |  |  | 0.49
2020 |  |  |  | 11030.83 |  |  | 8183 |  |  |  | 1410 | [10 empty] | 92.99 |  |  |  | 92.99 | [5 empty] | 89.06 |  |  | 93.16 |  |  |  | 0.10 |  | 0.18 | [8 empty] | 6.83 |  |  |  |  | 0.00
2021 |  |  |  | 11421.16 |  |  | 8304 |  |  |  | 1410 | [10 empty] | 94.62 |  |  |  | 94.62 | [5 empty] | 92.47 |  |  | 94.79 |  |  |  | 0.10 |  | 0.43 | [8 empty] | 4.95 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1988 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 29 | [14 empty] | 66
B. |  | Refuelling without maintenance | [35 empty] | 10
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 427 | [14 empty] | 474 |  |  |  | 6
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 0
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 1
L. |  | Human factor related | [39 empty] | 8
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 427 |  |  |  | 29 | [10 empty] | 484 |  |  |  | 82
Total | [22 empty] | 456 | [14 empty] | 566
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1988 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 29 | [14 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
41. |  |  | Main Generator Systems | [34 empty] | 28
42. |  |  | Electrical Power Supply Systems | [34 empty] | 0
Total | [22 empty] | 29 | [14 empty] | 65

## NECKARWESTHEIM-2
2021 Operating Experience
DE-44 | [8 empty] | NECKARWESTHEIM-2 | [26 empty] | GERMANY
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EnKK (EnBW Kernkraft GmbH)
Owner | [7 empty] | : | EnKK (EnBW Kernkraft GmbH)
Reactor Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / Konvoi | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-11-09
Thermal power | [12 empty] | : |  |  | 3850 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1989-01-03
Gross electrical power | [12 empty] | : |  |  | 1400 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-15
Reference unit power (net) | [12 empty] | : |  |  | 1310 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325.6
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.0 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 23 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.6 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.23
| Active core height/length [m] | [13 empty] | : |  |  | 3.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.4 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 10459.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.75 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.03 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.31 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.67 %
Load Factor (LF) | [18 empty] | : | 91.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.56 %
Operating Factor (OF) | [18 empty] | : | 92.26 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 678 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 979.58 | 880.81 |  |  |  | 966.31 |  | 940.06 | [8 empty] | 950.37 |  |  | 287.50 | [6 empty] | 681.56 |  | 947.48 |  |  |  | 931.26 |  |  | 973.25 |  |  | 946.92 | [9 empty] | 974.16 |  |  | 10459.26
EAF [%] |  |  |  |  | 99.94 | 99.94 |  |  |  | 99.93 |  | 99.86 | [8 empty] | 97.79 |  |  | 31.67 | [6 empty] | 72.30 |  | 99.87 |  |  |  | 99.92 |  |  | 99.86 |  |  | 99.95 | [9 empty] | 99.56 |  |  | 91.75
UCF [%] |  |  |  |  | 99.94 | 100.00 |  |  |  | 100.00 |  | 99.94 | [8 empty] | 100.00 |  |  | 35.56 | [6 empty] | 72.38 |  | 100.00 |  |  |  | 100.00 |  |  | 99.94 |  |  | 100.00 | [9 empty] | 99.62 |  |  | 92.31
LF [%] |  |  |  |  | 100.51 | 100.06 |  |  |  | 99.28 |  | 99.67 | [8 empty] | 97.51 |  |  | 30.48 | [6 empty] | 69.93 |  | 97.21 |  |  |  | 98.73 |  |  | 99.72 |  |  | 100.39 | [9 empty] | 99.95 |  |  | 91.14
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 35.56 | [6 empty] | 72.31 |  | 98.92 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.26
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.30 |  |  | 0.03
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.30 |  |  | 0.03
PUF [%] |  |  |  |  | 0.06 | 0.00 |  |  |  | 0.00 |  | 0.06 | [8 empty] | 0.00 |  |  | 64.44 | [6 empty] | 27.62 |  | 0.00 |  |  |  | 0.00 |  |  | 0.06 |  |  | 0.00 | [9 empty] | 0.09 |  |  | 7.67
XUF [%] |  |  |  |  | 0.00 | 0.06 |  |  |  | 0.07 |  | 0.08 | [8 empty] | 2.21 |  |  | 3.88 | [6 empty] | 0.08 |  | 0.13 |  |  |  | 0.08 |  |  | 0.08 |  |  | 0.05 | [9 empty] | 0.06 |  |  | 0.56
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 338983.59 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.92 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.23 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.55 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.22 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.26 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 92.79 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 8673.22 |  |  | 8205 |  |  |  | 1225 | [10 empty] | 99.76 |  |  |  | 99.76 | [5 empty] | 84.22 |  |  | 94.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.24 |  |  |  |  | 0.00
1990 |  |  |  | 9693.91 |  |  | 7958 |  |  |  | 1225 | [10 empty] | 90.21 |  |  |  | 90.21 | [5 empty] | 90.34 |  |  | 90.84 |  |  |  | 0.27 |  | 0.24 | [8 empty] | 9.55 |  |  |  |  | 0.00
1991 |  |  |  | 9434.93 |  |  | 7932 |  |  |  | 1225 | [10 empty] | 90.52 |  |  |  | 90.52 | [5 empty] | 87.92 |  |  | 90.55 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 9.35 |  |  |  |  | 0.00
1992 |  |  |  | 10204.58 |  |  | 8094 |  |  |  | 1269 | [10 empty] | 91.58 |  |  |  | 91.58 | [5 empty] | 91.55 |  |  | 92.14 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 8.35 |  |  |  |  | 0.00
1993 |  |  |  | 9912.15 |  |  | 8163 |  |  |  | 1269 | [10 empty] | 89.03 |  |  |  | 89.03 | [5 empty] | 89.17 |  |  | 93.18 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 10.93 |  |  |  |  | 0.00
1994 |  |  |  | 10320.67 |  |  | 8215 |  |  |  | 1269 | [10 empty] | 93.60 |  |  |  | 93.60 | [5 empty] | 92.84 |  |  | 93.78 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 6.26 |  |  |  |  | 0.00
1995 |  |  |  | 10532.05 |  |  | 8351 |  |  |  | 1269 | [10 empty] | 94.69 |  |  |  | 94.69 | [5 empty] | 94.74 |  |  | 95.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.31 |  |  |  |  | 0.00
1996 |  |  |  | 10614.28 |  |  | 8419 |  |  |  | 1269 | [10 empty] | 95.10 |  |  |  | 95.10 | [5 empty] | 95.22 |  |  | 95.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.90 |  |  |  |  | 0.00
1997 |  |  |  | 10111.62 |  |  | 8028 |  |  |  | 1269 | [10 empty] | 91.55 |  |  |  | 91.55 | [5 empty] | 90.96 |  |  | 91.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.45 |  |  |  |  | 0.00
1998 |  |  |  | 10610.81 |  |  | 8411 |  |  |  | 1269 | [10 empty] | 96.00 |  |  |  | 96.00 | [5 empty] | 95.45 |  |  | 96.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.00 |  |  |  |  | 0.00
1999 |  |  |  | 10460.93 |  |  | 8435 |  |  |  | 1269 | [10 empty] | 96.09 |  |  |  | 96.09 | [5 empty] | 94.10 |  |  | 96.29 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 3.87 |  |  |  |  | 0.00
2000 |  |  |  | 10473.89 |  |  | 8450 |  |  |  | 1269 | [10 empty] | 96.20 |  |  |  | 96.20 | [5 empty] | 93.96 |  |  | 96.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.80 |  |  |  |  | 0.00
2001 |  |  |  | 10423.94 |  |  | 8363 |  |  |  | 1269 | [10 empty] | 94.18 |  |  |  | 95.40 | [5 empty] | 93.77 |  |  | 95.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.60 |  |  |  |  | 1.22
2002 |  |  |  | 9787.51 |  |  | 7777 |  |  |  | 1269 | [10 empty] | 88.67 |  |  |  | 88.67 | [5 empty] | 88.05 |  |  | 88.78 |  |  |  | 6.64 |  | 6.30 | [8 empty] | 5.03 |  |  |  |  | 0.00
2003 |  |  |  | 10544.97 |  |  | 8408 |  |  |  | 1269 | [10 empty] | 95.80 |  |  |  | 95.80 | [5 empty] | 94.86 |  |  | 95.98 |  |  |  | 1.28 |  | 1.24 | [8 empty] | 2.96 |  |  |  |  | 0.00
2004 |  |  |  | 10470.68 |  |  | 8165 |  |  |  | 1269 | [10 empty] | 92.87 |  |  |  | 92.87 | [5 empty] | 93.93 |  |  | 92.95 |  |  |  | 0.00 |  | 1.02 | [8 empty] | 6.11 |  |  |  |  | 0.00
2005 |  |  |  | 10836.41 |  |  | 8371 |  |  |  | 1305 | [10 empty] | 94.81 |  |  |  | 95.38 | [5 empty] | 94.79 |  |  | 95.56 |  |  |  | 0.17 |  | 0.16 | [8 empty] | 4.47 |  |  |  |  | 0.56
2006 |  |  |  | 10877.47 |  |  | 8405 |  |  |  | 1305 | [10 empty] | 95.41 |  |  |  | 95.90 | [5 empty] | 95.15 |  |  | 95.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.10 |  |  |  |  | 0.49
2007 |  |  |  | 10411.09 |  |  | 8002 |  |  |  | 1310 | [10 empty] | 91.07 |  |  |  | 91.13 | [5 empty] | 90.72 |  |  | 91.35 |  |  |  | 1.84 |  | 1.70 | [8 empty] | 7.17 |  |  |  |  | 0.05
2008 |  |  |  | 10701.91 |  |  | 8245 |  |  |  | 1310 | [10 empty] | 93.26 |  |  |  | 93.47 | [5 empty] | 93.00 |  |  | 93.86 |  |  |  | 0.00 |  | 1.93 | [8 empty] | 4.61 |  |  |  |  | 0.20
2009 |  |  |  | 10779.73 |  |  | 8307 |  |  |  | 1310 | [10 empty] | 94.59 |  |  |  | 94.75 | [5 empty] | 93.94 |  |  | 94.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.25 |  |  |  |  | 0.16
2010 |  |  |  | 10180.15 |  |  | 7864 |  |  |  | 1310 | [10 empty] | 88.62 |  |  |  | 89.49 | [5 empty] | 88.71 |  |  | 89.77 |  |  |  | 0.13 |  | 3.23 | [8 empty] | 7.28 |  |  |  |  | 0.87
2011 |  |  |  | 10807.81 |  |  | 8319 |  |  |  | 1310 | [10 empty] | 94.95 |  |  |  | 94.96 | [5 empty] | 94.18 |  |  | 94.97 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 4.99 |  |  |  |  | 0.01
2012 |  |  |  | 10424.21 |  |  | 8098 |  |  |  | 1310 | [10 empty] | 91.83 |  |  |  | 91.83 | [5 empty] | 90.59 |  |  | 92.19 |  |  |  | 0.01 |  | 1.03 | [8 empty] | 7.15 |  |  |  |  | 0.00
2013 |  |  |  | 10218.79 |  |  | 7906 |  |  |  | 1310 | [10 empty] | 90.05 |  |  |  | 90.05 | [5 empty] | 89.05 |  |  | 90.25 |  |  |  | 4.22 |  | 3.97 | [8 empty] | 5.98 |  |  |  |  | 0.00
2014 |  |  |  | 10535.82 |  |  | 8159 |  |  |  | 1310 | [10 empty] | 92.88 |  |  |  | 92.88 | [5 empty] | 91.81 |  |  | 93.14 |  |  |  | 0.04 |  | 0.58 | [8 empty] | 6.54 |  |  |  |  | 0.00
2015 |  |  |  | 10532.84 |  |  | 8158 |  |  |  | 1310 | [10 empty] | 92.42 |  |  |  | 92.90 | [5 empty] | 91.78 |  |  | 93.13 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 6.95 |  |  |  |  | 0.49
2016 |  |  |  | 10684.13 |  |  | 8318 |  |  |  | 1310 | [10 empty] | 93.52 |  |  |  | 94.26 | [5 empty] | 92.85 |  |  | 94.69 |  |  |  | 0.17 |  | 0.16 | [8 empty] | 5.58 |  |  |  |  | 0.74
2017 |  |  |  | 9880.27 |  |  | 7791 |  |  |  | 1310 | [10 empty] | 86.97 |  |  |  | 88.60 | [5 empty] | 86.10 |  |  | 88.94 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 11.24 |  |  |  |  | 1.63
2018 |  |  |  | 9099.36 |  |  | 7121 |  |  |  | 1310 | [10 empty] | 80.54 |  |  |  | 81.00 | [5 empty] | 79.29 |  |  | 81.29 |  |  |  | 14.01 |  | 13.19 | [8 empty] | 5.81 |  |  |  |  | 0.46
2019 |  |  |  | 9758.34 |  |  | 7700 |  |  |  | 1310 | [10 empty] | 87.40 |  |  |  | 88.00 | [5 empty] | 85.04 |  |  | 87.90 |  |  |  | 0.08 |  | 4.18 | [8 empty] | 7.82 |  |  |  |  | 0.60
2020 |  |  |  | 10415.99 |  |  | 8141 |  |  |  | 1310 | [10 empty] | 92.33 |  |  |  | 92.61 | [5 empty] | 90.52 |  |  | 92.68 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 7.33 |  |  |  |  | 0.28
2021 |  |  |  | 10459.26 |  |  | 8082 |  |  |  | 1310 | [10 empty] | 91.75 |  |  |  | 92.31 | [5 empty] | 91.14 |  |  | 92.26 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 7.67 |  |  |  |  | 0.56
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1989 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 23
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 671 | [14 empty] | 524
L. |  | Human factor related | [39 empty] | 13
O. |  | Load dispatching, prioritization | [31 empty] | 8 | [19 empty] | 0
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 11
Subtotal | [22 empty] | 671 | [10 empty] | 8 |  |  |  | 524 |  |  |  | 47 | [11 empty] | 0
Total | [22 empty] | 679 | [14 empty] | 571
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1989 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 18
12. |  |  | Reactor I&C Systems | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 2
Total | [37 empty] | 34