## PAKS-1
2021 Operating Experience
HU-1 | [8 empty] | PAKS-1 | [26 empty] | HUNGARY
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAKS Zrt (PAKS NUCLEAR POWER PLANT, LTD.)
Owner | [7 empty] | : | MVM Zrt. (HUNGARIAN POWER COMPANIES LTD.)
Reactor Supplier | [7 empty] | : | AEE (ATOMENERGOEXPORT)
Turbine Supplier | [7 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-08-01
Thermal power | [12 empty] | : |  |  | 1485 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-12-28
Gross electrical power | [12 empty] | : |  |  | 509 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-08-10
Reference unit power (net) | [12 empty] | : |  |  | 479 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 297
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.6 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 37000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.2
| Active core height/length [m] | [13 empty] | : |  |  | 2.42 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 3759.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.17 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.95 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.54 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.43 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.03 %
Load Factor (LF) | [18 empty] | : | 89.59 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.48 %
Operating Factor (OF) | [18 empty] | : | 90.48 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 834 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 359.30 | 311.37 |  |  |  | 359.28 |  | 341.90 | [8 empty] | 39.58 |  |  | 338.56 | [6 empty] | 346.81 |  | 352.20 |  |  |  | 337.91 |  |  | 359.86 |  |  | 349.76 | [9 empty] | 262.90 |  |  | 3759.42
EAF [%] |  |  |  |  | 98.82 | 94.85 |  |  |  | 99.39 |  | 97.99 | [8 empty] | 12.00 |  |  | 98.17 | [6 empty] | 97.32 |  | 98.83 |  |  |  | 98.08 |  |  | 100.00 |  |  | 99.87 | [9 empty] | 73.92 |  |  | 88.95
UCF [%] |  |  |  |  | 98.82 | 94.85 |  |  |  | 99.39 |  | 97.99 | [8 empty] | 12.00 |  |  | 99.98 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 98.08 |  |  | 100.00 |  |  | 99.87 | [9 empty] | 73.92 |  |  | 89.43
LF [%] |  |  |  |  | 100.82 | 96.73 |  |  |  | 100.95 |  | 99.14 | [8 empty] | 11.11 |  |  | 98.17 | [6 empty] | 97.32 |  | 98.83 |  |  |  | 97.98 |  |  | 100.84 |  |  | 101.42 | [9 empty] | 73.77 |  |  | 89.59
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 98.33 | [8 empty] | 14.78 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 74.73 |  |  | 90.48
FLR [%] |  |  |  |  | 1.18 | 5.15 |  |  |  | 0.61 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 1.92 |  |  | 0.00 |  |  | 0.13 | [9 empty] | 26.08 |  |  | 3.17
UCL [%] |  |  |  |  | 1.18 | 5.15 |  |  |  | 0.61 |  | 0.00 | [8 empty] | 7.20 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 1.92 |  |  | 0.00 |  |  | 0.13 | [9 empty] | 26.08 |  |  | 3.54
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 2.01 | [8 empty] | 80.80 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.03
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.81 | [6 empty] | 2.68 |  | 1.17 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.48
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 131646.07 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.72 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.84 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.98 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.02 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.72 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.14 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.97 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 2299.70 |  |  | 7106 |  |  |  | 410 | [10 empty] | 91.00 |  |  |  | 91.00 | [5 empty] | 91.00 |  |  | 99.73 |  |  |  | 9.00 |  | 9.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 2595.30 |  |  | 6901 |  |  |  | 403 | [10 empty] | 75.63 |  |  |  | 75.73 | [5 empty] | 73.25 |  |  | 78.56 |  |  |  | 1.28 |  | 0.98 | [8 empty] | 23.29 |  |  |  |  | 0.10
1985 |  |  |  | 2997.30 |  |  | 7491 |  |  |  | 410 | [10 empty] | 84.15 |  |  |  | 84.15 | [5 empty] | 83.45 |  |  | 85.51 |  |  |  | 1.01 |  | 0.86 | [8 empty] | 14.99 |  |  |  |  | 0.00
1986 |  |  |  | 3114.64 |  |  | 7718 |  |  |  | 410 | [10 empty] | 87.11 |  |  |  | 87.11 | [5 empty] | 86.72 |  |  | 88.11 |  |  |  | 0.69 |  | 0.61 | [8 empty] | 12.28 |  |  |  |  | 0.00
1987 |  |  |  | 2883.09 |  |  | 7107 |  |  |  | 415 | [10 empty] | 79.20 |  |  |  | 79.20 | [5 empty] | 79.31 |  |  | 81.13 |  |  |  | 0.56 |  | 0.45 | [8 empty] | 20.35 |  |  |  |  | 0.00
1988 |  |  |  | 3076.94 |  |  | 7737 |  |  |  | 415 | [10 empty] | 85.83 |  |  |  | 85.83 | [5 empty] | 84.41 |  |  | 88.08 |  |  |  | 3.88 |  | 3.47 | [8 empty] | 10.70 |  |  |  |  | 0.00
1989 |  |  |  | 3182.18 |  |  | 7929 |  |  |  | 415 | [10 empty] | 87.68 |  |  |  | 87.68 | [5 empty] | 87.53 |  |  | 90.51 |  |  |  | 1.00 |  | 0.88 | [8 empty] | 11.44 |  |  |  |  | 0.00
1990 |  |  |  | 3216.83 |  |  | 7837 |  |  |  | 415 | [10 empty] | 87.22 |  |  |  | 87.22 | [5 empty] | 88.49 |  |  | 89.46 |  |  |  | 3.83 |  | 3.48 | [8 empty] | 9.31 |  |  |  |  | 0.00
1991 |  |  |  | 2883.91 |  |  | 6823 |  |  |  | 410 | [10 empty] | 75.08 |  |  |  | 75.08 | [5 empty] | 80.30 |  |  | 77.89 |  |  |  | 7.82 |  | 6.37 | [8 empty] | 18.55 |  |  |  |  | 0.00
1992 |  |  |  | 3498.85 |  |  | 7629 |  |  |  | 430 | [10 empty] | 84.92 |  |  |  | 84.94 | [5 empty] | 92.63 |  |  | 86.85 |  |  |  | 5.50 |  | 4.95 | [8 empty] | 10.11 |  |  |  |  | 0.02
1993 |  |  |  | 3512.43 |  |  | 7637 |  |  |  | 430 | [10 empty] | 85.80 |  |  |  | 85.80 | [5 empty] | 93.25 |  |  | 87.18 |  |  |  | 4.98 |  | 4.50 | [8 empty] | 9.70 |  |  |  |  | 0.00
1994 |  |  |  | 3441.51 |  |  | 8031 |  |  |  | 430 | [10 empty] | 89.81 |  |  |  | 89.86 | [5 empty] | 91.36 |  |  | 91.68 |  |  |  | 1.34 |  | 1.22 | [8 empty] | 8.92 |  |  |  |  | 0.05
1995 |  |  |  | 3056.32 |  |  | 7088 |  |  |  | 430 | [10 empty] | 79.54 |  |  |  | 79.64 | [5 empty] | 81.14 |  |  | 80.91 |  |  |  | 3.61 |  | 2.98 | [8 empty] | 17.38 |  |  |  |  | 0.10
1996 |  |  |  | 3472.68 |  |  | 8033 |  |  |  | 430 | [10 empty] | 90.62 |  |  |  | 90.74 | [5 empty] | 91.94 |  |  | 91.45 |  |  |  | 0.76 |  | 0.70 | [8 empty] | 8.57 |  |  |  |  | 0.11
1997 |  |  |  | 3328.48 |  |  | 7646 |  |  |  | 430 | [10 empty] | 86.95 |  |  |  | 87.04 | [5 empty] | 88.36 |  |  | 87.28 |  |  |  | 1.24 |  | 1.09 | [8 empty] | 11.87 |  |  |  |  | 0.09
1998 |  |  |  | 3487.73 |  |  | 8095 |  |  |  | 430 | [10 empty] | 92.37 |  |  |  | 92.41 | [5 empty] | 92.59 |  |  | 92.41 |  |  |  | 0.39 |  | 0.36 | [8 empty] | 7.23 |  |  |  |  | 0.04
1999 |  |  |  | 3117.54 |  |  | 7240 |  |  |  | 430 | [10 empty] | 81.25 |  |  |  | 81.61 | [5 empty] | 82.76 |  |  | 82.65 |  |  |  | 1.21 |  | 1.00 | [8 empty] | 17.39 |  |  |  |  | 0.36
2000 |  |  |  | 3192.12 |  |  | 7268 |  |  |  | 430 | [10 empty] | 82.27 |  |  |  | 82.53 | [5 empty] | 84.51 |  |  | 82.74 |  |  |  | 4.10 |  | 3.53 | [8 empty] | 13.95 |  |  |  |  | 0.26
2001 |  |  |  | 3514.87 |  |  | 8069 |  |  |  | 437 | [10 empty] | 91.61 |  |  |  | 91.77 | [5 empty] | 91.82 |  |  | 92.11 |  |  |  | 0.18 |  | 0.17 | [8 empty] | 8.07 |  |  |  |  | 0.15
2002 |  |  |  | 3330.66 |  |  | 7909 |  |  |  | 437 | [10 empty] | 90.08 |  |  |  | 90.21 | [5 empty] | 87.01 |  |  | 90.29 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 9.72 |  |  |  |  | 0.13
2003 |  |  |  | 3097.84 |  |  | 7197 |  |  |  | 437 | [10 empty] | 80.96 |  |  |  | 80.96 | [5 empty] | 80.91 |  |  | 82.15 |  |  |  | 3.43 |  | 3.04 | [8 empty] | 16.00 |  |  |  |  | 0.00
2004 |  |  |  | 3342.33 |  |  | 7692 |  |  |  | 437 | [10 empty] | 87.07 |  |  |  | 87.07 | [5 empty] | 87.07 |  |  | 87.57 |  |  |  | 0.21 |  | 2.70 | [8 empty] | 10.23 |  |  |  |  | 0.00
2005 |  |  |  | 3503.53 |  |  | 8029 |  |  |  | 437 | [10 empty] | 91.52 |  |  |  | 91.52 | [5 empty] | 91.52 |  |  | 91.66 |  |  |  | 0.18 |  | 0.25 | [8 empty] | 8.23 |  |  |  |  | 0.00
2006 |  |  |  | 3468.50 |  |  | 7979 |  |  |  | 437 | [10 empty] | 90.83 |  |  |  | 90.83 | [5 empty] | 90.61 |  |  | 91.08 |  |  |  | 0.26 |  | 1.48 | [8 empty] | 7.68 |  |  |  |  | 0.00
2007 |  |  |  | 3179.36 |  |  | 6933 |  |  |  | 470 | [10 empty] | 79.71 |  |  |  | 79.71 | [5 empty] | 79.74 |  |  | 79.14 |  |  |  | 0.52 |  | 3.33 | [8 empty] | 16.96 |  |  |  |  | 0.00
2008 |  |  |  | 3670.29 |  |  | 7824 |  |  |  | 470 | [10 empty] | 88.94 |  |  |  | 88.94 | [5 empty] | 88.90 |  |  | 89.07 |  |  |  | 2.35 |  | 2.59 | [8 empty] | 8.47 |  |  |  |  | 0.00
2009 |  |  |  | 3708.04 |  |  | 7926 |  |  |  | 470 | [10 empty] | 90.19 |  |  |  | 90.19 | [5 empty] | 90.06 |  |  | 90.48 |  |  |  | 0.34 |  | 1.34 | [8 empty] | 8.47 |  |  |  |  | 0.00
2010 |  |  |  | 3762.00 |  |  | 8031 |  |  |  | 470 | [10 empty] | 91.46 |  |  |  | 91.46 | [5 empty] | 91.37 |  |  | 91.68 |  |  |  | 0.00 |  | 0.67 | [8 empty] | 7.87 |  |  |  |  | 0.00
2011 |  |  |  | 3422.07 |  |  | 7291 |  |  |  | 470 | [10 empty] | 83.12 |  |  |  | 83.12 | [5 empty] | 83.12 |  |  | 83.23 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 16.80 |  |  |  |  | 0.00
2012 |  |  |  | 3697.01 |  |  | 7881 |  |  |  | 470 | [10 empty] | 89.57 |  |  |  | 89.57 | [5 empty] | 89.55 |  |  | 89.72 |  |  |  | 0.47 |  | 1.24 | [8 empty] | 9.19 |  |  |  |  | 0.00
2013 |  |  |  | 3834.70 |  |  | 8009 |  |  |  | 470 | [10 empty] | 91.29 |  |  |  | 91.45 | [5 empty] | 93.14 |  |  | 91.43 |  |  |  | 0.02 |  | 0.59 | [8 empty] | 7.97 |  |  |  |  | 0.16
2014 |  |  |  | 3787.47 |  |  | 8022 |  |  |  | 470 | [10 empty] | 90.51 |  |  |  | 90.69 | [5 empty] | 91.99 |  |  | 91.58 |  |  |  | 0.82 |  | 1.48 | [8 empty] | 7.83 |  |  |  |  | 0.18
2015 |  |  |  | 3418.04 |  |  | 7194 |  |  |  | 470 | [10 empty] | 81.59 |  |  |  | 82.00 | [5 empty] | 83.02 |  |  | 82.12 |  |  |  | 0.00 |  | 3.94 | [8 empty] | 14.06 |  |  |  |  | 0.41
2016 |  |  |  | 3806.89 |  |  | 8056 |  |  |  | 470 | [10 empty] | 90.69 |  |  |  | 90.80 | [5 empty] | 92.21 |  |  | 91.71 |  |  |  | 0.95 |  | 1.17 | [8 empty] | 8.03 |  |  |  |  | 0.10
2017 |  |  |  | 3492.07 |  |  | 7421 |  |  |  | 470 | [10 empty] | 82.88 |  |  |  | 83.23 | [5 empty] | 84.82 |  |  | 84.71 |  |  |  | 1.38 |  | 1.17 | [8 empty] | 15.60 |  |  |  |  | 0.35
2018 |  |  |  | 3822.70 |  |  | 8103 |  |  |  | 479 | [10 empty] | 90.59 |  |  |  | 91.46 | [5 empty] | 91.10 |  |  | 92.50 |  |  |  | 0.68 |  | 1.83 | [8 empty] | 6.71 |  |  |  |  | 0.87
2019 |  |  |  | 4192.05 |  |  | 8760 |  |  |  | 479 | [10 empty] | 99.16 |  |  |  | 99.73 | [5 empty] | 99.90 |  |  | 100.00 |  |  |  | 0.19 |  | 0.19 | [8 empty] | 0.08 |  |  |  |  | 0.57
2020 |  |  |  | 3709.65 |  |  | 8151 |  |  |  | 479 | [10 empty] | 87.60 |  |  |  | 88.11 | [5 empty] | 88.17 |  |  | 92.79 |  |  |  | 4.97 |  | 5.28 | [8 empty] | 6.61 |  |  |  |  | 0.51
2021 |  |  |  | 3759.42 |  |  | 7926 |  |  |  | 479 | [10 empty] | 88.95 |  |  |  | 89.43 | [5 empty] | 89.59 |  |  | 90.48 |  |  |  | 3.17 |  | 3.54 | [8 empty] | 7.03 |  |  |  |  | 0.48
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1983 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 222 | [14 empty] | 91
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 612 | [14 empty] | 931 |  |  |  | 18
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 15
E. |  | Testing of plant systems or components | [39 empty] | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 1
Z. |  | Other | [39 empty] | 10
Subtotal | [22 empty] | 612 |  |  |  | 222 | [10 empty] | 946 |  |  |  | 120 | [11 empty] | 0
Total | [22 empty] | 834 | [14 empty] | 1066
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1983 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 0
12. |  |  | Reactor I&C Systems | [19 empty] | 188 | [14 empty] | 16
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 9
16. |  |  | Steam generation systems | [34 empty] | 11
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 10
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [19 empty] | 34 | [14 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 222 | [14 empty] | 94
Highlights (2021)
Operation at full power in base load mode

## PAKS-2
2021 Operating Experience
HU-2 | [9 empty] | PAKS-2 | [28 empty] | HUNGARY
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | PAKS Zrt (PAKS NUCLEAR POWER PLANT, LTD.)
Owner | [8 empty] | : | MVM Zrt. (HUNGARIAN POWER COMPANIES LTD.)
Reactor Supplier | [8 empty] | : | AEE (ATOMENERGOEXPORT)
Turbine Supplier | [8 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PWR / VVER V-213 | [12 empty] | Construction Date | [16 empty] | : |  |  | 1974-08-01
Thermal power | [14 empty] | : |  |  | 1485 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 1984-09-06
Gross electrical power | [14 empty] | : |  |  | 506 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 1984-11-14
Reference unit power (net) | [14 empty] | : |  |  | 479 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Vertical | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 297
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 6
| Refuelling type | [15 empty] | : |  |  | OFF-line | [12 empty] | Containment type | [16 empty] | : |  |  | Confinement
| Moderator material | [15 empty] | : |  |  | H2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | 3.82 | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | 12 | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 2
| Part of the core refuelled [%] | [15 empty] | : |  |  | 30 | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | 37000 | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | 2
| Active core diameter [m] | [15 empty] | : |  |  | 2.88 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 4.315
| Active core height/length [m] | [15 empty] | : |  |  | 2.42 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 349 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 13.1 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | 3
| Number of control rod assemblies | [15 empty] | : |  |  | 37 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | 4
| Number of external reactor coolant loops | [15 empty] | : |  |  | 6 | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | 3
| Coolant type | [15 empty] | : |  |  | H2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | DH
Annual Production Results (2021)
Net Energy Production | [20 empty] | : | 3375.4 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 2.78 %
Energy Availability Factor (EAF) | [20 empty] | : | 80.05 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 3.33 %
Unit Capability Factor (UCF) | [20 empty] | : | 80.73 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 15.94 %
Load Factor (LF) | [20 empty] | : | 80.5 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0.68 %
Operating Factor (OF) | [20 empty] | : | 81.91 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 1585 hours
Equivalent non-electrical energy generated (NEG) | [20 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 360.89 |  | 326.68 |  |  |  |  | 335.55 |  | 350.01 | [8 empty] | 354.16 |  |  |  | 338.11 | [6 empty] | 271.41 |  | 349.14 |  |  |  |  | 342.82 |  |  | 172.14 |  |  | 0.00 | [9 empty] | 174.49 |  |  | 3375.40
EAF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 92.65 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 98.04 | [6 empty] | 76.16 |  | 97.97 |  |  |  |  | 100.00 |  |  | 48.27 |  |  | 0.00 | [9 empty] | 48.98 |  |  | 80.05
UCF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 92.65 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 80.22 |  | 100.00 |  |  |  |  | 100.00 |  |  | 48.27 |  |  | 0.00 | [9 empty] | 48.98 |  |  | 80.73
LF [%] |  |  |  |  | 101.69 |  | 101.91 |  |  |  |  | 94.28 |  | 101.49 | [8 empty] | 99.38 |  |  |  | 98.04 | [6 empty] | 76.16 |  | 97.97 |  |  |  |  | 99.40 |  |  | 48.24 |  |  | 0.00 | [9 empty] | 48.96 |  |  | 80.50
OF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 97.04 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 80.51 |  | 100.00 |  |  |  |  | 100.00 |  |  | 48.59 |  |  | 0.00 | [9 empty] | 57.66 |  |  | 81.91
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 7.35 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 19.78 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.78
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 7.35 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 19.78 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 12.07 |  |  | 3.33
PUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 51.73 |  |  | 100.00 | [9 empty] | 38.95 |  |  | 15.94
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 1.96 | [6 empty] | 4.06 |  | 2.03 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.68
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 121665.76 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 2.1 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 82.74 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 5.52 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 82.92 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 11.56 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 83.62 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.18 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 83.62 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 921.75 |  |  |  | 2659 |  |  |  |  | 425 | [10 empty] | 94.06 |  |  |  |  | 94.06 | [5 empty] | 97.33 |  |  | 99.45 |  |  |  |  | 1.21 |  | 1.15 | [8 empty] | 4.78 |  |  |  |  | 0.00
1985 |  |  |  | 3101.62 |  |  |  | 7695 |  |  |  |  | 415 | [10 empty] | 85.11 |  |  |  |  | 85.11 | [5 empty] | 85.32 |  |  | 87.84 |  |  |  |  | 0.75 |  | 0.64 | [8 empty] | 14.25 |  |  |  |  | 0.00
1986 |  |  |  | 3148.27 |  |  |  | 7643 |  |  |  |  | 415 | [10 empty] | 86.01 |  |  |  |  | 86.01 | [5 empty] | 86.60 |  |  | 87.25 |  |  |  |  | 2.11 |  | 1.85 | [8 empty] | 12.14 |  |  |  |  | 0.00
1987 |  |  |  | 3193.95 |  |  |  | 7770 |  |  |  |  | 415 | [10 empty] | 85.33 |  |  |  |  | 85.33 | [5 empty] | 87.86 |  |  | 88.70 |  |  |  |  | 3.06 |  | 2.69 | [8 empty] | 11.98 |  |  |  |  | 0.00
1988 |  |  |  | 3046.30 |  |  |  | 7352 |  |  |  |  | 415 | [10 empty] | 81.93 |  |  |  |  | 81.93 | [5 empty] | 83.57 |  |  | 83.70 |  |  |  |  | 0.20 |  | 0.17 | [8 empty] | 17.90 |  |  |  |  | 0.00
1989 |  |  |  | 3300.66 |  |  |  | 7962 |  |  |  |  | 415 | [10 empty] | 88.63 |  |  |  |  | 88.63 | [5 empty] | 90.79 |  |  | 90.89 |  |  |  |  | 1.01 |  | 0.91 | [8 empty] | 10.46 |  |  |  |  | 0.00
1990 |  |  |  | 3338.22 |  |  |  | 7845 |  |  |  |  | 425 | [10 empty] | 87.99 |  |  |  |  | 87.99 | [5 empty] | 89.66 |  |  | 89.55 |  |  |  |  | 3.12 |  | 2.83 | [8 empty] | 9.18 |  |  |  |  | 0.00
1991 |  |  |  | 3421.60 |  |  |  | 7912 |  |  |  |  | 415 | [10 empty] | 88.63 |  |  |  |  | 88.63 | [5 empty] | 94.12 |  |  | 90.32 |  |  |  |  | 2.25 |  | 2.04 | [8 empty] | 9.32 |  |  |  |  | 0.00
1992 |  |  |  | 3174.93 |  |  |  | 6829 |  |  |  |  | 433 | [10 empty] | 76.00 |  |  |  |  | 76.01 | [5 empty] | 83.47 |  |  | 77.74 |  |  |  |  | 6.63 |  | 5.40 | [8 empty] | 18.59 |  |  |  |  | 0.02
1993 |  |  |  | 3568.98 |  |  |  | 7731 |  |  |  |  | 433 | [10 empty] | 87.00 |  |  |  |  | 87.00 | [5 empty] | 94.09 |  |  | 88.25 |  |  |  |  | 0.43 |  | 0.38 | [8 empty] | 12.62 |  |  |  |  | 0.00
1994 |  |  |  | 3440.38 |  |  |  | 8000 |  |  |  |  | 433 | [10 empty] | 89.44 |  |  |  |  | 89.50 | [5 empty] | 90.70 |  |  | 91.32 |  |  |  |  | 0.18 |  | 0.16 | [8 empty] | 10.34 |  |  |  |  | 0.06
1995 |  |  |  | 3309.08 |  |  |  | 7657 |  |  |  |  | 433 | [10 empty] | 86.45 |  |  |  |  | 86.63 | [5 empty] | 87.24 |  |  | 87.41 |  |  |  |  | 5.62 |  | 5.16 | [8 empty] | 8.21 |  |  |  |  | 0.18
1996 |  |  |  | 3019.89 |  |  |  | 7011 |  |  |  |  | 433 | [10 empty] | 79.41 |  |  |  |  | 79.50 | [5 empty] | 79.40 |  |  | 79.82 |  |  |  |  | 5.89 |  | 4.98 | [8 empty] | 15.52 |  |  |  |  | 0.09
1997 |  |  |  | 3267.61 |  |  |  | 7807 |  |  |  |  | 433 | [10 empty] | 88.20 |  |  |  |  | 88.26 | [5 empty] | 86.15 |  |  | 89.12 |  |  |  |  | 6.15 |  | 5.78 | [8 empty] | 5.96 |  |  |  |  | 0.06
1998 |  |  |  | 3206.72 |  |  |  | 7717 |  |  |  |  | 433 | [10 empty] | 88.21 |  |  |  |  | 88.27 | [5 empty] | 84.54 |  |  | 88.09 |  |  |  |  | 2.83 |  | 2.57 | [8 empty] | 9.16 |  |  |  |  | 0.06
1999 |  |  |  | 3246.62 |  |  |  | 7780 |  |  |  |  | 433 | [10 empty] | 89.23 |  |  |  |  | 90.18 | [5 empty] | 85.59 |  |  | 88.81 |  |  |  |  | 2.10 |  | 1.93 | [8 empty] | 7.88 |  |  |  |  | 0.95
2000 |  |  |  | 3059.33 |  |  |  | 7073 |  |  |  |  | 433 | [10 empty] | 79.99 |  |  |  |  | 80.08 | [5 empty] | 80.44 |  |  | 80.52 |  |  |  |  | 0.89 |  | 0.72 | [8 empty] | 19.19 |  |  |  |  | 0.10
2001 |  |  |  | 3266.89 |  |  |  | 7484 |  |  |  |  | 441 | [10 empty] | 84.76 |  |  |  |  | 84.94 | [5 empty] | 84.57 |  |  | 85.43 |  |  |  |  | 6.50 |  | 5.91 | [8 empty] | 9.15 |  |  |  |  | 0.18
2002 |  |  |  | 3338.46 |  |  |  | 7644 |  |  |  |  | 441 | [10 empty] | 86.54 |  |  |  |  | 86.71 | [5 empty] | 86.42 |  |  | 87.26 |  |  |  |  | 1.93 |  | 2.19 | [8 empty] | 11.10 |  |  |  |  | 0.17
2003 |  |  |  | 918.84 |  |  |  | 2089 |  |  |  |  | 441 | [10 empty] | 23.80 |  |  |  |  | 23.80 | [5 empty] | 23.78 |  |  | 23.85 |  |  |  |  | 0.00 |  | 65.27 | [8 empty] | 10.94 |  |  |  |  | 0.00
2004 |  |  |  | 1137.22 |  |  |  | 2620 |  |  |  |  | 441 | [10 empty] | 29.36 |  |  |  |  | 29.36 | [5 empty] | 29.36 |  |  | 29.83 |  |  |  |  | 4.66 |  | 66.93 | [8 empty] | 3.71 |  |  |  |  | 0.00
2005 |  |  |  | 2929.48 |  |  |  | 6669 |  |  |  |  | 441 | [10 empty] | 75.84 |  |  |  |  | 75.84 | [5 empty] | 75.83 |  |  | 76.13 |  |  |  |  | 1.92 |  | 1.54 | [8 empty] | 22.63 |  |  |  |  | 0.00
2006 |  |  |  | 2399.56 |  |  |  | 5493 |  |  |  |  | 441 | [10 empty] | 62.34 |  |  |  |  | 62.59 | [5 empty] | 62.11 |  |  | 62.71 |  |  |  |  | 0.03 |  | 0.02 | [8 empty] | 37.39 |  |  |  |  | 0.25
2007 |  |  |  | 3477.05 |  |  |  | 7887 |  |  |  |  | 443 | [10 empty] | 89.16 |  |  |  |  | 89.16 | [5 empty] | 89.60 |  |  | 90.03 |  |  |  |  | 2.24 |  | 2.05 | [8 empty] | 8.79 |  |  |  |  | 0.00
2008 |  |  |  | 2993.79 |  |  |  | 6669 |  |  |  |  | 473 | [10 empty] | 76.24 |  |  |  |  | 76.26 | [5 empty] | 76.50 |  |  | 75.92 |  |  |  |  | 0.70 |  | 4.25 | [8 empty] | 19.50 |  |  |  |  | 0.02
2009 |  |  |  | 3772.51 |  |  |  | 7985 |  |  |  |  | 473 | [10 empty] | 91.14 |  |  |  |  | 91.14 | [5 empty] | 91.05 |  |  | 91.15 |  |  |  |  | 1.13 |  | 1.04 | [8 empty] | 7.82 |  |  |  |  | 0.00
2010 |  |  |  | 3715.76 |  |  |  | 7892 |  |  |  |  | 473 | [10 empty] | 89.74 |  |  |  |  | 89.74 | [5 empty] | 89.68 |  |  | 90.09 |  |  |  |  | 1.99 |  | 2.31 | [8 empty] | 7.95 |  |  |  |  | 0.00
2011 |  |  |  | 3770.49 |  |  |  | 7978 |  |  |  |  | 473 | [10 empty] | 91.02 |  |  |  |  | 91.02 | [5 empty] | 91.00 |  |  | 91.07 |  |  |  |  | 0.22 |  | 0.84 | [8 empty] | 8.15 |  |  |  |  | 0.00
2012 |  |  |  | 3521.36 |  |  |  | 7456 |  |  |  |  | 473 | [10 empty] | 84.77 |  |  |  |  | 84.77 | [5 empty] | 84.75 |  |  | 84.88 |  |  |  |  | 0.48 |  | 0.41 | [8 empty] | 14.82 |  |  |  |  | 0.00
2013 |  |  |  | 3794.73 |  |  |  | 7905 |  |  |  |  | 473 | [10 empty] | 89.72 |  |  |  |  | 90.25 | [5 empty] | 91.58 |  |  | 90.24 |  |  |  |  | 2.28 |  | 2.11 | [8 empty] | 7.64 |  |  |  |  | 0.53
2014 |  |  |  | 3903.00 |  |  |  | 8127 |  |  |  |  | 473 | [10 empty] | 92.41 |  |  |  |  | 92.50 | [5 empty] | 94.20 |  |  | 92.77 |  |  |  |  | 0.12 |  | 0.11 | [8 empty] | 7.39 |  |  |  |  | 0.09
2015 |  |  |  | 3889.01 |  |  |  | 8118 |  |  |  |  | 473 | [10 empty] | 91.91 |  |  |  |  | 92.25 | [5 empty] | 93.86 |  |  | 92.67 |  |  |  |  | 0.47 |  | 0.44 | [8 empty] | 7.31 |  |  |  |  | 0.34
2016 |  |  |  | 3375.14 |  |  |  | 7132 |  |  |  |  | 473 | [10 empty] | 80.09 |  |  |  |  | 80.16 | [5 empty] | 81.23 |  |  | 81.19 |  |  |  |  | 0.47 |  | 2.87 | [8 empty] | 16.96 |  |  |  |  | 0.07
2017 |  |  |  | 4178.74 |  |  |  | 8760 |  |  |  |  | 473 | [10 empty] | 99.46 |  |  |  |  | 99.83 | [5 empty] | 100.85 |  |  | 100.00 |  |  |  |  | 0.14 |  | 0.14 | [8 empty] | 0.03 |  |  |  |  | 0.37
2018 |  |  |  | 3670.36 |  |  |  | 7798 |  |  |  |  | 477 | [10 empty] | 87.44 |  |  |  |  | 88.51 | [5 empty] | 87.84 |  |  | 89.02 |  |  |  |  | 4.43 |  | 4.10 | [8 empty] | 7.38 |  |  |  |  | 1.07
2019 |  |  |  | 3872.20 |  |  |  | 8127 |  |  |  |  | 477 | [10 empty] | 91.47 |  |  |  |  | 92.04 | [5 empty] | 92.67 |  |  | 92.77 |  |  |  |  | 0.40 |  | 0.57 | [8 empty] | 7.39 |  |  |  |  | 0.56
2020 |  |  |  | 3819.36 |  |  |  | 8175 |  |  |  |  | 477 | [10 empty] | 90.36 |  |  |  |  | 91.00 | [5 empty] | 91.15 |  |  | 93.07 |  |  |  |  | 2.07 |  | 2.05 | [8 empty] | 6.95 |  |  |  |  | 0.65
2021 |  |  |  | 3375.40 |  |  |  | 7175 |  |  |  |  | 479 | [10 empty] | 80.05 |  |  |  |  | 80.73 | [5 empty] | 80.50 |  |  | 81.91 |  |  |  |  | 2.78 |  | 3.33 | [8 empty] | 15.94 |  |  |  |  | 0.68
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2021 | [16 empty] | 1984 to 2021
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [27 empty] | 195 | [15 empty] | 404
C. |  | Inspection, maintenance or repair combined with refuelling | [22 empty] | 1392 | [16 empty] | 924 |  |  |  | 12
D. |  | Inspection, maintenance or repair without refuelling | [39 empty] | 68
E. |  | Testing of plant systems or components | [39 empty] | 1 |  |  |  | 0
J. |  | Grid limitation, failure or grid unavailability | [55 empty] | 0
L. |  | Human factor related | [43 empty] | 15
Z. |  | Other | [43 empty] | 18
Subtotal | [24 empty] | 1392 |  |  |  |  | 195 | [11 empty] | 993 |  |  |  | 449 | [11 empty] | 0
Total | [24 empty] | 1587 | [16 empty] | 1442
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2021 | [16 empty] | 1984 to 2021
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [38 empty] | 153
12. |  |  | Reactor I&C Systems | [38 empty] | 19
13. |  |  | Reactor Auxiliary Systems | [38 empty] | 0
14. |  |  | Safety Systems | [21 empty] | 168 | [16 empty] | 4
15. |  |  | Reactor Cooling Systems | [38 empty] | 23
16. |  |  | Steam generation systems | [38 empty] | 14
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [38 empty] | 13
21. |  |  | Fuel Handling and Storage Facilities | [38 empty] | 156
31. |  |  | Turbine and auxiliaries | [21 empty] | 27 | [16 empty] | 14
32. |  |  | Feedwater and Main Steam System | [38 empty] | 1
34. |  |  | Miscellaneous Systems | [38 empty] | 3
41. |  |  | Main Generator Systems | [38 empty] | 11
42. |  |  | Electrical Power Supply Systems | [38 empty] | 2
Total | [24 empty] | 195 | [16 empty] | 413
RUP revision during the year (2021) due to power uprate
RUP at the end of previous year : 477 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
March | [5 empty] | 479 |  |  |  |  | Improved measurement (<2%) | [14 empty] | Balance of plant | [13 empty] | Turbine modernization
Highlights (2021)
Operation at full power in base load mode

## PAKS-3
2021 Operating Experience
HU-3 | [9 empty] | PAKS-3 | [28 empty] | HUNGARY
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | PAKS Zrt (PAKS NUCLEAR POWER PLANT, LTD.)
Owner | [8 empty] | : | MVM Zrt. (HUNGARIAN POWER COMPANIES LTD.)
Reactor Supplier | [8 empty] | : | AEE (ATOMENERGOEXPORT)
Turbine Supplier | [8 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PWR / VVER V-213 | [12 empty] | Construction Date | [16 empty] | : |  |  | 1979-10-01
Thermal power | [14 empty] | : |  |  | 1485 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 1986-09-28
Gross electrical power | [14 empty] | : |  |  | 506 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 1986-12-01
Reference unit power (net) | [14 empty] | : |  |  | 479 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Vertical | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 297
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 6
| Refuelling type | [15 empty] | : |  |  | OFF-line | [12 empty] | Containment type | [16 empty] | : |  |  | Confinement
| Moderator material | [15 empty] | : |  |  | H2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | 3.82 | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | 12 | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 2
| Part of the core refuelled [%] | [15 empty] | : |  |  | 30 | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | 37000 | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | 2
| Active core diameter [m] | [15 empty] | : |  |  | 2.88 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 4.4
| Active core height/length [m] | [15 empty] | : |  |  | 2.42 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 349 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 13.1 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | 3
| Number of control rod assemblies | [15 empty] | : |  |  | 37 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | 4
| Number of external reactor coolant loops | [15 empty] | : |  |  | 6 | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | 3
| Coolant type | [15 empty] | : |  |  | H2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | DH
Annual Production Results (2021)
Net Energy Production | [20 empty] | : | 4210.62 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 0.29 %
Energy Availability Factor (EAF) | [20 empty] | : | 99.24 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 0.29 %
Unit Capability Factor (UCF) | [20 empty] | : | 99.71 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 0 %
Load Factor (LF) | [20 empty] | : | 100.55 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0.47 %
Operating Factor (OF) | [20 empty] | : | 99.91 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 8 hours
Equivalent non-electrical energy generated (NEG) | [20 empty] | : | 3.16 GW(e).h
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 364.67 |  | 328.89 |  |  |  |  | 364.15 |  | 351.47 | [8 empty] | 356.64 |  |  |  | 338.20 | [6 empty] | 341.56 |  | 352.56 |  |  |  |  | 344.13 |  |  | 354.21 |  |  | 350.80 | [9 empty] | 363.33 |  |  | 4210.62
EAF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 98.30 | [6 empty] | 95.84 |  | 98.93 |  |  |  |  | 100.00 |  |  | 98.36 |  |  | 99.56 | [9 empty] | 100.00 |  |  | 99.24
UCF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 98.60 |  | 100.00 |  |  |  |  | 100.00 |  |  | 98.36 |  |  | 99.56 | [9 empty] | 100.00 |  |  | 99.71
LF [%] |  |  |  |  | 103.62 |  | 103.47 |  |  |  |  | 102.32 |  | 101.91 | [8 empty] | 100.07 |  |  |  | 98.06 | [6 empty] | 95.84 |  | 98.93 |  |  |  |  | 99.78 |  |  | 99.26 |  |  | 101.72 | [9 empty] | 101.95 |  |  | 100.55
OF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  |  | 98.93 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.91
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 1.40 |  | 0.00 |  |  |  |  | 0.00 |  |  | 1.64 |  |  | 0.44 | [9 empty] | 0.00 |  |  | 0.29
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 1.40 |  | 0.00 |  |  |  |  | 0.00 |  |  | 1.64 |  |  | 0.44 | [9 empty] | 0.00 |  |  | 0.29
PUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 1.70 | [6 empty] | 2.76 |  | 1.07 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.47
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 121176.68 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 1.62 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 87.49 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 2.06 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 87.86 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 10.08 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 88.34 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.38 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 88.45 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 718.54 |  |  |  | 2109 |  |  |  |  | 427 | [10 empty] | 99.65 |  |  |  |  | 99.65 | [5 empty] | 101.72 |  |  | 100.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.35 |  |  |  |  | 0.00
1987 |  |  |  | 3209.58 |  |  |  | 7648 |  |  |  |  | 415 | [10 empty] | 86.95 |  |  |  |  | 86.95 | [5 empty] | 88.29 |  |  | 87.31 |  |  |  |  | 0.92 |  | 0.81 | [8 empty] | 12.24 |  |  |  |  | 0.00
1988 |  |  |  | 3300.93 |  |  |  | 7874 |  |  |  |  | 415 | [10 empty] | 88.09 |  |  |  |  | 88.09 | [5 empty] | 90.55 |  |  | 89.64 |  |  |  |  | 1.12 |  | 0.99 | [8 empty] | 10.92 |  |  |  |  | 0.00
1989 |  |  |  | 3140.52 |  |  |  | 7343 |  |  |  |  | 415 | [10 empty] | 82.41 |  |  |  |  | 82.41 | [5 empty] | 86.39 |  |  | 83.82 |  |  |  |  | 2.15 |  | 1.81 | [8 empty] | 15.78 |  |  |  |  | 0.00
1990 |  |  |  | 3273.39 |  |  |  | 7755 |  |  |  |  | 435 | [10 empty] | 85.64 |  |  |  |  | 85.64 | [5 empty] | 85.90 |  |  | 88.53 |  |  |  |  | 4.39 |  | 3.93 | [8 empty] | 10.43 |  |  |  |  | 0.00
1991 |  |  |  | 3256.00 |  |  |  | 7580 |  |  |  |  | 410 | [10 empty] | 84.19 |  |  |  |  | 84.19 | [5 empty] | 90.66 |  |  | 86.53 |  |  |  |  | 6.82 |  | 6.16 | [8 empty] | 9.65 |  |  |  |  | 0.00
1992 |  |  |  | 3587.32 |  |  |  | 7852 |  |  |  |  | 433 | [10 empty] | 87.47 |  |  |  |  | 87.70 | [5 empty] | 94.32 |  |  | 89.39 |  |  |  |  | 3.49 |  | 3.17 | [8 empty] | 9.13 |  |  |  |  | 0.23
1993 |  |  |  | 3177.93 |  |  |  | 6950 |  |  |  |  | 433 | [10 empty] | 77.40 |  |  |  |  | 77.63 | [5 empty] | 83.78 |  |  | 79.34 |  |  |  |  | 1.05 |  | 0.82 | [8 empty] | 21.55 |  |  |  |  | 0.23
1994 |  |  |  | 3375.99 |  |  |  | 7884 |  |  |  |  | 433 | [10 empty] | 88.53 |  |  |  |  | 88.64 | [5 empty] | 89.00 |  |  | 90.00 |  |  |  |  | 0.41 |  | 0.36 | [8 empty] | 11.00 |  |  |  |  | 0.11
1995 |  |  |  | 3392.81 |  |  |  | 7911 |  |  |  |  | 433 | [10 empty] | 88.99 |  |  |  |  | 89.16 | [5 empty] | 89.45 |  |  | 90.31 |  |  |  |  | 3.29 |  | 3.03 | [8 empty] | 7.80 |  |  |  |  | 0.17
1996 |  |  |  | 3429.38 |  |  |  | 8136 |  |  |  |  | 433 | [10 empty] | 90.84 |  |  |  |  | 90.91 | [5 empty] | 90.16 |  |  | 92.62 |  |  |  |  | 2.04 |  | 1.89 | [8 empty] | 7.20 |  |  |  |  | 0.07
1997 |  |  |  | 3066.09 |  |  |  | 7136 |  |  |  |  | 433 | [10 empty] | 80.91 |  |  |  |  | 81.10 | [5 empty] | 80.83 |  |  | 81.46 |  |  |  |  | 5.11 |  | 4.37 | [8 empty] | 14.53 |  |  |  |  | 0.19
1998 |  |  |  | 3294.11 |  |  |  | 7566 |  |  |  |  | 433 | [10 empty] | 87.98 |  |  |  |  | 88.02 | [5 empty] | 86.85 |  |  | 86.37 |  |  |  |  | 6.17 |  | 5.79 | [8 empty] | 6.20 |  |  |  |  | 0.04
1999 |  |  |  | 3445.71 |  |  |  | 8058 |  |  |  |  | 433 | [10 empty] | 92.19 |  |  |  |  | 92.28 | [5 empty] | 90.84 |  |  | 91.99 |  |  |  |  | 0.47 |  | 0.43 | [8 empty] | 7.29 |  |  |  |  | 0.09
2000 |  |  |  | 3517.25 |  |  |  | 8163 |  |  |  |  | 433 | [10 empty] | 92.76 |  |  |  |  | 93.04 | [5 empty] | 92.47 |  |  | 92.93 |  |  |  |  | 0.73 |  | 0.68 | [8 empty] | 6.28 |  |  |  |  | 0.28
2001 |  |  |  | 3040.40 |  |  |  | 7159 |  |  |  |  | 433 | [10 empty] | 80.31 |  |  |  |  | 80.72 | [5 empty] | 80.16 |  |  | 81.72 |  |  |  |  | 2.68 |  | 2.22 | [8 empty] | 17.06 |  |  |  |  | 0.42
2002 |  |  |  | 3256.84 |  |  |  | 7900 |  |  |  |  | 433 | [10 empty] | 90.36 |  |  |  |  | 90.48 | [5 empty] | 85.86 |  |  | 90.18 |  |  |  |  | 0.38 |  | 0.35 | [8 empty] | 9.17 |  |  |  |  | 0.12
2003 |  |  |  | 3008.34 |  |  |  | 7746 |  |  |  |  | 433 | [10 empty] | 80.47 |  |  |  |  | 87.85 | [5 empty] | 79.31 |  |  | 88.42 |  |  |  |  | 0.85 |  | 0.88 | [8 empty] | 11.27 |  |  |  |  | 7.37
2004 |  |  |  | 3333.25 |  |  |  | 7732 |  |  |  |  | 433 | [10 empty] | 87.64 |  |  |  |  | 87.64 | [5 empty] | 87.64 |  |  | 88.02 |  |  |  |  | 1.86 |  | 4.45 | [8 empty] | 7.91 |  |  |  |  | 0.00
2005 |  |  |  | 3038.71 |  |  |  | 7088 |  |  |  |  | 433 | [10 empty] | 80.10 |  |  |  |  | 80.10 | [5 empty] | 80.11 |  |  | 80.91 |  |  |  |  | 3.96 |  | 3.39 | [8 empty] | 16.50 |  |  |  |  | 0.00
2006 |  |  |  | 3454.91 |  |  |  | 8007 |  |  |  |  | 433 | [10 empty] | 91.18 |  |  |  |  | 91.18 | [5 empty] | 91.08 |  |  | 91.40 |  |  |  |  | 0.25 |  | 1.40 | [8 empty] | 7.42 |  |  |  |  | 0.00
2007 |  |  |  | 3396.00 |  |  |  | 7691 |  |  |  |  | 443 | [10 empty] | 87.53 |  |  |  |  | 87.53 | [5 empty] | 87.51 |  |  | 87.80 |  |  |  |  | 0.45 |  | 0.40 | [8 empty] | 12.07 |  |  |  |  | 0.00
2008 |  |  |  | 3530.43 |  |  |  | 7962 |  |  |  |  | 443 | [10 empty] | 90.63 |  |  |  |  | 90.69 | [5 empty] | 90.73 |  |  | 90.64 |  |  |  |  | 0.72 |  | 0.65 | [8 empty] | 8.65 |  |  |  |  | 0.06
2009 |  |  |  | 3174.02 |  |  |  | 7078 |  |  |  |  | 473 | [10 empty] | 80.88 |  |  |  |  | 80.88 | [5 empty] | 80.88 |  |  | 80.80 |  |  |  |  | 0.12 |  | 1.21 | [8 empty] | 17.91 |  |  |  |  | 0.00
2010 |  |  |  | 3831.50 |  |  |  | 8123 |  |  |  |  | 473 | [10 empty] | 92.48 |  |  |  |  | 92.48 | [5 empty] | 92.47 |  |  | 92.73 |  |  |  |  | 0.04 |  | 0.04 | [8 empty] | 7.49 |  |  |  |  | 0.00
2011 |  |  |  | 3688.74 |  |  |  | 7823 |  |  |  |  | 473 | [10 empty] | 89.04 |  |  |  |  | 89.04 | [5 empty] | 89.03 |  |  | 89.30 |  |  |  |  | 0.58 |  | 1.10 | [8 empty] | 9.86 |  |  |  |  | 0.00
2012 |  |  |  | 3803.60 |  |  |  | 8080 |  |  |  |  | 473 | [10 empty] | 91.56 |  |  |  |  | 91.56 | [5 empty] | 91.55 |  |  | 91.99 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.44 |  |  |  |  | 0.00
2013 |  |  |  | 3054.56 |  |  |  | 6480 |  |  |  |  | 473 | [10 empty] | 73.20 |  |  |  |  | 73.92 | [5 empty] | 73.72 |  |  | 73.97 |  |  |  |  | 0.05 |  | 9.35 | [8 empty] | 16.73 |  |  |  |  | 0.72
2014 |  |  |  | 3598.71 |  |  |  | 7620 |  |  |  |  | 473 | [10 empty] | 86.02 |  |  |  |  | 86.30 | [5 empty] | 86.85 |  |  | 86.99 |  |  |  |  | 0.00 |  | 4.01 | [8 empty] | 9.70 |  |  |  |  | 0.28
2015 |  |  |  | 3803.38 |  |  |  | 8032 |  |  |  |  | 473 | [10 empty] | 90.61 |  |  |  |  | 91.15 | [5 empty] | 91.79 |  |  | 91.69 |  |  |  |  | 0.52 |  | 1.01 | [8 empty] | 7.84 |  |  |  |  | 0.55
2016 |  |  |  | 4172.78 |  |  |  | 8784 |  |  |  |  | 473 | [10 empty] | 99.46 |  |  |  |  | 99.96 | [5 empty] | 100.43 |  |  | 100.00 |  |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.00 |  |  |  |  | 0.50
2017 |  |  |  | 3813.11 |  |  |  | 8073 |  |  |  |  | 473 | [10 empty] | 90.95 |  |  |  |  | 91.43 | [5 empty] | 92.03 |  |  | 92.16 |  |  |  |  | 0.06 |  | 0.79 | [8 empty] | 7.79 |  |  |  |  | 0.48
2018 |  |  |  | 3307.59 |  |  |  | 7032 |  |  |  |  | 473 | [10 empty] | 78.50 |  |  |  |  | 78.93 | [5 empty] | 79.83 |  |  | 80.27 |  |  |  |  | 6.62 |  | 5.60 | [8 empty] | 15.47 |  |  |  |  | 0.44
2019 |  |  |  | 3908.46 |  |  |  | 8133 |  |  |  |  | 473 | [10 empty] | 92.20 |  |  |  |  | 92.38 | [5 empty] | 94.33 |  |  | 92.84 |  |  |  |  | 0.77 |  | 0.72 | [8 empty] | 6.90 |  |  |  |  | 0.18
2020 |  |  |  | 3871.06 |  |  |  | 8156 |  |  |  |  | 473 | [10 empty] | 91.55 |  |  |  |  | 91.75 | [5 empty] | 93.17 |  |  | 92.85 |  |  |  |  | 0.37 |  | 0.34 | [8 empty] | 7.92 |  |  |  |  | 0.19
2021 |  |  |  | 4210.62 |  |  |  | 8752 |  |  |  |  | 479 | [10 empty] | 99.24 |  |  |  |  | 99.71 | [5 empty] | 100.55 |  |  | 99.91 |  |  |  |  | 0.29 |  | 0.29 | [8 empty] | 0.00 |  |  |  |  | 0.47
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2021 | [16 empty] | 1986 to 2021
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [27 empty] | 8 | [15 empty] | 135
C. |  | Inspection, maintenance or repair combined with refuelling | [39 empty] | 832 |  |  |  | 76
D. |  | Inspection, maintenance or repair without refuelling | [39 empty] | 31
E. |  | Testing of plant systems or components | [39 empty] | 1 |  |  |  | 4
L. |  | Human factor related | [43 empty] | 0
Z. |  | Other | [43 empty] | 7
Subtotal | [29 empty] | 8 | [11 empty] | 864 |  |  |  | 222
Total | [24 empty] | 8 | [16 empty] | 1086
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2021 | [16 empty] | 1986 to 2021
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [38 empty] | 9
12. |  |  | Reactor I&C Systems | [38 empty] | 29
13. |  |  | Reactor Auxiliary Systems | [38 empty] | 2
14. |  |  | Safety Systems | [38 empty] | 7
15. |  |  | Reactor Cooling Systems | [38 empty] | 1
16. |  |  | Steam generation systems | [38 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [38 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [38 empty] | 30
31. |  |  | Turbine and auxiliaries | [38 empty] | 6
32. |  |  | Feedwater and Main Steam System | [38 empty] | 14
34. |  |  | Miscellaneous Systems | [21 empty] | 8 | [16 empty] | 6
42. |  |  | Electrical Power Supply Systems | [38 empty] | 33
Total | [24 empty] | 8 | [16 empty] | 138
RUP revision during the year (2021) due to power uprate
RUP at the end of previous year : 473 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
March | [5 empty] | 479 |  |  |  |  | Improved measurement (<2%) | [14 empty] | Balance of plant | [13 empty] | Turbine modernization
Highlights (2021)
Operation at full power in base load mode

## PAKS-4
2021 Operating Experience
HU-4 | [9 empty] | PAKS-4 | [28 empty] | HUNGARY
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | PAKS Zrt (PAKS NUCLEAR POWER PLANT, LTD.)
Owner | [8 empty] | : | MVM Zrt. (HUNGARIAN POWER COMPANIES LTD.)
Reactor Supplier | [8 empty] | : | AEE (ATOMENERGOEXPORT)
Turbine Supplier | [8 empty] | : | KTP (Kharkiv Turbine Plant "Turboatom")
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PWR / VVER V-213 | [12 empty] | Construction Date | [16 empty] | : |  |  | 1979-10-01
Thermal power | [14 empty] | : |  |  | 1485 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 1987-08-16
Gross electrical power | [14 empty] | : |  |  | 506 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 1987-11-01
Reference unit power (net) | [14 empty] | : |  |  | 479 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Vertical | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 297
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 6
| Refuelling type | [15 empty] | : |  |  | OFF-line | [12 empty] | Containment type | [16 empty] | : |  |  | Confinement
| Moderator material | [15 empty] | : |  |  | H2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | 3.82 | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | 12 | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 2
| Part of the core refuelled [%] | [15 empty] | : |  |  | 30 | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | 37000 | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | 2
| Active core diameter [m] | [15 empty] | : |  |  | 2.88 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 4.4
| Active core height/length [m] | [15 empty] | : |  |  | 2.42 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 349 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 13.1 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | 3
| Number of control rod assemblies | [15 empty] | : |  |  | 37 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | 4
| Number of external reactor coolant loops | [15 empty] | : |  |  | 6 | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | 3
| Coolant type | [15 empty] | : |  |  | H2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | DH
Annual Production Results (2021)
Net Energy Production | [20 empty] | : | 3775.68 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 0.5 %
Energy Availability Factor (EAF) | [20 empty] | : | 89.83 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 1.89 %
Unit Capability Factor (UCF) | [20 empty] | : | 91.11 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 7 %
Load Factor (LF) | [20 empty] | : | 90.16 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 1.28 %
Operating Factor (OF) | [20 empty] | : | 91.63 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 733 hours
Equivalent non-electrical energy generated (NEG) | [20 empty] | : | 12.1 GW(e).h
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 358.09 |  | 323.41 |  |  |  |  | 356.26 |  | 339.51 | [8 empty] | 348.24 |  |  |  | 331.79 | [6 empty] | 337.72 |  | 142.63 |  |  |  |  | 179.31 |  |  | 354.09 |  |  | 345.46 | [9 empty] | 359.17 |  |  | 3775.68
EAF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 98.71 | [8 empty] | 97.72 |  |  |  | 96.20 | [6 empty] | 94.76 |  | 40.02 |  |  |  |  | 51.99 |  |  | 99.39 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 89.83
UCF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 98.71 | [8 empty] | 99.46 |  |  |  | 100.00 | [6 empty] | 98.40 |  | 40.99 |  |  |  |  | 57.15 |  |  | 99.39 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 91.11
LF [%] |  |  |  |  | 101.76 |  | 101.75 |  |  |  |  | 100.10 |  | 98.44 | [8 empty] | 97.72 |  |  |  | 96.20 | [6 empty] | 94.76 |  | 40.02 |  |  |  |  | 51.99 |  |  | 99.23 |  |  | 100.17 | [9 empty] | 100.78 |  |  | 90.16
OF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 41.40 |  |  |  |  | 58.75 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.63
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 1.29 | [8 empty] | 0.54 |  |  |  | 0.00 | [6 empty] | 1.60 |  | 0.00 |  |  |  |  | 2.39 |  |  | 0.61 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 0.50
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 1.29 | [8 empty] | 0.54 |  |  |  | 0.00 | [6 empty] | 1.60 |  | 0.00 |  |  |  |  | 18.81 |  |  | 0.61 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 1.89
PUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 59.01 |  |  |  |  | 24.04 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.00
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.74 |  |  |  | 3.80 | [6 empty] | 3.63 |  | 0.97 |  |  |  |  | 5.16 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.28
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 120754.28 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 1.12 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 88.33 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 1.22 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 88.68 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 10.1 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 89.39 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.35 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 89.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 1039.12 |  |  |  | 2936 |  |  |  |  | 425 | [10 empty] | 100.00 |  |  |  |  | 100.00 | [5 empty] | 101.77 |  |  | 100.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1988 |  |  |  | 3200.89 |  |  |  | 7564 |  |  |  |  | 415 | [10 empty] | 85.65 |  |  |  |  | 85.65 | [5 empty] | 87.81 |  |  | 86.11 |  |  |  |  | 3.21 |  | 2.84 | [8 empty] | 11.51 |  |  |  |  | 0.00
1989 |  |  |  | 3425.34 |  |  |  | 7974 |  |  |  |  | 415 | [10 empty] | 89.67 |  |  |  |  | 89.67 | [5 empty] | 94.22 |  |  | 91.03 |  |  |  |  | 1.27 |  | 1.15 | [8 empty] | 9.17 |  |  |  |  | 0.00
1990 |  |  |  | 3064.45 |  |  |  | 7253 |  |  |  |  | 435 | [10 empty] | 76.69 |  |  |  |  | 76.69 | [5 empty] | 80.42 |  |  | 82.80 |  |  |  |  | 4.04 |  | 3.23 | [8 empty] | 20.08 |  |  |  |  | 0.00
1991 |  |  |  | 3342.95 |  |  |  | 7787 |  |  |  |  | 410 | [10 empty] | 86.54 |  |  |  |  | 86.54 | [5 empty] | 93.08 |  |  | 88.89 |  |  |  |  | 3.48 |  | 3.12 | [8 empty] | 10.34 |  |  |  |  | 0.00
1992 |  |  |  | 3702.82 |  |  |  | 8082 |  |  |  |  | 433 | [10 empty] | 90.69 |  |  |  |  | 90.86 | [5 empty] | 97.35 |  |  | 92.01 |  |  |  |  | 0.41 |  | 0.37 | [8 empty] | 8.77 |  |  |  |  | 0.18
1993 |  |  |  | 3537.22 |  |  |  | 7767 |  |  |  |  | 430 | [10 empty] | 87.05 |  |  |  |  | 87.48 | [5 empty] | 93.91 |  |  | 88.66 |  |  |  |  | 2.37 |  | 2.12 | [8 empty] | 10.40 |  |  |  |  | 0.44
1994 |  |  |  | 2971.22 |  |  |  | 7019 |  |  |  |  | 433 | [10 empty] | 78.06 |  |  |  |  | 78.13 | [5 empty] | 78.33 |  |  | 80.13 |  |  |  |  | 1.51 |  | 1.20 | [8 empty] | 20.67 |  |  |  |  | 0.07
1995 |  |  |  | 3443.81 |  |  |  | 8049 |  |  |  |  | 433 | [10 empty] | 90.45 |  |  |  |  | 90.77 | [5 empty] | 90.79 |  |  | 91.88 |  |  |  |  | 0.89 |  | 0.82 | [8 empty] | 8.41 |  |  |  |  | 0.33
1996 |  |  |  | 3487.53 |  |  |  | 8087 |  |  |  |  | 433 | [10 empty] | 90.71 |  |  |  |  | 91.31 | [5 empty] | 91.69 |  |  | 92.07 |  |  |  |  | 1.06 |  | 0.97 | [8 empty] | 7.72 |  |  |  |  | 0.60
1997 |  |  |  | 3487.08 |  |  |  | 8098 |  |  |  |  | 433 | [10 empty] | 91.61 |  |  |  |  | 92.04 | [5 empty] | 91.93 |  |  | 92.44 |  |  |  |  | 0.74 |  | 0.69 | [8 empty] | 7.27 |  |  |  |  | 0.43
1998 |  |  |  | 3136.11 |  |  |  | 7389 |  |  |  |  | 433 | [10 empty] | 83.72 |  |  |  |  | 84.26 | [5 empty] | 82.68 |  |  | 84.35 |  |  |  |  | 1.18 |  | 1.00 | [8 empty] | 14.73 |  |  |  |  | 0.54
1999 |  |  |  | 3464.00 |  |  |  | 8046 |  |  |  |  | 433 | [10 empty] | 89.27 |  |  |  |  | 89.33 | [5 empty] | 91.32 |  |  | 91.85 |  |  |  |  | 3.95 |  | 3.68 | [8 empty] | 6.99 |  |  |  |  | 0.06
2000 |  |  |  | 3578.42 |  |  |  | 8116 |  |  |  |  | 433 | [10 empty] | 92.20 |  |  |  |  | 92.31 | [5 empty] | 94.08 |  |  | 92.40 |  |  |  |  | 0.24 |  | 0.22 | [8 empty] | 7.47 |  |  |  |  | 0.11
2001 |  |  |  | 3471.72 |  |  |  | 7916 |  |  |  |  | 444 | [10 empty] | 89.98 |  |  |  |  | 90.14 | [5 empty] | 89.26 |  |  | 90.37 |  |  |  |  | 1.63 |  | 1.50 | [8 empty] | 8.36 |  |  |  |  | 0.16
2002 |  |  |  | 3182.88 |  |  |  | 7287 |  |  |  |  | 444 | [10 empty] | 83.14 |  |  |  |  | 83.35 | [5 empty] | 81.83 |  |  | 83.18 |  |  |  |  | 0.94 |  | 0.79 | [8 empty] | 15.86 |  |  |  |  | 0.21
2003 |  |  |  | 3607.64 |  |  |  | 8119 |  |  |  |  | 444 | [10 empty] | 92.75 |  |  |  |  | 92.99 | [5 empty] | 92.75 |  |  | 92.68 |  |  |  |  | 0.03 |  | 0.62 | [8 empty] | 6.40 |  |  |  |  | 0.23
2004 |  |  |  | 3396.64 |  |  |  | 7878 |  |  |  |  | 444 | [10 empty] | 87.09 |  |  |  |  | 87.09 | [5 empty] | 87.09 |  |  | 89.69 |  |  |  |  | 0.30 |  | 0.48 | [8 empty] | 12.43 |  |  |  |  | 0.00
2005 |  |  |  | 3548.78 |  |  |  | 8046 |  |  |  |  | 444 | [10 empty] | 91.24 |  |  |  |  | 91.24 | [5 empty] | 91.24 |  |  | 91.85 |  |  |  |  | 1.10 |  | 1.08 | [8 empty] | 7.68 |  |  |  |  | 0.00
2006 |  |  |  | 3185.19 |  |  |  | 7196 |  |  |  |  | 444 | [10 empty] | 81.91 |  |  |  |  | 81.91 | [5 empty] | 81.89 |  |  | 82.15 |  |  |  |  | 0.55 |  | 1.67 | [8 empty] | 16.42 |  |  |  |  | 0.00
2007 |  |  |  | 3810.43 |  |  |  | 8078 |  |  |  |  | 473 | [10 empty] | 91.99 |  |  |  |  | 91.99 | [5 empty] | 91.96 |  |  | 92.21 |  |  |  |  | 0.05 |  | 0.04 | [8 empty] | 7.97 |  |  |  |  | 0.00
2008 |  |  |  | 3671.44 |  |  |  | 7854 |  |  |  |  | 473 | [10 empty] | 88.40 |  |  |  |  | 88.40 | [5 empty] | 88.37 |  |  | 89.41 |  |  |  |  | 0.51 |  | 1.70 | [8 empty] | 9.91 |  |  |  |  | 0.00
2009 |  |  |  | 3643.09 |  |  |  | 7715 |  |  |  |  | 473 | [10 empty] | 88.04 |  |  |  |  | 88.04 | [5 empty] | 87.92 |  |  | 88.07 |  |  |  |  | 0.33 |  | 1.89 | [8 empty] | 10.06 |  |  |  |  | 0.00
2010 |  |  |  | 3348.24 |  |  |  | 7091 |  |  |  |  | 473 | [10 empty] | 80.85 |  |  |  |  | 80.85 | [5 empty] | 80.81 |  |  | 80.95 |  |  |  |  | 2.92 |  | 2.43 | [8 empty] | 16.71 |  |  |  |  | 0.00
2011 |  |  |  | 3825.62 |  |  |  | 8103 |  |  |  |  | 473 | [10 empty] | 92.34 |  |  |  |  | 92.34 | [5 empty] | 92.33 |  |  | 92.50 |  |  |  |  | 0.42 |  | 0.39 | [8 empty] | 7.27 |  |  |  |  | 0.00
2012 |  |  |  | 3741.44 |  |  |  | 7961 |  |  |  |  | 473 | [10 empty] | 90.07 |  |  |  |  | 90.07 | [5 empty] | 90.05 |  |  | 90.63 |  |  |  |  | 2.03 |  | 1.86 | [8 empty] | 8.07 |  |  |  |  | 0.00
2013 |  |  |  | 3853.52 |  |  |  | 8076 |  |  |  |  | 473 | [10 empty] | 91.68 |  |  |  |  | 92.06 | [5 empty] | 93.00 |  |  | 92.19 |  |  |  |  | 0.32 |  | 0.29 | [8 empty] | 7.65 |  |  |  |  | 0.38
2014 |  |  |  | 3488.55 |  |  |  | 7430 |  |  |  |  | 473 | [10 empty] | 83.52 |  |  |  |  | 84.28 | [5 empty] | 84.19 |  |  | 84.82 |  |  |  |  | 0.65 |  | 0.55 | [8 empty] | 15.17 |  |  |  |  | 0.76
2015 |  |  |  | 3849.34 |  |  |  | 8174 |  |  |  |  | 473 | [10 empty] | 92.33 |  |  |  |  | 93.24 | [5 empty] | 92.90 |  |  | 93.31 |  |  |  |  | 0.04 |  | 0.04 | [8 empty] | 6.72 |  |  |  |  | 0.92
2016 |  |  |  | 3828.20 |  |  |  | 8153 |  |  |  |  | 473 | [10 empty] | 91.92 |  |  |  |  | 92.69 | [5 empty] | 92.14 |  |  | 92.82 |  |  |  |  | 0.04 |  | 0.04 | [8 empty] | 7.27 |  |  |  |  | 0.77
2017 |  |  |  | 3735.00 |  |  |  | 8064 |  |  |  |  | 473 | [10 empty] | 90.14 |  |  |  |  | 91.86 | [5 empty] | 90.14 |  |  | 92.05 |  |  |  |  | 0.17 |  | 0.16 | [8 empty] | 7.98 |  |  |  |  | 1.72
2018 |  |  |  | 4056.61 |  |  |  | 8722 |  |  |  |  | 473 | [10 empty] | 97.84 |  |  |  |  | 99.36 | [5 empty] | 97.90 |  |  | 99.57 |  |  |  |  | 0.64 |  | 0.64 | [8 empty] | 0.00 |  |  |  |  | 1.53
2019 |  |  |  | 3442.12 |  |  |  | 7315 |  |  |  |  | 473 | [10 empty] | 82.37 |  |  |  |  | 82.83 | [5 empty] | 83.07 |  |  | 83.50 |  |  |  |  | 0.79 |  | 0.94 | [8 empty] | 16.23 |  |  |  |  | 0.46
2020 |  |  |  | 3778.60 |  |  |  | 8053 |  |  |  |  | 473 | [10 empty] | 90.19 |  |  |  |  | 90.70 | [5 empty] | 90.94 |  |  | 91.68 |  |  |  |  | 1.49 |  | 1.76 | [8 empty] | 7.55 |  |  |  |  | 0.51
2021 |  |  |  | 3775.68 |  |  |  | 8027 |  |  |  |  | 479 | [10 empty] | 89.83 |  |  |  |  | 91.11 | [5 empty] | 90.16 |  |  | 91.63 |  |  |  |  | 0.50 |  | 1.89 | [8 empty] | 7.00 |  |  |  |  | 1.28
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2021 | [16 empty] | 1987 to 2021
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [27 empty] | 125 | [15 empty] | 63
C. |  | Inspection, maintenance or repair combined with refuelling | [22 empty] | 612 | [16 empty] | 844 |  |  |  | 16
D. |  | Inspection, maintenance or repair without refuelling | [39 empty] | 4
E. |  | Testing of plant systems or components | [39 empty] | 1
L. |  | Human factor related | [43 empty] | 2
Z. |  | Other | [39 empty] | 2 |  |  |  | 2
Subtotal | [24 empty] | 612 |  |  |  |  | 125 | [11 empty] | 851 |  |  |  | 83
Total | [24 empty] | 737 | [16 empty] | 934
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2021 | [16 empty] | 1987 to 2021
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [38 empty] | 11
15. |  |  | Reactor Cooling Systems | [21 empty] | 125 | [16 empty] | 14
16. |  |  | Steam generation systems | [38 empty] | 14
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [38 empty] | 1
31. |  |  | Turbine and auxiliaries | [38 empty] | 12
32. |  |  | Feedwater and Main Steam System | [38 empty] | 4
34. |  |  | Miscellaneous Systems | [38 empty] | 4
41. |  |  | Main Generator Systems | [38 empty] | 0
42. |  |  | Electrical Power Supply Systems | [38 empty] | 2
Total | [24 empty] | 125 | [16 empty] | 62
RUP revision during the year (2021) due to power uprate
RUP at the end of previous year : 473 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
March | [5 empty] | 479 |  |  |  |  | Improved measurement (<2%) | [14 empty] | Balance of plant | [13 empty] | Turbine modernization
Highlights (2021)
Operation at full power in base load mode