## AKADEMIK LOMONOSOV-1
2021 Operating Experience
RU-151 | [8 empty] | AKADEMIK LOMONOSOV-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / KLT-40S 'Floating' | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-04-15
Thermal power | [12 empty] | : |  |  | 150 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-12-19
Gross electrical power | [12 empty] | : |  |  | 35 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2020-05-22
Reference unit power (net) | [12 empty] | : |  |  | 32 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 316
| Fuel material | [13 empty] | : |  |  | Other | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 14.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 29 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 100 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 68700 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | NA
| Active core diameter [m] | [13 empty] | : |  |  | 1.220 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.43
| Active core height/length [m] | [13 empty] | : |  |  | 1.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 10.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 11 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 125.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 8.98 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.08 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 8.39 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.08 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.53 %
Load Factor (LF) | [18 empty] | : | 44.69 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 81.1 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1656 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 12.18 | 10.44 |  |  |  | 12.84 |  | 10.77 | [8 empty] | 10.89 |  |  | 13.96 | [6 empty] | 10.75 |  | 14.57 |  |  |  | 1.37 |  |  | 7.23 |  |  | 0.26 | [9 empty] | 20.01 |  |  | 125.26
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.60 |  |  |  | 15.86 |  |  | 100.00 |  |  | 3.64 | [9 empty] | 99.42 |  |  | 85.08
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.60 |  |  |  | 15.86 |  |  | 100.00 |  |  | 3.64 | [9 empty] | 99.42 |  |  | 85.08
LF [%] |  |  |  |  | 51.14 | 48.53 |  |  |  | 53.92 |  | 46.72 | [8 empty] | 45.76 |  |  | 60.59 | [6 empty] | 45.14 |  | 61.19 |  |  |  | 5.93 |  |  | 30.38 |  |  | 1.15 | [9 empty] | 84.06 |  |  | 44.69
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 98.25 |  |  |  | 15.83 |  |  | 53.90 |  |  | 3.61 | [9 empty] | 100.00 |  |  | 81.10
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.40 |  |  |  | 22.94 |  |  | 0.00 |  |  | 96.36 | [9 empty] | 0.58 |  |  | 8.98
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.40 |  |  |  | 4.72 |  |  | 0.00 |  |  | 96.36 | [9 empty] | 0.58 |  |  | 8.39
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 79.42 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.53
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 190.88 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.83 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.04 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.39 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.04 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.57 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 38.8 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.6 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2020 |  |  |  | 64.94 |  |  | 5138 |  |  |  | 32 | [10 empty] | 90.38 |  |  |  | 90.38 | [5 empty] | 28.76 |  |  | 71.63 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 9.34 |  |  |  |  | 0.00
2021 |  |  |  | 125.26 |  |  | 7104 |  |  |  | 32 | [10 empty] | 85.08 |  |  |  | 85.08 | [5 empty] | 44.69 |  |  | 81.10 |  |  |  | 8.98 |  | 8.39 | [8 empty] | 6.53 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2020 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 728 | [14 empty] | 460
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 572 | [14 empty] | 664
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 324 | [19 empty] | 205
L. |  | Human factor related | [24 empty] | 4 | [14 empty] | 10
Subtotal | [22 empty] | 572 |  |  |  | 732 | [6 empty] | 324 |  |  |  | 664 |  |  |  | 470 | [11 empty] | 205
Total | [22 empty] | 1628 | [14 empty] | 1339
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2020 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [19 empty] | 694 | [14 empty] | 347
31. |  |  | Turbine and auxiliaries | [34 empty] | 6
33. |  |  | Circulating Water System | [19 empty] | 34 | [14 empty] | 17
Total | [22 empty] | 728 | [14 empty] | 370
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the routine maintenance outage from 2021.09.01 to 2021.09.24. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## AKADEMIK LOMONOSOV-2
2021 Operating Experience
RU-152 | [8 empty] | AKADEMIK LOMONOSOV-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / KLT-40S 'Floating' | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-04-15
Thermal power | [12 empty] | : |  |  | 150 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-12-19
Gross electrical power | [12 empty] | : |  |  | 35 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2020-05-22
Reference unit power (net) | [12 empty] | : |  |  | 32 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 316
| Fuel material | [13 empty] | : |  |  | Other | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 14.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 29 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 100 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 68700 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | NA
| Active core diameter [m] | [13 empty] | : |  |  | 1.220 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.43
| Active core height/length [m] | [13 empty] | : |  |  | 1.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 10.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 11 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 50.36 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 7.93 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.11 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.51 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.11 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.39 %
Load Factor (LF) | [18 empty] | : | 17.97 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 25.86 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 6495 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.71 |  | 2.59 |  |  |  | 14.06 |  |  | 11.94 |  |  | 18.29 | [9 empty] | 2.77 |  |  | 50.36
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 36.58 |  |  |  | 90.02 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 21.26 |  |  | 87.11
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 36.58 |  |  |  | 90.02 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 21.26 |  |  | 87.11
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 2.98 |  | 10.89 |  |  |  | 61.03 |  |  | 50.15 |  |  | 79.38 | [9 empty] | 11.63 |  |  | 17.97
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 10.08 |  | 15.05 |  |  |  | 90.00 |  |  | 74.19 |  |  | 100.00 | [9 empty] | 21.24 |  |  | 25.86
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 9.98 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 78.74 |  |  | 7.93
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 9.98 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 78.74 |  |  | 7.51
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 63.42 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.39
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 103.92 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.36 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.5 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.65 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.5 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.85 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 17.23 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 30.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2020 |  |  |  | 51.44 |  |  | 3942 |  |  |  | 32 | [10 empty] | 77.36 |  |  |  | 77.36 | [5 empty] | 15.99 |  |  | 38.32 |  |  |  | 14.66 |  | 13.29 | [8 empty] | 9.35 |  |  |  |  | 0.00
2021 |  |  |  | 50.36 |  |  | 2265 |  |  |  | 32 | [10 empty] | 87.11 |  |  |  | 87.11 | [5 empty] | 17.97 |  |  | 25.86 |  |  |  | 7.93 |  | 7.51 | [8 empty] | 5.39 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2020 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 679 | [14 empty] | 868
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 511 | [14 empty] | 702
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 5307 | [19 empty] | 3352
L. |  | Human factor related | [39 empty] | 12
Subtotal | [22 empty] | 511 |  |  |  | 679 | [6 empty] | 5307 |  |  |  | 702 |  |  |  | 880 | [11 empty] | 3352
Total | [22 empty] | 6497 | [14 empty] | 4934
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2020 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [19 empty] | 585 | [14 empty] | 641
33. |  |  | Circulating Water System | [19 empty] | 82 | [14 empty] | 41
42. |  |  | Electrical Power Supply Systems | [19 empty] | 12 | [14 empty] | 6
Total | [22 empty] | 679 | [14 empty] | 688
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the routine maintenance outage from 2021.08.01 to 2021.08.20. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-1
2021 Operating Experience
RU-96 | [8 empty] | BALAKOVO-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-12-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-12-28
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-05-23
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7475.86 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.33 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.51 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.28 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.74 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.98 %
Load Factor (LF) | [18 empty] | : | 89.83 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.23 %
Operating Factor (OF) | [18 empty] | : | 85.98 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1228 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 5.73 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 719.65 | 689.78 |  |  |  | 764.04 |  | 729.67 | [8 empty] | 719.61 |  |  | 712.92 | [6 empty] | 735.91 |  | 731.58 |  |  |  | 736.06 |  |  | 731.66 |  |  | 107.02 | [9 empty] | 97.95 |  |  | 7475.86
EAF [%] |  |  |  |  | 98.64 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.50 | [6 empty] | 100.00 |  | 98.51 |  |  |  | 100.00 |  |  | 99.21 |  |  | 16.36 | [9 empty] | 14.43 |  |  | 85.51
UCF [%] |  |  |  |  | 98.64 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.50 | [6 empty] | 100.00 |  | 98.51 |  |  |  | 100.00 |  |  | 100.00 |  |  | 18.33 | [9 empty] | 14.43 |  |  | 85.74
LF [%] |  |  |  |  | 101.82 | 108.05 |  |  |  | 108.10 |  | 106.68 | [8 empty] | 101.81 |  |  | 104.23 | [6 empty] | 104.12 |  | 103.51 |  |  |  | 107.61 |  |  | 103.52 |  |  | 15.65 | [9 empty] | 13.86 |  |  | 89.83
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 98.92 |  |  |  | 100.00 |  |  | 100.00 |  |  | 18.19 | [9 empty] | 15.19 |  |  | 85.98
FLR [%] |  |  |  |  | 1.36 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.50 | [6 empty] | 0.00 |  | 1.49 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.33
UCL [%] |  |  |  |  | 1.36 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.50 | [6 empty] | 0.00 |  | 1.49 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.28
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 81.67 | [9 empty] | 85.57 |  |  | 13.98
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.79 |  |  | 1.97 | [9 empty] | 0.00 |  |  | 0.23
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 221204.59 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.41 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.53 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.3 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.26 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.44 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.02 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.73 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.6 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 4868.03 |  |  | 6082 |  |  |  | 950 | [10 empty] | 64.85 |  |  |  | 64.85 | [5 empty] | 64.46 |  |  | 69.51 |  |  |  | 17.62 |  | 13.87 | [8 empty] | 21.28 |  |  |  |  | 0.00
1987 |  |  |  | 4703.68 |  |  | 5302 |  |  |  | 1000 | [10 empty] | 57.40 |  |  |  | 57.40 | [5 empty] | 53.70 |  |  | 60.53 |  |  |  | 25.51 |  | 19.66 | [8 empty] | 22.95 |  |  |  |  | 0.00
1988 |  |  |  | 6476.87 |  |  | 7207 |  |  |  | 950 | [10 empty] | 80.93 |  |  |  | 80.93 | [5 empty] | 77.62 |  |  | 82.05 |  |  |  | 6.99 |  | 6.08 | [8 empty] | 12.99 |  |  |  |  | 0.00
1989 |  |  |  | 4473.90 |  |  | 5141 |  |  |  | 950 | [10 empty] | 56.34 |  |  |  | 56.37 | [5 empty] | 53.76 |  |  | 58.69 |  |  |  | 32.94 |  | 27.69 | [8 empty] | 15.95 |  |  |  |  | 0.03
1990 |  |  |  | 739.06 |  |  | 887 |  |  |  | 950 | [10 empty] | 9.09 |  |  |  | 9.09 | [5 empty] | 8.88 |  |  | 10.13 |  |  |  | 56.91 |  | 12.01 | [8 empty] | 78.90 |  |  |  |  | 0.00
1991 |  |  |  | 4951.60 |  |  | 5780 |  |  |  | 950 | [10 empty] | 59.85 |  |  |  | 60.19 | [5 empty] | 59.50 |  |  | 65.98 |  |  |  | 24.74 |  | 19.79 | [8 empty] | 20.02 |  |  |  |  | 0.35
1992 |  |  |  | 6352.28 |  |  | 7666 |  |  |  | 950 | [10 empty] | 76.31 |  |  |  | 76.38 | [5 empty] | 76.11 |  |  | 87.26 |  |  |  | 23.62 |  | 23.62 | [8 empty] | 0.00 |  |  |  |  | 0.07
1993 |  |  |  | 3326.09 |  |  | 4230 |  |  |  | 950 | [10 empty] | 39.88 |  |  |  | 46.10 | [5 empty] | 39.97 |  |  | 48.29 |  |  |  | 24.25 |  | 14.76 | [8 empty] | 39.14 |  |  |  |  | 6.22
1994 |  |  |  | 1759.54 |  |  | 2307 |  |  |  | 950 | [10 empty] | 77.30 |  |  |  | 77.30 | [5 empty] | 21.14 |  |  | 26.34 |  |  |  | 22.70 |  | 22.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 2017.98 |  |  | 4810 |  |  |  | 950 | [10 empty] | 28.57 |  |  |  | 28.57 | [5 empty] | 24.25 |  |  | 54.91 |  |  |  | 62.91 |  | 48.46 | [8 empty] | 22.97 |  |  |  |  | 0.00
1996 |  |  |  | 4872.54 |  |  | 5913 |  |  |  | 950 | [10 empty] | 59.00 |  |  |  | 86.47 | [5 empty] | 58.39 |  |  | 67.32 |  |  |  | 0.82 |  | 0.72 | [8 empty] | 12.81 |  |  |  |  | 27.47
1997 |  |  |  | 4728.99 |  |  | 5818 |  |  |  | 950 | [10 empty] | 57.24 |  |  |  | 60.37 | [5 empty] | 56.83 |  |  | 66.42 |  |  |  | 1.49 |  | 0.91 | [8 empty] | 38.72 |  |  |  |  | 3.13
1998 |  |  |  | 4329.83 |  |  | 5671 |  |  |  | 950 | [10 empty] | 52.16 |  |  |  | 55.84 | [5 empty] | 52.03 |  |  | 64.74 |  |  |  | 4.87 |  | 2.86 | [8 empty] | 41.30 |  |  |  |  | 3.68
1999 |  |  |  | 5141.31 |  |  | 6337 |  |  |  | 950 | [10 empty] | 62.09 |  |  |  | 65.56 | [5 empty] | 61.78 |  |  | 72.34 |  |  |  | 0.25 |  | 0.16 | [8 empty] | 34.28 |  |  |  |  | 3.47
2000 |  |  |  | 7247.37 |  |  | 7705 |  |  |  | 950 | [10 empty] | 86.49 |  |  |  | 87.54 | [5 empty] | 86.85 |  |  | 87.72 |  |  |  | 2.30 |  | 2.06 | [8 empty] | 10.40 |  |  |  |  | 1.05
2001 |  |  |  | 7407.90 |  |  | 8041 |  |  |  | 950 | [10 empty] | 88.19 |  |  |  | 91.57 | [5 empty] | 89.02 |  |  | 91.79 |  |  |  | 1.55 |  | 1.44 | [8 empty] | 6.98 |  |  |  |  | 3.38
2002 |  |  |  | 6785.73 |  |  | 7501 |  |  |  | 950 | [10 empty] | 80.48 |  |  |  | 86.52 | [5 empty] | 81.54 |  |  | 85.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.48 |  |  |  |  | 6.04
2003 |  |  |  | 7032.19 |  |  | 7460 |  |  |  | 950 | [10 empty] | 83.12 |  |  |  | 84.71 | [5 empty] | 84.50 |  |  | 85.16 |  |  |  | 0.75 |  | 0.64 | [8 empty] | 14.64 |  |  |  |  | 1.60
2004 |  |  |  | 6626.43 |  |  | 6901 |  |  |  | 950 | [10 empty] | 78.00 |  |  |  | 78.22 | [5 empty] | 79.41 |  |  | 78.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.78 |  |  |  |  | 0.22
2005 |  |  |  | 7312.72 |  |  | 7638 |  |  |  | 950 | [10 empty] | 86.24 |  |  |  | 86.58 | [5 empty] | 87.86 |  |  | 87.18 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 13.27 |  |  |  |  | 0.34
2006 |  |  |  | 7276.97 |  |  | 7517 |  |  |  | 950 | [10 empty] | 85.24 |  |  |  | 85.49 | [5 empty] | 87.44 |  |  | 85.81 |  |  |  | 0.70 |  | 0.60 | [8 empty] | 13.91 |  |  |  |  | 0.25
2007 |  |  |  | 7397.29 |  |  | 7731 |  |  |  | 950 | [10 empty] | 86.54 |  |  |  | 87.98 | [5 empty] | 88.89 |  |  | 88.25 |  |  |  | 0.39 |  | 0.34 | [8 empty] | 11.68 |  |  |  |  | 1.44
2008 |  |  |  | 6810.23 |  |  | 7283 |  |  |  | 950 | [10 empty] | 81.73 |  |  |  | 82.41 | [5 empty] | 81.61 |  |  | 82.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.59 |  |  |  |  | 0.68
2009 |  |  |  | 7948.45 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.61 |  |  |  | 99.74 | [5 empty] | 95.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.26 |  |  |  |  | 0.13
2010 |  |  |  | 6843.30 |  |  | 7069 |  |  |  | 950 | [10 empty] | 80.31 |  |  |  | 80.43 | [5 empty] | 82.23 |  |  | 80.70 |  |  |  | 0.00 |  | 7.09 | [8 empty] | 12.48 |  |  |  |  | 0.12
2011 |  |  |  | 7469.27 |  |  | 7573 |  |  |  | 950 | [10 empty] | 86.15 |  |  |  | 86.25 | [5 empty] | 89.76 |  |  | 86.46 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 13.73 |  |  |  |  | 0.10
2012 |  |  |  | 6322.13 |  |  | 6424 |  |  |  | 950 | [10 empty] | 72.90 |  |  |  | 73.02 | [5 empty] | 75.76 |  |  | 73.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.98 |  |  |  |  | 0.12
2013 |  |  |  | 8766.85 |  |  | 8726 |  |  |  | 950 | [10 empty] | 99.58 |  |  |  | 99.58 | [5 empty] | 105.35 |  |  | 99.61 |  |  |  | 0.42 |  | 0.42 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 7012.47 |  |  | 7077 |  |  |  | 950 | [10 empty] | 79.98 |  |  |  | 80.50 | [5 empty] | 84.25 |  |  | 80.78 |  |  |  | 0.09 |  | 0.07 | [8 empty] | 19.43 |  |  |  |  | 0.51
2015 |  |  |  | 7392.01 |  |  | 7481 |  |  |  | 950 | [10 empty] | 84.74 |  |  |  | 85.21 | [5 empty] | 88.82 |  |  | 85.40 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 14.77 |  |  |  |  | 0.47
2016 |  |  |  | 8880.23 |  |  | 8784 |  |  |  | 950 | [10 empty] | 99.94 |  |  |  | 99.94 | [5 empty] | 106.42 |  |  | 100.00 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7699.56 |  |  | 7887 |  |  |  | 950 | [10 empty] | 89.31 |  |  |  | 89.82 | [5 empty] | 92.52 |  |  | 90.03 |  |  |  | 1.64 |  | 1.50 | [8 empty] | 8.69 |  |  |  |  | 0.50
2018 |  |  |  | 6656.19 |  |  | 6737 |  |  |  | 950 | [10 empty] | 76.80 |  |  |  | 76.80 | [5 empty] | 79.98 |  |  | 76.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.20 |  |  |  |  | 0.00
2019 |  |  |  | 8783.41 |  |  | 8662 |  |  |  | 950 | [10 empty] | 98.87 |  |  |  | 98.87 | [5 empty] | 105.54 |  |  | 98.88 |  |  |  | 1.13 |  | 1.13 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7533.32 |  |  | 7842 |  |  |  | 950 | [10 empty] | 88.96 |  |  |  | 88.96 | [5 empty] | 90.28 |  |  | 89.28 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 10.87 |  |  |  |  | 0.00
2021 |  |  |  | 7475.86 |  |  | 7532 |  |  |  | 950 | [10 empty] | 85.51 |  |  |  | 85.74 | [5 empty] | 89.83 |  |  | 85.98 |  |  |  | 0.33 |  | 0.28 | [8 empty] | 13.98 |  |  |  |  | 0.23
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1986 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 304
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1220 | [14 empty] | 1243 |  |  |  | 11
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 257
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 135
L. |  | Human factor related | [39 empty] | 8
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 69
Z. |  | Other | [39 empty] | 22
Subtotal | [22 empty] | 1220 | [14 empty] | 1501 |  |  |  | 346 | [11 empty] | 205
Total | [22 empty] | 1220 | [14 empty] | 2052
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1986 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 2
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 94
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 43
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 25
35. |  |  | All other I&C Systems | [34 empty] | 8
41. |  |  | Main Generator Systems | [34 empty] | 83
42. |  |  | Electrical Power Supply Systems | [34 empty] | 20
Total | [37 empty] | 306
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-September, Novenber-Desember. Additional electricity generation amounted to 359510 MWh. The unit was in the overhaul outage from 2021.11.06 to 2021.12.27. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-2
2021 Operating Experience
RU-97 | [8 empty] | BALAKOVO-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-08-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-10-08
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-01-18
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 34 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 8043.86 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.15 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.25 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.75 %
Load Factor (LF) | [18 empty] | : | 96.66 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.11 %
Operating Factor (OF) | [18 empty] | : | 90.33 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 847 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 1.92 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 764.60 | 692.48 |  |  |  | 768.46 |  | 742.11 | [8 empty] | 757.14 |  |  | 719.87 | [6 empty] | 577.30 |  | 23.95 |  |  |  | 734.22 |  |  | 760.70 |  |  | 739.38 | [9 empty] | 763.67 |  |  | 8043.86
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 79.54 |  | 4.46 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.15
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 80.78 |  | 4.46 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.25
LF [%] |  |  |  |  | 108.18 | 108.47 |  |  |  | 108.72 |  | 108.50 | [8 empty] | 107.12 |  |  | 105.24 | [6 empty] | 81.68 |  | 3.39 |  |  |  | 107.34 |  |  | 107.63 |  |  | 108.10 | [9 empty] | 108.05 |  |  | 96.66
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 80.65 |  | 5.51 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.33
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 19.22 |  | 95.54 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.75
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.24 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.11
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 213207.86 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.1 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.05 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.83 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.37 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.79 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.95 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.32 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 5978.43 |  |  | 6928 |  |  |  | 950 | [10 empty] | 75.49 |  |  |  | 75.49 | [5 empty] | 70.63 |  |  | 77.66 |  |  |  | 6.59 |  | 5.33 | [8 empty] | 19.18 |  |  |  |  | 0.00
1989 |  |  |  | 6703.63 |  |  | 7626 |  |  |  | 950 | [10 empty] | 84.75 |  |  |  | 84.77 | [5 empty] | 80.55 |  |  | 87.05 |  |  |  | 9.33 |  | 8.72 | [8 empty] | 6.51 |  |  |  |  | 0.02
1990 |  |  |  | 5476.67 |  |  | 6165 |  |  |  | 950 | [10 empty] | 66.35 |  |  |  | 66.53 | [5 empty] | 65.81 |  |  | 70.38 |  |  |  | 15.71 |  | 12.40 | [8 empty] | 21.07 |  |  |  |  | 0.18
1991 |  |  |  | 4308.38 |  |  | 4845 |  |  |  | 950 | [10 empty] | 51.23 |  |  |  | 51.52 | [5 empty] | 51.77 |  |  | 55.31 |  |  |  | 10.81 |  | 6.25 | [8 empty] | 42.23 |  |  |  |  | 0.29
1992 |  |  |  | 5958.20 |  |  | 6601 |  |  |  | 950 | [10 empty] | 70.60 |  |  |  | 70.60 | [5 empty] | 71.39 |  |  | 75.14 |  |  |  | 9.39 |  | 7.32 | [8 empty] | 22.08 |  |  |  |  | 0.00
1993 |  |  |  | 3776.17 |  |  | 4147 |  |  |  | 950 | [10 empty] | 44.25 |  |  |  | 46.97 | [5 empty] | 45.38 |  |  | 47.34 |  |  |  | 38.44 |  | 29.33 | [8 empty] | 23.69 |  |  |  |  | 2.72
1994 |  |  |  | 4778.52 |  |  | 8020 |  |  |  | 950 | [10 empty] | 73.08 |  |  |  | 83.53 | [5 empty] | 57.42 |  |  | 91.55 |  |  |  | 12.39 |  | 11.81 | [8 empty] | 4.66 |  |  |  |  | 10.45
1995 |  |  |  | 2204.81 |  |  | 3261 |  |  |  | 950 | [10 empty] | 30.13 |  |  |  | 30.13 | [5 empty] | 26.49 |  |  | 37.23 |  |  |  | 27.40 |  | 11.37 | [8 empty] | 58.50 |  |  |  |  | 0.00
1996 |  |  |  | 2227.25 |  |  | 2604 |  |  |  | 950 | [10 empty] | 26.71 |  |  |  | 26.71 | [5 empty] | 26.69 |  |  | 29.64 |  |  |  | 66.37 |  | 52.71 | [8 empty] | 20.58 |  |  |  |  | 0.00
1997 |  |  |  | 4015.92 |  |  | 6158 |  |  |  | 950 | [10 empty] | 55.66 |  |  |  | 63.92 | [5 empty] | 48.26 |  |  | 70.30 |  |  |  | 27.93 |  | 24.77 | [8 empty] | 11.31 |  |  |  |  | 8.26
1998 |  |  |  | 3293.76 |  |  | 4984 |  |  |  | 950 | [10 empty] | 40.24 |  |  |  | 50.96 | [5 empty] | 39.58 |  |  | 56.89 |  |  |  | 0.11 |  | 0.05 | [8 empty] | 48.98 |  |  |  |  | 10.72
1999 |  |  |  | 2927.12 |  |  | 3942 |  |  |  | 950 | [10 empty] | 35.40 |  |  |  | 40.27 | [5 empty] | 35.17 |  |  | 45.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 59.73 |  |  |  |  | 4.87
2000 |  |  |  | 5730.07 |  |  | 7646 |  |  |  | 950 | [10 empty] | 68.89 |  |  |  | 83.21 | [5 empty] | 68.67 |  |  | 87.04 |  |  |  | 1.61 |  | 1.36 | [8 empty] | 15.43 |  |  |  |  | 14.32
2001 |  |  |  | 6678.82 |  |  | 7415 |  |  |  | 950 | [10 empty] | 79.86 |  |  |  | 83.90 | [5 empty] | 80.25 |  |  | 84.65 |  |  |  | 0.82 |  | 0.70 | [8 empty] | 15.40 |  |  |  |  | 4.05
2002 |  |  |  | 6756.53 |  |  | 7408 |  |  |  | 950 | [10 empty] | 80.40 |  |  |  | 84.43 | [5 empty] | 81.19 |  |  | 84.57 |  |  |  | 2.74 |  | 2.38 | [8 empty] | 13.19 |  |  |  |  | 4.03
2003 |  |  |  | 6171.76 |  |  | 6467 |  |  |  | 950 | [10 empty] | 72.70 |  |  |  | 73.99 | [5 empty] | 74.16 |  |  | 73.82 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 25.99 |  |  |  |  | 1.29
2004 |  |  |  | 7010.41 |  |  | 7514 |  |  |  | 950 | [10 empty] | 82.36 |  |  |  | 85.00 | [5 empty] | 84.01 |  |  | 85.54 |  |  |  | 0.72 |  | 0.62 | [8 empty] | 14.38 |  |  |  |  | 2.64
2005 |  |  |  | 6948.86 |  |  | 7688 |  |  |  | 950 | [10 empty] | 82.48 |  |  |  | 86.92 | [5 empty] | 83.49 |  |  | 87.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.08 |  |  |  |  | 4.44
2006 |  |  |  | 7237.48 |  |  | 7710 |  |  |  | 950 | [10 empty] | 84.59 |  |  |  | 87.38 | [5 empty] | 86.97 |  |  | 88.01 |  |  |  | 0.41 |  | 0.36 | [8 empty] | 12.26 |  |  |  |  | 2.79
2007 |  |  |  | 6657.18 |  |  | 7327 |  |  |  | 950 | [10 empty] | 78.71 |  |  |  | 83.46 | [5 empty] | 79.99 |  |  | 83.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.54 |  |  |  |  | 4.75
2008 |  |  |  | 7451.24 |  |  | 7750 |  |  |  | 950 | [10 empty] | 87.71 |  |  |  | 87.82 | [5 empty] | 89.29 |  |  | 88.23 |  |  |  | 1.21 |  | 1.07 | [8 empty] | 11.11 |  |  |  |  | 0.11
2009 |  |  |  | 7630.69 |  |  | 7797 |  |  |  | 950 | [10 empty] | 88.63 |  |  |  | 88.78 | [5 empty] | 91.69 |  |  | 89.01 |  |  |  | 0.28 |  | 0.25 | [8 empty] | 10.97 |  |  |  |  | 0.15
2010 |  |  |  | 8683.93 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.86 |  |  |  | 100.00 | [5 empty] | 104.35 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.14
2011 |  |  |  | 7288.41 |  |  | 7531 |  |  |  | 950 | [10 empty] | 85.42 |  |  |  | 85.76 | [5 empty] | 87.59 |  |  | 85.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.24 |  |  |  |  | 0.35
2012 |  |  |  | 7706.49 |  |  | 7829 |  |  |  | 950 | [10 empty] | 88.30 |  |  |  | 88.99 | [5 empty] | 92.35 |  |  | 89.13 |  |  |  | 1.35 |  | 1.22 | [8 empty] | 9.79 |  |  |  |  | 0.70
2013 |  |  |  | 8222.79 |  |  | 8509 |  |  |  | 950 | [10 empty] | 95.56 |  |  |  | 96.54 | [5 empty] | 98.81 |  |  | 97.13 |  |  |  | 0.45 |  | 0.44 | [8 empty] | 3.02 |  |  |  |  | 0.98
2014 |  |  |  | 6497.72 |  |  | 6672 |  |  |  | 950 | [10 empty] | 75.62 |  |  |  | 75.62 | [5 empty] | 78.07 |  |  | 76.16 |  |  |  | 10.92 |  | 9.27 | [8 empty] | 15.11 |  |  |  |  | 0.00
2015 |  |  |  | 6850.26 |  |  | 6845 |  |  |  | 950 | [10 empty] | 78.02 |  |  |  | 78.03 | [5 empty] | 82.32 |  |  | 78.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.97 |  |  |  |  | 0.01
2016 |  |  |  | 7922.42 |  |  | 7900 |  |  |  | 950 | [10 empty] | 89.79 |  |  |  | 89.79 | [5 empty] | 94.94 |  |  | 89.94 |  |  |  | 10.21 |  | 10.21 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6880.73 |  |  | 6972 |  |  |  | 950 | [10 empty] | 79.07 |  |  |  | 79.07 | [5 empty] | 82.68 |  |  | 79.59 |  |  |  | 0.40 |  | 0.31 | [8 empty] | 20.61 |  |  |  |  | 0.00
2018 |  |  |  | 7858.92 |  |  | 7874 |  |  |  | 950 | [10 empty] | 89.46 |  |  |  | 89.82 | [5 empty] | 94.44 |  |  | 89.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.18 |  |  |  |  | 0.36
2019 |  |  |  | 8867.45 |  |  | 8760 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 106.55 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7538.45 |  |  | 7590 |  |  |  | 950 | [10 empty] | 86.37 |  |  |  | 86.37 | [5 empty] | 90.34 |  |  | 86.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.63 |  |  |  |  | 0.00
2021 |  |  |  | 8043.86 |  |  | 7913 |  |  |  | 950 | [10 empty] | 90.15 |  |  |  | 90.25 | [5 empty] | 96.66 |  |  | 90.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.75 |  |  |  |  | 0.11
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1988 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 337
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 865 | [14 empty] | 1383 |  |  |  | 81
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 88
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 3
Z. |  | Other | [39 empty] | 13
Subtotal | [22 empty] | 865 | [14 empty] | 1471 |  |  |  | 434 | [11 empty] | 6
Total | [22 empty] | 865 | [14 empty] | 1911
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1988 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 235
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
35. |  |  | All other I&C Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 67
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 337
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-December. Additional electricity generation amounted to 474807 MWh. The unit was in the intermediate outage from 2021.07.26 to 2021.08.31. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-3
2021 Operating Experience
RU-98 | [8 empty] | BALAKOVO-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-11-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-12-25
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-08
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7559.14 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.26 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.09 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.91 %
Load Factor (LF) | [18 empty] | : | 90.83 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.82 %
Operating Factor (OF) | [18 empty] | : | 87.15 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1126 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 5.51 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 730.12 | 689.97 |  |  |  | 764.37 |  | 739.07 | [8 empty] | 704.81 |  |  | 719.03 | [6 empty] | 723.34 |  | 388.81 |  |  |  | 0.00 |  |  | 597.24 |  |  | 738.44 | [9 empty] | 763.96 |  |  | 7559.14
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.36 |  | 55.58 |  |  |  | 0.00 |  |  | 80.09 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.26
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 64.65 |  |  |  | 0.00 |  |  | 80.09 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.09
LF [%] |  |  |  |  | 103.30 | 108.08 |  |  |  | 108.14 |  | 108.05 | [8 empty] | 99.72 |  |  | 105.12 | [6 empty] | 102.34 |  | 55.01 |  |  |  | 0.00 |  |  | 84.50 |  |  | 107.96 | [9 empty] | 108.09 |  |  | 90.83
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 64.52 |  |  |  | 0.00 |  |  | 80.91 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.15
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 35.35 |  |  |  | 100.00 |  |  | 19.91 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.91
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.64 |  | 9.07 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.82
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 211147.58 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.93 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.47 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.39 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.36 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.25 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.98 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.88 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.61 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 6621.41 |  |  | 7792 |  |  |  | 950 | [10 empty] | 88.36 |  |  |  | 88.36 | [5 empty] | 87.44 |  |  | 91.12 |  |  |  | 6.11 |  | 5.75 | [8 empty] | 5.90 |  |  |  |  | 0.00
1990 |  |  |  | 5718.71 |  |  | 6696 |  |  |  | 950 | [10 empty] | 67.84 |  |  |  | 68.04 | [5 empty] | 68.72 |  |  | 76.44 |  |  |  | 13.53 |  | 10.65 | [8 empty] | 21.31 |  |  |  |  | 0.19
1991 |  |  |  | 5403.35 |  |  | 6124 |  |  |  | 950 | [10 empty] | 64.23 |  |  |  | 67.13 | [5 empty] | 64.93 |  |  | 69.91 |  |  |  | 12.68 |  | 9.75 | [8 empty] | 23.13 |  |  |  |  | 2.90
1992 |  |  |  | 5545.43 |  |  | 6202 |  |  |  | 950 | [10 empty] | 64.77 |  |  |  | 66.42 | [5 empty] | 66.45 |  |  | 70.60 |  |  |  | 17.40 |  | 14.00 | [8 empty] | 19.59 |  |  |  |  | 1.65
1993 |  |  |  | 4378.64 |  |  | 5461 |  |  |  | 950 | [10 empty] | 52.73 |  |  |  | 61.63 | [5 empty] | 52.62 |  |  | 62.34 |  |  |  | 13.51 |  | 9.63 | [8 empty] | 28.74 |  |  |  |  | 8.90
1994 |  |  |  | 3340.14 |  |  | 5389 |  |  |  | 950 | [10 empty] | 70.66 |  |  |  | 70.69 | [5 empty] | 40.14 |  |  | 61.52 |  |  |  | 10.93 |  | 8.68 | [8 empty] | 20.64 |  |  |  |  | 0.03
1995 |  |  |  | 2674.65 |  |  | 5511 |  |  |  | 950 | [10 empty] | 47.52 |  |  |  | 53.12 | [5 empty] | 32.14 |  |  | 62.91 |  |  |  | 20.77 |  | 13.93 | [8 empty] | 32.95 |  |  |  |  | 5.60
1996 |  |  |  | 5315.40 |  |  | 7085 |  |  |  | 950 | [10 empty] | 64.26 |  |  |  | 75.94 | [5 empty] | 63.70 |  |  | 80.66 |  |  |  | 1.93 |  | 1.49 | [8 empty] | 22.57 |  |  |  |  | 11.68
1997 |  |  |  | 2058.79 |  |  | 3395 |  |  |  | 950 | [10 empty] | 25.29 |  |  |  | 38.78 | [5 empty] | 24.74 |  |  | 38.76 |  |  |  | 0.58 |  | 0.22 | [8 empty] | 60.99 |  |  |  |  | 13.49
1998 |  |  |  | 5348.52 |  |  | 7136 |  |  |  | 950 | [10 empty] | 64.42 |  |  |  | 73.01 | [5 empty] | 64.27 |  |  | 81.46 |  |  |  | 0.09 |  | 0.06 | [8 empty] | 26.93 |  |  |  |  | 8.59
1999 |  |  |  | 5457.98 |  |  | 6552 |  |  |  | 950 | [10 empty] | 65.61 |  |  |  | 71.98 | [5 empty] | 65.59 |  |  | 74.79 |  |  |  | 0.16 |  | 0.12 | [8 empty] | 27.91 |  |  |  |  | 6.37
2000 |  |  |  | 6482.85 |  |  | 7327 |  |  |  | 950 | [10 empty] | 77.18 |  |  |  | 82.00 | [5 empty] | 77.69 |  |  | 83.41 |  |  |  | 1.10 |  | 0.91 | [8 empty] | 17.09 |  |  |  |  | 4.82
2001 |  |  |  | 6050.74 |  |  | 6927 |  |  |  | 950 | [10 empty] | 72.10 |  |  |  | 78.65 | [5 empty] | 72.71 |  |  | 79.08 |  |  |  | 0.15 |  | 0.12 | [8 empty] | 21.23 |  |  |  |  | 6.55
2002 |  |  |  | 6926.31 |  |  | 7478 |  |  |  | 950 | [10 empty] | 81.99 |  |  |  | 85.35 | [5 empty] | 83.23 |  |  | 85.37 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 14.64 |  |  |  |  | 3.36
2003 |  |  |  | 7016.14 |  |  | 7471 |  |  |  | 950 | [10 empty] | 83.19 |  |  |  | 85.05 | [5 empty] | 84.31 |  |  | 85.29 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 14.86 |  |  |  |  | 1.86
2004 |  |  |  | 7227.76 |  |  | 7607 |  |  |  | 950 | [10 empty] | 85.13 |  |  |  | 86.38 | [5 empty] | 86.61 |  |  | 86.60 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 13.56 |  |  |  |  | 1.25
2005 |  |  |  | 6244.44 |  |  | 7060 |  |  |  | 950 | [10 empty] | 74.50 |  |  |  | 79.90 | [5 empty] | 75.04 |  |  | 80.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.10 |  |  |  |  | 5.40
2006 |  |  |  | 7741.84 |  |  | 8354 |  |  |  | 950 | [10 empty] | 91.38 |  |  |  | 95.30 | [5 empty] | 93.03 |  |  | 95.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.70 |  |  |  |  | 3.92
2007 |  |  |  | 7407.10 |  |  | 8050 |  |  |  | 950 | [10 empty] | 87.59 |  |  |  | 91.82 | [5 empty] | 89.01 |  |  | 91.89 |  |  |  | 0.68 |  | 0.63 | [8 empty] | 7.56 |  |  |  |  | 4.23
2008 |  |  |  | 7384.34 |  |  | 7693 |  |  |  | 950 | [10 empty] | 86.99 |  |  |  | 87.15 | [5 empty] | 88.49 |  |  | 87.58 |  |  |  | 1.09 |  | 0.96 | [8 empty] | 11.89 |  |  |  |  | 0.16
2009 |  |  |  | 6932.73 |  |  | 7276 |  |  |  | 950 | [10 empty] | 82.56 |  |  |  | 82.63 | [5 empty] | 83.31 |  |  | 83.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.37 |  |  |  |  | 0.08
2010 |  |  |  | 7649.62 |  |  | 7710 |  |  |  | 950 | [10 empty] | 87.13 |  |  |  | 87.75 | [5 empty] | 91.92 |  |  | 88.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.25 |  |  |  |  | 0.63
2011 |  |  |  | 8579.15 |  |  | 8627 |  |  |  | 950 | [10 empty] | 98.26 |  |  |  | 98.26 | [5 empty] | 103.10 |  |  | 98.49 |  |  |  | 1.61 |  | 1.61 | [8 empty] | 0.13 |  |  |  |  | 0.00
2012 |  |  |  | 7716.23 |  |  | 7854 |  |  |  | 950 | [10 empty] | 89.32 |  |  |  | 89.34 | [5 empty] | 92.47 |  |  | 89.41 |  |  |  | 0.59 |  | 0.53 | [8 empty] | 10.13 |  |  |  |  | 0.02
2013 |  |  |  | 7378.17 |  |  | 7481 |  |  |  | 950 | [10 empty] | 84.53 |  |  |  | 84.94 | [5 empty] | 88.66 |  |  | 85.40 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 14.97 |  |  |  |  | 0.41
2014 |  |  |  | 7746.92 |  |  | 7827 |  |  |  | 950 | [10 empty] | 88.55 |  |  |  | 88.82 | [5 empty] | 93.08 |  |  | 89.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.18 |  |  |  |  | 0.26
2015 |  |  |  | 8250.27 |  |  | 8415 |  |  |  | 950 | [10 empty] | 95.78 |  |  |  | 95.78 | [5 empty] | 99.14 |  |  | 96.06 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 4.16 |  |  |  |  | 0.00
2016 |  |  |  | 7307.38 |  |  | 7331 |  |  |  | 950 | [10 empty] | 82.96 |  |  |  | 83.26 | [5 empty] | 87.57 |  |  | 83.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.74 |  |  |  |  | 0.30
2017 |  |  |  | 8653.43 |  |  | 8727 |  |  |  | 950 | [10 empty] | 99.16 |  |  |  | 99.48 | [5 empty] | 103.98 |  |  | 99.62 |  |  |  | 0.41 |  | 0.40 | [8 empty] | 0.11 |  |  |  |  | 0.32
2018 |  |  |  | 7167.75 |  |  | 7163 |  |  |  | 950 | [10 empty] | 81.59 |  |  |  | 81.71 | [5 empty] | 86.13 |  |  | 81.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.29 |  |  |  |  | 0.12
2019 |  |  |  | 4983.36 |  |  | 4979 |  |  |  | 950 | [10 empty] | 56.33 |  |  |  | 56.84 | [5 empty] | 59.88 |  |  | 56.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 43.16 |  |  |  |  | 0.51
2020 |  |  |  | 6845.49 |  |  | 6880 |  |  |  | 950 | [10 empty] | 78.34 |  |  |  | 78.34 | [5 empty] | 82.03 |  |  | 78.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.66 |  |  |  |  | 0.00
2021 |  |  |  | 7559.14 |  |  | 7634 |  |  |  | 950 | [10 empty] | 86.26 |  |  |  | 87.09 | [5 empty] | 90.83 |  |  | 87.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.91 |  |  |  |  | 0.82
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1989 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 72
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1126 | [14 empty] | 1387 |  |  |  | 20
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 164
E. |  | Testing of plant systems or components | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 45
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 1126 | [14 empty] | 1551 |  |  |  | 100 | [11 empty] | 46
Total | [22 empty] | 1126 | [14 empty] | 1697
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1989 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 23
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 8
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [37 empty] | 75
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-July, October-Desember. Additional electricity generation amounted to 399885 MWh. The unit was in the overhaul outage from 2021.08.21 to 2021.10.06. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-4
2021 Operating Experience
RU-99 | [8 empty] | BALAKOVO-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-04-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-04-11
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-12-22
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 28 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 8516.23 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.64 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.64 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.36 %
Load Factor (LF) | [18 empty] | : | 102.33 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 94.7 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 464 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 5.72 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 275.40 | 704.77 |  |  |  | 776.92 |  | 751.01 | [8 empty] | 760.66 |  |  | 725.99 | [6 empty] | 741.70 |  | 748.15 |  |  |  | 743.14 |  |  | 768.79 |  |  | 746.58 | [9 empty] | 773.12 |  |  | 8516.23
EAF [%] |  |  |  |  | 36.87 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.64
UCF [%] |  |  |  |  | 36.87 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.64
LF [%] |  |  |  |  | 38.96 | 110.40 |  |  |  | 109.92 |  | 109.80 | [8 empty] | 107.62 |  |  | 106.14 | [6 empty] | 104.94 |  | 105.85 |  |  |  | 108.65 |  |  | 108.77 |  |  | 109.15 | [9 empty] | 109.38 |  |  | 102.33
OF [%] |  |  |  |  | 37.63 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.70
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 63.13 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.36
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 196840.19 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.36 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.01 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.16 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.1 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.84 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 3.09 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.3 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 3676.28 |  |  | 5206 |  |  |  | 950 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 3828.53 |  |  | 4604 |  |  |  | 950 | [10 empty] | 48.45 |  |  |  | 69.54 | [5 empty] | 46.00 |  |  | 52.56 |  |  |  | 1.58 |  | 1.12 | [8 empty] | 29.34 |  |  |  |  | 21.09
1995 |  |  |  | 5609.99 |  |  | 8760 |  |  |  | 950 | [10 empty] | 86.46 |  |  |  | 88.72 | [5 empty] | 67.41 |  |  | 100.00 |  |  |  | 11.28 |  | 11.28 | [8 empty] | 0.00 |  |  |  |  | 2.26
1996 |  |  |  | 4545.55 |  |  | 6652 |  |  |  | 950 | [10 empty] | 55.47 |  |  |  | 59.85 | [5 empty] | 54.47 |  |  | 75.73 |  |  |  | 13.90 |  | 9.66 | [8 empty] | 30.49 |  |  |  |  | 4.39
1997 |  |  |  | 4637.72 |  |  | 6637 |  |  |  | 950 | [10 empty] | 59.64 |  |  |  | 71.29 | [5 empty] | 55.73 |  |  | 75.76 |  |  |  | 0.16 |  | 0.11 | [8 empty] | 28.60 |  |  |  |  | 11.65
1998 |  |  |  | 5042.49 |  |  | 6936 |  |  |  | 950 | [10 empty] | 60.89 |  |  |  | 71.31 | [5 empty] | 60.59 |  |  | 79.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.69 |  |  |  |  | 10.42
1999 |  |  |  | 5803.91 |  |  | 7268 |  |  |  | 950 | [10 empty] | 69.59 |  |  |  | 77.55 | [5 empty] | 69.74 |  |  | 82.97 |  |  |  | 0.37 |  | 0.29 | [8 empty] | 22.17 |  |  |  |  | 7.95
2000 |  |  |  | 6665.85 |  |  | 7216 |  |  |  | 950 | [10 empty] | 78.95 |  |  |  | 80.96 | [5 empty] | 79.88 |  |  | 82.15 |  |  |  | 0.78 |  | 0.63 | [8 empty] | 18.40 |  |  |  |  | 2.01
2001 |  |  |  | 6578.09 |  |  | 7354 |  |  |  | 950 | [10 empty] | 78.30 |  |  |  | 83.91 | [5 empty] | 79.04 |  |  | 83.95 |  |  |  | 0.47 |  | 0.40 | [8 empty] | 15.69 |  |  |  |  | 5.61
2002 |  |  |  | 6292.92 |  |  | 6723 |  |  |  | 950 | [10 empty] | 72.80 |  |  |  | 77.28 | [5 empty] | 75.62 |  |  | 76.75 |  |  |  | 0.20 |  | 0.16 | [8 empty] | 22.57 |  |  |  |  | 4.47
2003 |  |  |  | 7223.84 |  |  | 7541 |  |  |  | 950 | [10 empty] | 84.64 |  |  |  | 85.84 | [5 empty] | 86.80 |  |  | 86.08 |  |  |  | 0.50 |  | 0.43 | [8 empty] | 13.73 |  |  |  |  | 1.20
2004 |  |  |  | 7022.94 |  |  | 7540 |  |  |  | 950 | [10 empty] | 82.51 |  |  |  | 85.37 | [5 empty] | 84.16 |  |  | 85.84 |  |  |  | 0.45 |  | 0.39 | [8 empty] | 14.24 |  |  |  |  | 2.86
2005 |  |  |  | 6938.28 |  |  | 7699 |  |  |  | 950 | [10 empty] | 82.14 |  |  |  | 87.62 | [5 empty] | 83.36 |  |  | 87.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.38 |  |  |  |  | 5.48
2006 |  |  |  | 6805.35 |  |  | 7230 |  |  |  | 950 | [10 empty] | 79.61 |  |  |  | 82.20 | [5 empty] | 81.78 |  |  | 82.53 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 17.74 |  |  |  |  | 2.58
2007 |  |  |  | 7153.35 |  |  | 7787 |  |  |  | 950 | [10 empty] | 84.70 |  |  |  | 88.53 | [5 empty] | 85.96 |  |  | 88.89 |  |  |  | 0.40 |  | 0.36 | [8 empty] | 11.11 |  |  |  |  | 3.83
2008 |  |  |  | 8330.42 |  |  | 8779 |  |  |  | 950 | [10 empty] | 99.71 |  |  |  | 99.73 | [5 empty] | 99.83 |  |  | 99.94 |  |  |  | 0.14 |  | 0.14 | [8 empty] | 0.13 |  |  |  |  | 0.02
2009 |  |  |  | 7409.95 |  |  | 7727 |  |  |  | 950 | [10 empty] | 87.83 |  |  |  | 87.83 | [5 empty] | 89.02 |  |  | 88.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.17 |  |  |  |  | 0.00
2010 |  |  |  | 7199.69 |  |  | 7168 |  |  |  | 950 | [10 empty] | 81.35 |  |  |  | 81.35 | [5 empty] | 86.51 |  |  | 81.83 |  |  |  | 2.02 |  | 1.68 | [8 empty] | 16.97 |  |  |  |  | 0.00
2011 |  |  |  | 7625.20 |  |  | 7619 |  |  |  | 950 | [10 empty] | 86.42 |  |  |  | 86.42 | [5 empty] | 91.64 |  |  | 86.98 |  |  |  | 2.50 |  | 2.22 | [8 empty] | 11.36 |  |  |  |  | 0.00
2012 |  |  |  | 8517.84 |  |  | 8608 |  |  |  | 950 | [10 empty] | 97.72 |  |  |  | 97.72 | [5 empty] | 102.07 |  |  | 98.00 |  |  |  | 2.08 |  | 2.07 | [8 empty] | 0.20 |  |  |  |  | 0.00
2013 |  |  |  | 7847.25 |  |  | 7847 |  |  |  | 950 | [10 empty] | 89.13 |  |  |  | 89.13 | [5 empty] | 94.30 |  |  | 89.58 |  |  |  | 0.61 |  | 0.54 | [8 empty] | 10.33 |  |  |  |  | 0.00
2014 |  |  |  | 7204.52 |  |  | 7173 |  |  |  | 950 | [10 empty] | 81.27 |  |  |  | 81.36 | [5 empty] | 86.56 |  |  | 81.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.64 |  |  |  |  | 0.09
2015 |  |  |  | 8800.05 |  |  | 8757 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.74 |  |  | 99.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 8006.24 |  |  | 8045 |  |  |  | 950 | [10 empty] | 91.07 |  |  |  | 91.58 | [5 empty] | 95.94 |  |  | 91.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.42 |  |  |  |  | 0.52
2017 |  |  |  | 7336.59 |  |  | 7386 |  |  |  | 950 | [10 empty] | 83.99 |  |  |  | 84.24 | [5 empty] | 88.16 |  |  | 84.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.76 |  |  |  |  | 0.25
2018 |  |  |  | 8777.02 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 105.47 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.00
2019 |  |  |  | 6075.81 |  |  | 5952 |  |  |  | 950 | [10 empty] | 67.76 |  |  |  | 67.76 | [5 empty] | 73.01 |  |  | 67.95 |  |  |  | 1.15 |  | 0.88 | [8 empty] | 31.36 |  |  |  |  | 0.00
2020 |  |  |  | 7368.35 |  |  | 7307 |  |  |  | 950 | [10 empty] | 83.11 |  |  |  | 83.11 | [5 empty] | 88.30 |  |  | 83.19 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 16.87 |  |  |  |  | 0.00
2021 |  |  |  | 8516.23 |  |  | 8296 |  |  |  | 950 | [10 empty] | 94.64 |  |  |  | 94.64 | [5 empty] | 102.33 |  |  | 94.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.36 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1993 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 27
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 464 | [14 empty] | 1173
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 16
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 12
L. |  | Human factor related | [39 empty] | 0
Z. |  | Other | [51 empty] | 60
Subtotal | [22 empty] | 464 | [14 empty] | 1189 |  |  |  | 27 | [11 empty] | 72
Total | [22 empty] | 464 | [14 empty] | 1288
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1993 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 1
16. |  |  | Steam generation systems | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 27
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-Desember. Additional electricity generation amounted to 583364 MWh. The unit was in the overhaul outage from 2020.10.31 to 2021.01.20. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BELOYARSK-3
2021 Operating Experience
RU-21 | [8 empty] | BELOYARSK-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | FBR / BN-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1969-01-01
Thermal power | [12 empty] | : |  |  | 1470 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-04-08
Gross electrical power | [12 empty] | : |  |  | 600 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-11-01
Reference unit power (net) | [12 empty] | : |  |  | 560 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 8.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 550
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 5 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 3
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 100000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.05 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 13
| Active core height/length [m] | [13 empty] | : |  |  | 1.03 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 369 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 38 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 19 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | Na | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 4152.25 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.1 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.23 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.63 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.23 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.14 %
Load Factor (LF) | [18 empty] | : | 84.64 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 85.43 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1276 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 118.45 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 428.49 | 369.24 |  |  |  | 246.45 |  | 420.68 | [8 empty] | 385.31 |  |  | 418.26 | [6 empty] | 382.05 |  | 0.00 |  |  |  | 256.63 |  |  | 396.76 |  |  | 417.30 | [9 empty] | 431.07 |  |  | 4152.25
EAF [%] |  |  |  |  | 100.00 | 95.86 |  |  |  | 57.95 |  | 100.00 | [8 empty] | 90.08 |  |  | 100.00 | [6 empty] | 89.81 |  | 0.04 |  |  |  | 62.87 |  |  | 92.53 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.23
UCF [%] |  |  |  |  | 100.00 | 95.86 |  |  |  | 57.95 |  | 100.00 | [8 empty] | 90.08 |  |  | 100.00 | [6 empty] | 89.81 |  | 0.04 |  |  |  | 62.87 |  |  | 92.53 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.23
LF [%] |  |  |  |  | 102.84 | 98.12 |  |  |  | 59.15 |  | 104.34 | [8 empty] | 92.48 |  |  | 103.74 | [6 empty] | 91.70 |  | 0.00 |  |  |  | 63.65 |  |  | 95.23 |  |  | 103.50 | [9 empty] | 103.46 |  |  | 84.64
OF [%] |  |  |  |  | 100.00 | 98.66 |  |  |  | 59.54 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 91.26 |  | 0.00 |  |  |  | 78.19 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.43
FLR [%] |  |  |  |  | 0.00 | 1.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.92 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 16.94 |  |  | 7.47 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.10
UCL [%] |  |  |  |  | 0.00 | 1.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.92 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 12.82 |  |  | 7.47 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.63
PUF [%] |  |  |  |  | 0.00 | 2.81 |  |  |  | 42.05 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 10.19 |  | 99.96 |  |  |  | 24.31 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.14
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 153283.28 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.67 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.89 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.98 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.41 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.61 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.37 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.51 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.94 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | Data not provided
1982 |  |  |  | 2771.00 |  |  | 5555 |  |  |  | 560 | [10 empty] | 59.25 |  |  |  | 59.25 | [5 empty] | 56.49 |  |  | 63.41 |  |  |  | 11.50 |  | 7.70 | [8 empty] | 33.05 |  |  |  |  | 0.00
1983 |  |  |  | 3545.21 |  |  | 6737 |  |  |  | 560 | [10 empty] | 72.72 |  |  |  | 73.35 | [5 empty] | 72.27 |  |  | 76.91 |  |  |  | 3.71 |  | 2.82 | [8 empty] | 23.83 |  |  |  |  | 0.63
1984 |  |  |  | 3584.11 |  |  | 6848 |  |  |  | 560 | [10 empty] | 73.29 |  |  |  | 73.29 | [5 empty] | 72.86 |  |  | 77.96 |  |  |  | 5.70 |  | 4.43 | [8 empty] | 22.28 |  |  |  |  | 0.00
1985 |  |  |  | 3561.83 |  |  | 6544 |  |  |  | 560 | [10 empty] | 72.85 |  |  |  | 72.85 | [5 empty] | 72.61 |  |  | 74.70 |  |  |  | 2.47 |  | 1.85 | [8 empty] | 25.30 |  |  |  |  | 0.00
1986 |  |  |  | 3600.73 |  |  | 6818 |  |  |  | 560 | [10 empty] | 73.82 |  |  |  | 74.28 | [5 empty] | 73.40 |  |  | 77.83 |  |  |  | 4.78 |  | 3.73 | [8 empty] | 21.99 |  |  |  |  | 0.46
1987 |  |  |  | 3894.99 |  |  | 6714 |  |  |  | 600 | [10 empty] | 75.93 |  |  |  | 75.93 | [5 empty] | 74.11 |  |  | 76.64 |  |  |  | 2.64 |  | 2.05 | [8 empty] | 22.02 |  |  |  |  | 0.00
1988 |  |  |  | 3762.19 |  |  | 6810 |  |  |  | 560 | [10 empty] | 76.97 |  |  |  | 76.97 | [5 empty] | 76.48 |  |  | 77.53 |  |  |  | 0.38 |  | 0.30 | [8 empty] | 22.74 |  |  |  |  | 0.00
1989 |  |  |  | 3694.43 |  |  | 6800 |  |  |  | 560 | [10 empty] | 76.95 |  |  |  | 76.95 | [5 empty] | 75.31 |  |  | 77.63 |  |  |  | 1.21 |  | 0.94 | [8 empty] | 22.10 |  |  |  |  | 0.00
1990 |  |  |  | 3198.00 |  |  | 6627 |  |  |  | 560 | [10 empty] | 65.85 |  |  |  | 66.65 | [5 empty] | 65.19 |  |  | 75.65 |  |  |  | 11.05 |  | 8.28 | [8 empty] | 25.07 |  |  |  |  | 0.79
1991 |  |  |  | 3394.00 |  |  | 6631 |  |  |  | 560 | [10 empty] | 63.57 |  |  |  | 63.57 | [5 empty] | 69.19 |  |  | 75.70 |  |  |  | 13.75 |  | 10.14 | [8 empty] | 26.29 |  |  |  |  | 0.00
1992 |  |  |  | 4094.97 |  |  | 7449 |  |  |  | 560 | [10 empty] | 82.82 |  |  |  | 83.06 | [5 empty] | 83.26 |  |  | 84.81 |  |  |  | 0.34 |  | 0.28 | [8 empty] | 16.66 |  |  |  |  | 0.24
1993 |  |  |  | 3914.92 |  |  | 7065 |  |  |  | 560 | [10 empty] | 79.49 |  |  |  | 79.57 | [5 empty] | 79.81 |  |  | 80.65 |  |  |  | 7.18 |  | 6.15 | [8 empty] | 14.28 |  |  |  |  | 0.07
1994 |  |  |  | 3810.67 |  |  | 6977 |  |  |  | 560 | [10 empty] | 78.78 |  |  |  | 78.92 | [5 empty] | 77.68 |  |  | 79.65 |  |  |  | 0.90 |  | 0.71 | [8 empty] | 20.37 |  |  |  |  | 0.14
1995 |  |  |  | 3413.27 |  |  | 6953 |  |  |  | 560 | [10 empty] | 70.70 |  |  |  | 72.28 | [5 empty] | 69.58 |  |  | 79.37 |  |  |  | 9.36 |  | 7.46 | [8 empty] | 20.26 |  |  |  |  | 1.57
1996 |  |  |  | 3722.33 |  |  | 7010 |  |  |  | 560 | [10 empty] | 76.32 |  |  |  | 78.07 | [5 empty] | 75.67 |  |  | 79.80 |  |  |  | 1.72 |  | 1.37 | [8 empty] | 20.57 |  |  |  |  | 1.75
1997 |  |  |  | 3545.80 |  |  | 6596 |  |  |  | 560 | [10 empty] | 72.97 |  |  |  | 74.58 | [5 empty] | 72.28 |  |  | 75.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.42 |  |  |  |  | 1.61
1998 |  |  |  | 2335.33 |  |  | 4385 |  |  |  | 560 | [10 empty] | 47.67 |  |  |  | 49.23 | [5 empty] | 47.61 |  |  | 50.06 |  |  |  | 38.80 |  | 31.21 | [8 empty] | 19.55 |  |  |  |  | 1.56
1999 |  |  |  | 3720.99 |  |  | 6972 |  |  |  | 560 | [10 empty] | 76.18 |  |  |  | 77.96 | [5 empty] | 75.85 |  |  | 79.59 |  |  |  | 4.10 |  | 3.34 | [8 empty] | 18.71 |  |  |  |  | 1.78
2000 |  |  |  | 3565.82 |  |  | 6820 |  |  |  | 560 | [10 empty] | 72.49 |  |  |  | 75.49 | [5 empty] | 72.49 |  |  | 77.64 |  |  |  | 0.31 |  | 0.23 | [8 empty] | 24.27 |  |  |  |  | 3.00
2001 |  |  |  | 3891.10 |  |  | 7214 |  |  |  | 560 | [10 empty] | 79.90 |  |  |  | 80.72 | [5 empty] | 79.32 |  |  | 82.35 |  |  |  | 1.24 |  | 1.01 | [8 empty] | 18.27 |  |  |  |  | 0.82
2002 |  |  |  | 3774.40 |  |  | 7069 |  |  |  | 560 | [10 empty] | 77.30 |  |  |  | 79.34 | [5 empty] | 76.94 |  |  | 80.70 |  |  |  | 2.14 |  | 1.74 | [8 empty] | 18.93 |  |  |  |  | 2.04
2003 |  |  |  | 3693.28 |  |  | 6836 |  |  |  | 560 | [10 empty] | 75.74 |  |  |  | 76.81 | [5 empty] | 75.29 |  |  | 78.04 |  |  |  | 0.91 |  | 0.71 | [8 empty] | 22.48 |  |  |  |  | 1.07
2004 |  |  |  | 3927.64 |  |  | 7185 |  |  |  | 560 | [10 empty] | 80.02 |  |  |  | 80.81 | [5 empty] | 79.85 |  |  | 81.80 |  |  |  | 0.78 |  | 0.64 | [8 empty] | 18.56 |  |  |  |  | 0.78
2005 |  |  |  | 3802.75 |  |  | 6977 |  |  |  | 560 | [10 empty] | 77.76 |  |  |  | 78.77 | [5 empty] | 77.52 |  |  | 79.65 |  |  |  | 0.09 |  | 0.07 | [8 empty] | 21.16 |  |  |  |  | 1.02
2006 |  |  |  | 3844.94 |  |  | 7001 |  |  |  | 560 | [10 empty] | 78.38 |  |  |  | 79.02 | [5 empty] | 78.38 |  |  | 79.92 |  |  |  | 0.36 |  | 0.29 | [8 empty] | 20.69 |  |  |  |  | 0.65
2007 |  |  |  | 3798.42 |  |  | 7089 |  |  |  | 560 | [10 empty] | 77.52 |  |  |  | 77.80 | [5 empty] | 77.43 |  |  | 80.92 |  |  |  | 0.46 |  | 0.36 | [8 empty] | 21.84 |  |  |  |  | 0.28
2008 |  |  |  | 3781.03 |  |  | 6918 |  |  |  | 560 | [10 empty] | 76.85 |  |  |  | 76.95 | [5 empty] | 76.87 |  |  | 78.76 |  |  |  | 0.47 |  | 0.36 | [8 empty] | 22.69 |  |  |  |  | 0.10
2009 |  |  |  | 3736.60 |  |  | 6734 |  |  |  | 560 | [10 empty] | 75.58 |  |  |  | 75.61 | [5 empty] | 76.17 |  |  | 76.87 |  |  |  | 0.49 |  | 0.37 | [8 empty] | 24.01 |  |  |  |  | 0.03
2010 |  |  |  | 3669.75 |  |  | 6541 |  |  |  | 560 | [10 empty] | 73.51 |  |  |  | 73.56 | [5 empty] | 74.81 |  |  | 74.67 |  |  |  | 0.73 |  | 0.54 | [8 empty] | 25.90 |  |  |  |  | 0.05
2011 |  |  |  | 3968.73 |  |  | 7141 |  |  |  | 560 | [10 empty] | 79.17 |  |  |  | 79.17 | [5 empty] | 80.91 |  |  | 81.53 |  |  |  | 0.71 |  | 0.57 | [8 empty] | 20.26 |  |  |  |  | 0.00
2012 |  |  |  | 3975.50 |  |  | 7250 |  |  |  | 560 | [10 empty] | 78.84 |  |  |  | 78.84 | [5 empty] | 80.82 |  |  | 82.54 |  |  |  | 1.62 |  | 2.69 | [8 empty] | 18.47 |  |  |  |  | 0.00
2013 |  |  |  | 3841.06 |  |  | 7398 |  |  |  | 560 | [10 empty] | 77.62 |  |  |  | 77.80 | [5 empty] | 78.30 |  |  | 84.45 |  |  |  | 7.27 |  | 6.10 | [8 empty] | 16.11 |  |  |  |  | 0.18
2014 |  |  |  | 4222.91 |  |  | 7455 |  |  |  | 560 | [10 empty] | 83.77 |  |  |  | 83.77 | [5 empty] | 86.07 |  |  | 85.09 |  |  |  | 0.58 |  | 0.49 | [8 empty] | 15.75 |  |  |  |  | 0.00
2015 |  |  |  | 4220.16 |  |  | 7414 |  |  |  | 560 | [10 empty] | 83.78 |  |  |  | 83.78 | [5 empty] | 86.03 |  |  | 84.63 |  |  |  | 0.39 |  | 0.33 | [8 empty] | 15.89 |  |  |  |  | 0.00
2016 |  |  |  | 4307.17 |  |  | 7517 |  |  |  | 560 | [10 empty] | 84.66 |  |  |  | 84.66 | [5 empty] | 87.56 |  |  | 85.58 |  |  |  | 0.41 |  | 0.35 | [8 empty] | 14.98 |  |  |  |  | 0.00
2017 |  |  |  | 4323.23 |  |  | 7548 |  |  |  | 560 | [10 empty] | 85.36 |  |  |  | 85.36 | [5 empty] | 88.13 |  |  | 86.16 |  |  |  | 0.32 |  | 0.27 | [8 empty] | 14.36 |  |  |  |  | 0.00
2018 |  |  |  | 3809.52 |  |  | 6911 |  |  |  | 560 | [10 empty] | 75.28 |  |  |  | 75.28 | [5 empty] | 77.66 |  |  | 78.89 |  |  |  | 3.23 |  | 3.38 | [8 empty] | 21.34 |  |  |  |  | 0.00
2019 |  |  |  | 4184.26 |  |  | 7453 |  |  |  | 560 | [10 empty] | 82.22 |  |  |  | 82.22 | [5 empty] | 85.30 |  |  | 85.08 |  |  |  | 1.95 |  | 2.15 | [8 empty] | 15.63 |  |  |  |  | 0.00
2020 |  |  |  | 4169.76 |  |  | 7338 |  |  |  | 560 | [10 empty] | 81.60 |  |  |  | 81.60 | [5 empty] | 84.77 |  |  | 83.54 |  |  |  | 1.47 |  | 1.22 | [8 empty] | 17.19 |  |  |  |  | 0.00
2021 |  |  |  | 4152.25 |  |  | 7484 |  |  |  | 560 | [10 empty] | 82.23 |  |  |  | 82.23 | [5 empty] | 84.64 |  |  | 85.43 |  |  |  | 3.10 |  | 2.63 | [8 empty] | 15.14 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1981 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 118
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1330 | [14 empty] | 1271
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 420 |  |  |  | 6
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 1
T. |  | Heat supply (on-site to support next unit or desalination and off-site distribution) | [51 empty] | 0
Subtotal | [22 empty] | 1330 | [14 empty] | 1691 |  |  |  | 126 | [11 empty] | 3
Total | [22 empty] | 1330 | [14 empty] | 1820
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1981 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 2
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 28
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 67
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 121
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-July, September-December. Additional electricity generation amounted to 120555 MWh. The unit was in the routine maintenance outage from 2021.02.28 to 2021.03.13 and the intermediate outage from 2021.07.29 to 2021.09.07. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BELOYARSK-4
2021 Operating Experience
RU-116 | [8 empty] | BELOYARSK-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | FBR / BN-800 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2006-07-18
Thermal power | [12 empty] | : |  |  | 2100 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-12-10
Gross electrical power | [12 empty] | : |  |  | 885 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-10-31
Reference unit power (net) | [12 empty] | : |  |  | 820 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 6 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 1.65
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 547
| Fuel material | [13 empty] | : |  |  | UO2/PuO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 6 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.56 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 13
| Active core height/length [m] | [13 empty] | : |  |  | 0.88 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 565 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 38 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 16 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | NA | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 3087.27 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 28.75 %
Energy Availability Factor (EAF) | [18 empty] | : | 43.31 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 17.95 %
Unit Capability Factor (UCF) | [18 empty] | : | 44.47 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 37.58 %
Load Factor (LF) | [18 empty] | : | 42.98 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.15 %
Operating Factor (OF) | [18 empty] | : | 46.22 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4711 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 124.14 | 155.59 |  |  |  | 456.65 |  | 582.86 | [8 empty] | 61.21 |  |  | 31.46 | [6 empty] | 569.72 |  | 584.70 |  |  |  | 520.95 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3087.27
EAF [%] |  |  |  |  | 21.25 | 29.28 |  |  |  | 74.81 |  | 97.79 | [8 empty] | 11.13 |  |  | 7.43 | [6 empty] | 93.30 |  | 95.70 |  |  |  | 88.20 |  |  | 0.06 |  |  | 0.06 | [9 empty] | 0.06 |  |  | 43.31
UCF [%] |  |  |  |  | 21.41 | 29.62 |  |  |  | 77.44 |  | 99.34 | [8 empty] | 11.73 |  |  | 7.88 | [6 empty] | 96.04 |  | 98.31 |  |  |  | 90.90 |  |  | 0.06 |  |  | 0.06 | [9 empty] | 0.06 |  |  | 44.47
LF [%] |  |  |  |  | 20.35 | 28.24 |  |  |  | 74.85 |  | 98.72 | [8 empty] | 10.03 |  |  | 5.33 | [6 empty] | 93.38 |  | 95.84 |  |  |  | 88.24 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 42.98
OF [%] |  |  |  |  | 24.33 | 31.25 |  |  |  | 78.36 |  | 100.00 | [8 empty] | 11.56 |  |  | 11.94 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 96.53 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 46.22
FLR [%] |  |  |  |  | 4.64 | 0.00 |  |  |  | 22.56 |  | 0.66 | [8 empty] | 88.27 |  |  | 92.12 | [6 empty] | 3.96 |  | 1.69 |  |  |  | 4.35 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 28.75
UCL [%] |  |  |  |  | 1.04 | 0.00 |  |  |  | 22.56 |  | 0.66 | [8 empty] | 88.27 |  |  | 92.12 | [6 empty] | 3.96 |  | 1.69 |  |  |  | 4.13 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 17.95
PUF [%] |  |  |  |  | 77.55 | 70.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 4.97 |  |  | 99.94 |  |  | 99.94 | [9 empty] | 99.94 |  |  | 37.58
XUF [%] |  |  |  |  | 0.16 | 0.34 |  |  |  | 2.63 |  | 1.54 | [8 empty] | 0.60 |  |  | 0.45 | [6 empty] | 2.75 |  | 2.61 |  |  |  | 2.70 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.15
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 26996.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.63 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 65.86 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.6 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 67.01 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 26.39 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.94 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.15 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 69.03 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 3456.96 |  |  | 5453 |  |  |  | 820 | [10 empty] | 81.92 |  |  |  | 81.92 | [5 empty] | 81.96 |  |  | 96.45 |  |  |  | 18.08 |  | 18.08 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 5165.75 |  |  | 6551 |  |  |  | 820 | [10 empty] | 71.81 |  |  |  | 73.11 | [5 empty] | 71.91 |  |  | 74.78 |  |  |  | 1.71 |  | 4.59 | [8 empty] | 22.30 |  |  |  |  | 1.29
2018 |  |  |  | 4408.98 |  |  | 5680 |  |  |  | 820 | [10 empty] | 61.25 |  |  |  | 62.29 | [5 empty] | 61.38 |  |  | 64.84 |  |  |  | 5.45 |  | 3.59 | [8 empty] | 34.12 |  |  |  |  | 1.04
2019 |  |  |  | 4909.25 |  |  | 6196 |  |  |  | 820 | [10 empty] | 68.26 |  |  |  | 69.65 | [5 empty] | 68.34 |  |  | 70.73 |  |  |  | 3.35 |  | 4.61 | [8 empty] | 25.74 |  |  |  |  | 1.39
2020 |  |  |  | 5934.14 |  |  | 7373 |  |  |  | 820 | [10 empty] | 81.92 |  |  |  | 82.98 | [5 empty] | 82.39 |  |  | 83.94 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 16.64 |  |  |  |  | 1.06
2021 |  |  |  | 3087.27 |  |  | 4049 |  |  |  | 820 | [10 empty] | 43.31 |  |  |  | 44.47 | [5 empty] | 42.98 |  |  | 46.22 |  |  |  | 28.75 |  | 17.95 | [8 empty] | 37.58 |  |  |  |  | 1.15
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2016 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 1453 | [14 empty] | 444
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1022 | [14 empty] | 1768
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2233 | [14 empty] | 514
Subtotal | [22 empty] | 3255 |  |  |  | 1453 | [10 empty] | 2282 |  |  |  | 444
Total | [22 empty] | 4708 | [14 empty] | 2726
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2016 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 32
14. |  |  | Safety Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [19 empty] | 1240 | [14 empty] | 207
31. |  |  | Turbine and auxiliaries | [19 empty] | 161 | [14 empty] | 76
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
41. |  |  | Main Generator Systems | [34 empty] | 39
42. |  |  | Electrical Power Supply Systems | [19 empty] | 52 | [14 empty] | 9
Total | [22 empty] | 1453 | [14 empty] | 384
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the intermediate outage from 2021.01.08 to 2021.02.20 and in the routine maintenance outage from 2021.09.10 to 2022.01.01. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BILIBINO-2
2021 Operating Experience
RU-142 | [8 empty] | BILIBINO-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / EGP-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-01-01
Thermal power | [12 empty] | : |  |  | 62 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-12-30
Gross electrical power | [12 empty] | : |  |  | 12 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-02-01
Reference unit power (net) | [12 empty] | : |  |  | 11 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 280
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 3000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 273 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 28.85 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.1 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.1 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 14.9 %
Load Factor (LF) | [18 empty] | : | 29.94 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 80.49 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1709 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 20.98 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 3.16 | 3.13 |  |  |  | 5.28 |  | 4.65 | [8 empty] | 3.70 |  |  | 0.43 | [6 empty] | 0.00 |  | 0.25 |  |  |  | 2.59 |  |  | 2.50 |  |  | 2.08 | [9 empty] | 1.08 |  |  | 28.85
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.90 | [8 empty] | 100.00 |  |  | 80.91 | [6 empty] | 4.55 |  | 38.58 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.10
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.90 | [8 empty] | 100.00 |  |  | 80.91 | [6 empty] | 4.55 |  | 38.58 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.10
LF [%] |  |  |  |  | 38.58 | 42.28 |  |  |  | 64.50 |  | 58.71 | [8 empty] | 45.23 |  |  | 5.48 | [6 empty] | 0.00 |  | 3.02 |  |  |  | 32.75 |  |  | 30.56 |  |  | 26.26 | [9 empty] | 13.23 |  |  | 29.94
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.86 | [8 empty] | 100.00 |  |  | 32.64 | [6 empty] | 0.00 |  | 35.62 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.49
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.10 | [8 empty] | 0.00 |  |  | 19.09 | [6 empty] | 95.45 |  | 61.42 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 14.90
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 2275.3 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.81 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.95 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.63 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.87 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 51.8 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 8.68 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.41 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 63.76 |  |  | 7365 |  |  |  | 10 | [10 empty] | 88.97 |  |  |  | 94.67 | [5 empty] | 78.14 |  |  | 90.14 |  |  |  | 1.31 |  | 1.26 | [8 empty] | 4.07 |  |  |  |  | 5.70
1976 |  |  |  | 66.10 |  |  | 7901 |  |  |  | 10 | [10 empty] | 83.67 |  |  |  | 89.44 | [5 empty] | 75.25 |  |  | 89.95 |  |  |  | 1.10 |  | 0.99 | [8 empty] | 9.56 |  |  |  |  | 5.77
1977 |  |  |  | 57.04 |  |  | 7865 |  |  |  | 10 | [10 empty] | 81.34 |  |  |  | 90.50 | [5 empty] | 65.12 |  |  | 89.78 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 9.46 |  |  |  |  | 9.16
1978 |  |  |  | 60.61 |  |  | 7929 |  |  |  | 10 | [10 empty] | 94.81 |  |  |  | 94.81 | [5 empty] | 69.19 |  |  | 90.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.19 |  |  |  |  | 0.00
1979 |  |  |  | 69.85 |  |  | 8170 |  |  |  | 10 | [10 empty] | 88.17 |  |  |  | 92.93 | [5 empty] | 79.74 |  |  | 93.26 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 7.00 |  |  |  |  | 4.76
1980 |  |  |  | 44.05 |  |  | 5666 |  |  |  | 10 | [10 empty] | 59.82 |  |  |  | 62.73 | [5 empty] | 50.15 |  |  | 64.50 |  |  |  | 35.24 |  | 34.13 | [8 empty] | 3.14 |  |  |  |  | 2.91
1981 |  |  |  | 41.36 |  |  | 6520 |  |  |  | 10 | [10 empty] | 70.39 |  |  |  | 73.15 | [5 empty] | 47.21 |  |  | 74.43 |  |  |  | 4.87 |  | 3.74 | [8 empty] | 23.11 |  |  |  |  | 2.76
1982 |  |  |  | 63.92 |  |  | 7028 |  |  |  | 10 | [10 empty] | 79.24 |  |  |  | 79.24 | [5 empty] | 72.97 |  |  | 80.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.76 |  |  |  |  | 0.00
1983 |  |  |  | 73.76 |  |  | 7880 |  |  |  | 10 | [10 empty] | 86.92 |  |  |  | 90.06 | [5 empty] | 84.20 |  |  | 89.95 |  |  |  | 1.96 |  | 1.80 | [8 empty] | 8.14 |  |  |  |  | 3.14
1984 |  |  |  | 77.63 |  |  | 7891 |  |  |  | 10 | [10 empty] | 88.51 |  |  |  | 89.32 | [5 empty] | 88.38 |  |  | 89.83 |  |  |  | 0.29 |  | 0.26 | [8 empty] | 10.41 |  |  |  |  | 0.81
1985 |  |  |  | 78.00 |  |  | 7940 |  |  |  | 10 | [10 empty] | 88.57 |  |  |  | 90.29 | [5 empty] | 89.04 |  |  | 90.64 |  |  |  | 0.46 |  | 0.42 | [8 empty] | 9.29 |  |  |  |  | 1.73
1986 |  |  |  | 76.34 |  |  | 7679 |  |  |  | 10 | [10 empty] | 84.69 |  |  |  | 87.04 | [5 empty] | 87.14 |  |  | 87.66 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 12.93 |  |  |  |  | 2.35
1987 |  |  |  | 88.42 |  |  | 7794 |  |  |  | 12 | [10 empty] | 89.10 |  |  |  | 89.10 | [5 empty] | 84.12 |  |  | 88.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.90 |  |  |  |  | 0.00
1988 |  |  |  | 75.07 |  |  | 7927 |  |  |  | 11 | [10 empty] | 90.84 |  |  |  | 90.84 | [5 empty] | 77.69 |  |  | 90.24 |  |  |  | 0.64 |  | 0.58 | [8 empty] | 8.57 |  |  |  |  | 0.00
1989 |  |  |  | 74.81 |  |  | 7943 |  |  |  | 11 | [10 empty] | 91.38 |  |  |  | 91.38 | [5 empty] | 77.64 |  |  | 90.67 |  |  |  | 0.34 |  | 0.31 | [8 empty] | 8.31 |  |  |  |  | 0.00
1990 |  |  |  | 72.62 |  |  | 7274 |  |  |  | 11 | [10 empty] | 84.57 |  |  |  | 84.57 | [5 empty] | 75.36 |  |  | 83.04 |  |  |  | 3.23 |  | 2.83 | [8 empty] | 12.61 |  |  |  |  | 0.00
1991 |  |  |  | 57.83 |  |  | 4821 |  |  |  | 11 | [10 empty] | 64.92 |  |  |  | 64.92 | [5 empty] | 60.02 |  |  | 55.03 |  |  |  | 20.10 |  | 16.33 | [8 empty] | 18.74 |  |  |  |  | 0.00
1992 |  |  |  | 68.24 |  |  | 7857 |  |  |  | 11 | [10 empty] | 89.91 |  |  |  | 89.91 | [5 empty] | 70.63 |  |  | 89.45 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 9.99 |  |  |  |  | 0.00
1993 |  |  |  | 52.45 |  |  | 7072 |  |  |  | 11 | [10 empty] | 62.17 |  |  |  | 81.86 | [5 empty] | 54.43 |  |  | 80.73 |  |  |  | 1.69 |  | 1.41 | [8 empty] | 16.73 |  |  |  |  | 19.69
1994 |  |  |  | 47.83 |  |  | 6763 |  |  |  | 11 | [10 empty] | 77.31 |  |  |  | 78.74 | [5 empty] | 49.64 |  |  | 77.20 |  |  |  | 2.81 |  | 2.28 | [8 empty] | 18.98 |  |  |  |  | 1.43
1995 |  |  |  | 45.45 |  |  | 8677 |  |  |  | 11 | [10 empty] | 97.19 |  |  |  | 99.19 | [5 empty] | 47.16 |  |  | 99.05 |  |  |  | 0.69 |  | 0.69 | [8 empty] | 0.12 |  |  |  |  | 2.00
1996 |  |  |  | 16.83 |  |  | 2894 |  |  |  | 11 | [10 empty] | 33.47 |  |  |  | 33.47 | [5 empty] | 17.42 |  |  | 32.95 |  |  |  | 2.84 |  | 0.98 | [8 empty] | 65.55 |  |  |  |  | 0.00
1997 |  |  |  | 44.11 |  |  | 8050 |  |  |  | 11 | [10 empty] | 87.71 |  |  |  | 92.70 | [5 empty] | 45.78 |  |  | 91.89 |  |  |  | 0.36 |  | 0.34 | [8 empty] | 6.97 |  |  |  |  | 4.99
1998 |  |  |  | 18.16 |  |  | 3727 |  |  |  | 11 | [10 empty] | 23.30 |  |  |  | 42.91 | [5 empty] | 18.85 |  |  | 42.55 |  |  |  | 0.07 |  | 0.03 | [8 empty] | 57.06 |  |  |  |  | 19.61
1999 |  |  |  | 54.16 |  |  | 7355 |  |  |  | 11 | [10 empty] | 64.09 |  |  |  | 84.73 | [5 empty] | 56.21 |  |  | 83.96 |  |  |  | 0.45 |  | 0.39 | [8 empty] | 14.88 |  |  |  |  | 20.64
2000 |  |  |  | 48.46 |  |  | 6656 |  |  |  | 11 | [10 empty] | 56.35 |  |  |  | 78.15 | [5 empty] | 50.15 |  |  | 75.77 |  |  |  | 0.22 |  | 0.17 | [8 empty] | 21.68 |  |  |  |  | 21.80
2001 |  |  |  | 56.71 |  |  | 7439 |  |  |  | 11 | [10 empty] | 65.81 |  |  |  | 85.23 | [5 empty] | 58.86 |  |  | 84.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.77 |  |  |  |  | 19.42
2002 |  |  |  | 30.02 |  |  | 5744 |  |  |  | 11 | [10 empty] | 38.39 |  |  |  | 66.40 | [5 empty] | 31.16 |  |  | 65.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.60 |  |  |  |  | 28.01
2003 |  |  |  | 33.25 |  |  | 7162 |  |  |  | 11 | [10 empty] | 44.48 |  |  |  | 82.22 | [5 empty] | 34.51 |  |  | 81.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.78 |  |  |  |  | 37.74
2004 |  |  |  | 17.92 |  |  | 5851 |  |  |  | 11 | [10 empty] | 27.23 |  |  |  | 70.29 | [5 empty] | 18.55 |  |  | 66.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.71 |  |  |  |  | 43.05
2005 |  |  |  | 25.33 |  |  | 7351 |  |  |  | 11 | [10 empty] | 38.19 |  |  |  | 84.94 | [5 empty] | 26.29 |  |  | 83.92 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 15.03 |  |  |  |  | 46.76
2006 |  |  |  | 20.34 |  |  | 7248 |  |  |  | 11 | [10 empty] | 32.71 |  |  |  | 84.22 | [5 empty] | 21.11 |  |  | 82.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.78 |  |  |  |  | 51.52
2007 |  |  |  | 26.38 |  |  | 7478 |  |  |  | 11 | [10 empty] | 39.89 |  |  |  | 86.70 | [5 empty] | 27.37 |  |  | 85.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.30 |  |  |  |  | 46.80
2008 |  |  |  | 30.27 |  |  | 6490 |  |  |  | 11 | [10 empty] | 78.78 |  |  |  | 78.78 | [5 empty] | 31.33 |  |  | 73.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.22 |  |  |  |  | 0.00
2009 |  |  |  | 42.44 |  |  | 7388 |  |  |  | 11 | [10 empty] | 86.12 |  |  |  | 86.12 | [5 empty] | 44.04 |  |  | 84.34 |  |  |  | 0.89 |  | 0.78 | [8 empty] | 13.10 |  |  |  |  | 0.00
2010 |  |  |  | 48.08 |  |  | 7627 |  |  |  | 11 | [10 empty] | 88.09 |  |  |  | 88.09 | [5 empty] | 49.89 |  |  | 87.07 |  |  |  | 0.75 |  | 0.66 | [8 empty] | 11.25 |  |  |  |  | 0.00
2011 |  |  |  | 21.71 |  |  | 4977 |  |  |  | 11 | [10 empty] | 84.38 |  |  |  | 84.38 | [5 empty] | 22.53 |  |  | 56.82 |  |  |  | 1.45 |  | 1.24 | [8 empty] | 14.38 |  |  |  |  | 0.00
2012 |  |  |  | 28.27 |  |  | 5461 |  |  |  | 11 | [10 empty] | 72.73 |  |  |  | 72.73 | [5 empty] | 29.26 |  |  | 62.17 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 27.24 |  |  |  |  | 0.00
2013 |  |  |  | 43.12 |  |  | 6904 |  |  |  | 11 | [10 empty] | 85.84 |  |  |  | 85.84 | [5 empty] | 44.75 |  |  | 78.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.16 |  |  |  |  | 0.00
2014 |  |  |  | 40.96 |  |  | 6457 |  |  |  | 11 | [10 empty] | 84.92 |  |  |  | 84.92 | [5 empty] | 42.51 |  |  | 73.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.08 |  |  |  |  | 0.00
2015 |  |  |  | 39.78 |  |  | 6331 |  |  |  | 11 | [10 empty] | 73.73 |  |  |  | 73.73 | [5 empty] | 41.28 |  |  | 72.27 |  |  |  | 0.44 |  | 0.32 | [8 empty] | 25.95 |  |  |  |  | 0.00
2016 |  |  |  | 35.79 |  |  | 6506 |  |  |  | 11 | [10 empty] | 75.88 |  |  |  | 75.88 | [5 empty] | 37.04 |  |  | 74.07 |  |  |  | 0.86 |  | 0.66 | [8 empty] | 23.46 |  |  |  |  | 0.00
2017 |  |  |  | 44.31 |  |  | 7393 |  |  |  | 11 | [10 empty] | 85.12 |  |  |  | 85.12 | [5 empty] | 45.98 |  |  | 84.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.88 |  |  |  |  | 0.00
2018 |  |  |  | 54.16 |  |  | 7383 |  |  |  | 11 | [10 empty] | 84.99 |  |  |  | 84.99 | [5 empty] | 56.20 |  |  | 84.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.01 |  |  |  |  | 0.00
2019 |  |  |  | 57.78 |  |  | 7398 |  |  |  | 11 | [10 empty] | 85.16 |  |  |  | 85.16 | [5 empty] | 59.97 |  |  | 84.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.84 |  |  |  |  | 0.00
2020 |  |  |  | 32.42 |  |  | 6429 |  |  |  | 11 | [10 empty] | 74.40 |  |  |  | 74.40 | [5 empty] | 33.55 |  |  | 73.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.60 |  |  |  |  | 0.00
2021 |  |  |  | 28.85 |  |  | 7051 |  |  |  | 11 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 29.94 |  |  | 80.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.90 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1975 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 105
B. |  | Refuelling without maintenance | [35 empty] | 8
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1367 | [14 empty] | 1422 |  |  |  | 64
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 102
E. |  | Testing of plant systems or components | [20 empty] | 1 | [14 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 13
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 340 | [19 empty] | 114
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [35 empty] | 5
Subtotal | [22 empty] | 1368 | [10 empty] | 340 |  |  |  | 1544 |  |  |  | 174 | [11 empty] | 127
Total | [22 empty] | 1708 | [14 empty] | 1845
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1975 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 54
12. |  |  | Reactor I&C Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 4
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 5
Total | [37 empty] | 104
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the intermediate outage from 2021.06.25 to 2021.08.20. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BILIBINO-3
2021 Operating Experience
RU-143 | [8 empty] | BILIBINO-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / EGP-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-01-01
Thermal power | [12 empty] | : |  |  | 62 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-12-22
Gross electrical power | [12 empty] | : |  |  | 12 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-02-01
Reference unit power (net) | [12 empty] | : |  |  | 11 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 280
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 3000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 273 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 21.89 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.29 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 80.29 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 19.71 %
Load Factor (LF) | [18 empty] | : | 22.72 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 77.02 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2013 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 20.99 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 3.23 | 2.92 |  |  |  | 2.38 |  | 3.01 | [8 empty] | 2.84 |  |  | 2.26 | [6 empty] | 1.54 |  | 0.99 |  |  |  | 0.00 |  |  | 0.30 |  |  | 1.05 | [9 empty] | 1.35 |  |  | 21.89
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 60.07 |  | 91.67 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 84.67 |  |  |  | 4.55 |  |  | 23.69 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.29
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 60.07 |  | 91.67 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 84.67 |  |  |  | 4.55 |  |  | 23.69 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.29
LF [%] |  |  |  |  | 39.49 | 39.52 |  |  |  | 29.04 |  | 38.04 | [8 empty] | 34.75 |  |  | 28.50 | [6 empty] | 18.83 |  | 12.15 |  |  |  | 0.00 |  |  | 3.73 |  |  | 13.32 | [9 empty] | 16.53 |  |  | 22.72
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 58.20 |  | 91.25 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 74.33 |  |  |  | 0.00 |  |  | 20.03 |  |  | 81.53 | [9 empty] | 100.00 |  |  | 77.02
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 39.93 |  | 8.33 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 15.33 |  |  |  | 95.45 |  |  | 76.31 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 19.71
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 2315.07 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.63 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.21 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.52 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.94 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 53.78 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 8.73 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.22 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | 51.20 |  |  | 6655 |  |  |  | 10 | [10 empty] | 83.33 |  |  |  | 90.55 | [5 empty] | 62.19 |  |  | 77.39 |  |  |  | 2.85 |  | 2.65 | [8 empty] | 6.80 |  |  |  |  | 7.21
1977 |  |  |  | 46.50 |  |  | 7533 |  |  |  | 10 | [10 empty] | 78.21 |  |  |  | 92.83 | [5 empty] | 53.08 |  |  | 85.99 |  |  |  | 0.39 |  | 0.36 | [8 empty] | 6.81 |  |  |  |  | 14.62
1978 |  |  |  | 61.86 |  |  | 7514 |  |  |  | 10 | [10 empty] | 86.25 |  |  |  | 86.25 | [5 empty] | 70.61 |  |  | 85.78 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 13.74 |  |  |  |  | 0.00
1979 |  |  |  | 62.12 |  |  | 7837 |  |  |  | 10 | [10 empty] | 82.45 |  |  |  | 88.94 | [5 empty] | 70.92 |  |  | 89.46 |  |  |  | 0.16 |  | 0.14 | [8 empty] | 10.92 |  |  |  |  | 6.49
1980 |  |  |  | 79.43 |  |  | 8130 |  |  |  | 10 | [10 empty] | 90.99 |  |  |  | 92.18 | [5 empty] | 90.42 |  |  | 92.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.82 |  |  |  |  | 1.20
1981 |  |  |  | 89.78 |  |  | 8480 |  |  |  | 10 | [10 empty] | 96.64 |  |  |  | 96.64 | [5 empty] | 102.49 |  |  | 96.80 |  |  |  | 0.13 |  | 0.12 | [8 empty] | 3.24 |  |  |  |  | 0.00
1982 |  |  |  | 79.34 |  |  | 8323 |  |  |  | 10 | [10 empty] | 94.83 |  |  |  | 94.83 | [5 empty] | 90.57 |  |  | 95.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.17 |  |  |  |  | 0.00
1983 |  |  |  | 72.81 |  |  | 7782 |  |  |  | 10 | [10 empty] | 85.31 |  |  |  | 88.85 | [5 empty] | 83.11 |  |  | 88.84 |  |  |  | 0.34 |  | 0.31 | [8 empty] | 10.85 |  |  |  |  | 3.54
1984 |  |  |  | 76.48 |  |  | 7876 |  |  |  | 10 | [10 empty] | 87.36 |  |  |  | 89.14 | [5 empty] | 87.07 |  |  | 89.66 |  |  |  | 0.48 |  | 0.43 | [8 empty] | 10.42 |  |  |  |  | 1.79
1985 |  |  |  | 69.83 |  |  | 7119 |  |  |  | 10 | [10 empty] | 78.48 |  |  |  | 80.33 | [5 empty] | 79.72 |  |  | 81.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.67 |  |  |  |  | 1.85
1986 |  |  |  | 77.11 |  |  | 8001 |  |  |  | 10 | [10 empty] | 87.71 |  |  |  | 91.02 | [5 empty] | 88.03 |  |  | 91.34 |  |  |  | 0.66 |  | 0.60 | [8 empty] | 8.38 |  |  |  |  | 3.31
1987 |  |  |  | 89.09 |  |  | 7801 |  |  |  | 12 | [10 empty] | 89.09 |  |  |  | 89.09 | [5 empty] | 84.75 |  |  | 89.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.91 |  |  |  |  | 0.00
1988 |  |  |  | 76.71 |  |  | 7815 |  |  |  | 11 | [10 empty] | 89.47 |  |  |  | 89.47 | [5 empty] | 79.39 |  |  | 88.97 |  |  |  | 0.57 |  | 0.51 | [8 empty] | 10.02 |  |  |  |  | 0.00
1989 |  |  |  | 74.26 |  |  | 7756 |  |  |  | 11 | [10 empty] | 89.05 |  |  |  | 89.46 | [5 empty] | 77.06 |  |  | 88.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.54 |  |  |  |  | 0.40
1990 |  |  |  | 73.74 |  |  | 8024 |  |  |  | 11 | [10 empty] | 91.12 |  |  |  | 91.98 | [5 empty] | 76.53 |  |  | 91.60 |  |  |  | 6.83 |  | 6.75 | [8 empty] | 1.28 |  |  |  |  | 0.86
1991 |  |  |  | 66.19 |  |  | 6749 |  |  |  | 11 | [10 empty] | 76.59 |  |  |  | 78.08 | [5 empty] | 68.69 |  |  | 77.04 |  |  |  | 1.34 |  | 1.06 | [8 empty] | 20.86 |  |  |  |  | 1.50
1992 |  |  |  | 70.92 |  |  | 7727 |  |  |  | 11 | [10 empty] | 79.70 |  |  |  | 79.70 | [5 empty] | 73.40 |  |  | 87.97 |  |  |  | 0.40 |  | 0.32 | [8 empty] | 19.98 |  |  |  |  | 0.00
1993 |  |  |  | 52.59 |  |  | 7218 |  |  |  | 11 | [10 empty] | 61.50 |  |  |  | 83.21 | [5 empty] | 54.58 |  |  | 82.40 |  |  |  | 0.16 |  | 0.13 | [8 empty] | 16.66 |  |  |  |  | 21.71
1994 |  |  |  | 44.71 |  |  | 6342 |  |  |  | 11 | [10 empty] | 71.96 |  |  |  | 73.69 | [5 empty] | 46.39 |  |  | 72.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.31 |  |  |  |  | 1.73
1995 |  |  |  | 17.30 |  |  | 3293 |  |  |  | 11 | [10 empty] | 34.90 |  |  |  | 38.15 | [5 empty] | 17.95 |  |  | 37.59 |  |  |  | 9.46 |  | 3.99 | [8 empty] | 57.86 |  |  |  |  | 3.26
1996 |  |  |  | 52.62 |  |  | 7142 |  |  |  | 11 | [10 empty] | 82.27 |  |  |  | 82.27 | [5 empty] | 54.46 |  |  | 81.31 |  |  |  | 6.51 |  | 5.73 | [8 empty] | 12.00 |  |  |  |  | 0.00
1997 |  |  |  | 25.83 |  |  | 3769 |  |  |  | 11 | [10 empty] | 42.86 |  |  |  | 42.86 | [5 empty] | 26.80 |  |  | 43.03 |  |  |  | 0.86 |  | 0.37 | [8 empty] | 56.77 |  |  |  |  | 0.00
1998 |  |  |  | 23.16 |  |  | 4200 |  |  |  | 11 | [10 empty] | 29.11 |  |  |  | 49.13 | [5 empty] | 24.04 |  |  | 47.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 50.87 |  |  |  |  | 20.02
1999 |  |  |  | 51.44 |  |  | 6607 |  |  |  | 11 | [10 empty] | 59.91 |  |  |  | 75.85 | [5 empty] | 53.38 |  |  | 75.42 |  |  |  | 0.12 |  | 0.09 | [8 empty] | 24.06 |  |  |  |  | 15.94
2000 |  |  |  | 45.23 |  |  | 7569 |  |  |  | 11 | [10 empty] | 54.84 |  |  |  | 86.83 | [5 empty] | 46.81 |  |  | 86.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.17 |  |  |  |  | 31.99
2001 |  |  |  | 53.94 |  |  | 7383 |  |  |  | 11 | [10 empty] | 62.96 |  |  |  | 84.88 | [5 empty] | 55.98 |  |  | 84.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.12 |  |  |  |  | 21.91
2002 |  |  |  | 30.73 |  |  | 6250 |  |  |  | 11 | [10 empty] | 39.39 |  |  |  | 71.50 | [5 empty] | 31.90 |  |  | 71.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.50 |  |  |  |  | 32.11
2003 |  |  |  | 35.42 |  |  | 7097 |  |  |  | 11 | [10 empty] | 46.72 |  |  |  | 81.51 | [5 empty] | 36.75 |  |  | 81.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.49 |  |  |  |  | 34.79
2004 |  |  |  | 31.09 |  |  | 7166 |  |  |  | 11 | [10 empty] | 42.00 |  |  |  | 85.77 | [5 empty] | 32.18 |  |  | 81.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.23 |  |  |  |  | 43.77
2005 |  |  |  | 20.37 |  |  | 6102 |  |  |  | 11 | [10 empty] | 30.86 |  |  |  | 71.09 | [5 empty] | 21.14 |  |  | 69.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.91 |  |  |  |  | 40.23
2006 |  |  |  | 26.25 |  |  | 6542 |  |  |  | 11 | [10 empty] | 36.94 |  |  |  | 76.74 | [5 empty] | 27.24 |  |  | 74.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.26 |  |  |  |  | 39.80
2007 |  |  |  | 27.45 |  |  | 7257 |  |  |  | 11 | [10 empty] | 38.64 |  |  |  | 85.73 | [5 empty] | 28.49 |  |  | 82.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.27 |  |  |  |  | 47.09
2008 |  |  |  | 33.28 |  |  | 7335 |  |  |  | 11 | [10 empty] | 85.73 |  |  |  | 85.73 | [5 empty] | 34.44 |  |  | 83.50 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 14.20 |  |  |  |  | 0.00
2009 |  |  |  | 44.57 |  |  | 7972 |  |  |  | 11 | [10 empty] | 91.43 |  |  |  | 91.43 | [5 empty] | 46.25 |  |  | 91.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.57 |  |  |  |  | 0.00
2010 |  |  |  | 33.69 |  |  | 6035 |  |  |  | 11 | [10 empty] | 77.50 |  |  |  | 77.50 | [5 empty] | 34.96 |  |  | 68.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.50 |  |  |  |  | 0.00
2011 |  |  |  | 22.19 |  |  | 4885 |  |  |  | 11 | [10 empty] | 87.96 |  |  |  | 87.96 | [5 empty] | 23.03 |  |  | 55.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.04 |  |  |  |  | 0.00
2012 |  |  |  | 34.63 |  |  | 7253 |  |  |  | 11 | [10 empty] | 86.71 |  |  |  | 86.71 | [5 empty] | 35.84 |  |  | 82.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.29 |  |  |  |  | 0.00
2013 |  |  |  | 43.85 |  |  | 7436 |  |  |  | 11 | [10 empty] | 85.64 |  |  |  | 85.64 | [5 empty] | 45.51 |  |  | 84.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.36 |  |  |  |  | 0.00
2014 |  |  |  | 45.10 |  |  | 6615 |  |  |  | 11 | [10 empty] | 76.67 |  |  |  | 76.67 | [5 empty] | 46.80 |  |  | 75.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.33 |  |  |  |  | 0.00
2015 |  |  |  | 51.64 |  |  | 7337 |  |  |  | 11 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 53.60 |  |  | 83.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.90 |  |  |  |  | 0.00
2016 |  |  |  | 49.20 |  |  | 7410 |  |  |  | 11 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 50.92 |  |  | 84.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.90 |  |  |  |  | 0.00
2017 |  |  |  | 50.50 |  |  | 7377 |  |  |  | 11 | [10 empty] | 84.93 |  |  |  | 84.93 | [5 empty] | 52.41 |  |  | 84.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.07 |  |  |  |  | 0.00
2018 |  |  |  | 48.41 |  |  | 6626 |  |  |  | 11 | [10 empty] | 76.75 |  |  |  | 76.75 | [5 empty] | 50.24 |  |  | 75.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.25 |  |  |  |  | 0.00
2019 |  |  |  | 63.23 |  |  | 7849 |  |  |  | 11 | [10 empty] | 90.08 |  |  |  | 90.08 | [5 empty] | 65.62 |  |  | 89.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.92 |  |  |  |  | 0.00
2020 |  |  |  | 38.00 |  |  | 7380 |  |  |  | 11 | [10 empty] | 84.73 |  |  |  | 84.73 | [5 empty] | 39.33 |  |  | 84.02 |  |  |  | 0.21 |  | 0.18 | [8 empty] | 15.09 |  |  |  |  | 0.00
2021 |  |  |  | 21.89 |  |  | 6747 |  |  |  | 11 | [10 empty] | 80.29 |  |  |  | 80.29 | [5 empty] | 22.72 |  |  | 77.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.71 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1976 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 45
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1793 | [14 empty] | 1319
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 248
E. |  | Testing of plant systems or components | [35 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 34
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 205 | [19 empty] | 100
Z. |  | Other | [35 empty] | 11 |  |  |  | 1
Subtotal | [22 empty] | 1793 | [10 empty] | 205 |  |  |  | 1584 |  |  |  | 46 | [11 empty] | 134
Total | [22 empty] | 1998 | [14 empty] | 1764
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1976 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 13
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 13
Total | [37 empty] | 45
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the routine maintenance outage from 2021.03.15 to 2021.04.03 and in the intermediate outage from 2021.08.27 to 2021.10.25 Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BILIBINO-4
2021 Operating Experience
RU-144 | [8 empty] | BILIBINO-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / EGP-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-01-01
Thermal power | [12 empty] | : |  |  | 62 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-12-27
Gross electrical power | [12 empty] | : |  |  | 12 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-01-01
Reference unit power (net) | [12 empty] | : |  |  | 11 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 280
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 3000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 273 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 22.23 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.19 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 80.19 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 19.81 %
Load Factor (LF) | [18 empty] | : | 23.07 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 78.65 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1870 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 17.83 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 2.64 | 2.54 |  |  |  | 4.04 |  | 0.51 | [8 empty] | 0.00 |  |  | 2.48 | [6 empty] | 2.20 |  | 2.10 |  |  |  | 2.38 |  |  | 1.54 |  |  | 0.51 | [9 empty] | 1.29 |  |  | 22.23
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 30.11 | [8 empty] | 4.55 |  |  | 84.20 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 90.76 |  |  | 52.87 | [9 empty] | 100.00 |  |  | 80.19
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 30.11 | [8 empty] | 4.55 |  |  | 84.20 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 90.76 |  |  | 52.87 | [9 empty] | 100.00 |  |  | 80.19
LF [%] |  |  |  |  | 32.29 | 34.35 |  |  |  | 49.35 |  | 6.43 | [8 empty] | 0.00 |  |  | 31.36 | [6 empty] | 26.93 |  | 25.65 |  |  |  | 30.06 |  |  | 18.77 |  |  | 6.40 | [9 empty] | 15.74 |  |  | 23.07
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 26.81 | [8 empty] | 0.00 |  |  | 83.47 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 83.20 |  |  | 50.69 | [9 empty] | 100.00 |  |  | 78.65
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 69.89 | [8 empty] | 95.45 |  |  | 15.80 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 9.24 |  |  | 47.13 | [9 empty] | 0.00 |  |  | 19.81
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 2154.6 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.64 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.78 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.52 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.12 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.36 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 52.06 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 8.34 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.98 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 52.65 |  |  | 7392 |  |  |  | 10 | [10 empty] | 82.89 |  |  |  | 93.56 | [5 empty] | 60.10 |  |  | 84.38 |  |  |  | 0.28 |  | 0.27 | [8 empty] | 6.17 |  |  |  |  | 10.67
1978 |  |  |  | 58.30 |  |  | 7827 |  |  |  | 10 | [10 empty] | 91.06 |  |  |  | 91.06 | [5 empty] | 66.55 |  |  | 89.35 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.93 |  |  |  |  | 0.00
1979 |  |  |  | 74.46 |  |  | 7552 |  |  |  | 10 | [10 empty] | 83.88 |  |  |  | 85.52 | [5 empty] | 85.00 |  |  | 86.21 |  |  |  | 0.20 |  | 0.17 | [8 empty] | 14.31 |  |  |  |  | 1.64
1980 |  |  |  | 77.62 |  |  | 8347 |  |  |  | 10 | [10 empty] | 92.91 |  |  |  | 94.77 | [5 empty] | 88.37 |  |  | 95.03 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 5.18 |  |  |  |  | 1.86
1981 |  |  |  | 78.26 |  |  | 7734 |  |  |  | 10 | [10 empty] | 86.61 |  |  |  | 87.69 | [5 empty] | 89.33 |  |  | 88.29 |  |  |  | 0.80 |  | 0.71 | [8 empty] | 11.60 |  |  |  |  | 1.08
1982 |  |  |  | 77.61 |  |  | 7976 |  |  |  | 10 | [10 empty] | 90.71 |  |  |  | 90.71 | [5 empty] | 88.59 |  |  | 91.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.29 |  |  |  |  | 0.00
1983 |  |  |  | 75.53 |  |  | 7923 |  |  |  | 10 | [10 empty] | 86.88 |  |  |  | 89.97 | [5 empty] | 86.23 |  |  | 90.45 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 9.94 |  |  |  |  | 3.09
1984 |  |  |  | 79.01 |  |  | 7744 |  |  |  | 10 | [10 empty] | 86.77 |  |  |  | 87.57 | [5 empty] | 89.95 |  |  | 88.16 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 12.36 |  |  |  |  | 0.80
1985 |  |  |  | 81.23 |  |  | 7919 |  |  |  | 10 | [10 empty] | 89.53 |  |  |  | 90.33 | [5 empty] | 92.73 |  |  | 90.40 |  |  |  | 1.23 |  | 1.13 | [8 empty] | 8.55 |  |  |  |  | 0.79
1986 |  |  |  | 74.54 |  |  | 7083 |  |  |  | 10 | [10 empty] | 79.84 |  |  |  | 79.90 | [5 empty] | 85.09 |  |  | 80.86 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 20.09 |  |  |  |  | 0.06
1987 |  |  |  | 95.55 |  |  | 8154 |  |  |  | 12 | [10 empty] | 93.26 |  |  |  | 93.26 | [5 empty] | 90.89 |  |  | 93.08 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 6.54 |  |  |  |  | 0.00
1988 |  |  |  | 75.85 |  |  | 7617 |  |  |  | 11 | [10 empty] | 87.34 |  |  |  | 87.34 | [5 empty] | 78.50 |  |  | 86.71 |  |  |  | 0.86 |  | 0.76 | [8 empty] | 11.90 |  |  |  |  | 0.00
1989 |  |  |  | 71.37 |  |  | 7853 |  |  |  | 11 | [10 empty] | 93.22 |  |  |  | 93.22 | [5 empty] | 74.06 |  |  | 89.65 |  |  |  | 0.25 |  | 0.24 | [8 empty] | 6.54 |  |  |  |  | 0.00
1990 |  |  |  | 75.29 |  |  | 7588 |  |  |  | 11 | [10 empty] | 86.36 |  |  |  | 87.22 | [5 empty] | 78.13 |  |  | 86.62 |  |  |  | 5.48 |  | 5.06 | [8 empty] | 7.73 |  |  |  |  | 0.86
1991 |  |  |  | 61.32 |  |  | 6139 |  |  |  | 11 | [10 empty] | 69.89 |  |  |  | 71.43 | [5 empty] | 63.64 |  |  | 70.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.57 |  |  |  |  | 1.54
1992 |  |  |  | 69.84 |  |  | 7756 |  |  |  | 11 | [10 empty] | 87.82 |  |  |  | 87.82 | [5 empty] | 72.28 |  |  | 88.30 |  |  |  | 1.22 |  | 1.08 | [8 empty] | 11.10 |  |  |  |  | 0.00
1993 |  |  |  | 56.00 |  |  | 6918 |  |  |  | 11 | [10 empty] | 64.39 |  |  |  | 80.22 | [5 empty] | 58.12 |  |  | 78.97 |  |  |  | 0.82 |  | 0.66 | [8 empty] | 19.11 |  |  |  |  | 15.83
1994 |  |  |  | 38.46 |  |  | 5266 |  |  |  | 11 | [10 empty] | 61.82 |  |  |  | 61.99 | [5 empty] | 39.91 |  |  | 60.11 |  |  |  | 9.18 |  | 6.27 | [8 empty] | 31.75 |  |  |  |  | 0.17
1995 |  |  |  | 29.88 |  |  | 5083 |  |  |  | 11 | [10 empty] | 62.73 |  |  |  | 63.94 | [5 empty] | 31.01 |  |  | 58.03 |  |  |  | 0.53 |  | 0.34 | [8 empty] | 35.72 |  |  |  |  | 1.21
1996 |  |  |  | 35.18 |  |  | 5109 |  |  |  | 11 | [10 empty] | 59.13 |  |  |  | 59.13 | [5 empty] | 36.41 |  |  | 58.16 |  |  |  | 1.36 |  | 0.81 | [8 empty] | 40.06 |  |  |  |  | 0.00
1997 |  |  |  | 15.13 |  |  | 2490 |  |  |  | 11 | [10 empty] | 28.42 |  |  |  | 37.04 | [5 empty] | 15.70 |  |  | 28.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 62.96 |  |  |  |  | 8.61
1998 |  |  |  | 37.29 |  |  | 5510 |  |  |  | 11 | [10 empty] | 44.52 |  |  |  | 63.14 | [5 empty] | 38.70 |  |  | 62.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.86 |  |  |  |  | 18.62
1999 |  |  |  | 28.69 |  |  | 3993 |  |  |  | 11 | [10 empty] | 34.77 |  |  |  | 46.74 | [5 empty] | 29.77 |  |  | 45.58 |  |  |  | 6.39 |  | 3.19 | [8 empty] | 50.07 |  |  |  |  | 11.97
2000 |  |  |  | 55.85 |  |  | 7740 |  |  |  | 11 | [10 empty] | 64.20 |  |  |  | 88.68 | [5 empty] | 57.80 |  |  | 88.11 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 11.29 |  |  |  |  | 24.48
2001 |  |  |  | 35.44 |  |  | 5931 |  |  |  | 11 | [10 empty] | 43.17 |  |  |  | 68.01 | [5 empty] | 36.78 |  |  | 67.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.99 |  |  |  |  | 24.84
2002 |  |  |  | 33.12 |  |  | 6419 |  |  |  | 11 | [10 empty] | 46.34 |  |  |  | 73.76 | [5 empty] | 34.37 |  |  | 73.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.24 |  |  |  |  | 27.42
2003 |  |  |  | 24.52 |  |  | 5849 |  |  |  | 11 | [10 empty] | 34.04 |  |  |  | 67.51 | [5 empty] | 25.45 |  |  | 66.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.49 |  |  |  |  | 33.47
2004 |  |  |  | 26.10 |  |  | 7303 |  |  |  | 11 | [10 empty] | 36.71 |  |  |  | 83.90 | [5 empty] | 27.01 |  |  | 83.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.10 |  |  |  |  | 47.19
2005 |  |  |  | 24.95 |  |  | 7300 |  |  |  | 11 | [10 empty] | 36.29 |  |  |  | 84.32 | [5 empty] | 25.89 |  |  | 83.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.68 |  |  |  |  | 48.03
2006 |  |  |  | 25.22 |  |  | 6626 |  |  |  | 11 | [10 empty] | 36.44 |  |  |  | 76.86 | [5 empty] | 26.18 |  |  | 75.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.14 |  |  |  |  | 40.42
2007 |  |  |  | 19.57 |  |  | 5983 |  |  |  | 11 | [10 empty] | 30.89 |  |  |  | 76.55 | [5 empty] | 20.31 |  |  | 68.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.45 |  |  |  |  | 45.65
2008 |  |  |  | 29.55 |  |  | 7023 |  |  |  | 11 | [10 empty] | 87.66 |  |  |  | 87.66 | [5 empty] | 30.59 |  |  | 79.95 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 12.25 |  |  |  |  | 0.00
2009 |  |  |  | 42.14 |  |  | 7663 |  |  |  | 11 | [10 empty] | 88.40 |  |  |  | 88.40 | [5 empty] | 43.74 |  |  | 87.48 |  |  |  | 0.14 |  | 0.12 | [8 empty] | 11.48 |  |  |  |  | 0.00
2010 |  |  |  | 37.48 |  |  | 7272 |  |  |  | 11 | [10 empty] | 86.93 |  |  |  | 86.93 | [5 empty] | 38.90 |  |  | 83.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.07 |  |  |  |  | 0.00
2011 |  |  |  | 32.79 |  |  | 5944 |  |  |  | 11 | [10 empty] | 77.29 |  |  |  | 77.29 | [5 empty] | 34.03 |  |  | 67.85 |  |  |  | 0.21 |  | 0.16 | [8 empty] | 22.55 |  |  |  |  | 0.00
2012 |  |  |  | 24.50 |  |  | 5886 |  |  |  | 11 | [10 empty] | 86.69 |  |  |  | 86.69 | [5 empty] | 25.36 |  |  | 67.01 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 13.28 |  |  |  |  | 0.00
2013 |  |  |  | 45.48 |  |  | 7472 |  |  |  | 11 | [10 empty] | 87.40 |  |  |  | 87.40 | [5 empty] | 47.19 |  |  | 85.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.60 |  |  |  |  | 0.00
2014 |  |  |  | 45.89 |  |  | 7187 |  |  |  | 11 | [10 empty] | 84.56 |  |  |  | 84.56 | [5 empty] | 47.63 |  |  | 82.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.44 |  |  |  |  | 0.00
2015 |  |  |  | 40.59 |  |  | 6307 |  |  |  | 11 | [10 empty] | 76.02 |  |  |  | 76.02 | [5 empty] | 42.12 |  |  | 72.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.98 |  |  |  |  | 0.00
2016 |  |  |  | 43.53 |  |  | 7163 |  |  |  | 11 | [10 empty] | 83.57 |  |  |  | 83.57 | [5 empty] | 45.05 |  |  | 81.55 |  |  |  | 1.87 |  | 1.59 | [8 empty] | 14.84 |  |  |  |  | 0.00
2017 |  |  |  | 46.22 |  |  | 7395 |  |  |  | 11 | [10 empty] | 85.13 |  |  |  | 85.13 | [5 empty] | 47.97 |  |  | 84.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.87 |  |  |  |  | 0.00
2018 |  |  |  | 54.77 |  |  | 7392 |  |  |  | 11 | [10 empty] | 85.09 |  |  |  | 85.09 | [5 empty] | 56.84 |  |  | 84.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.91 |  |  |  |  | 0.00
2019 |  |  |  | 50.73 |  |  | 6705 |  |  |  | 11 | [10 empty] | 77.60 |  |  |  | 77.60 | [5 empty] | 52.65 |  |  | 76.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.40 |  |  |  |  | 0.00
2020 |  |  |  | 38.06 |  |  | 7194 |  |  |  | 11 | [10 empty] | 82.72 |  |  |  | 82.72 | [5 empty] | 39.39 |  |  | 81.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.28 |  |  |  |  | 0.00
2021 |  |  |  | 22.23 |  |  | 6890 |  |  |  | 11 | [10 empty] | 80.19 |  |  |  | 80.19 | [5 empty] | 23.07 |  |  | 78.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.81 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1977 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 49
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1817 | [14 empty] | 1456
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 312
E. |  | Testing of plant systems or components | [35 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 43
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 52 | [19 empty] | 105
L. |  | Human factor related | [39 empty] | 0
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 1817 | [10 empty] | 52 |  |  |  | 1775 |  |  |  | 50 | [11 empty] | 148
Total | [22 empty] | 1869 | [14 empty] | 1973
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1977 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 13
Total | [37 empty] | 49
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the routine maintenance outage from 2021.10.29 to 2021.11.15. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-1
2021 Operating Experience
RU-30 | [8 empty] | KALININ-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-338 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-02-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-05-09
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-06-12
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7970.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.34 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.44 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.21 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.49 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.3 %
Load Factor (LF) | [18 empty] | : | 95.77 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.05 %
Operating Factor (OF) | [18 empty] | : | 89.6 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 911 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 37.5 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 741.27 | 689.90 |  |  |  | 651.84 |  | 739.71 | [8 empty] | 750.89 |  |  | 725.76 | [6 empty] | 715.45 |  | 0.00 |  |  |  | 687.73 |  |  | 764.00 |  |  | 739.42 | [9 empty] | 764.10 |  |  | 7970.06
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 85.74 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 96.17 |  | 0.00 |  |  |  | 93.56 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.44
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 85.74 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 96.79 |  | 0.00 |  |  |  | 93.56 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.49
LF [%] |  |  |  |  | 104.88 | 108.07 |  |  |  | 92.22 |  | 108.14 | [8 empty] | 106.24 |  |  | 106.10 | [6 empty] | 101.22 |  | 0.00 |  |  |  | 100.55 |  |  | 108.09 |  |  | 108.10 | [9 empty] | 108.11 |  |  | 95.77
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 86.29 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 96.91 |  | 0.00 |  |  |  | 94.17 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.60
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 14.26 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.34
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 14.26 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.21
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 3.21 |  | 100.00 |  |  |  | 6.44 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.30
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.61 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 235863.29 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.57 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.51 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.63 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.17 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.2 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.66 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4487.64 |  |  | 5824 |  |  |  | 950 | [10 empty] | 58.28 |  |  |  | 58.28 | [5 empty] | 57.38 |  |  | 60.38 |  |  |  | 10.99 |  | 7.20 | [8 empty] | 34.52 |  |  |  |  | 0.00
1986 |  |  |  | 5297.73 |  |  | 5946 |  |  |  | 950 | [10 empty] | 62.85 |  |  |  | 62.85 | [5 empty] | 63.66 |  |  | 67.88 |  |  |  | 28.18 |  | 24.65 | [8 empty] | 12.50 |  |  |  |  | 0.00
1987 |  |  |  | 6842.49 |  |  | 6972 |  |  |  | 1000 | [10 empty] | 78.71 |  |  |  | 78.71 | [5 empty] | 78.11 |  |  | 79.59 |  |  |  | 7.76 |  | 6.62 | [8 empty] | 14.67 |  |  |  |  | 0.00
1988 |  |  |  | 5891.61 |  |  | 6187 |  |  |  | 950 | [10 empty] | 70.12 |  |  |  | 70.12 | [5 empty] | 70.60 |  |  | 70.43 |  |  |  | 9.61 |  | 7.45 | [8 empty] | 22.43 |  |  |  |  | 0.00
1989 |  |  |  | 6129.71 |  |  | 6396 |  |  |  | 950 | [10 empty] | 71.91 |  |  |  | 71.94 | [5 empty] | 73.66 |  |  | 73.01 |  |  |  | 10.20 |  | 8.17 | [8 empty] | 19.89 |  |  |  |  | 0.03
1990 |  |  |  | 5192.31 |  |  | 5435 |  |  |  | 950 | [10 empty] | 61.53 |  |  |  | 61.56 | [5 empty] | 62.39 |  |  | 62.04 |  |  |  | 3.54 |  | 2.26 | [8 empty] | 36.18 |  |  |  |  | 0.03
1991 |  |  |  | 6482.72 |  |  | 7161 |  |  |  | 950 | [10 empty] | 77.09 |  |  |  | 78.06 | [5 empty] | 77.90 |  |  | 81.75 |  |  |  | 11.66 |  | 10.30 | [8 empty] | 11.64 |  |  |  |  | 0.97
1992 |  |  |  | 6781.35 |  |  | 7388 |  |  |  | 950 | [10 empty] | 80.33 |  |  |  | 80.36 | [5 empty] | 81.27 |  |  | 84.12 |  |  |  | 12.02 |  | 10.98 | [8 empty] | 8.66 |  |  |  |  | 0.03
1993 |  |  |  | 4927.21 |  |  | 6133 |  |  |  | 950 | [10 empty] | 59.38 |  |  |  | 66.61 | [5 empty] | 59.21 |  |  | 70.01 |  |  |  | 5.55 |  | 3.91 | [8 empty] | 29.48 |  |  |  |  | 7.23
1994 |  |  |  | 4437.58 |  |  | 5440 |  |  |  | 950 | [10 empty] | 54.09 |  |  |  | 54.37 | [5 empty] | 53.32 |  |  | 62.10 |  |  |  | 16.02 |  | 10.37 | [8 empty] | 35.26 |  |  |  |  | 0.29
1995 |  |  |  | 4699.05 |  |  | 6265 |  |  |  | 950 | [10 empty] | 56.75 |  |  |  | 57.00 | [5 empty] | 56.47 |  |  | 71.52 |  |  |  | 26.12 |  | 20.15 | [8 empty] | 22.85 |  |  |  |  | 0.25
1996 |  |  |  | 4431.67 |  |  | 5628 |  |  |  | 950 | [10 empty] | 53.22 |  |  |  | 53.31 | [5 empty] | 53.11 |  |  | 64.07 |  |  |  | 19.08 |  | 12.57 | [8 empty] | 34.11 |  |  |  |  | 0.09
1997 |  |  |  | 5197.08 |  |  | 6195 |  |  |  | 950 | [10 empty] | 63.23 |  |  |  | 65.00 | [5 empty] | 62.45 |  |  | 70.72 |  |  |  | 5.59 |  | 3.85 | [8 empty] | 31.16 |  |  |  |  | 1.77
1998 |  |  |  | 6100.97 |  |  | 6937 |  |  |  | 950 | [10 empty] | 73.04 |  |  |  | 73.33 | [5 empty] | 73.31 |  |  | 79.19 |  |  |  | 6.48 |  | 5.08 | [8 empty] | 21.59 |  |  |  |  | 0.29
1999 |  |  |  | 5775.11 |  |  | 6589 |  |  |  | 950 | [10 empty] | 69.32 |  |  |  | 73.06 | [5 empty] | 69.40 |  |  | 75.22 |  |  |  | 5.65 |  | 4.37 | [8 empty] | 22.56 |  |  |  |  | 3.74
2000 |  |  |  | 6289.72 |  |  | 6784 |  |  |  | 950 | [10 empty] | 75.00 |  |  |  | 76.79 | [5 empty] | 75.37 |  |  | 77.23 |  |  |  | 3.54 |  | 2.82 | [8 empty] | 20.39 |  |  |  |  | 1.79
2001 |  |  |  | 6627.54 |  |  | 7020 |  |  |  | 950 | [10 empty] | 78.18 |  |  |  | 79.37 | [5 empty] | 79.64 |  |  | 80.14 |  |  |  | 5.67 |  | 4.77 | [8 empty] | 15.86 |  |  |  |  | 1.19
2002 |  |  |  | 7248.38 |  |  | 7568 |  |  |  | 950 | [10 empty] | 84.66 |  |  |  | 86.10 | [5 empty] | 87.10 |  |  | 86.39 |  |  |  | 0.27 |  | 0.23 | [8 empty] | 13.66 |  |  |  |  | 1.44
2003 |  |  |  | 7155.92 |  |  | 7408 |  |  |  | 950 | [10 empty] | 83.10 |  |  |  | 83.75 | [5 empty] | 85.99 |  |  | 84.57 |  |  |  | 4.40 |  | 3.85 | [8 empty] | 12.40 |  |  |  |  | 0.65
2004 |  |  |  | 6936.97 |  |  | 7179 |  |  |  | 950 | [10 empty] | 80.69 |  |  |  | 81.55 | [5 empty] | 83.13 |  |  | 81.73 |  |  |  | 2.57 |  | 2.15 | [8 empty] | 16.30 |  |  |  |  | 0.86
2005 |  |  |  | 6836.33 |  |  | 7219 |  |  |  | 950 | [10 empty] | 80.39 |  |  |  | 81.50 | [5 empty] | 82.14 |  |  | 82.40 |  |  |  | 4.45 |  | 4.78 | [8 empty] | 13.72 |  |  |  |  | 1.11
2006 |  |  |  | 6743.58 |  |  | 7112 |  |  |  | 950 | [10 empty] | 79.48 |  |  |  | 80.58 | [5 empty] | 81.03 |  |  | 81.19 |  |  |  | 4.77 |  | 5.16 | [8 empty] | 14.26 |  |  |  |  | 1.10
2007 |  |  |  | 7150.35 |  |  | 7491 |  |  |  | 950 | [10 empty] | 84.04 |  |  |  | 85.24 | [5 empty] | 85.92 |  |  | 85.51 |  |  |  | 2.14 |  | 1.87 | [8 empty] | 12.90 |  |  |  |  | 1.20
2008 |  |  |  | 6953.55 |  |  | 7209 |  |  |  | 950 | [10 empty] | 81.53 |  |  |  | 81.53 | [5 empty] | 83.33 |  |  | 82.07 |  |  |  | 2.44 |  | 2.04 | [8 empty] | 16.43 |  |  |  |  | 0.00
2009 |  |  |  | 7234.70 |  |  | 7669 |  |  |  | 950 | [10 empty] | 87.27 |  |  |  | 87.27 | [5 empty] | 86.93 |  |  | 87.55 |  |  |  | 0.70 |  | 0.62 | [8 empty] | 12.11 |  |  |  |  | 0.00
2010 |  |  |  | 7006.14 |  |  | 7175 |  |  |  | 950 | [10 empty] | 82.65 |  |  |  | 82.74 | [5 empty] | 84.19 |  |  | 81.91 |  |  |  | 6.45 |  | 5.71 | [8 empty] | 11.55 |  |  |  |  | 0.09
2011 |  |  |  | 7516.88 |  |  | 7727 |  |  |  | 950 | [10 empty] | 87.91 |  |  |  | 87.91 | [5 empty] | 90.34 |  |  | 88.22 |  |  |  | 0.22 |  | 0.19 | [8 empty] | 11.89 |  |  |  |  | 0.00
2012 |  |  |  | 6648.33 |  |  | 6833 |  |  |  | 950 | [10 empty] | 77.49 |  |  |  | 77.49 | [5 empty] | 79.67 |  |  | 77.79 |  |  |  | 0.94 |  | 0.74 | [8 empty] | 21.77 |  |  |  |  | 0.00
2013 |  |  |  | 6963.99 |  |  | 6915 |  |  |  | 950 | [10 empty] | 78.67 |  |  |  | 78.67 | [5 empty] | 83.68 |  |  | 78.94 |  |  |  | 6.17 |  | 15.31 | [8 empty] | 6.03 |  |  |  |  | 0.00
2014 |  |  |  | 5892.14 |  |  | 6035 |  |  |  | 950 | [10 empty] | 67.51 |  |  |  | 67.51 | [5 empty] | 70.79 |  |  | 68.88 |  |  |  | 3.79 |  | 2.66 | [8 empty] | 29.83 |  |  |  |  | 0.00
2015 |  |  |  | 8036.64 |  |  | 7931 |  |  |  | 950 | [10 empty] | 90.46 |  |  |  | 90.46 | [5 empty] | 96.57 |  |  | 90.54 |  |  |  | 0.64 |  | 0.58 | [8 empty] | 8.96 |  |  |  |  | 0.00
2016 |  |  |  | 6966.43 |  |  | 6876 |  |  |  | 950 | [10 empty] | 78.17 |  |  |  | 78.17 | [5 empty] | 83.48 |  |  | 78.28 |  |  |  | 8.56 |  | 7.32 | [8 empty] | 14.52 |  |  |  |  | 0.00
2017 |  |  |  | 8025.20 |  |  | 7856 |  |  |  | 950 | [10 empty] | 89.63 |  |  |  | 89.63 | [5 empty] | 96.43 |  |  | 89.68 |  |  |  | 0.00 |  | 0.53 | [8 empty] | 9.84 |  |  |  |  | 0.00
2018 |  |  |  | 8802.94 |  |  | 8643 |  |  |  | 950 | [10 empty] | 98.20 |  |  |  | 98.21 | [5 empty] | 105.78 |  |  | 98.66 |  |  |  | 1.79 |  | 1.79 | [8 empty] | 0.00 |  |  |  |  | 0.01
2019 |  |  |  | 6650.32 |  |  | 6595 |  |  |  | 950 | [10 empty] | 75.05 |  |  |  | 75.10 | [5 empty] | 79.91 |  |  | 75.29 |  |  |  | 6.64 |  | 5.34 | [8 empty] | 19.56 |  |  |  |  | 0.05
2020 |  |  |  | 2709.37 |  |  | 2703 |  |  |  | 950 | [10 empty] | 30.56 |  |  |  | 30.56 | [5 empty] | 32.47 |  |  | 30.77 |  |  |  | 4.41 |  | 1.41 | [8 empty] | 68.03 |  |  |  |  | 0.00
2021 |  |  |  | 7970.06 |  |  | 7849 |  |  |  | 950 | [10 empty] | 89.44 |  |  |  | 89.49 | [5 empty] | 95.77 |  |  | 89.60 |  |  |  | 1.34 |  | 1.21 | [8 empty] | 9.30 |  |  |  |  | 0.05
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1985 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 102 | [14 empty] | 275
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 810 | [14 empty] | 1542 |  |  |  | 30
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 104 |  |  |  | 1
E. |  | Testing of plant systems or components | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 6
Z. |  | Other | [39 empty] | 35
Subtotal | [22 empty] | 810 |  |  |  | 102 | [10 empty] | 1646 |  |  |  | 348 | [11 empty] | 3
Total | [22 empty] | 912 | [14 empty] | 1997
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1985 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 34
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 102 | [14 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 37
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 24
32. |  |  | Feedwater and Main Steam System | [34 empty] | 20
34. |  |  | Miscellaneous Systems | [34 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 124
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [22 empty] | 102 | [14 empty] | 283
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-July, September-December. Additional electricity generation amounted to 510387 MWh. The unit was in the intermediate outage from 2021.07.31 to 2021.09.02. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-2
2021 Operating Experience
RU-31 | [8 empty] | KALININ-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-338 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-02-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-12-03
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-03-03
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 8688.57 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.76 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.24 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.76 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.24 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 104.4 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 98.69 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 115 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 62.83 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 753.67 | 692.22 |  |  |  | 765.25 |  | 741.37 | [8 empty] | 756.45 |  |  | 596.56 | [6 empty] | 620.65 |  | 757.54 |  |  |  | 738.49 |  |  | 762.64 |  |  | 738.55 | [9 empty] | 765.17 |  |  | 8688.57
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 83.24 | [6 empty] | 83.76 |  | 100.00 |  |  |  | 100.00 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.24
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 83.24 | [6 empty] | 83.76 |  | 100.00 |  |  |  | 100.00 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.24
LF [%] |  |  |  |  | 106.63 | 108.43 |  |  |  | 108.27 |  | 108.39 | [8 empty] | 107.02 |  |  | 87.22 | [6 empty] | 87.81 |  | 107.18 |  |  |  | 107.97 |  |  | 107.90 |  |  | 107.97 | [9 empty] | 108.26 |  |  | 104.40
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 84.54 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.69
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 16.76 | [6 empty] | 16.24 |  | 0.00 |  |  |  | 0.00 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.76
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 16.76 | [6 empty] | 16.24 |  | 0.00 |  |  |  | 0.00 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.76
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 234210.15 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.92 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.72 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.62 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.23 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.9 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.1 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 6494.00 |  |  | 7605 |  |  |  | 1000 | [10 empty] | 86.27 |  |  |  | 86.27 | [5 empty] | 79.18 |  |  | 87.96 |  |  |  | 9.13 |  | 8.67 | [8 empty] | 5.07 |  |  |  |  | 0.00
1988 |  |  |  | 5829.43 |  |  | 6446 |  |  |  | 950 | [10 empty] | 71.67 |  |  |  | 71.67 | [5 empty] | 69.86 |  |  | 73.38 |  |  |  | 9.64 |  | 7.64 | [8 empty] | 20.68 |  |  |  |  | 0.00
1989 |  |  |  | 6580.49 |  |  | 7034 |  |  |  | 950 | [10 empty] | 78.45 |  |  |  | 78.45 | [5 empty] | 79.07 |  |  | 80.30 |  |  |  | 5.86 |  | 4.88 | [8 empty] | 16.67 |  |  |  |  | 0.00
1990 |  |  |  | 6788.16 |  |  | 7083 |  |  |  | 950 | [10 empty] | 79.45 |  |  |  | 79.45 | [5 empty] | 81.57 |  |  | 80.86 |  |  |  | 5.85 |  | 4.94 | [8 empty] | 15.61 |  |  |  |  | 0.00
1991 |  |  |  | 4729.67 |  |  | 5154 |  |  |  | 950 | [10 empty] | 49.79 |  |  |  | 49.79 | [5 empty] | 56.83 |  |  | 58.84 |  |  |  | 30.08 |  | 21.42 | [8 empty] | 28.79 |  |  |  |  | 0.00
1992 |  |  |  | 5496.31 |  |  | 6145 |  |  |  | 950 | [10 empty] | 65.70 |  |  |  | 65.70 | [5 empty] | 65.87 |  |  | 69.96 |  |  |  | 5.58 |  | 3.88 | [8 empty] | 30.42 |  |  |  |  | 0.00
1993 |  |  |  | 5862.30 |  |  | 7078 |  |  |  | 950 | [10 empty] | 51.91 |  |  |  | 56.45 | [5 empty] | 70.44 |  |  | 80.80 |  |  |  | 28.07 |  | 22.03 | [8 empty] | 21.52 |  |  |  |  | 4.54
1994 |  |  |  | 4463.77 |  |  | 6989 |  |  |  | 950 | [10 empty] | 54.87 |  |  |  | 54.87 | [5 empty] | 53.64 |  |  | 79.78 |  |  |  | 31.92 |  | 25.73 | [8 empty] | 19.41 |  |  |  |  | 0.00
1995 |  |  |  | 5769.75 |  |  | 7283 |  |  |  | 950 | [10 empty] | 69.48 |  |  |  | 72.40 | [5 empty] | 69.33 |  |  | 83.14 |  |  |  | 15.96 |  | 13.75 | [8 empty] | 13.85 |  |  |  |  | 2.92
1996 |  |  |  | 4595.17 |  |  | 7501 |  |  |  | 950 | [10 empty] | 56.02 |  |  |  | 78.42 | [5 empty] | 55.07 |  |  | 85.39 |  |  |  | 2.81 |  | 2.26 | [8 empty] | 19.31 |  |  |  |  | 22.40
1997 |  |  |  | 3880.64 |  |  | 6117 |  |  |  | 950 | [10 empty] | 47.25 |  |  |  | 62.67 | [5 empty] | 46.63 |  |  | 69.83 |  |  |  | 2.47 |  | 1.59 | [8 empty] | 35.74 |  |  |  |  | 15.42
1998 |  |  |  | 4946.65 |  |  | 6839 |  |  |  | 950 | [10 empty] | 59.67 |  |  |  | 59.98 | [5 empty] | 59.44 |  |  | 78.07 |  |  |  | 26.91 |  | 22.08 | [8 empty] | 17.93 |  |  |  |  | 0.31
1999 |  |  |  | 6379.25 |  |  | 7155 |  |  |  | 950 | [10 empty] | 76.21 |  |  |  | 80.03 | [5 empty] | 76.66 |  |  | 81.68 |  |  |  | 0.26 |  | 0.21 | [8 empty] | 19.76 |  |  |  |  | 3.82
2000 |  |  |  | 6418.74 |  |  | 7441 |  |  |  | 950 | [10 empty] | 76.26 |  |  |  | 83.57 | [5 empty] | 76.92 |  |  | 84.71 |  |  |  | 0.55 |  | 0.46 | [8 empty] | 15.97 |  |  |  |  | 7.32
2001 |  |  |  | 6708.99 |  |  | 7070 |  |  |  | 950 | [10 empty] | 79.16 |  |  |  | 80.00 | [5 empty] | 80.62 |  |  | 80.71 |  |  |  | 2.26 |  | 1.85 | [8 empty] | 18.15 |  |  |  |  | 0.84
2002 |  |  |  | 7003.43 |  |  | 7554 |  |  |  | 950 | [10 empty] | 82.66 |  |  |  | 85.76 | [5 empty] | 84.16 |  |  | 86.23 |  |  |  | 1.00 |  | 0.86 | [8 empty] | 13.37 |  |  |  |  | 3.10
2003 |  |  |  | 7329.54 |  |  | 7541 |  |  |  | 950 | [10 empty] | 85.33 |  |  |  | 85.89 | [5 empty] | 88.07 |  |  | 86.08 |  |  |  | 0.77 |  | 0.67 | [8 empty] | 13.45 |  |  |  |  | 0.55
2004 |  |  |  | 7398.23 |  |  | 7674 |  |  |  | 950 | [10 empty] | 86.68 |  |  |  | 87.11 | [5 empty] | 88.66 |  |  | 87.36 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 12.79 |  |  |  |  | 0.44
2005 |  |  |  | 6116.27 |  |  | 6476 |  |  |  | 950 | [10 empty] | 72.11 |  |  |  | 73.62 | [5 empty] | 73.49 |  |  | 73.92 |  |  |  | 11.86 |  | 9.90 | [8 empty] | 16.48 |  |  |  |  | 1.51
2006 |  |  |  | 7074.89 |  |  | 7400 |  |  |  | 950 | [10 empty] | 82.73 |  |  |  | 84.26 | [5 empty] | 85.01 |  |  | 84.47 |  |  |  | 3.63 |  | 3.18 | [8 empty] | 12.56 |  |  |  |  | 1.53
2007 |  |  |  | 7231.43 |  |  | 7539 |  |  |  | 950 | [10 empty] | 84.16 |  |  |  | 85.49 | [5 empty] | 86.90 |  |  | 86.06 |  |  |  | 1.16 |  | 1.00 | [8 empty] | 13.51 |  |  |  |  | 1.33
2008 |  |  |  | 7474.79 |  |  | 7756 |  |  |  | 950 | [10 empty] | 88.19 |  |  |  | 88.19 | [5 empty] | 89.57 |  |  | 88.30 |  |  |  | 0.25 |  | 0.22 | [8 empty] | 11.59 |  |  |  |  | 0.00
2009 |  |  |  | 7004.16 |  |  | 7248 |  |  |  | 950 | [10 empty] | 82.51 |  |  |  | 82.51 | [5 empty] | 84.16 |  |  | 82.74 |  |  |  | 1.50 |  | 1.26 | [8 empty] | 16.23 |  |  |  |  | 0.00
2010 |  |  |  | 7423.50 |  |  | 7595 |  |  |  | 950 | [10 empty] | 87.77 |  |  |  | 87.77 | [5 empty] | 89.20 |  |  | 86.70 |  |  |  | 1.51 |  | 1.34 | [8 empty] | 10.89 |  |  |  |  | 0.00
2011 |  |  |  | 7570.61 |  |  | 7675 |  |  |  | 950 | [10 empty] | 86.98 |  |  |  | 86.98 | [5 empty] | 90.98 |  |  | 87.62 |  |  |  | 0.63 |  | 0.55 | [8 empty] | 12.47 |  |  |  |  | 0.00
2012 |  |  |  | 7164.85 |  |  | 7464 |  |  |  | 950 | [10 empty] | 84.47 |  |  |  | 84.47 | [5 empty] | 85.86 |  |  | 84.97 |  |  |  | 0.93 |  | 0.79 | [8 empty] | 14.74 |  |  |  |  | 0.00
2013 |  |  |  | 8635.13 |  |  | 8552 |  |  |  | 950 | [10 empty] | 97.57 |  |  |  | 97.57 | [5 empty] | 103.76 |  |  | 97.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.43 |  |  |  |  | 0.00
2014 |  |  |  | 7030.39 |  |  | 6984 |  |  |  | 950 | [10 empty] | 79.59 |  |  |  | 79.59 | [5 empty] | 84.47 |  |  | 79.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.41 |  |  |  |  | 0.00
2015 |  |  |  | 7883.15 |  |  | 7805 |  |  |  | 950 | [10 empty] | 88.94 |  |  |  | 88.94 | [5 empty] | 94.73 |  |  | 89.10 |  |  |  | 2.10 |  | 1.90 | [8 empty] | 9.16 |  |  |  |  | 0.00
2016 |  |  |  | 6776.88 |  |  | 6664 |  |  |  | 950 | [10 empty] | 75.75 |  |  |  | 75.75 | [5 empty] | 81.21 |  |  | 75.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.25 |  |  |  |  | 0.00
2017 |  |  |  | 7562.08 |  |  | 7439 |  |  |  | 950 | [10 empty] | 84.68 |  |  |  | 84.71 | [5 empty] | 90.87 |  |  | 84.92 |  |  |  | 1.93 |  | 6.54 | [8 empty] | 8.75 |  |  |  |  | 0.03
2018 |  |  |  | 8390.72 |  |  | 8224 |  |  |  | 950 | [10 empty] | 93.84 |  |  |  | 93.86 | [5 empty] | 100.83 |  |  | 93.88 |  |  |  | 6.14 |  | 6.14 | [8 empty] | 0.00 |  |  |  |  | 0.01
2019 |  |  |  | 7769.30 |  |  | 7721 |  |  |  | 950 | [10 empty] | 87.05 |  |  |  | 87.05 | [5 empty] | 93.36 |  |  | 88.14 |  |  |  | 1.94 |  | 1.73 | [8 empty] | 11.23 |  |  |  |  | 0.00
2020 |  |  |  | 7987.59 |  |  | 8031 |  |  |  | 950 | [10 empty] | 90.80 |  |  |  | 90.80 | [5 empty] | 95.72 |  |  | 91.43 |  |  |  | 0.52 |  | 0.48 | [8 empty] | 8.73 |  |  |  |  | 0.00
2021 |  |  |  | 8688.57 |  |  | 8645 |  |  |  | 950 | [10 empty] | 97.24 |  |  |  | 97.24 | [5 empty] | 104.40 |  |  | 98.69 |  |  |  | 2.76 |  | 2.76 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1987 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 115 | [14 empty] | 180
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1199 |  |  |  | 6
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 67
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 15
Z. |  | Other | [39 empty] | 3
Subtotal | [26 empty] | 115 | [10 empty] | 1266 |  |  |  | 204 | [11 empty] | 3
Total | [22 empty] | 115 | [14 empty] | 1473
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1987 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 18
15. |  |  | Reactor Cooling Systems | [19 empty] | 115 | [14 empty] | 33
16. |  |  | Steam generation systems | [34 empty] | 4
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 29
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 71
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 115 | [14 empty] | 187
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-Desember. Additional electricity generation amounted to 562380 MWh. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-3
2021 Operating Experience
RU-36 | [8 empty] | KALININ-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | FAEA (Federal Atomic Energy Agency)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-10-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2004-12-16
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2005-11-08
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 17 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7321.24 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.7 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.73 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.59 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.78 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.64 %
Load Factor (LF) | [18 empty] | : | 87.97 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.05 %
Operating Factor (OF) | [18 empty] | : | 84.12 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1391 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 18.86 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 715.42 | 684.29 |  |  |  | 748.20 |  | 36.11 | [8 empty] | 33.48 |  |  | 714.17 | [6 empty] | 729.81 |  | 742.38 |  |  |  | 729.64 |  |  | 699.23 |  |  | 731.38 | [9 empty] | 757.12 |  |  | 7321.24
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.99 |  | 6.13 | [8 empty] | 6.20 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 93.08 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.73
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 6.68 | [8 empty] | 6.20 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 93.08 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.78
LF [%] |  |  |  |  | 101.22 | 107.19 |  |  |  | 105.86 |  | 5.28 | [8 empty] | 4.74 |  |  | 104.41 | [6 empty] | 103.26 |  | 105.03 |  |  |  | 106.67 |  |  | 98.93 |  |  | 106.93 | [9 empty] | 107.12 |  |  | 87.97
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 6.81 | [8 empty] | 6.99 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 96.24 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.12
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 6.92 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.70
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 6.92 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.59
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 93.32 | [8 empty] | 93.80 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.64
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.56 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 118793.12 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.56 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.37 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.08 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.05 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.09 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.82 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2005 |  |  |  | 4345.70 |  |  | 5686 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.84 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 6287.23 |  |  | 6692 |  |  |  | 950 | [10 empty] | 74.90 |  |  |  | 75.20 | [5 empty] | 75.55 |  |  | 76.39 |  |  |  | 5.71 |  | 6.62 | [8 empty] | 18.18 |  |  |  |  | 0.29
2007 |  |  |  | 7185.22 |  |  | 7505 |  |  |  | 950 | [10 empty] | 84.96 |  |  |  | 85.51 | [5 empty] | 86.34 |  |  | 85.67 |  |  |  | 0.91 |  | 0.81 | [8 empty] | 13.68 |  |  |  |  | 0.55
2008 |  |  |  | 7561.73 |  |  | 7737 |  |  |  | 950 | [10 empty] | 87.74 |  |  |  | 87.78 | [5 empty] | 90.62 |  |  | 88.08 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 12.06 |  |  |  |  | 0.03
2009 |  |  |  | 6806.52 |  |  | 7553 |  |  |  | 950 | [10 empty] | 85.96 |  |  |  | 85.96 | [5 empty] | 81.79 |  |  | 86.22 |  |  |  | 3.61 |  | 3.22 | [8 empty] | 10.82 |  |  |  |  | 0.00
2010 |  |  |  | 6902.21 |  |  | 7248 |  |  |  | 950 | [10 empty] | 82.13 |  |  |  | 82.44 | [5 empty] | 82.94 |  |  | 82.74 |  |  |  | 1.25 |  | 1.04 | [8 empty] | 16.52 |  |  |  |  | 0.31
2011 |  |  |  | 7088.32 |  |  | 7427 |  |  |  | 950 | [10 empty] | 84.82 |  |  |  | 84.85 | [5 empty] | 85.19 |  |  | 84.79 |  |  |  | 0.59 |  | 2.84 | [8 empty] | 12.31 |  |  |  |  | 0.04
2012 |  |  |  | 7765.07 |  |  | 8091 |  |  |  | 950 | [10 empty] | 91.78 |  |  |  | 91.78 | [5 empty] | 93.05 |  |  | 92.11 |  |  |  | 6.68 |  | 6.57 | [8 empty] | 1.65 |  |  |  |  | 0.01
2013 |  |  |  | 6505.71 |  |  | 6698 |  |  |  | 950 | [10 empty] | 76.18 |  |  |  | 76.18 | [5 empty] | 78.17 |  |  | 76.46 |  |  |  | 1.31 |  | 10.15 | [8 empty] | 13.67 |  |  |  |  | 0.00
2014 |  |  |  | 6599.48 |  |  | 6918 |  |  |  | 950 | [10 empty] | 78.27 |  |  |  | 78.27 | [5 empty] | 79.29 |  |  | 78.96 |  |  |  | 5.79 |  | 5.33 | [8 empty] | 16.40 |  |  |  |  | 0.00
2015 |  |  |  | 7665.20 |  |  | 8196 |  |  |  | 950 | [10 empty] | 92.28 |  |  |  | 92.28 | [5 empty] | 92.11 |  |  | 93.56 |  |  |  | 7.67 |  | 7.67 | [8 empty] | 0.05 |  |  |  |  | 0.00
2016 |  |  |  | 5233.15 |  |  | 5612 |  |  |  | 950 | [10 empty] | 62.43 |  |  |  | 62.43 | [5 empty] | 62.71 |  |  | 63.89 |  |  |  | 10.35 |  | 13.02 | [8 empty] | 24.55 |  |  |  |  | 0.00
2017 |  |  |  | 7892.37 |  |  | 7990 |  |  |  | 950 | [10 empty] | 91.11 |  |  |  | 91.11 | [5 empty] | 94.84 |  |  | 91.21 |  |  |  | 8.89 |  | 8.89 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 7504.45 |  |  | 7558 |  |  |  | 950 | [10 empty] | 85.85 |  |  |  | 85.95 | [5 empty] | 90.18 |  |  | 86.28 |  |  |  | 2.29 |  | 2.01 | [8 empty] | 12.04 |  |  |  |  | 0.10
2019 |  |  |  | 7322.22 |  |  | 7362 |  |  |  | 950 | [10 empty] | 83.69 |  |  |  | 83.76 | [5 empty] | 87.99 |  |  | 84.04 |  |  |  | 4.44 |  | 4.74 | [8 empty] | 11.50 |  |  |  |  | 0.07
2020 |  |  |  | 8807.69 |  |  | 8784 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.55 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2021 |  |  |  | 7321.23 |  |  | 7369 |  |  |  | 950 | [10 empty] | 83.73 |  |  |  | 83.78 | [5 empty] | 87.97 |  |  | 84.12 |  |  |  | 0.70 |  | 0.59 | [8 empty] | 15.64 |  |  |  |  | 0.05
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2005 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 48 | [14 empty] | 340
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1363 | [14 empty] | 956 |  |  |  | 11
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 18
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 2
Z. |  | Other | [39 empty] | 12
Subtotal | [22 empty] | 1363 |  |  |  | 48 | [10 empty] | 974 |  |  |  | 371 | [11 empty] | 2
Total | [22 empty] | 1411 | [14 empty] | 1347
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2005 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [19 empty] | 48 | [14 empty] | 58
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 161
42. |  |  | Electrical Power Supply Systems | [34 empty] | 91
Total | [22 empty] | 48 | [14 empty] | 356
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-March, May-Desember. Additional electricity generation amounted to 396609 MWh. The unit was in the overhaul outage from 2021.04.03 to 2021.05.29. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-4
2021 Operating Experience
RU-37 | [8 empty] | KALININ-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1986-08-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2011-11-24
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2012-12-25
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 10 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 1.05
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 8673.29 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.29 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.71 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.29 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.71 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 104.22 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 98.82 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 103 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 26.6 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 749.58 | 680.96 |  |  |  | 755.46 |  | 731.79 | [8 empty] | 706.25 |  |  | 707.15 | [6 empty] | 718.97 |  | 729.91 |  |  |  | 650.79 |  |  | 754.00 |  |  | 731.69 | [9 empty] | 756.74 |  |  | 8673.29
EAF [%] |  |  |  |  | 99.97 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 95.08 |  |  | 100.00 | [6 empty] | 99.97 |  | 99.36 |  |  |  | 90.17 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 98.71
UCF [%] |  |  |  |  | 99.97 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 95.08 |  |  | 100.00 | [6 empty] | 99.97 |  | 99.36 |  |  |  | 90.17 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 98.71
LF [%] |  |  |  |  | 106.05 | 106.67 |  |  |  | 106.88 |  | 106.99 | [8 empty] | 99.92 |  |  | 103.38 | [6 empty] | 101.72 |  | 103.27 |  |  |  | 95.14 |  |  | 106.68 |  |  | 106.97 | [9 empty] | 107.07 |  |  | 104.22
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 95.43 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 90.42 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.82
FLR [%] |  |  |  |  | 0.03 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.92 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.64 |  |  |  | 9.83 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 1.29
UCL [%] |  |  |  |  | 0.03 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.92 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.64 |  |  |  | 9.83 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 1.29
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 73888.57 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.05 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.56 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.3 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.56 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.14 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.47 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.04 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2012 |  |  |  | 5166.49 |  |  | 6858 |  |  |  | 950 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 6342.91 |  |  | 6662 |  |  |  | 950 | [10 empty] | 75.72 |  |  |  | 75.73 | [5 empty] | 76.22 |  |  | 76.05 |  |  |  | 6.89 |  | 8.42 | [8 empty] | 15.85 |  |  |  |  | 0.02
2014 |  |  |  | 7249.38 |  |  | 7691 |  |  |  | 950 | [10 empty] | 87.21 |  |  |  | 87.21 | [5 empty] | 87.10 |  |  | 87.79 |  |  |  | 1.23 |  | 1.08 | [8 empty] | 11.71 |  |  |  |  | 0.00
2015 |  |  |  | 8086.65 |  |  | 8346 |  |  |  | 950 | [10 empty] | 95.01 |  |  |  | 95.01 | [5 empty] | 97.17 |  |  | 95.27 |  |  |  | 4.99 |  | 4.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6704.20 |  |  | 7255 |  |  |  | 950 | [10 empty] | 80.15 |  |  |  | 80.15 | [5 empty] | 80.34 |  |  | 82.59 |  |  |  | 9.83 |  | 8.96 | [8 empty] | 10.89 |  |  |  |  | 0.00
2017 |  |  |  | 7535.97 |  |  | 7490 |  |  |  | 950 | [10 empty] | 86.52 |  |  |  | 86.52 | [5 empty] | 90.55 |  |  | 85.50 |  |  |  | 0.92 |  | 2.39 | [8 empty] | 11.09 |  |  |  |  | 0.00
2018 |  |  |  | 8736.46 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.76 |  |  |  | 99.76 | [5 empty] | 104.98 |  |  | 100.00 |  |  |  | 0.24 |  | 0.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7668.87 |  |  | 7745 |  |  |  | 950 | [10 empty] | 87.66 |  |  |  | 87.66 | [5 empty] | 92.15 |  |  | 88.41 |  |  |  | 0.70 |  | 0.61 | [8 empty] | 11.72 |  |  |  |  | 0.00
2020 |  |  |  | 7553.71 |  |  | 7638 |  |  |  | 950 | [10 empty] | 86.28 |  |  |  | 86.28 | [5 empty] | 90.52 |  |  | 86.95 |  |  |  | 1.93 |  | 1.69 | [8 empty] | 12.02 |  |  |  |  | 0.00
2021 |  |  |  | 8673.29 |  |  | 8657 |  |  |  | 950 | [10 empty] | 98.71 |  |  |  | 98.71 | [5 empty] | 104.22 |  |  | 98.82 |  |  |  | 1.29 |  | 1.29 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2012 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 103 | [14 empty] | 237
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 698
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 15
L. |  | Human factor related | [39 empty] | 8
Subtotal | [26 empty] | 103 | [10 empty] | 713 |  |  |  | 245
Total | [22 empty] | 103 | [14 empty] | 958
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2012 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [19 empty] | 69 | [14 empty] | 14
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 75
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
33. |  |  | Circulating Water System | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 71
42. |  |  | Electrical Power Supply Systems | [19 empty] | 34 | [14 empty] | 43
Total | [22 empty] | 103 | [14 empty] | 219
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-December. Additional electricity generation amounted to 491353 MWh. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-1
2021 Operating Experience
RU-12 | [8 empty] | KOLA-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-230 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-05-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-06-29
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-12-28
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 1849.44 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.16 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.16 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.84 %
Load Factor (LF) | [18 empty] | : | 51.37 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 73.13 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2354 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 2.18 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 142.49 | 132.72 |  |  |  | 6.12 |  | 26.39 | [8 empty] | 247.24 |  |  | 184.46 | [6 empty] | 104.25 |  | 0.00 |  |  |  | 232.13 |  |  | 272.76 |  |  | 216.96 | [9 empty] | 283.92 |  |  | 1849.44
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 35.49 |  | 10.45 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.16
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 35.49 |  | 10.45 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.16
LF [%] |  |  |  |  | 46.60 | 48.05 |  |  |  | 2.00 |  | 8.92 | [8 empty] | 80.85 |  |  | 62.33 | [6 empty] | 34.09 |  | 0.00 |  |  |  | 78.44 |  |  | 89.20 |  |  | 73.32 | [9 empty] | 92.85 |  |  | 51.37
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 9.14 |  | 14.03 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 65.86 |  | 0.00 |  |  |  | 91.53 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 73.13
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 64.51 |  | 89.55 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.84
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 111129.38 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.63 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.24 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.37 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.48 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 63.74 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 5.13 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.12 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 918.20 |  |  | 4180 |  |  |  | 411 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1974 |  |  |  | 1990.06 |  |  | 8463 |  |  |  | 411 | [10 empty] | 79.22 |  |  |  | 79.22 | [5 empty] | 55.27 |  |  | 96.61 |  |  |  | 0.90 |  | 0.72 | [8 empty] | 20.06 |  |  |  |  | 0.01
1975 |  |  |  | 1015.76 |  |  | 5426 |  |  |  | 411 | [10 empty] | 50.91 |  |  |  | 50.94 | [5 empty] | 28.21 |  |  | 61.94 |  |  |  | 1.27 |  | 0.66 | [8 empty] | 48.40 |  |  |  |  | 0.03
1976 |  |  |  | 2421.71 |  |  | 8247 |  |  |  | 411 | [10 empty] | 74.05 |  |  |  | 74.17 | [5 empty] | 67.08 |  |  | 93.89 |  |  |  | 0.97 |  | 0.73 | [8 empty] | 25.10 |  |  |  |  | 0.12
1977 |  |  |  | 2101.05 |  |  | 7462 |  |  |  | 411 | [10 empty] | 76.38 |  |  |  | 76.40 | [5 empty] | 58.36 |  |  | 85.18 |  |  |  | 6.73 |  | 5.52 | [8 empty] | 18.09 |  |  |  |  | 0.01
1978 |  |  |  | 2978.78 |  |  | 8074 |  |  |  | 411 | [10 empty] | 82.58 |  |  |  | 82.60 | [5 empty] | 82.74 |  |  | 92.17 |  |  |  | 1.55 |  | 1.30 | [8 empty] | 16.10 |  |  |  |  | 0.02
1979 |  |  |  | 2435.60 |  |  | 6232 |  |  |  | 411 | [10 empty] | 64.63 |  |  |  | 64.65 | [5 empty] | 67.65 |  |  | 71.14 |  |  |  | 2.14 |  | 1.41 | [8 empty] | 33.94 |  |  |  |  | 0.02
1980 |  |  |  | 3466.37 |  |  | 8072 |  |  |  | 411 | [10 empty] | 90.90 |  |  |  | 91.05 | [5 empty] | 96.02 |  |  | 91.89 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 8.65 |  |  |  |  | 0.15
1981 |  |  |  | 2870.79 |  |  | 7448 |  |  |  | 411 | [10 empty] | 80.94 |  |  |  | 80.95 | [5 empty] | 79.74 |  |  | 85.02 |  |  |  | 2.81 |  | 2.34 | [8 empty] | 16.71 |  |  |  |  | 0.01
1982 |  |  |  | 2848.07 |  |  | 7875 |  |  |  | 411 | [10 empty] | 85.52 |  |  |  | 85.52 | [5 empty] | 79.11 |  |  | 89.90 |  |  |  | 1.80 |  | 1.56 | [8 empty] | 12.91 |  |  |  |  | 0.01
1983 |  |  |  | 3217.37 |  |  | 7884 |  |  |  | 411 | [10 empty] | 88.25 |  |  |  | 88.27 | [5 empty] | 89.36 |  |  | 90.00 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 11.57 |  |  |  |  | 0.02
1984 |  |  |  | 3112.02 |  |  | 8060 |  |  |  | 411 | [10 empty] | 84.90 |  |  |  | 84.92 | [5 empty] | 86.20 |  |  | 91.76 |  |  |  | 1.41 |  | 1.22 | [8 empty] | 13.87 |  |  |  |  | 0.01
1985 |  |  |  | 2388.76 |  |  | 6001 |  |  |  | 411 | [10 empty] | 67.02 |  |  |  | 67.05 | [5 empty] | 66.35 |  |  | 68.50 |  |  |  | 0.61 |  | 0.41 | [8 empty] | 32.54 |  |  |  |  | 0.03
1986 |  |  |  | 2805.84 |  |  | 8074 |  |  |  | 411 | [10 empty] | 85.08 |  |  |  | 85.08 | [5 empty] | 77.93 |  |  | 92.17 |  |  |  | 5.88 |  | 5.32 | [8 empty] | 9.60 |  |  |  |  | 0.00
1987 |  |  |  | 3268.23 |  |  | 7972 |  |  |  | 440 | [10 empty] | 86.00 |  |  |  | 86.00 | [5 empty] | 84.79 |  |  | 91.00 |  |  |  | 0.96 |  | 0.83 | [8 empty] | 13.17 |  |  |  |  | 0.00
1988 |  |  |  | 2925.01 |  |  | 7482 |  |  |  | 411 | [10 empty] | 82.67 |  |  |  | 82.73 | [5 empty] | 81.02 |  |  | 85.18 |  |  |  | 6.53 |  | 5.78 | [8 empty] | 11.49 |  |  |  |  | 0.06
1989 |  |  |  | 2675.48 |  |  | 6731 |  |  |  | 411 | [10 empty] | 75.44 |  |  |  | 76.23 | [5 empty] | 74.31 |  |  | 76.84 |  |  |  | 1.18 |  | 0.91 | [8 empty] | 22.86 |  |  |  |  | 0.79
1990 |  |  |  | 2735.50 |  |  | 6838 |  |  |  | 411 | [10 empty] | 75.95 |  |  |  | 75.95 | [5 empty] | 75.98 |  |  | 78.06 |  |  |  | 2.00 |  | 1.55 | [8 empty] | 22.50 |  |  |  |  | 0.00
1991 |  |  |  | 2773.12 |  |  | 6965 |  |  |  | 411 | [10 empty] | 77.27 |  |  |  | 77.27 | [5 empty] | 77.02 |  |  | 79.51 |  |  |  | 7.17 |  | 5.97 | [8 empty] | 16.76 |  |  |  |  | 0.00
1992 |  |  |  | 2271.37 |  |  | 6651 |  |  |  | 411 | [10 empty] | 63.44 |  |  |  | 63.70 | [5 empty] | 62.92 |  |  | 75.73 |  |  |  | 17.65 |  | 13.65 | [8 empty] | 22.65 |  |  |  |  | 0.26
1993 |  |  |  | 1992.62 |  |  | 5663 |  |  |  | 411 | [10 empty] | 56.14 |  |  |  | 59.56 | [5 empty] | 55.35 |  |  | 64.65 |  |  |  | 14.77 |  | 10.32 | [8 empty] | 30.11 |  |  |  |  | 3.42
1994 |  |  |  | 1971.62 |  |  | 5359 |  |  |  | 411 | [10 empty] | 56.50 |  |  |  | 58.63 | [5 empty] | 54.76 |  |  | 61.18 |  |  |  | 7.34 |  | 4.65 | [8 empty] | 36.72 |  |  |  |  | 2.13
1995 |  |  |  | 1581.37 |  |  | 5398 |  |  |  | 411 | [10 empty] | 62.24 |  |  |  | 62.24 | [5 empty] | 43.92 |  |  | 61.62 |  |  |  | 5.06 |  | 3.32 | [8 empty] | 34.44 |  |  |  |  | 0.00
1996 |  |  |  | 1409.96 |  |  | 4466 |  |  |  | 411 | [10 empty] | 46.43 |  |  |  | 47.44 | [5 empty] | 39.05 |  |  | 50.84 |  |  |  | 6.51 |  | 3.30 | [8 empty] | 49.26 |  |  |  |  | 1.00
1997 |  |  |  | 2404.12 |  |  | 7942 |  |  |  | 411 | [10 empty] | 88.48 |  |  |  | 88.48 | [5 empty] | 66.77 |  |  | 90.66 |  |  |  | 5.02 |  | 4.68 | [8 empty] | 6.84 |  |  |  |  | 0.00
1998 |  |  |  | 1291.73 |  |  | 5658 |  |  |  | 411 | [10 empty] | 37.66 |  |  |  | 59.27 | [5 empty] | 35.88 |  |  | 64.59 |  |  |  | 12.77 |  | 8.68 | [8 empty] | 32.05 |  |  |  |  | 21.61
1999 |  |  |  | 2028.49 |  |  | 7355 |  |  |  | 411 | [10 empty] | 58.01 |  |  |  | 86.57 | [5 empty] | 56.34 |  |  | 83.96 |  |  |  | 0.97 |  | 0.85 | [8 empty] | 12.58 |  |  |  |  | 28.56
2000 |  |  |  | 1298.85 |  |  | 4643 |  |  |  | 411 | [10 empty] | 37.17 |  |  |  | 84.13 | [5 empty] | 35.98 |  |  | 52.86 |  |  |  | 0.80 |  | 0.68 | [8 empty] | 15.19 |  |  |  |  | 46.96
2001 |  |  |  | 2243.22 |  |  | 7098 |  |  |  | 411 | [10 empty] | 63.27 |  |  |  | 81.60 | [5 empty] | 62.31 |  |  | 81.03 |  |  |  | 0.91 |  | 0.75 | [8 empty] | 17.65 |  |  |  |  | 18.33
2002 |  |  |  | 1841.48 |  |  | 5660 |  |  |  | 411 | [10 empty] | 51.65 |  |  |  | 68.90 | [5 empty] | 51.15 |  |  | 64.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.10 |  |  |  |  | 17.25
2003 |  |  |  | 2164.00 |  |  | 6444 |  |  |  | 411 | [10 empty] | 60.41 |  |  |  | 75.51 | [5 empty] | 60.11 |  |  | 73.56 |  |  |  | 0.73 |  | 0.55 | [8 empty] | 23.94 |  |  |  |  | 15.10
2004 |  |  |  | 2440.48 |  |  | 7326 |  |  |  | 411 | [10 empty] | 68.21 |  |  |  | 83.64 | [5 empty] | 67.60 |  |  | 83.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.36 |  |  |  |  | 15.43
2005 |  |  |  | 2151.67 |  |  | 6901 |  |  |  | 411 | [10 empty] | 60.60 |  |  |  | 90.57 | [5 empty] | 59.76 |  |  | 78.78 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.43 |  |  |  |  | 29.97
2006 |  |  |  | 2338.66 |  |  | 7661 |  |  |  | 411 | [10 empty] | 65.95 |  |  |  | 89.94 | [5 empty] | 64.96 |  |  | 87.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.06 |  |  |  |  | 23.98
2007 |  |  |  | 2658.02 |  |  | 7740 |  |  |  | 411 | [10 empty] | 74.43 |  |  |  | 90.96 | [5 empty] | 73.83 |  |  | 88.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.04 |  |  |  |  | 16.53
2008 |  |  |  | 2705.75 |  |  | 7397 |  |  |  | 411 | [10 empty] | 84.34 |  |  |  | 84.34 | [5 empty] | 74.95 |  |  | 84.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.66 |  |  |  |  | 0.00
2009 |  |  |  | 2277.43 |  |  | 7333 |  |  |  | 411 | [10 empty] | 83.76 |  |  |  | 83.77 | [5 empty] | 63.26 |  |  | 83.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.23 |  |  |  |  | 0.01
2010 |  |  |  | 2467.97 |  |  | 7912 |  |  |  | 411 | [10 empty] | 85.79 |  |  |  | 85.82 | [5 empty] | 68.55 |  |  | 90.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.18 |  |  |  |  | 0.03
2011 |  |  |  | 2465.32 |  |  | 7870 |  |  |  | 411 | [10 empty] | 83.47 |  |  |  | 83.62 | [5 empty] | 68.48 |  |  | 89.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.38 |  |  |  |  | 0.15
2012 |  |  |  | 2205.74 |  |  | 7021 |  |  |  | 411 | [10 empty] | 82.24 |  |  |  | 82.24 | [5 empty] | 61.10 |  |  | 79.93 |  |  |  | 1.67 |  | 1.39 | [8 empty] | 16.37 |  |  |  |  | 0.00
2013 |  |  |  | 2380.88 |  |  | 7811 |  |  |  | 411 | [10 empty] | 83.98 |  |  |  | 83.98 | [5 empty] | 66.13 |  |  | 89.17 |  |  |  | 4.60 |  | 4.05 | [8 empty] | 11.97 |  |  |  |  | 0.00
2014 |  |  |  | 1911.66 |  |  | 7536 |  |  |  | 411 | [10 empty] | 85.18 |  |  |  | 86.19 | [5 empty] | 53.09 |  |  | 86.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.81 |  |  |  |  | 1.01
2015 |  |  |  | 2112.22 |  |  | 7373 |  |  |  | 411 | [10 empty] | 83.10 |  |  |  | 84.00 | [5 empty] | 58.67 |  |  | 84.17 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 15.99 |  |  |  |  | 0.91
2016 |  |  |  | 2097.80 |  |  | 6386 |  |  |  | 411 | [10 empty] | 78.45 |  |  |  | 78.45 | [5 empty] | 58.11 |  |  | 72.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.55 |  |  |  |  | 0.00
2017 |  |  |  | 1982.33 |  |  | 7025 |  |  |  | 411 | [10 empty] | 77.78 |  |  |  | 78.62 | [5 empty] | 55.06 |  |  | 80.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.38 |  |  |  |  | 0.84
2018 |  |  |  | 688.02 |  |  | 2652 |  |  |  | 411 | [10 empty] | 28.92 |  |  |  | 30.25 | [5 empty] | 19.11 |  |  | 30.27 |  |  |  | 5.22 |  | 1.97 | [8 empty] | 67.78 |  |  |  |  | 1.33
2019 |  |  |  | 2796.96 |  |  | 7740 |  |  |  | 411 | [10 empty] | 80.24 |  |  |  | 80.62 | [5 empty] | 77.69 |  |  | 88.36 |  |  |  | 6.14 |  | 7.61 | [8 empty] | 11.77 |  |  |  |  | 0.38
2020 |  |  |  | 2327.08 |  |  | 7193 |  |  |  | 411 | [10 empty] | 84.03 |  |  |  | 84.03 | [5 empty] | 64.46 |  |  | 81.89 |  |  |  | 0.07 |  | 0.05 | [8 empty] | 15.92 |  |  |  |  | 0.00
2021 |  |  |  | 1849.44 |  |  | 6406 |  |  |  | 411 | [10 empty] | 87.16 |  |  |  | 87.16 | [5 empty] | 51.37 |  |  | 73.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.84 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1973 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 48
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1099 | [14 empty] | 1483 |  |  |  | 3
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 75
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 54
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 39
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 1254 | [19 empty] | 142
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 5
Z. |  | Other | [39 empty] | 8
Subtotal | [22 empty] | 1099 | [10 empty] | 1254 |  |  |  | 1612 |  |  |  | 60 | [11 empty] | 188
Total | [22 empty] | 2353 | [14 empty] | 1860
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1973 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 13
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [37 empty] | 48
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in April, May, September, December. Additional electricity generation amounted to 3400 MWh. The unit was in the intermediate outage from 2021.03.12 to 2021.04.28. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-2
2021 Operating Experience
RU-13 | [8 empty] | KOLA-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-230 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-05-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-12-09
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-02-21
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 1752.16 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.43 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 81.4 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 18.6 %
Load Factor (LF) | [18 empty] | : | 48.67 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.97 %
Operating Factor (OF) | [18 empty] | : | 79.12 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1829 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0.7 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 146.46 | 135.92 |  |  |  | 239.36 |  | 158.49 | [8 empty] | 293.10 |  |  | 245.52 | [6 empty] | 139.36 |  | 143.73 |  |  |  | 9.99 |  |  | 0.00 |  |  | 39.60 | [9 empty] | 200.64 |  |  | 1752.15
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.85 |  | 90.91 |  |  |  | 37.74 |  |  | 0.01 |  |  | 37.00 | [9 empty] | 100.00 |  |  | 80.43
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 40.01 |  |  | 0.01 |  |  | 37.00 | [9 empty] | 100.00 |  |  | 81.40
LF [%] |  |  |  |  | 47.90 | 49.21 |  |  |  | 78.28 |  | 53.56 | [8 empty] | 95.85 |  |  | 82.97 | [6 empty] | 45.57 |  | 47.00 |  |  |  | 3.38 |  |  | 0.00 |  |  | 13.38 | [9 empty] | 65.61 |  |  | 48.67
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 11.39 |  |  | 0.00 |  |  | 37.92 | [9 empty] | 100.00 |  |  | 79.12
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 59.99 |  |  | 99.99 |  |  | 63.00 | [9 empty] | 0.00 |  |  | 18.60
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.15 |  | 9.09 |  |  |  | 2.26 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.97
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 107933.47 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.66 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.94 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.11 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.42 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.46 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 63.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 4.49 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.81 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 1383.07 |  |  | 6449 |  |  |  | 411 | [10 empty] | 88.23 |  |  |  | 88.23 | [5 empty] | 37.48 |  |  | 73.97 |  |  |  | 3.66 |  | 3.35 | [8 empty] | 8.41 |  |  |  |  | 0.00
1976 |  |  |  | 1943.15 |  |  | 7083 |  |  |  | 411 | [10 empty] | 70.82 |  |  |  | 70.82 | [5 empty] | 53.82 |  |  | 80.64 |  |  |  | 0.74 |  | 0.53 | [8 empty] | 28.65 |  |  |  |  | 0.00
1977 |  |  |  | 2627.24 |  |  | 7038 |  |  |  | 411 | [10 empty] | 76.90 |  |  |  | 77.05 | [5 empty] | 72.97 |  |  | 80.34 |  |  |  | 1.10 |  | 0.85 | [8 empty] | 22.09 |  |  |  |  | 0.15
1978 |  |  |  | 2982.47 |  |  | 7576 |  |  |  | 411 | [10 empty] | 82.71 |  |  |  | 82.71 | [5 empty] | 82.84 |  |  | 86.48 |  |  |  | 0.67 |  | 0.56 | [8 empty] | 16.73 |  |  |  |  | 0.00
1979 |  |  |  | 3057.59 |  |  | 7663 |  |  |  | 411 | [10 empty] | 82.40 |  |  |  | 83.51 | [5 empty] | 84.92 |  |  | 87.48 |  |  |  | 3.13 |  | 2.70 | [8 empty] | 13.79 |  |  |  |  | 1.11
1980 |  |  |  | 3266.85 |  |  | 7966 |  |  |  | 411 | [10 empty] | 85.80 |  |  |  | 85.99 | [5 empty] | 90.49 |  |  | 90.69 |  |  |  | 0.71 |  | 0.62 | [8 empty] | 13.40 |  |  |  |  | 0.19
1981 |  |  |  | 3146.68 |  |  | 8225 |  |  |  | 411 | [10 empty] | 87.78 |  |  |  | 87.78 | [5 empty] | 87.40 |  |  | 93.89 |  |  |  | 2.81 |  | 2.54 | [8 empty] | 9.68 |  |  |  |  | 0.00
1982 |  |  |  | 2462.96 |  |  | 6742 |  |  |  | 411 | [10 empty] | 71.24 |  |  |  | 71.24 | [5 empty] | 68.41 |  |  | 76.96 |  |  |  | 3.13 |  | 2.30 | [8 empty] | 26.46 |  |  |  |  | 0.00
1983 |  |  |  | 3072.64 |  |  | 7963 |  |  |  | 411 | [10 empty] | 85.27 |  |  |  | 85.30 | [5 empty] | 85.34 |  |  | 90.90 |  |  |  | 3.18 |  | 2.80 | [8 empty] | 11.90 |  |  |  |  | 0.03
1984 |  |  |  | 3034.45 |  |  | 8079 |  |  |  | 411 | [10 empty] | 86.75 |  |  |  | 86.76 | [5 empty] | 84.05 |  |  | 91.97 |  |  |  | 1.97 |  | 1.74 | [8 empty] | 11.50 |  |  |  |  | 0.00
1985 |  |  |  | 3055.56 |  |  | 7872 |  |  |  | 411 | [10 empty] | 84.90 |  |  |  | 84.94 | [5 empty] | 84.87 |  |  | 89.86 |  |  |  | 3.18 |  | 2.79 | [8 empty] | 12.27 |  |  |  |  | 0.04
1986 |  |  |  | 2844.15 |  |  | 7405 |  |  |  | 411 | [10 empty] | 79.74 |  |  |  | 79.78 | [5 empty] | 79.00 |  |  | 84.53 |  |  |  | 4.19 |  | 3.49 | [8 empty] | 16.73 |  |  |  |  | 0.04
1987 |  |  |  | 3345.38 |  |  | 7900 |  |  |  | 440 | [10 empty] | 89.59 |  |  |  | 89.59 | [5 empty] | 86.79 |  |  | 90.18 |  |  |  | 0.58 |  | 0.52 | [8 empty] | 9.89 |  |  |  |  | 0.00
1988 |  |  |  | 2873.27 |  |  | 7451 |  |  |  | 411 | [10 empty] | 80.46 |  |  |  | 80.49 | [5 empty] | 79.59 |  |  | 84.82 |  |  |  | 5.60 |  | 4.78 | [8 empty] | 14.73 |  |  |  |  | 0.03
1989 |  |  |  | 2707.27 |  |  | 6859 |  |  |  | 411 | [10 empty] | 74.79 |  |  |  | 78.05 | [5 empty] | 75.19 |  |  | 78.30 |  |  |  | 0.67 |  | 0.52 | [8 empty] | 21.43 |  |  |  |  | 3.26
1990 |  |  |  | 2610.91 |  |  | 6751 |  |  |  | 411 | [10 empty] | 72.72 |  |  |  | 72.86 | [5 empty] | 72.52 |  |  | 77.07 |  |  |  | 6.09 |  | 4.73 | [8 empty] | 22.42 |  |  |  |  | 0.14
1991 |  |  |  | 2701.86 |  |  | 6983 |  |  |  | 411 | [10 empty] | 75.33 |  |  |  | 75.41 | [5 empty] | 75.04 |  |  | 79.71 |  |  |  | 11.29 |  | 9.60 | [8 empty] | 14.99 |  |  |  |  | 0.08
1992 |  |  |  | 2133.04 |  |  | 5871 |  |  |  | 411 | [10 empty] | 61.85 |  |  |  | 61.85 | [5 empty] | 59.09 |  |  | 66.85 |  |  |  | 16.94 |  | 12.61 | [8 empty] | 25.54 |  |  |  |  | 0.00
1993 |  |  |  | 2138.83 |  |  | 6377 |  |  |  | 411 | [10 empty] | 60.68 |  |  |  | 65.73 | [5 empty] | 59.41 |  |  | 72.80 |  |  |  | 7.71 |  | 5.49 | [8 empty] | 28.77 |  |  |  |  | 5.05
1994 |  |  |  | 398.60 |  |  | 1466 |  |  |  | 411 | [10 empty] | 16.68 |  |  |  | 16.68 | [5 empty] | 11.07 |  |  | 16.74 |  |  |  | 18.79 |  | 3.86 | [8 empty] | 79.46 |  |  |  |  | 0.00
1995 |  |  |  | 2205.78 |  |  | 6846 |  |  |  | 411 | [10 empty] | 93.58 |  |  |  | 93.58 | [5 empty] | 61.27 |  |  | 78.15 |  |  |  | 2.08 |  | 1.99 | [8 empty] | 4.43 |  |  |  |  | 0.00
1996 |  |  |  | 1946.17 |  |  | 6243 |  |  |  | 411 | [10 empty] | 65.47 |  |  |  | 66.30 | [5 empty] | 53.91 |  |  | 71.07 |  |  |  | 3.53 |  | 2.43 | [8 empty] | 31.27 |  |  |  |  | 0.84
1997 |  |  |  | 1157.94 |  |  | 3955 |  |  |  | 411 | [10 empty] | 40.64 |  |  |  | 53.44 | [5 empty] | 32.16 |  |  | 45.15 |  |  |  | 3.35 |  | 1.85 | [8 empty] | 44.70 |  |  |  |  | 12.80
1998 |  |  |  | 2655.63 |  |  | 8029 |  |  |  | 411 | [10 empty] | 74.46 |  |  |  | 83.64 | [5 empty] | 73.76 |  |  | 91.66 |  |  |  | 8.88 |  | 8.15 | [8 empty] | 8.22 |  |  |  |  | 9.18
1999 |  |  |  | 1272.59 |  |  | 4423 |  |  |  | 411 | [10 empty] | 36.30 |  |  |  | 48.99 | [5 empty] | 35.35 |  |  | 50.49 |  |  |  | 17.19 |  | 10.17 | [8 empty] | 40.84 |  |  |  |  | 12.69
2000 |  |  |  | 2430.51 |  |  | 7626 |  |  |  | 411 | [10 empty] | 68.16 |  |  |  | 83.38 | [5 empty] | 67.32 |  |  | 86.82 |  |  |  | 2.56 |  | 2.19 | [8 empty] | 14.43 |  |  |  |  | 15.22
2001 |  |  |  | 1722.31 |  |  | 6574 |  |  |  | 411 | [10 empty] | 49.08 |  |  |  | 84.74 | [5 empty] | 47.84 |  |  | 75.05 |  |  |  | 1.21 |  | 1.03 | [8 empty] | 14.22 |  |  |  |  | 35.67
2002 |  |  |  | 1738.75 |  |  | 5564 |  |  |  | 411 | [10 empty] | 48.66 |  |  |  | 83.24 | [5 empty] | 48.29 |  |  | 63.52 |  |  |  | 0.30 |  | 0.25 | [8 empty] | 16.51 |  |  |  |  | 34.58
2003 |  |  |  | 1866.10 |  |  | 5459 |  |  |  | 411 | [10 empty] | 52.04 |  |  |  | 66.40 | [5 empty] | 51.83 |  |  | 62.32 |  |  |  | 0.54 |  | 0.36 | [8 empty] | 33.24 |  |  |  |  | 14.37
2004 |  |  |  | 1787.07 |  |  | 5731 |  |  |  | 411 | [10 empty] | 49.92 |  |  |  | 73.84 | [5 empty] | 49.50 |  |  | 65.24 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 26.12 |  |  |  |  | 23.93
2005 |  |  |  | 2889.18 |  |  | 7379 |  |  |  | 411 | [10 empty] | 78.59 |  |  |  | 84.24 | [5 empty] | 80.25 |  |  | 84.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.76 |  |  |  |  | 5.65
2006 |  |  |  | 2640.13 |  |  | 7597 |  |  |  | 411 | [10 empty] | 71.98 |  |  |  | 85.73 | [5 empty] | 73.33 |  |  | 86.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.27 |  |  |  |  | 13.75
2007 |  |  |  | 2508.92 |  |  | 7474 |  |  |  | 411 | [10 empty] | 70.10 |  |  |  | 85.69 | [5 empty] | 69.69 |  |  | 85.32 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 14.14 |  |  |  |  | 15.59
2008 |  |  |  | 2554.70 |  |  | 7762 |  |  |  | 411 | [10 empty] | 89.13 |  |  |  | 89.92 | [5 empty] | 70.76 |  |  | 88.37 |  |  |  | 1.32 |  | 1.20 | [8 empty] | 8.88 |  |  |  |  | 0.79
2009 |  |  |  | 2384.55 |  |  | 6872 |  |  |  | 411 | [10 empty] | 79.44 |  |  |  | 80.28 | [5 empty] | 66.23 |  |  | 78.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.72 |  |  |  |  | 0.84
2010 |  |  |  | 2531.18 |  |  | 7619 |  |  |  | 411 | [10 empty] | 90.18 |  |  |  | 90.41 | [5 empty] | 70.30 |  |  | 86.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.59 |  |  |  |  | 0.24
2011 |  |  |  | 2501.98 |  |  | 7752 |  |  |  | 411 | [10 empty] | 83.07 |  |  |  | 83.63 | [5 empty] | 69.50 |  |  | 88.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.37 |  |  |  |  | 0.56
2012 |  |  |  | 2192.07 |  |  | 7775 |  |  |  | 411 | [10 empty] | 81.85 |  |  |  | 81.85 | [5 empty] | 60.72 |  |  | 88.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.14 |  |  |  |  | 0.00
2013 |  |  |  | 2412.70 |  |  | 7233 |  |  |  | 411 | [10 empty] | 82.80 |  |  |  | 82.80 | [5 empty] | 67.01 |  |  | 82.57 |  |  |  | 1.51 |  | 1.27 | [8 empty] | 15.93 |  |  |  |  | 0.00
2014 |  |  |  | 2596.45 |  |  | 7823 |  |  |  | 411 | [10 empty] | 89.32 |  |  |  | 90.15 | [5 empty] | 72.11 |  |  | 89.29 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 9.82 |  |  |  |  | 0.83
2015 |  |  |  | 1463.78 |  |  | 5450 |  |  |  | 411 | [10 empty] | 85.32 |  |  |  | 85.32 | [5 empty] | 40.66 |  |  | 62.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.68 |  |  |  |  | 0.00
2016 |  |  |  | 2053.14 |  |  | 6416 |  |  |  | 411 | [10 empty] | 79.35 |  |  |  | 79.79 | [5 empty] | 56.87 |  |  | 73.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.21 |  |  |  |  | 0.43
2017 |  |  |  | 1787.16 |  |  | 5615 |  |  |  | 411 | [10 empty] | 83.48 |  |  |  | 83.48 | [5 empty] | 49.64 |  |  | 64.10 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 16.45 |  |  |  |  | 0.00
2018 |  |  |  | 2765.53 |  |  | 7437 |  |  |  | 411 | [10 empty] | 84.10 |  |  |  | 84.42 | [5 empty] | 76.81 |  |  | 84.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.58 |  |  |  |  | 0.32
2019 |  |  |  | 670.53 |  |  | 1904 |  |  |  | 411 | [10 empty] | 20.38 |  |  |  | 21.54 | [5 empty] | 18.62 |  |  | 21.74 |  |  |  | 8.76 |  | 2.07 | [8 empty] | 76.39 |  |  |  |  | 1.17
2020 |  |  |  | 1890.68 |  |  | 7188 |  |  |  | 411 | [10 empty] | 86.71 |  |  |  | 86.71 | [5 empty] | 52.37 |  |  | 81.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.29 |  |  |  |  | 0.01
2021 |  |  |  | 1752.15 |  |  | 6931 |  |  |  | 411 | [10 empty] | 80.43 |  |  |  | 81.40 | [5 empty] | 48.67 |  |  | 79.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.60 |  |  |  |  | 0.97
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1975 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 66
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1623 | [14 empty] | 1484
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 53
E. |  | Testing of plant systems or components | [35 empty] | 7
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 105
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 28
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 206 | [19 empty] | 243
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Z. |  | Other | [39 empty] | 0
Subtotal | [22 empty] | 1623 | [10 empty] | 206 |  |  |  | 1649 |  |  |  | 71 | [11 empty] | 273
Total | [22 empty] | 1829 | [14 empty] | 1993
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1975 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 38
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 16
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 66
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in April-June. Additional electricity generation amounted to 5491 MWh. The unit was in the overhaul outage from 2021.09.13 to 2021.11.19. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-3
2021 Operating Experience
RU-32 | [8 empty] | KOLA-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-04-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-03-24
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1982-12-03
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 2539.74 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.53 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.91 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.44 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.91 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.65 %
Load Factor (LF) | [18 empty] | : | 70.54 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 80.34 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1722 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 1.83 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 317.34 | 276.72 |  |  |  | 298.57 |  | 181.44 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 201.78 |  | 173.74 |  |  |  | 287.50 |  |  | 252.29 |  |  | 277.27 | [9 empty] | 273.10 |  |  | 2539.74
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 9.69 |  |  | 0.01 | [6 empty] | 91.07 |  | 96.36 |  |  |  | 100.00 |  |  | 98.46 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.91
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 9.69 |  |  | 0.01 | [6 empty] | 91.07 |  | 96.36 |  |  |  | 100.00 |  |  | 98.46 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.91
LF [%] |  |  |  |  | 103.78 | 100.19 |  |  |  | 97.64 |  | 61.31 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 65.99 |  | 56.82 |  |  |  | 97.15 |  |  | 82.51 |  |  | 93.70 | [9 empty] | 89.31 |  |  | 70.54
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 67.64 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 97.85 |  | 98.79 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.34
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 3.64 |  |  |  | 0.00 |  |  | 1.54 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.53
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 3.64 |  |  |  | 0.00 |  |  | 1.54 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.44
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 90.31 |  |  | 99.99 | [6 empty] | 8.93 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.65
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 101032.45 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.33 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.58 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.98 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.37 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.65 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.03 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 5.79 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.25 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1982 |  |  |  | 1891.17 |  |  | 7252 |  |  |  | 411 | [10 empty] | 99.35 |  |  |  | 99.38 | [5 empty] | 98.74 |  |  | 100.00 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 0.54 |  |  |  |  | 0.03
1983 |  |  |  | 2459.86 |  |  | 6818 |  |  |  | 411 | [10 empty] | 71.98 |  |  |  | 71.99 | [5 empty] | 68.32 |  |  | 77.83 |  |  |  | 3.90 |  | 2.92 | [8 empty] | 25.09 |  |  |  |  | 0.01
1984 |  |  |  | 2830.67 |  |  | 7610 |  |  |  | 411 | [10 empty] | 82.71 |  |  |  | 82.71 | [5 empty] | 78.41 |  |  | 86.63 |  |  |  | 1.76 |  | 1.48 | [8 empty] | 15.80 |  |  |  |  | 0.01
1985 |  |  |  | 2972.56 |  |  | 7814 |  |  |  | 411 | [10 empty] | 86.68 |  |  |  | 86.77 | [5 empty] | 82.56 |  |  | 89.20 |  |  |  | 2.25 |  | 2.00 | [8 empty] | 11.23 |  |  |  |  | 0.09
1986 |  |  |  | 2627.25 |  |  | 7244 |  |  |  | 411 | [10 empty] | 74.11 |  |  |  | 74.11 | [5 empty] | 72.97 |  |  | 82.69 |  |  |  | 16.48 |  | 14.62 | [8 empty] | 11.27 |  |  |  |  | 0.00
1987 |  |  |  | 2837.81 |  |  | 7024 |  |  |  | 440 | [10 empty] | 74.79 |  |  |  | 74.79 | [5 empty] | 73.63 |  |  | 80.18 |  |  |  | 6.83 |  | 5.49 | [8 empty] | 19.73 |  |  |  |  | 0.00
1988 |  |  |  | 2933.19 |  |  | 7913 |  |  |  | 411 | [10 empty] | 81.43 |  |  |  | 81.52 | [5 empty] | 81.25 |  |  | 90.08 |  |  |  | 4.73 |  | 4.05 | [8 empty] | 14.44 |  |  |  |  | 0.08
1989 |  |  |  | 3186.68 |  |  | 8047 |  |  |  | 411 | [10 empty] | 87.85 |  |  |  | 90.50 | [5 empty] | 88.51 |  |  | 91.86 |  |  |  | 0.81 |  | 0.74 | [8 empty] | 8.76 |  |  |  |  | 2.65
1990 |  |  |  | 3256.91 |  |  | 8022 |  |  |  | 411 | [10 empty] | 89.72 |  |  |  | 89.77 | [5 empty] | 90.46 |  |  | 91.58 |  |  |  | 0.95 |  | 0.87 | [8 empty] | 9.37 |  |  |  |  | 0.05
1991 |  |  |  | 2935.21 |  |  | 7188 |  |  |  | 411 | [10 empty] | 79.78 |  |  |  | 79.78 | [5 empty] | 81.53 |  |  | 82.05 |  |  |  | 2.74 |  | 2.25 | [8 empty] | 17.97 |  |  |  |  | 0.00
1992 |  |  |  | 2806.37 |  |  | 7396 |  |  |  | 411 | [10 empty] | 87.75 |  |  |  | 87.95 | [5 empty] | 77.74 |  |  | 84.21 |  |  |  | 2.36 |  | 2.13 | [8 empty] | 9.93 |  |  |  |  | 0.20
1993 |  |  |  | 2548.00 |  |  | 6833 |  |  |  | 411 | [10 empty] | 70.46 |  |  |  | 81.91 | [5 empty] | 70.77 |  |  | 78.00 |  |  |  | 1.41 |  | 1.17 | [8 empty] | 16.93 |  |  |  |  | 11.45
1994 |  |  |  | 2466.01 |  |  | 6373 |  |  |  | 411 | [10 empty] | 70.82 |  |  |  | 70.90 | [5 empty] | 68.49 |  |  | 72.75 |  |  |  | 10.76 |  | 8.55 | [8 empty] | 20.55 |  |  |  |  | 0.08
1995 |  |  |  | 2526.12 |  |  | 7083 |  |  |  | 411 | [10 empty] | 80.64 |  |  |  | 81.00 | [5 empty] | 70.16 |  |  | 80.86 |  |  |  | 0.82 |  | 0.67 | [8 empty] | 18.33 |  |  |  |  | 0.36
1996 |  |  |  | 2327.31 |  |  | 6928 |  |  |  | 411 | [10 empty] | 79.77 |  |  |  | 79.77 | [5 empty] | 64.46 |  |  | 78.87 |  |  |  | 5.33 |  | 4.49 | [8 empty] | 15.74 |  |  |  |  | 0.00
1997 |  |  |  | 2340.50 |  |  | 7114 |  |  |  | 411 | [10 empty] | 74.96 |  |  |  | 78.46 | [5 empty] | 65.01 |  |  | 81.21 |  |  |  | 0.56 |  | 0.44 | [8 empty] | 21.11 |  |  |  |  | 3.49
1998 |  |  |  | 2006.34 |  |  | 6705 |  |  |  | 411 | [10 empty] | 56.35 |  |  |  | 86.29 | [5 empty] | 55.73 |  |  | 76.54 |  |  |  | 4.27 |  | 3.85 | [8 empty] | 9.86 |  |  |  |  | 29.94
1999 |  |  |  | 2140.57 |  |  | 7040 |  |  |  | 411 | [10 empty] | 59.90 |  |  |  | 72.59 | [5 empty] | 59.45 |  |  | 80.37 |  |  |  | 9.77 |  | 7.86 | [8 empty] | 19.55 |  |  |  |  | 12.69
2000 |  |  |  | 2244.74 |  |  | 7731 |  |  |  | 411 | [10 empty] | 62.46 |  |  |  | 87.91 | [5 empty] | 62.18 |  |  | 88.01 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 12.02 |  |  |  |  | 25.46
2001 |  |  |  | 2543.29 |  |  | 7057 |  |  |  | 411 | [10 empty] | 70.64 |  |  |  | 85.28 | [5 empty] | 70.64 |  |  | 80.56 |  |  |  | 1.10 |  | 0.95 | [8 empty] | 13.77 |  |  |  |  | 14.64
2002 |  |  |  | 2742.35 |  |  | 7909 |  |  |  | 411 | [10 empty] | 75.89 |  |  |  | 91.39 | [5 empty] | 76.17 |  |  | 90.29 |  |  |  | 0.43 |  | 0.40 | [8 empty] | 8.21 |  |  |  |  | 15.51
2003 |  |  |  | 2740.72 |  |  | 7335 |  |  |  | 411 | [10 empty] | 75.61 |  |  |  | 83.69 | [5 empty] | 76.12 |  |  | 83.73 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 16.26 |  |  |  |  | 8.08
2004 |  |  |  | 2816.85 |  |  | 7688 |  |  |  | 411 | [10 empty] | 77.37 |  |  |  | 88.10 | [5 empty] | 78.02 |  |  | 87.52 |  |  |  | 0.57 |  | 0.51 | [8 empty] | 11.39 |  |  |  |  | 10.73
2005 |  |  |  | 2059.39 |  |  | 7672 |  |  |  | 411 | [10 empty] | 57.64 |  |  |  | 88.49 | [5 empty] | 57.19 |  |  | 87.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.51 |  |  |  |  | 30.85
2006 |  |  |  | 2294.60 |  |  | 7436 |  |  |  | 411 | [10 empty] | 64.00 |  |  |  | 89.99 | [5 empty] | 63.73 |  |  | 84.89 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 9.97 |  |  |  |  | 25.99
2007 |  |  |  | 1815.27 |  |  | 6506 |  |  |  | 411 | [10 empty] | 50.72 |  |  |  | 82.86 | [5 empty] | 50.42 |  |  | 74.27 |  |  |  | 1.49 |  | 1.25 | [8 empty] | 15.89 |  |  |  |  | 32.14
2008 |  |  |  | 1876.73 |  |  | 7405 |  |  |  | 411 | [10 empty] | 83.82 |  |  |  | 83.82 | [5 empty] | 51.98 |  |  | 84.30 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 16.15 |  |  |  |  | 0.00
2009 |  |  |  | 2050.45 |  |  | 7340 |  |  |  | 411 | [10 empty] | 83.13 |  |  |  | 83.85 | [5 empty] | 56.95 |  |  | 83.79 |  |  |  | 0.10 |  | 0.08 | [8 empty] | 16.07 |  |  |  |  | 0.71
2010 |  |  |  | 1979.23 |  |  | 6009 |  |  |  | 411 | [10 empty] | 71.48 |  |  |  | 71.48 | [5 empty] | 54.97 |  |  | 68.60 |  |  |  | 1.03 |  | 0.75 | [8 empty] | 27.78 |  |  |  |  | 0.00
2011 |  |  |  | 2288.62 |  |  | 6405 |  |  |  | 411 | [10 empty] | 71.67 |  |  |  | 71.67 | [5 empty] | 63.57 |  |  | 73.12 |  |  |  | 2.56 |  | 1.89 | [8 empty] | 26.45 |  |  |  |  | 0.00
2012 |  |  |  | 2226.17 |  |  | 6701 |  |  |  | 411 | [10 empty] | 78.13 |  |  |  | 78.13 | [5 empty] | 61.66 |  |  | 76.29 |  |  |  | 1.74 |  | 1.38 | [8 empty] | 20.49 |  |  |  |  | 0.00
2013 |  |  |  | 2264.33 |  |  | 6396 |  |  |  | 411 | [10 empty] | 73.80 |  |  |  | 73.80 | [5 empty] | 62.89 |  |  | 73.01 |  |  |  | 2.75 |  | 2.09 | [8 empty] | 24.11 |  |  |  |  | 0.00
2014 |  |  |  | 2636.67 |  |  | 7712 |  |  |  | 411 | [10 empty] | 87.60 |  |  |  | 87.60 | [5 empty] | 73.23 |  |  | 88.03 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 12.38 |  |  |  |  | 0.00
2015 |  |  |  | 2581.99 |  |  | 7364 |  |  |  | 411 | [10 empty] | 84.12 |  |  |  | 84.12 | [5 empty] | 71.71 |  |  | 84.06 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 15.50 |  |  |  |  | 0.00
2016 |  |  |  | 2583.96 |  |  | 6573 |  |  |  | 411 | [10 empty] | 86.16 |  |  |  | 86.29 | [5 empty] | 71.57 |  |  | 74.83 |  |  |  | 0.41 |  | 0.36 | [8 empty] | 13.36 |  |  |  |  | 0.13
2017 |  |  |  | 2679.44 |  |  | 7494 |  |  |  | 411 | [10 empty] | 84.70 |  |  |  | 84.70 | [5 empty] | 74.42 |  |  | 85.55 |  |  |  | 0.31 |  | 0.27 | [8 empty] | 15.03 |  |  |  |  | 0.00
2018 |  |  |  | 3036.60 |  |  | 7433 |  |  |  | 411 | [10 empty] | 85.34 |  |  |  | 85.34 | [5 empty] | 84.34 |  |  | 84.85 |  |  |  | 2.24 |  | 2.62 | [8 empty] | 12.04 |  |  |  |  | 0.00
2019 |  |  |  | 2759.12 |  |  | 7606 |  |  |  | 411 | [10 empty] | 85.71 |  |  |  | 86.49 | [5 empty] | 76.63 |  |  | 86.83 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 13.47 |  |  |  |  | 0.78
2020 |  |  |  | 2527.89 |  |  | 7116 |  |  |  | 411 | [10 empty] | 81.99 |  |  |  | 82.81 | [5 empty] | 70.02 |  |  | 81.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.19 |  |  |  |  | 0.82
2021 |  |  |  | 2539.74 |  |  | 7038 |  |  |  | 411 | [10 empty] | 82.91 |  |  |  | 82.91 | [5 empty] | 70.54 |  |  | 80.34 |  |  |  | 0.53 |  | 0.44 | [8 empty] | 16.65 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1982 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 66
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1408 | [14 empty] | 1260
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 63
E. |  | Testing of plant systems or components | [35 empty] | 10 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 50
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 305 | [19 empty] | 112
L. |  | Human factor related | [39 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 3
Subtotal | [22 empty] | 1408 | [10 empty] | 305 |  |  |  | 1333 |  |  |  | 72 | [11 empty] | 163
Total | [22 empty] | 1713 | [14 empty] | 1568
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1982 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 23
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 8
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [37 empty] | 66
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-March, July, September, November-December. Additional electricity generation amounted to 26930 MWh. The unit was in the intermediate outage from 2021.05.04 to 2021.07.01. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-4
2021 Operating Experience
RU-33 | [8 empty] | KOLA-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-08-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-10-11
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-12-06
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 2516.21 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.85 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.77 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.71 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.77 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.52 %
Load Factor (LF) | [18 empty] | : | 69.89 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 77.64 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1959 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 1.29 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 330.67 | 286.36 |  |  |  | 308.40 |  | 260.90 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 45.39 |  | 274.73 |  |  |  | 235.18 |  |  | 185.54 |  |  | 291.49 | [9 empty] | 297.54 |  |  | 2516.21
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 70.97 |  |  | 0.01 | [6 empty] | 31.33 |  | 100.00 |  |  |  | 100.00 |  |  | 91.65 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.77
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 70.97 |  |  | 0.01 | [6 empty] | 31.33 |  | 100.00 |  |  |  | 100.00 |  |  | 91.65 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.77
LF [%] |  |  |  |  | 108.14 | 103.68 |  |  |  | 100.86 |  | 88.17 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 14.84 |  | 89.84 |  |  |  | 79.47 |  |  | 60.68 |  |  | 98.50 | [9 empty] | 97.31 |  |  | 69.89
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 96.53 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 36.83 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 77.64
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 8.35 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.85
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 8.35 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.71
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.03 |  |  | 99.99 | [6 empty] | 68.67 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.52
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 96274.97 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.6 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.66 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.33 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.47 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.08 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 5.67 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.55 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 249.38 |  |  | 1605 |  |  |  | 411 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 55.09 |  |  | 98.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 2585.77 |  |  | 7751 |  |  |  | 411 | [10 empty] | 78.18 |  |  |  | 78.19 | [5 empty] | 71.82 |  |  | 88.48 |  |  |  | 3.31 |  | 2.68 | [8 empty] | 19.14 |  |  |  |  | 0.01
1986 |  |  |  | 2690.18 |  |  | 7230 |  |  |  | 411 | [10 empty] | 72.36 |  |  |  | 72.36 | [5 empty] | 74.72 |  |  | 82.53 |  |  |  | 6.11 |  | 4.71 | [8 empty] | 22.93 |  |  |  |  | 0.00
1987 |  |  |  | 3341.17 |  |  | 7861 |  |  |  | 440 | [10 empty] | 85.50 |  |  |  | 85.50 | [5 empty] | 86.68 |  |  | 89.74 |  |  |  | 0.91 |  | 0.79 | [8 empty] | 13.72 |  |  |  |  | 0.00
1988 |  |  |  | 3124.21 |  |  | 7762 |  |  |  | 411 | [10 empty] | 84.95 |  |  |  | 84.96 | [5 empty] | 86.54 |  |  | 88.37 |  |  |  | 4.04 |  | 3.58 | [8 empty] | 11.47 |  |  |  |  | 0.01
1989 |  |  |  | 3111.51 |  |  | 7793 |  |  |  | 411 | [10 empty] | 85.77 |  |  |  | 87.57 | [5 empty] | 86.42 |  |  | 88.96 |  |  |  | 1.33 |  | 1.18 | [8 empty] | 11.25 |  |  |  |  | 1.80
1990 |  |  |  | 2930.40 |  |  | 7142 |  |  |  | 411 | [10 empty] | 80.24 |  |  |  | 80.28 | [5 empty] | 81.39 |  |  | 81.53 |  |  |  | 0.76 |  | 0.62 | [8 empty] | 19.10 |  |  |  |  | 0.05
1991 |  |  |  | 2790.49 |  |  | 7429 |  |  |  | 411 | [10 empty] | 76.70 |  |  |  | 76.70 | [5 empty] | 77.51 |  |  | 84.81 |  |  |  | 8.47 |  | 7.09 | [8 empty] | 16.21 |  |  |  |  | 0.00
1992 |  |  |  | 2764.94 |  |  | 7253 |  |  |  | 411 | [10 empty] | 79.99 |  |  |  | 80.51 | [5 empty] | 76.60 |  |  | 82.58 |  |  |  | 2.77 |  | 2.29 | [8 empty] | 17.19 |  |  |  |  | 0.52
1993 |  |  |  | 2826.99 |  |  | 8247 |  |  |  | 411 | [10 empty] | 79.00 |  |  |  | 92.43 | [5 empty] | 78.52 |  |  | 94.14 |  |  |  | 5.98 |  | 5.88 | [8 empty] | 1.69 |  |  |  |  | 13.43
1994 |  |  |  | 1939.77 |  |  | 5915 |  |  |  | 411 | [10 empty] | 55.77 |  |  |  | 62.72 | [5 empty] | 53.88 |  |  | 67.52 |  |  |  | 20.29 |  | 15.97 | [8 empty] | 21.31 |  |  |  |  | 6.95
1995 |  |  |  | 2288.81 |  |  | 7022 |  |  |  | 411 | [10 empty] | 73.83 |  |  |  | 73.83 | [5 empty] | 63.57 |  |  | 80.16 |  |  |  | 7.04 |  | 5.59 | [8 empty] | 20.57 |  |  |  |  | 0.00
1996 |  |  |  | 2537.72 |  |  | 7792 |  |  |  | 411 | [10 empty] | 84.09 |  |  |  | 84.09 | [5 empty] | 70.29 |  |  | 88.71 |  |  |  | 4.39 |  | 3.86 | [8 empty] | 12.05 |  |  |  |  | 0.00
1997 |  |  |  | 2271.67 |  |  | 6848 |  |  |  | 411 | [10 empty] | 74.56 |  |  |  | 76.16 | [5 empty] | 63.10 |  |  | 78.17 |  |  |  | 6.93 |  | 5.67 | [8 empty] | 18.18 |  |  |  |  | 1.59
1998 |  |  |  | 1927.55 |  |  | 6336 |  |  |  | 411 | [10 empty] | 49.19 |  |  |  | 69.38 | [5 empty] | 53.54 |  |  | 72.33 |  |  |  | 8.64 |  | 6.56 | [8 empty] | 24.05 |  |  |  |  | 20.20
1999 |  |  |  | 2567.48 |  |  | 7193 |  |  |  | 411 | [10 empty] | 71.16 |  |  |  | 82.00 | [5 empty] | 71.31 |  |  | 82.11 |  |  |  | 1.51 |  | 1.26 | [8 empty] | 16.75 |  |  |  |  | 10.84
2000 |  |  |  | 2177.50 |  |  | 7096 |  |  |  | 411 | [10 empty] | 60.44 |  |  |  | 86.31 | [5 empty] | 60.31 |  |  | 80.78 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 13.63 |  |  |  |  | 25.86
2001 |  |  |  | 2447.14 |  |  | 7149 |  |  |  | 411 | [10 empty] | 67.98 |  |  |  | 87.38 | [5 empty] | 67.97 |  |  | 81.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.62 |  |  |  |  | 19.40
2002 |  |  |  | 2601.71 |  |  | 7281 |  |  |  | 411 | [10 empty] | 71.52 |  |  |  | 79.71 | [5 empty] | 72.26 |  |  | 83.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.29 |  |  |  |  | 8.19
2003 |  |  |  | 2480.80 |  |  | 6663 |  |  |  | 411 | [10 empty] | 68.69 |  |  |  | 90.88 | [5 empty] | 68.90 |  |  | 76.06 |  |  |  | 1.45 |  | 1.34 | [8 empty] | 7.78 |  |  |  |  | 22.20
2004 |  |  |  | 2391.59 |  |  | 7863 |  |  |  | 411 | [10 empty] | 66.38 |  |  |  | 86.78 | [5 empty] | 66.24 |  |  | 89.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.22 |  |  |  |  | 20.40
2005 |  |  |  | 2231.75 |  |  | 7879 |  |  |  | 411 | [10 empty] | 62.10 |  |  |  | 90.21 | [5 empty] | 61.98 |  |  | 89.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.79 |  |  |  |  | 28.11
2006 |  |  |  | 2573.11 |  |  | 7217 |  |  |  | 411 | [10 empty] | 71.26 |  |  |  | 84.11 | [5 empty] | 71.47 |  |  | 82.39 |  |  |  | 0.13 |  | 0.11 | [8 empty] | 15.79 |  |  |  |  | 12.85
2007 |  |  |  | 2584.08 |  |  | 7640 |  |  |  | 411 | [10 empty] | 71.52 |  |  |  | 89.77 | [5 empty] | 71.77 |  |  | 87.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.23 |  |  |  |  | 18.25
2008 |  |  |  | 2793.49 |  |  | 7794 |  |  |  | 411 | [10 empty] | 85.15 |  |  |  | 85.20 | [5 empty] | 77.38 |  |  | 88.73 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 14.76 |  |  |  |  | 0.04
2009 |  |  |  | 2468.01 |  |  | 7538 |  |  |  | 411 | [10 empty] | 83.73 |  |  |  | 83.74 | [5 empty] | 68.55 |  |  | 86.05 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 16.25 |  |  |  |  | 0.02
2010 |  |  |  | 2956.73 |  |  | 7332 |  |  |  | 411 | [10 empty] | 84.73 |  |  |  | 84.73 | [5 empty] | 82.12 |  |  | 83.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.27 |  |  |  |  | 0.00
2011 |  |  |  | 2558.01 |  |  | 6803 |  |  |  | 411 | [10 empty] | 79.30 |  |  |  | 79.33 | [5 empty] | 71.06 |  |  | 77.67 |  |  |  | 5.98 |  | 5.05 | [8 empty] | 15.62 |  |  |  |  | 0.03
2012 |  |  |  | 2601.69 |  |  | 7459 |  |  |  | 411 | [10 empty] | 84.75 |  |  |  | 84.75 | [5 empty] | 72.06 |  |  | 84.92 |  |  |  | 0.11 |  | 0.09 | [8 empty] | 15.16 |  |  |  |  | 0.00
2013 |  |  |  | 2572.70 |  |  | 7084 |  |  |  | 411 | [10 empty] | 83.22 |  |  |  | 83.22 | [5 empty] | 71.46 |  |  | 80.87 |  |  |  | 0.26 |  | 0.22 | [8 empty] | 16.56 |  |  |  |  | 0.00
2014 |  |  |  | 2488.19 |  |  | 6241 |  |  |  | 411 | [10 empty] | 70.91 |  |  |  | 70.91 | [5 empty] | 69.10 |  |  | 71.24 |  |  |  | 2.61 |  | 1.90 | [8 empty] | 27.18 |  |  |  |  | 0.00
2015 |  |  |  | 2506.63 |  |  | 6870 |  |  |  | 411 | [10 empty] | 87.25 |  |  |  | 87.25 | [5 empty] | 69.62 |  |  | 78.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.75 |  |  |  |  | 0.00
2016 |  |  |  | 2425.95 |  |  | 6422 |  |  |  | 411 | [10 empty] | 83.44 |  |  |  | 83.44 | [5 empty] | 67.20 |  |  | 73.11 |  |  |  | 0.86 |  | 0.73 | [8 empty] | 15.83 |  |  |  |  | 0.00
2017 |  |  |  | 2994.93 |  |  | 7633 |  |  |  | 411 | [10 empty] | 84.56 |  |  |  | 84.56 | [5 empty] | 83.18 |  |  | 87.13 |  |  |  | 3.60 |  | 3.16 | [8 empty] | 12.28 |  |  |  |  | 0.00
2018 |  |  |  | 3058.96 |  |  | 7464 |  |  |  | 411 | [10 empty] | 84.97 |  |  |  | 84.97 | [5 empty] | 84.96 |  |  | 85.21 |  |  |  | 0.57 |  | 0.49 | [8 empty] | 14.54 |  |  |  |  | 0.00
2019 |  |  |  | 3188.15 |  |  | 7831 |  |  |  | 411 | [10 empty] | 87.41 |  |  |  | 87.48 | [5 empty] | 88.55 |  |  | 89.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.52 |  |  |  |  | 0.07
2020 |  |  |  | 1996.91 |  |  | 5992 |  |  |  | 411 | [10 empty] | 80.37 |  |  |  | 80.37 | [5 empty] | 55.31 |  |  | 68.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.63 |  |  |  |  | 0.00
2021 |  |  |  | 2516.21 |  |  | 6801 |  |  |  | 411 | [10 empty] | 82.77 |  |  |  | 82.77 | [5 empty] | 69.89 |  |  | 77.64 |  |  |  | 0.85 |  | 0.71 | [8 empty] | 16.52 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1984 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 52
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1406 | [14 empty] | 1156 |  |  |  | 16
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 70
E. |  | Testing of plant systems or components | [35 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 41
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 554 | [19 empty] | 177
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
Z. |  | Other | [39 empty] | 0
Subtotal | [22 empty] | 1406 | [10 empty] | 554 |  |  |  | 1230 |  |  |  | 71 | [11 empty] | 218
Total | [22 empty] | 1960 | [14 empty] | 1519
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1984 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 12
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
16. |  |  | Steam generation systems | [34 empty] | 9
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 13
Total | [37 empty] | 54
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-April, August-December. Additional electricity generation amounted to 49543 MWh. The unit was in the intermediate outage from 2021.05.04 to 2021.07.01. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-1
2021 Operating Experience
RU-17 | [8 empty] | KURSK-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-06-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-12-19
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-10-12
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1693 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 11.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 138 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 5656.38 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 5.5 %
Energy Availability Factor (EAF) | [18 empty] | : | 72.61 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.44 %
Unit Capability Factor (UCF) | [18 empty] | : | 76.26 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 19.3 %
Load Factor (LF) | [18 empty] | : | 72.18 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.65 %
Operating Factor (OF) | [18 empty] | : | 80.43 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1658 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 20.47 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 343.29 | 0.00 |  |  |  | 126.38 |  | 673.45 | [8 empty] | 681.13 |  |  | 619.13 | [6 empty] | 587.66 |  | 580.54 |  |  |  | 624.79 |  |  | 644.04 |  |  | 456.45 | [9 empty] | 319.51 |  |  | 5656.38
EAF [%] |  |  |  |  | 52.01 | 0.00 |  |  |  | 19.49 |  | 100.00 | [8 empty] | 98.40 |  |  | 93.26 | [6 empty] | 86.06 |  | 85.12 |  |  |  | 93.97 |  |  | 93.49 |  |  | 69.50 | [9 empty] | 76.77 |  |  | 72.61
UCF [%] |  |  |  |  | 52.01 | 0.00 |  |  |  | 19.49 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.05 | [6 empty] | 100.00 |  | 98.11 |  |  |  | 98.32 |  |  | 93.49 |  |  | 69.50 | [9 empty] | 81.98 |  |  | 76.26
LF [%] |  |  |  |  | 49.88 | 0.00 |  |  |  | 18.36 |  | 101.12 | [8 empty] | 98.97 |  |  | 92.96 | [6 empty] | 85.39 |  | 84.36 |  |  |  | 93.81 |  |  | 93.58 |  |  | 68.54 | [9 empty] | 75.75 |  |  | 72.18
OF [%] |  |  |  |  | 55.24 | 0.00 |  |  |  | 22.04 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 93.19 | [9 empty] | 94.74 |  |  | 80.43
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 1.89 |  |  |  | 1.68 |  |  | 6.51 |  |  | 30.50 | [9 empty] | 18.02 |  |  | 5.50
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 1.89 |  |  |  | 1.68 |  |  | 6.51 |  |  | 30.50 | [9 empty] | 18.02 |  |  | 4.44
PUF [%] |  |  |  |  | 47.99 | 100.00 |  |  |  | 80.51 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.95 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 19.30
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.60 |  |  | 5.79 | [6 empty] | 13.94 |  | 12.99 |  |  |  | 4.35 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 5.22 |  |  | 3.65
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 231065.38 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.39 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 64.03 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.51 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 65.77 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 29.73 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 64.01 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.74 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.27 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 3644.87 |  |  | 6899 |  |  |  | 925 | [10 empty] | 79.11 |  |  |  | 79.11 | [5 empty] | 71.43 |  |  | 85.91 |  |  |  | 9.31 |  | 8.12 | [8 empty] | 12.77 |  |  |  |  | 0.00
1978 |  |  |  | 5058.11 |  |  | 7573 |  |  |  | 925 | [10 empty] | 63.00 |  |  |  | 63.00 | [5 empty] | 62.42 |  |  | 86.45 |  |  |  | 17.07 |  | 12.96 | [8 empty] | 24.04 |  |  |  |  | 0.00
1979 |  |  |  | 5930.25 |  |  | 7528 |  |  |  | 925 | [10 empty] | 73.09 |  |  |  | 73.93 | [5 empty] | 73.19 |  |  | 85.94 |  |  |  | 14.94 |  | 12.98 | [8 empty] | 13.08 |  |  |  |  | 0.84
1980 |  |  |  | 6477.67 |  |  | 7669 |  |  |  | 925 | [10 empty] | 79.69 |  |  |  | 79.92 | [5 empty] | 79.72 |  |  | 87.31 |  |  |  | 7.39 |  | 6.38 | [8 empty] | 13.70 |  |  |  |  | 0.23
1981 |  |  |  | 6132.76 |  |  | 7885 |  |  |  | 925 | [10 empty] | 76.36 |  |  |  | 76.36 | [5 empty] | 75.69 |  |  | 90.01 |  |  |  | 12.25 |  | 10.66 | [8 empty] | 12.98 |  |  |  |  | 0.00
1982 |  |  |  | 7010.42 |  |  | 7788 |  |  |  | 925 | [10 empty] | 85.71 |  |  |  | 85.71 | [5 empty] | 86.52 |  |  | 88.90 |  |  |  | 2.73 |  | 2.40 | [8 empty] | 11.89 |  |  |  |  | 0.00
1983 |  |  |  | 6720.27 |  |  | 7456 |  |  |  | 925 | [10 empty] | 82.16 |  |  |  | 82.20 | [5 empty] | 82.94 |  |  | 85.11 |  |  |  | 1.94 |  | 1.63 | [8 empty] | 16.17 |  |  |  |  | 0.04
1984 |  |  |  | 6659.97 |  |  | 7369 |  |  |  | 925 | [10 empty] | 81.37 |  |  |  | 81.37 | [5 empty] | 81.97 |  |  | 83.89 |  |  |  | 2.66 |  | 2.22 | [8 empty] | 16.41 |  |  |  |  | 0.00
1985 |  |  |  | 6346.78 |  |  | 7186 |  |  |  | 925 | [10 empty] | 76.81 |  |  |  | 76.86 | [5 empty] | 78.33 |  |  | 82.03 |  |  |  | 3.99 |  | 3.19 | [8 empty] | 19.95 |  |  |  |  | 0.05
1986 |  |  |  | 5675.79 |  |  | 6598 |  |  |  | 925 | [10 empty] | 69.22 |  |  |  | 69.22 | [5 empty] | 70.05 |  |  | 75.32 |  |  |  | 14.73 |  | 11.96 | [8 empty] | 18.83 |  |  |  |  | 0.00
1987 |  |  |  | 7022.68 |  |  | 7407 |  |  |  | 1000 | [10 empty] | 82.56 |  |  |  | 82.56 | [5 empty] | 80.17 |  |  | 84.55 |  |  |  | 2.48 |  | 2.10 | [8 empty] | 15.34 |  |  |  |  | 0.00
1988 |  |  |  | 6637.98 |  |  | 7350 |  |  |  | 925 | [10 empty] | 81.75 |  |  |  | 81.75 | [5 empty] | 81.70 |  |  | 83.67 |  |  |  | 1.04 |  | 0.86 | [8 empty] | 17.39 |  |  |  |  | 0.00
1989 |  |  |  | 5745.43 |  |  | 6582 |  |  |  | 925 | [10 empty] | 68.25 |  |  |  | 68.29 | [5 empty] | 70.91 |  |  | 75.14 |  |  |  | 8.37 |  | 6.24 | [8 empty] | 25.48 |  |  |  |  | 0.03
1990 |  |  |  | 5090.51 |  |  | 6817 |  |  |  | 925 | [10 empty] | 65.69 |  |  |  | 65.69 | [5 empty] | 62.82 |  |  | 77.82 |  |  |  | 17.24 |  | 13.68 | [8 empty] | 20.63 |  |  |  |  | 0.00
1991 |  |  |  | 4163.08 |  |  | 7038 |  |  |  | 925 | [10 empty] | 52.50 |  |  |  | 53.46 | [5 empty] | 51.38 |  |  | 80.34 |  |  |  | 1.96 |  | 1.07 | [8 empty] | 45.47 |  |  |  |  | 0.96
1992 |  |  |  | 3669.24 |  |  | 6103 |  |  |  | 925 | [10 empty] | 46.25 |  |  |  | 46.25 | [5 empty] | 45.16 |  |  | 69.49 |  |  |  | 4.44 |  | 2.15 | [8 empty] | 51.60 |  |  |  |  | 0.00
1993 |  |  |  | 4809.41 |  |  | 8145 |  |  |  | 925 | [10 empty] | 61.81 |  |  |  | 91.61 | [5 empty] | 59.35 |  |  | 92.98 |  |  |  | 1.35 |  | 1.25 | [8 empty] | 7.13 |  |  |  |  | 29.80
1994 |  |  |  | 1560.59 |  |  | 2686 |  |  |  | 925 | [10 empty] | 19.76 |  |  |  | 20.64 | [5 empty] | 19.26 |  |  | 30.66 |  |  |  | 60.69 |  | 31.88 | [8 empty] | 47.48 |  |  |  |  | 0.88
1995 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1996 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1997 |  |  |  | 27.76 |  |  | 61 |  |  |  | 925 | [10 empty] | 0.54 |  |  |  | 0.54 | [5 empty] | 0.34 |  |  | 0.70 |  |  |  | 39.09 |  | 0.35 | [8 empty] | 99.11 |  |  |  |  | 0.00
1998 |  |  |  | 4508.63 |  |  | 7845 |  |  |  | 925 | [10 empty] | 57.36 |  |  |  | 59.33 | [5 empty] | 55.64 |  |  | 89.55 |  |  |  | 5.73 |  | 3.61 | [8 empty] | 37.07 |  |  |  |  | 1.96
1999 |  |  |  | 4557.04 |  |  | 7464 |  |  |  | 925 | [10 empty] | 57.64 |  |  |  | 58.74 | [5 empty] | 56.24 |  |  | 85.21 |  |  |  | 0.91 |  | 0.54 | [8 empty] | 40.72 |  |  |  |  | 1.11
2000 |  |  |  | 3449.69 |  |  | 5531 |  |  |  | 925 | [10 empty] | 43.56 |  |  |  | 44.33 | [5 empty] | 42.46 |  |  | 62.97 |  |  |  | 6.37 |  | 3.02 | [8 empty] | 52.65 |  |  |  |  | 0.77
2001 |  |  |  | 1296.07 |  |  | 2042 |  |  |  | 925 | [10 empty] | 16.39 |  |  |  | 16.62 | [5 empty] | 15.99 |  |  | 23.31 |  |  |  | 6.51 |  | 1.16 | [8 empty] | 82.22 |  |  |  |  | 0.23
2002 |  |  |  | 2462.70 |  |  | 3439 |  |  |  | 925 | [10 empty] | 30.83 |  |  |  | 32.51 | [5 empty] | 30.39 |  |  | 39.26 |  |  |  | 2.91 |  | 0.97 | [8 empty] | 66.52 |  |  |  |  | 1.68
2003 |  |  |  | 6452.71 |  |  | 7262 |  |  |  | 925 | [10 empty] | 78.90 |  |  |  | 80.17 | [5 empty] | 79.63 |  |  | 82.90 |  |  |  | 6.86 |  | 5.91 | [8 empty] | 13.93 |  |  |  |  | 1.27
2004 |  |  |  | 6601.33 |  |  | 7363 |  |  |  | 925 | [10 empty] | 81.11 |  |  |  | 83.00 | [5 empty] | 81.25 |  |  | 83.82 |  |  |  | 2.85 |  | 2.43 | [8 empty] | 14.57 |  |  |  |  | 1.89
2005 |  |  |  | 6219.96 |  |  | 7651 |  |  |  | 925 | [10 empty] | 76.99 |  |  |  | 82.99 | [5 empty] | 76.75 |  |  | 87.33 |  |  |  | 2.72 |  | 2.53 | [8 empty] | 14.48 |  |  |  |  | 5.99
2006 |  |  |  | 5837.69 |  |  | 7089 |  |  |  | 925 | [10 empty] | 72.19 |  |  |  | 78.44 | [5 empty] | 72.04 |  |  | 80.92 |  |  |  | 3.17 |  | 2.56 | [8 empty] | 18.99 |  |  |  |  | 6.25
2007 |  |  |  | 6736.18 |  |  | 7670 |  |  |  | 925 | [10 empty] | 82.77 |  |  |  | 89.05 | [5 empty] | 83.13 |  |  | 87.56 |  |  |  | 6.05 |  | 5.74 | [8 empty] | 5.21 |  |  |  |  | 6.29
2008 |  |  |  | 6464.58 |  |  | 7596 |  |  |  | 925 | [10 empty] | 81.36 |  |  |  | 84.43 | [5 empty] | 79.56 |  |  | 86.48 |  |  |  | 2.89 |  | 2.51 | [8 empty] | 13.06 |  |  |  |  | 3.08
2009 |  |  |  | 7161.20 |  |  | 8068 |  |  |  | 925 | [10 empty] | 89.95 |  |  |  | 90.26 | [5 empty] | 88.38 |  |  | 92.10 |  |  |  | 4.16 |  | 3.92 | [8 empty] | 5.82 |  |  |  |  | 0.31
2010 |  |  |  | 5640.73 |  |  | 5991 |  |  |  | 925 | [10 empty] | 69.52 |  |  |  | 69.65 | [5 empty] | 69.61 |  |  | 68.39 |  |  |  | 12.86 |  | 10.28 | [8 empty] | 20.06 |  |  |  |  | 0.13
2011 |  |  |  | 7654.80 |  |  | 8620 |  |  |  | 925 | [10 empty] | 90.66 |  |  |  | 90.80 | [5 empty] | 94.48 |  |  | 98.41 |  |  |  | 1.96 |  | 1.82 | [8 empty] | 7.38 |  |  |  |  | 0.15
2012 |  |  |  | 5988.71 |  |  | 6392 |  |  |  | 925 | [10 empty] | 71.19 |  |  |  | 71.72 | [5 empty] | 73.71 |  |  | 72.77 |  |  |  | 0.64 |  | 0.46 | [8 empty] | 27.82 |  |  |  |  | 0.53
2013 |  |  |  | 6759.55 |  |  | 7217 |  |  |  | 925 | [10 empty] | 80.99 |  |  |  | 81.37 | [5 empty] | 83.42 |  |  | 82.39 |  |  |  | 5.16 |  | 4.96 | [8 empty] | 13.67 |  |  |  |  | 0.38
2014 |  |  |  | 6277.53 |  |  | 6846 |  |  |  | 925 | [10 empty] | 75.22 |  |  |  | 75.72 | [5 empty] | 77.46 |  |  | 78.14 |  |  |  | 2.80 |  | 2.18 | [8 empty] | 22.10 |  |  |  |  | 0.49
2015 |  |  |  | 6849.24 |  |  | 7482 |  |  |  | 925 | [10 empty] | 82.74 |  |  |  | 84.12 | [5 empty] | 84.53 |  |  | 85.41 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 15.50 |  |  |  |  | 1.37
2016 |  |  |  | 5293.85 |  |  | 6143 |  |  |  | 925 | [10 empty] | 65.56 |  |  |  | 67.46 | [5 empty] | 65.15 |  |  | 69.93 |  |  |  | 6.10 |  | 4.38 | [8 empty] | 28.16 |  |  |  |  | 1.90
2017 |  |  |  | 6684.29 |  |  | 7504 |  |  |  | 925 | [10 empty] | 81.87 |  |  |  | 82.54 | [5 empty] | 82.49 |  |  | 85.66 |  |  |  | 5.99 |  | 5.26 | [8 empty] | 12.20 |  |  |  |  | 0.68
2018 |  |  |  | 4685.45 |  |  | 5302 |  |  |  | 925 | [10 empty] | 57.65 |  |  |  | 58.92 | [5 empty] | 57.82 |  |  | 60.53 |  |  |  | 5.30 |  | 3.29 | [8 empty] | 37.78 |  |  |  |  | 1.27
2019 |  |  |  | 5300.40 |  |  | 5889 |  |  |  | 925 | [10 empty] | 64.96 |  |  |  | 66.51 | [5 empty] | 65.41 |  |  | 67.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.49 |  |  |  |  | 1.55
2020 |  |  |  | 5208.97 |  |  | 5781 |  |  |  | 925 | [10 empty] | 63.74 |  |  |  | 65.06 | [5 empty] | 64.11 |  |  | 65.81 |  |  |  | 2.00 |  | 1.33 | [8 empty] | 33.61 |  |  |  |  | 1.32
2021 |  |  |  | 5656.38 |  |  | 6814 |  |  |  | 925 | [10 empty] | 72.61 |  |  |  | 76.26 | [5 empty] | 72.18 |  |  | 80.43 |  |  |  | 5.50 |  | 4.44 | [8 empty] | 19.30 |  |  |  |  | 3.65
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1977 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 49 | [14 empty] | 120
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1585 | [14 empty] | 926
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 1236
E. |  | Testing of plant systems or components | [35 empty] | 4
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 117
H. |  | Nuclear regulatory requirements | [39 empty] | 8
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 9
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [31 empty] | 24 | [7 empty] | 3 | [11 empty] | 1
Subtotal | [22 empty] | 1585 |  |  |  | 49 | [6 empty] | 24 |  |  |  | 2283 |  |  |  | 136 | [11 empty] | 10
Total | [22 empty] | 1658 | [14 empty] | 2429
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1977 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 35
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 19
16. |  |  | Steam generation systems | [34 empty] | 6
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [19 empty] | 49 | [14 empty] | 13
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
34. |  |  | Miscellaneous Systems | [34 empty] | 16
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 49 | [14 empty] | 123
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January, March-May, December. Additional electricity generation amounted to 16092 MWh. The unit was in the routine maintenance outage from 2021.01.18 to 2021.03.25. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-2
2021 Operating Experience
RU-22 | [8 empty] | KURSK-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-01-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1979-01-28
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-08-17
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1693 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 11.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 150 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 5567.7 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.85 %
Energy Availability Factor (EAF) | [18 empty] | : | 68.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.04 %
Unit Capability Factor (UCF) | [18 empty] | : | 69.35 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 28.61 %
Load Factor (LF) | [18 empty] | : | 68.71 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.07 %
Operating Factor (OF) | [18 empty] | : | 70.34 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2598 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 75.84 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 692.46 | 644.48 |  |  |  | 202.61 |  | 0.00 | [8 empty] | 0.00 |  |  | 170.16 | [6 empty] | 484.29 |  | 645.76 |  |  |  | 663.56 |  |  | 702.04 |  |  | 656.30 | [9 empty] | 706.04 |  |  | 5567.70
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 29.61 |  | 0.00 | [8 empty] | 0.00 |  |  | 26.90 | [6 empty] | 71.46 |  | 94.07 |  |  |  | 98.91 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 68.28
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 29.61 |  | 0.00 | [8 empty] | 0.00 |  |  | 27.93 | [6 empty] | 76.18 |  | 100.00 |  |  |  | 99.85 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 69.35
LF [%] |  |  |  |  | 100.62 | 103.68 |  |  |  | 29.44 |  | 0.00 | [8 empty] | 0.00 |  |  | 25.55 | [6 empty] | 70.37 |  | 93.83 |  |  |  | 99.63 |  |  | 102.01 |  |  | 98.54 | [9 empty] | 102.59 |  |  | 68.71
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 32.80 |  | 0.00 | [8 empty] | 0.00 |  |  | 32.36 | [6 empty] | 80.24 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 70.34
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 23.82 |  | 0.00 |  |  |  | 0.15 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.85
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 23.82 |  | 0.00 |  |  |  | 0.15 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.04
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 70.39 |  | 100.00 | [8 empty] | 100.00 |  |  | 72.07 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 28.61
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.03 | [6 empty] | 4.72 |  | 5.93 |  |  |  | 0.93 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.07
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 222922.11 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.07 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 64.08 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.47 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 65.98 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 29.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 64.37 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.9 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.28 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 3613.90 |  |  | 6734 |  |  |  | 925 | [10 empty] | 62.36 |  |  |  | 62.36 | [5 empty] | 62.31 |  |  | 80.40 |  |  |  | 27.83 |  | 24.04 | [8 empty] | 13.59 |  |  |  |  | 0.00
1980 |  |  |  | 6404.32 |  |  | 7658 |  |  |  | 925 | [10 empty] | 78.45 |  |  |  | 79.02 | [5 empty] | 78.82 |  |  | 87.18 |  |  |  | 10.04 |  | 8.82 | [8 empty] | 12.15 |  |  |  |  | 0.58
1981 |  |  |  | 6385.88 |  |  | 7874 |  |  |  | 925 | [10 empty] | 78.71 |  |  |  | 78.71 | [5 empty] | 78.81 |  |  | 89.89 |  |  |  | 8.73 |  | 7.53 | [8 empty] | 13.77 |  |  |  |  | 0.00
1982 |  |  |  | 5875.79 |  |  | 6443 |  |  |  | 925 | [10 empty] | 71.11 |  |  |  | 71.11 | [5 empty] | 72.51 |  |  | 73.55 |  |  |  | 6.25 |  | 4.74 | [8 empty] | 24.14 |  |  |  |  | 0.00
1983 |  |  |  | 5707.64 |  |  | 7104 |  |  |  | 925 | [10 empty] | 70.07 |  |  |  | 70.07 | [5 empty] | 70.44 |  |  | 81.10 |  |  |  | 10.00 |  | 7.78 | [8 empty] | 22.15 |  |  |  |  | 0.00
1984 |  |  |  | 6326.50 |  |  | 7219 |  |  |  | 925 | [10 empty] | 77.06 |  |  |  | 77.10 | [5 empty] | 77.86 |  |  | 82.18 |  |  |  | 5.31 |  | 4.33 | [8 empty] | 18.57 |  |  |  |  | 0.05
1985 |  |  |  | 6459.94 |  |  | 7598 |  |  |  | 925 | [10 empty] | 79.41 |  |  |  | 79.41 | [5 empty] | 79.72 |  |  | 86.74 |  |  |  | 6.09 |  | 5.15 | [8 empty] | 15.43 |  |  |  |  | 0.00
1986 |  |  |  | 5617.31 |  |  | 6575 |  |  |  | 925 | [10 empty] | 69.08 |  |  |  | 69.08 | [5 empty] | 69.32 |  |  | 75.06 |  |  |  | 15.66 |  | 12.82 | [8 empty] | 18.10 |  |  |  |  | 0.00
1987 |  |  |  | 7196.69 |  |  | 7539 |  |  |  | 1000 | [10 empty] | 83.29 |  |  |  | 83.29 | [5 empty] | 82.15 |  |  | 86.06 |  |  |  | 3.73 |  | 3.23 | [8 empty] | 13.48 |  |  |  |  | 0.00
1988 |  |  |  | 5725.66 |  |  | 6609 |  |  |  | 925 | [10 empty] | 73.88 |  |  |  | 73.88 | [5 empty] | 70.47 |  |  | 75.24 |  |  |  | 3.50 |  | 2.68 | [8 empty] | 23.44 |  |  |  |  | 0.00
1989 |  |  |  | 6164.20 |  |  | 6797 |  |  |  | 925 | [10 empty] | 74.90 |  |  |  | 74.91 | [5 empty] | 76.07 |  |  | 77.59 |  |  |  | 14.58 |  | 12.79 | [8 empty] | 12.30 |  |  |  |  | 0.02
1990 |  |  |  | 4789.70 |  |  | 6874 |  |  |  | 925 | [10 empty] | 62.20 |  |  |  | 62.20 | [5 empty] | 59.11 |  |  | 78.47 |  |  |  | 26.17 |  | 22.05 | [8 empty] | 15.75 |  |  |  |  | 0.00
1991 |  |  |  | 4375.96 |  |  | 7361 |  |  |  | 925 | [10 empty] | 55.26 |  |  |  | 56.28 | [5 empty] | 54.00 |  |  | 84.03 |  |  |  | 0.70 |  | 0.40 | [8 empty] | 43.32 |  |  |  |  | 1.02
1992 |  |  |  | 2158.37 |  |  | 3552 |  |  |  | 925 | [10 empty] | 27.24 |  |  |  | 27.24 | [5 empty] | 26.57 |  |  | 40.44 |  |  |  | 3.87 |  | 1.10 | [8 empty] | 71.67 |  |  |  |  | 0.00
1993 |  |  |  | 4438.15 |  |  | 7432 |  |  |  | 925 | [10 empty] | 57.09 |  |  |  | 85.00 | [5 empty] | 54.77 |  |  | 84.84 |  |  |  | 2.25 |  | 1.95 | [8 empty] | 13.04 |  |  |  |  | 27.91
1994 |  |  |  | 4212.17 |  |  | 7385 |  |  |  | 925 | [10 empty] | 53.46 |  |  |  | 55.29 | [5 empty] | 51.98 |  |  | 84.30 |  |  |  | 37.66 |  | 33.40 | [8 empty] | 11.31 |  |  |  |  | 1.82
1995 |  |  |  | 4745.36 |  |  | 7708 |  |  |  | 925 | [10 empty] | 59.79 |  |  |  | 90.79 | [5 empty] | 58.56 |  |  | 87.99 |  |  |  | 0.91 |  | 0.83 | [8 empty] | 8.38 |  |  |  |  | 31.00
1996 |  |  |  | 4196.12 |  |  | 7099 |  |  |  | 925 | [10 empty] | 52.69 |  |  |  | 52.84 | [5 empty] | 51.64 |  |  | 80.82 |  |  |  | 7.80 |  | 4.47 | [8 empty] | 42.69 |  |  |  |  | 0.15
1997 |  |  |  | 4354.28 |  |  | 7076 |  |  |  | 925 | [10 empty] | 54.94 |  |  |  | 55.26 | [5 empty] | 53.74 |  |  | 80.78 |  |  |  | 7.36 |  | 4.39 | [8 empty] | 40.36 |  |  |  |  | 0.32
1998 |  |  |  | 1685.05 |  |  | 2805 |  |  |  | 925 | [10 empty] | 21.30 |  |  |  | 21.71 | [5 empty] | 20.80 |  |  | 32.02 |  |  |  | 5.62 |  | 1.29 | [8 empty] | 77.00 |  |  |  |  | 0.41
1999 |  |  |  | 3708.09 |  |  | 6066 |  |  |  | 925 | [10 empty] | 46.84 |  |  |  | 48.03 | [5 empty] | 45.76 |  |  | 69.25 |  |  |  | 4.72 |  | 2.38 | [8 empty] | 49.59 |  |  |  |  | 1.19
2000 |  |  |  | 3668.06 |  |  | 6211 |  |  |  | 925 | [10 empty] | 46.19 |  |  |  | 48.87 | [5 empty] | 45.14 |  |  | 70.71 |  |  |  | 3.97 |  | 2.02 | [8 empty] | 49.11 |  |  |  |  | 2.68
2001 |  |  |  | 4768.15 |  |  | 7667 |  |  |  | 925 | [10 empty] | 60.09 |  |  |  | 61.11 | [5 empty] | 58.84 |  |  | 87.52 |  |  |  | 0.33 |  | 0.20 | [8 empty] | 38.69 |  |  |  |  | 1.02
2002 |  |  |  | 3027.77 |  |  | 4770 |  |  |  | 925 | [10 empty] | 38.07 |  |  |  | 38.25 | [5 empty] | 37.37 |  |  | 54.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 61.75 |  |  |  |  | 0.19
2003 |  |  |  | 3756.24 |  |  | 5834 |  |  |  | 925 | [10 empty] | 46.36 |  |  |  | 47.10 | [5 empty] | 46.36 |  |  | 66.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 52.90 |  |  |  |  | 0.74
2004 |  |  |  | 3692.07 |  |  | 4318 |  |  |  | 925 | [10 empty] | 44.97 |  |  |  | 45.06 | [5 empty] | 45.44 |  |  | 49.16 |  |  |  | 3.87 |  | 1.82 | [8 empty] | 53.13 |  |  |  |  | 0.09
2005 |  |  |  | 6896.62 |  |  | 7782 |  |  |  | 925 | [10 empty] | 84.68 |  |  |  | 87.51 | [5 empty] | 85.10 |  |  | 88.83 |  |  |  | 0.58 |  | 0.51 | [8 empty] | 11.98 |  |  |  |  | 2.83
2006 |  |  |  | 6574.42 |  |  | 7320 |  |  |  | 925 | [10 empty] | 80.34 |  |  |  | 82.92 | [5 empty] | 81.14 |  |  | 83.56 |  |  |  | 1.28 |  | 1.07 | [8 empty] | 16.01 |  |  |  |  | 2.58
2007 |  |  |  | 5728.65 |  |  | 6207 |  |  |  | 925 | [10 empty] | 69.48 |  |  |  | 69.99 | [5 empty] | 70.70 |  |  | 70.86 |  |  |  | 1.70 |  | 1.21 | [8 empty] | 28.80 |  |  |  |  | 0.51
2008 |  |  |  | 6835.74 |  |  | 7351 |  |  |  | 925 | [10 empty] | 82.61 |  |  |  | 82.63 | [5 empty] | 84.13 |  |  | 83.69 |  |  |  | 0.80 |  | 0.66 | [8 empty] | 16.70 |  |  |  |  | 0.03
2009 |  |  |  | 6428.15 |  |  | 6778 |  |  |  | 925 | [10 empty] | 76.64 |  |  |  | 76.67 | [5 empty] | 79.33 |  |  | 77.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.33 |  |  |  |  | 0.03
2010 |  |  |  | 7448.67 |  |  | 8076 |  |  |  | 925 | [10 empty] | 87.81 |  |  |  | 88.09 | [5 empty] | 91.92 |  |  | 92.19 |  |  |  | 1.15 |  | 1.03 | [8 empty] | 10.88 |  |  |  |  | 0.28
2011 |  |  |  | 6368.67 |  |  | 6539 |  |  |  | 925 | [10 empty] | 75.31 |  |  |  | 75.39 | [5 empty] | 78.61 |  |  | 74.65 |  |  |  | 1.56 |  | 1.20 | [8 empty] | 23.41 |  |  |  |  | 0.09
2012 |  |  |  | 7401.98 |  |  | 7802 |  |  |  | 925 | [10 empty] | 87.76 |  |  |  | 88.01 | [5 empty] | 91.10 |  |  | 88.82 |  |  |  | 1.85 |  | 1.66 | [8 empty] | 10.33 |  |  |  |  | 0.25
2013 |  |  |  | 1584.36 |  |  | 1606 |  |  |  | 925 | [10 empty] | 18.25 |  |  |  | 18.25 | [5 empty] | 19.55 |  |  | 18.33 |  |  |  | 0.44 |  | 0.08 | [8 empty] | 81.67 |  |  |  |  | 0.00
2014 |  |  |  | 6299.77 |  |  | 7011 |  |  |  | 925 | [10 empty] | 77.67 |  |  |  | 78.52 | [5 empty] | 77.74 |  |  | 80.03 |  |  |  | 0.54 |  | 0.43 | [8 empty] | 21.05 |  |  |  |  | 0.86
2015 |  |  |  | 6556.20 |  |  | 7160 |  |  |  | 925 | [10 empty] | 79.38 |  |  |  | 80.44 | [5 empty] | 80.91 |  |  | 81.74 |  |  |  | 2.96 |  | 4.25 | [8 empty] | 15.31 |  |  |  |  | 1.06
2016 |  |  |  | 5678.19 |  |  | 6425 |  |  |  | 925 | [10 empty] | 68.85 |  |  |  | 69.57 | [5 empty] | 69.88 |  |  | 73.14 |  |  |  | 3.29 |  | 2.37 | [8 empty] | 28.06 |  |  |  |  | 0.72
2017 |  |  |  | 5437.61 |  |  | 6209 |  |  |  | 925 | [10 empty] | 66.14 |  |  |  | 66.59 | [5 empty] | 67.11 |  |  | 70.88 |  |  |  | 3.75 |  | 7.38 | [8 empty] | 26.03 |  |  |  |  | 0.45
2018 |  |  |  | 4702.96 |  |  | 5689 |  |  |  | 925 | [10 empty] | 56.25 |  |  |  | 56.48 | [5 empty] | 58.04 |  |  | 64.94 |  |  |  | 11.38 |  | 9.58 | [8 empty] | 33.94 |  |  |  |  | 0.22
2019 |  |  |  | 5207.62 |  |  | 5656 |  |  |  | 925 | [10 empty] | 62.03 |  |  |  | 62.17 | [5 empty] | 64.27 |  |  | 64.57 |  |  |  | 2.74 |  | 1.75 | [8 empty] | 36.08 |  |  |  |  | 0.13
2020 |  |  |  | 5532.83 |  |  | 5945 |  |  |  | 925 | [10 empty] | 66.59 |  |  |  | 66.89 | [5 empty] | 68.09 |  |  | 67.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.10 |  |  |  |  | 0.30
2021 |  |  |  | 5567.70 |  |  | 6162 |  |  |  | 925 | [10 empty] | 68.28 |  |  |  | 69.35 | [5 empty] | 68.71 |  |  | 70.34 |  |  |  | 2.85 |  | 2.04 | [8 empty] | 28.61 |  |  |  |  | 1.07
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1979 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 162 | [14 empty] | 111
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2451 | [14 empty] | 1391
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 610
E. |  | Testing of plant systems or components | [35 empty] | 12
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 97
H. |  | Nuclear regulatory requirements | [39 empty] | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 3
Z. |  | Other | [39 empty] | 28
Subtotal | [22 empty] | 2451 |  |  |  | 162 | [10 empty] | 2110 |  |  |  | 147 | [11 empty] | 5
Total | [22 empty] | 2613 | [14 empty] | 2262
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1979 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 43
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 16
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
32. |  |  | Feedwater and Main Steam System | [19 empty] | 162 | [14 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 14
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 162 | [14 empty] | 111
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-March, September-December. Additional electricity generation amounted to 76821 MWh. The unit was in the intermediate outage from 2021.03.11 to 2021.06.21. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-3
2021 Operating Experience
RU-38 | [8 empty] | KURSK-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-04-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-10-17
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-03-30
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 170 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 5674.03 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 70.44 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 73.85 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 26.12 %
Load Factor (LF) | [18 empty] | : | 70.02 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.41 %
Operating Factor (OF) | [18 empty] | : | 74.39 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2243 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 53.41 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 693.81 | 653.83 |  |  |  | 714.79 |  | 671.13 | [8 empty] | 668.95 |  |  | 590.87 | [6 empty] | 490.25 |  | 6.15 |  |  |  | 0.00 |  |  | 0.00 |  |  | 477.86 | [9 empty] | 706.39 |  |  | 5674.03
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.85 | [8 empty] | 97.40 |  |  | 89.63 | [6 empty] | 73.37 |  | 2.53 |  |  |  | 0.00 |  |  | 0.00 |  |  | 85.19 | [9 empty] | 99.98 |  |  | 70.44
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.96 | [8 empty] | 100.00 |  |  | 99.80 | [6 empty] | 99.92 |  | 3.57 |  |  |  | 0.00 |  |  | 0.00 |  |  | 85.19 | [9 empty] | 99.98 |  |  | 73.85
LF [%] |  |  |  |  | 100.82 | 105.18 |  |  |  | 103.86 |  | 100.77 | [8 empty] | 97.20 |  |  | 88.72 | [6 empty] | 71.24 |  | 0.89 |  |  |  | 0.00 |  |  | 0.00 |  |  | 71.75 | [9 empty] | 102.64 |  |  | 70.02
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 6.85 |  |  |  | 0.00 |  |  | 0.00 |  |  | 88.06 | [9 empty] | 100.00 |  |  | 74.39
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.20 | [6 empty] | 0.08 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.20 | [6 empty] | 0.08 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.04 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 96.43 |  |  |  | 100.00 |  |  | 100.00 |  |  | 14.81 | [9 empty] | 0.02 |  |  | 26.12
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.11 | [8 empty] | 2.60 |  |  | 10.18 | [6 empty] | 26.55 |  | 1.03 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.41
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 228652.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.76 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.32 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.05 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.63 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.02 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.12 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.6 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 5479.24 |  |  | 6830 |  |  |  | 925 | [10 empty] | 72.49 |  |  |  | 72.49 | [5 empty] | 72.15 |  |  | 76.71 |  |  |  | 9.02 |  | 7.18 | [8 empty] | 20.33 |  |  |  |  | 0.00
1985 |  |  |  | 6260.75 |  |  | 7250 |  |  |  | 925 | [10 empty] | 77.59 |  |  |  | 77.93 | [5 empty] | 77.26 |  |  | 82.76 |  |  |  | 7.60 |  | 6.41 | [8 empty] | 15.66 |  |  |  |  | 0.34
1986 |  |  |  | 4810.84 |  |  | 6269 |  |  |  | 925 | [10 empty] | 60.00 |  |  |  | 60.42 | [5 empty] | 59.37 |  |  | 71.56 |  |  |  | 15.08 |  | 10.73 | [8 empty] | 28.85 |  |  |  |  | 0.42
1987 |  |  |  | 5458.95 |  |  | 6185 |  |  |  | 1000 | [10 empty] | 66.40 |  |  |  | 69.01 | [5 empty] | 62.32 |  |  | 70.61 |  |  |  | 5.11 |  | 3.71 | [8 empty] | 27.28 |  |  |  |  | 2.61
1988 |  |  |  | 6693.64 |  |  | 7471 |  |  |  | 925 | [10 empty] | 83.64 |  |  |  | 83.64 | [5 empty] | 82.38 |  |  | 85.05 |  |  |  | 3.44 |  | 2.98 | [8 empty] | 13.38 |  |  |  |  | 0.00
1989 |  |  |  | 5900.50 |  |  | 7200 |  |  |  | 925 | [10 empty] | 74.29 |  |  |  | 74.32 | [5 empty] | 72.82 |  |  | 82.19 |  |  |  | 8.84 |  | 7.21 | [8 empty] | 18.48 |  |  |  |  | 0.03
1990 |  |  |  | 6889.42 |  |  | 8096 |  |  |  | 925 | [10 empty] | 86.52 |  |  |  | 86.52 | [5 empty] | 85.02 |  |  | 92.42 |  |  |  | 7.78 |  | 7.30 | [8 empty] | 6.18 |  |  |  |  | 0.00
1991 |  |  |  | 5138.96 |  |  | 5704 |  |  |  | 925 | [10 empty] | 63.17 |  |  |  | 63.42 | [5 empty] | 63.42 |  |  | 65.11 |  |  |  | 1.30 |  | 0.83 | [8 empty] | 35.74 |  |  |  |  | 0.25
1992 |  |  |  | 6630.50 |  |  | 8126 |  |  |  | 925 | [10 empty] | 82.13 |  |  |  | 82.13 | [5 empty] | 81.61 |  |  | 92.52 |  |  |  | 5.97 |  | 5.22 | [8 empty] | 12.66 |  |  |  |  | 0.00
1993 |  |  |  | 5562.30 |  |  | 6438 |  |  |  | 925 | [10 empty] | 70.34 |  |  |  | 71.22 | [5 empty] | 68.64 |  |  | 73.49 |  |  |  | 8.24 |  | 6.39 | [8 empty] | 22.39 |  |  |  |  | 0.88
1994 |  |  |  | 5077.86 |  |  | 6495 |  |  |  | 925 | [10 empty] | 66.69 |  |  |  | 73.60 | [5 empty] | 62.67 |  |  | 74.14 |  |  |  | 0.74 |  | 0.55 | [8 empty] | 25.84 |  |  |  |  | 6.92
1995 |  |  |  | 5318.13 |  |  | 5974 |  |  |  | 925 | [10 empty] | 65.40 |  |  |  | 65.70 | [5 empty] | 65.63 |  |  | 68.20 |  |  |  | 2.80 |  | 1.90 | [8 empty] | 32.41 |  |  |  |  | 0.30
1996 |  |  |  | 6739.27 |  |  | 7383 |  |  |  | 925 | [10 empty] | 82.67 |  |  |  | 82.89 | [5 empty] | 82.94 |  |  | 84.05 |  |  |  | 2.36 |  | 2.00 | [8 empty] | 15.11 |  |  |  |  | 0.22
1997 |  |  |  | 6548.72 |  |  | 7325 |  |  |  | 925 | [10 empty] | 81.56 |  |  |  | 82.46 | [5 empty] | 80.82 |  |  | 83.62 |  |  |  | 0.21 |  | 0.17 | [8 empty] | 17.37 |  |  |  |  | 0.89
1998 |  |  |  | 4528.32 |  |  | 5405 |  |  |  | 925 | [10 empty] | 56.53 |  |  |  | 60.26 | [5 empty] | 55.88 |  |  | 61.70 |  |  |  | 17.21 |  | 12.53 | [8 empty] | 27.20 |  |  |  |  | 3.74
1999 |  |  |  | 6006.85 |  |  | 6749 |  |  |  | 925 | [10 empty] | 74.33 |  |  |  | 75.32 | [5 empty] | 74.13 |  |  | 77.04 |  |  |  | 4.80 |  | 3.80 | [8 empty] | 20.87 |  |  |  |  | 0.99
2000 |  |  |  | 6382.33 |  |  | 7415 |  |  |  | 925 | [10 empty] | 78.26 |  |  |  | 78.85 | [5 empty] | 78.55 |  |  | 84.41 |  |  |  | 7.98 |  | 6.83 | [8 empty] | 14.32 |  |  |  |  | 0.59
2001 |  |  |  | 3535.20 |  |  | 3948 |  |  |  | 925 | [10 empty] | 43.53 |  |  |  | 44.65 | [5 empty] | 43.63 |  |  | 45.07 |  |  |  | 0.15 |  | 0.07 | [8 empty] | 55.28 |  |  |  |  | 1.12
2002 |  |  |  | 6699.77 |  |  | 7788 |  |  |  | 925 | [10 empty] | 85.07 |  |  |  | 88.23 | [5 empty] | 82.68 |  |  | 88.90 |  |  |  | 0.29 |  | 0.26 | [8 empty] | 11.51 |  |  |  |  | 3.16
2003 |  |  |  | 5100.59 |  |  | 5469 |  |  |  | 925 | [10 empty] | 61.84 |  |  |  | 62.23 | [5 empty] | 62.95 |  |  | 62.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.77 |  |  |  |  | 0.39
2004 |  |  |  | 6894.20 |  |  | 7660 |  |  |  | 925 | [10 empty] | 84.35 |  |  |  | 86.33 | [5 empty] | 84.85 |  |  | 87.20 |  |  |  | 0.82 |  | 0.71 | [8 empty] | 12.96 |  |  |  |  | 1.98
2005 |  |  |  | 4987.10 |  |  | 5598 |  |  |  | 925 | [10 empty] | 61.31 |  |  |  | 63.49 | [5 empty] | 61.55 |  |  | 63.90 |  |  |  | 0.59 |  | 0.37 | [8 empty] | 36.14 |  |  |  |  | 2.17
2006 |  |  |  | 6711.22 |  |  | 7353 |  |  |  | 925 | [10 empty] | 81.93 |  |  |  | 83.37 | [5 empty] | 82.82 |  |  | 83.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.63 |  |  |  |  | 1.44
2007 |  |  |  | 5765.28 |  |  | 6535 |  |  |  | 925 | [10 empty] | 71.07 |  |  |  | 73.75 | [5 empty] | 71.15 |  |  | 74.60 |  |  |  | 1.12 |  | 0.84 | [8 empty] | 25.41 |  |  |  |  | 2.68
2008 |  |  |  | 2117.39 |  |  | 2374 |  |  |  | 925 | [10 empty] | 26.82 |  |  |  | 26.82 | [5 empty] | 26.06 |  |  | 27.03 |  |  |  | 1.30 |  | 0.35 | [8 empty] | 72.83 |  |  |  |  | 0.00
2009 |  |  |  | 7620.95 |  |  | 8216 |  |  |  | 925 | [10 empty] | 93.77 |  |  |  | 93.87 | [5 empty] | 94.05 |  |  | 93.79 |  |  |  | 0.58 |  | 0.55 | [8 empty] | 5.58 |  |  |  |  | 0.10
2010 |  |  |  | 6048.61 |  |  | 6352 |  |  |  | 925 | [10 empty] | 71.67 |  |  |  | 71.78 | [5 empty] | 74.65 |  |  | 72.51 |  |  |  | 1.44 |  | 1.05 | [8 empty] | 27.17 |  |  |  |  | 0.11
2011 |  |  |  | 7574.35 |  |  | 8228 |  |  |  | 925 | [10 empty] | 90.44 |  |  |  | 90.80 | [5 empty] | 93.49 |  |  | 93.94 |  |  |  | 3.77 |  | 3.56 | [8 empty] | 5.64 |  |  |  |  | 0.36
2012 |  |  |  | 6207.22 |  |  | 6900 |  |  |  | 925 | [10 empty] | 74.78 |  |  |  | 75.44 | [5 empty] | 76.39 |  |  | 78.55 |  |  |  | 5.35 |  | 7.58 | [8 empty] | 16.98 |  |  |  |  | 0.66
2013 |  |  |  | 7264.06 |  |  | 8022 |  |  |  | 925 | [10 empty] | 87.02 |  |  |  | 87.23 | [5 empty] | 89.65 |  |  | 91.58 |  |  |  | 5.04 |  | 4.63 | [8 empty] | 8.14 |  |  |  |  | 0.21
2014 |  |  |  | 6969.97 |  |  | 7506 |  |  |  | 925 | [10 empty] | 84.29 |  |  |  | 84.49 | [5 empty] | 86.01 |  |  | 85.68 |  |  |  | 0.85 |  | 4.03 | [8 empty] | 11.48 |  |  |  |  | 0.21
2015 |  |  |  | 7338.33 |  |  | 8075 |  |  |  | 925 | [10 empty] | 89.24 |  |  |  | 89.93 | [5 empty] | 90.56 |  |  | 92.18 |  |  |  | 1.22 |  | 1.11 | [8 empty] | 8.97 |  |  |  |  | 0.68
2016 |  |  |  | 7001.08 |  |  | 7556 |  |  |  | 925 | [10 empty] | 84.05 |  |  |  | 85.12 | [5 empty] | 86.17 |  |  | 86.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.88 |  |  |  |  | 1.07
2017 |  |  |  | 7405.52 |  |  | 8018 |  |  |  | 925 | [10 empty] | 90.09 |  |  |  | 90.92 | [5 empty] | 91.39 |  |  | 91.53 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 9.00 |  |  |  |  | 0.83
2018 |  |  |  | 6346.60 |  |  | 7060 |  |  |  | 925 | [10 empty] | 76.64 |  |  |  | 77.41 | [5 empty] | 78.32 |  |  | 80.59 |  |  |  | 4.10 |  | 8.89 | [8 empty] | 13.70 |  |  |  |  | 0.77
2019 |  |  |  | 4990.43 |  |  | 5623 |  |  |  | 925 | [10 empty] | 60.49 |  |  |  | 61.19 | [5 empty] | 61.59 |  |  | 64.19 |  |  |  | 2.25 |  | 2.92 | [8 empty] | 35.90 |  |  |  |  | 0.70
2020 |  |  |  | 6473.17 |  |  | 7464 |  |  |  | 925 | [10 empty] | 78.62 |  |  |  | 80.58 | [5 empty] | 79.67 |  |  | 84.97 |  |  |  | 4.13 |  | 4.32 | [8 empty] | 15.11 |  |  |  |  | 1.96
2021 |  |  |  | 5674.03 |  |  | 6517 |  |  |  | 925 | [10 empty] | 70.44 |  |  |  | 73.85 | [5 empty] | 70.02 |  |  | 74.39 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 26.12 |  |  |  |  | 3.41
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1984 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 139
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2265 | [14 empty] | 1142
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 676
E. |  | Testing of plant systems or components | [35 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 8
Subtotal | [22 empty] | 2265 | [14 empty] | 1819 |  |  |  | 139 | [11 empty] | 8
Total | [22 empty] | 2265 | [14 empty] | 1966
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1984 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 22
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 51
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
41. |  |  | Main Generator Systems | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 138
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-May, December. Additional electricity generation amounted to 117500 MWh. The unit was in the routine maintenance outage from 2021.08.03 to 2021.11.05. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-4
2021 Operating Experience
RU-39 | [8 empty] | KURSK-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-05-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-12-02
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-02-05
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 167 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 6292.87 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.79 %
Energy Availability Factor (EAF) | [18 empty] | : | 76.86 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.41 %
Unit Capability Factor (UCF) | [18 empty] | : | 77.33 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.26 %
Load Factor (LF) | [18 empty] | : | 77.66 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.47 %
Operating Factor (OF) | [18 empty] | : | 78.37 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1895 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 143.18 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 694.42 | 646.18 |  |  |  | 702.21 |  | 673.49 | [8 empty] | 672.48 |  |  | 333.07 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 625.04 |  |  | 696.69 |  |  | 649.49 | [9 empty] | 599.79 |  |  | 6292.87
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 98.68 |  | 99.92 | [8 empty] | 97.64 |  |  | 50.96 | [6 empty] | 0.00 |  | 0.31 |  |  |  | 93.54 |  |  | 99.96 |  |  | 99.56 | [9 empty] | 85.16 |  |  | 76.86
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 98.68 |  | 99.96 | [8 empty] | 100.00 |  |  | 53.83 | [6 empty] | 0.00 |  | 0.31 |  |  |  | 93.90 |  |  | 99.96 |  |  | 99.56 | [9 empty] | 85.16 |  |  | 77.33
LF [%] |  |  |  |  | 100.90 | 103.95 |  |  |  | 102.04 |  | 101.12 | [8 empty] | 97.72 |  |  | 50.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 93.85 |  |  | 101.23 |  |  | 97.52 | [9 empty] | 87.15 |  |  | 77.66
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 57.08 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 86.83 |  |  | 78.37
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.32 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.44 | [9 empty] | 14.84 |  |  | 1.79
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.32 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.44 | [9 empty] | 14.84 |  |  | 1.41
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.04 | [8 empty] | 0.00 |  |  | 46.17 | [6 empty] | 100.00 |  | 99.69 |  |  |  | 6.10 |  |  | 0.04 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 21.26
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.04 | [8 empty] | 2.36 |  |  | 2.87 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.37 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.47
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 228485.82 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.55 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.47 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.07 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.49 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.44 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.24 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.55 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 6328.54 |  |  | 7574 |  |  |  | 925 | [10 empty] | 80.35 |  |  |  | 80.81 | [5 empty] | 80.28 |  |  | 88.06 |  |  |  | 12.66 |  | 11.71 | [8 empty] | 7.47 |  |  |  |  | 0.46
1987 |  |  |  | 6167.68 |  |  | 6704 |  |  |  | 1000 | [10 empty] | 72.29 |  |  |  | 72.43 | [5 empty] | 70.41 |  |  | 76.53 |  |  |  | 6.80 |  | 5.28 | [8 empty] | 22.29 |  |  |  |  | 0.14
1988 |  |  |  | 6653.03 |  |  | 7390 |  |  |  | 925 | [10 empty] | 81.73 |  |  |  | 81.73 | [5 empty] | 81.88 |  |  | 84.13 |  |  |  | 5.02 |  | 4.32 | [8 empty] | 13.95 |  |  |  |  | 0.01
1989 |  |  |  | 6131.81 |  |  | 6954 |  |  |  | 925 | [10 empty] | 75.98 |  |  |  | 76.02 | [5 empty] | 75.67 |  |  | 79.38 |  |  |  | 4.04 |  | 3.20 | [8 empty] | 20.78 |  |  |  |  | 0.05
1990 |  |  |  | 6050.02 |  |  | 6922 |  |  |  | 925 | [10 empty] | 73.62 |  |  |  | 73.71 | [5 empty] | 74.66 |  |  | 79.02 |  |  |  | 7.62 |  | 6.08 | [8 empty] | 20.21 |  |  |  |  | 0.09
1991 |  |  |  | 7356.07 |  |  | 8469 |  |  |  | 925 | [10 empty] | 90.30 |  |  |  | 92.54 | [5 empty] | 90.78 |  |  | 96.68 |  |  |  | 4.21 |  | 4.06 | [8 empty] | 3.40 |  |  |  |  | 2.24
1992 |  |  |  | 6117.37 |  |  | 7324 |  |  |  | 925 | [10 empty] | 75.44 |  |  |  | 75.44 | [5 empty] | 75.30 |  |  | 83.39 |  |  |  | 2.41 |  | 1.87 | [8 empty] | 22.69 |  |  |  |  | 0.00
1993 |  |  |  | 5638.27 |  |  | 6439 |  |  |  | 925 | [10 empty] | 70.98 |  |  |  | 71.72 | [5 empty] | 69.58 |  |  | 73.50 |  |  |  | 4.54 |  | 3.41 | [8 empty] | 24.87 |  |  |  |  | 0.74
1994 |  |  |  | 5369.44 |  |  | 6255 |  |  |  | 925 | [10 empty] | 66.98 |  |  |  | 71.55 | [5 empty] | 66.26 |  |  | 71.40 |  |  |  | 1.27 |  | 0.92 | [8 empty] | 27.53 |  |  |  |  | 4.57
1995 |  |  |  | 6207.48 |  |  | 7001 |  |  |  | 925 | [10 empty] | 77.02 |  |  |  | 78.61 | [5 empty] | 76.61 |  |  | 79.92 |  |  |  | 3.36 |  | 2.74 | [8 empty] | 18.66 |  |  |  |  | 1.58
1996 |  |  |  | 6590.19 |  |  | 7373 |  |  |  | 925 | [10 empty] | 80.16 |  |  |  | 81.40 | [5 empty] | 81.11 |  |  | 83.94 |  |  |  | 3.23 |  | 2.71 | [8 empty] | 15.89 |  |  |  |  | 1.23
1997 |  |  |  | 5971.68 |  |  | 6664 |  |  |  | 925 | [10 empty] | 73.05 |  |  |  | 73.87 | [5 empty] | 73.70 |  |  | 76.07 |  |  |  | 2.70 |  | 2.05 | [8 empty] | 24.08 |  |  |  |  | 0.82
1998 |  |  |  | 6641.43 |  |  | 7751 |  |  |  | 925 | [10 empty] | 82.33 |  |  |  | 86.66 | [5 empty] | 81.96 |  |  | 88.48 |  |  |  | 1.46 |  | 1.29 | [8 empty] | 12.05 |  |  |  |  | 4.34
1999 |  |  |  | 5895.38 |  |  | 6595 |  |  |  | 925 | [10 empty] | 72.77 |  |  |  | 74.17 | [5 empty] | 72.76 |  |  | 75.29 |  |  |  | 1.02 |  | 0.77 | [8 empty] | 25.06 |  |  |  |  | 1.40
2000 |  |  |  | 6778.77 |  |  | 7423 |  |  |  | 925 | [10 empty] | 82.81 |  |  |  | 83.47 | [5 empty] | 83.43 |  |  | 84.51 |  |  |  | 0.59 |  | 0.50 | [8 empty] | 16.03 |  |  |  |  | 0.66
2001 |  |  |  | 6671.63 |  |  | 7281 |  |  |  | 925 | [10 empty] | 81.52 |  |  |  | 82.20 | [5 empty] | 82.34 |  |  | 83.12 |  |  |  | 0.81 |  | 0.67 | [8 empty] | 17.13 |  |  |  |  | 0.68
2002 |  |  |  | 5530.98 |  |  | 6094 |  |  |  | 925 | [10 empty] | 67.61 |  |  |  | 68.31 | [5 empty] | 68.26 |  |  | 69.57 |  |  |  | 1.54 |  | 1.07 | [8 empty] | 30.62 |  |  |  |  | 0.71
2003 |  |  |  | 6233.39 |  |  | 6802 |  |  |  | 925 | [10 empty] | 75.84 |  |  |  | 77.26 | [5 empty] | 76.93 |  |  | 77.65 |  |  |  | 0.27 |  | 0.21 | [8 empty] | 22.54 |  |  |  |  | 1.42
2004 |  |  |  | 5422.93 |  |  | 6005 |  |  |  | 925 | [10 empty] | 66.70 |  |  |  | 68.02 | [5 empty] | 66.74 |  |  | 68.36 |  |  |  | 0.27 |  | 0.18 | [8 empty] | 31.80 |  |  |  |  | 1.32
2005 |  |  |  | 7081.14 |  |  | 7858 |  |  |  | 925 | [10 empty] | 87.15 |  |  |  | 89.43 | [5 empty] | 87.38 |  |  | 89.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.57 |  |  |  |  | 2.28
2006 |  |  |  | 3636.44 |  |  | 4115 |  |  |  | 925 | [10 empty] | 44.24 |  |  |  | 44.77 | [5 empty] | 44.88 |  |  | 46.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 55.23 |  |  |  |  | 0.53
2007 |  |  |  | 7426.50 |  |  | 8298 |  |  |  | 925 | [10 empty] | 91.23 |  |  |  | 94.27 | [5 empty] | 91.65 |  |  | 94.73 |  |  |  | 0.19 |  | 0.18 | [8 empty] | 5.54 |  |  |  |  | 3.04
2008 |  |  |  | 6052.40 |  |  | 6580 |  |  |  | 925 | [10 empty] | 73.94 |  |  |  | 74.87 | [5 empty] | 74.49 |  |  | 74.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.13 |  |  |  |  | 0.93
2009 |  |  |  | 4184.28 |  |  | 4786 |  |  |  | 925 | [10 empty] | 52.34 |  |  |  | 52.46 | [5 empty] | 51.64 |  |  | 54.63 |  |  |  | 1.38 |  | 0.73 | [8 empty] | 46.81 |  |  |  |  | 0.12
2010 |  |  |  | 7557.08 |  |  | 8109 |  |  |  | 925 | [10 empty] | 91.31 |  |  |  | 91.65 | [5 empty] | 93.26 |  |  | 92.57 |  |  |  | 2.88 |  | 2.72 | [8 empty] | 5.62 |  |  |  |  | 0.35
2011 |  |  |  | 5500.69 |  |  | 5729 |  |  |  | 925 | [10 empty] | 64.46 |  |  |  | 64.51 | [5 empty] | 67.89 |  |  | 65.41 |  |  |  | 4.61 |  | 3.12 | [8 empty] | 32.37 |  |  |  |  | 0.05
2012 |  |  |  | 7470.41 |  |  | 8144 |  |  |  | 925 | [10 empty] | 89.18 |  |  |  | 89.36 | [5 empty] | 91.94 |  |  | 92.71 |  |  |  | 2.11 |  | 1.93 | [8 empty] | 8.72 |  |  |  |  | 0.18
2013 |  |  |  | 6213.89 |  |  | 6807 |  |  |  | 925 | [10 empty] | 74.33 |  |  |  | 74.78 | [5 empty] | 76.69 |  |  | 77.71 |  |  |  | 1.12 |  | 0.85 | [8 empty] | 24.37 |  |  |  |  | 0.46
2014 |  |  |  | 7517.80 |  |  | 8201 |  |  |  | 925 | [10 empty] | 89.67 |  |  |  | 90.11 | [5 empty] | 92.78 |  |  | 93.62 |  |  |  | 2.44 |  | 2.26 | [8 empty] | 7.64 |  |  |  |  | 0.44
2015 |  |  |  | 6745.34 |  |  | 7348 |  |  |  | 925 | [10 empty] | 81.17 |  |  |  | 82.83 | [5 empty] | 83.24 |  |  | 83.88 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 17.11 |  |  |  |  | 1.67
2016 |  |  |  | 7420.59 |  |  | 8055 |  |  |  | 925 | [10 empty] | 88.67 |  |  |  | 90.08 | [5 empty] | 91.33 |  |  | 91.70 |  |  |  | 0.76 |  | 0.69 | [8 empty] | 9.23 |  |  |  |  | 1.40
2017 |  |  |  | 6940.86 |  |  | 7471 |  |  |  | 925 | [10 empty] | 83.55 |  |  |  | 83.71 | [5 empty] | 85.66 |  |  | 85.29 |  |  |  | 2.08 |  | 1.78 | [8 empty] | 14.52 |  |  |  |  | 0.15
2018 |  |  |  | 7117.30 |  |  | 7645 |  |  |  | 925 | [10 empty] | 85.95 |  |  |  | 86.70 | [5 empty] | 87.84 |  |  | 87.27 |  |  |  | 3.14 |  | 2.81 | [8 empty] | 10.49 |  |  |  |  | 0.75
2019 |  |  |  | 6538.38 |  |  | 7095 |  |  |  | 925 | [10 empty] | 79.38 |  |  |  | 80.03 | [5 empty] | 80.69 |  |  | 80.99 |  |  |  | 2.71 |  | 2.99 | [8 empty] | 16.98 |  |  |  |  | 0.65
2020 |  |  |  | 7277.83 |  |  | 7991 |  |  |  | 925 | [10 empty] | 88.64 |  |  |  | 89.46 | [5 empty] | 89.57 |  |  | 90.97 |  |  |  | 0.62 |  | 0.56 | [8 empty] | 9.98 |  |  |  |  | 0.81
2021 |  |  |  | 6292.87 |  |  | 6865 |  |  |  | 925 | [10 empty] | 76.86 |  |  |  | 77.33 | [5 empty] | 77.66 |  |  | 78.37 |  |  |  | 1.79 |  | 1.41 | [8 empty] | 21.26 |  |  |  |  | 0.47
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1986 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 100 | [14 empty] | 72
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1781 | [14 empty] | 1152
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 392
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 76
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 6
Subtotal | [22 empty] | 1781 |  |  |  | 100 | [10 empty] | 1620 |  |  |  | 83 | [11 empty] | 1
Total | [22 empty] | 1881 | [14 empty] | 1704
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1986 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 8
12. |  |  | Reactor I&C Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [19 empty] | 100 | [14 empty] | 13
16. |  |  | Steam generation systems | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 23
Total | [22 empty] | 100 | [14 empty] | 71
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-May, September-December. Additional electricity generation amounted to 96487 MWh. The unit was in the routine maintenance outage from 2021.06.18 to 2021.08.31. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD 2-1
2021 Operating Experience
RU-163 | [8 empty] | LENINGRAD 2-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-491 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-10-25
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-03-09
Gross electrical power | [12 empty] | : |  |  | 1188 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-10-29
Reference unit power (net) | [12 empty] | : |  |  | 1101 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 8598.45 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.11 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.98 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.65 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.38 %
Load Factor (LF) | [18 empty] | : | 89.15 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.12 %
Operating Factor (OF) | [18 empty] | : | 95.02 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 436 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 588.09 | 620.56 |  |  |  | 803.33 |  | 700.28 | [8 empty] | 762.37 |  |  | 761.69 | [6 empty] | 658.40 |  | 794.14 |  |  |  | 753.82 |  |  | 800.90 |  |  | 605.47 | [9 empty] | 749.41 |  |  | 8598.45
EAF [%] |  |  |  |  | 80.09 | 89.67 |  |  |  | 97.96 |  | 88.25 | [8 empty] | 92.99 |  |  | 95.93 | [6 empty] | 83.12 |  | 96.78 |  |  |  | 95.02 |  |  | 97.50 |  |  | 77.10 | [9 empty] | 91.58 |  |  | 90.52
UCF [%] |  |  |  |  | 82.24 | 90.66 |  |  |  | 98.31 |  | 89.16 | [8 empty] | 94.02 |  |  | 97.97 | [6 empty] | 85.72 |  | 99.39 |  |  |  | 96.82 |  |  | 99.21 |  |  | 77.78 | [9 empty] | 100.00 |  |  | 92.65
LF [%] |  |  |  |  | 71.79 | 83.87 |  |  |  | 98.07 |  | 88.34 | [8 empty] | 93.07 |  |  | 96.09 | [6 empty] | 80.38 |  | 96.95 |  |  |  | 95.09 |  |  | 97.77 |  |  | 76.38 | [9 empty] | 91.49 |  |  | 89.15
OF [%] |  |  |  |  | 84.27 | 92.71 |  |  |  | 100.00 |  | 93.89 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 86.83 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 82.22 | [9 empty] | 100.00 |  |  | 95.02
FLR [%] |  |  |  |  | 0.02 | 7.92 |  |  |  | 0.00 |  | 7.10 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 3.18 |  |  | 0.00 |  |  | 19.57 | [9 empty] | 0.00 |  |  | 3.11
UCL [%] |  |  |  |  | 0.01 | 7.80 |  |  |  | 0.00 |  | 6.82 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 3.18 |  |  | 0.00 |  |  | 18.92 | [9 empty] | 0.00 |  |  | 2.98
PUF [%] |  |  |  |  | 17.74 | 1.54 |  |  |  | 1.69 |  | 4.02 | [8 empty] | 5.98 |  |  | 2.03 | [6 empty] | 14.28 |  | 0.61 |  |  |  | 0.00 |  |  | 0.79 |  |  | 3.29 | [9 empty] | 0.00 |  |  | 4.38
XUF [%] |  |  |  |  | 2.15 | 0.98 |  |  |  | 0.36 |  | 0.91 | [8 empty] | 1.02 |  |  | 2.04 | [6 empty] | 2.60 |  | 2.61 |  |  |  | 1.80 |  |  | 1.72 |  |  | 0.68 | [9 empty] | 8.42 |  |  | 2.12
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 25611.3 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 8.2 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.1 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.56 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.34 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.21 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.11 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.65 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 2344.91 |  |  | 3078 |  |  |  | 1085 | [10 empty] | 23.75 |  |  |  | 23.75 | [5 empty] | 20.26 |  |  | 25.14 |  |  |  | 76.25 |  | 76.25 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7137.13 |  |  | 6666 |  |  |  | 1101 | [10 empty] | 74.35 |  |  |  | 74.93 | [5 empty] | 74.00 |  |  | 76.10 |  |  |  | 8.67 |  | 9.99 | [8 empty] | 15.09 |  |  |  |  | 0.57
2020 |  |  |  | 7530.82 |  |  | 7037 |  |  |  | 1101 | [10 empty] | 82.64 |  |  |  | 83.44 | [5 empty] | 77.87 |  |  | 80.11 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 16.41 |  |  |  |  | 0.80
2021 |  |  |  | 8598.45 |  |  | 8324 |  |  |  | 1101 | [10 empty] | 90.52 |  |  |  | 92.65 | [5 empty] | 89.15 |  |  | 95.02 |  |  |  | 3.11 |  | 2.98 | [8 empty] | 4.38 |  |  |  |  | 2.12
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2018 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 260 | [14 empty] | 780
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 215 | [14 empty] | 865
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 77
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 101
Subtotal | [22 empty] | 215 |  |  |  | 260 | [10 empty] | 942 |  |  |  | 780 | [11 empty] | 101
Total | [22 empty] | 475 | [14 empty] | 1823
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2018 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [19 empty] | 128 | [14 empty] | 59
31. |  |  | Turbine and auxiliaries | [19 empty] | 66 | [14 empty] | 169
32. |  |  | Feedwater and Main Steam System | [34 empty] | 117
41. |  |  | Main Generator Systems | [19 empty] | 59 | [14 empty] | 297
42. |  |  | Electrical Power Supply Systems | [19 empty] | 7 | [14 empty] | 2
Total | [22 empty] | 260 | [14 empty] | 644
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. The unit was in the overhaul outage from 2021.01.07 to 2021.03.03 and the routine maintenance outage from 2021.07.02 to 2021.07.06. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD 2-2
2021 Operating Experience
RU-164 | [8 empty] | LENINGRAD 2-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-491 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-04-15
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-10-22
Gross electrical power | [12 empty] | : |  |  | 1188 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-03-18
Reference unit power (net) | [12 empty] | : |  |  | 1101 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 8361.9 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.43 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.88 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.96 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.16 %
Load Factor (LF) | [18 empty] | : | 88.87 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.53 %
Operating Factor (OF) | [18 empty] | : | 91.67 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 825 hours
Annual Summary
[5 empty] | Mar | Jan |  |  |  | Feb |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [11 empty] | 525.59 | [8 empty] | 749.26 |  |  | 771.32 | [6 empty] | 797.51 |  | 734.29 |  |  |  | 782.59 |  |  | 813.92 |  |  | 732.31 | [9 empty] | 551.34 |  |  | 6458.15
EAF [%] | [11 empty] | 66.31 | [8 empty] | 90.83 |  |  | 95.74 | [6 empty] | 96.91 |  | 89.51 |  |  |  | 98.08 |  |  | 98.64 |  |  | 92.09 | [9 empty] | 67.70 |  |  | 88.43
UCF [%] | [11 empty] | 66.49 | [8 empty] | 92.47 |  |  | 98.91 | [6 empty] | 100.00 |  | 91.39 |  |  |  | 99.58 |  |  | 100.00 |  |  | 93.09 | [9 empty] | 76.49 |  |  | 90.96
LF [%] | [11 empty] | 66.30 | [8 empty] | 91.47 |  |  | 97.30 | [6 empty] | 97.36 |  | 89.64 |  |  |  | 98.72 |  |  | 99.36 |  |  | 92.38 | [9 empty] | 67.31 |  |  | 88.87
OF [%] | [11 empty] | 66.81 | [8 empty] | 93.68 |  |  | 100.00 | [6 empty] | 100.00 |  | 92.20 |  |  |  | 99.86 |  |  | 100.00 |  |  | 94.72 | [9 empty] | 77.55 |  |  | 91.67
FLR [%] | [11 empty] | 0.00 | [8 empty] | 0.09 |  |  | 0.00 | [6 empty] | 0.00 |  | 8.61 |  |  |  | 0.42 |  |  | 0.00 |  |  | 6.91 | [9 empty] | 1.20 |  |  | 2.03
UCL [%] | [11 empty] | 0.00 | [8 empty] | 0.08 |  |  | 0.00 | [6 empty] | 0.00 |  | 8.61 |  |  |  | 0.42 |  |  | 0.00 |  |  | 6.91 | [9 empty] | 0.93 |  |  | 1.88
PUF [%] | [11 empty] | 33.51 | [8 empty] | 7.45 |  |  | 1.09 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 22.58 |  |  | 7.16
XUF [%] | [11 empty] | 0.18 | [8 empty] | 1.64 |  |  | 3.17 | [6 empty] | 3.09 |  | 1.88 |  |  |  | 1.50 |  |  | 1.36 |  |  | 1.00 | [9 empty] | 8.79 |  |  | 2.53
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 9021.44 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.03 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.43 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.88 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.96 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.16 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.87 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.53 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.67 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2021 |  |  |  | 8361.90 |  |  | 7935 |  |  |  | 1101 | [10 empty] | 88.43 |  |  |  | 90.96 | [5 empty] | 88.87 |  |  | 91.67 |  |  |  | 2.03 |  | 1.88 | [8 empty] | 7.16 |  |  |  |  | 2.53
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2021 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 110 | [14 empty] | 146
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 168 | [14 empty] | 223
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 287 | [14 empty] | 383
Subtotal | [22 empty] | 455 |  |  |  | 110 | [10 empty] | 606 |  |  |  | 146
Total | [22 empty] | 565 | [14 empty] | 752
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2021 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [19 empty] | 38 | [14 empty] | 38
41. |  |  | Main Generator Systems | [19 empty] | 65 | [14 empty] | 65
42. |  |  | Electrical Power Supply Systems | [19 empty] | 6 | [14 empty] | 6
Total | [22 empty] | 109 | [14 empty] | 109
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in April. Additional electricity generation amounted to 170 MWh. The unit was in the routine maintenance outage from 2021.04.21 to 2021.05.04 and the overhaul outage from 2021.12.25 to 2021.01.01. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD-3
2021 Operating Experience
RU-34 | [8 empty] | LENINGRAD-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-12-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1979-12-07
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-06-29
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 211 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 5763.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.8 %
Energy Availability Factor (EAF) | [18 empty] | : | 72.24 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.59 %
Unit Capability Factor (UCF) | [18 empty] | : | 72.94 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 26.47 %
Load Factor (LF) | [18 empty] | : | 71.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.7 %
Operating Factor (OF) | [18 empty] | : | 74.16 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2264 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 64.27 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 296.77 | 505.51 |  |  |  | 697.63 |  | 668.26 | [8 empty] | 530.52 |  |  | 261.78 | [6 empty] | 0.00 |  | 93.61 |  |  |  | 671.70 |  |  | 638.60 |  |  | 685.86 | [9 empty] | 713.35 |  |  | 5763.58
EAF [%] |  |  |  |  | 43.44 | 80.84 |  |  |  | 99.76 |  | 100.00 | [8 empty] | 98.37 |  |  | 40.23 | [6 empty] | 0.00 |  | 15.39 |  |  |  | 99.37 |  |  | 91.90 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 72.24
UCF [%] |  |  |  |  | 43.44 | 80.84 |  |  |  | 99.76 |  | 100.00 | [8 empty] | 98.42 |  |  | 40.37 | [6 empty] | 0.00 |  | 15.39 |  |  |  | 99.37 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 72.94
LF [%] |  |  |  |  | 43.12 | 81.32 |  |  |  | 101.37 |  | 100.34 | [8 empty] | 77.09 |  |  | 39.31 | [6 empty] | 0.00 |  | 13.60 |  |  |  | 100.86 |  |  | 92.79 |  |  | 102.98 | [9 empty] | 103.65 |  |  | 71.13
OF [%] |  |  |  |  | 45.30 | 86.46 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 43.33 | [6 empty] | 0.00 |  | 17.47 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 74.16
FLR [%] |  |  |  |  | 0.00 | 5.79 |  |  |  | 0.24 |  | 0.00 | [8 empty] | 1.58 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.63 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.80
UCL [%] |  |  |  |  | 0.00 | 4.97 |  |  |  | 0.24 |  | 0.00 | [8 empty] | 1.58 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.63 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.59
PUF [%] |  |  |  |  | 56.56 | 14.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 59.63 | [6 empty] | 100.00 |  | 84.61 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 26.47
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  | 0.13 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 8.10 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.70
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 246399.53 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.72 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.4 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.89 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.25 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 22.86 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.36 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.85 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.21 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 5345.39 |  |  | 7504 |  |  |  | 925 | [10 empty] | 81.59 |  |  |  | 81.61 | [5 empty] | 80.55 |  |  | 90.94 |  |  |  | 10.86 |  | 9.95 | [8 empty] | 8.45 |  |  |  |  | 0.02
1981 |  |  |  | 6553.56 |  |  | 7528 |  |  |  | 925 | [10 empty] | 81.35 |  |  |  | 81.66 | [5 empty] | 80.88 |  |  | 85.94 |  |  |  | 9.31 |  | 8.38 | [8 empty] | 9.96 |  |  |  |  | 0.32
1982 |  |  |  | 6413.26 |  |  | 7448 |  |  |  | 925 | [10 empty] | 80.27 |  |  |  | 80.80 | [5 empty] | 79.15 |  |  | 85.02 |  |  |  | 7.18 |  | 6.25 | [8 empty] | 12.95 |  |  |  |  | 0.53
1983 |  |  |  | 5708.44 |  |  | 6809 |  |  |  | 925 | [10 empty] | 70.90 |  |  |  | 71.30 | [5 empty] | 70.45 |  |  | 77.73 |  |  |  | 7.88 |  | 6.10 | [8 empty] | 22.61 |  |  |  |  | 0.39
1984 |  |  |  | 7214.95 |  |  | 8060 |  |  |  | 925 | [10 empty] | 89.22 |  |  |  | 89.76 | [5 empty] | 88.80 |  |  | 91.76 |  |  |  | 1.88 |  | 1.72 | [8 empty] | 8.52 |  |  |  |  | 0.55
1985 |  |  |  | 6831.90 |  |  | 7835 |  |  |  | 925 | [10 empty] | 84.94 |  |  |  | 85.42 | [5 empty] | 84.31 |  |  | 89.44 |  |  |  | 5.45 |  | 4.92 | [8 empty] | 9.67 |  |  |  |  | 0.47
1986 |  |  |  | 6890.93 |  |  | 7935 |  |  |  | 925 | [10 empty] | 85.89 |  |  |  | 86.44 | [5 empty] | 85.04 |  |  | 90.58 |  |  |  | 3.36 |  | 3.01 | [8 empty] | 10.55 |  |  |  |  | 0.55
1987 |  |  |  | 6010.31 |  |  | 6362 |  |  |  | 1000 | [10 empty] | 69.36 |  |  |  | 70.37 | [5 empty] | 68.61 |  |  | 72.63 |  |  |  | 1.12 |  | 0.79 | [8 empty] | 28.83 |  |  |  |  | 1.01
1988 |  |  |  | 6951.74 |  |  | 7885 |  |  |  | 925 | [10 empty] | 86.53 |  |  |  | 86.53 | [5 empty] | 85.56 |  |  | 89.77 |  |  |  | 1.44 |  | 1.26 | [8 empty] | 12.21 |  |  |  |  | 0.00
1989 |  |  |  | 6938.14 |  |  | 7455 |  |  |  | 925 | [10 empty] | 85.86 |  |  |  | 86.23 | [5 empty] | 85.62 |  |  | 85.10 |  |  |  | 0.97 |  | 0.84 | [8 empty] | 12.93 |  |  |  |  | 0.37
1990 |  |  |  | 7531.93 |  |  | 8280 |  |  |  | 925 | [10 empty] | 92.35 |  |  |  | 92.96 | [5 empty] | 92.95 |  |  | 94.52 |  |  |  | 1.36 |  | 1.28 | [8 empty] | 5.76 |  |  |  |  | 0.61
1991 |  |  |  | 6506.60 |  |  | 7197 |  |  |  | 925 | [10 empty] | 80.59 |  |  |  | 80.59 | [5 empty] | 80.30 |  |  | 82.16 |  |  |  | 1.25 |  | 1.02 | [8 empty] | 18.39 |  |  |  |  | 0.00
1992 |  |  |  | 5516.63 |  |  | 6122 |  |  |  | 925 | [10 empty] | 68.39 |  |  |  | 68.49 | [5 empty] | 67.90 |  |  | 69.70 |  |  |  | 2.92 |  | 2.06 | [8 empty] | 29.45 |  |  |  |  | 0.09
1993 |  |  |  | 7143.82 |  |  | 7966 |  |  |  | 925 | [10 empty] | 88.90 |  |  |  | 90.14 | [5 empty] | 88.16 |  |  | 90.94 |  |  |  | 0.56 |  | 0.51 | [8 empty] | 9.35 |  |  |  |  | 1.24
1994 |  |  |  | 6631.82 |  |  | 8135 |  |  |  | 925 | [10 empty] | 91.04 |  |  |  | 92.42 | [5 empty] | 81.84 |  |  | 92.87 |  |  |  | 0.26 |  | 0.24 | [8 empty] | 7.34 |  |  |  |  | 1.39
1995 |  |  |  | 3585.96 |  |  | 4332 |  |  |  | 925 | [10 empty] | 46.53 |  |  |  | 49.40 | [5 empty] | 44.25 |  |  | 49.45 |  |  |  | 0.44 |  | 0.22 | [8 empty] | 50.38 |  |  |  |  | 2.87
1996 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1998 |  |  |  | 1386.50 |  |  | 1610 |  |  |  | 925 | [10 empty] | 17.41 |  |  |  | 17.49 | [5 empty] | 17.11 |  |  | 18.38 |  |  |  | 4.00 |  | 0.73 | [8 empty] | 81.78 |  |  |  |  | 0.08
1999 |  |  |  | 7853.14 |  |  | 8701 |  |  |  | 925 | [10 empty] | 97.08 |  |  |  | 99.66 | [5 empty] | 96.92 |  |  | 99.33 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.00 |  |  |  |  | 2.58
2000 |  |  |  | 6352.80 |  |  | 7169 |  |  |  | 925 | [10 empty] | 78.25 |  |  |  | 79.64 | [5 empty] | 78.19 |  |  | 81.61 |  |  |  | 1.83 |  | 1.49 | [8 empty] | 18.87 |  |  |  |  | 1.39
2001 |  |  |  | 6173.49 |  |  | 7007 |  |  |  | 925 | [10 empty] | 76.58 |  |  |  | 78.92 | [5 empty] | 76.19 |  |  | 79.99 |  |  |  | 0.19 |  | 0.15 | [8 empty] | 20.93 |  |  |  |  | 2.34
2002 |  |  |  | 2514.75 |  |  | 3332 |  |  |  | 925 | [10 empty] | 31.88 |  |  |  | 33.60 | [5 empty] | 31.03 |  |  | 38.04 |  |  |  | 17.29 |  | 7.02 | [8 empty] | 59.38 |  |  |  |  | 1.72
2003 |  |  |  | 6729.17 |  |  | 8100 |  |  |  | 925 | [10 empty] | 84.54 |  |  |  | 86.65 | [5 empty] | 83.05 |  |  | 92.47 |  |  |  | 6.00 |  | 5.53 | [8 empty] | 7.82 |  |  |  |  | 2.11
2004 |  |  |  | 6909.08 |  |  | 8426 |  |  |  | 925 | [10 empty] | 86.47 |  |  |  | 90.86 | [5 empty] | 85.03 |  |  | 95.92 |  |  |  | 5.04 |  | 4.82 | [8 empty] | 4.31 |  |  |  |  | 4.40
2005 |  |  |  | 4447.28 |  |  | 5397 |  |  |  | 925 | [10 empty] | 61.10 |  |  |  | 61.46 | [5 empty] | 54.88 |  |  | 61.60 |  |  |  | 2.72 |  | 1.72 | [8 empty] | 36.83 |  |  |  |  | 0.36
2006 |  |  |  | 7332.11 |  |  | 8274 |  |  |  | 925 | [10 empty] | 89.86 |  |  |  | 89.86 | [5 empty] | 90.49 |  |  | 94.45 |  |  |  | 2.22 |  | 4.89 | [8 empty] | 5.25 |  |  |  |  | 0.00
2007 |  |  |  | 3755.96 |  |  | 4820 |  |  |  | 925 | [10 empty] | 47.04 |  |  |  | 54.08 | [5 empty] | 46.35 |  |  | 55.02 |  |  |  | 0.24 |  | 0.13 | [8 empty] | 45.78 |  |  |  |  | 7.04
2008 |  |  |  | 5013.64 |  |  | 5632 |  |  |  | 925 | [10 empty] | 62.68 |  |  |  | 62.71 | [5 empty] | 61.70 |  |  | 64.12 |  |  |  | 1.64 |  | 7.69 | [8 empty] | 29.60 |  |  |  |  | 0.03
2009 |  |  |  | 5336.12 |  |  | 6209 |  |  |  | 925 | [10 empty] | 70.38 |  |  |  | 70.65 | [5 empty] | 65.85 |  |  | 70.88 |  |  |  | 3.40 |  | 22.58 | [8 empty] | 6.78 |  |  |  |  | 0.26
2010 |  |  |  | 7303.22 |  |  | 8261 |  |  |  | 925 | [10 empty] | 92.58 |  |  |  | 92.88 | [5 empty] | 90.13 |  |  | 94.30 |  |  |  | 1.27 |  | 1.19 | [8 empty] | 5.93 |  |  |  |  | 0.29
2011 |  |  |  | 6803.29 |  |  | 7548 |  |  |  | 925 | [10 empty] | 83.65 |  |  |  | 83.81 | [5 empty] | 83.97 |  |  | 86.17 |  |  |  | 0.47 |  | 1.73 | [8 empty] | 14.46 |  |  |  |  | 0.15
2012 |  |  |  | 7401.44 |  |  | 8115 |  |  |  | 925 | [10 empty] | 91.56 |  |  |  | 91.65 | [5 empty] | 91.09 |  |  | 92.38 |  |  |  | 2.66 |  | 2.51 | [8 empty] | 5.84 |  |  |  |  | 0.10
2013 |  |  |  | 6892.27 |  |  | 7446 |  |  |  | 925 | [10 empty] | 83.65 |  |  |  | 83.95 | [5 empty] | 85.06 |  |  | 85.00 |  |  |  | 1.79 |  | 1.55 | [8 empty] | 14.50 |  |  |  |  | 0.30
2014 |  |  |  | 7199.40 |  |  | 8229 |  |  |  | 925 | [10 empty] | 89.69 |  |  |  | 90.10 | [5 empty] | 88.84 |  |  | 93.93 |  |  |  | 1.79 |  | 4.75 | [8 empty] | 5.15 |  |  |  |  | 0.41
2015 |  |  |  | 6817.12 |  |  | 7628 |  |  |  | 925 | [10 empty] | 86.76 |  |  |  | 86.85 | [5 empty] | 84.13 |  |  | 87.08 |  |  |  | 2.01 |  | 1.78 | [8 empty] | 11.37 |  |  |  |  | 0.09
2016 |  |  |  | 7024.91 |  |  | 7879 |  |  |  | 925 | [10 empty] | 87.77 |  |  |  | 87.94 | [5 empty] | 86.46 |  |  | 89.70 |  |  |  | 2.71 |  | 2.45 | [8 empty] | 9.62 |  |  |  |  | 0.16
2017 |  |  |  | 6786.43 |  |  | 7460 |  |  |  | 925 | [10 empty] | 84.94 |  |  |  | 84.96 | [5 empty] | 83.75 |  |  | 85.16 |  |  |  | 1.87 |  | 1.62 | [8 empty] | 13.42 |  |  |  |  | 0.03
2018 |  |  |  | 5801.48 |  |  | 6257 |  |  |  | 925 | [10 empty] | 72.16 |  |  |  | 72.21 | [5 empty] | 71.60 |  |  | 71.43 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 27.77 |  |  |  |  | 0.05
2019 |  |  |  | 6890.81 |  |  | 7642 |  |  |  | 925 | [10 empty] | 84.69 |  |  |  | 84.85 | [5 empty] | 85.04 |  |  | 87.24 |  |  |  | 0.65 |  | 0.56 | [8 empty] | 14.59 |  |  |  |  | 0.16
2020 |  |  |  | 5765.23 |  |  | 6269 |  |  |  | 925 | [10 empty] | 70.51 |  |  |  | 70.53 | [5 empty] | 70.95 |  |  | 71.37 |  |  |  | 1.02 |  | 0.72 | [8 empty] | 28.75 |  |  |  |  | 0.01
2021 |  |  |  | 5763.58 |  |  | 6496 |  |  |  | 925 | [10 empty] | 72.24 |  |  |  | 72.94 | [5 empty] | 71.13 |  |  | 74.16 |  |  |  | 0.80 |  | 0.59 | [8 empty] | 26.47 |  |  |  |  | 0.70
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1980 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 102
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2270 | [14 empty] | 817
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 920
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 16
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 126
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 77
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 13
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 2270 | [14 empty] | 1941 |  |  |  | 122 | [11 empty] | 17
Total | [22 empty] | 2270 | [14 empty] | 2080
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1980 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 9
12. |  |  | Reactor I&C Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 6
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 53
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
33. |  |  | Circulating Water System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 16
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 13
Total | [37 empty] | 120
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-June, August-December. Additional electricity generation amounted to 106640 MWh. The unit was in the routine maintenance outage from 2021.01.15 to 2021.02.05 and the overhaul outage from 2021.06.12 to 2021.08.30. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD-4
2021 Operating Experience
RU-35 | [8 empty] | LENINGRAD-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-02-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-02-09
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-08-29
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 211 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 5789.7 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.83 %
Energy Availability Factor (EAF) | [18 empty] | : | 72.99 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.91 %
Unit Capability Factor (UCF) | [18 empty] | : | 73.22 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 23.87 %
Load Factor (LF) | [18 empty] | : | 71.45 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.23 %
Operating Factor (OF) | [18 empty] | : | 75.17 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2175 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 55.59 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 634.43 | 177.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 336.58 |  |  | 640.04 | [6 empty] | 663.08 |  | 687.91 |  |  |  | 550.64 |  |  | 704.50 |  |  | 688.59 | [9 empty] | 706.32 |  |  | 5789.70
EAF [%] |  |  |  |  | 94.31 | 29.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 73.45 |  |  | 95.89 | [6 empty] | 96.86 |  | 99.83 |  |  |  | 82.04 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.46 |  |  | 72.99
UCF [%] |  |  |  |  | 94.31 | 29.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 73.45 |  |  | 96.73 | [6 empty] | 98.64 |  | 100.00 |  |  |  | 82.04 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.46 |  |  | 73.22
LF [%] |  |  |  |  | 92.19 | 28.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 48.91 |  |  | 96.10 | [6 empty] | 96.35 |  | 99.96 |  |  |  | 82.68 |  |  | 102.37 |  |  | 103.39 | [9 empty] | 102.63 |  |  | 71.45
OF [%] |  |  |  |  | 93.55 | 32.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 86.69 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 85.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 75.17
FLR [%] |  |  |  |  | 5.69 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.74 |  |  | 3.27 | [6 empty] | 1.36 |  | 0.00 |  |  |  | 17.96 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.54 |  |  | 3.83
UCL [%] |  |  |  |  | 5.69 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.17 |  |  | 3.27 | [6 empty] | 1.36 |  | 0.00 |  |  |  | 17.96 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.54 |  |  | 2.91
PUF [%] |  |  |  |  | 0.00 | 70.70 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 20.39 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 23.87
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.83 | [6 empty] | 1.78 |  | 0.17 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.23
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 237518.46 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.01 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.83 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.03 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.74 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.23 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.99 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.92 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.48 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 3931.27 |  |  | 6151 |  |  |  | 925 | [10 empty] | 76.82 |  |  |  | 76.83 | [5 empty] | 76.06 |  |  | 83.41 |  |  |  | 12.21 |  | 10.69 | [8 empty] | 12.48 |  |  |  |  | 0.01
1982 |  |  |  | 6715.19 |  |  | 7609 |  |  |  | 925 | [10 empty] | 83.59 |  |  |  | 83.72 | [5 empty] | 82.87 |  |  | 86.86 |  |  |  | 4.43 |  | 3.88 | [8 empty] | 12.40 |  |  |  |  | 0.13
1983 |  |  |  | 6844.23 |  |  | 8159 |  |  |  | 925 | [10 empty] | 85.33 |  |  |  | 86.12 | [5 empty] | 84.47 |  |  | 93.14 |  |  |  | 6.80 |  | 6.29 | [8 empty] | 7.59 |  |  |  |  | 0.79
1984 |  |  |  | 6126.32 |  |  | 6803 |  |  |  | 925 | [10 empty] | 74.43 |  |  |  | 74.94 | [5 empty] | 75.40 |  |  | 77.45 |  |  |  | 3.19 |  | 2.47 | [8 empty] | 22.59 |  |  |  |  | 0.52
1985 |  |  |  | 7335.31 |  |  | 8309 |  |  |  | 925 | [10 empty] | 90.92 |  |  |  | 91.18 | [5 empty] | 90.53 |  |  | 94.85 |  |  |  | 3.29 |  | 3.10 | [8 empty] | 5.72 |  |  |  |  | 0.26
1986 |  |  |  | 7060.95 |  |  | 7826 |  |  |  | 925 | [10 empty] | 87.65 |  |  |  | 88.69 | [5 empty] | 87.14 |  |  | 89.34 |  |  |  | 0.49 |  | 0.44 | [8 empty] | 10.87 |  |  |  |  | 1.04
1987 |  |  |  | 7319.23 |  |  | 7530 |  |  |  | 1000 | [10 empty] | 84.15 |  |  |  | 85.01 | [5 empty] | 83.55 |  |  | 85.96 |  |  |  | 2.18 |  | 1.90 | [8 empty] | 13.09 |  |  |  |  | 0.86
1988 |  |  |  | 6050.44 |  |  | 6667 |  |  |  | 925 | [10 empty] | 74.82 |  |  |  | 74.82 | [5 empty] | 74.47 |  |  | 75.90 |  |  |  | 0.72 |  | 0.54 | [8 empty] | 24.64 |  |  |  |  | 0.00
1989 |  |  |  | 7409.69 |  |  | 8185 |  |  |  | 925 | [10 empty] | 91.46 |  |  |  | 91.89 | [5 empty] | 91.44 |  |  | 93.44 |  |  |  | 2.23 |  | 2.10 | [8 empty] | 6.01 |  |  |  |  | 0.43
1990 |  |  |  | 7762.56 |  |  | 8588 |  |  |  | 925 | [10 empty] | 95.38 |  |  |  | 96.06 | [5 empty] | 95.80 |  |  | 98.04 |  |  |  | 2.33 |  | 2.29 | [8 empty] | 1.65 |  |  |  |  | 0.68
1991 |  |  |  | 6130.70 |  |  | 6870 |  |  |  | 925 | [10 empty] | 76.14 |  |  |  | 76.77 | [5 empty] | 75.66 |  |  | 78.42 |  |  |  | 1.77 |  | 1.38 | [8 empty] | 21.85 |  |  |  |  | 0.62
1992 |  |  |  | 5618.11 |  |  | 6617 |  |  |  | 925 | [10 empty] | 70.29 |  |  |  | 70.79 | [5 empty] | 69.15 |  |  | 75.34 |  |  |  | 4.30 |  | 3.18 | [8 empty] | 26.02 |  |  |  |  | 0.51
1993 |  |  |  | 6735.70 |  |  | 7762 |  |  |  | 925 | [10 empty] | 85.27 |  |  |  | 87.61 | [5 empty] | 83.13 |  |  | 88.61 |  |  |  | 1.54 |  | 1.37 | [8 empty] | 11.02 |  |  |  |  | 2.34
1994 |  |  |  | 6167.07 |  |  | 7340 |  |  |  | 925 | [10 empty] | 82.08 |  |  |  | 83.16 | [5 empty] | 76.11 |  |  | 83.79 |  |  |  | 1.33 |  | 1.12 | [8 empty] | 15.72 |  |  |  |  | 1.07
1995 |  |  |  | 6140.97 |  |  | 7270 |  |  |  | 925 | [10 empty] | 82.96 |  |  |  | 86.06 | [5 empty] | 75.79 |  |  | 82.99 |  |  |  | 0.29 |  | 0.25 | [8 empty] | 13.69 |  |  |  |  | 3.11
1996 |  |  |  | 7079.69 |  |  | 8048 |  |  |  | 925 | [10 empty] | 88.30 |  |  |  | 88.78 | [5 empty] | 87.13 |  |  | 91.62 |  |  |  | 4.63 |  | 4.31 | [8 empty] | 6.91 |  |  |  |  | 0.47
1997 |  |  |  | 7644.68 |  |  | 8760 |  |  |  | 925 | [10 empty] | 95.95 |  |  |  | 98.19 | [5 empty] | 94.34 |  |  | 100.00 |  |  |  | 1.81 |  | 1.81 | [8 empty] | 0.00 |  |  |  |  | 2.24
1998 |  |  |  | 3681.98 |  |  | 4341 |  |  |  | 925 | [10 empty] | 45.98 |  |  |  | 47.31 | [5 empty] | 45.44 |  |  | 49.55 |  |  |  | 2.11 |  | 1.02 | [8 empty] | 51.68 |  |  |  |  | 1.32
1999 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2000 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2001 |  |  |  | 3585.73 |  |  | 4387 |  |  |  | 925 | [10 empty] | 44.56 |  |  |  | 45.54 | [5 empty] | 44.25 |  |  | 50.08 |  |  |  | 23.52 |  | 14.00 | [8 empty] | 40.46 |  |  |  |  | 0.98
2002 |  |  |  | 7528.53 |  |  | 8760 |  |  |  | 925 | [10 empty] | 93.93 |  |  |  | 97.55 | [5 empty] | 92.91 |  |  | 100.00 |  |  |  | 2.45 |  | 2.45 | [8 empty] | 0.00 |  |  |  |  | 3.62
2003 |  |  |  | 1957.16 |  |  | 2399 |  |  |  | 925 | [10 empty] | 24.69 |  |  |  | 26.03 | [5 empty] | 24.15 |  |  | 27.39 |  |  |  | 2.58 |  | 0.69 | [8 empty] | 73.28 |  |  |  |  | 1.35
2004 |  |  |  | 7232.18 |  |  | 8243 |  |  |  | 925 | [10 empty] | 89.58 |  |  |  | 92.27 | [5 empty] | 89.01 |  |  | 93.84 |  |  |  | 3.43 |  | 3.28 | [8 empty] | 4.45 |  |  |  |  | 2.70
2005 |  |  |  | 6730.12 |  |  | 7838 |  |  |  | 925 | [10 empty] | 83.76 |  |  |  | 89.33 | [5 empty] | 83.05 |  |  | 89.46 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 10.57 |  |  |  |  | 5.57
2006 |  |  |  | 5611.94 |  |  | 6197 |  |  |  | 925 | [10 empty] | 69.36 |  |  |  | 69.36 | [5 empty] | 69.26 |  |  | 70.74 |  |  |  | 0.80 |  | 1.36 | [8 empty] | 29.29 |  |  |  |  | 0.00
2007 |  |  |  | 4827.43 |  |  | 5713 |  |  |  | 925 | [10 empty] | 59.73 |  |  |  | 64.85 | [5 empty] | 59.58 |  |  | 65.22 |  |  |  | 3.84 |  | 18.24 | [8 empty] | 16.91 |  |  |  |  | 5.11
2008 |  |  |  | 7526.25 |  |  | 8714 |  |  |  | 925 | [10 empty] | 94.69 |  |  |  | 94.90 | [5 empty] | 92.63 |  |  | 99.20 |  |  |  | 2.93 |  | 2.86 | [8 empty] | 2.24 |  |  |  |  | 0.22
2009 |  |  |  | 4052.83 |  |  | 4695 |  |  |  | 925 | [10 empty] | 53.23 |  |  |  | 53.37 | [5 empty] | 50.02 |  |  | 53.60 |  |  |  | 4.90 |  | 2.75 | [8 empty] | 43.88 |  |  |  |  | 0.14
2010 |  |  |  | 5222.37 |  |  | 5798 |  |  |  | 925 | [10 empty] | 64.04 |  |  |  | 64.18 | [5 empty] | 64.45 |  |  | 66.19 |  |  |  | 3.64 |  | 9.60 | [8 empty] | 26.21 |  |  |  |  | 0.14
2011 |  |  |  | 6589.79 |  |  | 7177 |  |  |  | 925 | [10 empty] | 80.76 |  |  |  | 81.01 | [5 empty] | 81.33 |  |  | 81.94 |  |  |  | 3.53 |  | 4.93 | [8 empty] | 14.06 |  |  |  |  | 0.25
2012 |  |  |  | 7559.92 |  |  | 8254 |  |  |  | 925 | [10 empty] | 92.28 |  |  |  | 92.30 | [5 empty] | 93.04 |  |  | 93.97 |  |  |  | 0.23 |  | 0.52 | [8 empty] | 7.18 |  |  |  |  | 0.02
2013 |  |  |  | 6992.92 |  |  | 7739 |  |  |  | 925 | [10 empty] | 85.84 |  |  |  | 85.93 | [5 empty] | 86.30 |  |  | 88.34 |  |  |  | 2.97 |  | 2.63 | [8 empty] | 11.43 |  |  |  |  | 0.09
2014 |  |  |  | 6942.49 |  |  | 7665 |  |  |  | 925 | [10 empty] | 85.92 |  |  |  | 86.00 | [5 empty] | 85.67 |  |  | 87.49 |  |  |  | 2.03 |  | 2.77 | [8 empty] | 11.23 |  |  |  |  | 0.08
2015 |  |  |  | 6617.16 |  |  | 7414 |  |  |  | 925 | [10 empty] | 85.58 |  |  |  | 85.60 | [5 empty] | 81.66 |  |  | 84.63 |  |  |  | 2.97 |  | 2.62 | [8 empty] | 11.78 |  |  |  |  | 0.02
2016 |  |  |  | 6912.04 |  |  | 7660 |  |  |  | 925 | [10 empty] | 85.43 |  |  |  | 85.45 | [5 empty] | 85.07 |  |  | 87.20 |  |  |  | 0.85 |  | 0.73 | [8 empty] | 13.82 |  |  |  |  | 0.01
2017 |  |  |  | 6846.75 |  |  | 7873 |  |  |  | 925 | [10 empty] | 85.57 |  |  |  | 85.58 | [5 empty] | 84.50 |  |  | 89.87 |  |  |  | 4.04 |  | 4.04 | [8 empty] | 10.39 |  |  |  |  | 0.01
2018 |  |  |  | 6951.25 |  |  | 7499 |  |  |  | 925 | [10 empty] | 84.68 |  |  |  | 84.83 | [5 empty] | 85.79 |  |  | 85.61 |  |  |  | 4.62 |  | 4.11 | [8 empty] | 11.06 |  |  |  |  | 0.15
2019 |  |  |  | 6265.79 |  |  | 6730 |  |  |  | 925 | [10 empty] | 75.83 |  |  |  | 75.83 | [5 empty] | 77.33 |  |  | 76.83 |  |  |  | 0.31 |  | 0.24 | [8 empty] | 23.94 |  |  |  |  | 0.00
2020 |  |  |  | 6842.29 |  |  | 7486 |  |  |  | 925 | [10 empty] | 84.44 |  |  |  | 84.44 | [5 empty] | 84.21 |  |  | 85.22 |  |  |  | 0.42 |  | 0.35 | [8 empty] | 15.20 |  |  |  |  | 0.01
2021 |  |  |  | 5789.70 |  |  | 6585 |  |  |  | 925 | [10 empty] | 72.99 |  |  |  | 73.22 | [5 empty] | 71.45 |  |  | 75.17 |  |  |  | 3.83 |  | 2.91 | [8 empty] | 23.87 |  |  |  |  | 0.23
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1981 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 163 | [14 empty] | 87
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2019 | [14 empty] | 1334
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 209
E. |  | Testing of plant systems or components | [39 empty] | 0
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 158
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 100 |  |  |  | 35
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 0
Z. |  | Other | [39 empty] | 19 | [11 empty] | 1
Subtotal | [22 empty] | 2019 |  |  |  | 163 | [10 empty] | 1801 |  |  |  | 142 | [11 empty] | 13
Total | [22 empty] | 2182 | [14 empty] | 1956
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1981 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [19 empty] | 130 | [14 empty] | 21
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 19
16. |  |  | Steam generation systems | [34 empty] | 11
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
33. |  |  | Circulating Water System | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [19 empty] | 33 | [14 empty] | 9
Total | [22 empty] | 163 | [14 empty] | 87
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-February, May-December. Additional electricity generation amounted to 106662 MWh. The unit was in the intermediate outage from 2021.02.10 to 2021.05.10. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH 2-1
2021 Operating Experience
RU-161 | [8 empty] | NOVOVORONEZH 2-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-392M | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-06-24
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-08-05
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2017-02-27
Reference unit power (net) | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7523.13 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.37 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.81 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 11.39 %
Unit Capability Factor (UCF) | [18 empty] | : | 80.41 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.19 %
Load Factor (LF) | [18 empty] | : | 78.07 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.6 %
Operating Factor (OF) | [18 empty] | : | 79.37 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1807 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 601.50 | 739.31 |  |  |  | 809.35 |  | 782.53 | [8 empty] | 773.83 |  |  | 0.00 | [6 empty] | 0.00 |  | 629.24 |  |  |  | 769.92 |  |  | 808.20 |  |  | 788.60 | [9 empty] | 820.66 |  |  | 7523.13
EAF [%] |  |  |  |  | 76.90 | 100.00 |  |  |  | 99.64 |  | 100.00 | [8 empty] | 96.07 |  |  | 0.30 | [6 empty] | 0.76 |  | 78.14 |  |  |  | 97.34 |  |  | 98.59 |  |  | 99.47 | [9 empty] | 100.00 |  |  | 78.81
UCF [%] |  |  |  |  | 77.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 0.30 | [6 empty] | 0.76 |  | 88.11 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.41
LF [%] |  |  |  |  | 73.50 | 100.01 |  |  |  | 98.89 |  | 98.80 | [8 empty] | 94.55 |  |  | 0.00 | [6 empty] | 0.00 |  | 76.89 |  |  |  | 97.21 |  |  | 98.75 |  |  | 99.57 | [9 empty] | 100.28 |  |  | 78.07
OF [%] |  |  |  |  | 77.55 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 76.34 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 79.37
FLR [%] |  |  |  |  | 23.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 91.72 |  | 11.89 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.37
UCL [%] |  |  |  |  | 23.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 99.24 |  | 11.89 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 11.39
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 99.70 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.19
XUF [%] |  |  |  |  | 0.10 | 0.00 |  |  |  | 0.36 |  | 0.00 | [8 empty] | 3.93 |  |  | 0.00 | [6 empty] | 0.00 |  | 9.97 |  |  |  | 2.66 |  |  | 1.41 |  |  | 0.53 | [9 empty] | 0.00 |  |  | 1.60
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 36552.59 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.41 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.23 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.75 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.88 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.63 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2017 |  |  |  | 5620.47 |  |  | 6226 |  |  |  | 1114 | [10 empty] | 62.35 |  |  |  | 65.08 | [5 empty] | 60.87 |  |  | 75.08 |  |  |  | 19.08 |  | 15.34 | [8 empty] | 19.58 |  |  |  |  | 2.73
2018 |  |  |  | 7746.87 |  |  | 7378 |  |  |  | 1114 | [10 empty] | 81.34 |  |  |  | 83.60 | [5 empty] | 79.38 |  |  | 84.22 |  |  |  | 5.56 |  | 4.92 | [8 empty] | 11.47 |  |  |  |  | 2.27
2019 |  |  |  | 7186.30 |  |  | 6885 |  |  |  | 1100 | [10 empty] | 76.74 |  |  |  | 77.97 | [5 empty] | 74.58 |  |  | 78.60 |  |  |  | 1.81 |  | 1.44 | [8 empty] | 20.59 |  |  |  |  | 1.22
2020 |  |  |  | 7602.46 |  |  | 7465 |  |  |  | 1100 | [10 empty] | 80.29 |  |  |  | 82.00 | [5 empty] | 78.68 |  |  | 84.98 |  |  |  | 3.44 |  | 4.32 | [8 empty] | 13.67 |  |  |  |  | 1.71
2021 |  |  |  | 7523.13 |  |  | 6953 |  |  |  | 1100 | [10 empty] | 78.81 |  |  |  | 80.41 | [5 empty] | 78.07 |  |  | 79.37 |  |  |  | 4.37 |  | 11.39 | [8 empty] | 8.19 |  |  |  |  | 1.60
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2017 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 315 | [14 empty] | 294
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 716 | [14 empty] | 1271
Z. |  | Other | [24 empty] | 672 | [14 empty] | 139
Subtotal | [22 empty] | 716 |  |  |  | 987 | [10 empty] | 1271 |  |  |  | 433
Total | [22 empty] | 1703 | [14 empty] | 1704
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2017 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
14. |  |  | Safety Systems | [34 empty] | 25
31. |  |  | Turbine and auxiliaries | [19 empty] | 188 | [14 empty] | 91
32. |  |  | Feedwater and Main Steam System | [19 empty] | 127 | [14 empty] | 78
33. |  |  | Circulating Water System | [34 empty] | 43
41. |  |  | Main Generator Systems | [34 empty] | 47
Total | [22 empty] | 315 | [14 empty] | 284
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in Febriary, December. Additional electricity generation amounted to 939.55 MWh. The unit was in the routine maintenance outage from 2021.06.01 to 2021.07.01. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH 2-2
2021 Operating Experience
RU-162 | [8 empty] | NOVOVORONEZH 2-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-392M | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-07-12
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-05-01
Gross electrical power | [12 empty] | : |  |  | 1181 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2019-10-31
Reference unit power (net) | [12 empty] | : |  |  | 1101 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7348.32 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.15 %
Energy Availability Factor (EAF) | [18 empty] | : | 76.69 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.4 %
Unit Capability Factor (UCF) | [18 empty] | : | 79.28 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 18.33 %
Load Factor (LF) | [18 empty] | : | 76.19 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.59 %
Operating Factor (OF) | [18 empty] | : | 79.37 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1807 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 795.82 | 739.49 |  |  |  | 808.10 |  | 0.00 | [8 empty] | 0.00 |  |  | 357.40 | [6 empty] | 745.92 |  | 730.23 |  |  |  | 756.99 |  |  | 804.99 |  |  | 789.78 | [9 empty] | 819.61 |  |  | 7348.32
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.70 |  | 0.34 | [8 empty] | 0.03 |  |  | 47.22 | [6 empty] | 91.58 |  | 89.42 |  |  |  | 95.28 |  |  | 97.87 |  |  | 99.05 | [9 empty] | 100.00 |  |  | 76.69
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 0.34 | [8 empty] | 0.03 |  |  | 52.31 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 98.54 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 79.28
LF [%] |  |  |  |  | 97.15 | 99.95 |  |  |  | 98.65 |  | 0.00 | [8 empty] | 0.00 |  |  | 45.09 | [6 empty] | 91.06 |  | 89.15 |  |  |  | 95.49 |  |  | 98.27 |  |  | 99.63 | [9 empty] | 100.06 |  |  | 76.19
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 53.61 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 98.75 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 79.37
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 1.46 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.15
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 27.70 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 1.46 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.40
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 99.66 | [8 empty] | 99.97 |  |  | 19.99 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 18.33
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.30 |  | 0.00 | [8 empty] | 0.00 |  |  | 5.09 | [6 empty] | 8.42 |  | 10.58 |  |  |  | 3.26 |  |  | 2.13 |  |  | 0.95 | [9 empty] | 0.00 |  |  | 2.59
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 18507.93 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.94 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.59 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.69 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.87 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.2 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.13 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2019 |  |  |  | 3557.06 |  |  | 4222 |  |  |  | 1101 | [10 empty] | 85.48 |  |  |  | 85.48 | [5 empty] | 83.47 |  |  | 88.25 |  |  |  | 13.57 |  | 13.43 | [8 empty] | 1.09 |  |  |  |  | 0.00
2020 |  |  |  | 7602.61 |  |  | 7367 |  |  |  | 1101 | [10 empty] | 81.50 |  |  |  | 83.68 | [5 empty] | 78.61 |  |  | 83.87 |  |  |  | 3.46 |  | 3.00 | [8 empty] | 13.32 |  |  |  |  | 2.18
2021 |  |  |  | 7348.32 |  |  | 6953 |  |  |  | 1101 | [10 empty] | 76.69 |  |  |  | 79.28 | [5 empty] | 76.19 |  |  | 79.37 |  |  |  | 0.15 |  | 2.40 | [8 empty] | 18.33 |  |  |  |  | 2.59
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2019 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 10 | [14 empty] | 191
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1603 | [14 empty] | 1280
L. |  | Human factor related | [39 empty] | 10
Z. |  | Other | [24 empty] | 285 | [14 empty] | 131
Subtotal | [22 empty] | 1603 |  |  |  | 295 | [10 empty] | 1280 |  |  |  | 332
Total | [22 empty] | 1898 | [14 empty] | 1612
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2019 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [19 empty] | 10 | [14 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 116
33. |  |  | Circulating Water System | [34 empty] | 18
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 10 | [14 empty] | 162
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. The unit was in the overhaul outage from 2021.04.01 to 2021.06.06. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH-4
2021 Operating Experience
RU-11 | [8 empty] | NOVOVORONEZH-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-179 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-07-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1972-12-28
Gross electrical power | [12 empty] | : |  |  | 417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-03-24
Reference unit power (net) | [12 empty] | : |  |  | 385 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 295.8
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 3020.99 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.69 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.51 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.46 %
Load Factor (LF) | [18 empty] | : | 89.57 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.82 %
Operating Factor (OF) | [18 empty] | : | 90.76 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 809 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 97.27 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 270.32 | 262.82 |  |  |  | 289.58 |  | 281.08 | [8 empty] | 279.95 |  |  | 268.20 | [6 empty] | 272.88 |  | 170.59 |  |  |  | 57.60 |  |  | 282.57 |  |  | 286.19 | [9 empty] | 299.21 |  |  | 3020.99
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.46 |  |  | 97.82 | [6 empty] | 96.42 |  | 61.05 |  |  |  | 21.27 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.69
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.72 |  |  | 100.00 | [6 empty] | 100.00 |  | 64.77 |  |  |  | 21.27 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.51
LF [%] |  |  |  |  | 94.37 | 101.59 |  |  |  | 101.10 |  | 101.40 | [8 empty] | 97.73 |  |  | 96.75 | [6 empty] | 95.27 |  | 59.55 |  |  |  | 20.78 |  |  | 98.65 |  |  | 103.24 | [9 empty] | 104.46 |  |  | 89.57
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 65.05 |  |  |  | 23.75 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.76
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.28 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.28 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 35.23 |  |  |  | 78.73 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.46
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.26 |  |  | 2.18 | [6 empty] | 3.58 |  | 3.72 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.82
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 129144.73 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.37 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.2 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.71 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.52 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.77 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.06 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.33 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 2570.51 |  |  | 8072 |  |  |  | 385 | [10 empty] | 84.20 |  |  |  | 84.20 | [5 empty] | 84.95 |  |  | 93.15 |  |  |  | 14.82 |  | 14.65 | [8 empty] | 1.15 |  |  |  |  | 0.00
1974 |  |  |  | 2411.84 |  |  | 7159 |  |  |  | 385 | [10 empty] | 71.28 |  |  |  | 71.28 | [5 empty] | 71.51 |  |  | 81.72 |  |  |  | 15.90 |  | 13.48 | [8 empty] | 15.24 |  |  |  |  | 0.00
1975 |  |  |  | 2644.87 |  |  | 7950 |  |  |  | 385 | [10 empty] | 75.64 |  |  |  | 75.64 | [5 empty] | 78.42 |  |  | 90.75 |  |  |  | 9.17 |  | 7.63 | [8 empty] | 16.73 |  |  |  |  | 0.00
1976 |  |  |  | 2924.13 |  |  | 7963 |  |  |  | 385 | [10 empty] | 84.48 |  |  |  | 84.48 | [5 empty] | 86.47 |  |  | 90.65 |  |  |  | 4.63 |  | 4.10 | [8 empty] | 11.42 |  |  |  |  | 0.00
1977 |  |  |  | 2822.95 |  |  | 7637 |  |  |  | 385 | [10 empty] | 81.34 |  |  |  | 81.34 | [5 empty] | 83.70 |  |  | 87.18 |  |  |  | 4.88 |  | 4.17 | [8 empty] | 14.49 |  |  |  |  | 0.00
1978 |  |  |  | 2658.54 |  |  | 7388 |  |  |  | 385 | [10 empty] | 78.18 |  |  |  | 78.18 | [5 empty] | 78.83 |  |  | 84.34 |  |  |  | 3.70 |  | 3.00 | [8 empty] | 18.82 |  |  |  |  | 0.00
1979 |  |  |  | 2442.24 |  |  | 6888 |  |  |  | 385 | [10 empty] | 72.44 |  |  |  | 72.44 | [5 empty] | 72.41 |  |  | 78.63 |  |  |  | 8.70 |  | 6.90 | [8 empty] | 20.66 |  |  |  |  | 0.00
1980 |  |  |  | 2842.93 |  |  | 7690 |  |  |  | 385 | [10 empty] | 84.08 |  |  |  | 84.08 | [5 empty] | 84.06 |  |  | 87.55 |  |  |  | 3.15 |  | 2.74 | [8 empty] | 13.18 |  |  |  |  | 0.00
1981 |  |  |  | 3019.87 |  |  | 8278 |  |  |  | 385 | [10 empty] | 90.03 |  |  |  | 90.03 | [5 empty] | 89.55 |  |  | 94.51 |  |  |  | 4.32 |  | 4.06 | [8 empty] | 5.91 |  |  |  |  | 0.00
1982 |  |  |  | 2797.51 |  |  | 8278 |  |  |  | 385 | [10 empty] | 83.88 |  |  |  | 83.88 | [5 empty] | 82.95 |  |  | 94.50 |  |  |  | 9.47 |  | 8.78 | [8 empty] | 7.35 |  |  |  |  | 0.00
1983 |  |  |  | 2950.30 |  |  | 8216 |  |  |  | 385 | [10 empty] | 89.15 |  |  |  | 89.15 | [5 empty] | 87.48 |  |  | 93.79 |  |  |  | 3.80 |  | 3.52 | [8 empty] | 7.33 |  |  |  |  | 0.00
1984 |  |  |  | 2974.10 |  |  | 7982 |  |  |  | 385 | [10 empty] | 87.89 |  |  |  | 87.89 | [5 empty] | 87.94 |  |  | 90.87 |  |  |  | 3.16 |  | 2.87 | [8 empty] | 9.24 |  |  |  |  | 0.00
1985 |  |  |  | 3097.87 |  |  | 8250 |  |  |  | 385 | [10 empty] | 91.30 |  |  |  | 91.30 | [5 empty] | 91.85 |  |  | 94.18 |  |  |  | 2.71 |  | 2.54 | [8 empty] | 6.16 |  |  |  |  | 0.00
1986 |  |  |  | 2792.21 |  |  | 7688 |  |  |  | 385 | [10 empty] | 82.62 |  |  |  | 82.62 | [5 empty] | 82.79 |  |  | 87.76 |  |  |  | 5.57 |  | 4.88 | [8 empty] | 12.51 |  |  |  |  | 0.00
1987 |  |  |  | 3262.68 |  |  | 8252 |  |  |  | 417 | [10 empty] | 91.72 |  |  |  | 91.72 | [5 empty] | 89.32 |  |  | 94.20 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 8.14 |  |  |  |  | 0.00
1988 |  |  |  | 2529.37 |  |  | 7152 |  |  |  | 385 | [10 empty] | 79.97 |  |  |  | 79.97 | [5 empty] | 74.79 |  |  | 81.42 |  |  |  | 1.21 |  | 0.98 | [8 empty] | 19.05 |  |  |  |  | 0.00
1989 |  |  |  | 2710.26 |  |  | 8357 |  |  |  | 385 | [10 empty] | 90.16 |  |  |  | 90.19 | [5 empty] | 80.36 |  |  | 95.40 |  |  |  | 5.71 |  | 5.46 | [8 empty] | 4.35 |  |  |  |  | 0.04
1990 |  |  |  | 2244.69 |  |  | 6622 |  |  |  | 385 | [10 empty] | 69.63 |  |  |  | 70.55 | [5 empty] | 66.56 |  |  | 75.59 |  |  |  | 11.28 |  | 8.97 | [8 empty] | 20.48 |  |  |  |  | 0.92
1991 |  |  |  | 1827.62 |  |  | 5540 |  |  |  | 385 | [10 empty] | 57.96 |  |  |  | 58.24 | [5 empty] | 54.19 |  |  | 63.24 |  |  |  | 9.28 |  | 5.96 | [8 empty] | 35.80 |  |  |  |  | 0.28
1992 |  |  |  | 2853.44 |  |  | 8163 |  |  |  | 385 | [10 empty] | 82.38 |  |  |  | 87.35 | [5 empty] | 84.38 |  |  | 92.94 |  |  |  | 6.01 |  | 5.58 | [8 empty] | 7.07 |  |  |  |  | 4.97
1993 |  |  |  | 2613.71 |  |  | 7204 |  |  |  | 385 | [10 empty] | 76.60 |  |  |  | 79.73 | [5 empty] | 77.50 |  |  | 82.24 |  |  |  | 2.64 |  | 2.16 | [8 empty] | 18.11 |  |  |  |  | 3.13
1994 |  |  |  | 1954.27 |  |  | 6033 |  |  |  | 385 | [10 empty] | 56.65 |  |  |  | 66.91 | [5 empty] | 57.95 |  |  | 68.87 |  |  |  | 2.79 |  | 1.92 | [8 empty] | 31.17 |  |  |  |  | 10.26
1995 |  |  |  | 2119.99 |  |  | 5818 |  |  |  | 385 | [10 empty] | 62.15 |  |  |  | 65.50 | [5 empty] | 62.86 |  |  | 66.42 |  |  |  | 0.64 |  | 0.42 | [8 empty] | 34.08 |  |  |  |  | 3.35
1996 |  |  |  | 3080.28 |  |  | 8362 |  |  |  | 385 | [10 empty] | 90.38 |  |  |  | 93.78 | [5 empty] | 91.08 |  |  | 95.20 |  |  |  | 1.08 |  | 1.02 | [8 empty] | 5.20 |  |  |  |  | 3.40
1997 |  |  |  | 2235.48 |  |  | 6690 |  |  |  | 385 | [10 empty] | 66.98 |  |  |  | 70.29 | [5 empty] | 66.28 |  |  | 76.37 |  |  |  | 0.76 |  | 0.54 | [8 empty] | 29.17 |  |  |  |  | 3.30
1998 |  |  |  | 2714.87 |  |  | 7366 |  |  |  | 385 | [10 empty] | 80.18 |  |  |  | 83.16 | [5 empty] | 80.50 |  |  | 84.09 |  |  |  | 0.98 |  | 0.82 | [8 empty] | 16.02 |  |  |  |  | 2.98
1999 |  |  |  | 1791.48 |  |  | 4927 |  |  |  | 385 | [10 empty] | 53.21 |  |  |  | 54.93 | [5 empty] | 53.12 |  |  | 56.24 |  |  |  | 17.55 |  | 11.69 | [8 empty] | 33.38 |  |  |  |  | 1.72
2000 |  |  |  | 2474.25 |  |  | 6784 |  |  |  | 385 | [10 empty] | 73.08 |  |  |  | 74.64 | [5 empty] | 73.16 |  |  | 77.23 |  |  |  | 3.12 |  | 2.40 | [8 empty] | 22.96 |  |  |  |  | 1.56
2001 |  |  |  | 2655.95 |  |  | 7173 |  |  |  | 385 | [10 empty] | 79.22 |  |  |  | 80.72 | [5 empty] | 78.75 |  |  | 81.88 |  |  |  | 1.24 |  | 1.01 | [8 empty] | 18.26 |  |  |  |  | 1.51
2002 |  |  |  | 2184.85 |  |  | 5857 |  |  |  | 385 | [10 empty] | 64.21 |  |  |  | 65.37 | [5 empty] | 64.78 |  |  | 66.86 |  |  |  | 4.51 |  | 3.09 | [8 empty] | 31.55 |  |  |  |  | 1.15
2003 |  |  |  | 2583.05 |  |  | 6950 |  |  |  | 385 | [10 empty] | 76.75 |  |  |  | 78.78 | [5 empty] | 76.59 |  |  | 79.34 |  |  |  | 1.32 |  | 1.05 | [8 empty] | 20.17 |  |  |  |  | 2.02
2004 |  |  |  | 2714.01 |  |  | 7685 |  |  |  | 385 | [10 empty] | 80.75 |  |  |  | 83.75 | [5 empty] | 80.25 |  |  | 87.49 |  |  |  | 4.90 |  | 4.32 | [8 empty] | 11.94 |  |  |  |  | 2.99
2005 |  |  |  | 2433.38 |  |  | 7228 |  |  |  | 385 | [10 empty] | 73.09 |  |  |  | 75.27 | [5 empty] | 72.15 |  |  | 82.51 |  |  |  | 12.96 |  | 11.20 | [8 empty] | 13.53 |  |  |  |  | 2.18
2006 |  |  |  | 2575.08 |  |  | 7636 |  |  |  | 385 | [10 empty] | 76.49 |  |  |  | 81.29 | [5 empty] | 76.35 |  |  | 87.17 |  |  |  | 8.30 |  | 7.36 | [8 empty] | 11.36 |  |  |  |  | 4.79
2007 |  |  |  | 2290.27 |  |  | 6488 |  |  |  | 385 | [10 empty] | 67.88 |  |  |  | 69.12 | [5 empty] | 67.91 |  |  | 74.06 |  |  |  | 8.19 |  | 9.08 | [8 empty] | 21.80 |  |  |  |  | 1.24
2008 |  |  |  | 2876.30 |  |  | 7464 |  |  |  | 385 | [10 empty] | 83.37 |  |  |  | 84.02 | [5 empty] | 85.05 |  |  | 84.97 |  |  |  | 3.95 |  | 3.45 | [8 empty] | 12.53 |  |  |  |  | 0.65
2009 |  |  |  | 2931.78 |  |  | 7580 |  |  |  | 385 | [10 empty] | 85.23 |  |  |  | 86.31 | [5 empty] | 86.93 |  |  | 86.53 |  |  |  | 0.01 |  | 0.78 | [8 empty] | 12.91 |  |  |  |  | 1.08
2010 |  |  |  | 2928.70 |  |  | 7727 |  |  |  | 385 | [10 empty] | 85.82 |  |  |  | 87.48 | [5 empty] | 86.84 |  |  | 88.21 |  |  |  | 3.36 |  | 3.04 | [8 empty] | 9.48 |  |  |  |  | 1.66
2011 |  |  |  | 2707.55 |  |  | 7263 |  |  |  | 385 | [10 empty] | 80.64 |  |  |  | 82.08 | [5 empty] | 80.29 |  |  | 82.92 |  |  |  | 1.69 |  | 1.41 | [8 empty] | 16.51 |  |  |  |  | 1.44
2012 |  |  |  | 2944.86 |  |  | 7707 |  |  |  | 385 | [10 empty] | 87.14 |  |  |  | 87.87 | [5 empty] | 87.08 |  |  | 87.74 |  |  |  | 1.22 |  | 1.09 | [8 empty] | 11.04 |  |  |  |  | 0.73
2013 |  |  |  | 3038.98 |  |  | 7929 |  |  |  | 385 | [10 empty] | 89.36 |  |  |  | 90.36 | [5 empty] | 90.11 |  |  | 90.51 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.63 |  |  |  |  | 1.00
2014 |  |  |  | 3061.07 |  |  | 7932 |  |  |  | 385 | [10 empty] | 89.26 |  |  |  | 90.33 | [5 empty] | 90.75 |  |  | 90.54 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 9.56 |  |  |  |  | 1.07
2015 |  |  |  | 2704.38 |  |  | 7085 |  |  |  | 385 | [10 empty] | 79.59 |  |  |  | 80.43 | [5 empty] | 80.19 |  |  | 80.88 |  |  |  | 0.45 |  | 0.36 | [8 empty] | 19.21 |  |  |  |  | 0.83
2016 |  |  |  | 2959.49 |  |  | 7783 |  |  |  | 385 | [10 empty] | 87.26 |  |  |  | 88.31 | [5 empty] | 87.51 |  |  | 88.60 |  |  |  | 2.91 |  | 2.65 | [8 empty] | 9.04 |  |  |  |  | 1.05
2017 |  |  |  | 3148.86 |  |  | 8259 |  |  |  | 385 | [10 empty] | 92.54 |  |  |  | 93.92 | [5 empty] | 93.37 |  |  | 94.28 |  |  |  | 0.37 |  | 0.35 | [8 empty] | 5.73 |  |  |  |  | 1.38
2018 |  |  |  | 8.92 |  |  | 73 |  |  |  | 385 | [10 empty] | 0.43 |  |  |  | 0.43 | [5 empty] | 0.26 |  |  | 0.83 |  |  |  | 47.79 |  | 0.39 | [8 empty] | 99.18 |  |  |  |  | 0.00
2019 |  |  |  | 2994.94 |  |  | 7654 |  |  |  | 385 | [10 empty] | 86.23 |  |  |  | 86.33 | [5 empty] | 88.80 |  |  | 87.37 |  |  |  | 3.00 |  | 2.67 | [8 empty] | 11.01 |  |  |  |  | 0.09
2020 |  |  |  | 2945.24 |  |  | 7956 |  |  |  | 385 | [10 empty] | 89.27 |  |  |  | 90.40 | [5 empty] | 87.09 |  |  | 90.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.60 |  |  |  |  | 1.13
2021 |  |  |  | 3020.99 |  |  | 7951 |  |  |  | 385 | [10 empty] | 89.69 |  |  |  | 90.51 | [5 empty] | 89.57 |  |  | 90.76 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 9.46 |  |  |  |  | 0.82
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1973 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 68
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 809 | [14 empty] | 1228
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 91
E. |  | Testing of plant systems or components | [35 empty] | 12
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 56
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 8
L. |  | Human factor related | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 9
Z. |  | Other | [35 empty] | 2 |  |  |  | 13
Subtotal | [22 empty] | 809 | [14 empty] | 1389 |  |  |  | 92 | [11 empty] | 8
Total | [22 empty] | 809 | [14 empty] | 1489
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1973 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
16. |  |  | Steam generation systems | [34 empty] | 32
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 0
Total | [37 empty] | 69
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-April, September-December. Additional electricity generation amounted to 48330 MWh. The unit was in the intermediate outage from 2021.08.21 to 2021.09.23. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH-5
2021 Operating Experience
RU-20 | [8 empty] | NOVOVORONEZH-5 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-187 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-03-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-05-31
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-02-20
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 324
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.5
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 109 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7227.84 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.45 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.16 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.77 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.84 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.4 %
Load Factor (LF) | [18 empty] | : | 86.85 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.68 %
Operating Factor (OF) | [18 empty] | : | 88.74 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 986 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 7.03 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 704.55 | 645.25 |  |  |  | 709.41 |  | 683.91 | [8 empty] | 699.86 |  |  | 658.21 | [6 empty] | 188.57 |  | 208.28 |  |  |  | 664.77 |  |  | 672.60 |  |  | 684.11 | [9 empty] | 708.32 |  |  | 7227.84
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.80 |  | 99.76 | [8 empty] | 99.56 |  |  | 96.88 | [6 empty] | 27.77 |  | 30.91 |  |  |  | 97.98 |  |  | 95.93 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.16
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.80 |  | 99.76 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 29.23 |  | 32.04 |  |  |  | 100.00 |  |  | 95.93 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.84
LF [%] |  |  |  |  | 99.68 | 101.07 |  |  |  | 100.37 |  | 99.99 | [8 empty] | 99.02 |  |  | 96.23 | [6 empty] | 26.68 |  | 29.47 |  |  |  | 97.19 |  |  | 95.16 |  |  | 100.02 | [9 empty] | 100.22 |  |  | 86.85
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 29.84 |  | 37.63 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.74
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.20 |  | 0.24 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.63 |  | 0.00 |  |  |  | 0.00 |  |  | 4.07 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.45
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.20 |  | 0.24 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.19 |  | 4.32 |  |  |  | 0.00 |  |  | 4.07 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.77
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 70.59 |  | 63.63 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 11.40
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.44 |  |  | 3.12 | [6 empty] | 1.46 |  | 1.13 |  |  |  | 2.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.68
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 221811.01 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 11.76 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 66.98 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.02 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 67.8 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.18 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 66.76 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.82 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.83 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 4639.79 |  |  | 6929 |  |  |  | 950 | [10 empty] | 56.62 |  |  |  | 56.62 | [5 empty] | 56.10 |  |  | 77.77 |  |  |  | 28.48 |  | 22.54 | [8 empty] | 20.83 |  |  |  |  | 0.00
1982 |  |  |  | 5042.84 |  |  | 6631 |  |  |  | 950 | [10 empty] | 60.89 |  |  |  | 60.89 | [5 empty] | 60.60 |  |  | 75.70 |  |  |  | 25.30 |  | 20.62 | [8 empty] | 18.49 |  |  |  |  | 0.00
1983 |  |  |  | 6607.53 |  |  | 7716 |  |  |  | 950 | [10 empty] | 79.53 |  |  |  | 79.53 | [5 empty] | 79.40 |  |  | 88.08 |  |  |  | 7.92 |  | 6.84 | [8 empty] | 13.64 |  |  |  |  | 0.00
1984 |  |  |  | 6979.64 |  |  | 7742 |  |  |  | 950 | [10 empty] | 83.42 |  |  |  | 83.42 | [5 empty] | 83.64 |  |  | 88.14 |  |  |  | 5.18 |  | 4.56 | [8 empty] | 12.02 |  |  |  |  | 0.00
1985 |  |  |  | 6894.29 |  |  | 7979 |  |  |  | 950 | [10 empty] | 83.12 |  |  |  | 83.12 | [5 empty] | 82.84 |  |  | 91.08 |  |  |  | 8.96 |  | 8.18 | [8 empty] | 8.69 |  |  |  |  | 0.00
1986 |  |  |  | 5523.75 |  |  | 6806 |  |  |  | 950 | [10 empty] | 65.91 |  |  |  | 65.96 | [5 empty] | 66.38 |  |  | 77.69 |  |  |  | 17.36 |  | 13.86 | [8 empty] | 20.18 |  |  |  |  | 0.04
1987 |  |  |  | 7052.70 |  |  | 7399 |  |  |  | 1000 | [10 empty] | 81.79 |  |  |  | 81.79 | [5 empty] | 80.51 |  |  | 84.46 |  |  |  | 2.68 |  | 2.26 | [8 empty] | 15.96 |  |  |  |  | 0.00
1988 |  |  |  | 3017.85 |  |  | 3439 |  |  |  | 950 | [10 empty] | 36.51 |  |  |  | 36.51 | [5 empty] | 36.16 |  |  | 39.15 |  |  |  | 59.88 |  | 54.50 | [8 empty] | 8.98 |  |  |  |  | 0.00
1989 |  |  |  | 3308.95 |  |  | 3778 |  |  |  | 950 | [10 empty] | 40.88 |  |  |  | 40.88 | [5 empty] | 39.76 |  |  | 43.13 |  |  |  | 25.41 |  | 13.93 | [8 empty] | 45.19 |  |  |  |  | 0.00
1990 |  |  |  | 3913.28 |  |  | 4715 |  |  |  | 950 | [10 empty] | 47.63 |  |  |  | 47.72 | [5 empty] | 47.02 |  |  | 53.82 |  |  |  | 15.35 |  | 8.66 | [8 empty] | 43.62 |  |  |  |  | 0.09
1991 |  |  |  | 5878.22 |  |  | 6996 |  |  |  | 950 | [10 empty] | 71.54 |  |  |  | 71.54 | [5 empty] | 70.63 |  |  | 79.86 |  |  |  | 19.86 |  | 17.72 | [8 empty] | 10.74 |  |  |  |  | 0.00
1992 |  |  |  | 3752.83 |  |  | 5244 |  |  |  | 950 | [10 empty] | 45.70 |  |  |  | 45.89 | [5 empty] | 44.98 |  |  | 59.71 |  |  |  | 8.71 |  | 4.38 | [8 empty] | 49.73 |  |  |  |  | 0.20
1993 |  |  |  | 5935.41 |  |  | 7448 |  |  |  | 950 | [10 empty] | 72.55 |  |  |  | 73.79 | [5 empty] | 71.32 |  |  | 85.02 |  |  |  | 10.42 |  | 8.59 | [8 empty] | 17.62 |  |  |  |  | 1.24
1994 |  |  |  | 2281.89 |  |  | 4288 |  |  |  | 950 | [10 empty] | 28.94 |  |  |  | 33.19 | [5 empty] | 27.42 |  |  | 48.95 |  |  |  | 50.98 |  | 34.51 | [8 empty] | 32.29 |  |  |  |  | 4.26
1995 |  |  |  | 4753.72 |  |  | 6670 |  |  |  | 950 | [10 empty] | 57.46 |  |  |  | 63.87 | [5 empty] | 57.12 |  |  | 76.14 |  |  |  | 14.52 |  | 10.85 | [8 empty] | 25.28 |  |  |  |  | 6.41
1996 |  |  |  | 3861.84 |  |  | 4759 |  |  |  | 950 | [10 empty] | 46.71 |  |  |  | 46.71 | [5 empty] | 46.28 |  |  | 54.18 |  |  |  | 15.10 |  | 8.31 | [8 empty] | 44.98 |  |  |  |  | 0.00
1997 |  |  |  | 5949.25 |  |  | 6854 |  |  |  | 950 | [10 empty] | 71.37 |  |  |  | 71.69 | [5 empty] | 71.49 |  |  | 78.24 |  |  |  | 7.84 |  | 6.10 | [8 empty] | 22.21 |  |  |  |  | 0.33
1998 |  |  |  | 3771.78 |  |  | 4457 |  |  |  | 950 | [10 empty] | 44.89 |  |  |  | 45.48 | [5 empty] | 45.32 |  |  | 50.88 |  |  |  | 28.35 |  | 17.99 | [8 empty] | 36.52 |  |  |  |  | 0.60
1999 |  |  |  | 4845.42 |  |  | 6062 |  |  |  | 950 | [10 empty] | 58.73 |  |  |  | 61.16 | [5 empty] | 58.22 |  |  | 69.20 |  |  |  | 17.37 |  | 12.86 | [8 empty] | 25.99 |  |  |  |  | 2.43
2000 |  |  |  | 5278.64 |  |  | 6479 |  |  |  | 950 | [10 empty] | 63.54 |  |  |  | 65.56 | [5 empty] | 63.26 |  |  | 73.76 |  |  |  | 7.30 |  | 5.17 | [8 empty] | 29.27 |  |  |  |  | 2.02
2001 |  |  |  | 5984.59 |  |  | 7508 |  |  |  | 950 | [10 empty] | 72.26 |  |  |  | 73.22 | [5 empty] | 71.91 |  |  | 85.71 |  |  |  | 6.60 |  | 5.17 | [8 empty] | 21.61 |  |  |  |  | 0.96
2002 |  |  |  | 6762.21 |  |  | 7430 |  |  |  | 950 | [10 empty] | 80.68 |  |  |  | 83.14 | [5 empty] | 81.26 |  |  | 84.82 |  |  |  | 1.95 |  | 1.65 | [8 empty] | 15.21 |  |  |  |  | 2.45
2003 |  |  |  | 6951.21 |  |  | 7507 |  |  |  | 950 | [10 empty] | 83.05 |  |  |  | 84.51 | [5 empty] | 83.53 |  |  | 85.70 |  |  |  | 0.93 |  | 0.79 | [8 empty] | 14.70 |  |  |  |  | 1.46
2004 |  |  |  | 3610.61 |  |  | 4032 |  |  |  | 950 | [10 empty] | 43.13 |  |  |  | 43.61 | [5 empty] | 43.27 |  |  | 45.90 |  |  |  | 44.15 |  | 34.48 | [8 empty] | 21.91 |  |  |  |  | 0.48
2005 |  |  |  | 2544.26 |  |  | 2861 |  |  |  | 950 | [10 empty] | 30.60 |  |  |  | 31.42 | [5 empty] | 30.57 |  |  | 32.66 |  |  |  | 0.00 |  | 68.58 | [8 empty] | 0.00 |  |  |  |  | 0.82
2006 |  |  |  | 7264.41 |  |  | 7762 |  |  |  | 950 | [10 empty] | 86.70 |  |  |  | 87.75 | [5 empty] | 87.29 |  |  | 88.61 |  |  |  | 0.61 |  | 0.54 | [8 empty] | 11.71 |  |  |  |  | 1.05
2007 |  |  |  | 6556.27 |  |  | 7140 |  |  |  | 950 | [10 empty] | 78.48 |  |  |  | 79.84 | [5 empty] | 78.78 |  |  | 81.51 |  |  |  | 7.10 |  | 7.85 | [8 empty] | 12.31 |  |  |  |  | 1.36
2008 |  |  |  | 7285.18 |  |  | 7718 |  |  |  | 950 | [10 empty] | 86.89 |  |  |  | 87.00 | [5 empty] | 87.30 |  |  | 87.86 |  |  |  | 0.51 |  | 0.44 | [8 empty] | 12.56 |  |  |  |  | 0.11
2009 |  |  |  | 6518.11 |  |  | 6865 |  |  |  | 950 | [10 empty] | 77.59 |  |  |  | 77.86 | [5 empty] | 78.32 |  |  | 78.37 |  |  |  | 4.04 |  | 3.28 | [8 empty] | 18.86 |  |  |  |  | 0.27
2010 |  |  |  | 5585.30 |  |  | 6404 |  |  |  | 950 | [10 empty] | 66.98 |  |  |  | 69.12 | [5 empty] | 67.11 |  |  | 73.11 |  |  |  | 5.83 |  | 4.28 | [8 empty] | 26.61 |  |  |  |  | 2.13
2011 |  |  |  | 2085.77 |  |  | 2422 |  |  |  | 950 | [10 empty] | 25.11 |  |  |  | 25.11 | [5 empty] | 25.07 |  |  | 27.65 |  |  |  | 7.01 |  | 7.99 | [8 empty] | 66.90 |  |  |  |  | 0.00
2012 |  |  |  | 7014.58 |  |  | 7457 |  |  |  | 950 | [10 empty] | 83.60 |  |  |  | 83.72 | [5 empty] | 84.06 |  |  | 84.89 |  |  |  | 1.80 |  | 2.89 | [8 empty] | 13.38 |  |  |  |  | 0.13
2013 |  |  |  | 7205.36 |  |  | 7773 |  |  |  | 950 | [10 empty] | 85.97 |  |  |  | 86.24 | [5 empty] | 86.58 |  |  | 88.73 |  |  |  | 1.20 |  | 1.23 | [8 empty] | 12.54 |  |  |  |  | 0.27
2014 |  |  |  | 6193.58 |  |  | 7712 |  |  |  | 950 | [10 empty] | 74.39 |  |  |  | 74.40 | [5 empty] | 74.42 |  |  | 88.03 |  |  |  | 11.44 |  | 9.61 | [8 empty] | 15.99 |  |  |  |  | 0.01
2015 |  |  |  | 6209.76 |  |  | 7120 |  |  |  | 950 | [10 empty] | 74.34 |  |  |  | 74.50 | [5 empty] | 74.62 |  |  | 81.28 |  |  |  | 8.43 |  | 7.73 | [8 empty] | 17.77 |  |  |  |  | 0.16
2016 |  |  |  | 7191.83 |  |  | 7777 |  |  |  | 950 | [10 empty] | 85.94 |  |  |  | 86.18 | [5 empty] | 86.18 |  |  | 88.54 |  |  |  | 1.73 |  | 1.85 | [8 empty] | 11.97 |  |  |  |  | 0.24
2017 |  |  |  | 6560.03 |  |  | 7811 |  |  |  | 950 | [10 empty] | 78.87 |  |  |  | 79.36 | [5 empty] | 78.83 |  |  | 89.17 |  |  |  | 0.60 |  | 0.48 | [8 empty] | 20.16 |  |  |  |  | 0.49
2018 |  |  |  | 7134.80 |  |  | 7766 |  |  |  | 950 | [10 empty] | 86.22 |  |  |  | 87.70 | [5 empty] | 85.73 |  |  | 88.65 |  |  |  | 0.99 |  | 2.46 | [8 empty] | 9.84 |  |  |  |  | 1.48
2019 |  |  |  | 6092.49 |  |  | 6806 |  |  |  | 950 | [10 empty] | 74.19 |  |  |  | 74.67 | [5 empty] | 73.21 |  |  | 77.69 |  |  |  | 8.33 |  | 6.79 | [8 empty] | 18.54 |  |  |  |  | 0.49
2020 |  |  |  | 6787.87 |  |  | 7483 |  |  |  | 950 | [10 empty] | 83.89 |  |  |  | 84.60 | [5 empty] | 81.34 |  |  | 85.19 |  |  |  | 2.96 |  | 2.84 | [8 empty] | 12.56 |  |  |  |  | 0.71
2021 |  |  |  | 7227.84 |  |  | 7774 |  |  |  | 950 | [10 empty] | 87.16 |  |  |  | 87.84 | [5 empty] | 86.85 |  |  | 88.74 |  |  |  | 0.45 |  | 0.77 | [8 empty] | 11.40 |  |  |  |  | 0.68
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1981 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 611
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 986 | [14 empty] | 1436
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 301
L. |  | Human factor related | [39 empty] | 2
Z. |  | Other | [39 empty] | 11
Subtotal | [22 empty] | 986 | [14 empty] | 1737 |  |  |  | 624
Total | [22 empty] | 986 | [14 empty] | 2361
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1981 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 235
12. |  |  | Reactor I&C Systems | [34 empty] | 19
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 51
16. |  |  | Steam generation systems | [34 empty] | 213
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 13
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 6
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 49
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 610
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-April, October-December. Additional electricity generation amounted to 43367 MWh. The unit was in the intermediate outage from 2021.07.10 to 2021.08.20. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-1
2021 Operating Experience
RU-59 | [8 empty] | ROSTOV-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-09-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2001-03-30
Gross electrical power | [12 empty] | : |  |  | 1041 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2001-12-25
Reference unit power (net) | [12 empty] | : |  |  | 989 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 20 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7416.99 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.73 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.04 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.96 %
Load Factor (LF) | [18 empty] | : | 85.61 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.31 %
Operating Factor (OF) | [18 empty] | : | 87.01 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1138 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 746.79 | 689.60 |  |  |  | 763.56 |  | 721.17 | [8 empty] | 654.39 |  |  | 685.48 | [6 empty] | 716.97 |  | 703.74 |  |  |  | 351.34 |  |  | 0.00 |  |  | 620.54 | [9 empty] | 763.38 |  |  | 7416.99
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.29 | [6 empty] | 97.39 |  | 96.20 |  |  |  | 50.52 |  |  | 1.10 |  |  | 85.36 | [9 empty] | 100.00 |  |  | 85.73
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 59.14 |  |  | 1.10 |  |  | 85.36 | [9 empty] | 100.00 |  |  | 87.04
LF [%] |  |  |  |  | 101.49 | 103.76 |  |  |  | 103.77 |  | 101.28 | [8 empty] | 88.93 |  |  | 96.26 | [6 empty] | 97.44 |  | 95.64 |  |  |  | 49.34 |  |  | 0.00 |  |  | 87.15 | [9 empty] | 103.75 |  |  | 85.61
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 59.03 |  |  | 0.00 |  |  | 86.25 | [9 empty] | 100.00 |  |  | 87.01
FLR [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 40.86 |  |  | 98.90 |  |  | 14.64 | [9 empty] | 0.00 |  |  | 12.96
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.71 | [6 empty] | 2.61 |  | 3.80 |  |  |  | 8.62 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.31
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 155917.83 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.13 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.26 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.3 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.44 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.04 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.38 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.6 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2001 |  |  |  | Data not provided
2002 |  |  |  | 7176.18 |  |  | 7543 |  |  |  | 950 | [10 empty] | 84.06 |  |  |  | 85.51 | [5 empty] | 86.23 |  |  | 86.11 |  |  |  | 1.33 |  | 1.16 | [8 empty] | 13.33 |  |  |  |  | 1.45
2003 |  |  |  | 6973.93 |  |  | 7154 |  |  |  | 950 | [10 empty] | 81.33 |  |  |  | 82.56 | [5 empty] | 83.80 |  |  | 81.67 |  |  |  | 2.81 |  | 2.39 | [8 empty] | 15.05 |  |  |  |  | 1.23
2004 |  |  |  | 7439.31 |  |  | 7766 |  |  |  | 950 | [10 empty] | 87.75 |  |  |  | 87.96 | [5 empty] | 89.15 |  |  | 88.41 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 11.87 |  |  |  |  | 0.21
2005 |  |  |  | 7232.86 |  |  | 7628 |  |  |  | 950 | [10 empty] | 85.85 |  |  |  | 86.87 | [5 empty] | 86.90 |  |  | 87.07 |  |  |  | 0.60 |  | 0.52 | [8 empty] | 12.60 |  |  |  |  | 1.02
2006 |  |  |  | 7216.42 |  |  | 7386 |  |  |  | 950 | [10 empty] | 83.82 |  |  |  | 84.19 | [5 empty] | 86.71 |  |  | 84.32 |  |  |  | 0.29 |  | 3.46 | [8 empty] | 12.35 |  |  |  |  | 0.38
2007 |  |  |  | 7309.44 |  |  | 7536 |  |  |  | 950 | [10 empty] | 85.28 |  |  |  | 85.48 | [5 empty] | 87.83 |  |  | 86.03 |  |  |  | 0.55 |  | 0.47 | [8 empty] | 14.04 |  |  |  |  | 0.20
2008 |  |  |  | 7745.73 |  |  | 7799 |  |  |  | 950 | [10 empty] | 88.53 |  |  |  | 88.56 | [5 empty] | 92.82 |  |  | 88.79 |  |  |  | 1.00 |  | 0.89 | [8 empty] | 10.54 |  |  |  |  | 0.03
2009 |  |  |  | 7927.02 |  |  | 7916 |  |  |  | 950 | [10 empty] | 90.27 |  |  |  | 90.29 | [5 empty] | 95.25 |  |  | 90.37 |  |  |  | 0.52 |  | 0.47 | [8 empty] | 9.25 |  |  |  |  | 0.01
2010 |  |  |  | 7398.47 |  |  | 7828 |  |  |  | 950 | [10 empty] | 88.60 |  |  |  | 88.91 | [5 empty] | 88.90 |  |  | 89.36 |  |  |  | 2.23 |  | 2.02 | [8 empty] | 9.06 |  |  |  |  | 0.32
2011 |  |  |  | 7695.35 |  |  | 7736 |  |  |  | 950 | [10 empty] | 88.24 |  |  |  | 88.24 | [5 empty] | 92.48 |  |  | 88.32 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 11.68 |  |  |  |  | 0.00
2012 |  |  |  | 7569.03 |  |  | 7614 |  |  |  | 950 | [10 empty] | 86.42 |  |  |  | 86.51 | [5 empty] | 90.70 |  |  | 86.68 |  |  |  | 0.10 |  | 1.40 | [8 empty] | 12.09 |  |  |  |  | 0.09
2013 |  |  |  | 8557.12 |  |  | 8618 |  |  |  | 950 | [10 empty] | 98.15 |  |  |  | 98.15 | [5 empty] | 102.83 |  |  | 98.38 |  |  |  | 1.85 |  | 1.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 7227.67 |  |  | 7498 |  |  |  | 950 | [10 empty] | 85.13 |  |  |  | 85.37 | [5 empty] | 86.84 |  |  | 85.58 |  |  |  | 1.82 |  | 1.58 | [8 empty] | 13.05 |  |  |  |  | 0.25
2015 |  |  |  | 6713.50 |  |  | 6980 |  |  |  | 950 | [10 empty] | 76.83 |  |  |  | 76.83 | [5 empty] | 80.67 |  |  | 79.68 |  |  |  | 7.21 |  | 5.97 | [8 empty] | 17.21 |  |  |  |  | 0.00
2016 |  |  |  | 8833.60 |  |  | 8753 |  |  |  | 950 | [10 empty] | 99.63 |  |  |  | 99.63 | [5 empty] | 105.86 |  |  | 99.65 |  |  |  | 0.37 |  | 0.37 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7840.38 |  |  | 7825 |  |  |  | 950 | [10 empty] | 89.24 |  |  |  | 89.24 | [5 empty] | 94.21 |  |  | 89.33 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 10.76 |  |  |  |  | 0.00
2018 |  |  |  | 7609.90 |  |  | 7719 |  |  |  | 950 | [10 empty] | 87.71 |  |  |  | 87.98 | [5 empty] | 91.44 |  |  | 88.12 |  |  |  | 0.74 |  | 1.07 | [8 empty] | 10.95 |  |  |  |  | 0.27
2019 |  |  |  | 8620.25 |  |  | 8723 |  |  |  | 950 | [10 empty] | 99.49 |  |  |  | 99.52 | [5 empty] | 103.58 |  |  | 99.58 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.00 |  |  |  |  | 0.03
2020 |  |  |  | 7443.25 |  |  | 7689 |  |  |  | 950 | [10 empty] | 86.60 |  |  |  | 87.29 | [5 empty] | 89.20 |  |  | 87.53 |  |  |  | 0.96 |  | 0.85 | [8 empty] | 11.86 |  |  |  |  | 0.68
2021 |  |  |  | 7416.99 |  |  | 7622 |  |  |  | 989 | [10 empty] | 85.73 |  |  |  | 87.04 | [5 empty] | 85.61 |  |  | 87.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.96 |  |  |  |  | 1.31
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2001 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 86
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1138 | [14 empty] | 897
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 7
E. |  | Testing of plant systems or components | [39 empty] | 2
L. |  | Human factor related | [39 empty] | 3
Subtotal | [22 empty] | 1138 | [14 empty] | 904 |  |  |  | 91
Total | [22 empty] | 1138 | [14 empty] | 995
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2001 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 2
16. |  |  | Steam generation systems | [34 empty] | 34
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
33. |  |  | Circulating Water System | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 30
42. |  |  | Electrical Power Supply Systems | [34 empty] | 16
Total | [37 empty] | 91
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-April, November-December. Additional electricity generation amounted to 121343.5 MWh. The unit was in the intermediate outage from 2021.09.18 to 2021.11.05. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-2
2021 Operating Experience
RU-62 | [8 empty] | ROSTOV-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | FAEA (Federal Atomic Energy Agency)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1983-05-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2010-03-18
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2010-12-10
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 11 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 0.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7418.56 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.31 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.14 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.79 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.85 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.36 %
Load Factor (LF) | [18 empty] | : | 89.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.71 %
Operating Factor (OF) | [18 empty] | : | 85.98 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1228 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 763.30 | 685.04 |  |  |  | 767.28 |  | 727.70 | [8 empty] | 654.88 |  |  | 691.88 | [6 empty] | 653.73 |  | 17.46 |  |  |  | 287.69 |  |  | 660.90 |  |  | 741.64 | [9 empty] | 767.05 |  |  | 7418.56
EAF [%] |  |  |  |  | 100.00 | 98.96 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 92.22 |  | 2.80 |  |  |  | 41.50 |  |  | 87.52 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.14
UCF [%] |  |  |  |  | 100.00 | 98.96 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 3.42 |  |  |  | 41.50 |  |  | 87.52 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.85
LF [%] |  |  |  |  | 107.99 | 107.31 |  |  |  | 108.56 |  | 106.39 | [8 empty] | 92.65 |  |  | 101.15 | [6 empty] | 92.49 |  | 2.47 |  |  |  | 42.06 |  |  | 93.51 |  |  | 108.43 | [9 empty] | 108.52 |  |  | 89.14
OF [%] |  |  |  |  | 100.00 | 99.26 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 3.76 |  |  |  | 42.08 |  |  | 87.90 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.98
FLR [%] |  |  |  |  | 0.00 | 1.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 12.48 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.31
UCL [%] |  |  |  |  | 0.00 | 1.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 7.92 |  |  | 12.48 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.79
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 96.58 |  |  |  | 50.58 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.36
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 7.78 |  | 0.63 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.71
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 88440.61 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.95 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.91 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.77 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.25 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.98 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.89 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.33 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.51 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2010 |  |  |  | 4303.76 |  |  | 6133 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.93 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 7368.43 |  |  | 7944 |  |  |  | 950 | [10 empty] | 89.41 |  |  |  | 90.23 | [5 empty] | 88.55 |  |  | 90.70 |  |  |  | 0.63 |  | 0.58 | [8 empty] | 9.19 |  |  |  |  | 0.82
2012 |  |  |  | 7433.18 |  |  | 7781 |  |  |  | 950 | [10 empty] | 87.61 |  |  |  | 87.79 | [5 empty] | 89.08 |  |  | 88.58 |  |  |  | 1.30 |  | 1.16 | [8 empty] | 11.05 |  |  |  |  | 0.18
2013 |  |  |  | 7832.67 |  |  | 8151 |  |  |  | 950 | [10 empty] | 92.80 |  |  |  | 92.80 | [5 empty] | 94.12 |  |  | 93.05 |  |  |  | 0.55 |  | 0.51 | [8 empty] | 6.69 |  |  |  |  | 0.00
2014 |  |  |  | 7741.45 |  |  | 8018 |  |  |  | 950 | [10 empty] | 91.20 |  |  |  | 91.29 | [5 empty] | 93.01 |  |  | 91.52 |  |  |  | 0.26 |  | 0.24 | [8 empty] | 8.47 |  |  |  |  | 0.09
2015 |  |  |  | 7525.83 |  |  | 7610 |  |  |  | 950 | [10 empty] | 86.39 |  |  |  | 86.41 | [5 empty] | 90.43 |  |  | 86.87 |  |  |  | 1.26 |  | 1.11 | [8 empty] | 12.48 |  |  |  |  | 0.03
2016 |  |  |  | 7890.03 |  |  | 7974 |  |  |  | 950 | [10 empty] | 90.15 |  |  |  | 90.69 | [5 empty] | 94.55 |  |  | 90.78 |  |  |  | 1.44 |  | 1.33 | [8 empty] | 7.98 |  |  |  |  | 0.54
2017 |  |  |  | 7734.15 |  |  | 7755 |  |  |  | 950 | [10 empty] | 88.29 |  |  |  | 88.31 | [5 empty] | 92.94 |  |  | 88.53 |  |  |  | 11.64 |  | 11.63 | [8 empty] | 0.06 |  |  |  |  | 0.01
2018 |  |  |  | 6666.68 |  |  | 6845 |  |  |  | 950 | [10 empty] | 76.80 |  |  |  | 77.90 | [5 empty] | 80.11 |  |  | 78.14 |  |  |  | 12.50 |  | 11.13 | [8 empty] | 10.98 |  |  |  |  | 1.09
2019 |  |  |  | 8662.06 |  |  | 8650 |  |  |  | 950 | [10 empty] | 98.71 |  |  |  | 98.72 | [5 empty] | 104.09 |  |  | 98.74 |  |  |  | 1.28 |  | 1.28 | [8 empty] | 0.00 |  |  |  |  | 0.01
2020 |  |  |  | 7864.15 |  |  | 7982 |  |  |  | 950 | [10 empty] | 90.61 |  |  |  | 90.79 | [5 empty] | 94.24 |  |  | 90.87 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.21 |  |  |  |  | 0.18
2021 |  |  |  | 7418.56 |  |  | 7532 |  |  |  | 950 | [10 empty] | 85.14 |  |  |  | 85.85 | [5 empty] | 89.14 |  |  | 85.98 |  |  |  | 1.31 |  | 1.79 | [8 empty] | 12.36 |  |  |  |  | 0.71
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2010 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 95 | [14 empty] | 222
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1076 | [14 empty] | 636
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 52
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
Z. |  | Other | [24 empty] | 57 | [14 empty] | 5
Subtotal | [22 empty] | 1076 |  |  |  | 152 | [10 empty] | 688 |  |  |  | 227 | [11 empty] | 1
Total | [22 empty] | 1228 | [14 empty] | 916
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2010 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [19 empty] | 90 | [14 empty] | 12
31. |  |  | Turbine and auxiliaries | [34 empty] | 41
41. |  |  | Main Generator Systems | [19 empty] | 5 | [14 empty] | 93
42. |  |  | Electrical Power Supply Systems | [34 empty] | 49
Total | [22 empty] | 95 | [14 empty] | 208
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-July, September-Desember. Additional electricity generation amounted to 403196 MWh. The unit was in the overhaul outage from 2021.08.02 to 2021.09.16. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-3
2021 Operating Experience
RU-63 | [8 empty] | ROSTOV-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-09-15
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-12-27
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-09-17
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7615.55 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.97 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.16 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.89 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.67 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.45 %
Load Factor (LF) | [18 empty] | : | 91.51 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.51 %
Operating Factor (OF) | [18 empty] | : | 91.44 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 750 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 748.24 | 656.36 |  |  |  | 752.56 |  | 710.84 | [8 empty] | 609.81 |  |  | 637.87 | [6 empty] | 3.70 |  | 678.87 |  |  |  | 692.60 |  |  | 723.33 |  |  | 715.88 | [9 empty] | 685.50 |  |  | 7615.55
EAF [%] |  |  |  |  | 100.00 | 97.66 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 96.78 | [6 empty] | 0.52 |  | 97.14 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 91.68 |  |  | 90.16
UCF [%] |  |  |  |  | 100.00 | 97.66 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 0.52 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 91.68 |  |  | 90.67
LF [%] |  |  |  |  | 105.86 | 102.81 |  |  |  | 106.47 |  | 103.92 | [8 empty] | 86.28 |  |  | 93.26 | [6 empty] | 0.52 |  | 96.05 |  |  |  | 101.26 |  |  | 102.34 |  |  | 104.66 | [9 empty] | 96.99 |  |  | 91.51
OF [%] |  |  |  |  | 100.00 | 97.92 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 1.08 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.44
FLR [%] |  |  |  |  | 0.00 | 2.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 8.32 |  |  | 0.97
UCL [%] |  |  |  |  | 0.00 | 2.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 8.32 |  |  | 0.89
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 99.48 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.45
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 3.22 | [6 empty] | 0.00 |  | 2.86 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.51
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 48002.13 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.82 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.97 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.07 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.73 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.54 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.1 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.06 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 5132.22 |  |  | 7040 |  |  |  | 950 | [10 empty] | 99.65 |  |  |  | 99.65 | [5 empty] | 104.56 |  |  | 100.00 |  |  |  | 0.35 |  | 0.35 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6110.00 |  |  | 6728 |  |  |  | 950 | [10 empty] | 71.98 |  |  |  | 73.43 | [5 empty] | 73.22 |  |  | 76.59 |  |  |  | 5.40 |  | 14.24 | [8 empty] | 12.33 |  |  |  |  | 1.45
2017 |  |  |  | 6422.53 |  |  | 6888 |  |  |  | 950 | [10 empty] | 76.35 |  |  |  | 77.80 | [5 empty] | 77.18 |  |  | 78.63 |  |  |  | 3.24 |  | 2.60 | [8 empty] | 19.60 |  |  |  |  | 1.45
2018 |  |  |  | 7709.57 |  |  | 7962 |  |  |  | 950 | [10 empty] | 90.24 |  |  |  | 90.77 | [5 empty] | 92.64 |  |  | 90.89 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 8.95 |  |  |  |  | 0.53
2019 |  |  |  | 7360.63 |  |  | 7848 |  |  |  | 950 | [10 empty] | 87.53 |  |  |  | 89.97 | [5 empty] | 88.45 |  |  | 89.59 |  |  |  | 0.71 |  | 0.64 | [8 empty] | 9.39 |  |  |  |  | 2.44
2020 |  |  |  | 7651.88 |  |  | 8081 |  |  |  | 950 | [10 empty] | 89.89 |  |  |  | 90.36 | [5 empty] | 91.70 |  |  | 92.00 |  |  |  | 1.38 |  | 1.26 | [8 empty] | 8.38 |  |  |  |  | 0.47
2021 |  |  |  | 7615.55 |  |  | 8010 |  |  |  | 950 | [10 empty] | 90.16 |  |  |  | 90.67 | [5 empty] | 91.51 |  |  | 91.44 |  |  |  | 0.97 |  | 0.89 | [8 empty] | 8.45 |  |  |  |  | 0.51
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2015 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 14 | [14 empty] | 202
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 736 | [14 empty] | 646
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 16
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 267
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
Subtotal | [22 empty] | 736 |  |  |  | 14 | [10 empty] | 929 |  |  |  | 202 | [11 empty] | 11
Total | [22 empty] | 750 | [14 empty] | 1142
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2015 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 29
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [19 empty] | 14 | [14 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 15
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
33. |  |  | Circulating Water System | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 129
Total | [22 empty] | 14 | [14 empty] | 181
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-June, August-December. Additional electricity generation amounted to 312156 MWh. The unit was in the intermediate outage from 2021.07.01 to 2021.07.31. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-4
2021 Operating Experience
RU-64 | [8 empty] | ROSTOV-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-06-16
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-02-02
Gross electrical power | [12 empty] | : |  |  | 1030 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-09-28
Reference unit power (net) | [12 empty] | : |  |  | 979 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7521.96 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.91 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.05 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.82 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.52 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.66 %
Load Factor (LF) | [18 empty] | : | 87.71 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.47 %
Operating Factor (OF) | [18 empty] | : | 89.75 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 898 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 702.50 | 0.00 |  |  |  | 592.94 |  | 716.57 | [8 empty] | 662.80 |  |  | 661.75 | [6 empty] | 657.59 |  | 615.23 |  |  |  | 701.40 |  |  | 737.00 |  |  | 722.14 | [9 empty] | 752.05 |  |  | 7521.96
EAF [%] |  |  |  |  | 95.08 | 0.02 |  |  |  | 79.61 |  | 100.00 | [8 empty] | 99.82 |  |  | 96.97 | [6 empty] | 92.33 |  | 86.02 |  |  |  | 99.69 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.05
UCF [%] |  |  |  |  | 96.98 | 0.02 |  |  |  | 79.61 |  | 100.00 | [8 empty] | 99.82 |  |  | 100.00 | [6 empty] | 98.24 |  | 92.27 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.52
LF [%] |  |  |  |  | 96.45 | 0.00 |  |  |  | 81.41 |  | 101.66 | [8 empty] | 91.00 |  |  | 93.88 | [6 empty] | 90.28 |  | 84.47 |  |  |  | 99.51 |  |  | 101.18 |  |  | 102.45 | [9 empty] | 103.25 |  |  | 87.71
OF [%] |  |  |  |  | 97.18 | 0.00 |  |  |  | 80.38 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 92.07 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.75
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.18 |  |  | 0.00 | [6 empty] | 1.76 |  | 7.73 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.91
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.18 |  |  | 0.00 | [6 empty] | 1.76 |  | 7.73 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.82
PUF [%] |  |  |  |  | 3.02 | 99.98 |  |  |  | 20.39 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.66
XUF [%] |  |  |  |  | 1.89 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 3.03 | [6 empty] | 5.92 |  | 6.25 |  |  |  | 0.31 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.47
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 28634.16 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.21 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.73 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.13 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.49 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 90.47 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.64 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 92.57 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 5681.92 |  |  | 6556 |  |  |  | 950 | [10 empty] | 99.97 |  |  |  | 99.99 | [5 empty] | 103.76 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.00 |  |  |  |  | 0.01
2019 |  |  |  | 7430.57 |  |  | 7751 |  |  |  | 979 | [10 empty] | 87.01 |  |  |  | 88.29 | [5 empty] | 86.64 |  |  | 88.48 |  |  |  | 0.40 |  | 0.35 | [8 empty] | 11.36 |  |  |  |  | 1.28
2020 |  |  |  | 8066.50 |  |  | 8573 |  |  |  | 979 | [10 empty] | 94.86 |  |  |  | 97.45 | [5 empty] | 93.80 |  |  | 97.60 |  |  |  | 2.50 |  | 2.50 | [8 empty] | 0.05 |  |  |  |  | 2.58
2021 |  |  |  | 7521.96 |  |  | 7862 |  |  |  | 979 | [10 empty] | 88.05 |  |  |  | 89.52 | [5 empty] | 87.71 |  |  | 89.75 |  |  |  | 0.91 |  | 0.82 | [8 empty] | 9.66 |  |  |  |  | 1.47
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2018 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 62 | [14 empty] | 93
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 839 | [14 empty] | 613
L. |  | Human factor related | [39 empty] | 3
Subtotal | [22 empty] | 839 |  |  |  | 62 | [10 empty] | 613 |  |  |  | 96
Total | [22 empty] | 901 | [14 empty] | 709
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2018 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [19 empty] | 62 | [14 empty] | 30
32. |  |  | Feedwater and Main Steam System | [34 empty] | 63
33. |  |  | Circulating Water System | [34 empty] | 3
Total | [22 empty] | 62 | [14 empty] | 96
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January, March, April, June, September-December. Additional electricity generation amounted to 126869 MWh. The unit was in the intermediate outage from 2021.01.31 to 2021.03.07. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## SMOLENSK-1
2021 Operating Experience
RU-23 | [8 empty] | SMOLENSK-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-10-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-12-09
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-09-30
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 175 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | PH / DH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7267.29 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.27 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.94 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.17 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.89 %
Load Factor (LF) | [18 empty] | : | 89.69 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.66 %
Operating Factor (OF) | [18 empty] | : | 88.31 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1024 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 73.06 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 718.84 | 658.92 |  |  |  | 525.08 |  | 699.63 | [8 empty] | 705.50 |  |  | 654.59 | [6 empty] | 657.35 |  | 412.59 |  |  |  | 112.48 |  |  | 730.45 |  |  | 709.74 | [9 empty] | 682.13 |  |  | 7267.29
EAF [%] |  |  |  |  | 98.83 | 100.00 |  |  |  | 73.31 |  | 100.00 | [8 empty] | 99.92 |  |  | 98.20 | [6 empty] | 95.76 |  | 60.91 |  |  |  | 17.96 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 93.66 |  |  | 86.52
UCF [%] |  |  |  |  | 98.83 | 100.00 |  |  |  | 73.31 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.56 |  | 63.00 |  |  |  | 17.96 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 93.66 |  |  | 87.17
LF [%] |  |  |  |  | 104.45 | 106.00 |  |  |  | 76.30 |  | 105.05 | [8 empty] | 102.51 |  |  | 98.29 | [6 empty] | 95.52 |  | 59.95 |  |  |  | 16.89 |  |  | 106.14 |  |  | 106.57 | [9 empty] | 99.12 |  |  | 89.69
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 75.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 64.65 |  |  |  | 20.14 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.31
FLR [%] |  |  |  |  | 1.17 | 0.00 |  |  |  | 26.69 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.44 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 6.34 |  |  | 3.27
UCL [%] |  |  |  |  | 1.17 | 0.00 |  |  |  | 26.69 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.44 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 6.34 |  |  | 2.94
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 37.00 |  |  |  | 82.04 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.89
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.08 |  |  | 1.80 | [6 empty] | 3.81 |  | 2.09 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.66
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 234839.56 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.44 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.2 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.02 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.94 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 22.04 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.83 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.73 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.43 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 4744.20 |  |  | 7223 |  |  |  | 925 | [10 empty] | 99.64 |  |  |  | 99.64 | [5 empty] | 100.76 |  |  | 99.86 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 6921.35 |  |  | 7830 |  |  |  | 925 | [10 empty] | 84.23 |  |  |  | 84.23 | [5 empty] | 85.18 |  |  | 89.14 |  |  |  | 2.64 |  | 2.28 | [8 empty] | 13.49 |  |  |  |  | 0.00
1985 |  |  |  | 5850.24 |  |  | 6806 |  |  |  | 925 | [10 empty] | 72.40 |  |  |  | 74.87 | [5 empty] | 72.20 |  |  | 77.69 |  |  |  | 1.52 |  | 1.15 | [8 empty] | 23.97 |  |  |  |  | 2.47
1986 |  |  |  | 3039.75 |  |  | 3472 |  |  |  | 925 | [10 empty] | 37.79 |  |  |  | 37.79 | [5 empty] | 37.51 |  |  | 39.63 |  |  |  | 0.05 |  | 0.02 | [8 empty] | 62.20 |  |  |  |  | 0.00
1987 |  |  |  | 7445.76 |  |  | 7620 |  |  |  | 1000 | [10 empty] | 86.72 |  |  |  | 86.72 | [5 empty] | 85.00 |  |  | 86.99 |  |  |  | 2.08 |  | 1.84 | [8 empty] | 11.44 |  |  |  |  | 0.00
1988 |  |  |  | 6695.59 |  |  | 7288 |  |  |  | 925 | [10 empty] | 81.89 |  |  |  | 81.89 | [5 empty] | 82.41 |  |  | 82.97 |  |  |  | 0.44 |  | 0.36 | [8 empty] | 17.75 |  |  |  |  | 0.00
1989 |  |  |  | 6506.46 |  |  | 7177 |  |  |  | 925 | [10 empty] | 79.32 |  |  |  | 79.70 | [5 empty] | 80.30 |  |  | 81.93 |  |  |  | 6.44 |  | 5.49 | [8 empty] | 14.82 |  |  |  |  | 0.38
1990 |  |  |  | 6227.84 |  |  | 6851 |  |  |  | 925 | [10 empty] | 76.14 |  |  |  | 76.59 | [5 empty] | 76.86 |  |  | 78.21 |  |  |  | 3.90 |  | 3.11 | [8 empty] | 20.30 |  |  |  |  | 0.45
1991 |  |  |  | 6693.92 |  |  | 7252 |  |  |  | 925 | [10 empty] | 81.29 |  |  |  | 81.29 | [5 empty] | 82.61 |  |  | 82.79 |  |  |  | 3.68 |  | 3.11 | [8 empty] | 15.60 |  |  |  |  | 0.00
1992 |  |  |  | 6849.38 |  |  | 7563 |  |  |  | 925 | [10 empty] | 83.69 |  |  |  | 83.69 | [5 empty] | 84.31 |  |  | 86.11 |  |  |  | 2.55 |  | 2.19 | [8 empty] | 14.12 |  |  |  |  | 0.00
1993 |  |  |  | 6290.56 |  |  | 6993 |  |  |  | 925 | [10 empty] | 78.01 |  |  |  | 78.41 | [5 empty] | 77.63 |  |  | 79.83 |  |  |  | 0.38 |  | 0.30 | [8 empty] | 21.29 |  |  |  |  | 0.40
1994 |  |  |  | 4217.84 |  |  | 6286 |  |  |  | 925 | [10 empty] | 57.81 |  |  |  | 71.04 | [5 empty] | 52.05 |  |  | 71.76 |  |  |  | 0.20 |  | 0.14 | [8 empty] | 28.82 |  |  |  |  | 13.23
1995 |  |  |  | 5002.47 |  |  | 6390 |  |  |  | 925 | [10 empty] | 62.97 |  |  |  | 77.35 | [5 empty] | 61.74 |  |  | 72.95 |  |  |  | 1.91 |  | 1.50 | [8 empty] | 21.15 |  |  |  |  | 14.38
1996 |  |  |  | 5666.43 |  |  | 6604 |  |  |  | 925 | [10 empty] | 71.56 |  |  |  | 71.73 | [5 empty] | 69.74 |  |  | 75.18 |  |  |  | 1.05 |  | 0.76 | [8 empty] | 27.51 |  |  |  |  | 0.17
1997 |  |  |  | 4674.51 |  |  | 5366 |  |  |  | 925 | [10 empty] | 57.82 |  |  |  | 59.14 | [5 empty] | 57.69 |  |  | 61.26 |  |  |  | 2.88 |  | 1.75 | [8 empty] | 39.11 |  |  |  |  | 1.32
1998 |  |  |  | 3554.08 |  |  | 5411 |  |  |  | 925 | [10 empty] | 45.04 |  |  |  | 58.85 | [5 empty] | 43.86 |  |  | 61.77 |  |  |  | 3.49 |  | 2.13 | [8 empty] | 39.02 |  |  |  |  | 13.81
1999 |  |  |  | 6478.89 |  |  | 7417 |  |  |  | 925 | [10 empty] | 80.06 |  |  |  | 83.51 | [5 empty] | 79.96 |  |  | 84.67 |  |  |  | 3.29 |  | 2.84 | [8 empty] | 13.65 |  |  |  |  | 3.45
2000 |  |  |  | 5228.48 |  |  | 5738 |  |  |  | 925 | [10 empty] | 63.83 |  |  |  | 64.36 | [5 empty] | 64.35 |  |  | 65.32 |  |  |  | 0.06 |  | 0.04 | [8 empty] | 35.60 |  |  |  |  | 0.53
2001 |  |  |  | 5165.12 |  |  | 5940 |  |  |  | 925 | [10 empty] | 63.24 |  |  |  | 67.43 | [5 empty] | 63.74 |  |  | 67.81 |  |  |  | 2.61 |  | 1.81 | [8 empty] | 30.76 |  |  |  |  | 4.19
2002 |  |  |  | 6866.73 |  |  | 7587 |  |  |  | 925 | [10 empty] | 83.69 |  |  |  | 85.10 | [5 empty] | 84.74 |  |  | 86.61 |  |  |  | 2.59 |  | 2.26 | [8 empty] | 12.64 |  |  |  |  | 1.41
2003 |  |  |  | 6711.76 |  |  | 7533 |  |  |  | 925 | [10 empty] | 82.90 |  |  |  | 84.38 | [5 empty] | 82.83 |  |  | 85.99 |  |  |  | 3.18 |  | 2.77 | [8 empty] | 12.85 |  |  |  |  | 1.48
2004 |  |  |  | 2337.12 |  |  | 2592 |  |  |  | 925 | [10 empty] | 28.50 |  |  |  | 29.09 | [5 empty] | 28.76 |  |  | 29.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 70.91 |  |  |  |  | 0.59
2005 |  |  |  | 7354.10 |  |  | 8414 |  |  |  | 925 | [10 empty] | 90.63 |  |  |  | 94.66 | [5 empty] | 90.75 |  |  | 96.04 |  |  |  | 0.80 |  | 0.76 | [8 empty] | 4.58 |  |  |  |  | 4.03
2006 |  |  |  | 5417.08 |  |  | 6021 |  |  |  | 925 | [10 empty] | 67.09 |  |  |  | 67.09 | [5 empty] | 66.85 |  |  | 68.73 |  |  |  | 1.33 |  | 3.79 | [8 empty] | 29.12 |  |  |  |  | 0.00
2007 |  |  |  | 6569.65 |  |  | 7138 |  |  |  | 925 | [10 empty] | 80.25 |  |  |  | 80.82 | [5 empty] | 81.08 |  |  | 81.48 |  |  |  | 0.20 |  | 0.16 | [8 empty] | 19.02 |  |  |  |  | 0.57
2008 |  |  |  | 7794.93 |  |  | 8430 |  |  |  | 925 | [10 empty] | 94.94 |  |  |  | 95.19 | [5 empty] | 95.94 |  |  | 95.97 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 4.79 |  |  |  |  | 0.25
2009 |  |  |  | 6122.29 |  |  | 6974 |  |  |  | 925 | [10 empty] | 77.32 |  |  |  | 77.60 | [5 empty] | 75.56 |  |  | 79.61 |  |  |  | 12.28 |  | 10.86 | [8 empty] | 11.54 |  |  |  |  | 0.28
2010 |  |  |  | 4896.26 |  |  | 5424 |  |  |  | 925 | [10 empty] | 61.10 |  |  |  | 61.75 | [5 empty] | 60.43 |  |  | 61.92 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 38.24 |  |  |  |  | 0.65
2011 |  |  |  | 5444.54 |  |  | 5899 |  |  |  | 925 | [10 empty] | 65.97 |  |  |  | 66.24 | [5 empty] | 67.20 |  |  | 67.35 |  |  |  | 0.05 |  | 0.03 | [8 empty] | 33.73 |  |  |  |  | 0.27
2012 |  |  |  | 6306.76 |  |  | 6741 |  |  |  | 925 | [10 empty] | 75.88 |  |  |  | 76.32 | [5 empty] | 77.62 |  |  | 76.74 |  |  |  | 1.76 |  | 1.37 | [8 empty] | 22.31 |  |  |  |  | 0.45
2013 |  |  |  | 7775.27 |  |  | 8267 |  |  |  | 925 | [10 empty] | 93.47 |  |  |  | 93.80 | [5 empty] | 95.96 |  |  | 94.37 |  |  |  | 3.63 |  | 3.53 | [8 empty] | 2.67 |  |  |  |  | 0.34
2014 |  |  |  | 7330.99 |  |  | 7691 |  |  |  | 925 | [10 empty] | 87.06 |  |  |  | 87.27 | [5 empty] | 90.46 |  |  | 87.79 |  |  |  | 0.92 |  | 0.83 | [8 empty] | 11.89 |  |  |  |  | 0.21
2015 |  |  |  | 7050.99 |  |  | 7394 |  |  |  | 925 | [10 empty] | 83.24 |  |  |  | 83.37 | [5 empty] | 87.02 |  |  | 84.41 |  |  |  | 2.18 |  | 1.86 | [8 empty] | 14.77 |  |  |  |  | 0.14
2016 |  |  |  | 6746.07 |  |  | 7003 |  |  |  | 925 | [10 empty] | 79.38 |  |  |  | 79.45 | [5 empty] | 83.03 |  |  | 79.72 |  |  |  | 0.15 |  | 0.12 | [8 empty] | 20.42 |  |  |  |  | 0.07
2017 |  |  |  | 6710.68 |  |  | 7720 |  |  |  | 925 | [10 empty] | 80.35 |  |  |  | 80.44 | [5 empty] | 82.82 |  |  | 88.13 |  |  |  | 9.47 |  | 8.41 | [8 empty] | 11.15 |  |  |  |  | 0.08
2018 |  |  |  | 6788.06 |  |  | 7256 |  |  |  | 925 | [10 empty] | 80.82 |  |  |  | 80.92 | [5 empty] | 83.77 |  |  | 82.83 |  |  |  | 4.80 |  | 4.08 | [8 empty] | 15.00 |  |  |  |  | 0.10
2019 |  |  |  | 6373.86 |  |  | 6673 |  |  |  | 925 | [10 empty] | 75.51 |  |  |  | 75.51 | [5 empty] | 78.66 |  |  | 76.18 |  |  |  | 0.54 |  | 2.32 | [8 empty] | 22.17 |  |  |  |  | 0.00
2020 |  |  |  | 6155.00 |  |  | 6930 |  |  |  | 925 | [10 empty] | 73.88 |  |  |  | 73.96 | [5 empty] | 75.75 |  |  | 78.89 |  |  |  | 0.51 |  | 0.38 | [8 empty] | 25.66 |  |  |  |  | 0.08
2021 |  |  |  | 7267.29 |  |  | 7736 |  |  |  | 925 | [10 empty] | 86.52 |  |  |  | 87.17 | [5 empty] | 89.69 |  |  | 88.31 |  |  |  | 3.27 |  | 2.94 | [8 empty] | 9.89 |  |  |  |  | 0.66
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1983 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 201 | [14 empty] | 101
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 860 | [14 empty] | 1173
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 279
E. |  | Testing of plant systems or components | [35 empty] | 20
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 269
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 12
Subtotal | [22 empty] | 860 |  |  |  | 201 | [10 empty] | 1741 |  |  |  | 102 | [11 empty] | 16
Total | [22 empty] | 1061 | [14 empty] | 1859
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1983 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 21
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 23
16. |  |  | Steam generation systems | [34 empty] | 0
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 0
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [19 empty] | 201 | [14 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [22 empty] | 201 | [14 empty] | 101
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-June, September-December. Additional electricity generation amounted to 252705 MWh. The unit was in the routine maintenance outage from 2021.08.21 to 2021.09.26. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## SMOLENSK-2
2021 Operating Experience
RU-24 | [8 empty] | SMOLENSK-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-06-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-05-31
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-07-02
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 175 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | PH / DH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 6939.32 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.39 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.12 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.33 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.8 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.87 %
Load Factor (LF) | [18 empty] | : | 85.64 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.68 %
Operating Factor (OF) | [18 empty] | : | 84.98 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1316 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 59.23 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 691.29 | 646.44 |  |  |  | 723.58 |  | 189.33 | [8 empty] | 0.00 |  |  | 545.05 | [6 empty] | 663.07 |  | 667.54 |  |  |  | 679.13 |  |  | 707.80 |  |  | 698.87 | [9 empty] | 727.22 |  |  | 6939.32
EAF [%] |  |  |  |  | 96.75 | 100.00 |  |  |  | 100.00 |  | 28.22 | [8 empty] | 0.00 |  |  | 80.79 | [6 empty] | 96.11 |  | 96.75 |  |  |  | 99.97 |  |  | 99.69 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.12
UCF [%] |  |  |  |  | 96.75 | 100.00 |  |  |  | 100.00 |  | 28.22 | [8 empty] | 0.00 |  |  | 81.97 | [6 empty] | 100.00 |  | 99.68 |  |  |  | 100.00 |  |  | 99.69 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.80
LF [%] |  |  |  |  | 100.45 | 104.00 |  |  |  | 105.14 |  | 28.43 | [8 empty] | 0.00 |  |  | 81.84 | [6 empty] | 96.35 |  | 97.00 |  |  |  | 101.97 |  |  | 102.85 |  |  | 104.93 | [9 empty] | 105.67 |  |  | 85.64
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 30.28 | [8 empty] | 0.00 |  |  | 90.28 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.98
FLR [%] |  |  |  |  | 3.25 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.32 |  |  |  | 0.00 |  |  | 0.31 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.39
UCL [%] |  |  |  |  | 3.25 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.32 |  |  |  | 0.00 |  |  | 0.31 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.33
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 71.78 | [8 empty] | 100.00 |  |  | 18.03 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.87
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.18 | [6 empty] | 3.89 |  | 2.93 |  |  |  | 0.03 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.68
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 226917.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.81 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.94 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.28 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.77 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.95 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.84 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 3623.94 |  |  | 4593 |  |  |  | 925 | [10 empty] | 81.32 |  |  |  | 90.61 | [5 empty] | 80.97 |  |  | 91.89 |  |  |  | 6.31 |  | 6.10 | [8 empty] | 3.29 |  |  |  |  | 9.28
1986 |  |  |  | 6667.30 |  |  | 7442 |  |  |  | 925 | [10 empty] | 82.57 |  |  |  | 82.57 | [5 empty] | 82.28 |  |  | 84.95 |  |  |  | 1.56 |  | 1.31 | [8 empty] | 16.12 |  |  |  |  | 0.00
1987 |  |  |  | 6364.93 |  |  | 6707 |  |  |  | 1000 | [10 empty] | 74.52 |  |  |  | 74.52 | [5 empty] | 72.66 |  |  | 76.56 |  |  |  | 4.46 |  | 3.48 | [8 empty] | 22.01 |  |  |  |  | 0.00
1988 |  |  |  | 6757.16 |  |  | 7594 |  |  |  | 925 | [10 empty] | 83.49 |  |  |  | 83.55 | [5 empty] | 83.16 |  |  | 86.45 |  |  |  | 1.83 |  | 1.56 | [8 empty] | 14.89 |  |  |  |  | 0.06
1989 |  |  |  | 6627.33 |  |  | 7336 |  |  |  | 925 | [10 empty] | 81.50 |  |  |  | 81.85 | [5 empty] | 81.79 |  |  | 83.74 |  |  |  | 2.69 |  | 2.26 | [8 empty] | 15.88 |  |  |  |  | 0.36
1990 |  |  |  | 6710.59 |  |  | 7453 |  |  |  | 925 | [10 empty] | 82.52 |  |  |  | 82.97 | [5 empty] | 82.82 |  |  | 85.08 |  |  |  | 5.48 |  | 4.81 | [8 empty] | 12.22 |  |  |  |  | 0.45
1991 |  |  |  | 5796.72 |  |  | 6495 |  |  |  | 925 | [10 empty] | 71.36 |  |  |  | 71.36 | [5 empty] | 71.54 |  |  | 74.14 |  |  |  | 3.36 |  | 2.48 | [8 empty] | 26.16 |  |  |  |  | 0.00
1992 |  |  |  | 6731.61 |  |  | 7472 |  |  |  | 925 | [10 empty] | 82.63 |  |  |  | 83.90 | [5 empty] | 82.86 |  |  | 85.07 |  |  |  | 1.14 |  | 0.96 | [8 empty] | 15.13 |  |  |  |  | 1.28
1993 |  |  |  | 6634.11 |  |  | 7492 |  |  |  | 925 | [10 empty] | 82.69 |  |  |  | 84.90 | [5 empty] | 81.87 |  |  | 85.53 |  |  |  | 0.29 |  | 0.25 | [8 empty] | 14.86 |  |  |  |  | 2.21
1994 |  |  |  | 5259.83 |  |  | 7044 |  |  |  | 925 | [10 empty] | 66.56 |  |  |  | 80.25 | [5 empty] | 64.91 |  |  | 80.41 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 19.73 |  |  |  |  | 13.69
1995 |  |  |  | 5337.40 |  |  | 6738 |  |  |  | 925 | [10 empty] | 66.84 |  |  |  | 80.32 | [5 empty] | 65.87 |  |  | 76.92 |  |  |  | 0.26 |  | 0.21 | [8 empty] | 19.47 |  |  |  |  | 13.49
1996 |  |  |  | 6127.71 |  |  | 7010 |  |  |  | 925 | [10 empty] | 77.82 |  |  |  | 79.09 | [5 empty] | 75.42 |  |  | 79.80 |  |  |  | 0.89 |  | 0.71 | [8 empty] | 20.20 |  |  |  |  | 1.27
1997 |  |  |  | 4991.02 |  |  | 5642 |  |  |  | 925 | [10 empty] | 61.57 |  |  |  | 61.70 | [5 empty] | 61.59 |  |  | 64.41 |  |  |  | 4.41 |  | 2.84 | [8 empty] | 35.46 |  |  |  |  | 0.13
1998 |  |  |  | 5297.02 |  |  | 6576 |  |  |  | 925 | [10 empty] | 65.58 |  |  |  | 73.88 | [5 empty] | 65.37 |  |  | 75.07 |  |  |  | 1.37 |  | 1.03 | [8 empty] | 25.09 |  |  |  |  | 8.30
1999 |  |  |  | 5362.50 |  |  | 6090 |  |  |  | 925 | [10 empty] | 66.03 |  |  |  | 69.14 | [5 empty] | 66.18 |  |  | 69.52 |  |  |  | 0.12 |  | 0.09 | [8 empty] | 30.78 |  |  |  |  | 3.11
2000 |  |  |  | 6566.15 |  |  | 7108 |  |  |  | 925 | [10 empty] | 80.10 |  |  |  | 80.54 | [5 empty] | 80.81 |  |  | 80.92 |  |  |  | 3.91 |  | 3.28 | [8 empty] | 16.19 |  |  |  |  | 0.44
2001 |  |  |  | 6457.64 |  |  | 7537 |  |  |  | 925 | [10 empty] | 78.96 |  |  |  | 81.02 | [5 empty] | 79.69 |  |  | 86.04 |  |  |  | 6.08 |  | 5.25 | [8 empty] | 13.73 |  |  |  |  | 2.06
2002 |  |  |  | 3431.09 |  |  | 3890 |  |  |  | 925 | [10 empty] | 41.69 |  |  |  | 43.60 | [5 empty] | 42.34 |  |  | 44.41 |  |  |  | 1.66 |  | 0.74 | [8 empty] | 55.66 |  |  |  |  | 1.91
2003 |  |  |  | 6438.59 |  |  | 7734 |  |  |  | 925 | [10 empty] | 79.13 |  |  |  | 81.42 | [5 empty] | 79.46 |  |  | 88.29 |  |  |  | 8.45 |  | 7.52 | [8 empty] | 11.06 |  |  |  |  | 2.29
2004 |  |  |  | 7480.14 |  |  | 8312 |  |  |  | 925 | [10 empty] | 90.85 |  |  |  | 93.66 | [5 empty] | 92.06 |  |  | 94.63 |  |  |  | 0.62 |  | 0.59 | [8 empty] | 5.75 |  |  |  |  | 2.80
2005 |  |  |  | 3053.40 |  |  | 3734 |  |  |  | 925 | [10 empty] | 37.72 |  |  |  | 41.71 | [5 empty] | 37.68 |  |  | 42.63 |  |  |  | 0.42 |  | 0.17 | [8 empty] | 58.11 |  |  |  |  | 4.00
2006 |  |  |  | 7623.87 |  |  | 8306 |  |  |  | 925 | [10 empty] | 93.15 |  |  |  | 93.15 | [5 empty] | 94.09 |  |  | 94.82 |  |  |  | 0.16 |  | 1.27 | [8 empty] | 5.58 |  |  |  |  | 0.00
2007 |  |  |  | 4096.43 |  |  | 4878 |  |  |  | 925 | [10 empty] | 49.68 |  |  |  | 50.76 | [5 empty] | 50.55 |  |  | 55.68 |  |  |  | 2.50 |  | 1.30 | [8 empty] | 47.94 |  |  |  |  | 1.08
2008 |  |  |  | 6718.76 |  |  | 7823 |  |  |  | 925 | [10 empty] | 83.20 |  |  |  | 83.66 | [5 empty] | 82.69 |  |  | 89.06 |  |  |  | 1.71 |  | 1.46 | [8 empty] | 14.89 |  |  |  |  | 0.46
2009 |  |  |  | 7668.41 |  |  | 8279 |  |  |  | 925 | [10 empty] | 93.84 |  |  |  | 94.10 | [5 empty] | 94.64 |  |  | 94.51 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 5.82 |  |  |  |  | 0.26
2010 |  |  |  | 6651.23 |  |  | 7626 |  |  |  | 925 | [10 empty] | 82.04 |  |  |  | 82.31 | [5 empty] | 82.08 |  |  | 87.05 |  |  |  | 0.56 |  | 0.46 | [8 empty] | 17.23 |  |  |  |  | 0.27
2011 |  |  |  | 7328.17 |  |  | 8314 |  |  |  | 925 | [10 empty] | 89.65 |  |  |  | 90.28 | [5 empty] | 90.45 |  |  | 94.92 |  |  |  | 3.58 |  | 3.36 | [8 empty] | 6.36 |  |  |  |  | 0.63
2012 |  |  |  | 6802.21 |  |  | 7767 |  |  |  | 925 | [10 empty] | 85.94 |  |  |  | 86.34 | [5 empty] | 83.72 |  |  | 88.42 |  |  |  | 3.24 |  | 2.89 | [8 empty] | 10.76 |  |  |  |  | 0.41
2013 |  |  |  | 2630.28 |  |  | 3045 |  |  |  | 925 | [10 empty] | 32.61 |  |  |  | 32.62 | [5 empty] | 32.46 |  |  | 34.76 |  |  |  | 5.82 |  | 2.02 | [8 empty] | 65.36 |  |  |  |  | 0.01
2014 |  |  |  | 7821.17 |  |  | 8524 |  |  |  | 925 | [10 empty] | 94.28 |  |  |  | 94.57 | [5 empty] | 96.51 |  |  | 97.29 |  |  |  | 1.89 |  | 1.82 | [8 empty] | 3.61 |  |  |  |  | 0.29
2015 |  |  |  | 7404.36 |  |  | 7809 |  |  |  | 925 | [10 empty] | 87.61 |  |  |  | 87.79 | [5 empty] | 91.38 |  |  | 89.14 |  |  |  | 1.26 |  | 1.12 | [8 empty] | 11.09 |  |  |  |  | 0.17
2016 |  |  |  | 6910.57 |  |  | 7360 |  |  |  | 925 | [10 empty] | 82.20 |  |  |  | 82.32 | [5 empty] | 85.05 |  |  | 83.79 |  |  |  | 11.12 |  | 10.30 | [8 empty] | 7.39 |  |  |  |  | 0.12
2017 |  |  |  | 6307.00 |  |  | 6734 |  |  |  | 925 | [10 empty] | 74.22 |  |  |  | 74.29 | [5 empty] | 77.84 |  |  | 76.87 |  |  |  | 5.42 |  | 4.26 | [8 empty] | 21.45 |  |  |  |  | 0.07
2018 |  |  |  | 7352.87 |  |  | 7772 |  |  |  | 925 | [10 empty] | 87.37 |  |  |  | 87.42 | [5 empty] | 90.74 |  |  | 88.72 |  |  |  | 3.77 |  | 3.43 | [8 empty] | 9.16 |  |  |  |  | 0.05
2019 |  |  |  | 5918.57 |  |  | 6573 |  |  |  | 925 | [10 empty] | 70.29 |  |  |  | 70.31 | [5 empty] | 73.04 |  |  | 75.03 |  |  |  | 7.33 |  | 5.56 | [8 empty] | 24.13 |  |  |  |  | 0.03
2020 |  |  |  | 7313.92 |  |  | 7838 |  |  |  | 925 | [10 empty] | 87.74 |  |  |  | 87.86 | [5 empty] | 90.02 |  |  | 89.23 |  |  |  | 0.86 |  | 0.76 | [8 empty] | 11.38 |  |  |  |  | 0.11
2021 |  |  |  | 6939.32 |  |  | 7444 |  |  |  | 925 | [10 empty] | 83.12 |  |  |  | 83.80 | [5 empty] | 85.64 |  |  | 84.98 |  |  |  | 0.39 |  | 0.33 | [8 empty] | 15.87 |  |  |  |  | 0.68
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1985 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 84
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1317 | [14 empty] | 1020
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 264
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 132
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 242
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 10
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 1317 | [14 empty] | 1658 |  |  |  | 88 | [11 empty] | 21
Total | [22 empty] | 1317 | [14 empty] | 1767
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1985 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 23
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 5
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 14
Total | [37 empty] | 87
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-April, June-July, September-December. Additional electricity generation amounted to 168909 MWh. The unit was in the routine maintenance outage from 2021.04.10 to 2021.06.08. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## SMOLENSK-3
2021 Operating Experience
RU-67 | [8 empty] | SMOLENSK-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-05-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-01-17
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-10-12
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 175 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | PH / DH
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 7044.34 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.94 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.13 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.85 %
Load Factor (LF) | [18 empty] | : | 86.93 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.19 %
Operating Factor (OF) | [18 empty] | : | 84.68 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1342 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 41.6 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 11.49 | 22.35 |  |  |  | 714.89 |  | 703.21 | [8 empty] | 724.80 |  |  | 669.09 | [6 empty] | 675.10 |  | 681.34 |  |  |  | 685.98 |  |  | 723.14 |  |  | 702.87 | [9 empty] | 730.08 |  |  | 7044.34
EAF [%] |  |  |  |  | 1.67 | 3.60 |  |  |  | 98.77 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.63 | [6 empty] | 98.61 |  | 99.34 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.94
UCF [%] |  |  |  |  | 1.67 | 3.60 |  |  |  | 98.77 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.82 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.13
LF [%] |  |  |  |  | 1.67 | 3.60 |  |  |  | 103.88 |  | 105.59 | [8 empty] | 105.32 |  |  | 100.46 | [6 empty] | 98.10 |  | 99.00 |  |  |  | 103.00 |  |  | 105.08 |  |  | 105.54 | [9 empty] | 106.09 |  |  | 86.93
OF [%] |  |  |  |  | 3.09 | 7.59 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.68
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.18 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.18 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
PUF [%] |  |  |  |  | 98.33 | 96.40 |  |  |  | 1.23 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.85
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.37 | [6 empty] | 1.39 |  | 0.48 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.19
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 206221.73 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.98 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.65 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.29 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.56 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.38 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 4570.76 |  |  | 6767 |  |  |  | 925 | [10 empty] | 99.06 |  |  |  | 99.06 | [5 empty] | 101.20 |  |  | 100.00 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.32 |  |  |  |  | 0.00
1991 |  |  |  | 6561.74 |  |  | 7338 |  |  |  | 925 | [10 empty] | 80.87 |  |  |  | 80.87 | [5 empty] | 80.98 |  |  | 83.77 |  |  |  | 3.91 |  | 3.29 | [8 empty] | 15.84 |  |  |  |  | 0.00
1992 |  |  |  | 6866.56 |  |  | 7515 |  |  |  | 925 | [10 empty] | 83.90 |  |  |  | 83.92 | [5 empty] | 84.52 |  |  | 85.56 |  |  |  | 6.83 |  | 6.15 | [8 empty] | 9.93 |  |  |  |  | 0.03
1993 |  |  |  | 6595.99 |  |  | 7419 |  |  |  | 925 | [10 empty] | 81.42 |  |  |  | 82.61 | [5 empty] | 81.40 |  |  | 84.69 |  |  |  | 1.76 |  | 1.48 | [8 empty] | 15.91 |  |  |  |  | 1.19
1994 |  |  |  | 5513.66 |  |  | 6701 |  |  |  | 925 | [10 empty] | 72.50 |  |  |  | 82.28 | [5 empty] | 68.04 |  |  | 76.50 |  |  |  | 0.43 |  | 0.35 | [8 empty] | 17.37 |  |  |  |  | 9.78
1995 |  |  |  | 5090.97 |  |  | 5844 |  |  |  | 925 | [10 empty] | 63.17 |  |  |  | 78.19 | [5 empty] | 62.83 |  |  | 66.71 |  |  |  | 1.13 |  | 0.89 | [8 empty] | 20.92 |  |  |  |  | 15.02
1996 |  |  |  | 6496.64 |  |  | 7268 |  |  |  | 925 | [10 empty] | 80.83 |  |  |  | 82.16 | [5 empty] | 79.96 |  |  | 82.74 |  |  |  | 7.42 |  | 6.58 | [8 empty] | 11.25 |  |  |  |  | 1.34
1997 |  |  |  | 5559.27 |  |  | 6469 |  |  |  | 925 | [10 empty] | 69.32 |  |  |  | 69.32 | [5 empty] | 68.61 |  |  | 73.85 |  |  |  | 6.03 |  | 4.45 | [8 empty] | 26.23 |  |  |  |  | 0.00
1998 |  |  |  | 4575.89 |  |  | 6162 |  |  |  | 925 | [10 empty] | 57.53 |  |  |  | 68.95 | [5 empty] | 56.47 |  |  | 70.34 |  |  |  | 3.48 |  | 2.49 | [8 empty] | 28.56 |  |  |  |  | 11.42
1999 |  |  |  | 6410.98 |  |  | 7063 |  |  |  | 925 | [10 empty] | 78.19 |  |  |  | 79.31 | [5 empty] | 79.12 |  |  | 80.63 |  |  |  | 0.39 |  | 0.31 | [8 empty] | 20.38 |  |  |  |  | 1.12
2000 |  |  |  | 6970.48 |  |  | 7542 |  |  |  | 925 | [10 empty] | 84.58 |  |  |  | 84.70 | [5 empty] | 85.79 |  |  | 85.86 |  |  |  | 2.37 |  | 2.06 | [8 empty] | 13.24 |  |  |  |  | 0.12
2001 |  |  |  | 6951.72 |  |  | 7823 |  |  |  | 925 | [10 empty] | 85.39 |  |  |  | 87.30 | [5 empty] | 85.79 |  |  | 89.30 |  |  |  | 0.15 |  | 0.13 | [8 empty] | 12.57 |  |  |  |  | 1.91
2002 |  |  |  | 7204.90 |  |  | 7831 |  |  |  | 925 | [10 empty] | 87.67 |  |  |  | 88.71 | [5 empty] | 88.92 |  |  | 89.39 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 11.02 |  |  |  |  | 1.03
2003 |  |  |  | 7038.23 |  |  | 7697 |  |  |  | 925 | [10 empty] | 86.26 |  |  |  | 87.09 | [5 empty] | 86.86 |  |  | 87.87 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 12.73 |  |  |  |  | 0.82
2004 |  |  |  | 7085.74 |  |  | 7765 |  |  |  | 925 | [10 empty] | 86.88 |  |  |  | 87.86 | [5 empty] | 87.21 |  |  | 88.40 |  |  |  | 0.00 |  | 0.08 | [8 empty] | 12.05 |  |  |  |  | 0.99
2005 |  |  |  | 7303.68 |  |  | 8192 |  |  |  | 925 | [10 empty] | 90.36 |  |  |  | 93.06 | [5 empty] | 90.14 |  |  | 93.52 |  |  |  | 1.07 |  | 1.01 | [8 empty] | 5.93 |  |  |  |  | 2.70
2006 |  |  |  | 4942.96 |  |  | 5631 |  |  |  | 925 | [10 empty] | 60.71 |  |  |  | 60.71 | [5 empty] | 61.00 |  |  | 64.28 |  |  |  | 4.39 |  | 3.15 | [8 empty] | 36.14 |  |  |  |  | 0.00
2007 |  |  |  | 7566.25 |  |  | 8247 |  |  |  | 925 | [10 empty] | 92.46 |  |  |  | 93.15 | [5 empty] | 93.38 |  |  | 94.14 |  |  |  | 1.48 |  | 1.40 | [8 empty] | 5.44 |  |  |  |  | 0.70
2008 |  |  |  | 5093.44 |  |  | 5396 |  |  |  | 925 | [10 empty] | 61.23 |  |  |  | 61.29 | [5 empty] | 62.69 |  |  | 61.43 |  |  |  | 0.07 |  | 0.04 | [8 empty] | 38.67 |  |  |  |  | 0.06
2009 |  |  |  | 6082.98 |  |  | 6706 |  |  |  | 925 | [10 empty] | 74.30 |  |  |  | 74.31 | [5 empty] | 75.07 |  |  | 76.55 |  |  |  | 1.66 |  | 1.26 | [8 empty] | 24.44 |  |  |  |  | 0.00
2010 |  |  |  | 7738.82 |  |  | 8233 |  |  |  | 925 | [10 empty] | 93.55 |  |  |  | 93.71 | [5 empty] | 95.51 |  |  | 93.98 |  |  |  | 0.12 |  | 0.38 | [8 empty] | 5.91 |  |  |  |  | 0.16
2011 |  |  |  | 6241.79 |  |  | 6579 |  |  |  | 925 | [10 empty] | 73.98 |  |  |  | 74.01 | [5 empty] | 77.04 |  |  | 75.11 |  |  |  | 0.15 |  | 0.11 | [8 empty] | 25.88 |  |  |  |  | 0.03
2012 |  |  |  | 5845.23 |  |  | 6279 |  |  |  | 925 | [10 empty] | 70.62 |  |  |  | 70.62 | [5 empty] | 71.94 |  |  | 71.48 |  |  |  | 7.04 |  | 5.35 | [8 empty] | 24.03 |  |  |  |  | 0.00
2013 |  |  |  | 7942.17 |  |  | 8471 |  |  |  | 925 | [10 empty] | 95.12 |  |  |  | 95.19 | [5 empty] | 98.02 |  |  | 96.70 |  |  |  | 2.12 |  | 2.06 | [8 empty] | 2.75 |  |  |  |  | 0.07
2014 |  |  |  | 6894.49 |  |  | 7219 |  |  |  | 925 | [10 empty] | 81.72 |  |  |  | 81.82 | [5 empty] | 85.08 |  |  | 82.40 |  |  |  | 0.30 |  | 0.24 | [8 empty] | 17.94 |  |  |  |  | 0.10
2015 |  |  |  | 8079.91 |  |  | 8364 |  |  |  | 925 | [10 empty] | 95.01 |  |  |  | 95.01 | [5 empty] | 99.71 |  |  | 95.48 |  |  |  | 0.33 |  | 0.31 | [8 empty] | 4.67 |  |  |  |  | 0.00
2016 |  |  |  | 7116.59 |  |  | 7352 |  |  |  | 925 | [10 empty] | 83.34 |  |  |  | 83.35 | [5 empty] | 87.59 |  |  | 83.70 |  |  |  | 2.89 |  | 2.48 | [8 empty] | 14.17 |  |  |  |  | 0.02
2017 |  |  |  | 7946.26 |  |  | 8266 |  |  |  | 925 | [10 empty] | 93.42 |  |  |  | 93.49 | [5 empty] | 98.07 |  |  | 94.36 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 6.40 |  |  |  |  | 0.06
2018 |  |  |  | 3494.62 |  |  | 3601 |  |  |  | 925 | [10 empty] | 40.84 |  |  |  | 40.84 | [5 empty] | 43.13 |  |  | 41.11 |  |  |  | 0.66 |  | 1.09 | [8 empty] | 58.07 |  |  |  |  | 0.00
2019 |  |  |  | 6207.98 |  |  | 6723 |  |  |  | 925 | [10 empty] | 74.43 |  |  |  | 74.46 | [5 empty] | 76.61 |  |  | 76.75 |  |  |  | 5.25 |  | 4.90 | [8 empty] | 20.64 |  |  |  |  | 0.03
2020 |  |  |  | 6927.47 |  |  | 7624 |  |  |  | 925 | [10 empty] | 83.21 |  |  |  | 83.22 | [5 empty] | 85.26 |  |  | 86.79 |  |  |  | 0.35 |  | 0.29 | [8 empty] | 16.49 |  |  |  |  | 0.00
2021 |  |  |  | 7044.34 |  |  | 7418 |  |  |  | 925 | [10 empty] | 83.94 |  |  |  | 84.13 | [5 empty] | 86.93 |  |  | 84.68 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 15.85 |  |  |  |  | 0.19
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1990 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 70
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1342 | [14 empty] | 1016
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 253
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 172
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 100
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 51
Z. |  | Other | [39 empty] | 17
Subtotal | [22 empty] | 1342 | [14 empty] | 1541 |  |  |  | 89 | [11 empty] | 52
Total | [22 empty] | 1342 | [14 empty] | 1682
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1990 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 9
16. |  |  | Steam generation systems | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 8
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 4
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [37 empty] | 71
Highlights (2021)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in March-Desember. Additional electricity generation amounted to 23553 MWh. The unit was in the overhaul outage from 2020.03.14 to 2020.05.08. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.