## KRSKO
2021 Operating Experience
SI-1 | [8 empty] | KRSKO | [26 empty] | SLOVENIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NEK (Nuklearna elektrarna Krško)
Owner | [7 empty] | : | GEN (GEN Energija, d.o.o)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-03-30
Thermal power | [12 empty] | : |  |  | 1994 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-10-02
Gross electrical power | [12 empty] | : |  |  | 727 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-01-01
Reference unit power (net) | [12 empty] | : |  |  | 688 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325.2
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.309
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 46 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44029 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.13
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 21
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.62 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 5418.64 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.57 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.15 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.85 %
Load Factor (LF) | [18 empty] | : | 89.91 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.58 %
Operating Factor (OF) | [18 empty] | : | 90.64 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 820 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 516.97 | 467.20 |  |  |  | 514.65 |  | 0.35 | [8 empty] | 417.15 |  |  | 491.43 | [6 empty] | 501.75 |  | 501.68 |  |  |  | 486.41 |  |  | 507.91 |  |  | 497.72 | [9 empty] | 515.43 |  |  | 5418.64
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 0.07 | [8 empty] | 81.29 |  |  | 99.21 | [6 empty] | 98.02 |  | 98.01 |  |  |  | 98.19 |  |  | 99.09 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.57
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 0.07 | [8 empty] | 81.29 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.45 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.15
LF [%] |  |  |  |  | 101.00 | 101.05 |  |  |  | 100.68 |  | 0.07 | [8 empty] | 81.50 |  |  | 99.21 | [6 empty] | 98.02 |  | 98.01 |  |  |  | 98.19 |  |  | 99.09 |  |  | 100.48 | [9 empty] | 100.69 |  |  | 89.91
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 0.28 | [8 empty] | 86.29 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.64
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 99.93 | [8 empty] | 18.71 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.55 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.85
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.79 | [6 empty] | 1.98 |  | 1.99 |  |  |  | 1.81 |  |  | 0.36 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.58
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 194715.46 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.36 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.5 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.97 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.85 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 3724.10 |  |  | 6255 |  |  |  | 632 | [10 empty] | 69.63 |  |  |  | 69.63 | [5 empty] | 67.27 |  |  | 71.40 |  |  |  | 5.54 |  | 4.08 | [8 empty] | 26.29 |  |  |  |  | 0.00
1984 |  |  |  | 4207.60 |  |  | 7073 |  |  |  | 632 | [10 empty] | 79.80 |  |  |  | 79.80 | [5 empty] | 75.79 |  |  | 80.52 |  |  |  | 5.16 |  | 4.34 | [8 empty] | 15.86 |  |  |  |  | 0.00
1985 |  |  |  | 3845.27 |  |  | 6421 |  |  |  | 632 | [10 empty] | 72.06 |  |  |  | 72.06 | [5 empty] | 69.46 |  |  | 73.30 |  |  |  | 8.22 |  | 6.46 | [8 empty] | 21.48 |  |  |  |  | 0.00
1986 |  |  |  | 3821.99 |  |  | 6561 |  |  |  | 620 | [10 empty] | 73.74 |  |  |  | 74.83 | [5 empty] | 70.37 |  |  | 74.90 |  |  |  | 2.64 |  | 2.03 | [8 empty] | 23.14 |  |  |  |  | 1.10
1987 |  |  |  | 4278.82 |  |  | 7287 |  |  |  | 620 | [10 empty] | 83.54 |  |  |  | 83.54 | [5 empty] | 78.78 |  |  | 83.18 |  |  |  | 1.90 |  | 1.62 | [8 empty] | 14.84 |  |  |  |  | 0.00
1988 |  |  |  | 3935.75 |  |  | 6866 |  |  |  | 620 | [10 empty] | 76.94 |  |  |  | 77.03 | [5 empty] | 72.27 |  |  | 78.16 |  |  |  | 6.58 |  | 5.43 | [8 empty] | 17.54 |  |  |  |  | 0.09
1989 |  |  |  | 4453.95 |  |  | 7500 |  |  |  | 620 | [10 empty] | 85.18 |  |  |  | 85.46 | [5 empty] | 82.01 |  |  | 85.62 |  |  |  | 1.38 |  | 1.20 | [8 empty] | 13.34 |  |  |  |  | 0.27
1990 |  |  |  | 4386.77 |  |  | 7592 |  |  |  | 620 | [10 empty] | 85.38 |  |  |  | 87.10 | [5 empty] | 80.77 |  |  | 86.67 |  |  |  | 0.17 |  | 0.15 | [8 empty] | 12.75 |  |  |  |  | 1.72
1991 |  |  |  | 4718.22 |  |  | 8133 |  |  |  | 632 | [10 empty] | 88.67 |  |  |  | 94.63 | [5 empty] | 85.22 |  |  | 92.84 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 5.28 |  |  |  |  | 5.96
1992 |  |  |  | 3767.25 |  |  | 6699 |  |  |  | 632 | [10 empty] | 68.60 |  |  |  | 73.98 | [5 empty] | 67.86 |  |  | 76.26 |  |  |  | 2.41 |  | 1.83 | [8 empty] | 24.19 |  |  |  |  | 5.38
1993 |  |  |  | 3762.77 |  |  | 6493 |  |  |  | 620 | [10 empty] | 69.28 |  |  |  | 72.53 | [5 empty] | 69.28 |  |  | 74.12 |  |  |  | 6.46 |  | 5.01 | [8 empty] | 22.46 |  |  |  |  | 3.26
1994 |  |  |  | 4403.53 |  |  | 7402 |  |  |  | 620 | [10 empty] | 81.08 |  |  |  | 82.10 | [5 empty] | 81.08 |  |  | 84.50 |  |  |  | 0.80 |  | 0.66 | [8 empty] | 17.25 |  |  |  |  | 1.02
1995 |  |  |  | 4568.50 |  |  | 7606 |  |  |  | 620 | [10 empty] | 84.07 |  |  |  | 85.09 | [5 empty] | 84.12 |  |  | 86.83 |  |  |  | 2.21 |  | 1.92 | [8 empty] | 12.99 |  |  |  |  | 1.02
1996 |  |  |  | 4361.62 |  |  | 7143 |  |  |  | 620 | [10 empty] | 79.64 |  |  |  | 79.64 | [5 empty] | 80.09 |  |  | 81.32 |  |  |  | 0.27 |  | 0.22 | [8 empty] | 20.14 |  |  |  |  | 0.00
1997 |  |  |  | 4793.98 |  |  | 7824 |  |  |  | 620 | [10 empty] | 87.76 |  |  |  | 88.27 | [5 empty] | 88.27 |  |  | 89.32 |  |  |  | 2.28 |  | 2.06 | [8 empty] | 9.66 |  |  |  |  | 0.51
1998 |  |  |  | 4793.60 |  |  | 7913 |  |  |  | 620 | [10 empty] | 88.01 |  |  |  | 89.54 | [5 empty] | 88.26 |  |  | 90.33 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 10.42 |  |  |  |  | 1.53
1999 |  |  |  | 4492.38 |  |  | 7480 |  |  |  | 620 | [10 empty] | 82.45 |  |  |  | 84.73 | [5 empty] | 82.71 |  |  | 85.39 |  |  |  | 1.17 |  | 1.00 | [8 empty] | 14.27 |  |  |  |  | 2.28
2000 |  |  |  | 4548.79 |  |  | 7295 |  |  |  | 676 | [10 empty] | 80.49 |  |  |  | 82.56 | [5 empty] | 80.10 |  |  | 83.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.43 |  |  |  |  | 2.08
2001 |  |  |  | 5036.28 |  |  | 7790 |  |  |  | 656 | [10 empty] | 86.22 |  |  |  | 88.45 | [5 empty] | 87.64 |  |  | 88.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.55 |  |  |  |  | 2.23
2002 |  |  |  | 5308.75 |  |  | 8111 |  |  |  | 676 | [10 empty] | 91.09 |  |  |  | 91.99 | [5 empty] | 89.65 |  |  | 92.59 |  |  |  | 0.86 |  | 0.80 | [8 empty] | 7.20 |  |  |  |  | 0.91
2003 |  |  |  | 4963.34 |  |  | 8084 |  |  |  | 676 | [10 empty] | 86.19 |  |  |  | 91.60 | [5 empty] | 83.82 |  |  | 92.28 |  |  |  | 0.87 |  | 0.81 | [8 empty] | 7.59 |  |  |  |  | 5.42
2004 |  |  |  | 5212.18 |  |  | 8081 |  |  |  | 676 | [10 empty] | 89.88 |  |  |  | 91.41 | [5 empty] | 87.78 |  |  | 92.00 |  |  |  | 0.40 |  | 0.88 | [8 empty] | 7.71 |  |  |  |  | 1.53
2005 |  |  |  | 5613.65 |  |  | 8664 |  |  |  | 656 | [10 empty] | 98.32 |  |  |  | 98.55 | [5 empty] | 97.69 |  |  | 98.90 |  |  |  | 1.45 |  | 1.45 | [8 empty] | 0.00 |  |  |  |  | 0.22
2006 |  |  |  | 5289.47 |  |  | 7883 |  |  |  | 666 | [10 empty] | 89.92 |  |  |  | 90.06 | [5 empty] | 91.34 |  |  | 89.99 |  |  |  | 0.00 |  | 0.83 | [8 empty] | 9.11 |  |  |  |  | 0.14
2007 |  |  |  | 5428.19 |  |  | 7989 |  |  |  | 666 | [10 empty] | 90.90 |  |  |  | 91.01 | [5 empty] | 93.04 |  |  | 91.20 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 8.89 |  |  |  |  | 0.11
2008 |  |  |  | 5972.03 |  |  | 8660 |  |  |  | 666 | [10 empty] | 98.59 |  |  |  | 98.59 | [5 empty] | 102.08 |  |  | 98.59 |  |  |  | 1.41 |  | 1.41 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 5459.72 |  |  | 7992 |  |  |  | 666 | [10 empty] | 90.75 |  |  |  | 90.75 | [5 empty] | 93.58 |  |  | 91.23 |  |  |  | 0.03 |  | 0.60 | [8 empty] | 8.65 |  |  |  |  | 0.00
2010 |  |  |  | 5380.71 |  |  | 7876 |  |  |  | 666 | [10 empty] | 89.33 |  |  |  | 89.33 | [5 empty] | 92.23 |  |  | 89.91 |  |  |  | 0.00 |  | 1.52 | [8 empty] | 9.15 |  |  |  |  | 0.00
2011 |  |  |  | 5902.24 |  |  | 8600 |  |  |  | 688 | [10 empty] | 98.64 |  |  |  | 99.20 | [5 empty] | 97.93 |  |  | 98.17 |  |  |  | 0.77 |  | 0.77 | [8 empty] | 0.03 |  |  |  |  | 0.55
2012 |  |  |  | 5243.68 |  |  | 7697 |  |  |  | 688 | [10 empty] | 86.48 |  |  |  | 87.00 | [5 empty] | 86.77 |  |  | 87.63 |  |  |  | 0.72 |  | 1.96 | [8 empty] | 11.04 |  |  |  |  | 0.52
2013 |  |  |  | 5036.47 |  |  | 7391 |  |  |  | 688 | [10 empty] | 83.04 |  |  |  | 83.47 | [5 empty] | 83.57 |  |  | 84.37 |  |  |  | 2.79 |  | 6.28 | [8 empty] | 10.25 |  |  |  |  | 0.43
2014 |  |  |  | 6060.82 |  |  | 8760 |  |  |  | 688 | [10 empty] | 99.95 |  |  |  | 100.00 | [5 empty] | 100.56 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.05
2015 |  |  |  | 5371.66 |  |  | 7826 |  |  |  | 688 | [10 empty] | 88.47 |  |  |  | 88.78 | [5 empty] | 89.13 |  |  | 89.34 |  |  |  | 0.00 |  | 0.31 | [8 empty] | 10.91 |  |  |  |  | 0.31
2016 |  |  |  | 5431.27 |  |  | 7923 |  |  |  | 688 | [10 empty] | 89.25 |  |  |  | 89.62 | [5 empty] | 89.87 |  |  | 90.20 |  |  |  | 0.00 |  | 1.15 | [8 empty] | 9.23 |  |  |  |  | 0.36
2017 |  |  |  | 5967.83 |  |  | 8708 |  |  |  | 688 | [10 empty] | 98.52 |  |  |  | 99.19 | [5 empty] | 99.01 |  |  | 99.40 |  |  |  | 0.81 |  | 0.81 | [8 empty] | 0.00 |  |  |  |  | 0.67
2018 |  |  |  | 5489.91 |  |  | 8010 |  |  |  | 688 | [10 empty] | 90.57 |  |  |  | 90.92 | [5 empty] | 91.09 |  |  | 91.44 |  |  |  | 0.20 |  | 0.98 | [8 empty] | 8.09 |  |  |  |  | 0.35
2019 |  |  |  | 5532.98 |  |  | 8081 |  |  |  | 688 | [10 empty] | 91.28 |  |  |  | 91.72 | [5 empty] | 91.81 |  |  | 92.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.28 |  |  |  |  | 0.44
2020 |  |  |  | 6040.85 |  |  | 8748 |  |  |  | 688 | [10 empty] | 99.34 |  |  |  | 99.51 | [5 empty] | 99.96 |  |  | 99.59 |  |  |  | 0.49 |  | 0.49 | [8 empty] | 0.00 |  |  |  |  | 0.17
2021 |  |  |  | 5418.64 |  |  | 7940 |  |  |  | 688 | [10 empty] | 89.57 |  |  |  | 90.15 | [5 empty] | 89.91 |  |  | 90.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.85 |  |  |  |  | 0.58
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1983 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 128
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 813
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 125
E. |  | Testing of plant systems or components | [35 empty] | 39 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [20 empty] | 819 | [14 empty] | 39
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 819 | [14 empty] | 1016 |  |  |  | 131 | [11 empty] | 4
Total | [22 empty] | 819 | [14 empty] | 1151
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1983 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 14
12. |  |  | Reactor I&C Systems | [34 empty] | 4
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 11
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 25
32. |  |  | Feedwater and Main Steam System | [34 empty] | 35
33. |  |  | Circulating Water System | [34 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 7
42. |  |  | Electrical Power Supply Systems | [34 empty] | 13
Total | [37 empty] | 131
Highlights (2021)
Planned outage with refuelling from 1.4.2021 to 5.5.2021.