## BARAKAH-1
2021 Operating Experience
AE-01 | [8 empty] | BARAKAH-1 | [26 empty] | UNITED ARAB EMIRATES
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NAWAH (Nawah Energy Company)
Owner | [7 empty] | : | ENEC (Emirates Nuclear Energy Corporation)
Reactor Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Turbine Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / APR-1400 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2012-07-19
Thermal power | [12 empty] | : |  |  | 3983 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-08-19
Gross electrical power | [12 empty] | : |  |  | 1417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-04-01
Reference unit power (net) | [12 empty] | : |  |  | 1417 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.513
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.414
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.66 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28914 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.647 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.629
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 47.572 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 81 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 8926.09 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 13.54 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.44 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 13.47 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.55 %
Load Factor (LF) | [18 empty] | : | 85.49 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.54 %
Operating Factor (OF) | [18 empty] | : | 91.77 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1997 hours
Annual Summary
[5 empty] | Mar | Jan |  |  |  | Feb |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [11 empty] | 790.74 | [8 empty] | 1039.52 |  |  | 924.80 | [6 empty] | 897.70 |  | 982.90 |  |  |  | 975.15 |  |  | 339.93 |  |  | 997.65 | [9 empty] | 1046.97 |  |  | 7995.36
EAF [%] | [11 empty] | 77.02 | [8 empty] | 98.60 |  |  | 90.65 | [6 empty] | 85.15 |  | 93.23 |  |  |  | 95.58 |  |  | 32.24 |  |  | 97.79 | [9 empty] | 99.31 |  |  | 85.44
UCF [%] | [11 empty] | 77.02 | [8 empty] | 99.08 |  |  | 91.53 | [6 empty] | 86.69 |  | 95.01 |  |  |  | 96.76 |  |  | 32.44 |  |  | 97.39 | [9 empty] | 98.52 |  |  | 85.98
LF [%] | [11 empty] | 77.50 | [8 empty] | 98.60 |  |  | 90.65 | [6 empty] | 85.15 |  | 93.23 |  |  |  | 95.58 |  |  | 32.24 |  |  | 97.79 | [9 empty] | 99.31 |  |  | 85.49
OF [%] | [11 empty] | 81.67 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 44.76 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.77
FLR [%] | [11 empty] | 22.96 | [8 empty] | 0.10 |  |  | 7.28 | [6 empty] | 12.38 |  | 4.50 |  |  |  | 3.11 |  |  | 67.20 |  |  | 2.61 | [9 empty] | 1.48 |  |  | 13.54
UCL [%] | [11 empty] | 22.95 | [8 empty] | 0.10 |  |  | 7.18 | [6 empty] | 12.25 |  | 4.48 |  |  |  | 3.11 |  |  | 66.47 |  |  | 2.61 | [9 empty] | 1.48 |  |  | 13.47
PUF [%] | [11 empty] | 0.03 | [8 empty] | 0.82 |  |  | 1.29 | [6 empty] | 1.06 |  | 0.51 |  |  |  | 0.14 |  |  | 1.10 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.55
XUF [%] | [11 empty] | 0.00 | [8 empty] | 0.47 |  |  | 0.88 | [6 empty] | 1.54 |  | 1.78 |  |  |  | 1.18 |  |  | 0.19 |  |  | -0.40 | [9 empty] | -0.79 |  |  | 0.54
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 10487.9 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 13.54 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.44 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.47 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.98 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0.55 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.49 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.54 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.77 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2021 |  |  |  | 8926.09 |  |  | 6763 |  |  |  | 1417 | [10 empty] | 85.44 |  |  |  | 85.98 | [5 empty] | 85.49 |  |  | 91.77 |  |  |  | 13.54 |  | 13.47 | [8 empty] | 0.55 |  |  |  |  | 0.54
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 2021 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 830 | [14 empty] | 1107
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 854 | [14 empty] | 1139
Z. |  | Other | [24 empty] | 581 | [14 empty] | 775
Subtotal | [22 empty] | 854 |  |  |  | 1411 | [10 empty] | 1139 |  |  |  | 1882
Total | [22 empty] | 2265 | [14 empty] | 3021
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 2021 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [19 empty] | 462 | [14 empty] | 462
33. |  |  | Circulating Water System | [19 empty] | 368 | [14 empty] | 368
Total | [22 empty] | 830 | [14 empty] | 830

## BARAKAH-2
2021 Operating Experience
AE-02 | [8 empty] | BARAKAH-2 | [26 empty] | UNITED ARAB EMIRATES
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NAWAH (Nawah Energy Company)
Owner | [7 empty] | : | ENEC (Emirates Nuclear Energy Corporation)
Reactor Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Turbine Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / APR-1400 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2013-04-15
Thermal power | [12 empty] | : |  |  | 3983 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2021-09-14
Gross electrical power | [12 empty] | : |  |  | 1417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | :
Reference unit power (net) | [12 empty] | : |  |  | 1345 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 0 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.513
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.414
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.66 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28914 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.647 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.629
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 81 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2021)
Net Energy Production | [18 empty] | : | 1200.19 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 725 hours
Annual Summary
[5 empty] | Jan | Oct |  |  |  | Nov |  | Dec | [8 empty] | Feb |  |  | Mar | [6 empty] | Apr |  | May |  |  |  | Jun |  |  | Jul |  |  | Aug | [9 empty] | Sep
GW(e)-h
EAF [%]
UCF [%]
LF [%]
OF [%]
FLR [%]
UCL [%]
PUF [%]
XUF [%]
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 1200.19 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 0 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2021 | [14 empty] | 1 to 2021
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 560
Subtotal | [26 empty] | 560
Total | [22 empty] | 560 | [14 empty] | 0
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2021 | [14 empty] | 1 to 2021
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [19 empty] | 301 | [14 empty] | 903
31. |  |  | Turbine and auxiliaries | [19 empty] | 259 | [14 empty] | 777
Total | [22 empty] | 560 | [14 empty] | 1680