## BARAKAH-1
2022 Operating Experience
AE-01 | [8 empty] | BARAKAH-1 | [26 empty] | UNITED ARAB EMIRATES
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NAWAH (Nawah Energy Company)
Owner | [7 empty] | : | ENEC (Emirates Nuclear Energy Corporation)
Reactor Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Turbine Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / APR-1400 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2012-07-19
Thermal power | [12 empty] | : |  |  | 3983 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-08-19
Gross electrical power | [12 empty] | : |  |  | 1417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-04-01
Reference unit power (net) | [12 empty] | : |  |  | 1337 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.513
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.414
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.66 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28914 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.647 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.629
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 47.572 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 81 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2022)
Net Energy Production | [18 empty] | : | 8196.79 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.53 %
Energy Availability Factor (EAF) | [18 empty] | : | 69.89 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 8.26 %
Unit Capability Factor (UCF) | [18 empty] | : | 70.18 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.55 %
Load Factor (LF) | [18 empty] | : | 69.99 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.3 %
Operating Factor (OF) | [18 empty] | : | 71.56 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2491 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 977.00 | 885.77 |  |  |  | 983.00 |  | 199.55 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 763.17 |  | 977.01 |  |  |  | 660.78 |  |  | 763.84 |  |  | 973.00 | [9 empty] | 1013.69 |  |  | 8196.79
EAF [%] |  |  |  |  | 97.91 | 98.29 |  |  |  | 98.61 |  | 20.69 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 77.18 |  | 98.92 |  |  |  | 69.69 |  |  | 77.25 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 69.89
UCF [%] |  |  |  |  | 97.91 | 98.29 |  |  |  | 98.61 |  | 20.69 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 78.37 |  | 100.00 |  |  |  | 70.56 |  |  | 77.61 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 70.18
LF [%] |  |  |  |  | 98.22 | 98.59 |  |  |  | 98.82 |  | 20.73 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 76.72 |  | 98.22 |  |  |  | 68.64 |  |  | 76.79 |  |  | 101.08 | [9 empty] | 101.91 |  |  | 69.99
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 22.36 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 85.35 |  | 100.00 |  |  |  | 70.56 |  |  | 80.24 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 71.56
FLR [%] |  |  |  |  | 1.39 | 1.48 |  |  |  | 1.39 |  | 1.61 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.53
UCL [%] |  |  |  |  | 1.38 | 1.47 |  |  |  | 1.39 |  | 0.34 | [8 empty] | 0.00 |  |  | 80.83 | [6 empty] | 14.65 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.26
PUF [%] |  |  |  |  | 0.71 | 0.24 |  |  |  | 0.00 |  | 78.97 | [8 empty] | 100.00 |  |  | 19.17 | [6 empty] | 6.98 |  | 0.00 |  |  |  | 29.44 |  |  | 22.39 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 21.55
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.20 |  | 1.08 |  |  |  | 0.86 |  |  | 0.37 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.30
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 18684.69 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.42 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.79 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 10.57 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.2 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.23 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.87 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.4 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.25 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2021 |  |  |  | 8926.09 |  |  | 6763 |  |  |  | 1417 | [10 empty] | 85.44 |  |  |  | 85.98 | [5 empty] | 85.49 |  |  | 91.77 |  |  |  | 13.54 |  | 13.47 | [8 empty] | 0.55 |  |  |  |  | 0.54
2022 |  |  |  | 8196.79 |  |  | 6269 |  |  |  | 1337 | [10 empty] | 69.89 |  |  |  | 70.18 | [5 empty] | 69.99 |  |  | 71.56 |  |  |  | 0.53 |  | 8.26 | [8 empty] | 21.55 |  |  |  |  | 0.30
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2022 | [14 empty] | 2021 to 2022
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 474
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1441 | [14 empty] | 823
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 359 | [14 empty] | 693
Z. |  | Other | [24 empty] | 691 | [14 empty] | 727
Subtotal | [22 empty] | 1800 |  |  |  | 691 | [10 empty] | 1516 |  |  |  | 1201
Total | [22 empty] | 2491 | [14 empty] | 2717
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2022 | [14 empty] | 2021 to 2022
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 231
33. |  |  | Circulating Water System | [34 empty] | 184
Total | [37 empty] | 415

## BARAKAH-2
2022 Operating Experience
AE-02 | [8 empty] | BARAKAH-2 | [26 empty] | UNITED ARAB EMIRATES
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NAWAH (Nawah Energy Company)
Owner | [7 empty] | : | ENEC (Emirates Nuclear Energy Corporation)
Reactor Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Turbine Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / APR-1400 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2013-04-15
Thermal power | [12 empty] | : |  |  | 3983 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2021-09-14
Gross electrical power | [12 empty] | : |  |  | 1417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | :
Reference unit power (net) | [12 empty] | : |  |  | 1337 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.513
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.414
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.66 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28914 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.647 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.629
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 81 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2022)
Net Energy Production | [18 empty] | : | 9914.13 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1037 hours
Annual Summary
[5 empty] | Jan | Oct |  |  |  | Nov |  | Dec | [8 empty] | Feb |  |  | Mar | [6 empty] | Apr |  | May |  |  |  | Jun |  |  | Jul |  |  | Aug | [9 empty] | Sep
GW(e)-h
EAF [%]
UCF [%]
LF [%]
OF [%]
FLR [%]
UCL [%]
PUF [%]
XUF [%]
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 11114.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 0 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2022 | [14 empty] | 1 to 2022
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 58
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 979
Subtotal | [22 empty] | 979 |  |  |  | 58
Total | [22 empty] | 1037 | [14 empty] | 0
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2022 | [14 empty] | 1 to 2022
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 58 | [14 empty] | 44
15. |  |  | Reactor Cooling Systems | [34 empty] | 226
31. |  |  | Turbine and auxiliaries | [34 empty] | 194
Total | [22 empty] | 58 | [14 empty] | 464

## BARAKAH-3
2022 Operating Experience
AE-03 | [8 empty] | BARAKAH-3 | [26 empty] | UNITED ARAB EMIRATES
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NAWAH (Nawah Energy Company)
Owner | [7 empty] | : | ENEC (Emirates Nuclear Energy Corporation)
Reactor Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Turbine Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / APR-1400 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2014-09-24
Thermal power | [12 empty] | : |  |  | 3983 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2022-10-08
Gross electrical power | [12 empty] | : |  |  | 1417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2023-02-24
Reference unit power (net) | [12 empty] | : |  |  | 1337 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 0 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28914 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2022)
Net Energy Production | [18 empty] | : | 1189.53 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 337 hours
Annual Summary
[5 empty] | Jan | Oct |  |  |  | Nov |  | Dec | [8 empty] | Feb |  |  | Mar | [6 empty] | Apr |  | May |  |  |  | Jun |  |  | Jul |  |  | Aug | [9 empty] | Sep
GW(e)-h
EAF [%]
UCF [%]
LF [%]
OF [%]
FLR [%]
UCL [%]
PUF [%]
XUF [%]
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 1189.53 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 0 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 0 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2022 | [14 empty] | 2023 to 2022
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 83
E. |  | Testing of plant systems or components | [20 empty] | 254
Subtotal | [22 empty] | 254 |  |  |  | 83
Total | [22 empty] | 337 | [14 empty] | 0
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2022 | [14 empty] | 2023 to 2022
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 83 | [14 empty] | 332
Total | [22 empty] | 83 | [14 empty] | 332