## ATUCHA-1
2023 Operating Experience
AR-1 | [8 empty] | ATUCHA-1 | [26 empty] | ARGENTINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Owner | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Reactor Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Turbine Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / PHWR KWU | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-05-31
Thermal power | [12 empty] | : |  |  | 1179 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-03-18
Gross electrical power | [12 empty] | : |  |  | 362 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-06-23
Reference unit power (net) | [12 empty] | : |  |  | 340 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 11.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 303.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.28
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.85 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 11140 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.51 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.26
| Active core height/length [m] | [13 empty] | : |  |  | 5.3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 21
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 250 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 23.22 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 29 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2197.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 6.47 %
Energy Availability Factor (EAF) | [18 empty] | : | 73.77 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 5.15 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.46 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.4 %
Load Factor (LF) | [18 empty] | : | 73.77 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.69 %
Operating Factor (OF) | [18 empty] | : | 78.25 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1905 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 193.40 | 218.68 |  |  |  | 218.95 |  | 235.59 | [8 empty] | 228.53 |  |  | 241.96 | [6 empty] | 249.34 |  | 251.30 |  |  |  | 64.37 |  |  | 0.00 |  |  | 70.30 | [9 empty] | 224.69 |  |  | 2197.12
EAF [%] |  |  |  |  | 76.45 | 95.71 |  |  |  | 86.55 |  | 96.24 | [8 empty] | 90.34 |  |  | 98.84 | [6 empty] | 98.57 |  | 99.34 |  |  |  | 26.30 |  |  | 0.00 |  |  | 28.72 | [9 empty] | 88.83 |  |  | 73.77
UCF [%] |  |  |  |  | 76.45 | 95.71 |  |  |  | 86.55 |  | 96.24 | [8 empty] | 98.45 |  |  | 98.84 | [6 empty] | 98.57 |  | 99.34 |  |  |  | 26.30 |  |  | 0.00 |  |  | 28.72 | [9 empty] | 88.83 |  |  | 74.46
LF [%] |  |  |  |  | 76.45 | 95.71 |  |  |  | 86.55 |  | 96.24 | [8 empty] | 90.34 |  |  | 98.84 | [6 empty] | 98.57 |  | 99.34 |  |  |  | 26.30 |  |  | 0.00 |  |  | 28.72 | [9 empty] | 88.83 |  |  | 73.77
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 93.82 |  | 100.00 | [8 empty] | 93.68 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 26.67 |  |  | 0.00 |  |  | 31.67 | [9 empty] | 93.55 |  |  | 78.25
FLR [%] |  |  |  |  | 23.55 | 4.29 |  |  |  | 13.45 |  | 2.48 | [8 empty] | 1.55 |  |  | 1.16 | [6 empty] | 1.43 |  | 0.66 |  |  |  | 1.57 |  |  | 0.00 |  |  | 3.61 | [9 empty] | 11.17 |  |  | 6.47
UCL [%] |  |  |  |  | 23.55 | 4.29 |  |  |  | 13.45 |  | 2.44 | [8 empty] | 1.55 |  |  | 1.16 | [6 empty] | 1.43 |  | 0.66 |  |  |  | 0.42 |  |  | 0.00 |  |  | 1.08 | [9 empty] | 11.17 |  |  | 5.15
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 1.32 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 73.29 |  |  | 100.00 |  |  | 70.21 | [9 empty] | 0.00 |  |  | 20.40
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.11 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.69
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 105719.72 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 10.42 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.43 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.28 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.36 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.37 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.54 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.93 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 947.50 |  |  | 4458 |  |  |  | 321 | [10 empty] | 50.27 |  |  |  | 51.01 | [5 empty] | 50.29 |  |  | 65.96 |  |  |  | 16.06 |  | 9.76 | [8 empty] | 39.23 |  |  |  |  | 0.73
1975 |  |  |  | 2357.80 |  |  | 7730 |  |  |  | 319 | [10 empty] | 85.63 |  |  |  | 85.63 | [5 empty] | 84.37 |  |  | 88.24 |  |  |  | 5.33 |  | 4.82 | [8 empty] | 9.55 |  |  |  |  | 0.00
1976 |  |  |  | 2408.60 |  |  | 7808 |  |  |  | 319 | [10 empty] | 86.89 |  |  |  | 86.89 | [5 empty] | 85.96 |  |  | 88.89 |  |  |  | 10.93 |  | 10.66 | [8 empty] | 2.45 |  |  |  |  | 0.00
1977 |  |  |  | 1537.00 |  |  | 4650 |  |  |  | 336 | [10 empty] | 52.99 |  |  |  | 52.99 | [5 empty] | 52.15 |  |  | 53.08 |  |  |  | 24.01 |  | 16.75 | [8 empty] | 30.26 |  |  |  |  | 0.00
1978 |  |  |  | 2711.81 |  |  | 8026 |  |  |  | 345 | [10 empty] | 90.89 |  |  |  | 90.89 | [5 empty] | 89.73 |  |  | 91.62 |  |  |  | 8.88 |  | 8.85 | [8 empty] | 0.26 |  |  |  |  | 0.00
1979 |  |  |  | 2503.70 |  |  | 7551 |  |  |  | 335 | [10 empty] | 84.14 |  |  |  | 84.14 | [5 empty] | 85.32 |  |  | 86.20 |  |  |  | 15.72 |  | 15.70 | [8 empty] | 0.16 |  |  |  |  | 0.00
1980 |  |  |  | 2180.50 |  |  | 6947 |  |  |  | 335 | [10 empty] | 73.51 |  |  |  | 73.51 | [5 empty] | 74.10 |  |  | 79.09 |  |  |  | 8.40 |  | 6.74 | [8 empty] | 19.74 |  |  |  |  | 0.00
1981 |  |  |  | 2647.60 |  |  | 8120 |  |  |  | 335 | [10 empty] | 89.66 |  |  |  | 89.66 | [5 empty] | 90.22 |  |  | 92.69 |  |  |  | 8.38 |  | 8.20 | [8 empty] | 2.13 |  |  |  |  | 0.00
1982 |  |  |  | 1753.60 |  |  | 5600 |  |  |  | 335 | [10 empty] | 59.17 |  |  |  | 59.17 | [5 empty] | 59.76 |  |  | 63.93 |  |  |  | 13.18 |  | 8.98 | [8 empty] | 31.85 |  |  |  |  | 0.00
1983 |  |  |  | 2356.00 |  |  | 8101 |  |  |  | 335 | [10 empty] | 78.36 |  |  |  | 78.36 | [5 empty] | 80.28 |  |  | 92.48 |  |  |  | 11.09 |  | 9.77 | [8 empty] | 11.87 |  |  |  |  | 0.00
1984 |  |  |  | 1706.12 |  |  | 8678 |  |  |  | 335 | [10 empty] | 98.74 |  |  |  | 98.74 | [5 empty] | 57.98 |  |  | 98.79 |  |  |  | 1.26 |  | 1.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 1470.45 |  |  | 7159 |  |  |  | 335 | [10 empty] | 91.58 |  |  |  | 91.58 | [5 empty] | 50.11 |  |  | 81.72 |  |  |  | 8.42 |  | 8.42 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 2204.96 |  |  | 7532 |  |  |  | 335 | [10 empty] | 75.83 |  |  |  | 75.83 | [5 empty] | 75.14 |  |  | 85.98 |  |  |  | 10.36 |  | 8.76 | [8 empty] | 15.40 |  |  |  |  | 0.00
1987 |  |  |  | 1405.80 |  |  | 4391 |  |  |  | 335 | [10 empty] | 49.18 |  |  |  | 49.24 | [5 empty] | 47.90 |  |  | 50.13 |  |  |  | 29.90 |  | 21.01 | [8 empty] | 29.75 |  |  |  |  | 0.06
1988 |  |  |  | 808.10 |  |  | 2515 |  |  |  | 335 | [10 empty] | 27.07 |  |  |  | 27.07 | [5 empty] | 27.46 |  |  | 28.63 |  |  |  | 72.93 |  | 72.93 | [8 empty] | 0.00 |  |  |  |  | 0.00
1989 |  |  |  | 0.00 |  |  | 0 |  |  |  | 335 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1990 |  |  |  | 1722.59 |  |  | 7201 |  |  |  | 335 | [10 empty] | 58.70 |  |  |  | 84.89 | [5 empty] | 58.70 |  |  | 82.20 |  |  |  | 6.76 |  | 6.15 | [8 empty] | 8.96 |  |  |  |  | 26.19
1991 |  |  |  | 2721.89 |  |  | 8390 |  |  |  | 335 | [10 empty] | 92.58 |  |  |  | 92.58 | [5 empty] | 92.75 |  |  | 95.78 |  |  |  | 7.35 |  | 7.34 | [8 empty] | 0.08 |  |  |  |  | 0.00
1992 |  |  |  | 2230.24 |  |  | 7089 |  |  |  | 335 | [10 empty] | 76.33 |  |  |  | 76.33 | [5 empty] | 75.79 |  |  | 80.70 |  |  |  | 7.71 |  | 6.38 | [8 empty] | 17.29 |  |  |  |  | 0.00
1993 |  |  |  | 2403.66 |  |  | 7287 |  |  |  | 335 | [10 empty] | 82.16 |  |  |  | 82.16 | [5 empty] | 81.91 |  |  | 83.18 |  |  |  | 6.54 |  | 5.75 | [8 empty] | 12.09 |  |  |  |  | 0.00
1994 |  |  |  | 2651.86 |  |  | 7916 |  |  |  | 335 | [10 empty] | 90.37 |  |  |  | 90.37 | [5 empty] | 90.37 |  |  | 90.37 |  |  |  | 1.19 |  | 1.08 | [8 empty] | 8.55 |  |  |  |  | 0.00
1995 |  |  |  | 2671.71 |  |  | 8376 |  |  |  | 335 | [10 empty] | 92.28 |  |  |  | 92.28 | [5 empty] | 91.04 |  |  | 95.62 |  |  |  | 7.58 |  | 7.57 | [8 empty] | 0.15 |  |  |  |  | 0.00
1996 |  |  |  | 2038.80 |  |  | 6990 |  |  |  | 335 | [10 empty] | 70.62 |  |  |  | 70.62 | [5 empty] | 69.28 |  |  | 79.58 |  |  |  | 6.80 |  | 5.15 | [8 empty] | 24.23 |  |  |  |  | 0.00
1997 |  |  |  | 2720.14 |  |  | 8329 |  |  |  | 335 | [10 empty] | 93.36 |  |  |  | 93.36 | [5 empty] | 92.69 |  |  | 95.08 |  |  |  | 6.64 |  | 6.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 2374.36 |  |  | 7242 |  |  |  | 335 | [10 empty] | 81.32 |  |  |  | 81.40 | [5 empty] | 80.91 |  |  | 82.67 |  |  |  | 6.76 |  | 5.90 | [8 empty] | 12.69 |  |  |  |  | 0.08
1999 |  |  |  | 1395.50 |  |  | 4364 |  |  |  | 335 | [10 empty] | 47.81 |  |  |  | 47.81 | [5 empty] | 47.55 |  |  | 49.82 |  |  |  | 25.70 |  | 16.54 | [8 empty] | 35.66 |  |  |  |  | 0.00
2000 |  |  |  | 1677.85 |  |  | 5038 |  |  |  | 335 | [10 empty] | 56.85 |  |  |  | 72.76 | [5 empty] | 57.02 |  |  | 57.35 |  |  |  | 27.24 |  | 27.24 | [8 empty] | 0.00 |  |  |  |  | 15.92
2001 |  |  |  | 1425.96 |  |  | 4407 |  |  |  | 335 | [10 empty] | 48.74 |  |  |  | 48.74 | [5 empty] | 48.59 |  |  | 50.31 |  |  |  | 28.98 |  | 19.89 | [8 empty] | 31.38 |  |  |  |  | 0.00
2002 |  |  |  | 1011.50 |  |  | 3030 |  |  |  | 335 | [10 empty] | 34.58 |  |  |  | 34.58 | [5 empty] | 34.47 |  |  | 34.59 |  |  |  | 16.39 |  | 6.78 | [8 empty] | 58.64 |  |  |  |  | 0.00
2003 |  |  |  | 2020.60 |  |  | 6094 |  |  |  | 335 | [10 empty] | 68.76 |  |  |  | 68.76 | [5 empty] | 68.85 |  |  | 69.57 |  |  |  | 9.42 |  | 7.15 | [8 empty] | 24.09 |  |  |  |  | 0.00
2004 |  |  |  | 2725.01 |  |  | 8250 |  |  |  | 335 | [10 empty] | 92.17 |  |  |  | 92.17 | [5 empty] | 92.60 |  |  | 93.92 |  |  |  | 7.83 |  | 7.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 1997.96 |  |  | 7004 |  |  |  | 335 | [10 empty] | 68.50 |  |  |  | 68.50 | [5 empty] | 68.08 |  |  | 79.95 |  |  |  | 6.44 |  | 4.72 | [8 empty] | 26.79 |  |  |  |  | 0.00
2006 |  |  |  | 2100.55 |  |  | 6403 |  |  |  | 335 | [10 empty] | 72.10 |  |  |  | 72.10 | [5 empty] | 71.58 |  |  | 73.09 |  |  |  | 14.45 |  | 12.18 | [8 empty] | 15.72 |  |  |  |  | 0.00
2007 |  |  |  | 2718.74 |  |  | 8300 |  |  |  | 335 | [10 empty] | 93.83 |  |  |  | 93.95 | [5 empty] | 92.64 |  |  | 94.75 |  |  |  | 6.05 |  | 6.05 | [8 empty] | 0.00 |  |  |  |  | 0.12
2008 |  |  |  | 2481.26 |  |  | 7562 |  |  |  | 335 | [10 empty] | 85.27 |  |  |  | 85.27 | [5 empty] | 84.32 |  |  | 86.09 |  |  |  | 2.49 |  | 2.18 | [8 empty] | 12.55 |  |  |  |  | 0.00
2009 |  |  |  | 2397.18 |  |  | 7296 |  |  |  | 335 | [10 empty] | 82.88 |  |  |  | 82.88 | [5 empty] | 81.69 |  |  | 83.29 |  |  |  | 0.38 |  | 0.32 | [8 empty] | 16.80 |  |  |  |  | 0.00
2010 |  |  |  | 2782.75 |  |  | 8560 |  |  |  | 335 | [10 empty] | 95.52 |  |  |  | 95.52 | [5 empty] | 94.83 |  |  | 97.72 |  |  |  | 4.48 |  | 4.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 2334.46 |  |  | 7289 |  |  |  | 335 | [10 empty] | 79.63 |  |  |  | 80.28 | [5 empty] | 79.55 |  |  | 83.21 |  |  |  | 4.07 |  | 5.45 | [8 empty] | 14.27 |  |  |  |  | 0.65
2012 |  |  |  | 2477.36 |  |  | 7521 |  |  |  | 335 | [10 empty] | 84.15 |  |  |  | 84.15 | [5 empty] | 84.19 |  |  | 85.62 |  |  |  | 5.20 |  | 4.61 | [8 empty] | 11.24 |  |  |  |  | 0.00
2013 |  |  |  | 2449.53 |  |  | 7310 |  |  |  | 340 | [10 empty] | 82.55 |  |  |  | 83.29 | [5 empty] | 82.75 |  |  | 83.45 |  |  |  | 2.94 |  | 3.49 | [8 empty] | 13.22 |  |  |  |  | 0.73
2014 |  |  |  | 2631.71 |  |  | 7875 |  |  |  | 340 | [10 empty] | 88.78 |  |  |  | 89.28 | [5 empty] | 88.36 |  |  | 89.90 |  |  |  | 0.00 |  | 1.89 | [8 empty] | 8.83 |  |  |  |  | 0.50
2015 |  |  |  | 1951.35 |  |  | 6109 |  |  |  | 340 | [10 empty] | 66.00 |  |  |  | 66.03 | [5 empty] | 65.52 |  |  | 69.74 |  |  |  | 6.26 |  | 6.69 | [8 empty] | 27.28 |  |  |  |  | 0.03
2016 |  |  |  | 2476.82 |  |  | 7700 |  |  |  | 340 | [10 empty] | 83.27 |  |  |  | 83.27 | [5 empty] | 82.93 |  |  | 87.66 |  |  |  | 4.66 |  | 4.40 | [8 empty] | 12.33 |  |  |  |  | 0.00
2017 |  |  |  | 2359.66 |  |  | 7832 |  |  |  | 340 | [10 empty] | 79.70 |  |  |  | 79.70 | [5 empty] | 79.23 |  |  | 89.41 |  |  |  | 5.87 |  | 4.97 | [8 empty] | 15.33 |  |  |  |  | 0.00
2018 |  |  |  | 2274.09 |  |  | 7393 |  |  |  | 340 | [10 empty] | 76.27 |  |  |  | 76.27 | [5 empty] | 76.35 |  |  | 84.39 |  |  |  | 7.72 |  | 7.01 | [8 empty] | 16.73 |  |  |  |  | 0.00
2019 |  |  |  | 2392.40 |  |  | 7341 |  |  |  | 340 | [10 empty] | 80.33 |  |  |  | 80.33 | [5 empty] | 80.33 |  |  | 83.80 |  |  |  | 5.48 |  | 4.66 | [8 empty] | 15.01 |  |  |  |  | 0.00
2020 |  |  |  | 2680.41 |  |  | 8067 |  |  |  | 340 | [10 empty] | 89.75 |  |  |  | 89.75 | [5 empty] | 89.75 |  |  | 91.84 |  |  |  | 3.80 |  | 3.84 | [8 empty] | 6.41 |  |  |  |  | 0.00
2021 |  |  |  | 2318.78 |  |  | 7243 |  |  |  | 340 | [10 empty] | 77.85 |  |  |  | 78.38 | [5 empty] | 77.85 |  |  | 82.68 |  |  |  | 7.80 |  | 6.90 | [8 empty] | 14.72 |  |  |  |  | 0.53
2022 |  |  |  | 2034.01 |  |  | 6528 |  |  |  | 340 | [10 empty] | 68.29 |  |  |  | 68.34 | [5 empty] | 68.29 |  |  | 74.52 |  |  |  | 11.42 |  | 25.21 | [8 empty] | 6.45 |  |  |  |  | 0.05
2023 |  |  |  | 2197.12 |  |  | 6855 |  |  |  | 340 | [10 empty] | 73.77 |  |  |  | 74.46 | [5 empty] | 73.77 |  |  | 78.25 |  |  |  | 6.47 |  | 5.15 | [8 empty] | 20.40 |  |  |  |  | 0.69
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1974 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 94 | [14 empty] | 614
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 27
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 1764 | [14 empty] | 1125 |  |  |  | 11
E. |  | Testing of plant systems or components | [35 empty] | 9
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 29
H. |  | Nuclear regulatory requirements | [39 empty] | 60
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 47 | [19 empty] | 17
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 20
L. |  | Human factor related | [39 empty] | 38
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 2
Subtotal | [22 empty] | 1764 |  |  |  | 94 | [6 empty] | 47 |  |  |  | 1190 |  |  |  | 723 | [11 empty] | 39
Total | [22 empty] | 1905 | [14 empty] | 1952
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1974 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 92
12. |  |  | Reactor I&C Systems | [19 empty] | 48 | [14 empty] | 44
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 123
14. |  |  | Safety Systems | [34 empty] | 37
15. |  |  | Reactor Cooling Systems | [19 empty] | 46 | [14 empty] | 144
16. |  |  | Steam generation systems | [34 empty] | 45
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 9
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 19
31. |  |  | Turbine and auxiliaries | [34 empty] | 10
32. |  |  | Feedwater and Main Steam System | [34 empty] | 21
33. |  |  | Circulating Water System | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 7
42. |  |  | Electrical Power Supply Systems | [19 empty] | 47 | [14 empty] | 84
Total | [22 empty] | 141 | [14 empty] | 645
Highlights (2023)
01/01/2023 00:00 to 25/01/2023 00:00 - Power reduction due to a refueling machine intervention (80 %). 25/01/2023 00:00 to 28/01/2023 23:19 - Power reduction due to a refueling machine intervention (90 %). 28/01/2023 23:19 to 29/01/2023 21:50 - Power reduction due to a refueling machine intervention (95 %). 29/01/2023 21:50 to 24/02/2023 07:44 - Normal Operation. Losses due to plant performance 24/02/2023 07:44 to 24/02/2023 12:23 - Power reduction due to RM03D001 intervention. 24/02/2023 12:23 to 01/03/2023 15:59 - Normal Operation. Losses due to plant performance. 01/03/2023 15:59 to 03/03/2023 14:22 - Automatic Scram. Spurious trip of QF01D001. 03/03/2023 14:22 to 05/03/2023 22:15 - Power ramp up. 05/03/2023 22:15 to 23/04/2023 23:30 - Normal Operation. Losses due to plant performance. 23/04/2023 23:30 to 24/04/2023 06:30 - Power ramp down. 24/04/2023 06:30 to 25/04/2023 15:20 - Power reduction due to SD11W001 intervention. 25/04/2023 15:20 to 25/04/2023 21:50 - Power ramp up. 25/04/2023 21:50 to 25/05/2023 18:19 - Normal Operation. Losses due to plant performance. 25/05/2023 18:19 to 27/05/2023 17:42 - Automatic Scram. Load rejection due to power grid unavailability. 27/05/2023 17:42 to 29/05/2023 10:20 - Power ramp up. 29/05/2023 10:20 to 09/09/2023 00:21 - Normal Operation. Losses due to plant performance. 09/09/2023 00:21 to 21/11/2023 12:15 - 2023 programmed full maintenance. 21/11/2023 12:15 to 23/11/2023 11:38 - Power ramp up. 23/11/2023 11:38 to 02/12/2023 07:23 - Normal Operation. Losses due to plant performance. 02/12/2023 07:23 to 04/12/2023 07:01 - Automatic turbine trip - manual Scram due to perturbation in JH02 rack. 04/12/2023 07:01 to 05/12/2023 19:33 - Power Ramp up 05/12/2023 19:33 to 01/01/2024 00:00 - Normal Operation. Losses due to plant performance.

## ATUCHA-2
2023 Operating Experience
AR-3 | [8 empty] | ATUCHA-2 | [26 empty] | ARGENTINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Owner | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Reactor Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / PHWR KWU | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-07-13
Thermal power | [12 empty] | : |  |  | 2160 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-06-24
Gross electrical power | [12 empty] | : |  |  | 745 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-05-25
Reference unit power (net) | [12 empty] | : |  |  | 693 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 4.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 312.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.48
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7800 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.59
| Active core height/length [m] | [13 empty] | : |  |  | 5.3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 21
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 451 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 23.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 18 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 1541.93 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 5.7 %
Energy Availability Factor (EAF) | [18 empty] | : | 25.4 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.57 %
Unit Capability Factor (UCF) | [18 empty] | : | 25.99 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 72.44 %
Load Factor (LF) | [18 empty] | : | 25.4 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.59 %
Operating Factor (OF) | [18 empty] | : | 33.77 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 5802 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 18.49 |  |  |  | 306.28 |  |  | 408.67 |  |  | 366.46 | [9 empty] | 442.03 |  |  | 1541.93
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 3.59 |  |  |  | 61.38 |  |  | 79.26 |  |  | 73.45 | [9 empty] | 85.73 |  |  | 25.40
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 3.59 |  |  |  | 61.38 |  |  | 79.26 |  |  | 80.61 | [9 empty] | 85.73 |  |  | 25.99
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 3.59 |  |  |  | 61.38 |  |  | 79.26 |  |  | 73.45 | [9 empty] | 85.73 |  |  | 25.40
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 10.08 |  |  |  | 100.00 |  |  | 100.00 |  |  | 93.75 | [9 empty] | 100.00 |  |  | 33.77
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 32.30 |  |  |  | 22.03 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.70
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 1.71 |  |  |  | 17.35 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.57
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 94.70 |  |  |  | 21.27 |  |  | 20.74 |  |  | 19.39 | [9 empty] | 14.27 |  |  | 72.44
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 7.16 | [9 empty] | 0.00 |  |  | 0.59
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 28237.1 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 37.75 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 45.78 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 31.67 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 45.86 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 22.48 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 45.57 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.08 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 64.51 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 5200.54 |  |  | 8063 |  |  |  | 692 | [10 empty] | 84.64 |  |  |  | 84.64 | [5 empty] | 83.75 |  |  | 89.49 |  |  |  | 15.36 |  | 15.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 3356.61 |  |  | 5130 |  |  |  | 693 | [10 empty] | 56.27 |  |  |  | 56.27 | [5 empty] | 55.29 |  |  | 58.56 |  |  |  | 7.12 |  | 27.04 | [8 empty] | 16.68 |  |  |  |  | 0.00
2018 |  |  |  | 4178.88 |  |  | 6448 |  |  |  | 693 | [10 empty] | 68.84 |  |  |  | 68.84 | [5 empty] | 68.84 |  |  | 73.61 |  |  |  | 20.72 |  | 17.99 | [8 empty] | 13.17 |  |  |  |  | 0.00
2019 |  |  |  | 1748.39 |  |  | 7001 |  |  |  | 693 | [10 empty] | 28.85 |  |  |  | 28.85 | [5 empty] | 28.80 |  |  | 79.92 |  |  |  | 68.93 |  | 64.83 | [8 empty] | 6.32 |  |  |  |  | 0.00
2020 |  |  |  | 2421.87 |  |  | 6155 |  |  |  | 693 | [10 empty] | 39.79 |  |  |  | 39.79 | [5 empty] | 39.79 |  |  | 70.07 |  |  |  | 47.24 |  | 40.55 | [8 empty] | 19.67 |  |  |  |  | 0.00
2021 |  |  |  | 3510.88 |  |  | 7217 |  |  |  | 693 | [10 empty] | 57.83 |  |  |  | 57.83 | [5 empty] | 57.83 |  |  | 82.39 |  |  |  | 41.72 |  | 42.16 | [8 empty] | 0.00 |  |  |  |  | 0.00
2022 |  |  |  | 1259.03 |  |  | 3381 |  |  |  | 693 | [10 empty] | 20.74 |  |  |  | 20.74 | [5 empty] | 20.74 |  |  | 38.60 |  |  |  | 64.11 |  | 37.05 | [8 empty] | 42.21 |  |  |  |  | 0.00
2023 |  |  |  | 1541.93 |  |  | 2958 |  |  |  | 693 | [10 empty] | 25.40 |  |  |  | 25.99 | [5 empty] | 25.40 |  |  | 33.77 |  |  |  | 5.70 |  | 1.57 | [8 empty] | 72.44 |  |  |  |  | 0.59
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2016 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1322
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 5757 | [14 empty] | 1806
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 45 | [19 empty] | 6
Subtotal | [22 empty] | 5757 | [10 empty] | 45 |  |  |  | 1806 |  |  |  | 1322 | [11 empty] | 6
Total | [22 empty] | 5802 | [14 empty] | 3134
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2016 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 314
12. |  |  | Reactor I&C Systems | [34 empty] | 62
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 33
14. |  |  | Safety Systems | [34 empty] | 52
15. |  |  | Reactor Cooling Systems | [34 empty] | 480
16. |  |  | Steam generation systems | [34 empty] | 9
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 17
31. |  |  | Turbine and auxiliaries | [34 empty] | 251
32. |  |  | Feedwater and Main Steam System | [34 empty] | 26
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [37 empty] | 1252
Highlights (2023)
01/01/2023 0:00 al 28/08/2023 21:16 – Programmed shutdown due to reactor intervention 28/08/2023 21:16 al 28/09/2023 16:45 - Operation at reduced power due to reactor fill up. 28/08/2023 21:16 al 28/09/2023 16:45 - Operation at reduced power. Debris removal strategy in the primary cooling system. (85%). 28/09/2023 16:45 al 11/11/2023 01:41 - Operation at reduced power. Debris removal strategy in the primary cooling system. (85%). 11/11/2023 01:41 al 12/11/2023 22:33 – Reactor and turbine automatic trip. scram due to low JFB10/30AP001 pumps flow as e result of a 500 kV. Atucha-Gral. Rodriguez line disconnection. 12/11/2023 22:33 al 13/11/2023 13:10- Power ramp up. 13/11/2023 13:10 al 13/12/2023 06:03 - Operation at reduced power. Debris removal strategy in the primary cooling system. (85 %). 13/12/2023 06:03 al 01/01/2024 00:00 - Operation at reduced power. Debris removal strategy in the primary cooling system. (95 %).

## EMBALSE
2023 Operating Experience
AR-2 | [8 empty] | EMBALSE | [26 empty] | ARGENTINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Owner | [7 empty] | : | NASA (NUCLEOELECTRICA ARGENTINA S.A.)
Reactor Supplier | [7 empty] | : | AECL (ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | AMN (ANSALDO/Asgen)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-03-31
Thermal power | [12 empty] | : |  |  | 2064 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-04-24
Gross electrical power | [12 empty] | : |  |  | 656 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-01-19
Reference unit power (net) | [12 empty] | : |  |  | 608 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 312
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.125
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.7 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7190 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 6.28 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.62
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.75 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5224.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.95 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.05 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.95 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.04 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 98.08 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.98 %
Operating Factor (OF) | [18 empty] | : | 98.86 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 100 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 439.47 | 403.04 |  |  |  | 415.47 |  | 434.06 | [8 empty] | 451.38 |  |  | 438.81 | [6 empty] | 452.53 |  | 452.79 |  |  |  | 437.53 |  |  | 450.82 |  |  | 433.83 | [9 empty] | 414.34 |  |  | 5224.06
EAF [%] |  |  |  |  | 97.15 | 98.64 |  |  |  | 91.85 |  | 99.15 | [8 empty] | 99.78 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.95 |  |  | 99.66 |  |  | 99.10 | [9 empty] | 91.60 |  |  | 98.05
UCF [%] |  |  |  |  | 99.02 | 100.00 |  |  |  | 99.73 |  | 99.58 | [8 empty] | 99.78 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.95 |  |  | 99.66 |  |  | 99.10 | [9 empty] | 91.81 |  |  | 99.04
LF [%] |  |  |  |  | 97.15 | 98.64 |  |  |  | 91.85 |  | 99.15 | [8 empty] | 99.78 |  |  | 100.24 | [6 empty] | 100.04 |  | 100.10 |  |  |  | 99.95 |  |  | 99.66 |  |  | 99.10 | [9 empty] | 91.60 |  |  | 98.08
OF [%] |  |  |  |  | 99.87 | 100.00 |  |  |  | 93.41 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 93.28 |  |  | 98.86
FLR [%] |  |  |  |  | 0.98 | 0.00 |  |  |  | 0.27 |  | 0.41 | [8 empty] | 0.22 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.05 |  |  | 0.33 |  |  | 0.90 | [9 empty] | 8.05 |  |  | 0.95
UCL [%] |  |  |  |  | 0.98 | 0.00 |  |  |  | 0.27 |  | 0.41 | [8 empty] | 0.22 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.05 |  |  | 0.33 |  |  | 0.90 | [9 empty] | 8.04 |  |  | 0.95
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.01 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.14 |  |  | 0.01
XUF [%] |  |  |  |  | 1.87 | 1.36 |  |  |  | 7.88 |  | 0.42 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.22 |  |  | 0.98
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 156061.92 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.96 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.14 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.45 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.5 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.05 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.48 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.36 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.64 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 2527.07 |  |  | 6355 |  |  |  | 600 | [10 empty] | 68.74 |  |  |  | 68.74 | [5 empty] | 44.29 |  |  | 70.56 |  |  |  | 5.92 |  | 4.32 | [8 empty] | 26.93 |  |  |  |  | 0.00
1985 |  |  |  | 3778.57 |  |  | 8170 |  |  |  | 600 | [10 empty] | 93.44 |  |  |  | 93.44 | [5 empty] | 71.89 |  |  | 93.26 |  |  |  | 6.15 |  | 6.13 | [8 empty] | 0.43 |  |  |  |  | 0.00
1986 |  |  |  | 3061.67 |  |  | 5847 |  |  |  | 600 | [10 empty] | 66.34 |  |  |  | 67.12 | [5 empty] | 58.25 |  |  | 66.75 |  |  |  | 1.85 |  | 1.27 | [8 empty] | 31.62 |  |  |  |  | 0.78
1987 |  |  |  | 4577.05 |  |  | 7951 |  |  |  | 600 | [10 empty] | 87.92 |  |  |  | 87.92 | [5 empty] | 87.08 |  |  | 90.76 |  |  |  | 5.89 |  | 5.50 | [8 empty] | 6.58 |  |  |  |  | 0.00
1988 |  |  |  | 4560.58 |  |  | 7798 |  |  |  | 600 | [10 empty] | 88.78 |  |  |  | 88.79 | [5 empty] | 86.53 |  |  | 88.78 |  |  |  | 11.21 |  | 11.21 | [8 empty] | 0.00 |  |  |  |  | 0.01
1989 |  |  |  | 4658.98 |  |  | 7804 |  |  |  | 600 | [10 empty] | 89.11 |  |  |  | 90.09 | [5 empty] | 88.64 |  |  | 89.09 |  |  |  | 1.00 |  | 0.91 | [8 empty] | 9.00 |  |  |  |  | 0.98
1990 |  |  |  | 5000.74 |  |  | 8404 |  |  |  | 600 | [10 empty] | 95.10 |  |  |  | 96.49 | [5 empty] | 95.14 |  |  | 95.94 |  |  |  | 1.87 |  | 1.84 | [8 empty] | 1.67 |  |  |  |  | 1.38
1991 |  |  |  | 4498.81 |  |  | 7855 |  |  |  | 600 | [10 empty] | 85.76 |  |  |  | 89.68 | [5 empty] | 85.59 |  |  | 89.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.32 |  |  |  |  | 3.92
1992 |  |  |  | 4353.98 |  |  | 7440 |  |  |  | 600 | [10 empty] | 81.59 |  |  |  | 83.42 | [5 empty] | 82.61 |  |  | 84.70 |  |  |  | 1.12 |  | 0.95 | [8 empty] | 15.64 |  |  |  |  | 1.83
1993 |  |  |  | 4773.27 |  |  | 7956 |  |  |  | 600 | [10 empty] | 90.60 |  |  |  | 90.68 | [5 empty] | 90.82 |  |  | 90.82 |  |  |  | 0.73 |  | 0.67 | [8 empty] | 8.65 |  |  |  |  | 0.08
1994 |  |  |  | 5157.89 |  |  | 8575 |  |  |  | 600 | [10 empty] | 97.78 |  |  |  | 98.27 | [5 empty] | 98.13 |  |  | 97.89 |  |  |  | 1.69 |  | 1.69 | [8 empty] | 0.03 |  |  |  |  | 0.49
1995 |  |  |  | 3897.91 |  |  | 6541 |  |  |  | 600 | [10 empty] | 74.34 |  |  |  | 74.34 | [5 empty] | 74.16 |  |  | 74.67 |  |  |  | 5.54 |  | 4.36 | [8 empty] | 21.30 |  |  |  |  | 0.00
1996 |  |  |  | 4891.97 |  |  | 8176 |  |  |  | 600 | [10 empty] | 92.77 |  |  |  | 92.77 | [5 empty] | 92.82 |  |  | 93.08 |  |  |  | 1.38 |  | 1.30 | [8 empty] | 5.94 |  |  |  |  | 0.00
1997 |  |  |  | 4737.03 |  |  | 7821 |  |  |  | 600 | [10 empty] | 89.27 |  |  |  | 89.27 | [5 empty] | 90.13 |  |  | 89.28 |  |  |  | 0.54 |  | 0.48 | [8 empty] | 10.25 |  |  |  |  | 0.00
1998 |  |  |  | 4555.43 |  |  | 7629 |  |  |  | 600 | [10 empty] | 86.87 |  |  |  | 86.88 | [5 empty] | 86.67 |  |  | 87.09 |  |  |  | 4.13 |  | 3.75 | [8 empty] | 9.38 |  |  |  |  | 0.01
1999 |  |  |  | 5201.79 |  |  | 8700 |  |  |  | 598 | [10 empty] | 99.14 |  |  |  | 99.14 | [5 empty] | 99.30 |  |  | 99.32 |  |  |  | 0.73 |  | 0.73 | [8 empty] | 0.14 |  |  |  |  | 0.00
2000 |  |  |  | 4064.48 |  |  | 6837 |  |  |  | 643 | [10 empty] | 78.08 |  |  |  | 78.19 | [5 empty] | 71.96 |  |  | 77.83 |  |  |  | 8.13 |  | 6.92 | [8 empty] | 14.89 |  |  |  |  | 0.10
2001 |  |  |  | 5128.11 |  |  | 8564 |  |  |  | 600 | [10 empty] | 97.45 |  |  |  | 97.47 | [5 empty] | 97.57 |  |  | 97.76 |  |  |  | 2.29 |  | 2.28 | [8 empty] | 0.25 |  |  |  |  | 0.02
2002 |  |  |  | 4385.52 |  |  | 7401 |  |  |  | 600 | [10 empty] | 83.40 |  |  |  | 84.00 | [5 empty] | 83.44 |  |  | 84.49 |  |  |  | 0.86 |  | 0.72 | [8 empty] | 15.28 |  |  |  |  | 0.59
2003 |  |  |  | 5004.14 |  |  | 8367 |  |  |  | 600 | [10 empty] | 95.07 |  |  |  | 95.13 | [5 empty] | 95.21 |  |  | 95.51 |  |  |  | 4.58 |  | 4.57 | [8 empty] | 0.30 |  |  |  |  | 0.05
2004 |  |  |  | 4589.57 |  |  | 7704 |  |  |  | 600 | [10 empty] | 87.51 |  |  |  | 87.54 | [5 empty] | 87.08 |  |  | 87.70 |  |  |  | 1.27 |  | 1.12 | [8 empty] | 11.33 |  |  |  |  | 0.03
2005 |  |  |  | 4372.48 |  |  | 7341 |  |  |  | 600 | [10 empty] | 83.32 |  |  |  | 83.32 | [5 empty] | 83.19 |  |  | 83.80 |  |  |  | 0.00 |  | 0.43 | [8 empty] | 16.25 |  |  |  |  | 0.00
2006 |  |  |  | 5052.10 |  |  | 8455 |  |  |  | 600 | [10 empty] | 96.23 |  |  |  | 96.23 | [5 empty] | 96.12 |  |  | 96.52 |  |  |  | 3.66 |  | 3.66 | [8 empty] | 0.11 |  |  |  |  | 0.00
2007 |  |  |  | 4003.72 |  |  | 6771 |  |  |  | 600 | [10 empty] | 76.51 |  |  |  | 76.51 | [5 empty] | 76.17 |  |  | 77.29 |  |  |  | 6.19 |  | 5.53 | [8 empty] | 17.96 |  |  |  |  | 0.00
2008 |  |  |  | 4368.61 |  |  | 7382 |  |  |  | 600 | [10 empty] | 82.89 |  |  |  | 82.89 | [5 empty] | 82.89 |  |  | 84.04 |  |  |  | 5.24 |  | 4.65 | [8 empty] | 12.46 |  |  |  |  | 0.00
2009 |  |  |  | 5192.43 |  |  | 8705 |  |  |  | 600 | [10 empty] | 98.79 |  |  |  | 98.79 | [5 empty] | 98.78 |  |  | 99.36 |  |  |  | 0.78 |  | 0.78 | [8 empty] | 0.44 |  |  |  |  | 0.00
2010 |  |  |  | 3908.69 |  |  | 6701 |  |  |  | 600 | [10 empty] | 74.37 |  |  |  | 74.86 | [5 empty] | 74.37 |  |  | 76.50 |  |  |  | 6.11 |  | 4.87 | [8 empty] | 20.26 |  |  |  |  | 0.50
2011 |  |  |  | 3559.35 |  |  | 7405 |  |  |  | 600 | [10 empty] | 67.72 |  |  |  | 67.72 | [5 empty] | 67.72 |  |  | 84.53 |  |  |  | 0.69 |  | 0.47 | [8 empty] | 31.81 |  |  |  |  | 0.00
2012 |  |  |  | 3425.53 |  |  | 7214 |  |  |  | 600 | [10 empty] | 65.07 |  |  |  | 65.07 | [5 empty] | 65.00 |  |  | 82.13 |  |  |  | 0.11 |  | 0.07 | [8 empty] | 34.86 |  |  |  |  | 0.00
2013 |  |  |  | 3285.69 |  |  | 6841 |  |  |  | 600 | [10 empty] | 69.65 |  |  |  | 69.65 | [5 empty] | 62.51 |  |  | 78.09 |  |  |  | 1.31 |  | 0.92 | [8 empty] | 29.43 |  |  |  |  | 0.00
2014 |  |  |  | 1533.11 |  |  | 3678 |  |  |  | 600 | [10 empty] | 99.79 |  |  |  | 99.79 | [5 empty] | 29.17 |  |  | 41.99 |  |  |  | 0.14 |  | 0.14 | [8 empty] | 0.07 |  |  |  |  | 0.00
2015 |  |  |  | 641.36 |  |  | 1564 |  |  |  | 600 | [10 empty] | 99.78 |  |  |  | 99.78 | [5 empty] | 12.20 |  |  | 17.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.22 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 600 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 600 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 600 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 3786.17 |  |  | 7051 |  |  |  | 608 | [10 empty] | 71.76 |  |  |  | 71.76 | [5 empty] | 71.09 |  |  | 80.49 |  |  |  | 3.80 |  | 2.83 | [8 empty] | 25.41 |  |  |  |  | 0.00
2020 |  |  |  | 4910.14 |  |  | 8447 |  |  |  | 608 | [10 empty] | 91.88 |  |  |  | 91.93 | [5 empty] | 91.94 |  |  | 96.16 |  |  |  | 6.33 |  | 6.22 | [8 empty] | 1.85 |  |  |  |  | 0.05
2021 |  |  |  | 4340.06 |  |  | 7227 |  |  |  | 608 | [10 empty] | 81.49 |  |  |  | 81.70 | [5 empty] | 81.49 |  |  | 82.50 |  |  |  | 3.56 |  | 3.01 | [8 empty] | 15.29 |  |  |  |  | 0.21
2022 |  |  |  | 4176.48 |  |  | 6993 |  |  |  | 608 | [10 empty] | 78.42 |  |  |  | 80.73 | [5 empty] | 78.42 |  |  | 79.83 |  |  |  | 2.96 |  | 2.46 | [8 empty] | 16.81 |  |  |  |  | 2.32
2023 |  |  |  | 5224.06 |  |  | 8660 |  |  |  | 608 | [10 empty] | 98.05 |  |  |  | 99.04 | [5 empty] | 98.08 |  |  | 98.86 |  |  |  | 0.95 |  | 0.95 | [8 empty] | 0.01 |  |  |  |  | 0.98
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1984 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 52 | [14 empty] | 209
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 88
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 683
E. |  | Testing of plant systems or components | [35 empty] | 36 |  |  |  | 1
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 686
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 49 | [19 empty] | 16
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 16
L. |  | Human factor related | [39 empty] | 2
M. |  | Governmental requirements or court decisions | [51 empty] | 307
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 5
Z. |  | Other | [39 empty] | 2
Subtotal | [26 empty] | 52 | [6 empty] | 49 |  |  |  | 1493 |  |  |  | 215 | [11 empty] | 345
Total | [22 empty] | 101 | [14 empty] | 2053
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1984 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [19 empty] | 1 | [14 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 30
14. |  |  | Safety Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 10
16. |  |  | Steam generation systems | [34 empty] | 58
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [19 empty] | 51 | [14 empty] | 26
32. |  |  | Feedwater and Main Steam System | [34 empty] | 20
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 37
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [22 empty] | 52 | [14 empty] | 213
Highlights (2023)
R1 1/1/2023 00:00 a 9/1/2023 00:11 Environmental condition: seasonal variation in cooling water temperature R2 9/1/2023 00:11 a 9/1/2023 20:58 4313 P531/P532 pumps out of service due to steam losses in 4313 P532 R3 9/1/2023 20:58 a 18/1/2023 1:22 Environmental condition: seasonal variation in cooling water temperature S1 18/1/2023 1:22 a 18/1/2023 2:27 Spurious trip of channel E of the SP N°1 during execution of test. Activation of SP N°1 R4 18/1/2023 2:27 a 19/1/2023 23:11 Power ramp up due to full outage S1 R5 19/1/2023 23:11 a 1/3/2023 16:32 Environmental condition: seasonal variation in cooling water temperature S2 1/3/2023 16:32 a 3/3/2023 17:19 Activation of SP N° 1 due to disturbances in the power grid R6 3/3/2023 17:19 a 3/3/2023 20:47 Power ramp up due to full outage S2. R7 3/3/2023 20:47 a 3/3/2023 22:15 Trip of Channel F of SP N° 1 during power ramp up due to low level in SG's. R8 3/3/2023 22:15 a 5/3/2023 00:50 Power ramp up due to full outage S2 R9 5/3/2023 00:50 a 6/3/2023 16:20 Environmental condition: seasonal variation in cooling water temperature R10 6/3/2023 16:20 a 6/3/2023 17:00 Failure 63611 FT3, Steam generator N° 3 flow transmitter. R11 6/3/2023 17:00 a 23/3/2023 00:48 Environmental condition: seasonal variation in cooling water temperature R12 23/3/2023 00:48 a 23/3/2023 17:27 4313 P103B pump out of service due to mechanic seal failure. R13 23/3/2023 17:27 a 2/4/2023 8:15 Environmental condition: seasonal variation in cooling water temperature R14 28/3/2023 00:30 a 2/4/2023 8:15 4313 P103B pump out of service due to mechanic seal failure. R15 2/4/2023 8:15 a 2/4/2023 8:45 Turbine control valves test (PF-41100-08) R16 2/4/2023 8:45 a 2/5/2023 00:00 Environmental condition: seasonal variation in cooling water temperature R17 2/4/2023 8:45 a 31/5/2023 12:48 4313 P103B pump out of service due to mechanic seal failure. R18 21/9/2023 7:38 a 21/9/2023 8:12 Turbine control valves test (PF-41100-08) R19 25/9/2023 00:45 a 25/9/2023 8:02 4313 9531/9532 pumps F/S and Set back. during work protection application. R20 1/10/2023 00:00 a 5/10/2023 8:15 Unknown internal causes R21 5/10/2023 8:15 a 5/102023 17:45 Planned repair of 64113 LCV593 R22 5/10/2023 17:45 a 1/11/2023 00:27 Unknown internal causes R23 1/11/2023 00:27 a 1/11/2023 16:50 Failure in 64312 LCV46, level control valve R24 1/11/2023 16:50 a 5/12/2023 16:30 Unknown internal causes R25 5/12/2023 16:30 a 6/12/2023 19:11 Maintenance in 64113 LCV594, level control valve R26 6/12/2023 19:11 a 7/12/2023 8:15 Unknown internal causes R27 7/12/2023 8:15 a 7/12/2023 8:30 Turbine control valves test (PF-14400-08) R28 7/12/2023 8:30 a 19/12/2023 16:35 Unknown internal causes R29 19/12/2023 16:35 a 21/12/2023 1:45 Planned repair of 64113 LCV593 R30 21/12/2023 1:45 a 21/12/2023 11:56 Environmental condition: seasonal variation in cooling water temperature S3 21/12/2023 11:56 a 23/12/2023 14:27 Manual Scram of SP N°1 due to failure in DEHC system. R31 23/12/2023 14:27 a 24/12/2023 7:46 Power ramp up R32 24/12/2023 7:46 a 1/1/2024 00:00 Environmental condition: seasonal variation in cooling water temperature