## ARMENIAN-2
2023 Operating Experience
AM-19 | [8 empty] | ARMENIAN-2 | [26 empty] | ARMENIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | ANPPCJSC (Closed Joint Stock Company Armenian NPP)
Owner | [7 empty] | : | M.E. (Ministry of Territorial Administration and Infrastructure)
Reactor Supplier | [7 empty] | : | FAEA (Federal Atomic Energy Agency)
Turbine Supplier | [7 empty] | : | ElTM ("Electrotiazhmash" Kharkiv)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-270 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-07-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-01-05
Gross electrical power | [12 empty] | : |  |  | 448 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-05-03
Reference unit power (net) | [12 empty] | : |  |  | 416 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 295.8
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2512.03 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 9.58 %
Energy Availability Factor (EAF) | [18 empty] | : | 67.31 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.44 %
Unit Capability Factor (UCF) | [18 empty] | : | 70.21 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 22.35 %
Load Factor (LF) | [18 empty] | : | 68.93 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.9 %
Operating Factor (OF) | [18 empty] | : | 74.09 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2270 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 305.69 | 272.86 |  |  |  | 293.98 |  | 283.89 | [8 empty] | 38.33 |  |  | 0.00 | [6 empty] | 28.18 |  | 176.44 |  |  |  | 263.25 |  |  | 290.56 |  |  | 259.94 | [9 empty] | 298.92 |  |  | 2512.03
EAF [%] |  |  |  |  | 97.20 | 96.32 |  |  |  | 90.14 |  | 89.42 | [8 empty] | 12.10 |  |  | 0.00 | [6 empty] | 9.82 |  | 58.24 |  |  |  | 84.54 |  |  | 91.27 |  |  | 86.09 | [9 empty] | 95.09 |  |  | 67.31
UCF [%] |  |  |  |  | 99.77 | 99.29 |  |  |  | 96.39 |  | 96.03 | [8 empty] | 12.90 |  |  | 0.00 | [6 empty] | 10.51 |  | 61.70 |  |  |  | 89.60 |  |  | 94.88 |  |  | 88.33 | [9 empty] | 95.73 |  |  | 70.21
LF [%] |  |  |  |  | 98.77 | 97.61 |  |  |  | 94.98 |  | 94.78 | [8 empty] | 12.38 |  |  | 0.00 | [6 empty] | 9.10 |  | 57.01 |  |  |  | 87.89 |  |  | 93.88 |  |  | 86.78 | [9 empty] | 96.58 |  |  | 68.93
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 13.17 |  |  | 0.00 | [6 empty] | 11.42 |  | 67.07 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 74.09
FLR [%] |  |  |  |  | 0.23 | 0.71 |  |  |  | 3.61 |  | 3.97 | [8 empty] | 10.79 |  |  | 0.00 | [6 empty] | 80.41 |  | 32.93 |  |  |  | 3.18 |  |  | 1.16 |  |  | 0.00 | [9 empty] | 0.28 |  |  | 9.58
UCL [%] |  |  |  |  | 0.23 | 0.71 |  |  |  | 3.61 |  | 3.97 | [8 empty] | 1.56 |  |  | 0.00 | [6 empty] | 43.15 |  | 30.30 |  |  |  | 2.94 |  |  | 1.12 |  |  | 0.00 | [9 empty] | 0.27 |  |  | 7.44
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 85.54 |  |  | 100.00 | [6 empty] | 46.34 |  | 8.00 |  |  |  | 7.47 |  |  | 4.00 |  |  | 11.67 | [9 empty] | 4.00 |  |  | 22.35
XUF [%] |  |  |  |  | 2.57 | 2.97 |  |  |  | 6.25 |  | 6.61 | [8 empty] | 0.80 |  |  | 0.00 | [6 empty] | 0.69 |  | 3.47 |  |  |  | 5.05 |  |  | 3.62 |  |  | 2.24 | [9 empty] | 0.65 |  |  | 2.90
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 82950.68 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.4 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 65.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.45 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 67.45 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 29.09 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.14 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.17 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.61 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | Data not provided
1981 |  |  |  | "
1982 |  |  |  | "
1983 |  |  |  | "
1984 |  |  |  | "
1985 |  |  |  | "
1986 |  |  |  | "
1987 |  |  |  | 2629.08 |  |  | 7040 |  |  |  | 408 | [10 empty] | 79.34 |  |  |  | 79.34 | [5 empty] | 73.56 |  |  | 80.37 |  |  |  | 10.91 |  | 9.71 | [8 empty] | 10.95 |  |  |  |  | 0.00
1988 |  |  |  | 2254.53 |  |  | 6741 |  |  |  | 376 | [10 empty] | 73.40 |  |  |  | 73.40 | [5 empty] | 68.26 |  |  | 76.74 |  |  |  | 7.07 |  | 5.58 | [8 empty] | 21.02 |  |  |  |  | 0.00
1989 |  |  |  | 671.28 |  |  | 1838 |  |  |  | 376 | [10 empty] | 99.58 |  |  |  | 99.58 | [5 empty] | 82.69 |  |  | 85.13 |  |  |  | 0.42 |  | 0.42 | [8 empty] | 0.00 |  |  |  |  | 0.00
1990 |  |  |  | Data not available - Suspended Operation
1991 |  |  |  | "
1992 |  |  |  | "
1993 |  |  |  | "
1994 |  |  |  | "
1995 |  |  |  | Data not provided
1996 |  |  |  | 2097.98 |  |  | 7561 |  |  |  | 376 | [10 empty] | 63.60 |  |  |  | 86.25 | [5 empty] | 63.52 |  |  | 86.08 |  |  |  | 0.42 |  | 0.37 | [8 empty] | 13.39 |  |  |  |  | 22.64
1997 |  |  |  | 1429.96 |  |  | 5700 |  |  |  | 376 | [10 empty] | 43.41 |  |  |  | 43.41 | [5 empty] | 43.41 |  |  | 65.07 |  |  |  | 1.59 |  | 0.70 | [8 empty] | 55.88 |  |  |  |  | 0.00
1998 |  |  |  | 1416.47 |  |  | 6408 |  |  |  | 376 | [10 empty] | 44.62 |  |  |  | 44.62 | [5 empty] | 43.00 |  |  | 73.15 |  |  |  | 0.11 |  | 0.05 | [8 empty] | 55.33 |  |  |  |  | 0.00
1999 |  |  |  | 1890.37 |  |  | 6193 |  |  |  | 376 | [10 empty] | 57.39 |  |  |  | 57.39 | [5 empty] | 57.39 |  |  | 70.70 |  |  |  | 0.41 |  | 0.23 | [8 empty] | 42.37 |  |  |  |  | 0.00
2000 |  |  |  | 1841.51 |  |  | 5699 |  |  |  | 376 | [10 empty] | 55.77 |  |  |  | 55.78 | [5 empty] | 55.76 |  |  | 64.88 |  |  |  | 2.17 |  | 1.24 | [8 empty] | 42.99 |  |  |  |  | 0.01
2001 |  |  |  | 1815.41 |  |  | 5660 |  |  |  | 376 | [10 empty] | 55.11 |  |  |  | 55.12 | [5 empty] | 55.12 |  |  | 64.61 |  |  |  | 0.57 |  | 0.32 | [8 empty] | 44.57 |  |  |  |  | 0.01
2002 |  |  |  | 2078.90 |  |  | 6961 |  |  |  | 376 | [10 empty] | 63.20 |  |  |  | 63.31 | [5 empty] | 63.12 |  |  | 79.46 |  |  |  | 0.87 |  | 0.56 | [8 empty] | 36.13 |  |  |  |  | 0.11
2003 |  |  |  | 1997.55 |  |  | 6120 |  |  |  | 376 | [10 empty] | 60.65 |  |  |  | 63.39 | [5 empty] | 60.65 |  |  | 69.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.61 |  |  |  |  | 2.74
2004 |  |  |  | 2196.58 |  |  | 7135 |  |  |  | 376 | [10 empty] | 64.18 |  |  |  | 70.29 | [5 empty] | 66.51 |  |  | 81.23 |  |  |  | 0.75 |  | 0.89 | [8 empty] | 28.82 |  |  |  |  | 6.11
2005 |  |  |  | 2504.49 |  |  | 7658 |  |  |  | 376 | [10 empty] | 76.25 |  |  |  | 76.25 | [5 empty] | 76.04 |  |  | 87.42 |  |  |  | 3.26 |  | 2.57 | [8 empty] | 21.18 |  |  |  |  | 0.00
2006 |  |  |  | 2421.62 |  |  | 7632 |  |  |  | 376 | [10 empty] | 76.13 |  |  |  | 76.13 | [5 empty] | 73.52 |  |  | 87.12 |  |  |  | 3.15 |  | 2.48 | [8 empty] | 21.39 |  |  |  |  | 0.00
2007 |  |  |  | 2347.83 |  |  | 7447 |  |  |  | 376 | [10 empty] | 73.81 |  |  |  | 73.81 | [5 empty] | 71.28 |  |  | 85.01 |  |  |  | 6.26 |  | 4.93 | [8 empty] | 21.26 |  |  |  |  | 0.00
2008 |  |  |  | 2265.89 |  |  | 7013 |  |  |  | 376 | [10 empty] | 69.01 |  |  |  | 69.01 | [5 empty] | 68.61 |  |  | 79.84 |  |  |  | 3.79 |  | 2.72 | [8 empty] | 28.27 |  |  |  |  | 0.00
2009 |  |  |  | 2290.42 |  |  | 7408 |  |  |  | 375 | [10 empty] | 69.85 |  |  |  | 71.28 | [5 empty] | 69.72 |  |  | 84.57 |  |  |  | 7.74 |  | 6.32 | [8 empty] | 22.39 |  |  |  |  | 1.43
2010 |  |  |  | 2286.54 |  |  | 7535 |  |  |  | 375 | [10 empty] | 69.70 |  |  |  | 71.78 | [5 empty] | 69.61 |  |  | 86.02 |  |  |  | 7.26 |  | 5.62 | [8 empty] | 22.61 |  |  |  |  | 2.08
2011 |  |  |  | 2356.84 |  |  | 7552 |  |  |  | 375 | [10 empty] | 73.70 |  |  |  | 75.49 | [5 empty] | 71.75 |  |  | 86.21 |  |  |  | 3.76 |  | 3.64 | [8 empty] | 20.87 |  |  |  |  | 1.79
2012 |  |  |  | 2123.50 |  |  | 7052 |  |  |  | 375 | [10 empty] | 66.39 |  |  |  | 68.31 | [5 empty] | 64.47 |  |  | 80.28 |  |  |  | 4.50 |  | 3.22 | [8 empty] | 28.47 |  |  |  |  | 1.92
2013 |  |  |  | 2167.63 |  |  | 7237 |  |  |  | 375 | [10 empty] | 64.44 |  |  |  | 66.45 | [5 empty] | 65.99 |  |  | 82.61 |  |  |  | 14.48 |  | 11.25 | [8 empty] | 22.30 |  |  |  |  | 2.01
2014 |  |  |  | 2265.64 |  |  | 7542 |  |  |  | 375 | [10 empty] | 67.32 |  |  |  | 70.51 | [5 empty] | 68.97 |  |  | 86.10 |  |  |  | 3.94 |  | 2.89 | [8 empty] | 26.60 |  |  |  |  | 3.19
2015 |  |  |  | 2571.10 |  |  | 7859 |  |  |  | 375 | [10 empty] | 77.43 |  |  |  | 79.90 | [5 empty] | 78.27 |  |  | 89.71 |  |  |  | 1.91 |  | 1.55 | [8 empty] | 18.55 |  |  |  |  | 2.47
2016 |  |  |  | 2194.85 |  |  | 6756 |  |  |  | 375 | [10 empty] | 65.45 |  |  |  | 67.82 | [5 empty] | 66.63 |  |  | 76.91 |  |  |  | 1.76 |  | 5.72 | [8 empty] | 26.45 |  |  |  |  | 2.37
2017 |  |  |  | 2411.39 |  |  | 7341 |  |  |  | 375 | [10 empty] | 71.41 |  |  |  | 73.43 | [5 empty] | 73.41 |  |  | 83.80 |  |  |  | 3.19 |  | 2.42 | [8 empty] | 24.15 |  |  |  |  | 2.02
2018 |  |  |  | 1898.08 |  |  | 7169 |  |  |  | 375 | [10 empty] | 55.75 |  |  |  | 56.87 | [5 empty] | 57.78 |  |  | 81.84 |  |  |  | 3.81 |  | 2.25 | [8 empty] | 40.88 |  |  |  |  | 1.12
2019 |  |  |  | 2028.96 |  |  | 6252 |  |  |  | 375 | [10 empty] | 57.15 |  |  |  | 57.76 | [5 empty] | 61.76 |  |  | 71.37 |  |  |  | 5.62 |  | 3.44 | [8 empty] | 38.80 |  |  |  |  | 0.60
2020 |  |  |  | 2551.80 |  |  | 7295 |  |  |  | 415 | [10 empty] | 70.30 |  |  |  | 73.30 | [5 empty] | 70.00 |  |  | 83.05 |  |  |  | 6.29 |  | 4.92 | [8 empty] | 21.78 |  |  |  |  | 3.00
2021 |  |  |  | 1850.04 |  |  | 5028 |  |  |  | 448 | [10 empty] | 49.46 |  |  |  | 51.55 | [5 empty] | 50.22 |  |  | 57.40 |  |  |  | 2.74 |  | 5.78 | [8 empty] | 42.67 |  |  |  |  | 2.09
2022 |  |  |  | 2630.85 |  |  | 7110 |  |  |  | 416 | [10 empty] | 68.17 |  |  |  | 72.88 | [5 empty] | 72.19 |  |  | 81.16 |  |  |  | 5.40 |  | 4.16 | [8 empty] | 22.96 |  |  |  |  | 4.72
2023 |  |  |  | 2512.03 |  |  | 6490 |  |  |  | 416 | [10 empty] | 67.31 |  |  |  | 70.21 | [5 empty] | 68.93 |  |  | 74.09 |  |  |  | 9.58 |  | 7.44 | [8 empty] | 22.35 |  |  |  |  | 2.90
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1980 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 566 | [14 empty] | 112
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1704 | [14 empty] | 1516 |  |  |  | 14
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 130
E. |  | Testing of plant systems or components | [39 empty] | 2
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 52
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 9
L. |  | Human factor related | [39 empty] | 2
Z. |  | Other | [39 empty] | 14
Subtotal | [22 empty] | 1704 |  |  |  | 566 | [10 empty] | 1698 |  |  |  | 144 | [11 empty] | 9
Total | [22 empty] | 2270 | [14 empty] | 1851
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1980 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 26
12. |  |  | Reactor I&C Systems | [34 empty] | 11
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [19 empty] | 566 | [14 empty] | 33
16. |  |  | Steam generation systems | [34 empty] | 7
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 22
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 566 | [14 empty] | 116
Highlights (2023)
Highlights for the year 2023 On May 5, 2023 at 01:45 the ANPP Unit 2 was shut down for annual outage-2023 which will last 75 days. In addition to the scope of the annual outage, as part of outage-2023 a number of activities were implemented which were aimed at improving the safety of the plant operation. The employees of the main departments of the ANPP, as well as other experienced specialists from the Russian Federation, Croatia, the Czech Republic, Slovakia and other countries were involved in the work. The following main activities are scheduled to be performed during outage-2023. - reactor intermediate maintenance with a complete core unloading, - major overhaul of reactor coolant pumps ?2 and ?3, - major overhaul of steam generators ?2 and ?3, - routine maintenance of turbine generators, - routine maintenance of steam turbines. - activities on replacement of Unit 2 2RCP-1÷6 pump units wraparound pipelines, - improvement of reactor facility confinement leak-tightness, - installation of a new system of boron unit air-cooling, - installation/dismantling of the I and II channel ELCS pipelines and support & suspension system in the turbine hall, - installation/dismantling of sections of the circulating water pipelines to cooling tower ?1 and other activities were performed. - modernization of some of the safety systems will be carried out, such as replacing the pipelines of the Essential Load Cooling System. - In the framework of the ANPP Unit 2 life extension project, during outage-2023 MAW type valves installed in the unit systems were replaced with valves of a new type and units 2?-1, 2?-2, 2?-4 of the air-cooling systems of the reactor facility confinement were replaced. - installation of auxiliary equipment of turbine generators ?3 and ?4 was performed. Currently activities are underway to prepare Unit 2 for start-up after the outage. All the activities included in outage schedule 2023 have been completed and the unit was connected to the grid on 15 of July, 2023, Unit 2 of the Armenian NPP was put into operation; activities of planned outage were finished 3 days before planned date.