## DOEL-1
2023 Operating Experience
BE-2 | [8 empty] | DOEL-1 | [26 empty] | BELGIUM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EBL+EDF (ENGIE ELECTRABEL + EDF BELGIUM + EDF LUMINUS)
Owner | [7 empty] | : | IND.DOEL (INDIVISION DOEL (EBES , INTERCOM , UNERG))
Reactor Supplier | [7 empty] | : | ACECOWEN (ACECOWEN (ACEC-COCKERILL-WESTINGHOUSE))
Turbine Supplier | [7 empty] | : | COC/ACEC (TURBINE: COCKERILL-TOSI ; ALTERNATOR: ACEC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1969-07-01
Thermal power | [12 empty] | : |  |  | 1311 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-08-28
Gross electrical power | [12 empty] | : |  |  | 454 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-02-15
Reference unit power (net) | [12 empty] | : |  |  | 445 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.73
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.08
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 2.9
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.8
| Active core height/length [m] | [13 empty] | : |  |  | 2.44 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 22.22 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3540.07 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.98 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.9 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.84 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.08 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.09 %
Load Factor (LF) | [18 empty] | : | 90.81 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.17 %
Operating Factor (OF) | [18 empty] | : | 92.18 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 685 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 336.59 | 304.02 |  |  |  | 334.98 |  | 322.86 | [8 empty] | 314.24 |  |  | 74.14 | [6 empty] | 269.31 |  | 296.57 |  |  |  | 318.73 |  |  | 333.97 |  |  | 323.66 | [9 empty] | 311.00 |  |  | 3540.07
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 94.72 |  |  | 23.14 | [6 empty] | 81.34 |  | 89.58 |  |  |  | 99.48 |  |  | 100.00 |  |  | 98.83 | [9 empty] | 91.50 |  |  | 89.90
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 29.14 | [6 empty] | 82.57 |  | 90.59 |  |  |  | 100.00 |  |  | 100.00 |  |  | 98.83 | [9 empty] | 91.50 |  |  | 91.08
LF [%] |  |  |  |  | 101.66 | 101.67 |  |  |  | 101.31 |  | 100.77 | [8 empty] | 94.91 |  |  | 23.14 | [6 empty] | 81.34 |  | 89.58 |  |  |  | 99.48 |  |  | 100.74 |  |  | 101.02 | [9 empty] | 93.93 |  |  | 90.81
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 29.44 | [6 empty] | 85.48 |  | 98.12 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 92.61 |  |  | 92.18
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 3.05 |  | 9.41 |  |  |  | 0.00 |  |  | 0.00 |  |  | 1.15 | [9 empty] | 8.50 |  |  | 1.98
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 2.60 |  | 9.41 |  |  |  | 0.00 |  |  | 0.00 |  |  | 1.15 | [9 empty] | 8.50 |  |  | 1.84
PUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 70.86 | [6 empty] | 14.83 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 7.09
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.28 |  |  | 6.00 | [6 empty] | 1.23 |  | 1.01 |  |  |  | 0.52 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.17
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 143911.9 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.04 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.87 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.01 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.69 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.3 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.35 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.82 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.88 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 2557.60 |  |  | 7257 |  |  |  | 392 | [10 empty] | 75.78 |  |  |  | 75.78 | [5 empty] | 75.77 |  |  | 81.78 |  |  |  | 24.22 |  | 24.22 | [8 empty] | 0.00 |  |  |  |  | 0.00
1976 |  |  |  | 2667.10 |  |  | 6928 |  |  |  | 395 | [10 empty] | 75.48 |  |  |  | 75.48 | [5 empty] | 76.87 |  |  | 78.87 |  |  |  | 12.67 |  | 10.95 | [8 empty] | 13.57 |  |  |  |  | 0.00
1977 |  |  |  | 2830.00 |  |  | 7332 |  |  |  | 395 | [10 empty] | 81.77 |  |  |  | 81.77 | [5 empty] | 81.79 |  |  | 83.70 |  |  |  | 8.45 |  | 7.55 | [8 empty] | 10.67 |  |  |  |  | 0.00
1978 |  |  |  | 2731.20 |  |  | 7071 |  |  |  | 395 | [10 empty] | 78.89 |  |  |  | 78.89 | [5 empty] | 78.93 |  |  | 80.72 |  |  |  | 0.99 |  | 0.78 | [8 empty] | 20.33 |  |  |  |  | 0.00
1979 |  |  |  | 3037.00 |  |  | 7812 |  |  |  | 395 | [10 empty] | 86.38 |  |  |  | 86.38 | [5 empty] | 87.77 |  |  | 89.18 |  |  |  | 1.45 |  | 1.27 | [8 empty] | 12.35 |  |  |  |  | 0.00
1980 |  |  |  | 2901.00 |  |  | 7596 |  |  |  | 395 | [10 empty] | 84.36 |  |  |  | 84.36 | [5 empty] | 83.61 |  |  | 86.48 |  |  |  | 2.96 |  | 2.57 | [8 empty] | 13.07 |  |  |  |  | 0.00
1981 |  |  |  | 2946.00 |  |  | 7644 |  |  |  | 395 | [10 empty] | 85.00 |  |  |  | 85.00 | [5 empty] | 85.14 |  |  | 87.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.00 |  |  |  |  | 0.00
1982 |  |  |  | 3184.50 |  |  | 8103 |  |  |  | 395 | [10 empty] | 91.24 |  |  |  | 91.24 | [5 empty] | 92.03 |  |  | 92.50 |  |  |  | 1.45 |  | 1.34 | [8 empty] | 7.42 |  |  |  |  | 0.00
1983 |  |  |  | 2823.00 |  |  | 7316 |  |  |  | 393 | [10 empty] | 81.78 |  |  |  | 81.78 | [5 empty] | 82.00 |  |  | 83.52 |  |  |  | 17.98 |  | 17.92 | [8 empty] | 0.30 |  |  |  |  | 0.00
1984 |  |  |  | 3129.00 |  |  | 7988 |  |  |  | 393 | [10 empty] | 90.22 |  |  |  | 90.22 | [5 empty] | 90.64 |  |  | 90.94 |  |  |  | 1.88 |  | 1.73 | [8 empty] | 8.06 |  |  |  |  | 0.00
1985 |  |  |  | 2896.32 |  |  | 7330 |  |  |  | 392 | [10 empty] | 82.44 |  |  |  | 82.44 | [5 empty] | 84.34 |  |  | 83.68 |  |  |  | 2.58 |  | 2.18 | [8 empty] | 15.38 |  |  |  |  | 0.00
1986 |  |  |  | 2685.93 |  |  | 7040 |  |  |  | 392 | [10 empty] | 78.85 |  |  |  | 79.15 | [5 empty] | 78.22 |  |  | 80.37 |  |  |  | 3.69 |  | 3.03 | [8 empty] | 17.82 |  |  |  |  | 0.30
1987 |  |  |  | 2928.35 |  |  | 7306 |  |  |  | 400 | [10 empty] | 85.44 |  |  |  | 85.45 | [5 empty] | 83.57 |  |  | 83.40 |  |  |  | 3.59 |  | 3.18 | [8 empty] | 11.37 |  |  |  |  | 0.01
1988 |  |  |  | 2694.15 |  |  | 7686 |  |  |  | 400 | [10 empty] | 81.28 |  |  |  | 86.59 | [5 empty] | 76.68 |  |  | 87.50 |  |  |  | 1.53 |  | 1.35 | [8 empty] | 12.06 |  |  |  |  | 5.31
1989 |  |  |  | 2513.10 |  |  | 6475 |  |  |  | 400 | [10 empty] | 71.87 |  |  |  | 73.57 | [5 empty] | 71.72 |  |  | 73.92 |  |  |  | 9.59 |  | 7.81 | [8 empty] | 18.63 |  |  |  |  | 1.70
1990 |  |  |  | 2859.89 |  |  | 7380 |  |  |  | 400 | [10 empty] | 83.54 |  |  |  | 85.62 | [5 empty] | 81.62 |  |  | 84.25 |  |  |  | 0.84 |  | 0.73 | [8 empty] | 13.65 |  |  |  |  | 2.07
1991 |  |  |  | 3061.38 |  |  | 7860 |  |  |  | 400 | [10 empty] | 89.20 |  |  |  | 89.48 | [5 empty] | 87.37 |  |  | 89.73 |  |  |  | 1.12 |  | 1.02 | [8 empty] | 9.51 |  |  |  |  | 0.28
1992 |  |  |  | 2990.54 |  |  | 7741 |  |  |  | 400 | [10 empty] | 86.52 |  |  |  | 87.69 | [5 empty] | 85.11 |  |  | 88.13 |  |  |  | 1.18 |  | 1.05 | [8 empty] | 11.26 |  |  |  |  | 1.17
1993 |  |  |  | 2908.89 |  |  | 7580 |  |  |  | 400 | [10 empty] | 84.38 |  |  |  | 86.00 | [5 empty] | 83.02 |  |  | 86.53 |  |  |  | 3.84 |  | 3.43 | [8 empty] | 10.57 |  |  |  |  | 1.62
1994 |  |  |  | 2921.78 |  |  | 7635 |  |  |  | 400 | [10 empty] | 84.32 |  |  |  | 88.72 | [5 empty] | 83.38 |  |  | 87.16 |  |  |  | 0.38 |  | 0.34 | [8 empty] | 10.94 |  |  |  |  | 4.40
1995 |  |  |  | 2791.52 |  |  | 7342 |  |  |  | 392 | [10 empty] | 80.96 |  |  |  | 82.67 | [5 empty] | 81.29 |  |  | 83.81 |  |  |  | 3.45 |  | 2.95 | [8 empty] | 14.37 |  |  |  |  | 1.72
1996 |  |  |  | 3169.35 |  |  | 8141 |  |  |  | 392 | [10 empty] | 91.25 |  |  |  | 91.48 | [5 empty] | 92.04 |  |  | 92.68 |  |  |  | 0.48 |  | 0.44 | [8 empty] | 8.08 |  |  |  |  | 0.23
1997 |  |  |  | 3113.83 |  |  | 7899 |  |  |  | 392 | [10 empty] | 88.92 |  |  |  | 88.97 | [5 empty] | 90.68 |  |  | 90.17 |  |  |  | 2.08 |  | 1.89 | [8 empty] | 9.14 |  |  |  |  | 0.05
1998 |  |  |  | 3292.46 |  |  | 8277 |  |  |  | 392 | [10 empty] | 93.74 |  |  |  | 94.05 | [5 empty] | 95.88 |  |  | 94.49 |  |  |  | 0.17 |  | 0.16 | [8 empty] | 5.78 |  |  |  |  | 0.31
1999 |  |  |  | 3196.84 |  |  | 8123 |  |  |  | 392 | [10 empty] | 91.12 |  |  |  | 92.58 | [5 empty] | 93.10 |  |  | 92.73 |  |  |  | 0.27 |  | 0.25 | [8 empty] | 7.16 |  |  |  |  | 1.46
2000 |  |  |  | 3264.77 |  |  | 8317 |  |  |  | 392 | [10 empty] | 92.34 |  |  |  | 94.25 | [5 empty] | 94.81 |  |  | 94.68 |  |  |  | 0.39 |  | 0.37 | [8 empty] | 5.39 |  |  |  |  | 1.91
2001 |  |  |  | 3157.62 |  |  | 8098 |  |  |  | 392 | [10 empty] | 90.47 |  |  |  | 91.37 | [5 empty] | 91.94 |  |  | 92.43 |  |  |  | 3.11 |  | 2.93 | [8 empty] | 5.70 |  |  |  |  | 0.90
2002 |  |  |  | 3260.70 |  |  | 8308 |  |  |  | 392 | [10 empty] | 93.33 |  |  |  | 93.44 | [5 empty] | 94.96 |  |  | 94.84 |  |  |  | 0.39 |  | 0.37 | [8 empty] | 6.19 |  |  |  |  | 0.11
2003 |  |  |  | 3024.60 |  |  | 7953 |  |  |  | 392 | [10 empty] | 86.35 |  |  |  | 90.29 | [5 empty] | 88.08 |  |  | 90.79 |  |  |  | 0.23 |  | 0.58 | [8 empty] | 9.13 |  |  |  |  | 3.94
2004 |  |  |  | 2989.10 |  |  | 7742 |  |  |  | 392 | [10 empty] | 85.54 |  |  |  | 87.55 | [5 empty] | 86.81 |  |  | 88.14 |  |  |  | 1.66 |  | 1.72 | [8 empty] | 10.72 |  |  |  |  | 2.02
2005 |  |  |  | 3062.65 |  |  | 7849 |  |  |  | 392 | [10 empty] | 87.95 |  |  |  | 89.14 | [5 empty] | 89.18 |  |  | 89.59 |  |  |  | 0.78 |  | 0.70 | [8 empty] | 10.16 |  |  |  |  | 1.18
2006 |  |  |  | 3100.48 |  |  | 8030 |  |  |  | 392 | [10 empty] | 89.19 |  |  |  | 91.10 | [5 empty] | 90.29 |  |  | 91.67 |  |  |  | 0.89 |  | 0.82 | [8 empty] | 8.08 |  |  |  |  | 1.91
2007 |  |  |  | 3028.97 |  |  | 7709 |  |  |  | 392 | [10 empty] | 87.64 |  |  |  | 87.72 | [5 empty] | 88.21 |  |  | 88.00 |  |  |  | 0.00 |  | 3.70 | [8 empty] | 8.58 |  |  |  |  | 0.08
2008 |  |  |  | 2690.32 |  |  | 6847 |  |  |  | 392 | [10 empty] | 77.29 |  |  |  | 77.29 | [5 empty] | 78.13 |  |  | 77.95 |  |  |  | 12.89 |  | 11.96 | [8 empty] | 10.75 |  |  |  |  | 0.00
2009 |  |  |  | 2874.05 |  |  | 7266 |  |  |  | 392 | [10 empty] | 82.89 |  |  |  | 82.90 | [5 empty] | 83.70 |  |  | 82.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.09 |  |  |  |  | 0.01
2010 |  |  |  | 3401.38 |  |  | 7801 |  |  |  | 433 | [10 empty] | 88.25 |  |  |  | 88.25 | [5 empty] | 89.67 |  |  | 89.05 |  |  |  | 1.09 |  | 0.97 | [8 empty] | 10.78 |  |  |  |  | 0.01
2011 |  |  |  | 3328.53 |  |  | 7740 |  |  |  | 433 | [10 empty] | 87.77 |  |  |  | 87.94 | [5 empty] | 87.75 |  |  | 88.36 |  |  |  | 0.34 |  | 2.72 | [8 empty] | 9.34 |  |  |  |  | 0.17
2012 |  |  |  | 3444.69 |  |  | 8019 |  |  |  | 433 | [10 empty] | 90.91 |  |  |  | 90.91 | [5 empty] | 90.57 |  |  | 91.29 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 9.02 |  |  |  |  | 0.00
2013 |  |  |  | 3707.93 |  |  | 8595 |  |  |  | 433 | [10 empty] | 97.23 |  |  |  | 97.93 | [5 empty] | 97.76 |  |  | 98.12 |  |  |  | 0.37 |  | 0.36 | [8 empty] | 1.71 |  |  |  |  | 0.70
2014 |  |  |  | 3556.42 |  |  | 8230 |  |  |  | 433 | [10 empty] | 93.35 |  |  |  | 93.62 | [5 empty] | 93.76 |  |  | 93.95 |  |  |  | 0.32 |  | 0.30 | [8 empty] | 6.08 |  |  |  |  | 0.27
2015 |  |  |  | 396.78 |  |  | 1143 |  |  |  | 433 | [10 empty] | 95.33 |  |  |  | 97.63 | [5 empty] | 10.46 |  |  | 13.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.37 |  |  |  |  | 2.30
2016 |  |  |  | 3014.51 |  |  | 7056 |  |  |  | 433 | [10 empty] | 79.41 |  |  |  | 79.64 | [5 empty] | 79.26 |  |  | 80.33 |  |  |  | 13.14 |  | 13.44 | [8 empty] | 6.92 |  |  |  |  | 0.23
2017 |  |  |  | 3426.38 |  |  | 8019 |  |  |  | 433 | [10 empty] | 90.28 |  |  |  | 90.68 | [5 empty] | 90.33 |  |  | 91.54 |  |  |  | 0.61 |  | 1.85 | [8 empty] | 7.46 |  |  |  |  | 0.40
2018 |  |  |  | 1172.49 |  |  | 2700 |  |  |  | 433 | [10 empty] | 30.81 |  |  |  | 30.81 | [5 empty] | 30.91 |  |  | 30.82 |  |  |  | 3.61 |  | 1.15 | [8 empty] | 68.04 |  |  |  |  | 0.00
2019 |  |  |  | 2185.67 |  |  | 4968 |  |  |  | 445 | [10 empty] | 55.84 |  |  |  | 56.39 | [5 empty] | 56.31 |  |  | 56.71 |  |  |  | 0.05 |  | 0.03 | [8 empty] | 43.58 |  |  |  |  | 0.55
2020 |  |  |  | 2172.18 |  |  | 4946 |  |  |  | 445 | [10 empty] | 55.19 |  |  |  | 55.81 | [5 empty] | 55.57 |  |  | 56.31 |  |  |  | 0.00 |  | 6.55 | [8 empty] | 37.64 |  |  |  |  | 0.62
2021 |  |  |  | 3587.85 |  |  | 8045 |  |  |  | 445 | [10 empty] | 91.05 |  |  |  | 91.44 | [5 empty] | 92.04 |  |  | 91.84 |  |  |  | 0.51 |  | 0.47 | [8 empty] | 8.10 |  |  |  |  | 0.39
2022 |  |  |  | 3551.15 |  |  | 8045 |  |  |  | 445 | [10 empty] | 90.40 |  |  |  | 91.39 | [5 empty] | 91.10 |  |  | 91.84 |  |  |  | 1.13 |  | 1.04 | [8 empty] | 7.56 |  |  |  |  | 0.99
2023 |  |  |  | 3540.07 |  |  | 8075 |  |  |  | 445 | [10 empty] | 89.90 |  |  |  | 91.08 | [5 empty] | 90.81 |  |  | 92.18 |  |  |  | 1.98 |  | 1.84 | [8 empty] | 7.09 |  |  |  |  | 1.17
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1975 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 87 | [14 empty] | 189
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 598 | [14 empty] | 717
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 6
E. |  | Testing of plant systems or components | [35 empty] | 44 |  |  |  | 2
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 266
H. |  | Nuclear regulatory requirements | [39 empty] | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 25
M. |  | Governmental requirements or court decisions | [51 empty] | 152
P. |  | Fire | [39 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 17 |  |  |  | 32
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 598 |  |  |  | 87 | [10 empty] | 1050 |  |  |  | 255 | [11 empty] | 157
Total | [22 empty] | 685 | [14 empty] | 1462
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1975 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 8
12. |  |  | Reactor I&C Systems | [34 empty] | 29
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 32
16. |  |  | Steam generation systems | [34 empty] | 30
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [19 empty] | 73 | [14 empty] | 57
32. |  |  | Feedwater and Main Steam System | [19 empty] | 14 | [14 empty] | 17
33. |  |  | Circulating Water System | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 0
Total | [22 empty] | 87 | [14 empty] | 195
Highlights (2023)
27-04-2023: start Stretch-out 09-06-2023: Refuelling outage 04-07-2023: startup cycle 48 05-07-2023: scram automatic 26-08-2023: scram automatic 05-12-2023: scram automatic

## DOEL-2
2023 Operating Experience
BE-4 | [8 empty] | DOEL-2 | [26 empty] | BELGIUM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EBL+EDF (ENGIE ELECTRABEL + EDF BELGIUM + EDF LUMINUS)
Owner | [7 empty] | : | IND.DOEL (INDIVISION DOEL (EBES , INTERCOM , UNERG))
Reactor Supplier | [7 empty] | : | ACECOWEN (ACECOWEN (ACEC-COCKERILL-WESTINGHOUSE))
Turbine Supplier | [7 empty] | : | COC/ACEC (TURBINE: COCKERILL-TOSI ; ALTERNATOR: ACEC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-09-01
Thermal power | [12 empty] | : |  |  | 1311 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-08-21
Gross electrical power | [12 empty] | : |  |  | 454 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-12-01
Reference unit power (net) | [12 empty] | : |  |  | 445 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.73
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.08
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 2.9
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.46 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.8
| Active core height/length [m] | [13 empty] | : |  |  | 2.44 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 22.22 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3570.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.45 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.16 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.41 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.7 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.89 %
Load Factor (LF) | [18 empty] | : | 91.6 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.54 %
Operating Factor (OF) | [18 empty] | : | 92.36 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 669 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 332.23 | 299.57 |  |  |  | 168.22 |  | 165.69 | [8 empty] | 329.36 |  |  | 313.39 | [6 empty] | 322.50 |  | 324.93 |  |  |  | 317.32 |  |  | 332.54 |  |  | 327.02 | [9 empty] | 337.82 |  |  | 3570.58
EAF [%] |  |  |  |  | 100.00 | 99.90 |  |  |  | 50.88 |  | 51.61 | [8 empty] | 99.50 |  |  | 97.81 | [6 empty] | 97.41 |  | 98.14 |  |  |  | 99.04 |  |  | 99.86 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.16
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 53.90 |  | 51.61 | [8 empty] | 99.50 |  |  | 98.89 | [6 empty] | 98.88 |  | 98.90 |  |  |  | 99.04 |  |  | 99.86 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.70
LF [%] |  |  |  |  | 100.35 | 100.18 |  |  |  | 50.88 |  | 51.71 | [8 empty] | 99.48 |  |  | 97.81 | [6 empty] | 97.41 |  | 98.14 |  |  |  | 99.04 |  |  | 100.31 |  |  | 102.07 | [9 empty] | 102.04 |  |  | 91.60
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 54.37 |  | 54.17 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.36
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.50 |  |  | 1.11 | [6 empty] | 1.12 |  | 1.10 |  |  |  | 0.94 |  |  | 0.14 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.45
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.50 |  |  | 1.11 | [6 empty] | 1.12 |  | 1.10 |  |  |  | 0.94 |  |  | 0.14 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.41
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 46.10 |  | 48.39 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.02 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.89
XUF [%] |  |  |  |  | 0.00 | 0.10 |  |  |  | 3.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.08 | [6 empty] | 1.47 |  | 0.76 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.54
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 142247.64 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.37 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.57 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.25 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.33 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.42 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.82 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.76 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.66 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 711.50 |  |  | 2305 |  |  |  | 392 | [10 empty] | 91.30 |  |  |  | 91.30 | [5 empty] | 91.34 |  |  | 93.28 |  |  |  | 8.70 |  | 8.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
1976 |  |  |  | 2462.80 |  |  | 6519 |  |  |  | 395 | [10 empty] | 71.64 |  |  |  | 71.64 | [5 empty] | 70.98 |  |  | 74.21 |  |  |  | 6.58 |  | 5.05 | [8 empty] | 23.31 |  |  |  |  | 0.00
1977 |  |  |  | 2576.80 |  |  | 6649 |  |  |  | 395 | [10 empty] | 74.30 |  |  |  | 74.30 | [5 empty] | 74.47 |  |  | 75.90 |  |  |  | 15.58 |  | 13.71 | [8 empty] | 11.99 |  |  |  |  | 0.00
1978 |  |  |  | 2750.60 |  |  | 7114 |  |  |  | 395 | [10 empty] | 79.53 |  |  |  | 79.53 | [5 empty] | 79.49 |  |  | 81.21 |  |  |  | 8.68 |  | 7.56 | [8 empty] | 12.91 |  |  |  |  | 0.00
1979 |  |  |  | 2593.30 |  |  | 6639 |  |  |  | 395 | [10 empty] | 74.56 |  |  |  | 74.56 | [5 empty] | 74.95 |  |  | 75.79 |  |  |  | 2.02 |  | 1.54 | [8 empty] | 23.90 |  |  |  |  | 0.00
1980 |  |  |  | 2782.00 |  |  | 7111 |  |  |  | 395 | [10 empty] | 79.75 |  |  |  | 79.75 | [5 empty] | 80.18 |  |  | 80.95 |  |  |  | 0.36 |  | 0.29 | [8 empty] | 19.96 |  |  |  |  | 0.00
1981 |  |  |  | 2841.70 |  |  | 7226 |  |  |  | 395 | [10 empty] | 81.36 |  |  |  | 81.36 | [5 empty] | 82.13 |  |  | 82.49 |  |  |  | 2.77 |  | 2.32 | [8 empty] | 16.33 |  |  |  |  | 0.00
1982 |  |  |  | 2582.00 |  |  | 6598 |  |  |  | 395 | [10 empty] | 73.82 |  |  |  | 73.82 | [5 empty] | 74.62 |  |  | 75.32 |  |  |  | 19.44 |  | 17.82 | [8 empty] | 8.37 |  |  |  |  | 0.00
1983 |  |  |  | 2017.00 |  |  | 5190 |  |  |  | 393 | [10 empty] | 58.02 |  |  |  | 58.02 | [5 empty] | 58.59 |  |  | 59.25 |  |  |  | 0.06 |  | 0.03 | [8 empty] | 41.95 |  |  |  |  | 0.00
1984 |  |  |  | 2916.00 |  |  | 7508 |  |  |  | 393 | [10 empty] | 84.15 |  |  |  | 84.15 | [5 empty] | 84.47 |  |  | 85.47 |  |  |  | 3.08 |  | 2.67 | [8 empty] | 13.18 |  |  |  |  | 0.00
1985 |  |  |  | 2908.66 |  |  | 7341 |  |  |  | 392 | [10 empty] | 83.04 |  |  |  | 83.04 | [5 empty] | 84.70 |  |  | 83.80 |  |  |  | 7.64 |  | 6.86 | [8 empty] | 10.10 |  |  |  |  | 0.00
1986 |  |  |  | 2282.63 |  |  | 5891 |  |  |  | 392 | [10 empty] | 69.76 |  |  |  | 69.85 | [5 empty] | 66.47 |  |  | 67.25 |  |  |  | 5.08 |  | 3.74 | [8 empty] | 26.41 |  |  |  |  | 0.09
1987 |  |  |  | 2616.44 |  |  | 6612 |  |  |  | 400 | [10 empty] | 76.77 |  |  |  | 77.75 | [5 empty] | 74.67 |  |  | 75.48 |  |  |  | 8.61 |  | 7.32 | [8 empty] | 14.92 |  |  |  |  | 0.99
1988 |  |  |  | 2906.68 |  |  | 7408 |  |  |  | 400 | [10 empty] | 82.60 |  |  |  | 83.20 | [5 empty] | 82.73 |  |  | 84.34 |  |  |  | 5.39 |  | 4.74 | [8 empty] | 12.06 |  |  |  |  | 0.60
1989 |  |  |  | 2479.80 |  |  | 6436 |  |  |  | 400 | [10 empty] | 70.79 |  |  |  | 71.79 | [5 empty] | 70.77 |  |  | 73.47 |  |  |  | 11.54 |  | 9.36 | [8 empty] | 18.85 |  |  |  |  | 1.00
1990 |  |  |  | 1982.58 |  |  | 5170 |  |  |  | 400 | [10 empty] | 56.58 |  |  |  | 66.48 | [5 empty] | 56.58 |  |  | 59.02 |  |  |  | 19.63 |  | 16.23 | [8 empty] | 17.29 |  |  |  |  | 9.90
1991 |  |  |  | 2779.83 |  |  | 7136 |  |  |  | 400 | [10 empty] | 81.02 |  |  |  | 81.17 | [5 empty] | 79.33 |  |  | 81.46 |  |  |  | 2.08 |  | 1.72 | [8 empty] | 17.10 |  |  |  |  | 0.15
1992 |  |  |  | 2971.94 |  |  | 7617 |  |  |  | 400 | [10 empty] | 86.12 |  |  |  | 86.33 | [5 empty] | 84.58 |  |  | 86.71 |  |  |  | 0.88 |  | 0.76 | [8 empty] | 12.91 |  |  |  |  | 0.21
1993 |  |  |  | 2949.55 |  |  | 7551 |  |  |  | 400 | [10 empty] | 85.68 |  |  |  | 85.94 | [5 empty] | 84.18 |  |  | 86.20 |  |  |  | 2.40 |  | 2.12 | [8 empty] | 11.94 |  |  |  |  | 0.27
1994 |  |  |  | 2982.45 |  |  | 7810 |  |  |  | 392 | [10 empty] | 86.22 |  |  |  | 87.28 | [5 empty] | 86.85 |  |  | 89.16 |  |  |  | 0.54 |  | 0.48 | [8 empty] | 12.24 |  |  |  |  | 1.06
1995 |  |  |  | 2867.54 |  |  | 7342 |  |  |  | 392 | [10 empty] | 82.70 |  |  |  | 82.92 | [5 empty] | 83.51 |  |  | 83.81 |  |  |  | 5.02 |  | 4.38 | [8 empty] | 12.70 |  |  |  |  | 0.23
1996 |  |  |  | 2888.76 |  |  | 7390 |  |  |  | 392 | [10 empty] | 83.13 |  |  |  | 83.39 | [5 empty] | 83.89 |  |  | 84.13 |  |  |  | 7.17 |  | 6.44 | [8 empty] | 10.18 |  |  |  |  | 0.25
1997 |  |  |  | 2935.03 |  |  | 7749 |  |  |  | 392 | [10 empty] | 84.50 |  |  |  | 87.71 | [5 empty] | 85.47 |  |  | 88.46 |  |  |  | 2.97 |  | 2.68 | [8 empty] | 9.61 |  |  |  |  | 3.21
1998 |  |  |  | 3145.01 |  |  | 7987 |  |  |  | 392 | [10 empty] | 90.13 |  |  |  | 90.18 | [5 empty] | 91.59 |  |  | 91.18 |  |  |  | 2.50 |  | 2.31 | [8 empty] | 7.51 |  |  |  |  | 0.05
1999 |  |  |  | 3091.67 |  |  | 7875 |  |  |  | 392 | [10 empty] | 88.88 |  |  |  | 89.57 | [5 empty] | 90.03 |  |  | 89.90 |  |  |  | 3.65 |  | 3.39 | [8 empty] | 7.04 |  |  |  |  | 0.70
2000 |  |  |  | 3135.59 |  |  | 8022 |  |  |  | 392 | [10 empty] | 89.81 |  |  |  | 90.43 | [5 empty] | 91.06 |  |  | 91.33 |  |  |  | 3.57 |  | 3.34 | [8 empty] | 6.23 |  |  |  |  | 0.62
2001 |  |  |  | 3150.54 |  |  | 8060 |  |  |  | 392 | [10 empty] | 90.30 |  |  |  | 90.89 | [5 empty] | 91.75 |  |  | 92.01 |  |  |  | 2.41 |  | 2.25 | [8 empty] | 6.87 |  |  |  |  | 0.58
2002 |  |  |  | 3104.45 |  |  | 8076 |  |  |  | 392 | [10 empty] | 89.51 |  |  |  | 91.39 | [5 empty] | 90.41 |  |  | 92.19 |  |  |  | 1.37 |  | 1.27 | [8 empty] | 7.34 |  |  |  |  | 1.89
2003 |  |  |  | 3142.62 |  |  | 8184 |  |  |  | 392 | [10 empty] | 90.13 |  |  |  | 93.09 | [5 empty] | 91.52 |  |  | 93.42 |  |  |  | 0.47 |  | 0.59 | [8 empty] | 6.32 |  |  |  |  | 2.96
2004 |  |  |  | 2951.91 |  |  | 7174 |  |  |  | 433 | [10 empty] | 80.50 |  |  |  | 81.92 | [5 empty] | 81.35 |  |  | 81.67 |  |  |  | 0.37 |  | 0.30 | [8 empty] | 17.77 |  |  |  |  | 1.43
2005 |  |  |  | 3506.72 |  |  | 8036 |  |  |  | 433 | [10 empty] | 90.79 |  |  |  | 91.26 | [5 empty] | 92.44 |  |  | 91.72 |  |  |  | 2.11 |  | 1.97 | [8 empty] | 6.77 |  |  |  |  | 0.47
2006 |  |  |  | 3399.32 |  |  | 7954 |  |  |  | 433 | [10 empty] | 88.18 |  |  |  | 90.10 | [5 empty] | 89.62 |  |  | 90.80 |  |  |  | 1.86 |  | 1.71 | [8 empty] | 8.19 |  |  |  |  | 1.91
2007 |  |  |  | 3483.14 |  |  | 7985 |  |  |  | 433 | [10 empty] | 90.76 |  |  |  | 90.77 | [5 empty] | 91.83 |  |  | 91.15 |  |  |  | 0.09 |  | 1.43 | [8 empty] | 7.80 |  |  |  |  | 0.01
2008 |  |  |  | 3478.91 |  |  | 8000 |  |  |  | 433 | [10 empty] | 90.26 |  |  |  | 90.26 | [5 empty] | 91.47 |  |  | 91.07 |  |  |  | 0.68 |  | 0.61 | [8 empty] | 9.12 |  |  |  |  | 0.00
2009 |  |  |  | 3468.52 |  |  | 7941 |  |  |  | 433 | [10 empty] | 90.11 |  |  |  | 90.11 | [5 empty] | 91.44 |  |  | 90.65 |  |  |  | 0.39 |  | 0.36 | [8 empty] | 9.54 |  |  |  |  | 0.00
2010 |  |  |  | 3411.40 |  |  | 7823 |  |  |  | 433 | [10 empty] | 88.29 |  |  |  | 88.40 | [5 empty] | 89.95 |  |  | 89.31 |  |  |  | 0.70 |  | 0.90 | [8 empty] | 10.70 |  |  |  |  | 0.11
2011 |  |  |  | 3570.91 |  |  | 8292 |  |  |  | 433 | [10 empty] | 94.12 |  |  |  | 94.12 | [5 empty] | 94.14 |  |  | 94.66 |  |  |  | 0.49 |  | 0.47 | [8 empty] | 5.41 |  |  |  |  | 0.00
2012 |  |  |  | 3261.59 |  |  | 7605 |  |  |  | 433 | [10 empty] | 86.06 |  |  |  | 86.14 | [5 empty] | 85.75 |  |  | 86.58 |  |  |  | 1.34 |  | 1.17 | [8 empty] | 12.68 |  |  |  |  | 0.09
2013 |  |  |  | 3566.80 |  |  | 8238 |  |  |  | 433 | [10 empty] | 93.52 |  |  |  | 93.77 | [5 empty] | 94.03 |  |  | 94.04 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 6.21 |  |  |  |  | 0.26
2014 |  |  |  | 3528.42 |  |  | 8291 |  |  |  | 433 | [10 empty] | 92.67 |  |  |  | 94.33 | [5 empty] | 93.02 |  |  | 94.65 |  |  |  | 0.59 |  | 0.56 | [8 empty] | 5.10 |  |  |  |  | 1.66
2015 |  |  |  | 2971.43 |  |  | 6883 |  |  |  | 433 | [10 empty] | 83.77 |  |  |  | 83.98 | [5 empty] | 78.34 |  |  | 78.57 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 16.01 |  |  |  |  | 0.20
2016 |  |  |  | 3037.09 |  |  | 7056 |  |  |  | 433 | [10 empty] | 79.47 |  |  |  | 79.90 | [5 empty] | 79.85 |  |  | 80.33 |  |  |  | 0.07 |  | 0.05 | [8 empty] | 20.05 |  |  |  |  | 0.43
2017 |  |  |  | 3413.43 |  |  | 8071 |  |  |  | 433 | [10 empty] | 89.78 |  |  |  | 91.54 | [5 empty] | 89.99 |  |  | 92.13 |  |  |  | 0.30 |  | 2.35 | [8 empty] | 6.11 |  |  |  |  | 1.76
2018 |  |  |  | 1475.20 |  |  | 3400 |  |  |  | 433 | [10 empty] | 38.68 |  |  |  | 38.70 | [5 empty] | 38.89 |  |  | 38.81 |  |  |  | 0.24 |  | 0.09 | [8 empty] | 61.21 |  |  |  |  | 0.02
2019 |  |  |  | 2405.33 |  |  | 5653 |  |  |  | 433 | [10 empty] | 63.12 |  |  |  | 63.46 | [5 empty] | 63.41 |  |  | 64.53 |  |  |  | 0.23 |  | 0.14 | [8 empty] | 36.39 |  |  |  |  | 0.34
2020 |  |  |  | 2161.14 |  |  | 5003 |  |  |  | 445 | [10 empty] | 55.74 |  |  |  | 56.73 | [5 empty] | 55.91 |  |  | 56.96 |  |  |  | 0.26 |  | 13.38 | [8 empty] | 29.89 |  |  |  |  | 0.99
2021 |  |  |  | 3490.70 |  |  | 7901 |  |  |  | 445 | [10 empty] | 89.11 |  |  |  | 89.66 | [5 empty] | 89.55 |  |  | 90.19 |  |  |  | 1.05 |  | 0.95 | [8 empty] | 9.39 |  |  |  |  | 0.55
2022 |  |  |  | 3538.97 |  |  | 8105 |  |  |  | 445 | [10 empty] | 90.46 |  |  |  | 91.80 | [5 empty] | 90.78 |  |  | 92.52 |  |  |  | 0.88 |  | 0.81 | [8 empty] | 7.39 |  |  |  |  | 1.34
2023 |  |  |  | 3570.58 |  |  | 8091 |  |  |  | 445 | [10 empty] | 91.16 |  |  |  | 91.70 | [5 empty] | 91.60 |  |  | 92.36 |  |  |  | 0.45 |  | 0.41 | [8 empty] | 7.89 |  |  |  |  | 0.54
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1975 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 226
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 670 | [14 empty] | 770
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 137
E. |  | Testing of plant systems or components | [35 empty] | 62 |  |  |  | 10
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 226
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 15
L. |  | Human factor related | [39 empty] | 42
M. |  | Governmental requirements or court decisions | [51 empty] | 11
P. |  | Fire | [39 empty] | 1
Z. |  | Other | [39 empty] | 7
Subtotal | [22 empty] | 670 | [14 empty] | 1195 |  |  |  | 286 | [11 empty] | 26
Total | [22 empty] | 670 | [14 empty] | 1507
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1975 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 9
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 19
16. |  |  | Steam generation systems | [34 empty] | 62
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 20
31. |  |  | Turbine and auxiliaries | [34 empty] | 63
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
34. |  |  | Miscellaneous Systems | [34 empty] | 18
41. |  |  | Main Generator Systems | [34 empty] | 20
42. |  |  | Electrical Power Supply Systems | [34 empty] | 6
Total | [37 empty] | 249
Highlights (2023)
14-02-2023: start stretch-out 17-03-2023: refuelling outage 14-04-2023: startup cycle 48

## DOEL-4
2023 Operating Experience
BE-7 | [8 empty] | DOEL-4 | [26 empty] | BELGIUM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EBL+EDF (ENGIE ELECTRABEL + EDF BELGIUM + EDF LUMINUS)
Owner | [7 empty] | : | EBES (SOCIETES REUNIES D'ENERGIE DU BASSIN DE L'ESCAUT SA)
Reactor Supplier | [7 empty] | : | ACECOWEN (ACECOWEN (ACEC-COCKERILL-WESTINGHOUSE))
Turbine Supplier | [7 empty] | : | AA/BB/AC ((ALSTHOM - BBC / ACEC))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-12-01
Thermal power | [12 empty] | : |  |  | 2988 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-04-08
Gross electrical power | [12 empty] | : |  |  | 1090 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-07-01
Reference unit power (net) | [12 empty] | : |  |  | 1026 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.73
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.08
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 3.5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.28
| Active core height/length [m] | [13 empty] | : |  |  | 4.27 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.47 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7670.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.13 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.58 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.8 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.55 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.65 %
Load Factor (LF) | [18 empty] | : | 84.6 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.97 %
Operating Factor (OF) | [18 empty] | : | 87.16 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1125 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 770.21 | 696.27 |  |  |  | 742.62 |  | 427.45 | [8 empty] | 37.14 |  |  | 485.66 | [6 empty] | 745.27 |  | 757.23 |  |  |  | 727.76 |  |  | 764.18 |  |  | 744.88 | [9 empty] | 771.38 |  |  | 7670.06
EAF [%] |  |  |  |  | 99.74 | 99.80 |  |  |  | 96.28 |  | 57.19 | [8 empty] | 4.81 |  |  | 64.98 | [6 empty] | 97.99 |  | 98.05 |  |  |  | 97.76 |  |  | 99.76 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.58
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 68.97 | [8 empty] | 4.81 |  |  | 66.29 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.55
LF [%] |  |  |  |  | 99.73 | 99.82 |  |  |  | 96.29 |  | 57.19 | [8 empty] | 4.81 |  |  | 64.98 | [6 empty] | 96.50 |  | 98.05 |  |  |  | 97.38 |  |  | 99.98 |  |  | 100.83 | [9 empty] | 101.05 |  |  | 84.60
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 69.03 | [8 empty] | 8.87 |  |  | 68.89 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.16
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.51 |  |  | 33.64 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.13
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.33 |  |  | 33.60 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.80
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 31.03 | [8 empty] | 94.86 |  |  | 0.11 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.65
XUF [%] |  |  |  |  | 0.26 | 0.20 |  |  |  | 3.72 |  | 11.77 | [8 empty] | 0.00 |  |  | 1.30 | [6 empty] | 2.01 |  | 1.95 |  |  |  | 2.24 |  |  | 0.24 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.97
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 286537.37 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.85 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.9 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.55 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.58 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.87 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.61 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.67 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.88 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4282.13 |  |  | 5263 |  |  |  | 981 | [10 empty] | 82.56 |  |  |  | 82.56 | [5 empty] | 82.59 |  |  | 87.93 |  |  |  | 17.44 |  | 17.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 7722.89 |  |  | 7973 |  |  |  | 1006 | [10 empty] | 87.77 |  |  |  | 87.77 | [5 empty] | 87.64 |  |  | 91.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.23 |  |  |  |  | 0.00
1987 |  |  |  | 6809.26 |  |  | 7448 |  |  |  | 1006 | [10 empty] | 77.04 |  |  |  | 81.42 | [5 empty] | 77.27 |  |  | 85.02 |  |  |  | 4.33 |  | 3.69 | [8 empty] | 14.89 |  |  |  |  | 4.38
1988 |  |  |  | 7551.97 |  |  | 7784 |  |  |  | 1000 | [10 empty] | 85.90 |  |  |  | 87.60 | [5 empty] | 85.97 |  |  | 88.62 |  |  |  | 2.34 |  | 2.10 | [8 empty] | 10.30 |  |  |  |  | 1.70
1989 |  |  |  | 7445.90 |  |  | 7737 |  |  |  | 1010 | [10 empty] | 84.43 |  |  |  | 87.37 | [5 empty] | 84.16 |  |  | 88.32 |  |  |  | 5.46 |  | 5.05 | [8 empty] | 7.59 |  |  |  |  | 2.94
1990 |  |  |  | 7535.84 |  |  | 7790 |  |  |  | 1010 | [10 empty] | 85.25 |  |  |  | 88.23 | [5 empty] | 85.17 |  |  | 88.93 |  |  |  | 2.53 |  | 2.29 | [8 empty] | 9.48 |  |  |  |  | 2.97
1991 |  |  |  | 7425.40 |  |  | 7673 |  |  |  | 1010 | [10 empty] | 84.07 |  |  |  | 84.76 | [5 empty] | 83.93 |  |  | 87.59 |  |  |  | 3.04 |  | 2.66 | [8 empty] | 12.59 |  |  |  |  | 0.69
1992 |  |  |  | 7418.56 |  |  | 7481 |  |  |  | 1010 | [10 empty] | 85.93 |  |  |  | 86.73 | [5 empty] | 83.62 |  |  | 85.17 |  |  |  | 5.16 |  | 4.72 | [8 empty] | 8.55 |  |  |  |  | 0.80
1993 |  |  |  | 6980.93 |  |  | 7112 |  |  |  | 1010 | [10 empty] | 78.90 |  |  |  | 79.63 | [5 empty] | 78.90 |  |  | 81.19 |  |  |  | 12.71 |  | 11.59 | [8 empty] | 8.78 |  |  |  |  | 0.74
1994 |  |  |  | 3462.74 |  |  | 3637 |  |  |  | 1001 | [10 empty] | 39.18 |  |  |  | 39.18 | [5 empty] | 39.49 |  |  | 41.52 |  |  |  | 52.92 |  | 44.04 | [8 empty] | 16.78 |  |  |  |  | 0.00
1995 |  |  |  | 6769.69 |  |  | 7381 |  |  |  | 1001 | [10 empty] | 76.83 |  |  |  | 76.93 | [5 empty] | 77.20 |  |  | 84.26 |  |  |  | 5.55 |  | 4.52 | [8 empty] | 18.55 |  |  |  |  | 0.10
1996 |  |  |  | 6186.80 |  |  | 6565 |  |  |  | 1001 | [10 empty] | 69.86 |  |  |  | 70.57 | [5 empty] | 70.36 |  |  | 74.74 |  |  |  | 1.92 |  | 1.38 | [8 empty] | 28.05 |  |  |  |  | 0.72
1997 |  |  |  | 7548.66 |  |  | 7653 |  |  |  | 1001 | [10 empty] | 86.99 |  |  |  | 87.10 | [5 empty] | 86.09 |  |  | 87.36 |  |  |  | 6.16 |  | 5.72 | [8 empty] | 7.19 |  |  |  |  | 0.11
1998 |  |  |  | 7844.02 |  |  | 7998 |  |  |  | 985 | [10 empty] | 89.99 |  |  |  | 89.99 | [5 empty] | 90.91 |  |  | 91.30 |  |  |  | 1.51 |  | 1.38 | [8 empty] | 8.63 |  |  |  |  | 0.00
1999 |  |  |  | 8008.40 |  |  | 8150 |  |  |  | 985 | [10 empty] | 92.41 |  |  |  | 92.51 | [5 empty] | 92.81 |  |  | 93.04 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 7.42 |  |  |  |  | 0.10
2000 |  |  |  | 7992.87 |  |  | 8323 |  |  |  | 985 | [10 empty] | 91.98 |  |  |  | 92.01 | [5 empty] | 92.38 |  |  | 94.75 |  |  |  | 2.75 |  | 2.60 | [8 empty] | 5.40 |  |  |  |  | 0.03
2001 |  |  |  | 8098.91 |  |  | 8264 |  |  |  | 985 | [10 empty] | 93.25 |  |  |  | 93.30 | [5 empty] | 93.86 |  |  | 94.34 |  |  |  | 0.81 |  | 0.77 | [8 empty] | 5.93 |  |  |  |  | 0.05
2002 |  |  |  | 7831.93 |  |  | 8017 |  |  |  | 985 | [10 empty] | 90.45 |  |  |  | 90.61 | [5 empty] | 90.77 |  |  | 91.52 |  |  |  | 1.97 |  | 1.82 | [8 empty] | 7.57 |  |  |  |  | 0.16
2003 |  |  |  | 7781.23 |  |  | 8015 |  |  |  | 985 | [10 empty] | 90.55 |  |  |  | 91.06 | [5 empty] | 90.18 |  |  | 91.50 |  |  |  | 0.52 |  | 0.47 | [8 empty] | 8.47 |  |  |  |  | 0.51
2004 |  |  |  | 7519.82 |  |  | 7843 |  |  |  | 985 | [10 empty] | 86.98 |  |  |  | 88.35 | [5 empty] | 86.90 |  |  | 89.28 |  |  |  | 0.81 |  | 2.24 | [8 empty] | 9.40 |  |  |  |  | 1.37
2005 |  |  |  | 7394.83 |  |  | 7647 |  |  |  | 985 | [10 empty] | 85.86 |  |  |  | 86.08 | [5 empty] | 85.69 |  |  | 87.28 |  |  |  | 1.24 |  | 1.08 | [8 empty] | 12.83 |  |  |  |  | 0.22
2006 |  |  |  | 7461.97 |  |  | 7633 |  |  |  | 1008 | [10 empty] | 86.21 |  |  |  | 86.53 | [5 empty] | 84.51 |  |  | 87.13 |  |  |  | 2.14 |  | 1.89 | [8 empty] | 11.58 |  |  |  |  | 0.32
2007 |  |  |  | 8496.87 |  |  | 8608 |  |  |  | 1008 | [10 empty] | 98.06 |  |  |  | 98.09 | [5 empty] | 96.22 |  |  | 98.25 |  |  |  | 1.91 |  | 1.91 | [8 empty] | 0.00 |  |  |  |  | 0.04
2008 |  |  |  | 7466.73 |  |  | 7534 |  |  |  | 1008 | [10 empty] | 85.22 |  |  |  | 85.22 | [5 empty] | 84.33 |  |  | 85.77 |  |  |  | 0.10 |  | 4.40 | [8 empty] | 10.38 |  |  |  |  | 0.00
2009 |  |  |  | 6910.95 |  |  | 6946 |  |  |  | 1047 | [10 empty] | 78.29 |  |  |  | 78.32 | [5 empty] | 77.76 |  |  | 79.29 |  |  |  | 8.59 |  | 11.42 | [8 empty] | 10.26 |  |  |  |  | 0.03
2010 |  |  |  | 7395.39 |  |  | 7192 |  |  |  | 1038 | [10 empty] | 81.59 |  |  |  | 81.59 | [5 empty] | 81.27 |  |  | 82.10 |  |  |  | 18.41 |  | 18.41 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 7978.47 |  |  | 7832 |  |  |  | 1039 | [10 empty] | 88.78 |  |  |  | 88.78 | [5 empty] | 87.66 |  |  | 89.41 |  |  |  | 3.38 |  | 3.11 | [8 empty] | 8.11 |  |  |  |  | 0.00
2012 |  |  |  | 7818.70 |  |  | 7659 |  |  |  | 1039 | [10 empty] | 86.44 |  |  |  | 86.52 | [5 empty] | 85.67 |  |  | 87.19 |  |  |  | 3.89 |  | 3.62 | [8 empty] | 9.86 |  |  |  |  | 0.08
2013 |  |  |  | 8447.48 |  |  | 8192 |  |  |  | 1039 | [10 empty] | 93.48 |  |  |  | 93.48 | [5 empty] | 92.81 |  |  | 93.52 |  |  |  | 6.51 |  | 6.51 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 4886.99 |  |  | 4796 |  |  |  | 1039 | [10 empty] | 53.72 |  |  |  | 54.19 | [5 empty] | 53.69 |  |  | 54.75 |  |  |  | 40.90 |  | 37.50 | [8 empty] | 8.30 |  |  |  |  | 0.48
2015 |  |  |  | 7743.88 |  |  | 7568 |  |  |  | 1033 | [10 empty] | 85.53 |  |  |  | 85.91 | [5 empty] | 85.58 |  |  | 86.39 |  |  |  | 0.20 |  | 1.43 | [8 empty] | 12.66 |  |  |  |  | 0.38
2016 |  |  |  | 8782.01 |  |  | 8630 |  |  |  | 1033 | [10 empty] | 97.49 |  |  |  | 98.03 | [5 empty] | 96.78 |  |  | 98.25 |  |  |  | 1.97 |  | 1.97 | [8 empty] | 0.00 |  |  |  |  | 0.54
2017 |  |  |  | 7461.43 |  |  | 7326 |  |  |  | 1038 | [10 empty] | 83.17 |  |  |  | 83.82 | [5 empty] | 82.19 |  |  | 83.63 |  |  |  | 5.25 |  | 4.65 | [8 empty] | 11.54 |  |  |  |  | 0.65
2018 |  |  |  | 5514.68 |  |  | 5479 |  |  |  | 1038 | [10 empty] | 60.56 |  |  |  | 60.98 | [5 empty] | 60.65 |  |  | 62.55 |  |  |  | 4.86 |  | 3.12 | [8 empty] | 35.90 |  |  |  |  | 0.42
2019 |  |  |  | 8730.31 |  |  | 8760 |  |  |  | 1038 | [10 empty] | 96.30 |  |  |  | 97.16 | [5 empty] | 96.01 |  |  | 100.00 |  |  |  | 2.84 |  | 2.84 | [8 empty] | 0.00 |  |  |  |  | 0.87
2020 |  |  |  | 7270.15 |  |  | 7147 |  |  |  | 1038 | [10 empty] | 79.80 |  |  |  | 80.60 | [5 empty] | 79.74 |  |  | 81.36 |  |  |  | 0.28 |  | 0.23 | [8 empty] | 19.17 |  |  |  |  | 0.81
2021 |  |  |  | 7952.78 |  |  | 7802 |  |  |  | 1038 | [10 empty] | 87.82 |  |  |  | 88.54 | [5 empty] | 87.46 |  |  | 89.06 |  |  |  | 0.14 |  | 0.33 | [8 empty] | 11.12 |  |  |  |  | 0.73
2022 |  |  |  | 8940.45 |  |  | 8760 |  |  |  | 1038 | [10 empty] | 99.03 |  |  |  | 99.98 | [5 empty] | 98.32 |  |  | 100.00 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 0.00 |  |  |  |  | 0.95
2023 |  |  |  | 7670.06 |  |  | 7635 |  |  |  | 1026 | [10 empty] | 84.58 |  |  |  | 86.55 | [5 empty] | 84.60 |  |  | 87.16 |  |  |  | 3.13 |  | 2.80 | [8 empty] | 10.65 |  |  |  |  | 1.97
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 224 | [14 empty] | 345
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 901 | [14 empty] | 708
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 43
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 84
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 24
P. |  | Fire | [39 empty] | 23
Z. |  | Other | [39 empty] | 30
Subtotal | [22 empty] | 901 |  |  |  | 224 | [10 empty] | 836 |  |  |  | 424 | [11 empty] | 4
Total | [22 empty] | 1125 | [14 empty] | 1264
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 0
12. |  |  | Reactor I&C Systems | [34 empty] | 4
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 15
16. |  |  | Steam generation systems | [34 empty] | 132
31. |  |  | Turbine and auxiliaries | [34 empty] | 153
32. |  |  | Feedwater and Main Steam System | [34 empty] | 12
33. |  |  | Circulating Water System | [34 empty] | 5
41. |  |  | Main Generator Systems | [19 empty] | 224 | [14 empty] | 50
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 224 | [14 empty] | 388
Highlights (2023)
25-02-2023: start stretch-out 21-04-2023: refuelling outage 29-05-2023: start up cycle 33 02-06-2023 to 12-06-2023: shutdown for an oil leak generator

## TIHANGE-1
2023 Operating Experience
BE-3 | [8 empty] | TIHANGE-1 | [26 empty] | BELGIUM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EBL (ENGIE ELECTRABEL )
Owner | [7 empty] | : | EBL (ENGIE ELECTRABEL )
Reactor Supplier | [7 empty] | : | ACLF ((ACECOWEN - CREUSOT LOIRE - FRAMATOME))
Turbine Supplier | [7 empty] | : | AAJSCH ((ALSTOM - ACEC - JEUMONT - SCHNEIDER ))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / Framatome 3 loops reactor | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-06-01
Thermal power | [12 empty] | : |  |  | 2873 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-03-07
Gross electrical power | [12 empty] | : |  |  | 1009 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-10-01
Reference unit power (net) | [12 empty] | : |  |  | 962 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.41
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.41
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.6 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.65
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 18
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 23.8 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8242.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.47 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.4 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.47 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.5 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.03 %
Load Factor (LF) | [18 empty] | : | 97.8 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.1 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 723.25 | 655.44 |  |  |  | 721.10 |  | 698.58 | [8 empty] | 712.41 |  |  | 671.49 | [6 empty] | 692.28 |  | 694.03 |  |  |  | 669.17 |  |  | 593.13 |  |  | 693.18 | [9 empty] | 717.99 |  |  | 8242.06
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.90 |  | 99.97 | [8 empty] | 99.55 |  |  | 96.95 | [6 empty] | 96.74 |  | 96.97 |  |  |  | 96.61 |  |  | 82.76 |  |  | 99.95 | [9 empty] | 99.83 |  |  | 97.40
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.90 |  | 99.97 | [8 empty] | 99.95 |  |  | 99.97 | [6 empty] | 99.98 |  | 99.56 |  |  |  | 99.50 |  |  | 83.78 |  |  | 99.95 | [9 empty] | 99.83 |  |  | 98.50
LF [%] |  |  |  |  | 101.05 | 101.39 |  |  |  | 100.89 |  | 100.86 | [8 empty] | 99.54 |  |  | 96.95 | [6 empty] | 96.72 |  | 96.97 |  |  |  | 96.61 |  |  | 82.76 |  |  | 100.08 | [9 empty] | 100.32 |  |  | 97.80
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.10 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.40 |  |  |  | 0.44 |  |  | 16.19 |  |  | 0.03 | [9 empty] | 0.11 |  |  | 1.47
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.10 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.40 |  |  |  | 0.44 |  |  | 16.19 |  |  | 0.03 | [9 empty] | 0.11 |  |  | 1.47
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.03 | [8 empty] | 0.05 |  |  | 0.03 | [6 empty] | 0.01 |  | 0.04 |  |  |  | 0.06 |  |  | 0.03 |  |  | 0.02 | [9 empty] | 0.06 |  |  | 0.03
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.40 |  |  | 3.03 | [6 empty] | 3.24 |  | 2.59 |  |  |  | 2.89 |  |  | 1.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.10
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 314563.68 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.15 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.31 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.1 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.59 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.02 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.99 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.65 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 3096.30 |  |  | 5360 |  |  |  | 885 | [10 empty] | 76.15 |  |  |  | 76.15 | [5 empty] | 76.16 |  |  | 94.52 |  |  |  | 23.85 |  | 23.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
1976 |  |  |  | 4409.50 |  |  | 6354 |  |  |  | 870 | [10 empty] | 57.54 |  |  |  | 89.78 | [5 empty] | 57.70 |  |  | 72.34 |  |  |  | 3.70 |  | 3.45 | [8 empty] | 6.76 |  |  |  |  | 32.24
1977 |  |  |  | 5842.30 |  |  | 7234 |  |  |  | 870 | [10 empty] | 76.67 |  |  |  | 76.67 | [5 empty] | 76.66 |  |  | 82.58 |  |  |  | 1.49 |  | 1.16 | [8 empty] | 22.17 |  |  |  |  | 0.00
1978 |  |  |  | 6371.00 |  |  | 7582 |  |  |  | 870 | [10 empty] | 84.31 |  |  |  | 84.31 | [5 empty] | 83.60 |  |  | 86.55 |  |  |  | 0.51 |  | 0.43 | [8 empty] | 15.26 |  |  |  |  | 0.00
1979 |  |  |  | 5159.00 |  |  | 6121 |  |  |  | 870 | [10 empty] | 67.58 |  |  |  | 67.58 | [5 empty] | 67.69 |  |  | 69.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.42 |  |  |  |  | 0.00
1980 |  |  |  | 6173.00 |  |  | 7337 |  |  |  | 870 | [10 empty] | 80.70 |  |  |  | 80.71 | [5 empty] | 80.78 |  |  | 83.53 |  |  |  | 8.46 |  | 7.46 | [8 empty] | 11.83 |  |  |  |  | 0.01
1981 |  |  |  | 6414.20 |  |  | 7762 |  |  |  | 870 | [10 empty] | 83.80 |  |  |  | 83.80 | [5 empty] | 84.16 |  |  | 88.61 |  |  |  | 0.54 |  | 0.45 | [8 empty] | 15.75 |  |  |  |  | 0.00
1982 |  |  |  | 6164.80 |  |  | 7269 |  |  |  | 870 | [10 empty] | 80.80 |  |  |  | 80.80 | [5 empty] | 80.89 |  |  | 82.98 |  |  |  | 2.21 |  | 1.82 | [8 empty] | 17.38 |  |  |  |  | 0.00
1983 |  |  |  | 5843.00 |  |  | 7135 |  |  |  | 870 | [10 empty] | 76.50 |  |  |  | 76.50 | [5 empty] | 76.67 |  |  | 81.45 |  |  |  | 14.43 |  | 12.90 | [8 empty] | 10.60 |  |  |  |  | 0.00
1984 |  |  |  | 6374.00 |  |  | 7774 |  |  |  | 870 | [10 empty] | 83.44 |  |  |  | 83.44 | [5 empty] | 83.41 |  |  | 88.50 |  |  |  | 4.99 |  | 4.38 | [8 empty] | 12.18 |  |  |  |  | 0.00
1985 |  |  |  | 5979.00 |  |  | 8077 |  |  |  | 870 | [10 empty] | 81.07 |  |  |  | 90.80 | [5 empty] | 78.45 |  |  | 92.20 |  |  |  | 1.13 |  | 1.04 | [8 empty] | 8.16 |  |  |  |  | 9.72
1986 |  |  |  | 4005.00 |  |  | 5429 |  |  |  | 870 | [10 empty] | 54.78 |  |  |  | 59.15 | [5 empty] | 52.55 |  |  | 61.97 |  |  |  | 5.05 |  | 3.15 | [8 empty] | 37.70 |  |  |  |  | 4.37
1987 |  |  |  | 7337.00 |  |  | 8733 |  |  |  | 870 | [10 empty] | 97.57 |  |  |  | 98.50 | [5 empty] | 96.27 |  |  | 99.69 |  |  |  | 1.50 |  | 1.50 | [8 empty] | 0.00 |  |  |  |  | 0.93
1988 |  |  |  | 6310.00 |  |  | 7520 |  |  |  | 870 | [10 empty] | 83.89 |  |  |  | 84.93 | [5 empty] | 82.57 |  |  | 85.61 |  |  |  | 8.66 |  | 8.05 | [8 empty] | 7.01 |  |  |  |  | 1.05
1989 |  |  |  | 6508.00 |  |  | 7854 |  |  |  | 870 | [10 empty] | 87.85 |  |  |  | 88.40 | [5 empty] | 85.39 |  |  | 89.66 |  |  |  | 1.29 |  | 1.16 | [8 empty] | 10.44 |  |  |  |  | 0.54
1990 |  |  |  | 6683.00 |  |  | 8082 |  |  |  | 870 | [10 empty] | 88.40 |  |  |  | 90.85 | [5 empty] | 87.69 |  |  | 92.26 |  |  |  | 1.09 |  | 1.00 | [8 empty] | 8.15 |  |  |  |  | 2.45
1991 |  |  |  | 6163.00 |  |  | 7714 |  |  |  | 870 | [10 empty] | 80.98 |  |  |  | 86.71 | [5 empty] | 80.87 |  |  | 88.06 |  |  |  | 2.10 |  | 1.86 | [8 empty] | 11.43 |  |  |  |  | 5.73
1992 |  |  |  | 6059.00 |  |  | 7807 |  |  |  | 870 | [10 empty] | 79.10 |  |  |  | 80.45 | [5 empty] | 79.28 |  |  | 88.88 |  |  |  | 5.88 |  | 5.02 | [8 empty] | 14.52 |  |  |  |  | 1.35
1993 |  |  |  | 7317.00 |  |  | 8459 |  |  |  | 870 | [10 empty] | 96.37 |  |  |  | 99.80 | [5 empty] | 96.01 |  |  | 96.56 |  |  |  | 0.20 |  | 0.20 | [8 empty] | 0.00 |  |  |  |  | 3.44
1994 |  |  |  | 6737.00 |  |  | 8018 |  |  |  | 863 | [10 empty] | 89.97 |  |  |  | 90.66 | [5 empty] | 89.12 |  |  | 91.53 |  |  |  | 0.66 |  | 0.60 | [8 empty] | 8.74 |  |  |  |  | 0.69
1995 |  |  |  | 5442.00 |  |  | 6488 |  |  |  | 882 | [10 empty] | 69.96 |  |  |  | 72.88 | [5 empty] | 70.36 |  |  | 74.06 |  |  |  | 2.38 |  | 1.77 | [8 empty] | 25.35 |  |  |  |  | 2.92
1996 |  |  |  | 7210.66 |  |  | 7823 |  |  |  | 931 | [10 empty] | 88.22 |  |  |  | 88.40 | [5 empty] | 88.18 |  |  | 89.07 |  |  |  | 1.71 |  | 1.54 | [8 empty] | 10.06 |  |  |  |  | 0.18
1997 |  |  |  | 7942.57 |  |  | 8385 |  |  |  | 962 | [10 empty] | 94.30 |  |  |  | 95.50 | [5 empty] | 94.25 |  |  | 95.72 |  |  |  | 1.16 |  | 1.12 | [8 empty] | 3.38 |  |  |  |  | 1.20
1998 |  |  |  | 7264.00 |  |  | 7777 |  |  |  | 962 | [10 empty] | 86.32 |  |  |  | 87.44 | [5 empty] | 86.20 |  |  | 88.78 |  |  |  | 2.68 |  | 2.41 | [8 empty] | 10.15 |  |  |  |  | 1.12
1999 |  |  |  | 7272.00 |  |  | 7905 |  |  |  | 962 | [10 empty] | 85.53 |  |  |  | 86.91 | [5 empty] | 86.29 |  |  | 90.24 |  |  |  | 3.34 |  | 3.00 | [8 empty] | 10.09 |  |  |  |  | 1.38
2000 |  |  |  | 8457.00 |  |  | 8782 |  |  |  | 962 | [10 empty] | 99.28 |  |  |  | 99.28 | [5 empty] | 100.08 |  |  | 99.98 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 0.70 |  |  |  |  | 0.00
2001 |  |  |  | 6969.00 |  |  | 7481 |  |  |  | 962 | [10 empty] | 82.52 |  |  |  | 91.20 | [5 empty] | 82.70 |  |  | 85.40 |  |  |  | 0.24 |  | 0.22 | [8 empty] | 8.58 |  |  |  |  | 8.69
2002 |  |  |  | 7047.15 |  |  | 7631 |  |  |  | 962 | [10 empty] | 83.92 |  |  |  | 85.98 | [5 empty] | 83.62 |  |  | 87.11 |  |  |  | 0.96 |  | 0.83 | [8 empty] | 13.19 |  |  |  |  | 2.06
2003 |  |  |  | 7990.42 |  |  | 8552 |  |  |  | 962 | [10 empty] | 95.11 |  |  |  | 95.54 | [5 empty] | 94.81 |  |  | 97.61 |  |  |  | 4.46 |  | 4.46 | [8 empty] | 0.00 |  |  |  |  | 0.44
2004 |  |  |  | 7106.47 |  |  | 7456 |  |  |  | 962 | [10 empty] | 84.50 |  |  |  | 84.50 | [5 empty] | 84.10 |  |  | 84.88 |  |  |  | 2.05 |  | 2.41 | [8 empty] | 13.09 |  |  |  |  | 0.00
2005 |  |  |  | 6810.95 |  |  | 7403 |  |  |  | 962 | [10 empty] | 80.24 |  |  |  | 82.67 | [5 empty] | 80.82 |  |  | 84.51 |  |  |  | 2.72 |  | 4.08 | [8 empty] | 13.25 |  |  |  |  | 2.43
2006 |  |  |  | 8186.91 |  |  | 8693 |  |  |  | 962 | [10 empty] | 98.79 |  |  |  | 98.79 | [5 empty] | 97.15 |  |  | 99.24 |  |  |  | 1.21 |  | 1.21 | [8 empty] | 0.00 |  |  |  |  | 0.00
2007 |  |  |  | 7055.90 |  |  | 7627 |  |  |  | 962 | [10 empty] | 85.07 |  |  |  | 85.58 | [5 empty] | 83.73 |  |  | 87.07 |  |  |  | 4.93 |  | 4.44 | [8 empty] | 9.98 |  |  |  |  | 0.50
2008 |  |  |  | 7264.54 |  |  | 7650 |  |  |  | 962 | [10 empty] | 85.25 |  |  |  | 86.24 | [5 empty] | 85.97 |  |  | 87.09 |  |  |  | 1.60 |  | 1.68 | [8 empty] | 12.09 |  |  |  |  | 0.98
2009 |  |  |  | 8269.54 |  |  | 8679 |  |  |  | 962 | [10 empty] | 97.83 |  |  |  | 98.68 | [5 empty] | 98.13 |  |  | 99.08 |  |  |  | 1.04 |  | 1.03 | [8 empty] | 0.29 |  |  |  |  | 0.85
2010 |  |  |  | 7316.10 |  |  | 7752 |  |  |  | 962 | [10 empty] | 86.35 |  |  |  | 87.47 | [5 empty] | 86.82 |  |  | 88.49 |  |  |  | 1.64 |  | 1.46 | [8 empty] | 11.07 |  |  |  |  | 1.12
2011 |  |  |  | 6848.28 |  |  | 7333 |  |  |  | 962 | [10 empty] | 81.20 |  |  |  | 82.59 | [5 empty] | 81.26 |  |  | 83.71 |  |  |  | 1.97 |  | 2.96 | [8 empty] | 14.45 |  |  |  |  | 1.40
2012 |  |  |  | 6763.30 |  |  | 8784 |  |  |  | 962 | [10 empty] | 79.44 |  |  |  | 82.88 | [5 empty] | 80.04 |  |  | 100.00 |  |  |  | 17.12 |  | 17.12 | [8 empty] | 0.00 |  |  |  |  | 3.44
2013 |  |  |  | 6878.12 |  |  | 7203 |  |  |  | 962 | [10 empty] | 80.40 |  |  |  | 80.90 | [5 empty] | 81.62 |  |  | 82.23 |  |  |  | 1.20 |  | 4.40 | [8 empty] | 14.70 |  |  |  |  | 0.49
2014 |  |  |  | 7192.76 |  |  | 7503 |  |  |  | 962 | [10 empty] | 84.51 |  |  |  | 85.06 | [5 empty] | 85.35 |  |  | 85.65 |  |  |  | 0.32 |  | 1.57 | [8 empty] | 13.37 |  |  |  |  | 0.55
2015 |  |  |  | 5927.29 |  |  | 6211 |  |  |  | 962 | [10 empty] | 69.69 |  |  |  | 69.84 | [5 empty] | 70.34 |  |  | 70.90 |  |  |  | 7.56 |  | 7.34 | [8 empty] | 22.82 |  |  |  |  | 0.15
2016 |  |  |  | 2871.03 |  |  | 3026 |  |  |  | 962 | [10 empty] | 33.69 |  |  |  | 33.85 | [5 empty] | 33.98 |  |  | 34.45 |  |  |  | 52.16 |  | 42.50 | [8 empty] | 23.65 |  |  |  |  | 0.16
2017 |  |  |  | 3409.97 |  |  | 3675 |  |  |  | 962 | [10 empty] | 40.36 |  |  |  | 41.23 | [5 empty] | 40.46 |  |  | 41.95 |  |  |  | 55.23 |  | 50.86 | [8 empty] | 7.90 |  |  |  |  | 0.87
2018 |  |  |  | 7633.87 |  |  | 8024 |  |  |  | 962 | [10 empty] | 89.79 |  |  |  | 91.05 | [5 empty] | 90.59 |  |  | 91.60 |  |  |  | 0.40 |  | 0.36 | [8 empty] | 8.59 |  |  |  |  | 1.26
2019 |  |  |  | 8319.24 |  |  | 8714 |  |  |  | 962 | [10 empty] | 98.19 |  |  |  | 99.28 | [5 empty] | 98.72 |  |  | 99.47 |  |  |  | 0.43 |  | 0.43 | [8 empty] | 0.29 |  |  |  |  | 1.10
2020 |  |  |  | 303.85 |  |  | 434 |  |  |  | 962 | [10 empty] | 3.57 |  |  |  | 3.57 | [5 empty] | 3.60 |  |  | 4.94 |  |  |  | 30.28 |  | 43.82 | [8 empty] | 52.61 |  |  |  |  | 0.00
2021 |  |  |  | 8384.09 |  |  | 8760 |  |  |  | 962 | [10 empty] | 98.96 |  |  |  | 99.75 | [5 empty] | 99.49 |  |  | 100.00 |  |  |  | 0.23 |  | 0.23 | [8 empty] | 0.02 |  |  |  |  | 0.79
2022 |  |  |  | 4685.63 |  |  | 4940 |  |  |  | 962 | [10 empty] | 55.27 |  |  |  | 55.67 | [5 empty] | 55.60 |  |  | 56.39 |  |  |  | 6.80 |  | 31.55 | [8 empty] | 12.78 |  |  |  |  | 0.40
2023 |  |  |  | 8242.06 |  |  | 8760 |  |  |  | 962 | [10 empty] | 97.40 |  |  |  | 98.50 | [5 empty] | 97.80 |  |  | 100.00 |  |  |  | 1.47 |  | 1.47 | [8 empty] | 0.03 |  |  |  |  | 1.10
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1975 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 333
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 874
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 22
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 41
L. |  | Human factor related | [39 empty] | 82
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 59
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 6
Z. |  | Other | [39 empty] | 6
Subtotal | [37 empty] | 937 |  |  |  | 421 | [11 empty] | 65
Total | [22 empty] | 0 | [14 empty] | 1423
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1975 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 88
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 57
16. |  |  | Steam generation systems | [34 empty] | 12
31. |  |  | Turbine and auxiliaries | [34 empty] | 9
32. |  |  | Feedwater and Main Steam System | [34 empty] | 188
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 12
42. |  |  | Electrical Power Supply Systems | [34 empty] | 14
Total | [37 empty] | 410

## TIHANGE-2
2023 Operating Experience
BE-6 | [8 empty] | TIHANGE-2 | [26 empty] | BELGIUM
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | EBL (ENGIE ELECTRABEL )
Owner | [7 empty] | : | EBL (ENGIE ELECTRABEL )
Reactor Supplier | [7 empty] | : | FRAMACEC (FRAMACECO ( FRAMATOME-ACEC-COCKERILL ))
Turbine Supplier | [7 empty] | : | ALS/ACEC (TURBINE: ALSTOM; ALTERNATOR: ACEC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-04-01
Thermal power | [12 empty] | : |  |  | 3064 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-10-13
Gross electrical power | [12 empty] | : |  |  | 1055 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-06-01
Reference unit power (net) | [12 empty] | : |  |  | 1008 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.52
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 324.7
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.35
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.35 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.4
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.85 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 32 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 6
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 721.74 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.24 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.61 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.39 %
Load Factor (LF) | [18 empty] | : | 96.24 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.37 %
Operating Factor (OF) | [18 empty] | : | 99.87 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 25 hours
Annual Summary
[5 empty] | Oct | Nov |  |  |  | Dec |  | Feb | [8 empty] | Mar |  |  | Apr | [6 empty] | May |  | Jun |  |  |  | Jul |  |  | Aug |  |  | Sep | [9 empty] | Jan |  |  | Annual
GW(e)-h | [52 empty] | 721.74 |  |  | 721.74
EAF [%] | [52 empty] | 96.24 |  |  | 96.24
UCF [%] | [52 empty] | 99.61 |  |  | 99.61
LF [%] | [52 empty] | 96.24 |  |  | 96.24
OF [%] | [52 empty] | 99.87 |  |  | 99.87
FLR [%] | [52 empty] | 0.00 |  |  | 0.00
UCL [%] | [52 empty] | 0.00 |  |  | 0.00
PUF [%] | [52 empty] | 0.39 |  |  | 0.39
XUF [%] | [52 empty] | 3.37 |  |  | 3.37
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 270828.36 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.2 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.06 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 10.47 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.91 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.62 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.06 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.85 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 5507.00 |  |  | 6373 |  |  |  | 901 | [10 empty] | 86.91 |  |  |  | 86.91 | [5 empty] | 86.90 |  |  | 89.78 |  |  |  | 6.11 |  | 5.65 | [8 empty] | 7.44 |  |  |  |  | 0.00
1984 |  |  |  | 6856.00 |  |  | 7693 |  |  |  | 901 | [10 empty] | 86.39 |  |  |  | 86.39 | [5 empty] | 86.63 |  |  | 87.58 |  |  |  | 4.58 |  | 4.15 | [8 empty] | 9.46 |  |  |  |  | 0.00
1985 |  |  |  | 6636.00 |  |  | 7890 |  |  |  | 900 | [10 empty] | 87.77 |  |  |  | 89.42 | [5 empty] | 84.17 |  |  | 90.07 |  |  |  | 2.48 |  | 2.27 | [8 empty] | 8.31 |  |  |  |  | 1.65
1986 |  |  |  | 6189.00 |  |  | 7509 |  |  |  | 900 | [10 empty] | 83.08 |  |  |  | 84.95 | [5 empty] | 78.50 |  |  | 85.72 |  |  |  | 3.80 |  | 3.35 | [8 empty] | 11.69 |  |  |  |  | 1.87
1987 |  |  |  | 6584.00 |  |  | 7477 |  |  |  | 900 | [10 empty] | 83.41 |  |  |  | 84.30 | [5 empty] | 83.51 |  |  | 85.35 |  |  |  | 5.97 |  | 5.35 | [8 empty] | 10.35 |  |  |  |  | 0.89
1988 |  |  |  | 6966.00 |  |  | 7992 |  |  |  | 900 | [10 empty] | 87.93 |  |  |  | 89.88 | [5 empty] | 88.11 |  |  | 90.98 |  |  |  | 1.01 |  | 0.91 | [8 empty] | 9.21 |  |  |  |  | 1.95
1989 |  |  |  | 6663.00 |  |  | 7728 |  |  |  | 901 | [10 empty] | 84.74 |  |  |  | 86.02 | [5 empty] | 84.42 |  |  | 88.22 |  |  |  | 2.34 |  | 2.06 | [8 empty] | 11.92 |  |  |  |  | 1.28
1990 |  |  |  | 6919.00 |  |  | 7827 |  |  |  | 901 | [10 empty] | 88.04 |  |  |  | 88.48 | [5 empty] | 87.66 |  |  | 89.35 |  |  |  | 3.01 |  | 2.75 | [8 empty] | 8.77 |  |  |  |  | 0.44
1991 |  |  |  | 6850.00 |  |  | 7790 |  |  |  | 901 | [10 empty] | 87.75 |  |  |  | 88.41 | [5 empty] | 86.79 |  |  | 88.93 |  |  |  | 2.26 |  | 2.04 | [8 empty] | 9.55 |  |  |  |  | 0.66
1992 |  |  |  | 6746.00 |  |  | 7912 |  |  |  | 901 | [10 empty] | 86.92 |  |  |  | 89.72 | [5 empty] | 85.24 |  |  | 90.07 |  |  |  | 0.29 |  | 0.26 | [8 empty] | 10.02 |  |  |  |  | 2.79
1993 |  |  |  | 6555.00 |  |  | 7507 |  |  |  | 901 | [10 empty] | 83.62 |  |  |  | 86.44 | [5 empty] | 83.05 |  |  | 85.70 |  |  |  | 1.49 |  | 1.31 | [8 empty] | 12.25 |  |  |  |  | 2.83
1994 |  |  |  | 7585.00 |  |  | 8501 |  |  |  | 894 | [10 empty] | 96.69 |  |  |  | 98.32 | [5 empty] | 96.85 |  |  | 97.04 |  |  |  | 1.68 |  | 1.68 | [8 empty] | 0.00 |  |  |  |  | 1.63
1995 |  |  |  | 6849.00 |  |  | 7697 |  |  |  | 921 | [10 empty] | 85.01 |  |  |  | 90.18 | [5 empty] | 84.88 |  |  | 87.87 |  |  |  | 1.08 |  | 0.99 | [8 empty] | 8.84 |  |  |  |  | 5.17
1996 |  |  |  | 7253.00 |  |  | 7810 |  |  |  | 943 | [10 empty] | 86.99 |  |  |  | 88.57 | [5 empty] | 87.51 |  |  | 88.91 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 11.34 |  |  |  |  | 1.58
1997 |  |  |  | 6854.00 |  |  | 7241 |  |  |  | 960 | [10 empty] | 81.31 |  |  |  | 82.29 | [5 empty] | 81.50 |  |  | 82.66 |  |  |  | 8.78 |  | 7.92 | [8 empty] | 9.79 |  |  |  |  | 0.99
1998 |  |  |  | 7664.00 |  |  | 8015 |  |  |  | 960 | [10 empty] | 90.56 |  |  |  | 91.05 | [5 empty] | 91.13 |  |  | 91.50 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 8.68 |  |  |  |  | 0.49
1999 |  |  |  | 8111.00 |  |  | 8380 |  |  |  | 960 | [10 empty] | 95.46 |  |  |  | 95.46 | [5 empty] | 96.45 |  |  | 95.66 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 4.41 |  |  |  |  | 0.01
2000 |  |  |  | 7481.00 |  |  | 7901 |  |  |  | 960 | [10 empty] | 87.97 |  |  |  | 89.44 | [5 empty] | 88.71 |  |  | 89.95 |  |  |  | 2.72 |  | 2.50 | [8 empty] | 8.05 |  |  |  |  | 1.48
2001 |  |  |  | 6976.00 |  |  | 7137 |  |  |  | 960 | [10 empty] | 80.69 |  |  |  | 80.77 | [5 empty] | 82.95 |  |  | 81.47 |  |  |  | 1.72 |  | 1.42 | [8 empty] | 17.81 |  |  |  |  | 0.08
2002 |  |  |  | 7833.39 |  |  | 7821 |  |  |  | 1008 | [10 empty] | 87.92 |  |  |  | 89.03 | [5 empty] | 88.71 |  |  | 89.28 |  |  |  | 0.26 |  | 0.23 | [8 empty] | 10.73 |  |  |  |  | 1.12
2003 |  |  |  | 7600.97 |  |  | 7589 |  |  |  | 1008 | [10 empty] | 85.56 |  |  |  | 86.34 | [5 empty] | 86.08 |  |  | 86.63 |  |  |  | 1.19 |  | 1.40 | [8 empty] | 12.26 |  |  |  |  | 0.79
2004 |  |  |  | 8517.32 |  |  | 8478 |  |  |  | 1008 | [10 empty] | 96.01 |  |  |  | 96.43 | [5 empty] | 96.19 |  |  | 96.52 |  |  |  | 3.57 |  | 3.57 | [8 empty] | 0.00 |  |  |  |  | 0.42
2005 |  |  |  | 7890.01 |  |  | 7929 |  |  |  | 1008 | [10 empty] | 89.48 |  |  |  | 90.09 | [5 empty] | 89.35 |  |  | 90.51 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 9.77 |  |  |  |  | 0.61
2006 |  |  |  | 7219.32 |  |  | 7348 |  |  |  | 1008 | [10 empty] | 82.37 |  |  |  | 83.01 | [5 empty] | 81.76 |  |  | 83.88 |  |  |  | 2.31 |  | 3.86 | [8 empty] | 13.13 |  |  |  |  | 0.64
2007 |  |  |  | 8751.57 |  |  | 8760 |  |  |  | 1008 | [10 empty] | 99.95 |  |  |  | 99.97 | [5 empty] | 99.11 |  |  | 100.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.00 |  |  |  |  | 0.02
2008 |  |  |  | 7129.35 |  |  | 7165 |  |  |  | 1008 | [10 empty] | 80.43 |  |  |  | 81.12 | [5 empty] | 80.52 |  |  | 81.57 |  |  |  | 0.33 |  | 2.75 | [8 empty] | 16.12 |  |  |  |  | 0.69
2009 |  |  |  | 7732.29 |  |  | 7664 |  |  |  | 1008 | [10 empty] | 86.69 |  |  |  | 86.76 | [5 empty] | 87.57 |  |  | 87.49 |  |  |  | 1.02 |  | 0.95 | [8 empty] | 12.29 |  |  |  |  | 0.07
2010 |  |  |  | 8823.79 |  |  | 8726 |  |  |  | 1008 | [10 empty] | 99.25 |  |  |  | 99.47 | [5 empty] | 99.93 |  |  | 99.61 |  |  |  | 0.53 |  | 0.53 | [8 empty] | 0.00 |  |  |  |  | 0.23
2011 |  |  |  | 7322.51 |  |  | 7345 |  |  |  | 1008 | [10 empty] | 82.86 |  |  |  | 83.26 | [5 empty] | 82.93 |  |  | 83.85 |  |  |  | 1.08 |  | 5.33 | [8 empty] | 11.41 |  |  |  |  | 0.40
2012 |  |  |  | 5506.11 |  |  | 5475 |  |  |  | 1008 | [10 empty] | 61.79 |  |  |  | 62.11 | [5 empty] | 62.19 |  |  | 62.33 |  |  |  | 0.59 |  | 25.24 | [8 empty] | 12.64 |  |  |  |  | 0.33
2013 |  |  |  | 4939.33 |  |  | 4963 |  |  |  | 1008 | [10 empty] | 55.58 |  |  |  | 55.75 | [5 empty] | 55.94 |  |  | 56.66 |  |  |  | 0.98 |  | 43.74 | [8 empty] | 0.51 |  |  |  |  | 0.17
2014 |  |  |  | 2056.12 |  |  | 2025 |  |  |  | 1008 | [10 empty] | 22.95 |  |  |  | 22.95 | [5 empty] | 23.29 |  |  | 23.12 |  |  |  | 74.07 |  | 65.55 | [8 empty] | 11.51 |  |  |  |  | 0.00
2015 |  |  |  | 385.00 |  |  | 411 |  |  |  | 1008 | [10 empty] | 4.29 |  |  |  | 4.29 | [5 empty] | 4.36 |  |  | 4.69 |  |  |  | 95.71 |  | 95.71 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 8603.65 |  |  | 8521 |  |  |  | 1008 | [10 empty] | 96.20 |  |  |  | 96.42 | [5 empty] | 97.17 |  |  | 97.01 |  |  |  | 3.56 |  | 3.56 | [8 empty] | 0.02 |  |  |  |  | 0.23
2017 |  |  |  | 7131.59 |  |  | 7351 |  |  |  | 1008 | [10 empty] | 80.14 |  |  |  | 80.45 | [5 empty] | 80.76 |  |  | 83.92 |  |  |  | 0.34 |  | 7.46 | [8 empty] | 12.09 |  |  |  |  | 0.31
2018 |  |  |  | 5478.07 |  |  | 5460 |  |  |  | 1008 | [10 empty] | 61.46 |  |  |  | 61.67 | [5 empty] | 62.04 |  |  | 62.33 |  |  |  | 1.85 |  | 17.88 | [8 empty] | 20.46 |  |  |  |  | 0.20
2019 |  |  |  | 3276.69 |  |  | 3377 |  |  |  | 1008 | [10 empty] | 37.06 |  |  |  | 37.70 | [5 empty] | 37.11 |  |  | 38.55 |  |  |  | 23.60 |  | 61.81 | [8 empty] | 0.49 |  |  |  |  | 0.65
2020 |  |  |  | 7373.82 |  |  | 7398 |  |  |  | 1008 | [10 empty] | 83.13 |  |  |  | 83.88 | [5 empty] | 83.28 |  |  | 84.22 |  |  |  | 2.92 |  | 4.17 | [8 empty] | 11.95 |  |  |  |  | 0.75
2021 |  |  |  | 7597.40 |  |  | 7835 |  |  |  | 1008 | [10 empty] | 85.75 |  |  |  | 86.16 | [5 empty] | 86.04 |  |  | 89.44 |  |  |  | 7.80 |  | 13.07 | [8 empty] | 0.76 |  |  |  |  | 0.41
2022 |  |  |  | 7476.91 |  |  | 7665 |  |  |  | 1008 | [10 empty] | 84.64 |  |  |  | 85.35 | [5 empty] | 84.68 |  |  | 87.50 |  |  |  | 1.99 |  | 2.57 | [8 empty] | 12.08 |  |  |  |  | 0.71
2023 |  |  |  | 721.74 |  |  | 743 |  |  |  | 1008 | [10 empty] | 96.24 |  |  |  | 99.61 | [5 empty] | 96.24 |  |  | 99.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.39 |  |  |  |  | 3.37
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1983 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 812
B. |  | Refuelling without maintenance | [39 empty] | 12
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 690 |  |  |  | 4
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 84
E. |  | Testing of plant systems or components | [39 empty] | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 29
M. |  | Governmental requirements or court decisions | [31 empty] | 1 | [19 empty] | 0
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 10
Z. |  | Other | [35 empty] | 9 |  |  |  | 1
Subtotal | [33 empty] | 1 |  |  |  | 783 |  |  |  | 860 | [11 empty] | 10
Total | [22 empty] | 1 | [14 empty] | 1653
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1983 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 491
12. |  |  | Reactor I&C Systems | [34 empty] | 9
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 31
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 38
16. |  |  | Steam generation systems | [34 empty] | 20
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 39
32. |  |  | Feedwater and Main Steam System | [34 empty] | 155
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 10
Total | [37 empty] | 812
Highlights (2023)
2023 02 01 : STOP FINAL

## TIHANGE-3
2023 Operating Experience
BE-8 | [8 empty] | TIHANGE-3 | [26 empty] | BELGIUM
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | EBL (ENGIE ELECTRABEL )
Owner | [7 empty] | : | EBL (ENGIE ELECTRABEL )
Reactor Supplier | [7 empty] | : | ACECOWEN (ACECOWEN (ACEC-COCKERILL-WESTINGHOUSE))
Turbine Supplier | [7 empty] | : | BBC/ACEC (BBC - CEM / ACEC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-11-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-06-15
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-09-01
Reference unit power (net) | [12 empty] | : |  |  | 1030 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.52
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 330.3
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.35
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.35 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7.28
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.47 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 28 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 6
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7544.13 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.74 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.03 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.27 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.9 %
Load Factor (LF) | [18 empty] | : | 83.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.79 %
Operating Factor (OF) | [18 empty] | : | 84.35 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1371 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 771.53 | 695.78 |  |  |  | 771.26 |  | 745.96 | [8 empty] | 770.69 |  |  | 730.07 | [6 empty] | 750.27 |  | 419.72 |  |  |  | 0.00 |  |  | 373.75 |  |  | 746.60 | [9 empty] | 768.50 |  |  | 7544.13
EAF [%] |  |  |  |  | 99.81 | 99.75 |  |  |  | 99.98 |  | 99.81 | [8 empty] | 99.81 |  |  | 97.69 | [6 empty] | 97.15 |  | 54.35 |  |  |  | 0.00 |  |  | 48.61 |  |  | 99.98 | [9 empty] | 99.98 |  |  | 83.03
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.98 |  | 99.96 | [8 empty] | 99.95 |  |  | 99.87 | [6 empty] | 99.93 |  | 58.05 |  |  |  | 0.00 |  |  | 48.61 |  |  | 99.98 | [9 empty] | 99.99 |  |  | 83.82
LF [%] |  |  |  |  | 99.90 | 99.75 |  |  |  | 100.00 |  | 99.81 | [8 empty] | 99.80 |  |  | 97.69 | [6 empty] | 97.15 |  | 54.35 |  |  |  | 0.00 |  |  | 48.71 |  |  | 100.67 | [9 empty] | 100.28 |  |  | 83.13
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 58.60 |  |  |  | 0.00 |  |  | 53.96 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.35
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 0.01 |  |  | 0.02 | [6 empty] | 0.02 |  | 0.05 |  |  |  | 0.00 |  |  | 13.04 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 0.74
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 0.01 |  |  | 0.02 | [6 empty] | 0.02 |  | 0.03 |  |  |  | 0.00 |  |  | 26.78 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 2.27
PUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.01 |  | 0.03 | [8 empty] | 0.04 |  |  | 0.11 | [6 empty] | 0.04 |  | 41.93 |  |  |  | 100.00 |  |  | 24.61 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 13.90
XUF [%] |  |  |  |  | 0.18 | 0.25 |  |  |  | 0.00 |  | 0.15 | [8 empty] | 0.13 |  |  | 2.19 | [6 empty] | 2.78 |  | 3.70 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 0.79
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 297104.96 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.52 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.43 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.05 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.35 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.93 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | Data not provided
1986 |  |  |  | 7558.00 |  |  | 7733 |  |  |  | 1020 | [10 empty] | 85.57 |  |  |  | 86.51 | [5 empty] | 84.59 |  |  | 88.28 |  |  |  | 4.86 |  | 4.42 | [8 empty] | 9.07 |  |  |  |  | 0.94
1987 |  |  |  | 7829.00 |  |  | 7872 |  |  |  | 1020 | [10 empty] | 87.31 |  |  |  | 89.01 | [5 empty] | 87.62 |  |  | 89.86 |  |  |  | 0.98 |  | 0.88 | [8 empty] | 10.12 |  |  |  |  | 1.70
1988 |  |  |  | 7623.00 |  |  | 7773 |  |  |  | 1020 | [10 empty] | 85.05 |  |  |  | 87.38 | [5 empty] | 85.08 |  |  | 88.49 |  |  |  | 3.04 |  | 2.74 | [8 empty] | 9.88 |  |  |  |  | 2.33
1989 |  |  |  | 7749.00 |  |  | 7790 |  |  |  | 1020 | [10 empty] | 86.99 |  |  |  | 87.45 | [5 empty] | 86.72 |  |  | 88.93 |  |  |  | 0.89 |  | 0.79 | [8 empty] | 11.76 |  |  |  |  | 0.46
1990 |  |  |  | 7794.00 |  |  | 7924 |  |  |  | 1020 | [10 empty] | 87.11 |  |  |  | 90.01 | [5 empty] | 87.23 |  |  | 90.46 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 9.73 |  |  |  |  | 2.90
1991 |  |  |  | 7649.00 |  |  | 7903 |  |  |  | 1020 | [10 empty] | 86.15 |  |  |  | 88.35 | [5 empty] | 85.61 |  |  | 90.22 |  |  |  | 2.95 |  | 2.69 | [8 empty] | 8.96 |  |  |  |  | 2.20
1992 |  |  |  | 8335.00 |  |  | 8246 |  |  |  | 1020 | [10 empty] | 93.30 |  |  |  | 93.36 | [5 empty] | 93.03 |  |  | 93.88 |  |  |  | 0.55 |  | 0.51 | [8 empty] | 6.13 |  |  |  |  | 0.06
1993 |  |  |  | 7748.00 |  |  | 7874 |  |  |  | 1020 | [10 empty] | 88.06 |  |  |  | 89.50 | [5 empty] | 86.71 |  |  | 89.89 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 10.49 |  |  |  |  | 1.43
1994 |  |  |  | 7480.00 |  |  | 7666 |  |  |  | 1015 | [10 empty] | 84.68 |  |  |  | 86.84 | [5 empty] | 84.13 |  |  | 87.51 |  |  |  | 3.22 |  | 2.89 | [8 empty] | 10.27 |  |  |  |  | 2.16
1995 |  |  |  | 7559.00 |  |  | 7632 |  |  |  | 1015 | [10 empty] | 84.70 |  |  |  | 86.70 | [5 empty] | 85.01 |  |  | 87.12 |  |  |  | 1.06 |  | 0.93 | [8 empty] | 12.37 |  |  |  |  | 2.00
1996 |  |  |  | 7189.00 |  |  | 7142 |  |  |  | 1015 | [10 empty] | 81.08 |  |  |  | 81.08 | [5 empty] | 80.63 |  |  | 81.31 |  |  |  | 11.24 |  | 10.26 | [8 empty] | 8.66 |  |  |  |  | 0.00
1997 |  |  |  | 8357.00 |  |  | 8342 |  |  |  | 1015 | [10 empty] | 94.40 |  |  |  | 99.15 | [5 empty] | 93.99 |  |  | 95.23 |  |  |  | 0.49 |  | 0.49 | [8 empty] | 0.36 |  |  |  |  | 4.76
1998 |  |  |  | 6738.00 |  |  | 6903 |  |  |  | 1015 | [10 empty] | 75.93 |  |  |  | 77.89 | [5 empty] | 75.78 |  |  | 78.80 |  |  |  | 0.46 |  | 0.36 | [8 empty] | 21.75 |  |  |  |  | 1.96
1999 |  |  |  | 8799.00 |  |  | 8686 |  |  |  | 1015 | [10 empty] | 98.92 |  |  |  | 99.13 | [5 empty] | 98.96 |  |  | 99.16 |  |  |  | 0.87 |  | 0.87 | [8 empty] | 0.00 |  |  |  |  | 0.21
2000 |  |  |  | 7597.00 |  |  | 7656 |  |  |  | 1015 | [10 empty] | 84.93 |  |  |  | 86.40 | [5 empty] | 85.21 |  |  | 87.16 |  |  |  | 5.04 |  | 4.59 | [8 empty] | 9.01 |  |  |  |  | 1.47
2001 |  |  |  | 7729.00 |  |  | 7929 |  |  |  | 1015 | [10 empty] | 86.49 |  |  |  | 89.90 | [5 empty] | 86.92 |  |  | 90.50 |  |  |  | 2.47 |  | 2.28 | [8 empty] | 7.82 |  |  |  |  | 3.41
2002 |  |  |  | 8340.47 |  |  | 8368 |  |  |  | 1015 | [10 empty] | 93.71 |  |  |  | 95.68 | [5 empty] | 93.80 |  |  | 95.53 |  |  |  | 1.23 |  | 1.19 | [8 empty] | 3.13 |  |  |  |  | 1.97
2003 |  |  |  | 7661.54 |  |  | 7846 |  |  |  | 1015 | [10 empty] | 86.51 |  |  |  | 89.43 | [5 empty] | 86.16 |  |  | 89.56 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 10.45 |  |  |  |  | 2.91
2004 |  |  |  | 7936.43 |  |  | 7969 |  |  |  | 1015 | [10 empty] | 89.18 |  |  |  | 90.40 | [5 empty] | 89.02 |  |  | 90.72 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 9.50 |  |  |  |  | 1.22
2005 |  |  |  | 8707.53 |  |  | 8753 |  |  |  | 1015 | [10 empty] | 99.58 |  |  |  | 99.77 | [5 empty] | 97.93 |  |  | 99.92 |  |  |  | 0.23 |  | 0.23 | [8 empty] | 0.00 |  |  |  |  | 0.18
2006 |  |  |  | 7237.59 |  |  | 7592 |  |  |  | 1015 | [10 empty] | 83.33 |  |  |  | 86.09 | [5 empty] | 81.40 |  |  | 86.67 |  |  |  | 1.08 |  | 0.94 | [8 empty] | 12.97 |  |  |  |  | 2.76
2007 |  |  |  | 7339.40 |  |  | 7406 |  |  |  | 1015 | [10 empty] | 82.97 |  |  |  | 83.40 | [5 empty] | 82.54 |  |  | 84.54 |  |  |  | 4.73 |  | 4.14 | [8 empty] | 12.47 |  |  |  |  | 0.43
2008 |  |  |  | 8385.26 |  |  | 8365 |  |  |  | 1015 | [10 empty] | 93.88 |  |  |  | 94.26 | [5 empty] | 94.05 |  |  | 95.23 |  |  |  | 0.75 |  | 0.71 | [8 empty] | 5.03 |  |  |  |  | 0.38
2009 |  |  |  | 7717.15 |  |  | 7480 |  |  |  | 1054 | [10 empty] | 84.64 |  |  |  | 85.23 | [5 empty] | 84.61 |  |  | 85.39 |  |  |  | 0.23 |  | 3.02 | [8 empty] | 11.75 |  |  |  |  | 0.59
2010 |  |  |  | 7563.23 |  |  | 7489 |  |  |  | 1046 | [10 empty] | 81.88 |  |  |  | 82.49 | [5 empty] | 82.02 |  |  | 85.49 |  |  |  | 3.79 |  | 4.91 | [8 empty] | 12.60 |  |  |  |  | 0.61
2011 |  |  |  | 8981.89 |  |  | 8701 |  |  |  | 1046 | [10 empty] | 98.01 |  |  |  | 99.11 | [5 empty] | 98.02 |  |  | 99.33 |  |  |  | 0.73 |  | 0.73 | [8 empty] | 0.15 |  |  |  |  | 1.10
2012 |  |  |  | 7974.73 |  |  | 7800 |  |  |  | 1046 | [10 empty] | 87.85 |  |  |  | 88.17 | [5 empty] | 86.79 |  |  | 88.80 |  |  |  | 0.53 |  | 1.10 | [8 empty] | 10.72 |  |  |  |  | 0.33
2013 |  |  |  | 8094.07 |  |  | 7839 |  |  |  | 1046 | [10 empty] | 88.34 |  |  |  | 88.89 | [5 empty] | 88.33 |  |  | 89.49 |  |  |  | 0.63 |  | 0.56 | [8 empty] | 10.54 |  |  |  |  | 0.55
2014 |  |  |  | 8800.74 |  |  | 8550 |  |  |  | 1046 | [10 empty] | 96.61 |  |  |  | 99.30 | [5 empty] | 96.05 |  |  | 97.60 |  |  |  | 0.68 |  | 0.68 | [8 empty] | 0.02 |  |  |  |  | 2.69
2015 |  |  |  | 7336.42 |  |  | 7264 |  |  |  | 1038 | [10 empty] | 80.45 |  |  |  | 82.40 | [5 empty] | 80.48 |  |  | 82.92 |  |  |  | 4.90 |  | 4.25 | [8 empty] | 13.35 |  |  |  |  | 1.95
2016 |  |  |  | 7835.57 |  |  | 7623 |  |  |  | 1038 | [10 empty] | 85.78 |  |  |  | 86.19 | [5 empty] | 85.94 |  |  | 86.78 |  |  |  | 0.30 |  | 4.46 | [8 empty] | 9.36 |  |  |  |  | 0.40
2017 |  |  |  | 8963.79 |  |  | 8737 |  |  |  | 1038 | [10 empty] | 98.52 |  |  |  | 99.59 | [5 empty] | 98.58 |  |  | 99.74 |  |  |  | 0.41 |  | 0.41 | [8 empty] | 0.00 |  |  |  |  | 1.07
2018 |  |  |  | 2221.56 |  |  | 2138 |  |  |  | 1038 | [10 empty] | 24.37 |  |  |  | 24.37 | [5 empty] | 24.43 |  |  | 24.41 |  |  |  | 0.00 |  | 63.44 | [8 empty] | 12.19 |  |  |  |  | 0.00
2019 |  |  |  | 8945.12 |  |  | 8758 |  |  |  | 1038 | [10 empty] | 98.45 |  |  |  | 99.43 | [5 empty] | 98.37 |  |  | 99.98 |  |  |  | 0.03 |  | 0.05 | [8 empty] | 0.52 |  |  |  |  | 0.98
2020 |  |  |  | 5838.22 |  |  | 5686 |  |  |  | 1038 | [10 empty] | 63.97 |  |  |  | 64.08 | [5 empty] | 64.03 |  |  | 64.73 |  |  |  | 0.59 |  | 0.38 | [8 empty] | 35.54 |  |  |  |  | 0.11
2021 |  |  |  | 9001.86 |  |  | 8760 |  |  |  | 1038 | [10 empty] | 99.16 |  |  |  | 99.96 | [5 empty] | 99.00 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.04 |  |  |  |  | 0.80
2022 |  |  |  | 7366.37 |  |  | 7297 |  |  |  | 1038 | [10 empty] | 81.11 |  |  |  | 82.64 | [5 empty] | 81.01 |  |  | 83.30 |  |  |  | 5.00 |  | 4.35 | [8 empty] | 13.01 |  |  |  |  | 1.53
2023 |  |  |  | 7544.13 |  |  | 7389 |  |  |  | 1030 | [10 empty] | 83.03 |  |  |  | 83.82 | [5 empty] | 83.13 |  |  | 84.35 |  |  |  | 0.74 |  | 2.27 | [8 empty] | 13.90 |  |  |  |  | 0.79
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 198 | [14 empty] | 272
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1172 | [14 empty] | 720 |  |  |  | 7
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 21
E. |  | Testing of plant systems or components | [35 empty] | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 3
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 14 | [15 empty] | 15
Z. |  | Other | [35 empty] | 4
Subtotal | [22 empty] | 1172 |  |  |  | 198 | [10 empty] | 760 |  |  |  | 283 | [11 empty] | 16
Total | [22 empty] | 1370 | [14 empty] | 1059
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [19 empty] | 145 | [14 empty] | 29
16. |  |  | Steam generation systems | [34 empty] | 30
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [19 empty] | 53 | [14 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 169
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 198 | [14 empty] | 276