## BRUCE-1
2023 Operating Experience
CA-8 | [8 empty] | BRUCE-1 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 791 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-06-01
Thermal power | [12 empty] | : |  |  | 2620 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-01-14
Gross electrical power | [12 empty] | : |  |  | 868 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-09-01
Reference unit power (net) | [12 empty] | : |  |  | 811 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8750 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.37
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 4 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 1 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7022.43 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.38 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.59 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.38 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.59 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.03 %
Load Factor (LF) | [18 empty] | : | 101.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 98.73 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 111 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 609.35 | 547.12 |  |  |  | 608.44 |  | 589.55 | [8 empty] | 608.55 |  |  | 588.59 | [6 empty] | 597.66 |  | 597.28 |  |  |  | 484.57 |  |  | 600.07 |  |  | 585.93 | [9 empty] | 605.33 |  |  | 7022.43
EAF [%] |  |  |  |  | 99.92 | 100.00 |  |  |  | 99.88 |  | 100.00 | [8 empty] | 99.88 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 83.60 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.95 |  |  | 98.59
UCF [%] |  |  |  |  | 99.92 | 100.00 |  |  |  | 99.88 |  | 100.00 | [8 empty] | 99.88 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 83.60 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.95 |  |  | 98.59
LF [%] |  |  |  |  | 105.82 | 105.19 |  |  |  | 105.66 |  | 105.79 | [8 empty] | 105.68 |  |  | 105.62 | [6 empty] | 99.05 |  | 98.99 |  |  |  | 82.99 |  |  | 99.45 |  |  | 100.34 | [9 empty] | 100.32 |  |  | 101.13
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 84.58 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.73
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 16.40 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.05 |  |  | 1.38
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 16.40 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.05 |  |  | 1.38
PUF [%] |  |  |  |  | 0.08 | 0.00 |  |  |  | 0.12 |  | 0.00 | [8 empty] | 0.12 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 159703.03 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 17.51 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.79 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 15.89 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.22 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.89 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.54 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.43 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.62 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 1860.70 |  |  | 2698 |  |  |  | 740 | [10 empty] | 88.40 |  |  |  | 88.40 | [5 empty] | 88.04 |  |  | 94.47 |  |  |  | 11.60 |  | 11.60 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 4152.60 |  |  | 6649 |  |  |  | 740 | [10 empty] | 72.65 |  |  |  | 72.65 | [5 empty] | 64.24 |  |  | 76.11 |  |  |  | 15.38 |  | 13.20 | [8 empty] | 14.15 |  |  |  |  | 0.00
1979 |  |  |  | 5018.80 |  |  | 7334 |  |  |  | 740 | [10 empty] | 81.48 |  |  |  | 81.48 | [5 empty] | 76.58 |  |  | 82.81 |  |  |  | 18.52 |  | 18.52 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 5597.50 |  |  | 7902 |  |  |  | 740 | [10 empty] | 86.18 |  |  |  | 86.18 | [5 empty] | 86.11 |  |  | 89.96 |  |  |  | 7.87 |  | 7.36 | [8 empty] | 6.46 |  |  |  |  | 0.00
1981 |  |  |  | 6253.30 |  |  | 8486 |  |  |  | 740 | [10 empty] | 96.66 |  |  |  | 96.66 | [5 empty] | 96.47 |  |  | 96.87 |  |  |  | 3.34 |  | 3.34 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 5914.90 |  |  | 7884 |  |  |  | 740 | [10 empty] | 88.80 |  |  |  | 88.80 | [5 empty] | 91.25 |  |  | 90.00 |  |  |  | 11.20 |  | 11.20 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 5802.80 |  |  | 7590 |  |  |  | 740 | [10 empty] | 84.81 |  |  |  | 84.81 | [5 empty] | 89.52 |  |  | 86.64 |  |  |  | 15.04 |  | 15.01 | [8 empty] | 0.18 |  |  |  |  | 0.00
1984 |  |  |  | 6457.62 |  |  | 8546 |  |  |  | 740 | [10 empty] | 94.76 |  |  |  | 94.76 | [5 empty] | 99.35 |  |  | 97.29 |  |  |  | 5.10 |  | 5.09 | [8 empty] | 0.15 |  |  |  |  | 0.00
1985 |  |  |  | 6417.45 |  |  | 8349 |  |  |  | 772 | [10 empty] | 94.89 |  |  |  | 99.99 | [5 empty] | 94.78 |  |  | 95.31 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.00 |  |  |  |  | 5.10
1986 |  |  |  | 4398.02 |  |  | 5783 |  |  |  | 770 | [10 empty] | 65.33 |  |  |  | 65.97 | [5 empty] | 65.20 |  |  | 66.02 |  |  |  | 0.07 |  | 0.05 | [8 empty] | 33.98 |  |  |  |  | 0.64
1987 |  |  |  | 4087.07 |  |  | 5462 |  |  |  | 848 | [10 empty] | 60.73 |  |  |  | 63.26 | [5 empty] | 55.02 |  |  | 62.35 |  |  |  | 19.62 |  | 15.44 | [8 empty] | 21.29 |  |  |  |  | 2.54
1988 |  |  |  | 4642.66 |  |  | 6066 |  |  |  | 848 | [10 empty] | 65.95 |  |  |  | 66.85 | [5 empty] | 62.33 |  |  | 69.06 |  |  |  | 15.12 |  | 11.91 | [8 empty] | 21.24 |  |  |  |  | 0.89
1989 |  |  |  | 5094.78 |  |  | 7543 |  |  |  | 848 | [10 empty] | 68.74 |  |  |  | 69.91 | [5 empty] | 68.58 |  |  | 86.11 |  |  |  | 25.23 |  | 23.59 | [8 empty] | 6.50 |  |  |  |  | 1.16
1990 |  |  |  | 2451.13 |  |  | 4629 |  |  |  | 848 | [10 empty] | 32.98 |  |  |  | 33.58 | [5 empty] | 33.00 |  |  | 52.84 |  |  |  | 39.00 |  | 21.46 | [8 empty] | 44.96 |  |  |  |  | 0.60
1991 |  |  |  | 2394.45 |  |  | 3467 |  |  |  | 848 | [10 empty] | 32.22 |  |  |  | 34.08 | [5 empty] | 32.23 |  |  | 39.58 |  |  |  | 65.87 |  | 65.78 | [8 empty] | 0.14 |  |  |  |  | 1.87
1992 |  |  |  | 4546.54 |  |  | 7484 |  |  |  | 848 | [10 empty] | 61.04 |  |  |  | 61.04 | [5 empty] | 61.04 |  |  | 85.20 |  |  |  | 38.96 |  | 38.96 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 3389.20 |  |  | 6869 |  |  |  | 848 | [10 empty] | 45.67 |  |  |  | 45.67 | [5 empty] | 45.62 |  |  | 78.41 |  |  |  | 45.60 |  | 38.28 | [8 empty] | 16.06 |  |  |  |  | 0.00
1994 |  |  |  | 3849.03 |  |  | 7094 |  |  |  | 848 | [10 empty] | 51.81 |  |  |  | 51.81 | [5 empty] | 51.81 |  |  | 80.98 |  |  |  | 48.19 |  | 48.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 3531.45 |  |  | 5827 |  |  |  | 848 | [10 empty] | 47.54 |  |  |  | 47.54 | [5 empty] | 47.54 |  |  | 66.52 |  |  |  | 34.50 |  | 25.04 | [8 empty] | 27.42 |  |  |  |  | 0.00
1996 |  |  |  | 4326.40 |  |  | 7306 |  |  |  | 848 | [10 empty] | 58.09 |  |  |  | 58.09 | [5 empty] | 58.08 |  |  | 83.17 |  |  |  | 39.23 |  | 37.49 | [8 empty] | 4.42 |  |  |  |  | 0.00
1997 |  |  |  | 1383.58 |  |  | 2254 |  |  |  | 848 | [10 empty] | 23.52 |  |  |  | 23.52 | [5 empty] | 23.52 |  |  | 32.50 |  |  |  | 63.04 |  | 40.12 | [8 empty] | 36.35 |  |  |  |  | 0.00
1998 |  |  |  | Data not available - Suspended Operation
1999 |  |  |  | "
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | "
2005 |  |  |  | "
2006 |  |  |  | "
2007 |  |  |  | "
2008 |  |  |  | "
2009 |  |  |  | "
2010 |  |  |  | "
2011 |  |  |  | "
2012 |  |  |  | 743.65 |  |  | 1365 |  |  |  | 772 | [10 empty] | 42.86 |  |  |  | 42.86 | [5 empty] | 42.87 |  |  | 57.11 |  |  |  | 14.46 |  | 7.25 | [8 empty] | 49.90 |  |  |  |  | 0.00
2013 |  |  |  | 5257.07 |  |  | 7883 |  |  |  | 772 | [10 empty] | 85.98 |  |  |  | 86.14 | [5 empty] | 77.74 |  |  | 89.99 |  |  |  | 5.31 |  | 4.83 | [8 empty] | 9.03 |  |  |  |  | 0.16
2014 |  |  |  | 5630.95 |  |  | 7540 |  |  |  | 772 | [10 empty] | 85.52 |  |  |  | 85.52 | [5 empty] | 83.26 |  |  | 86.07 |  |  |  | 14.48 |  | 14.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 5816.97 |  |  | 7711 |  |  |  | 760 | [10 empty] | 86.96 |  |  |  | 86.96 | [5 empty] | 87.37 |  |  | 88.03 |  |  |  | 2.37 |  | 2.11 | [8 empty] | 10.94 |  |  |  |  | 0.00
2016 |  |  |  | 6122.17 |  |  | 8004 |  |  |  | 760 | [10 empty] | 90.36 |  |  |  | 90.42 | [5 empty] | 91.71 |  |  | 91.12 |  |  |  | 1.55 |  | 1.69 | [8 empty] | 7.89 |  |  |  |  | 0.06
2017 |  |  |  | 6434.23 |  |  | 8412 |  |  |  | 760 | [10 empty] | 95.42 |  |  |  | 95.42 | [5 empty] | 96.64 |  |  | 96.03 |  |  |  | 3.40 |  | 3.59 | [8 empty] | 0.99 |  |  |  |  | 0.01
2018 |  |  |  | 5424.38 |  |  | 7046 |  |  |  | 760 | [10 empty] | 79.92 |  |  |  | 79.93 | [5 empty] | 81.48 |  |  | 80.43 |  |  |  | 7.03 |  | 6.04 | [8 empty] | 14.03 |  |  |  |  | 0.01
2019 |  |  |  | 6720.15 |  |  | 8760 |  |  |  | 760 | [10 empty] | 99.95 |  |  |  | 99.95 | [5 empty] | 100.94 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  |  |  | 0.00
2020 |  |  |  | 6658.49 |  |  | 8630 |  |  |  | 774 | [10 empty] | 98.13 |  |  |  | 98.15 | [5 empty] | 97.94 |  |  | 98.25 |  |  |  | 0.76 |  | 0.75 | [8 empty] | 1.10 |  |  |  |  | 0.02
2021 |  |  |  | 5613.00 |  |  | 7075 |  |  |  | 774 | [10 empty] | 80.11 |  |  |  | 80.17 | [5 empty] | 82.78 |  |  | 80.76 |  |  |  | 1.24 |  | 4.84 | [8 empty] | 14.99 |  |  |  |  | 0.06
2022 |  |  |  | 6691.27 |  |  | 8298 |  |  |  | 774 | [10 empty] | 94.38 |  |  |  | 94.38 | [5 empty] | 98.69 |  |  | 94.73 |  |  |  | 1.07 |  | 1.02 | [8 empty] | 4.60 |  |  |  |  | 0.00
2023 |  |  |  | 7022.43 |  |  | 8649 |  |  |  | 811 | [10 empty] | 98.59 |  |  |  | 98.59 | [5 empty] | 101.13 |  |  | 98.73 |  |  |  | 1.38 |  | 1.38 | [8 empty] | 0.03 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1977 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 112 | [14 empty] | 752
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 733
E. |  | Testing of plant systems or components | [35 empty] | 72 |  |  |  | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 16
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 6
P. |  | Fire | [39 empty] | 4
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 13
Z. |  | Other | [35 empty] | 11 |  |  |  | 2
Subtotal | [26 empty] | 112 | [10 empty] | 816 |  |  |  | 782 | [11 empty] | 18
Total | [22 empty] | 112 | [14 empty] | 1616
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1977 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 47
12. |  |  | Reactor I&C Systems | [34 empty] | 70
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 78
14. |  |  | Safety Systems | [34 empty] | 55
15. |  |  | Reactor Cooling Systems | [34 empty] | 80
16. |  |  | Steam generation systems | [34 empty] | 206
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 26
31. |  |  | Turbine and auxiliaries | [19 empty] | 112 | [14 empty] | 39
32. |  |  | Feedwater and Main Steam System | [34 empty] | 23
34. |  |  | Miscellaneous Systems | [34 empty] | 19
41. |  |  | Main Generator Systems | [34 empty] | 65
42. |  |  | Electrical Power Supply Systems | [34 empty] | 41
Total | [22 empty] | 112 | [14 empty] | 749

## BRUCE-2
2023 Operating Experience
CA-9 | [8 empty] | BRUCE-2 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 791 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-12-01
Thermal power | [12 empty] | : |  |  | 2620 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-09-04
Gross electrical power | [12 empty] | : |  |  | 836 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-09-01
Reference unit power (net) | [12 empty] | : |  |  | 777 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8750 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.37
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 4 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 1 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6992.4 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.68 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.54 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.67 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.54 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 1.79 %
Load Factor (LF) | [18 empty] | : | 102.73 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 97.76 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 196 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 611.20 | 553.31 |  |  |  | 612.82 |  | 592.66 | [8 empty] | 563.10 |  |  | 461.87 | [6 empty] | 602.18 |  | 601.70 |  |  |  | 583.01 |  |  | 606.52 |  |  | 592.22 | [9 empty] | 611.82 |  |  | 6992.40
EAF [%] |  |  |  |  | 99.90 | 100.00 |  |  |  | 100.00 |  | 99.92 | [8 empty] | 92.11 |  |  | 78.52 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.92 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 97.54
UCF [%] |  |  |  |  | 99.90 | 100.00 |  |  |  | 100.00 |  | 99.92 | [8 empty] | 92.11 |  |  | 78.52 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.92 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 97.54
LF [%] |  |  |  |  | 105.73 | 105.97 |  |  |  | 106.01 |  | 105.94 | [8 empty] | 97.41 |  |  | 82.56 | [6 empty] | 104.17 |  | 104.09 |  |  |  | 104.21 |  |  | 104.92 |  |  | 105.86 | [9 empty] | 105.84 |  |  | 102.73
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 93.55 |  |  | 79.44 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.76
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.89 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 0.68
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.89 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 0.67
PUF [%] |  |  |  |  | 0.10 | 0.00 |  |  |  | 0.00 |  | 0.08 | [8 empty] | 0.00 |  |  | 21.48 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.08 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.79
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 143112.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 18.98 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.35 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 16.98 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 71.78 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.24 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.09 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.43 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 1696.80 |  |  | 2481 |  |  |  | 740 | [10 empty] | 87.01 |  |  |  | 87.01 | [5 empty] | 80.29 |  |  | 86.87 |  |  |  | 12.99 |  | 12.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 3603.80 |  |  | 5946 |  |  |  | 740 | [10 empty] | 65.23 |  |  |  | 65.45 | [5 empty] | 55.75 |  |  | 68.06 |  |  |  | 22.17 |  | 18.65 | [8 empty] | 15.91 |  |  |  |  | 0.22
1979 |  |  |  | 4408.80 |  |  | 6534 |  |  |  | 740 | [10 empty] | 73.76 |  |  |  | 73.76 | [5 empty] | 67.27 |  |  | 73.78 |  |  |  | 19.40 |  | 17.75 | [8 empty] | 8.49 |  |  |  |  | 0.00
1980 |  |  |  | 6074.90 |  |  | 8463 |  |  |  | 740 | [10 empty] | 93.52 |  |  |  | 93.52 | [5 empty] | 93.46 |  |  | 96.35 |  |  |  | 6.48 |  | 6.48 | [8 empty] | 0.00 |  |  |  |  | 0.00
1981 |  |  |  | 5795.10 |  |  | 7904 |  |  |  | 740 | [10 empty] | 89.57 |  |  |  | 89.57 | [5 empty] | 89.40 |  |  | 90.23 |  |  |  | 4.02 |  | 3.75 | [8 empty] | 6.67 |  |  |  |  | 0.00
1982 |  |  |  | 4432.40 |  |  | 6163 |  |  |  | 740 | [10 empty] | 68.00 |  |  |  | 68.00 | [5 empty] | 68.38 |  |  | 70.35 |  |  |  | 32.00 |  | 32.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 6112.80 |  |  | 7941 |  |  |  | 740 | [10 empty] | 89.51 |  |  |  | 89.51 | [5 empty] | 94.30 |  |  | 90.65 |  |  |  | 10.35 |  | 10.34 | [8 empty] | 0.15 |  |  |  |  | 0.00
1984 |  |  |  | 6223.90 |  |  | 8649 |  |  |  | 740 | [10 empty] | 91.03 |  |  |  | 91.03 | [5 empty] | 95.75 |  |  | 98.46 |  |  |  | 8.84 |  | 8.83 | [8 empty] | 0.15 |  |  |  |  | 0.00
1985 |  |  |  | 4979.30 |  |  | 6525 |  |  |  | 781 | [10 empty] | 73.54 |  |  |  | 77.95 | [5 empty] | 72.76 |  |  | 74.49 |  |  |  | 11.25 |  | 9.88 | [8 empty] | 12.17 |  |  |  |  | 4.41
1986 |  |  |  | 4257.63 |  |  | 5308 |  |  |  | 848 | [10 empty] | 56.97 |  |  |  | 59.21 | [5 empty] | 57.31 |  |  | 60.59 |  |  |  | 40.79 |  | 40.79 | [8 empty] | 0.00 |  |  |  |  | 2.24
1987 |  |  |  | 3781.40 |  |  | 4636 |  |  |  | 848 | [10 empty] | 50.56 |  |  |  | 52.18 | [5 empty] | 50.90 |  |  | 52.92 |  |  |  | 6.98 |  | 3.91 | [8 empty] | 43.91 |  |  |  |  | 1.62
1988 |  |  |  | 4971.25 |  |  | 7741 |  |  |  | 848 | [10 empty] | 71.70 |  |  |  | 71.70 | [5 empty] | 66.74 |  |  | 88.13 |  |  |  | 25.15 |  | 24.08 | [8 empty] | 4.22 |  |  |  |  | 0.00
1989 |  |  |  | 1316.31 |  |  | 2149 |  |  |  | 848 | [10 empty] | 17.72 |  |  |  | 17.82 | [5 empty] | 17.72 |  |  | 24.53 |  |  |  | 26.85 |  | 6.54 | [8 empty] | 75.64 |  |  |  |  | 0.10
1990 |  |  |  | 2578.32 |  |  | 3460 |  |  |  | 848 | [10 empty] | 35.22 |  |  |  | 35.48 | [5 empty] | 34.71 |  |  | 39.50 |  |  |  | 41.05 |  | 24.71 | [8 empty] | 39.81 |  |  |  |  | 0.26
1991 |  |  |  | 4483.48 |  |  | 5915 |  |  |  | 848 | [10 empty] | 60.25 |  |  |  | 63.20 | [5 empty] | 60.36 |  |  | 67.52 |  |  |  | 36.71 |  | 36.66 | [8 empty] | 0.15 |  |  |  |  | 2.95
1992 |  |  |  | 353.88 |  |  | 625 |  |  |  | 848 | [10 empty] | 4.73 |  |  |  | 4.73 | [5 empty] | 4.75 |  |  | 7.12 |  |  |  | 95.27 |  | 95.27 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 3016.81 |  |  | 6041 |  |  |  | 848 | [10 empty] | 40.75 |  |  |  | 40.75 | [5 empty] | 40.61 |  |  | 68.96 |  |  |  | 45.16 |  | 33.56 | [8 empty] | 25.69 |  |  |  |  | 0.00
1994 |  |  |  | 3882.47 |  |  | 7046 |  |  |  | 848 | [10 empty] | 52.26 |  |  |  | 52.26 | [5 empty] | 52.26 |  |  | 80.43 |  |  |  | 40.39 |  | 35.41 | [8 empty] | 12.32 |  |  |  |  | 0.00
1995 |  |  |  | 3791.00 |  |  | 6225 |  |  |  | 848 | [10 empty] | 66.34 |  |  |  | 66.34 | [5 empty] | 66.34 |  |  | 92.22 |  |  |  | 27.76 |  | 25.50 | [8 empty] | 8.16 |  |  |  |  | 0.00
1996 |  |  |  | Data not available - Suspended Operation
1997 |  |  |  | "
1998 |  |  |  | "
1999 |  |  |  | "
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | "
2005 |  |  |  | "
2006 |  |  |  | "
2007 |  |  |  | "
2008 |  |  |  | "
2009 |  |  |  | "
2010 |  |  |  | "
2011 |  |  |  | "
2012 |  |  |  | 1039.20 |  |  | 1826 |  |  |  | 734 | [10 empty] | 85.69 |  |  |  | 85.71 | [5 empty] | 85.41 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.29 |  |  |  |  | 0.02
2013 |  |  |  | 5607.65 |  |  | 8190 |  |  |  | 734 | [10 empty] | 88.10 |  |  |  | 88.23 | [5 empty] | 87.21 |  |  | 93.49 |  |  |  | 7.18 |  | 6.82 | [8 empty] | 4.94 |  |  |  |  | 0.13
2014 |  |  |  | 4910.32 |  |  | 6984 |  |  |  | 734 | [10 empty] | 81.74 |  |  |  | 81.74 | [5 empty] | 76.37 |  |  | 79.73 |  |  |  | 18.26 |  | 18.26 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6365.71 |  |  | 8660 |  |  |  | 730 | [10 empty] | 98.65 |  |  |  | 98.65 | [5 empty] | 99.55 |  |  | 98.86 |  |  |  | 0.68 |  | 0.68 | [8 empty] | 0.68 |  |  |  |  | 0.00
2016 |  |  |  | 4804.60 |  |  | 6408 |  |  |  | 760 | [10 empty] | 73.21 |  |  |  | 73.23 | [5 empty] | 73.17 |  |  | 72.95 |  |  |  | 2.57 |  | 6.93 | [8 empty] | 19.84 |  |  |  |  | 0.02
2017 |  |  |  | 6482.56 |  |  | 8560 |  |  |  | 760 | [10 empty] | 97.35 |  |  |  | 97.35 | [5 empty] | 97.37 |  |  | 97.72 |  |  |  | 0.88 |  | 0.87 | [8 empty] | 1.78 |  |  |  |  | 0.00
2018 |  |  |  | 5989.70 |  |  | 7828 |  |  |  | 760 | [10 empty] | 88.11 |  |  |  | 88.12 | [5 empty] | 89.97 |  |  | 89.36 |  |  |  | 7.67 |  | 7.32 | [8 empty] | 4.55 |  |  |  |  | 0.01
2019 |  |  |  | 5766.96 |  |  | 7526 |  |  |  | 760 | [10 empty] | 85.27 |  |  |  | 85.27 | [5 empty] | 86.62 |  |  | 85.91 |  |  |  | 2.92 |  | 2.57 | [8 empty] | 12.16 |  |  |  |  | 0.00
2020 |  |  |  | 6717.44 |  |  | 8584 |  |  |  | 777 | [10 empty] | 97.69 |  |  |  | 97.69 | [5 empty] | 98.42 |  |  | 97.72 |  |  |  | 1.69 |  | 1.68 | [8 empty] | 0.63 |  |  |  |  | 0.00
2021 |  |  |  | 6797.00 |  |  | 8760 |  |  |  | 777 | [10 empty] | 99.29 |  |  |  | 99.40 | [5 empty] | 99.86 |  |  | 100.00 |  |  |  | 0.47 |  | 0.47 | [8 empty] | 0.13 |  |  |  |  | 0.11
2022 |  |  |  | 5878.11 |  |  | 7481 |  |  |  | 777 | [10 empty] | 84.33 |  |  |  | 84.33 | [5 empty] | 86.36 |  |  | 85.40 |  |  |  | 0.28 |  | 0.23 | [8 empty] | 15.44 |  |  |  |  | 0.00
2023 |  |  |  | 6992.40 |  |  | 8564 |  |  |  | 777 | [10 empty] | 97.54 |  |  |  | 97.54 | [5 empty] | 102.73 |  |  | 97.76 |  |  |  | 0.68 |  | 0.67 | [8 empty] | 1.79 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1977 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 943
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 147 | [14 empty] | 901
E. |  | Testing of plant systems or components | [24 empty] | 48 | [14 empty] | 3
H. |  | Nuclear regulatory requirements | [39 empty] | 9
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 24
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 36
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 14
Z. |  | Other | [39 empty] | 30
Subtotal | [22 empty] | 147 |  |  |  | 48 | [10 empty] | 901 |  |  |  | 1021 | [11 empty] | 40
Total | [22 empty] | 195 | [14 empty] | 1962
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1977 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 119
12. |  |  | Reactor I&C Systems | [34 empty] | 46
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [19 empty] | 48 | [14 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 128
16. |  |  | Steam generation systems | [34 empty] | 426
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 26
31. |  |  | Turbine and auxiliaries | [34 empty] | 20
32. |  |  | Feedwater and Main Steam System | [34 empty] | 12
34. |  |  | Miscellaneous Systems | [34 empty] | 13
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 125
42. |  |  | Electrical Power Supply Systems | [34 empty] | 27
Total | [22 empty] | 48 | [14 empty] | 963

## BRUCE-3
2023 Operating Experience
CA-10 | [8 empty] | BRUCE-3 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750A | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-07-01
Thermal power | [12 empty] | : |  |  | 2550 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-12-12
Gross electrical power | [12 empty] | : |  |  | 865 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1978-02-01
Reference unit power (net) | [12 empty] | : |  |  | 770 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8750 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.37
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 4 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 1 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 1145.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 16.24 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 16.24 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 83.76 %
Load Factor (LF) | [18 empty] | : | 16.98 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 16.42 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 7322 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 593.56 | 533.97 |  |  |  | 17.53 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1145.06
EAF [%] |  |  |  |  | 98.91 | 98.84 |  |  |  | 3.06 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.24
UCF [%] |  |  |  |  | 98.91 | 98.84 |  |  |  | 3.06 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.24
LF [%] |  |  |  |  | 103.61 | 103.19 |  |  |  | 3.06 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.98
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 2.96 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.42
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 1.09 | 1.16 |  |  |  | 96.94 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.76
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 187117.98 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 13.66 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.79 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 12.86 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 73.33 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.81 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.91 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.54 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.02 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1978 |  |  |  | 4793.00 |  |  | 7361 |  |  |  | 740 | [10 empty] | 87.56 |  |  |  | 87.56 | [5 empty] | 82.03 |  |  | 93.22 |  |  |  | 12.44 |  | 12.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
1979 |  |  |  | 4797.90 |  |  | 6885 |  |  |  | 740 | [10 empty] | 77.78 |  |  |  | 77.78 | [5 empty] | 73.21 |  |  | 77.74 |  |  |  | 11.80 |  | 10.41 | [8 empty] | 11.82 |  |  |  |  | 0.00
1980 |  |  |  | 5939.80 |  |  | 8276 |  |  |  | 740 | [10 empty] | 91.44 |  |  |  | 91.44 | [5 empty] | 91.38 |  |  | 94.22 |  |  |  | 8.56 |  | 8.56 | [8 empty] | 0.00 |  |  |  |  | 0.00
1981 |  |  |  | 5795.00 |  |  | 7873 |  |  |  | 740 | [10 empty] | 89.48 |  |  |  | 89.48 | [5 empty] | 89.40 |  |  | 89.87 |  |  |  | 4.74 |  | 4.45 | [8 empty] | 6.07 |  |  |  |  | 0.00
1982 |  |  |  | 6381.90 |  |  | 8497 |  |  |  | 740 | [10 empty] | 96.72 |  |  |  | 96.72 | [5 empty] | 98.45 |  |  | 97.00 |  |  |  | 3.28 |  | 3.28 | [8 empty] | 0.00 |  |  |  |  | 0.00
1983 |  |  |  | 6091.10 |  |  | 7905 |  |  |  | 740 | [10 empty] | 89.23 |  |  |  | 89.23 | [5 empty] | 93.96 |  |  | 90.24 |  |  |  | 10.64 |  | 10.62 | [8 empty] | 0.15 |  |  |  |  | 0.00
1984 |  |  |  | 6148.73 |  |  | 8077 |  |  |  | 740 | [10 empty] | 91.19 |  |  |  | 91.19 | [5 empty] | 94.59 |  |  | 91.95 |  |  |  | 8.56 |  | 8.54 | [8 empty] | 0.27 |  |  |  |  | 0.00
1985 |  |  |  | 6015.13 |  |  | 8118 |  |  |  | 775 | [10 empty] | 88.59 |  |  |  | 93.91 | [5 empty] | 88.60 |  |  | 92.67 |  |  |  | 6.09 |  | 6.09 | [8 empty] | 0.00 |  |  |  |  | 5.32
1986 |  |  |  | 5891.24 |  |  | 7600 |  |  |  | 796 | [10 empty] | 84.18 |  |  |  | 86.94 | [5 empty] | 84.48 |  |  | 86.76 |  |  |  | 13.01 |  | 13.00 | [8 empty] | 0.06 |  |  |  |  | 2.76
1987 |  |  |  | 6073.27 |  |  | 7724 |  |  |  | 848 | [10 empty] | 81.91 |  |  |  | 85.78 | [5 empty] | 81.76 |  |  | 88.17 |  |  |  | 7.86 |  | 7.32 | [8 empty] | 6.90 |  |  |  |  | 3.87
1988 |  |  |  | 3310.57 |  |  | 4044 |  |  |  | 848 | [10 empty] | 45.61 |  |  |  | 45.61 | [5 empty] | 44.44 |  |  | 46.04 |  |  |  | 4.02 |  | 1.91 | [8 empty] | 52.48 |  |  |  |  | 0.00
1989 |  |  |  | 4031.74 |  |  | 5364 |  |  |  | 848 | [10 empty] | 54.79 |  |  |  | 57.43 | [5 empty] | 54.27 |  |  | 61.23 |  |  |  | 31.42 |  | 26.31 | [8 empty] | 16.26 |  |  |  |  | 2.64
1990 |  |  |  | 5652.68 |  |  | 7472 |  |  |  | 848 | [10 empty] | 76.30 |  |  |  | 76.77 | [5 empty] | 76.09 |  |  | 85.30 |  |  |  | 23.03 |  | 22.97 | [8 empty] | 0.26 |  |  |  |  | 0.48
1991 |  |  |  | 6126.29 |  |  | 7950 |  |  |  | 848 | [10 empty] | 82.38 |  |  |  | 84.29 | [5 empty] | 82.47 |  |  | 90.75 |  |  |  | 15.71 |  | 15.71 | [8 empty] | 0.00 |  |  |  |  | 1.90
1992 |  |  |  | 5800.97 |  |  | 7438 |  |  |  | 848 | [10 empty] | 77.89 |  |  |  | 77.89 | [5 empty] | 77.88 |  |  | 84.68 |  |  |  | 18.25 |  | 17.39 | [8 empty] | 4.72 |  |  |  |  | 0.00
1993 |  |  |  | 3158.23 |  |  | 6557 |  |  |  | 848 | [10 empty] | 42.99 |  |  |  | 42.99 | [5 empty] | 42.52 |  |  | 74.85 |  |  |  | 54.42 |  | 51.32 | [8 empty] | 5.69 |  |  |  |  | 0.00
1994 |  |  |  | 2737.62 |  |  | 5006 |  |  |  | 848 | [10 empty] | 36.85 |  |  |  | 36.85 | [5 empty] | 36.85 |  |  | 57.15 |  |  |  | 37.07 |  | 21.71 | [8 empty] | 41.44 |  |  |  |  | 0.00
1995 |  |  |  | 4225.82 |  |  | 7000 |  |  |  | 848 | [10 empty] | 56.89 |  |  |  | 56.89 | [5 empty] | 56.89 |  |  | 79.91 |  |  |  | 43.11 |  | 43.11 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 3321.48 |  |  | 5684 |  |  |  | 848 | [10 empty] | 44.59 |  |  |  | 44.59 | [5 empty] | 44.59 |  |  | 64.71 |  |  |  | 32.38 |  | 21.35 | [8 empty] | 34.06 |  |  |  |  | 0.00
1997 |  |  |  | 4214.82 |  |  | 6325 |  |  |  | 848 | [10 empty] | 56.76 |  |  |  | 56.76 | [5 empty] | 56.74 |  |  | 72.20 |  |  |  | 43.24 |  | 43.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 1642.52 |  |  | 2328 |  |  |  | 848 | [10 empty] | 81.45 |  |  |  | 81.45 | [5 empty] | 81.45 |  |  | 97.87 |  |  |  | 18.55 |  | 18.55 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | Data not available - Suspended Operation
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | 4971.58 |  |  | 7154 |  |  |  | 750 | [10 empty] | 76.09 |  |  |  | 76.45 | [5 empty] | 75.30 |  |  | 81.44 |  |  |  | 22.51 |  | 22.21 | [8 empty] | 1.34 |  |  |  |  | 0.36
2005 |  |  |  | 4938.11 |  |  | 6782 |  |  |  | 750 | [10 empty] | 75.24 |  |  |  | 75.52 | [5 empty] | 75.16 |  |  | 77.42 |  |  |  | 8.92 |  | 7.40 | [8 empty] | 17.08 |  |  |  |  | 0.28
2006 |  |  |  | 5440.25 |  |  | 7435 |  |  |  | 750 | [10 empty] | 82.86 |  |  |  | 83.27 | [5 empty] | 82.80 |  |  | 84.87 |  |  |  | 8.75 |  | 8.05 | [8 empty] | 8.68 |  |  |  |  | 0.41
2007 |  |  |  | 4966.67 |  |  | 6911 |  |  |  | 750 | [10 empty] | 75.95 |  |  |  | 76.68 | [5 empty] | 75.60 |  |  | 78.89 |  |  |  | 3.18 |  | 3.34 | [8 empty] | 19.97 |  |  |  |  | 0.73
2008 |  |  |  | 5148.88 |  |  | 7125 |  |  |  | 734 | [10 empty] | 79.32 |  |  |  | 79.77 | [5 empty] | 79.86 |  |  | 81.11 |  |  |  | 3.51 |  | 2.90 | [8 empty] | 17.33 |  |  |  |  | 0.45
2009 |  |  |  | 5162.09 |  |  | 7148 |  |  |  | 730 | [10 empty] | 80.39 |  |  |  | 80.59 | [5 empty] | 80.72 |  |  | 81.60 |  |  |  | 2.07 |  | 10.14 | [8 empty] | 9.27 |  |  |  |  | 0.20
2010 |  |  |  | 4375.77 |  |  | 6198 |  |  |  | 730 | [10 empty] | 68.44 |  |  |  | 69.58 | [5 empty] | 68.43 |  |  | 70.75 |  |  |  | 16.32 |  | 13.57 | [8 empty] | 16.85 |  |  |  |  | 1.15
2011 |  |  |  | 5084.86 |  |  | 6959 |  |  |  | 730 | [10 empty] | 78.89 |  |  |  | 79.13 | [5 empty] | 79.52 |  |  | 79.44 |  |  |  | 4.24 |  | 3.50 | [8 empty] | 17.37 |  |  |  |  | 0.25
2012 |  |  |  | 3352.06 |  |  | 4617 |  |  |  | 730 | [10 empty] | 52.21 |  |  |  | 52.26 | [5 empty] | 52.28 |  |  | 52.56 |  |  |  | 5.80 |  | 9.96 | [8 empty] | 37.78 |  |  |  |  | 0.06
2013 |  |  |  | 5518.71 |  |  | 7914 |  |  |  | 730 | [10 empty] | 94.01 |  |  |  | 94.16 | [5 empty] | 86.30 |  |  | 90.34 |  |  |  | 4.71 |  | 4.66 | [8 empty] | 1.18 |  |  |  |  | 0.14
2014 |  |  |  | 4125.00 |  |  | 5718 |  |  |  | 730 | [10 empty] | 64.55 |  |  |  | 64.55 | [5 empty] | 64.51 |  |  | 65.27 |  |  |  | 3.30 |  | 2.20 | [8 empty] | 33.25 |  |  |  |  | 0.00
2015 |  |  |  | 5827.57 |  |  | 7831 |  |  |  | 750 | [10 empty] | 89.01 |  |  |  | 89.01 | [5 empty] | 88.90 |  |  | 89.39 |  |  |  | 10.00 |  | 9.89 | [8 empty] | 1.09 |  |  |  |  | 0.00
2016 |  |  |  | 4995.72 |  |  | 6579 |  |  |  | 750 | [10 empty] | 75.54 |  |  |  | 75.60 | [5 empty] | 75.83 |  |  | 74.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.40 |  |  |  |  | 0.06
2017 |  |  |  | 5502.68 |  |  | 7344 |  |  |  | 750 | [10 empty] | 83.22 |  |  |  | 83.22 | [5 empty] | 83.75 |  |  | 83.84 |  |  |  | 0.08 |  | 9.65 | [8 empty] | 7.13 |  |  |  |  | 0.00
2018 |  |  |  | 6268.88 |  |  | 8079 |  |  |  | 750 | [10 empty] | 92.18 |  |  |  | 92.21 | [5 empty] | 95.42 |  |  | 92.23 |  |  |  | 3.26 |  | 3.11 | [8 empty] | 4.68 |  |  |  |  | 0.03
2019 |  |  |  | 4213.89 |  |  | 5592 |  |  |  | 750 | [10 empty] | 62.40 |  |  |  | 62.40 | [5 empty] | 64.14 |  |  | 63.84 |  |  |  | 1.68 |  | 24.63 | [8 empty] | 12.98 |  |  |  |  | 0.00
2020 |  |  |  | 6776.48 |  |  | 8574 |  |  |  | 770 | [10 empty] | 97.08 |  |  |  | 97.12 | [5 empty] | 100.19 |  |  | 97.61 |  |  |  | 1.35 |  | 1.33 | [8 empty] | 1.54 |  |  |  |  | 0.04
2021 |  |  |  | 3164.00 |  |  | 4022 |  |  |  | 770 | [10 empty] | 45.09 |  |  |  | 45.09 | [5 empty] | 46.91 |  |  | 45.91 |  |  |  | 0.00 |  | 3.40 | [8 empty] | 51.51 |  |  |  |  | 0.00
2022 |  |  |  | 6220.67 |  |  | 7953 |  |  |  | 770 | [10 empty] | 89.12 |  |  |  | 89.15 | [5 empty] | 92.22 |  |  | 90.79 |  |  |  | 6.16 |  | 5.85 | [8 empty] | 5.00 |  |  |  |  | 0.03
2023 |  |  |  | 1145.06 |  |  | 1438 |  |  |  | 770 | [10 empty] | 16.24 |  |  |  | 16.24 | [5 empty] | 16.98 |  |  | 16.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 83.76 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1978 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 683
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 37 |  |  |  | 0
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 884
E. |  | Testing of plant systems or components | [35 empty] | 13 |  |  |  | 1
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 7320 | [14 empty] | 254
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 16
L. |  | Human factor related | [39 empty] | 10
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 12
Z. |  | Other | [39 empty] | 8
Subtotal | [22 empty] | 7320 | [14 empty] | 1188 |  |  |  | 702 | [11 empty] | 32
Total | [22 empty] | 7320 | [14 empty] | 1922
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1978 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 128
12. |  |  | Reactor I&C Systems | [34 empty] | 42
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 22
14. |  |  | Safety Systems | [34 empty] | 61
15. |  |  | Reactor Cooling Systems | [34 empty] | 83
16. |  |  | Steam generation systems | [34 empty] | 96
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 28
31. |  |  | Turbine and auxiliaries | [34 empty] | 95
32. |  |  | Feedwater and Main Steam System | [34 empty] | 33
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 7
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 75
42. |  |  | Electrical Power Supply Systems | [34 empty] | 18
Total | [37 empty] | 701
Highlights (2023)
Unit taken off-line 01MAR @ 22:03 to begin Major Component Replacement (MCR) & Refurbishment.

## BRUCE-4
2023 Operating Experience
CA-11 | [8 empty] | BRUCE-4 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750A | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-09-01
Thermal power | [12 empty] | : |  |  | 2550 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-12-21
Gross electrical power | [12 empty] | : |  |  | 868 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-01-18
Reference unit power (net) | [12 empty] | : |  |  | 807 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.36
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.74
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8750 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.37
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 4 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 1 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5895.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.23 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.15 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.91 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.77 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.32 %
Load Factor (LF) | [18 empty] | : | 85.38 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.62 %
Operating Factor (OF) | [18 empty] | : | 88.76 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 985 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 589.22 | 373.55 |  |  |  | 429.32 |  | 478.12 | [8 empty] | 433.46 |  |  | 365.09 | [6 empty] | 426.51 |  | 584.42 |  |  |  | 565.93 |  |  | 586.88 |  |  | 466.93 | [9 empty] | 595.71 |  |  | 5895.12
EAF [%] |  |  |  |  | 98.77 | 70.43 |  |  |  | 72.54 |  | 82.68 | [8 empty] | 72.73 |  |  | 65.94 | [6 empty] | 70.93 |  | 97.39 |  |  |  | 97.38 |  |  | 97.78 |  |  | 80.41 | [9 empty] | 99.28 |  |  | 84.15
UCF [%] |  |  |  |  | 98.77 | 70.43 |  |  |  | 72.54 |  | 82.68 | [8 empty] | 72.73 |  |  | 65.94 | [6 empty] | 73.35 |  | 99.67 |  |  |  | 98.93 |  |  | 98.62 |  |  | 80.50 | [9 empty] | 99.32 |  |  | 84.77
LF [%] |  |  |  |  | 102.99 | 72.29 |  |  |  | 75.04 |  | 86.35 | [8 empty] | 75.76 |  |  | 65.94 | [6 empty] | 71.04 |  | 97.34 |  |  |  | 97.40 |  |  | 97.75 |  |  | 80.36 | [9 empty] | 99.22 |  |  | 85.38
OF [%] |  |  |  |  | 100.00 | 71.13 |  |  |  | 75.81 |  | 83.06 | [8 empty] | 73.79 |  |  | 83.61 | [6 empty] | 93.01 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 82.78 | [9 empty] | 100.00 |  |  | 88.76
FLR [%] |  |  |  |  | 1.04 | 0.00 |  |  |  | 8.85 |  | 17.32 | [8 empty] | 1.44 |  |  | 0.00 | [6 empty] | 9.66 |  | 0.01 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.23
UCL [%] |  |  |  |  | 1.04 | 0.00 |  |  |  | 20.08 |  | 17.32 | [8 empty] | 1.06 |  |  | 0.00 | [6 empty] | 7.85 |  | 0.01 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.91
PUF [%] |  |  |  |  | 0.19 | 29.57 |  |  |  | 7.38 |  | 0.00 | [8 empty] | 26.21 |  |  | 34.06 | [6 empty] | 18.81 |  | 0.31 |  |  |  | 1.07 |  |  | 1.38 |  |  | 19.50 | [9 empty] | 0.68 |  |  | 11.32
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 2.42 |  | 2.29 |  |  |  | 1.55 |  |  | 0.84 |  |  | 0.09 | [9 empty] | 0.04 |  |  | 0.62
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 190125.39 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 13.8 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.69 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.33 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.63 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.55 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.64 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.44 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 4966.40 |  |  | 7084 |  |  |  | 740 | [10 empty] | 84.17 |  |  |  | 84.17 | [5 empty] | 79.65 |  |  | 84.18 |  |  |  | 15.83 |  | 15.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 4945.10 |  |  | 6962 |  |  |  | 740 | [10 empty] | 76.12 |  |  |  | 76.12 | [5 empty] | 76.08 |  |  | 79.26 |  |  |  | 14.06 |  | 12.46 | [8 empty] | 11.42 |  |  |  |  | 0.00
1981 |  |  |  | 5753.50 |  |  | 7874 |  |  |  | 740 | [10 empty] | 89.10 |  |  |  | 89.10 | [5 empty] | 88.76 |  |  | 89.89 |  |  |  | 10.90 |  | 10.90 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 6050.20 |  |  | 8150 |  |  |  | 740 | [10 empty] | 92.18 |  |  |  | 92.18 | [5 empty] | 93.33 |  |  | 93.04 |  |  |  | 2.13 |  | 2.01 | [8 empty] | 5.81 |  |  |  |  | 0.00
1983 |  |  |  | 6407.40 |  |  | 8345 |  |  |  | 740 | [10 empty] | 94.25 |  |  |  | 94.25 | [5 empty] | 98.84 |  |  | 95.26 |  |  |  | 5.68 |  | 5.67 | [8 empty] | 0.07 |  |  |  |  | 0.00
1984 |  |  |  | 6664.64 |  |  | 8625 |  |  |  | 740 | [10 empty] | 97.85 |  |  |  | 97.85 | [5 empty] | 102.53 |  |  | 98.19 |  |  |  | 2.08 |  | 2.07 | [8 empty] | 0.08 |  |  |  |  | 0.00
1985 |  |  |  | 4995.16 |  |  | 6518 |  |  |  | 788 | [10 empty] | 73.24 |  |  |  | 78.99 | [5 empty] | 72.29 |  |  | 74.41 |  |  |  | 7.88 |  | 6.76 | [8 empty] | 14.26 |  |  |  |  | 5.75
1986 |  |  |  | 6891.57 |  |  | 8644 |  |  |  | 848 | [10 empty] | 92.85 |  |  |  | 95.51 | [5 empty] | 92.77 |  |  | 98.68 |  |  |  | 4.49 |  | 4.49 | [8 empty] | 0.00 |  |  |  |  | 2.67
1987 |  |  |  | 5044.99 |  |  | 6366 |  |  |  | 848 | [10 empty] | 67.90 |  |  |  | 71.54 | [5 empty] | 67.91 |  |  | 72.67 |  |  |  | 5.78 |  | 4.39 | [8 empty] | 24.07 |  |  |  |  | 3.64
1988 |  |  |  | 4663.68 |  |  | 5997 |  |  |  | 848 | [10 empty] | 65.71 |  |  |  | 66.92 | [5 empty] | 62.61 |  |  | 68.27 |  |  |  | 18.05 |  | 14.74 | [8 empty] | 18.34 |  |  |  |  | 1.21
1989 |  |  |  | 5584.21 |  |  | 7290 |  |  |  | 848 | [10 empty] | 75.29 |  |  |  | 77.00 | [5 empty] | 75.17 |  |  | 83.22 |  |  |  | 17.87 |  | 16.75 | [8 empty] | 6.25 |  |  |  |  | 1.71
1990 |  |  |  | 3533.03 |  |  | 4611 |  |  |  | 848 | [10 empty] | 47.54 |  |  |  | 48.29 | [5 empty] | 47.56 |  |  | 52.64 |  |  |  | 51.71 |  | 51.71 | [8 empty] | 0.00 |  |  |  |  | 0.75
1991 |  |  |  | 5940.70 |  |  | 7955 |  |  |  | 848 | [10 empty] | 79.91 |  |  |  | 81.65 | [5 empty] | 79.97 |  |  | 90.81 |  |  |  | 17.92 |  | 17.83 | [8 empty] | 0.52 |  |  |  |  | 1.74
1992 |  |  |  | 5843.37 |  |  | 8070 |  |  |  | 848 | [10 empty] | 78.37 |  |  |  | 80.08 | [5 empty] | 78.45 |  |  | 91.87 |  |  |  | 19.92 |  | 19.92 | [8 empty] | 0.00 |  |  |  |  | 1.71
1993 |  |  |  | 350.09 |  |  | 527 |  |  |  | 848 | [10 empty] | 4.71 |  |  |  | 4.71 | [5 empty] | 4.71 |  |  | 6.02 |  |  |  | 79.26 |  | 18.01 | [8 empty] | 77.27 |  |  |  |  | 0.00
1994 |  |  |  | 3655.98 |  |  | 7206 |  |  |  | 848 | [10 empty] | 49.30 |  |  |  | 49.30 | [5 empty] | 49.22 |  |  | 82.26 |  |  |  | 50.38 |  | 50.06 | [8 empty] | 0.64 |  |  |  |  | 0.00
1995 |  |  |  | 3034.92 |  |  | 5024 |  |  |  | 848 | [10 empty] | 40.87 |  |  |  | 40.87 | [5 empty] | 40.86 |  |  | 57.35 |  |  |  | 42.28 |  | 29.94 | [8 empty] | 29.19 |  |  |  |  | 0.00
1996 |  |  |  | 5296.28 |  |  | 8686 |  |  |  | 848 | [10 empty] | 71.17 |  |  |  | 71.17 | [5 empty] | 71.10 |  |  | 98.88 |  |  |  | 28.83 |  | 28.83 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 2923.05 |  |  | 4968 |  |  |  | 848 | [10 empty] | 39.36 |  |  |  | 39.36 | [5 empty] | 39.35 |  |  | 56.71 |  |  |  | 60.64 |  | 60.64 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 12.34 |  |  | 45 |  |  |  | 848 | [10 empty] | 0.81 |  |  |  | 0.81 | [5 empty] | 0.81 |  |  | 2.50 |  |  |  | 99.19 |  | 99.19 | [8 empty] | 0.00 |  |  |  |  | 0.00
1999 |  |  |  | Data not available - Suspended Operation
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | 934.47 |  |  | 802 |  |  |  | 769 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 55.01 |  |  | 36.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 5418.78 |  |  | 7469 |  |  |  | 769 | [10 empty] | 83.42 |  |  |  | 83.42 | [5 empty] | 82.08 |  |  | 85.03 |  |  |  | 6.58 |  | 6.45 | [8 empty] | 10.13 |  |  |  |  | 0.00
2005 |  |  |  | 5499.12 |  |  | 7469 |  |  |  | 750 | [10 empty] | 83.67 |  |  |  | 84.10 | [5 empty] | 83.70 |  |  | 85.26 |  |  |  | 3.21 |  | 2.79 | [8 empty] | 13.11 |  |  |  |  | 0.43
2006 |  |  |  | 5308.22 |  |  | 7261 |  |  |  | 750 | [10 empty] | 80.78 |  |  |  | 81.59 | [5 empty] | 80.79 |  |  | 82.89 |  |  |  | 2.28 |  | 4.12 | [8 empty] | 14.29 |  |  |  |  | 0.81
2007 |  |  |  | 5250.98 |  |  | 7298 |  |  |  | 750 | [10 empty] | 80.15 |  |  |  | 80.78 | [5 empty] | 79.92 |  |  | 83.31 |  |  |  | 4.27 |  | 3.60 | [8 empty] | 15.62 |  |  |  |  | 0.63
2008 |  |  |  | 5504.43 |  |  | 7603 |  |  |  | 734 | [10 empty] | 84.92 |  |  |  | 85.62 | [5 empty] | 85.37 |  |  | 86.56 |  |  |  | 2.17 |  | 2.35 | [8 empty] | 12.03 |  |  |  |  | 0.70
2009 |  |  |  | 4907.55 |  |  | 7014 |  |  |  | 730 | [10 empty] | 76.92 |  |  |  | 77.37 | [5 empty] | 76.74 |  |  | 80.07 |  |  |  | 5.42 |  | 9.91 | [8 empty] | 12.72 |  |  |  |  | 0.44
2010 |  |  |  | 5976.18 |  |  | 8360 |  |  |  | 730 | [10 empty] | 94.11 |  |  |  | 94.49 | [5 empty] | 93.45 |  |  | 95.43 |  |  |  | 5.50 |  | 5.50 | [8 empty] | 0.02 |  |  |  |  | 0.37
2011 |  |  |  | 6259.24 |  |  | 8670 |  |  |  | 730 | [10 empty] | 98.71 |  |  |  | 98.97 | [5 empty] | 97.88 |  |  | 98.97 |  |  |  | 1.03 |  | 1.03 | [8 empty] | 0.00 |  |  |  |  | 0.26
2012 |  |  |  | 3700.41 |  |  | 5137 |  |  |  | 730 | [10 empty] | 58.31 |  |  |  | 58.46 | [5 empty] | 57.71 |  |  | 58.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 41.54 |  |  |  |  | 0.15
2013 |  |  |  | 4131.32 |  |  | 5778 |  |  |  | 730 | [10 empty] | 63.44 |  |  |  | 63.55 | [5 empty] | 64.60 |  |  | 65.96 |  |  |  | 10.79 |  | 31.78 | [8 empty] | 4.67 |  |  |  |  | 0.11
2014 |  |  |  | 6027.76 |  |  | 8243 |  |  |  | 730 | [10 empty] | 99.39 |  |  |  | 99.39 | [5 empty] | 94.26 |  |  | 94.10 |  |  |  | 0.61 |  | 0.61 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 4503.60 |  |  | 6069 |  |  |  | 750 | [10 empty] | 68.26 |  |  |  | 68.26 | [5 empty] | 68.55 |  |  | 69.28 |  |  |  | 0.00 |  | 2.74 | [8 empty] | 29.00 |  |  |  |  | 0.00
2016 |  |  |  | 5731.38 |  |  | 7511 |  |  |  | 750 | [10 empty] | 85.23 |  |  |  | 85.25 | [5 empty] | 87.00 |  |  | 85.51 |  |  |  | 6.54 |  | 5.96 | [8 empty] | 8.78 |  |  |  |  | 0.02
2017 |  |  |  | 6188.10 |  |  | 8262 |  |  |  | 750 | [10 empty] | 93.76 |  |  |  | 93.77 | [5 empty] | 94.19 |  |  | 94.32 |  |  |  | 4.65 |  | 4.58 | [8 empty] | 1.65 |  |  |  |  | 0.02
2018 |  |  |  | 4638.81 |  |  | 6146 |  |  |  | 750 | [10 empty] | 69.12 |  |  |  | 69.13 | [5 empty] | 70.61 |  |  | 70.16 |  |  |  | 4.78 |  | 7.58 | [8 empty] | 23.30 |  |  |  |  | 0.00
2019 |  |  |  | 6115.21 |  |  | 8168 |  |  |  | 750 | [10 empty] | 92.93 |  |  |  | 92.93 | [5 empty] | 93.08 |  |  | 93.24 |  |  |  | 3.71 |  | 3.58 | [8 empty] | 3.49 |  |  |  |  | 0.00
2020 |  |  |  | 4506.10 |  |  | 5775 |  |  |  | 769 | [10 empty] | 65.21 |  |  |  | 65.35 | [5 empty] | 66.71 |  |  | 65.74 |  |  |  | 2.84 |  | 1.91 | [8 empty] | 32.74 |  |  |  |  | 0.14
2021 |  |  |  | 6922.00 |  |  | 8760 |  |  |  | 769 | [10 empty] | 99.98 |  |  |  | 100.00 | [5 empty] | 102.75 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.02
2022 |  |  |  | 4701.86 |  |  | 6006 |  |  |  | 769 | [10 empty] | 67.91 |  |  |  | 68.04 | [5 empty] | 69.80 |  |  | 68.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.96 |  |  |  |  | 0.13
2023 |  |  |  | 5895.12 |  |  | 7775 |  |  |  | 807 | [10 empty] | 84.15 |  |  |  | 84.77 | [5 empty] | 85.38 |  |  | 88.76 |  |  |  | 3.23 |  | 3.91 | [8 empty] | 11.32 |  |  |  |  | 0.62
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1979 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 320 | [14 empty] | 730
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 58
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 668 | [14 empty] | 886
E. |  | Testing of plant systems or components | [35 empty] | 39
H. |  | Nuclear regulatory requirements | [39 empty] | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 15
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 7
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 13
Z. |  | Other | [39 empty] | 11 | [11 empty] | 2
Subtotal | [22 empty] | 668 |  |  |  | 320 | [10 empty] | 983 |  |  |  | 753 | [11 empty] | 34
Total | [22 empty] | 988 | [14 empty] | 1770
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1979 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 98
12. |  |  | Reactor I&C Systems | [19 empty] | 47 | [14 empty] | 41
14. |  |  | Safety Systems | [34 empty] | 41
15. |  |  | Reactor Cooling Systems | [34 empty] | 65
16. |  |  | Steam generation systems | [19 empty] | 123 | [14 empty] | 162
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 17
31. |  |  | Turbine and auxiliaries | [19 empty] | 97 | [14 empty] | 62
32. |  |  | Feedwater and Main Steam System | [34 empty] | 32
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 31
35. |  |  | All other I&C Systems | [34 empty] | 88
41. |  |  | Main Generator Systems | [34 empty] | 73
42. |  |  | Electrical Power Supply Systems | [19 empty] | 52 | [14 empty] | 33
Total | [22 empty] | 319 | [14 empty] | 750

## BRUCE-5
2023 Operating Experience
CA-18 | [8 empty] | BRUCE-5 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-05-31
Thermal power | [12 empty] | : |  |  | 2832 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-12-01
Gross electrical power | [12 empty] | : |  |  | 872 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-02-28
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 1 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6928.72 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.18 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.25 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.75 %
Load Factor (LF) | [18 empty] | : | 96.81 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.07 %
Operating Factor (OF) | [18 empty] | : | 97.34 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 233 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 606.91 | 544.08 |  |  |  | 606.54 |  | 587.72 | [8 empty] | 606.15 |  |  | 585.82 | [6 empty] | 603.28 |  | 606.77 |  |  |  | 584.32 |  |  | 428.91 |  |  | 562.43 | [9 empty] | 605.80 |  |  | 6928.72
EAF [%] |  |  |  |  | 100.00 | 99.30 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.91 |  |  | 99.92 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 70.97 |  |  | 96.49 | [9 empty] | 100.00 |  |  | 97.18
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 70.97 |  |  | 96.49 | [9 empty] | 100.00 |  |  | 97.25
LF [%] |  |  |  |  | 99.85 | 99.10 |  |  |  | 99.79 |  | 99.91 | [8 empty] | 99.72 |  |  | 99.59 | [6 empty] | 99.25 |  | 99.82 |  |  |  | 99.33 |  |  | 70.56 |  |  | 95.61 | [9 empty] | 99.66 |  |  | 96.81
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 70.97 |  |  | 97.64 | [9 empty] | 100.00 |  |  | 97.34
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 29.03 |  |  | 3.51 | [9 empty] | 0.00 |  |  | 2.75
XUF [%] |  |  |  |  | 0.00 | 0.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.09 |  |  | 0.08 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.07
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 237713.67 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.56 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.74 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.47 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.2 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.33 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.06 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.46 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.1 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 5464.16 |  |  | 7163 |  |  |  | 805 | [10 empty] | 85.86 |  |  |  | 91.57 | [5 empty] | 84.23 |  |  | 86.11 |  |  |  | 8.43 |  | 8.43 | [8 empty] | 0.00 |  |  |  |  | 5.71
1986 |  |  |  | 7078.03 |  |  | 8675 |  |  |  | 835 | [10 empty] | 96.67 |  |  |  | 98.43 | [5 empty] | 96.77 |  |  | 99.03 |  |  |  | 1.57 |  | 1.57 | [8 empty] | 0.00 |  |  |  |  | 1.76
1987 |  |  |  | 5730.15 |  |  | 7197 |  |  |  | 835 | [10 empty] | 78.18 |  |  |  | 80.17 | [5 empty] | 78.34 |  |  | 82.16 |  |  |  | 8.82 |  | 7.76 | [8 empty] | 12.08 |  |  |  |  | 1.99
1988 |  |  |  | 6673.56 |  |  | 7824 |  |  |  | 860 | [10 empty] | 88.49 |  |  |  | 88.52 | [5 empty] | 88.34 |  |  | 89.07 |  |  |  | 6.14 |  | 5.79 | [8 empty] | 5.69 |  |  |  |  | 0.02
1989 |  |  |  | 7130.76 |  |  | 8589 |  |  |  | 860 | [10 empty] | 94.14 |  |  |  | 97.10 | [5 empty] | 94.65 |  |  | 98.05 |  |  |  | 2.28 |  | 2.26 | [8 empty] | 0.64 |  |  |  |  | 2.96
1990 |  |  |  | 5534.66 |  |  | 6656 |  |  |  | 860 | [10 empty] | 73.53 |  |  |  | 74.60 | [5 empty] | 73.47 |  |  | 75.98 |  |  |  | 10.83 |  | 9.06 | [8 empty] | 16.34 |  |  |  |  | 1.06
1991 |  |  |  | 6769.63 |  |  | 8130 |  |  |  | 860 | [10 empty] | 90.30 |  |  |  | 90.74 | [5 empty] | 89.86 |  |  | 92.81 |  |  |  | 2.14 |  | 1.98 | [8 empty] | 7.27 |  |  |  |  | 0.44
1992 |  |  |  | 6452.05 |  |  | 7636 |  |  |  | 860 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 85.41 |  |  | 86.93 |  |  |  | 4.20 |  | 3.76 | [8 empty] | 10.45 |  |  |  |  | 0.00
1993 |  |  |  | 5118.34 |  |  | 7457 |  |  |  | 860 | [10 empty] | 68.08 |  |  |  | 68.08 | [5 empty] | 67.94 |  |  | 85.13 |  |  |  | 21.44 |  | 18.58 | [8 empty] | 13.34 |  |  |  |  | 0.00
1994 |  |  |  | 5629.34 |  |  | 7671 |  |  |  | 860 | [10 empty] | 75.02 |  |  |  | 75.02 | [5 empty] | 74.72 |  |  | 87.57 |  |  |  | 15.74 |  | 14.02 | [8 empty] | 10.97 |  |  |  |  | 0.00
1995 |  |  |  | 6125.27 |  |  | 7859 |  |  |  | 860 | [10 empty] | 81.41 |  |  |  | 81.41 | [5 empty] | 81.31 |  |  | 89.71 |  |  |  | 18.59 |  | 18.59 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 5767.61 |  |  | 7153 |  |  |  | 860 | [10 empty] | 76.40 |  |  |  | 76.40 | [5 empty] | 76.35 |  |  | 81.43 |  |  |  | 8.58 |  | 7.17 | [8 empty] | 16.42 |  |  |  |  | 0.00
1997 |  |  |  | 6388.27 |  |  | 8148 |  |  |  | 860 | [10 empty] | 84.80 |  |  |  | 84.80 | [5 empty] | 84.80 |  |  | 93.01 |  |  |  | 13.20 |  | 12.89 | [8 empty] | 2.31 |  |  |  |  | 0.00
1998 |  |  |  | 5623.11 |  |  | 7305 |  |  |  | 785 | [10 empty] | 81.68 |  |  |  | 81.69 | [5 empty] | 81.77 |  |  | 83.39 |  |  |  | 10.74 |  | 9.83 | [8 empty] | 8.48 |  |  |  |  | 0.01
1999 |  |  |  | 5281.90 |  |  | 6719 |  |  |  | 785 | [10 empty] | 76.57 |  |  |  | 76.58 | [5 empty] | 76.81 |  |  | 76.70 |  |  |  | 4.27 |  | 3.42 | [8 empty] | 20.01 |  |  |  |  | 0.01
2000 |  |  |  | 6908.74 |  |  | 8719 |  |  |  | 785 | [10 empty] | 99.08 |  |  |  | 99.08 | [5 empty] | 100.19 |  |  | 99.26 |  |  |  | 0.92 |  | 0.92 | [8 empty] | 0.00 |  |  |  |  | 0.00
2001 |  |  |  | 4902.08 |  |  | 6220 |  |  |  | 790 | [10 empty] | 70.91 |  |  |  | 70.91 | [5 empty] | 70.84 |  |  | 71.00 |  |  |  | 2.07 |  | 1.50 | [8 empty] | 27.59 |  |  |  |  | 0.00
2002 |  |  |  | 5993.14 |  |  | 7630 |  |  |  | 790 | [10 empty] | 86.28 |  |  |  | 86.28 | [5 empty] | 86.60 |  |  | 87.10 |  |  |  | 3.85 |  | 3.86 | [8 empty] | 9.86 |  |  |  |  | 0.00
2003 |  |  |  | 5302.51 |  |  | 6783 |  |  |  | 790 | [10 empty] | 77.26 |  |  |  | 77.26 | [5 empty] | 76.62 |  |  | 77.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.74 |  |  |  |  | 0.00
2004 |  |  |  | 5889.11 |  |  | 7543 |  |  |  | 790 | [10 empty] | 85.13 |  |  |  | 85.13 | [5 empty] | 84.87 |  |  | 85.87 |  |  |  | 2.05 |  | 7.33 | [8 empty] | 7.54 |  |  |  |  | 0.00
2005 |  |  |  | 5109.63 |  |  | 6678 |  |  |  | 790 | [10 empty] | 74.14 |  |  |  | 74.64 | [5 empty] | 73.83 |  |  | 76.23 |  |  |  | 4.77 |  | 6.14 | [8 empty] | 19.22 |  |  |  |  | 0.50
2006 |  |  |  | 6723.49 |  |  | 8694 |  |  |  | 806 | [10 empty] | 96.79 |  |  |  | 97.18 | [5 empty] | 95.89 |  |  | 99.25 |  |  |  | 2.60 |  | 2.60 | [8 empty] | 0.22 |  |  |  |  | 0.38
2007 |  |  |  | 6710.89 |  |  | 8760 |  |  |  | 795 | [10 empty] | 97.23 |  |  |  | 97.69 | [5 empty] | 96.36 |  |  | 100.00 |  |  |  | 0.74 |  | 0.73 | [8 empty] | 1.58 |  |  |  |  | 0.46
2008 |  |  |  | 5596.97 |  |  | 6943 |  |  |  | 817 | [10 empty] | 78.05 |  |  |  | 78.30 | [5 empty] | 77.99 |  |  | 79.04 |  |  |  | 6.40 |  | 7.64 | [8 empty] | 14.05 |  |  |  |  | 0.25
2009 |  |  |  | 6826.70 |  |  | 8597 |  |  |  | 817 | [10 empty] | 97.91 |  |  |  | 98.00 | [5 empty] | 95.39 |  |  | 98.14 |  |  |  | 1.98 |  | 1.98 | [8 empty] | 0.01 |  |  |  |  | 0.10
2010 |  |  |  | 6699.69 |  |  | 8368 |  |  |  | 817 | [10 empty] | 93.97 |  |  |  | 94.15 | [5 empty] | 93.61 |  |  | 95.53 |  |  |  | 1.20 |  | 1.14 | [8 empty] | 4.71 |  |  |  |  | 0.18
2011 |  |  |  | 6149.76 |  |  | 7666 |  |  |  | 817 | [10 empty] | 86.78 |  |  |  | 86.86 | [5 empty] | 85.93 |  |  | 87.51 |  |  |  | 1.23 |  | 1.08 | [8 empty] | 12.06 |  |  |  |  | 0.08
2012 |  |  |  | 6927.64 |  |  | 8690 |  |  |  | 817 | [10 empty] | 98.24 |  |  |  | 98.38 | [5 empty] | 96.53 |  |  | 98.93 |  |  |  | 1.58 |  | 1.58 | [8 empty] | 0.03 |  |  |  |  | 0.14
2013 |  |  |  | 6421.79 |  |  | 8141 |  |  |  | 817 | [10 empty] | 92.04 |  |  |  | 92.11 | [5 empty] | 89.73 |  |  | 92.93 |  |  |  | 0.62 |  | 0.85 | [8 empty] | 7.04 |  |  |  |  | 0.07
2014 |  |  |  | 5859.11 |  |  | 7487 |  |  |  | 817 | [10 empty] | 84.64 |  |  |  | 84.76 | [5 empty] | 81.87 |  |  | 85.47 |  |  |  | 0.00 |  | 0.51 | [8 empty] | 14.73 |  |  |  |  | 0.11
2015 |  |  |  | 6180.84 |  |  | 7978 |  |  |  | 817 | [10 empty] | 90.60 |  |  |  | 90.70 | [5 empty] | 86.36 |  |  | 91.07 |  |  |  | 1.65 |  | 1.63 | [8 empty] | 7.66 |  |  |  |  | 0.10
2016 |  |  |  | 6742.40 |  |  | 8613 |  |  |  | 817 | [10 empty] | 97.45 |  |  |  | 97.86 | [5 empty] | 93.95 |  |  | 98.05 |  |  |  | 0.87 |  | 0.86 | [8 empty] | 1.28 |  |  |  |  | 0.41
2017 |  |  |  | 5034.08 |  |  | 6394 |  |  |  | 817 | [10 empty] | 72.35 |  |  |  | 72.75 | [5 empty] | 70.34 |  |  | 72.99 |  |  |  | 0.52 |  | 3.12 | [8 empty] | 24.13 |  |  |  |  | 0.40
2018 |  |  |  | 7076.65 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.38 |  |  |  | 99.64 | [5 empty] | 98.88 |  |  | 100.00 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.00 |  |  |  |  | 0.26
2019 |  |  |  | 4865.80 |  |  | 6173 |  |  |  | 817 | [10 empty] | 69.74 |  |  |  | 69.96 | [5 empty] | 67.99 |  |  | 70.47 |  |  |  | 2.10 |  | 1.50 | [8 empty] | 28.54 |  |  |  |  | 0.22
2020 |  |  |  | 6227.87 |  |  | 7682 |  |  |  | 817 | [10 empty] | 87.06 |  |  |  | 87.37 | [5 empty] | 86.78 |  |  | 87.45 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 12.56 |  |  |  |  | 0.31
2021 |  |  |  | 7138.88 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.56 |  |  |  | 99.78 | [5 empty] | 99.75 |  |  | 100.00 |  |  |  | 0.20 |  | 0.20 | [8 empty] | 0.03 |  |  |  |  | 0.22
2022 |  |  |  | 5465.11 |  |  | 6776 |  |  |  | 817 | [10 empty] | 76.36 |  |  |  | 76.78 | [5 empty] | 76.36 |  |  | 77.35 |  |  |  | 2.08 |  | 1.63 | [8 empty] | 21.58 |  |  |  |  | 0.43
2023 |  |  |  | 6928.72 |  |  | 8527 |  |  |  | 817 | [10 empty] | 97.18 |  |  |  | 97.25 | [5 empty] | 96.81 |  |  | 97.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.75 |  |  |  |  | 0.07
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 212
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 17
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 233 | [14 empty] | 776 |  |  |  | 6
E. |  | Testing of plant systems or components | [35 empty] | 5 |  |  |  | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 4
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 12
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 233 | [14 empty] | 798 |  |  |  | 223 | [11 empty] | 15
Total | [22 empty] | 233 | [14 empty] | 1036
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 23
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 8
14. |  |  | Safety Systems | [34 empty] | 16
15. |  |  | Reactor Cooling Systems | [34 empty] | 70
16. |  |  | Steam generation systems | [34 empty] | 19
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 22
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 18
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 13
42. |  |  | Electrical Power Supply Systems | [34 empty] | 10
Total | [37 empty] | 222

## BRUCE-6
2023 Operating Experience
CA-19 | [8 empty] | BRUCE-6 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-01-01
Thermal power | [12 empty] | : |  |  | 2690 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-06-26
Gross electrical power | [12 empty] | : |  |  | 891 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-09-14
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 1 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2197.13 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 30.8 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 30.8 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 69.2 %
Load Factor (LF) | [18 empty] | : | 30.7 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 31.5 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 6001 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 398.96 |  |  | 603.89 |  |  | 585.87 | [9 empty] | 608.40 |  |  | 2197.13
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 68.08 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 30.80
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 68.08 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 30.80
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 67.82 |  |  | 99.35 |  |  | 99.60 | [9 empty] | 100.09 |  |  | 30.70
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 76.53 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 31.50
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 31.92 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 69.20
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 206774.61 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.97 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.83 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.34 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.29 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.19 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.54 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.17 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 3068.32 |  |  | 4230 |  |  |  | 822 | [10 empty] | 98.80 |  |  |  | 99.38 | [5 empty] | 98.85 |  |  | 99.93 |  |  |  | 0.46 |  | 0.46 | [8 empty] | 0.17 |  |  |  |  | 0.58
1985 |  |  |  | 5900.13 |  |  | 7369 |  |  |  | 805 | [10 empty] | 84.04 |  |  |  | 88.69 | [5 empty] | 83.66 |  |  | 84.12 |  |  |  | 10.23 |  | 10.10 | [8 empty] | 1.20 |  |  |  |  | 4.65
1986 |  |  |  | 5716.03 |  |  | 7213 |  |  |  | 835 | [10 empty] | 77.78 |  |  |  | 81.71 | [5 empty] | 78.13 |  |  | 82.34 |  |  |  | 6.94 |  | 6.09 | [8 empty] | 12.20 |  |  |  |  | 3.93
1987 |  |  |  | 7017.10 |  |  | 8610 |  |  |  | 837 | [10 empty] | 95.33 |  |  |  | 97.85 | [5 empty] | 95.70 |  |  | 98.29 |  |  |  | 1.92 |  | 1.92 | [8 empty] | 0.23 |  |  |  |  | 2.52
1988 |  |  |  | 6139.49 |  |  | 7880 |  |  |  | 837 | [10 empty] | 89.10 |  |  |  | 89.22 | [5 empty] | 83.51 |  |  | 89.71 |  |  |  | 4.88 |  | 4.58 | [8 empty] | 6.20 |  |  |  |  | 0.12
1989 |  |  |  | 5386.17 |  |  | 7069 |  |  |  | 837 | [10 empty] | 73.43 |  |  |  | 78.94 | [5 empty] | 73.46 |  |  | 80.70 |  |  |  | 8.94 |  | 7.75 | [8 empty] | 13.32 |  |  |  |  | 5.50
1990 |  |  |  | 6213.64 |  |  | 7429 |  |  |  | 852 | [10 empty] | 82.31 |  |  |  | 83.85 | [5 empty] | 83.21 |  |  | 84.81 |  |  |  | 5.69 |  | 5.06 | [8 empty] | 11.09 |  |  |  |  | 1.54
1991 |  |  |  | 7013.36 |  |  | 8194 |  |  |  | 860 | [10 empty] | 93.03 |  |  |  | 93.31 | [5 empty] | 93.09 |  |  | 93.54 |  |  |  | 0.94 |  | 0.89 | [8 empty] | 5.81 |  |  |  |  | 0.27
1992 |  |  |  | 5328.20 |  |  | 6393 |  |  |  | 860 | [10 empty] | 70.51 |  |  |  | 70.55 | [5 empty] | 70.53 |  |  | 72.78 |  |  |  | 7.40 |  | 5.64 | [8 empty] | 23.82 |  |  |  |  | 0.04
1993 |  |  |  | 4351.00 |  |  | 6950 |  |  |  | 860 | [10 empty] | 58.03 |  |  |  | 58.03 | [5 empty] | 57.75 |  |  | 79.34 |  |  |  | 38.84 |  | 36.85 | [8 empty] | 5.12 |  |  |  |  | 0.00
1994 |  |  |  | 6451.71 |  |  | 8760 |  |  |  | 860 | [10 empty] | 85.75 |  |  |  | 85.75 | [5 empty] | 85.64 |  |  | 100.00 |  |  |  | 14.25 |  | 14.25 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 4671.57 |  |  | 6049 |  |  |  | 860 | [10 empty] | 62.10 |  |  |  | 62.10 | [5 empty] | 62.01 |  |  | 69.05 |  |  |  | 11.48 |  | 8.05 | [8 empty] | 29.85 |  |  |  |  | 0.00
1996 |  |  |  | 6822.75 |  |  | 8682 |  |  |  | 860 | [10 empty] | 90.38 |  |  |  | 90.39 | [5 empty] | 90.32 |  |  | 98.84 |  |  |  | 9.61 |  | 9.61 | [8 empty] | 0.00 |  |  |  |  | 0.01
1997 |  |  |  | 4796.41 |  |  | 6201 |  |  |  | 860 | [10 empty] | 63.70 |  |  |  | 63.70 | [5 empty] | 63.67 |  |  | 70.79 |  |  |  | 26.88 |  | 23.42 | [8 empty] | 12.88 |  |  |  |  | 0.00
1998 |  |  |  | 4678.62 |  |  | 6137 |  |  |  | 785 | [10 empty] | 68.04 |  |  |  | 68.11 | [5 empty] | 68.04 |  |  | 70.06 |  |  |  | 21.80 |  | 18.98 | [8 empty] | 12.91 |  |  |  |  | 0.07
1999 |  |  |  | 6860.15 |  |  | 8760 |  |  |  | 785 | [10 empty] | 99.32 |  |  |  | 99.44 | [5 empty] | 99.76 |  |  | 100.00 |  |  |  | 0.56 |  | 0.56 | [8 empty] | 0.00 |  |  |  |  | 0.12
2000 |  |  |  | 4668.21 |  |  | 5912 |  |  |  | 785 | [10 empty] | 66.81 |  |  |  | 66.81 | [5 empty] | 67.70 |  |  | 67.30 |  |  |  | 11.72 |  | 8.87 | [8 empty] | 24.32 |  |  |  |  | 0.00
2001 |  |  |  | 6840.06 |  |  | 8624 |  |  |  | 790 | [10 empty] | 98.32 |  |  |  | 98.32 | [5 empty] | 98.84 |  |  | 98.45 |  |  |  | 1.68 |  | 1.68 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 3522.45 |  |  | 4539 |  |  |  | 790 | [10 empty] | 50.64 |  |  |  | 50.64 | [5 empty] | 50.90 |  |  | 51.82 |  |  |  | 0.42 |  | 14.91 | [8 empty] | 34.45 |  |  |  |  | 0.00
2003 |  |  |  | 6750.85 |  |  | 8559 |  |  |  | 790 | [10 empty] | 98.18 |  |  |  | 98.18 | [5 empty] | 97.55 |  |  | 97.71 |  |  |  | 1.81 |  | 1.81 | [8 empty] | 0.01 |  |  |  |  | 0.00
2004 |  |  |  | 5379.09 |  |  | 6698 |  |  |  | 790 | [10 empty] | 76.65 |  |  |  | 76.65 | [5 empty] | 75.43 |  |  | 76.25 |  |  |  | 1.06 |  | 0.98 | [8 empty] | 22.37 |  |  |  |  | 0.00
2005 |  |  |  | 5721.10 |  |  | 7151 |  |  |  | 841 | [10 empty] | 79.56 |  |  |  | 79.56 | [5 empty] | 78.90 |  |  | 81.63 |  |  |  | 20.44 |  | 20.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 7104.45 |  |  | 8760 |  |  |  | 822 | [10 empty] | 99.32 |  |  |  | 99.45 | [5 empty] | 98.66 |  |  | 100.00 |  |  |  | 0.50 |  | 0.50 | [8 empty] | 0.06 |  |  |  |  | 0.12
2007 |  |  |  | 5145.02 |  |  | 6363 |  |  |  | 822 | [10 empty] | 71.77 |  |  |  | 71.77 | [5 empty] | 71.45 |  |  | 72.64 |  |  |  | 7.49 |  | 5.81 | [8 empty] | 22.42 |  |  |  |  | 0.00
2008 |  |  |  | 6857.25 |  |  | 8452 |  |  |  | 817 | [10 empty] | 95.35 |  |  |  | 95.52 | [5 empty] | 95.55 |  |  | 96.22 |  |  |  | 2.77 |  | 2.72 | [8 empty] | 1.77 |  |  |  |  | 0.17
2009 |  |  |  | 6063.07 |  |  | 7732 |  |  |  | 817 | [10 empty] | 91.32 |  |  |  | 91.36 | [5 empty] | 84.72 |  |  | 88.26 |  |  |  | 8.43 |  | 8.41 | [8 empty] | 0.23 |  |  |  |  | 0.04
2010 |  |  |  | 5471.91 |  |  | 6815 |  |  |  | 817 | [10 empty] | 76.54 |  |  |  | 76.67 | [5 empty] | 76.46 |  |  | 77.80 |  |  |  | 4.31 |  | 8.21 | [8 empty] | 15.12 |  |  |  |  | 0.13
2011 |  |  |  | 6552.52 |  |  | 8277 |  |  |  | 817 | [10 empty] | 94.00 |  |  |  | 94.07 | [5 empty] | 91.55 |  |  | 94.49 |  |  |  | 0.84 |  | 0.80 | [8 empty] | 5.13 |  |  |  |  | 0.07
2012 |  |  |  | 7125.32 |  |  | 8784 |  |  |  | 817 | [10 empty] | 99.58 |  |  |  | 99.72 | [5 empty] | 99.29 |  |  | 100.00 |  |  |  | 0.28 |  | 0.28 | [8 empty] | 0.00 |  |  |  |  | 0.14
2013 |  |  |  | 5684.00 |  |  | 7174 |  |  |  | 817 | [10 empty] | 81.00 |  |  |  | 81.07 | [5 empty] | 79.42 |  |  | 81.89 |  |  |  | 0.67 |  | 3.27 | [8 empty] | 15.66 |  |  |  |  | 0.07
2014 |  |  |  | 6768.62 |  |  | 8488 |  |  |  | 817 | [10 empty] | 97.74 |  |  |  | 97.85 | [5 empty] | 94.57 |  |  | 96.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.15 |  |  |  |  | 0.11
2015 |  |  |  | 5344.31 |  |  | 6694 |  |  |  | 817 | [10 empty] | 76.15 |  |  |  | 76.15 | [5 empty] | 74.67 |  |  | 76.42 |  |  |  | 0.74 |  | 0.57 | [8 empty] | 23.28 |  |  |  |  | 0.00
2016 |  |  |  | 6875.21 |  |  | 8613 |  |  |  | 817 | [10 empty] | 97.09 |  |  |  | 97.61 | [5 empty] | 95.80 |  |  | 98.05 |  |  |  | 2.39 |  | 2.39 | [8 empty] | 0.00 |  |  |  |  | 0.52
2017 |  |  |  | 5741.56 |  |  | 7164 |  |  |  | 817 | [10 empty] | 80.96 |  |  |  | 81.10 | [5 empty] | 80.22 |  |  | 81.78 |  |  |  | 0.19 |  | 2.89 | [8 empty] | 16.01 |  |  |  |  | 0.14
2018 |  |  |  | 7059.65 |  |  | 8718 |  |  |  | 817 | [10 empty] | 99.03 |  |  |  | 99.18 | [5 empty] | 98.64 |  |  | 99.52 |  |  |  | 0.80 |  | 0.80 | [8 empty] | 0.02 |  |  |  |  | 0.15
2019 |  |  |  | 6498.25 |  |  | 8224 |  |  |  | 817 | [10 empty] | 91.71 |  |  |  | 92.35 | [5 empty] | 90.80 |  |  | 93.88 |  |  |  | 7.63 |  | 7.63 | [8 empty] | 0.02 |  |  |  |  | 0.64
2020 |  |  |  | 313.80 |  |  | 408 |  |  |  | 817 | [10 empty] | 4.74 |  |  |  | 4.74 | [5 empty] | 4.37 |  |  | 4.64 |  |  |  | 0.74 |  | 0.04 | [8 empty] | 95.22 |  |  |  |  | 0.00
2021 |  |  |  | 0.00 |  |  | 0 |  |  |  | 817 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2022 |  |  |  | 0.00 |  |  | 0 |  |  |  | 817 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2023 |  |  |  | 2197.13 |  |  | 2759 |  |  |  | 817 | [10 empty] | 30.80 |  |  |  | 30.80 | [5 empty] | 30.70 |  |  | 31.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 69.20 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1984 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 328
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 289
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 610 |  |  |  | 4
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 16
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 454
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 6001 | [14 empty] | 153
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 14
L. |  | Human factor related | [39 empty] | 15
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 11
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 10
Z. |  | Other | [39 empty] | 12
Subtotal | [22 empty] | 6001 | [14 empty] | 1506 |  |  |  | 385 | [11 empty] | 27
Total | [22 empty] | 6001 | [14 empty] | 1918
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1984 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 81
12. |  |  | Reactor I&C Systems | [34 empty] | 50
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 91
16. |  |  | Steam generation systems | [34 empty] | 51
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 12
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
33. |  |  | Circulating Water System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 18
Total | [37 empty] | 367

## BRUCE-7
2023 Operating Experience
CA-20 | [8 empty] | BRUCE-7 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-05-01
Thermal power | [12 empty] | : |  |  | 2832 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-02-22
Gross electrical power | [12 empty] | : |  |  | 872 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-04-10
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 1 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7176.72 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 100.28 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 610.84 | 551.54 |  |  |  | 610.71 |  | 590.96 | [8 empty] | 611.88 |  |  | 589.67 | [6 empty] | 607.96 |  | 606.67 |  |  |  | 587.39 |  |  | 608.22 |  |  | 590.45 | [9 empty] | 610.41 |  |  | 7176.72
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 100.49 | 100.46 |  |  |  | 100.47 |  | 100.46 | [8 empty] | 100.66 |  |  | 100.24 | [6 empty] | 100.02 |  | 99.81 |  |  |  | 99.86 |  |  | 100.06 |  |  | 100.38 | [9 empty] | 100.42 |  |  | 100.28
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 232224.54 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.75 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.92 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.08 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.64 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 5256.62 |  |  | 6957 |  |  |  | 838 | [10 empty] | 89.83 |  |  |  | 96.68 | [5 empty] | 89.66 |  |  | 97.55 |  |  |  | 3.31 |  | 3.30 | [8 empty] | 0.02 |  |  |  |  | 6.85
1987 |  |  |  | 6288.05 |  |  | 8489 |  |  |  | 837 | [10 empty] | 85.91 |  |  |  | 96.87 | [5 empty] | 85.76 |  |  | 96.91 |  |  |  | 2.80 |  | 2.79 | [8 empty] | 0.34 |  |  |  |  | 10.96
1988 |  |  |  | 4866.19 |  |  | 6636 |  |  |  | 846 | [10 empty] | 74.75 |  |  |  | 74.75 | [5 empty] | 65.44 |  |  | 75.55 |  |  |  | 9.46 |  | 7.81 | [8 empty] | 17.44 |  |  |  |  | 0.00
1989 |  |  |  | 7280.79 |  |  | 8632 |  |  |  | 860 | [10 empty] | 96.44 |  |  |  | 97.83 | [5 empty] | 96.64 |  |  | 98.54 |  |  |  | 1.83 |  | 1.82 | [8 empty] | 0.35 |  |  |  |  | 1.39
1990 |  |  |  | 6659.40 |  |  | 8065 |  |  |  | 860 | [10 empty] | 88.53 |  |  |  | 90.69 | [5 empty] | 88.40 |  |  | 92.07 |  |  |  | 4.64 |  | 4.41 | [8 empty] | 4.89 |  |  |  |  | 2.17
1991 |  |  |  | 5733.63 |  |  | 6835 |  |  |  | 860 | [10 empty] | 76.27 |  |  |  | 76.39 | [5 empty] | 76.11 |  |  | 78.03 |  |  |  | 8.22 |  | 6.84 | [8 empty] | 16.77 |  |  |  |  | 0.12
1992 |  |  |  | 6413.41 |  |  | 7589 |  |  |  | 860 | [10 empty] | 85.11 |  |  |  | 85.16 | [5 empty] | 84.90 |  |  | 86.40 |  |  |  | 1.64 |  | 1.42 | [8 empty] | 13.42 |  |  |  |  | 0.05
1993 |  |  |  | 5802.33 |  |  | 8760 |  |  |  | 860 | [10 empty] | 78.12 |  |  |  | 78.12 | [5 empty] | 77.02 |  |  | 100.00 |  |  |  | 21.87 |  | 21.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 5496.71 |  |  | 7577 |  |  |  | 860 | [10 empty] | 73.20 |  |  |  | 73.20 | [5 empty] | 72.96 |  |  | 86.50 |  |  |  | 17.13 |  | 15.13 | [8 empty] | 11.67 |  |  |  |  | 0.00
1995 |  |  |  | 6285.10 |  |  | 8092 |  |  |  | 860 | [10 empty] | 83.47 |  |  |  | 83.47 | [5 empty] | 83.43 |  |  | 92.37 |  |  |  | 16.53 |  | 16.53 | [8 empty] | 0.00 |  |  |  |  | 0.00
1996 |  |  |  | 5475.68 |  |  | 7000 |  |  |  | 860 | [10 empty] | 72.55 |  |  |  | 72.58 | [5 empty] | 72.48 |  |  | 79.69 |  |  |  | 16.16 |  | 13.98 | [8 empty] | 13.44 |  |  |  |  | 0.03
1997 |  |  |  | 6154.48 |  |  | 7874 |  |  |  | 860 | [10 empty] | 81.69 |  |  |  | 81.69 | [5 empty] | 81.69 |  |  | 89.89 |  |  |  | 18.31 |  | 18.31 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 4990.76 |  |  | 6474 |  |  |  | 785 | [10 empty] | 72.42 |  |  |  | 72.42 | [5 empty] | 72.58 |  |  | 73.90 |  |  |  | 6.83 |  | 5.31 | [8 empty] | 22.27 |  |  |  |  | 0.00
1999 |  |  |  | 6315.74 |  |  | 8208 |  |  |  | 785 | [10 empty] | 91.84 |  |  |  | 92.29 | [5 empty] | 91.84 |  |  | 93.70 |  |  |  | 7.71 |  | 7.71 | [8 empty] | 0.00 |  |  |  |  | 0.44
2000 |  |  |  | 5322.68 |  |  | 6790 |  |  |  | 785 | [10 empty] | 76.91 |  |  |  | 78.20 | [5 empty] | 77.19 |  |  | 77.30 |  |  |  | 1.57 |  | 1.25 | [8 empty] | 20.55 |  |  |  |  | 1.29
2001 |  |  |  | 7026.30 |  |  | 8760 |  |  |  | 790 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.53 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2002 |  |  |  | 4819.35 |  |  | 6121 |  |  |  | 790 | [10 empty] | 69.49 |  |  |  | 69.49 | [5 empty] | 69.64 |  |  | 69.87 |  |  |  | 1.46 |  | 3.67 | [8 empty] | 26.84 |  |  |  |  | 0.00
2003 |  |  |  | 6730.24 |  |  | 8592 |  |  |  | 790 | [10 empty] | 97.66 |  |  |  | 97.66 | [5 empty] | 97.25 |  |  | 98.08 |  |  |  | 2.20 |  | 2.20 | [8 empty] | 0.14 |  |  |  |  | 0.00
2004 |  |  |  | 6428.77 |  |  | 8188 |  |  |  | 790 | [10 empty] | 92.77 |  |  |  | 92.77 | [5 empty] | 92.64 |  |  | 93.21 |  |  |  | 0.00 |  | 0.03 | [8 empty] | 7.20 |  |  |  |  | 0.00
2005 |  |  |  | 4890.45 |  |  | 6310 |  |  |  | 790 | [10 empty] | 70.21 |  |  |  | 70.23 | [5 empty] | 70.07 |  |  | 72.03 |  |  |  | 3.28 |  | 5.70 | [8 empty] | 24.07 |  |  |  |  | 0.02
2006 |  |  |  | 6740.47 |  |  | 8486 |  |  |  | 806 | [10 empty] | 94.79 |  |  |  | 95.06 | [5 empty] | 94.37 |  |  | 96.87 |  |  |  | 4.30 |  | 4.27 | [8 empty] | 0.67 |  |  |  |  | 0.28
2007 |  |  |  | 6969.91 |  |  | 8570 |  |  |  | 822 | [10 empty] | 97.07 |  |  |  | 97.33 | [5 empty] | 96.79 |  |  | 97.83 |  |  |  | 2.49 |  | 2.48 | [8 empty] | 0.18 |  |  |  |  | 0.26
2008 |  |  |  | 5763.74 |  |  | 7101 |  |  |  | 817 | [10 empty] | 79.92 |  |  |  | 80.08 | [5 empty] | 80.31 |  |  | 80.84 |  |  |  | 3.49 |  | 5.99 | [8 empty] | 13.93 |  |  |  |  | 0.16
2009 |  |  |  | 6475.33 |  |  | 8144 |  |  |  | 817 | [10 empty] | 97.93 |  |  |  | 97.93 | [5 empty] | 90.48 |  |  | 92.97 |  |  |  | 1.99 |  | 1.98 | [8 empty] | 0.08 |  |  |  |  | 0.01
2010 |  |  |  | 6726.64 |  |  | 8610 |  |  |  | 817 | [10 empty] | 93.68 |  |  |  | 93.84 | [5 empty] | 93.99 |  |  | 98.29 |  |  |  | 5.98 |  | 5.97 | [8 empty] | 0.19 |  |  |  |  | 0.16
2011 |  |  |  | 5761.53 |  |  | 7137 |  |  |  | 817 | [10 empty] | 80.73 |  |  |  | 80.82 | [5 empty] | 80.50 |  |  | 81.47 |  |  |  | 0.17 |  | 4.98 | [8 empty] | 14.20 |  |  |  |  | 0.09
2012 |  |  |  | 7055.97 |  |  | 8731 |  |  |  | 817 | [10 empty] | 99.55 |  |  |  | 99.68 | [5 empty] | 98.32 |  |  | 99.40 |  |  |  | 0.24 |  | 0.24 | [8 empty] | 0.08 |  |  |  |  | 0.14
2013 |  |  |  | 7003.57 |  |  | 8758 |  |  |  | 817 | [10 empty] | 99.42 |  |  |  | 99.49 | [5 empty] | 97.86 |  |  | 99.98 |  |  |  | 0.51 |  | 0.51 | [8 empty] | 0.00 |  |  |  |  | 0.07
2014 |  |  |  | 5479.21 |  |  | 7113 |  |  |  | 817 | [10 empty] | 80.72 |  |  |  | 80.72 | [5 empty] | 76.56 |  |  | 81.20 |  |  |  | 1.04 |  | 4.01 | [8 empty] | 15.27 |  |  |  |  | 0.00
2015 |  |  |  | 6324.10 |  |  | 8029 |  |  |  | 817 | [10 empty] | 91.46 |  |  |  | 91.46 | [5 empty] | 88.36 |  |  | 91.66 |  |  |  | 1.35 |  | 1.26 | [8 empty] | 7.29 |  |  |  |  | 0.00
2016 |  |  |  | 4983.38 |  |  | 6332 |  |  |  | 817 | [10 empty] | 71.92 |  |  |  | 72.20 | [5 empty] | 69.44 |  |  | 72.09 |  |  |  | 0.00 |  | 2.23 | [8 empty] | 25.57 |  |  |  |  | 0.27
2017 |  |  |  | 6643.16 |  |  | 8431 |  |  |  | 817 | [10 empty] | 96.33 |  |  |  | 96.53 | [5 empty] | 92.82 |  |  | 96.24 |  |  |  | 3.28 |  | 3.27 | [8 empty] | 0.20 |  |  |  |  | 0.20
2018 |  |  |  | 7116.79 |  |  | 8715 |  |  |  | 817 | [10 empty] | 99.01 |  |  |  | 99.07 | [5 empty] | 99.44 |  |  | 99.49 |  |  |  | 0.91 |  | 0.91 | [8 empty] | 0.02 |  |  |  |  | 0.06
2019 |  |  |  | 4849.09 |  |  | 6036 |  |  |  | 817 | [10 empty] | 68.32 |  |  |  | 68.46 | [5 empty] | 67.75 |  |  | 68.90 |  |  |  | 0.19 |  | 6.15 | [8 empty] | 25.39 |  |  |  |  | 0.14
2020 |  |  |  | 7036.81 |  |  | 8664 |  |  |  | 817 | [10 empty] | 97.96 |  |  |  | 98.04 | [5 empty] | 98.05 |  |  | 98.63 |  |  |  | 1.71 |  | 1.71 | [8 empty] | 0.25 |  |  |  |  | 0.08
2021 |  |  |  | 5948.94 |  |  | 7264 |  |  |  | 817 | [10 empty] | 82.66 |  |  |  | 82.76 | [5 empty] | 83.12 |  |  | 82.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.24 |  |  |  |  | 0.09
2022 |  |  |  | 6676.03 |  |  | 8208 |  |  |  | 817 | [10 empty] | 92.94 |  |  |  | 93.10 | [5 empty] | 93.28 |  |  | 93.70 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 6.84 |  |  |  |  | 0.16
2023 |  |  |  | 7176.72 |  |  | 8760 |  |  |  | 817 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1986 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 228
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 17
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 610 |  |  |  | 8
E. |  | Testing of plant systems or components | [35 empty] | 8
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 60
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 18
L. |  | Human factor related | [39 empty] | 3
Z. |  | Other | [39 empty] | 9 | [11 empty] | 3
Subtotal | [37 empty] | 695 |  |  |  | 248 | [11 empty] | 21
Total | [22 empty] | 0 | [14 empty] | 964
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1986 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 30
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 5
15. |  |  | Reactor Cooling Systems | [34 empty] | 37
16. |  |  | Steam generation systems | [34 empty] | 23
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 25
31. |  |  | Turbine and auxiliaries | [34 empty] | 29
32. |  |  | Feedwater and Main Steam System | [34 empty] | 27
33. |  |  | Circulating Water System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 28
41. |  |  | Main Generator Systems | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [37 empty] | 247

## BRUCE-8
2023 Operating Experience
CA-21 | [8 empty] | BRUCE-8 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | BRUCEPOW (Bruce Power)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | CGE (CANADIAN GENERAL ELECTRIC)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 750B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-07-30
Thermal power | [12 empty] | : |  |  | 2690 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-03-07
Gross electrical power | [12 empty] | : |  |  | 872 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-05-20
Reference unit power (net) | [12 empty] | : |  |  | 817 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.49
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 305
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 8
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.88
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7710 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.78
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 1 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 4955.12 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.77 %
Energy Availability Factor (EAF) | [18 empty] | : | 69.63 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.26 %
Unit Capability Factor (UCF) | [18 empty] | : | 69.63 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 29.12 %
Load Factor (LF) | [18 empty] | : | 69.24 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 71.32 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2512 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 608.77 | 496.72 |  |  |  | 455.90 |  | 583.41 | [8 empty] | 600.04 |  |  | 582.17 | [6 empty] | 597.23 |  | 595.81 |  |  |  | 235.53 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 199.53 |  |  | 4955.12
EAF [%] |  |  |  |  | 100.00 | 90.92 |  |  |  | 75.22 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 98.55 |  | 98.23 |  |  |  | 40.61 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 32.83 |  |  | 69.63
UCF [%] |  |  |  |  | 100.00 | 90.92 |  |  |  | 75.22 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 98.55 |  | 98.23 |  |  |  | 40.61 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 32.83 |  |  | 69.63
LF [%] |  |  |  |  | 100.15 | 90.47 |  |  |  | 75.00 |  | 99.18 | [8 empty] | 98.72 |  |  | 98.97 | [6 empty] | 98.25 |  | 98.02 |  |  |  | 40.04 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 32.83 |  |  | 69.24
OF [%] |  |  |  |  | 100.00 | 90.92 |  |  |  | 76.88 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 42.92 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 45.70 |  |  | 71.32
FLR [%] |  |  |  |  | 0.00 | 9.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 14.35 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.77
UCL [%] |  |  |  |  | 0.00 | 9.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 6.81 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.26
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 24.78 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 1.45 |  | 1.77 |  |  |  | 52.59 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 67.17 |  |  | 29.12
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 217835.18 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.61 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.98 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.79 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.42 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.82 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.93 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 3673.23 |  |  | 5849 |  |  |  | 844 | [10 empty] | 76.58 |  |  |  | 99.06 | [5 empty] | 76.45 |  |  | 99.90 |  |  |  | 0.69 |  | 0.69 | [8 empty] | 0.25 |  |  |  |  | 22.48
1988 |  |  |  | 5958.52 |  |  | 7659 |  |  |  | 837 | [10 empty] | 86.53 |  |  |  | 86.85 | [5 empty] | 81.04 |  |  | 87.19 |  |  |  | 8.74 |  | 8.32 | [8 empty] | 4.83 |  |  |  |  | 0.32
1989 |  |  |  | 6523.47 |  |  | 8661 |  |  |  | 837 | [10 empty] | 89.21 |  |  |  | 98.45 | [5 empty] | 88.97 |  |  | 98.87 |  |  |  | 1.29 |  | 1.29 | [8 empty] | 0.26 |  |  |  |  | 9.24
1990 |  |  |  | 5758.67 |  |  | 7186 |  |  |  | 842 | [10 empty] | 78.09 |  |  |  | 80.67 | [5 empty] | 78.00 |  |  | 82.03 |  |  |  | 7.58 |  | 6.62 | [8 empty] | 12.71 |  |  |  |  | 2.58
1991 |  |  |  | 6932.70 |  |  | 8213 |  |  |  | 860 | [10 empty] | 92.47 |  |  |  | 92.96 | [5 empty] | 92.02 |  |  | 93.76 |  |  |  | 1.65 |  | 1.56 | [8 empty] | 5.48 |  |  |  |  | 0.48
1992 |  |  |  | 5451.09 |  |  | 6587 |  |  |  | 860 | [10 empty] | 72.41 |  |  |  | 72.43 | [5 empty] | 72.16 |  |  | 74.99 |  |  |  | 11.73 |  | 9.63 | [8 empty] | 17.94 |  |  |  |  | 0.02
1993 |  |  |  | 4675.90 |  |  | 7064 |  |  |  | 860 | [10 empty] | 62.27 |  |  |  | 62.27 | [5 empty] | 62.07 |  |  | 80.64 |  |  |  | 28.79 |  | 25.18 | [8 empty] | 12.55 |  |  |  |  | 0.00
1994 |  |  |  | 6443.16 |  |  | 8760 |  |  |  | 860 | [10 empty] | 86.00 |  |  |  | 86.00 | [5 empty] | 85.53 |  |  | 100.00 |  |  |  | 13.88 |  | 13.86 | [8 empty] | 0.15 |  |  |  |  | 0.00
1995 |  |  |  | 6113.35 |  |  | 7876 |  |  |  | 860 | [10 empty] | 81.34 |  |  |  | 81.34 | [5 empty] | 81.15 |  |  | 89.91 |  |  |  | 9.36 |  | 8.40 | [8 empty] | 10.26 |  |  |  |  | 0.00
1996 |  |  |  | 6957.82 |  |  | 8783 |  |  |  | 860 | [10 empty] | 92.14 |  |  |  | 92.14 | [5 empty] | 92.10 |  |  | 99.99 |  |  |  | 7.86 |  | 7.86 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 6346.54 |  |  | 8003 |  |  |  | 860 | [10 empty] | 84.24 |  |  |  | 84.24 | [5 empty] | 84.24 |  |  | 91.36 |  |  |  | 15.73 |  | 15.72 | [8 empty] | 0.03 |  |  |  |  | 0.00
1998 |  |  |  | 4122.43 |  |  | 5368 |  |  |  | 785 | [10 empty] | 59.76 |  |  |  | 59.86 | [5 empty] | 59.95 |  |  | 61.28 |  |  |  | 18.78 |  | 13.84 | [8 empty] | 26.30 |  |  |  |  | 0.10
1999 |  |  |  | 4114.43 |  |  | 5414 |  |  |  | 785 | [10 empty] | 59.77 |  |  |  | 59.98 | [5 empty] | 59.83 |  |  | 61.80 |  |  |  | 15.23 |  | 10.77 | [8 empty] | 29.25 |  |  |  |  | 0.21
2000 |  |  |  | 6530.94 |  |  | 8293 |  |  |  | 785 | [10 empty] | 93.67 |  |  |  | 93.67 | [5 empty] | 94.71 |  |  | 94.41 |  |  |  | 4.25 |  | 4.16 | [8 empty] | 2.17 |  |  |  |  | 0.00
2001 |  |  |  | 5424.77 |  |  | 6852 |  |  |  | 790 | [10 empty] | 78.03 |  |  |  | 78.03 | [5 empty] | 78.39 |  |  | 78.22 |  |  |  | 4.50 |  | 3.67 | [8 empty] | 18.30 |  |  |  |  | 0.00
2002 |  |  |  | 6685.96 |  |  | 8543 |  |  |  | 790 | [10 empty] | 97.01 |  |  |  | 97.01 | [5 empty] | 96.61 |  |  | 97.52 |  |  |  | 2.99 |  | 2.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 4959.99 |  |  | 6301 |  |  |  | 790 | [10 empty] | 71.89 |  |  |  | 71.89 | [5 empty] | 71.67 |  |  | 71.93 |  |  |  | 0.08 |  | 11.29 | [8 empty] | 16.81 |  |  |  |  | 0.00
2004 |  |  |  | 5695.77 |  |  | 7374 |  |  |  | 790 | [10 empty] | 82.80 |  |  |  | 83.01 | [5 empty] | 82.08 |  |  | 83.95 |  |  |  | 11.13 |  | 10.39 | [8 empty] | 6.60 |  |  |  |  | 0.21
2005 |  |  |  | 6889.22 |  |  | 8745 |  |  |  | 790 | [10 empty] | 99.44 |  |  |  | 99.65 | [5 empty] | 99.55 |  |  | 99.83 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.01 |  |  |  |  | 0.22
2006 |  |  |  | 5283.88 |  |  | 6791 |  |  |  | 790 | [10 empty] | 76.37 |  |  |  | 76.58 | [5 empty] | 76.31 |  |  | 77.52 |  |  |  | 4.47 |  | 5.14 | [8 empty] | 18.28 |  |  |  |  | 0.20
2007 |  |  |  | 6485.25 |  |  | 8341 |  |  |  | 795 | [10 empty] | 93.39 |  |  |  | 94.04 | [5 empty] | 93.12 |  |  | 95.22 |  |  |  | 2.41 |  | 2.32 | [8 empty] | 3.64 |  |  |  |  | 0.65
2008 |  |  |  | 6514.39 |  |  | 8699 |  |  |  | 782 | [10 empty] | 94.30 |  |  |  | 94.52 | [5 empty] | 94.84 |  |  | 99.03 |  |  |  | 5.43 |  | 5.42 | [8 empty] | 0.06 |  |  |  |  | 0.22
2009 |  |  |  | 5266.44 |  |  | 6906 |  |  |  | 782 | [10 empty] | 80.58 |  |  |  | 80.58 | [5 empty] | 76.88 |  |  | 78.84 |  |  |  | 1.79 |  | 4.43 | [8 empty] | 14.99 |  |  |  |  | 0.00
2010 |  |  |  | 6930.19 |  |  | 8760 |  |  |  | 817 | [10 empty] | 98.61 |  |  |  | 98.78 | [5 empty] | 98.93 |  |  | 100.00 |  |  |  | 0.75 |  | 0.74 | [8 empty] | 0.48 |  |  |  |  | 0.16
2011 |  |  |  | 6453.40 |  |  | 8015 |  |  |  | 817 | [10 empty] | 91.37 |  |  |  | 91.44 | [5 empty] | 90.17 |  |  | 91.50 |  |  |  | 1.81 |  | 2.81 | [8 empty] | 5.75 |  |  |  |  | 0.07
2012 |  |  |  | 5682.67 |  |  | 7161 |  |  |  | 817 | [10 empty] | 85.48 |  |  |  | 85.62 | [5 empty] | 79.18 |  |  | 81.52 |  |  |  | 1.87 |  | 3.88 | [8 empty] | 10.51 |  |  |  |  | 0.14
2013 |  |  |  | 5656.62 |  |  | 7141 |  |  |  | 817 | [10 empty] | 80.58 |  |  |  | 80.64 | [5 empty] | 79.04 |  |  | 81.52 |  |  |  | 7.01 |  | 6.08 | [8 empty] | 13.28 |  |  |  |  | 0.07
2014 |  |  |  | 6873.54 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.87 |  |  |  | 99.87 | [5 empty] | 96.04 |  |  | 100.00 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6288.54 |  |  | 8001 |  |  |  | 817 | [10 empty] | 90.66 |  |  |  | 90.66 | [5 empty] | 87.87 |  |  | 91.34 |  |  |  | 2.36 |  | 2.19 | [8 empty] | 7.15 |  |  |  |  | 0.00
2016 |  |  |  | 5038.39 |  |  | 6291 |  |  |  | 817 | [10 empty] | 71.41 |  |  |  | 71.41 | [5 empty] | 70.21 |  |  | 71.62 |  |  |  | 1.17 |  | 0.84 | [8 empty] | 27.74 |  |  |  |  | 0.00
2017 |  |  |  | 6992.50 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.70 |  |  |  | 99.98 | [5 empty] | 97.70 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.28
2018 |  |  |  | 4816.88 |  |  | 6123 |  |  |  | 817 | [10 empty] | 67.07 |  |  |  | 67.14 | [5 empty] | 67.30 |  |  | 69.90 |  |  |  | 2.68 |  | 10.62 | [8 empty] | 22.25 |  |  |  |  | 0.07
2019 |  |  |  | 7082.00 |  |  | 8760 |  |  |  | 817 | [10 empty] | 99.75 |  |  |  | 99.82 | [5 empty] | 98.95 |  |  | 100.00 |  |  |  | 0.18 |  | 0.18 | [8 empty] | 0.01 |  |  |  |  | 0.07
2020 |  |  |  | 4936.59 |  |  | 6141 |  |  |  | 817 | [10 empty] | 68.69 |  |  |  | 68.82 | [5 empty] | 68.79 |  |  | 69.91 |  |  |  | 2.40 |  | 1.69 | [8 empty] | 29.49 |  |  |  |  | 0.13
2021 |  |  |  | 6880.50 |  |  | 8472 |  |  |  | 817 | [10 empty] | 95.80 |  |  |  | 96.12 | [5 empty] | 96.14 |  |  | 96.71 |  |  |  | 3.81 |  | 3.81 | [8 empty] | 0.07 |  |  |  |  | 0.32
2022 |  |  |  | 6985.60 |  |  | 8616 |  |  |  | 817 | [10 empty] | 97.52 |  |  |  | 97.85 | [5 empty] | 97.61 |  |  | 98.36 |  |  |  | 2.01 |  | 2.01 | [8 empty] | 0.14 |  |  |  |  | 0.33
2023 |  |  |  | 4955.12 |  |  | 6248 |  |  |  | 817 | [10 empty] | 69.63 |  |  |  | 69.63 | [5 empty] | 69.24 |  |  | 71.32 |  |  |  | 1.77 |  | 1.26 | [8 empty] | 29.12 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1987 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 110 | [14 empty] | 287
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 103
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2402 | [14 empty] | 706 |  |  |  | 27
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 21
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 2402 |  |  |  | 110 | [10 empty] | 809 |  |  |  | 321 | [11 empty] | 21
Total | [22 empty] | 2512 | [14 empty] | 1151
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1987 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 31
12. |  |  | Reactor I&C Systems | [34 empty] | 8
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 50
16. |  |  | Steam generation systems | [34 empty] | 137
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 12
31. |  |  | Turbine and auxiliaries | [19 empty] | 49 | [14 empty] | 17
32. |  |  | Feedwater and Main Steam System | [34 empty] | 12
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [19 empty] | 61 | [14 empty] | 17
Total | [22 empty] | 110 | [14 empty] | 318

## DARLINGTON-1
2023 Operating Experience
CA-22 | [8 empty] | DARLINGTON-1 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-04-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-12-19
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1992-11-14
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 0 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 0 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 100 %
Load Factor (LF) | [18 empty] | : | 0 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 0 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 8760 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 196048.69 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.53 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.05 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.8 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.97 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.23 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 79.66 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.92 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.43 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1992 |  |  |  | 973.98 |  |  | 1152 |  |  |  | 881 | [10 empty] | 96.83 |  |  |  | 96.83 | [5 empty] | 75.51 |  |  | 78.69 |  |  |  | 3.17 |  | 3.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 6016.23 |  |  | 7213 |  |  |  | 881 | [10 empty] | 78.72 |  |  |  | 79.18 | [5 empty] | 77.96 |  |  | 82.34 |  |  |  | 9.34 |  | 8.16 | [8 empty] | 12.66 |  |  |  |  | 0.45
1994 |  |  |  | 6326.65 |  |  | 7446 |  |  |  | 881 | [10 empty] | 83.13 |  |  |  | 83.46 | [5 empty] | 81.98 |  |  | 85.00 |  |  |  | 10.94 |  | 10.25 | [8 empty] | 6.29 |  |  |  |  | 0.33
1995 |  |  |  | 6853.27 |  |  | 8046 |  |  |  | 881 | [10 empty] | 89.72 |  |  |  | 90.65 | [5 empty] | 88.80 |  |  | 91.85 |  |  |  | 4.41 |  | 4.19 | [8 empty] | 5.16 |  |  |  |  | 0.94
1996 |  |  |  | 5745.25 |  |  | 6827 |  |  |  | 881 | [10 empty] | 75.03 |  |  |  | 75.68 | [5 empty] | 74.24 |  |  | 77.72 |  |  |  | 20.47 |  | 19.48 | [8 empty] | 4.84 |  |  |  |  | 0.65
1997 |  |  |  | 4765.08 |  |  | 7236 |  |  |  | 881 | [10 empty] | 62.33 |  |  |  | 63.04 | [5 empty] | 61.74 |  |  | 82.60 |  |  |  | 31.33 |  | 28.76 | [8 empty] | 8.20 |  |  |  |  | 0.71
1998 |  |  |  | 6427.46 |  |  | 7717 |  |  |  | 881 | [10 empty] | 83.28 |  |  |  | 84.27 | [5 empty] | 83.28 |  |  | 88.09 |  |  |  | 6.58 |  | 5.94 | [8 empty] | 9.79 |  |  |  |  | 0.99
1999 |  |  |  | 7175.13 |  |  | 8705 |  |  |  | 881 | [10 empty] | 92.97 |  |  |  | 94.35 | [5 empty] | 92.97 |  |  | 99.37 |  |  |  | 5.65 |  | 5.65 | [8 empty] | 0.00 |  |  |  |  | 1.38
2000 |  |  |  | 6280.57 |  |  | 7615 |  |  |  | 881 | [10 empty] | 81.18 |  |  |  | 81.97 | [5 empty] | 81.16 |  |  | 86.69 |  |  |  | 5.20 |  | 4.49 | [8 empty] | 13.54 |  |  |  |  | 0.79
2001 |  |  |  | 6980.80 |  |  | 8502 |  |  |  | 881 | [10 empty] | 90.45 |  |  |  | 91.17 | [5 empty] | 90.45 |  |  | 97.05 |  |  |  | 5.81 |  | 5.62 | [8 empty] | 3.21 |  |  |  |  | 0.71
2002 |  |  |  | 6532.91 |  |  | 7887 |  |  |  | 881 | [10 empty] | 84.65 |  |  |  | 85.51 | [5 empty] | 84.65 |  |  | 90.03 |  |  |  | 7.89 |  | 7.32 | [8 empty] | 7.16 |  |  |  |  | 0.86
2003 |  |  |  | 6562.38 |  |  | 7846 |  |  |  | 881 | [10 empty] | 85.10 |  |  |  | 87.47 | [5 empty] | 85.03 |  |  | 89.57 |  |  |  | 5.14 |  | 4.74 | [8 empty] | 7.79 |  |  |  |  | 2.38
2004 |  |  |  | 5612.12 |  |  | 6540 |  |  |  | 881 | [10 empty] | 72.82 |  |  |  | 73.58 | [5 empty] | 72.52 |  |  | 74.45 |  |  |  | 9.72 |  | 7.92 | [8 empty] | 18.50 |  |  |  |  | 0.76
2005 |  |  |  | 7366.26 |  |  | 8553 |  |  |  | 881 | [10 empty] | 96.20 |  |  |  | 97.04 | [5 empty] | 95.69 |  |  | 97.64 |  |  |  | 2.96 |  | 2.96 | [8 empty] | 0.00 |  |  |  |  | 0.84
2006 |  |  |  | 6388.89 |  |  | 7520 |  |  |  | 878 | [10 empty] | 83.43 |  |  |  | 85.16 | [5 empty] | 83.07 |  |  | 85.84 |  |  |  | 1.85 |  | 2.36 | [8 empty] | 12.47 |  |  |  |  | 1.73
2007 |  |  |  | 7412.62 |  |  | 8647 |  |  |  | 878 | [10 empty] | 96.81 |  |  |  | 98.15 | [5 empty] | 96.38 |  |  | 98.71 |  |  |  | 1.74 |  | 1.74 | [8 empty] | 0.11 |  |  |  |  | 1.35
2008 |  |  |  | 6125.27 |  |  | 7125 |  |  |  | 878 | [10 empty] | 79.73 |  |  |  | 80.79 | [5 empty] | 79.42 |  |  | 81.11 |  |  |  | 0.08 |  | 0.06 | [8 empty] | 19.15 |  |  |  |  | 1.06
2009 |  |  |  | 6870.24 |  |  | 8038 |  |  |  | 878 | [10 empty] | 89.79 |  |  |  | 90.98 | [5 empty] | 89.33 |  |  | 91.76 |  |  |  | 0.66 |  | 0.60 | [8 empty] | 8.42 |  |  |  |  | 1.19
2010 |  |  |  | 7244.93 |  |  | 8660 |  |  |  | 878 | [10 empty] | 94.48 |  |  |  | 95.47 | [5 empty] | 94.20 |  |  | 98.86 |  |  |  | 4.48 |  | 4.48 | [8 empty] | 0.04 |  |  |  |  | 1.00
2011 |  |  |  | 6256.80 |  |  | 7313 |  |  |  | 878 | [10 empty] | 81.55 |  |  |  | 82.66 | [5 empty] | 81.35 |  |  | 83.48 |  |  |  | 0.44 |  | 0.36 | [8 empty] | 16.98 |  |  |  |  | 1.11
2012 |  |  |  | 7256.40 |  |  | 8468 |  |  |  | 878 | [10 empty] | 94.31 |  |  |  | 95.50 | [5 empty] | 94.09 |  |  | 96.40 |  |  |  | 4.44 |  | 4.44 | [8 empty] | 0.06 |  |  |  |  | 1.19
2013 |  |  |  | 7454.01 |  |  | 8760 |  |  |  | 878 | [10 empty] | 97.12 |  |  |  | 98.37 | [5 empty] | 96.92 |  |  | 100.00 |  |  |  | 1.37 |  | 1.37 | [8 empty] | 0.26 |  |  |  |  | 1.25
2014 |  |  |  | 5818.57 |  |  | 6848 |  |  |  | 878 | [10 empty] | 75.86 |  |  |  | 76.51 | [5 empty] | 75.65 |  |  | 78.17 |  |  |  | 2.22 |  | 1.74 | [8 empty] | 21.75 |  |  |  |  | 0.65
2015 |  |  |  | 5480.95 |  |  | 6449 |  |  |  | 878 | [10 empty] | 71.43 |  |  |  | 72.33 | [5 empty] | 71.26 |  |  | 73.62 |  |  |  | 8.35 |  | 7.09 | [8 empty] | 20.58 |  |  |  |  | 0.90
2016 |  |  |  | 7570.79 |  |  | 8784 |  |  |  | 878 | [10 empty] | 98.62 |  |  |  | 99.69 | [5 empty] | 98.16 |  |  | 100.00 |  |  |  | 0.25 |  | 0.25 | [8 empty] | 0.07 |  |  |  |  | 1.07
2017 |  |  |  | 4638.42 |  |  | 6181 |  |  |  | 878 | [10 empty] | 60.26 |  |  |  | 60.87 | [5 empty] | 60.31 |  |  | 70.56 |  |  |  | 3.49 |  | 2.20 | [8 empty] | 36.93 |  |  |  |  | 0.61
2018 |  |  |  | 7477.90 |  |  | 8606 |  |  |  | 878 | [10 empty] | 97.02 |  |  |  | 97.92 | [5 empty] | 97.23 |  |  | 98.24 |  |  |  | 0.69 |  | 1.43 | [8 empty] | 0.64 |  |  |  |  | 0.90
2019 |  |  |  | 7619.17 |  |  | 8760 |  |  |  | 878 | [10 empty] | 99.13 |  |  |  | 99.70 | [5 empty] | 99.06 |  |  | 100.00 |  |  |  | 0.29 |  | 0.29 | [8 empty] | 0.01 |  |  |  |  | 0.57
2020 |  |  |  | 7565.81 |  |  | 8784 |  |  |  | 878 | [10 empty] | 98.22 |  |  |  | 99.08 | [5 empty] | 98.10 |  |  | 100.00 |  |  |  | 0.81 |  | 0.81 | [8 empty] | 0.11 |  |  |  |  | 0.85
2021 |  |  |  | 5603.75 |  |  | 6621 |  |  |  | 878 | [10 empty] | 72.88 |  |  |  | 74.29 | [5 empty] | 72.86 |  |  | 75.58 |  |  |  | 5.32 |  | 4.17 | [8 empty] | 21.54 |  |  |  |  | 1.41
2022 |  |  |  | 943.49 |  |  | 1080 |  |  |  | 878 | [10 empty] | 12.26 |  |  |  | 12.26 | [5 empty] | 12.27 |  |  | 12.33 |  |  |  | 0.40 |  | 0.05 | [8 empty] | 87.69 |  |  |  |  | 0.00
2023 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1992 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 373
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 60
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 637
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [20 empty] | 8760 | [14 empty] | 562
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 0
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 8760 | [14 empty] | 1259 |  |  |  | 374 | [11 empty] | 3
Total | [22 empty] | 8760 | [14 empty] | 1636
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1992 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 27
12. |  |  | Reactor I&C Systems | [34 empty] | 32
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 12
15. |  |  | Reactor Cooling Systems | [34 empty] | 162
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 22
31. |  |  | Turbine and auxiliaries | [34 empty] | 15
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 7
35. |  |  | All other I&C Systems | [34 empty] | 20
41. |  |  | Main Generator Systems | [34 empty] | 43
42. |  |  | Electrical Power Supply Systems | [34 empty] | 10
Total | [37 empty] | 354
Highlights (2023)
Darlington Unit 1 continued its Refurbishment.

## DARLINGTON-2
2023 Operating Experience
CA-23 | [8 empty] | DARLINGTON-2 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-09-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-01-15
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-10-09
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7240.39 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.94 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.4 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.91 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.4 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 1.69 %
Load Factor (LF) | [18 empty] | : | 94.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2 %
Operating Factor (OF) | [18 empty] | : | 98.41 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 139 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 648.22 | 585.44 |  |  |  | 648.51 |  | 631.99 | [8 empty] | 649.27 |  |  | 615.94 | [6 empty] | 496.08 |  | 598.36 |  |  |  | 567.63 |  |  | 586.72 |  |  | 589.69 | [9 empty] | 622.54 |  |  | 7240.39
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 97.69 | [6 empty] | 75.94 |  | 91.60 |  |  |  | 89.79 |  |  | 89.82 |  |  | 93.28 | [9 empty] | 95.30 |  |  | 94.40
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.34 | [6 empty] | 80.55 |  | 98.82 |  |  |  | 99.37 |  |  | 90.14 |  |  | 93.56 | [9 empty] | 95.60 |  |  | 96.40
LF [%] |  |  |  |  | 99.23 | 99.22 |  |  |  | 99.28 |  | 99.97 | [8 empty] | 99.39 |  |  | 97.43 | [6 empty] | 75.94 |  | 91.60 |  |  |  | 89.79 |  |  | 89.82 |  |  | 93.28 | [9 empty] | 95.30 |  |  | 94.14
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 81.32 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.41
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.66 | [6 empty] | 19.45 |  | 1.18 |  |  |  | 0.06 |  |  | 0.25 |  |  | 0.36 | [9 empty] | 0.58 |  |  | 1.94
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.66 | [6 empty] | 19.45 |  | 1.18 |  |  |  | 0.06 |  |  | 0.23 |  |  | 0.34 | [9 empty] | 0.56 |  |  | 1.91
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.57 |  |  | 9.64 |  |  | 6.09 | [9 empty] | 3.84 |  |  | 1.69
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.65 | [6 empty] | 4.61 |  | 7.22 |  |  |  | 9.58 |  |  | 0.32 |  |  | 0.28 | [9 empty] | 0.30 |  |  | 2.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 185933.44 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 11.99 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.13 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 10.26 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 73.07 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.67 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.94 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.94 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 75.57 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 1153.47 |  |  | 1608 |  |  |  | 881 | [10 empty] | 64.94 |  |  |  | 64.94 | [5 empty] | 65.73 |  |  | 80.72 |  |  |  | 35.03 |  | 35.02 | [8 empty] | 0.04 |  |  |  |  | 0.00
1991 |  |  |  | 51.48 |  |  | 102 |  |  |  | 881 | [10 empty] | 0.67 |  |  |  | 0.67 | [5 empty] | 0.67 |  |  | 1.16 |  |  |  | 99.33 |  | 99.33 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 1290.16 |  |  | 2418 |  |  |  | 881 | [10 empty] | 16.68 |  |  |  | 16.68 | [5 empty] | 16.67 |  |  | 27.53 |  |  |  | 83.32 |  | 83.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 6370.16 |  |  | 7594 |  |  |  | 881 | [10 empty] | 82.74 |  |  |  | 83.28 | [5 empty] | 82.54 |  |  | 86.69 |  |  |  | 8.13 |  | 7.37 | [8 empty] | 9.34 |  |  |  |  | 0.54
1994 |  |  |  | 6750.76 |  |  | 8069 |  |  |  | 881 | [10 empty] | 88.52 |  |  |  | 88.90 | [5 empty] | 87.47 |  |  | 92.11 |  |  |  | 5.87 |  | 5.54 | [8 empty] | 5.56 |  |  |  |  | 0.38
1995 |  |  |  | 6952.96 |  |  | 8104 |  |  |  | 881 | [10 empty] | 90.65 |  |  |  | 91.30 | [5 empty] | 90.09 |  |  | 92.51 |  |  |  | 5.07 |  | 4.88 | [8 empty] | 3.82 |  |  |  |  | 0.65
1996 |  |  |  | 6705.75 |  |  | 7752 |  |  |  | 881 | [10 empty] | 87.22 |  |  |  | 87.76 | [5 empty] | 86.65 |  |  | 88.25 |  |  |  | 5.55 |  | 5.15 | [8 empty] | 7.09 |  |  |  |  | 0.53
1997 |  |  |  | 4710.39 |  |  | 7069 |  |  |  | 881 | [10 empty] | 61.53 |  |  |  | 61.73 | [5 empty] | 61.03 |  |  | 80.70 |  |  |  | 29.89 |  | 26.32 | [8 empty] | 11.95 |  |  |  |  | 0.20
1998 |  |  |  | 6227.93 |  |  | 7492 |  |  |  | 881 | [10 empty] | 80.70 |  |  |  | 81.91 | [5 empty] | 80.70 |  |  | 85.53 |  |  |  | 18.09 |  | 18.09 | [8 empty] | 0.00 |  |  |  |  | 1.21
1999 |  |  |  | 6469.08 |  |  | 7824 |  |  |  | 881 | [10 empty] | 83.82 |  |  |  | 85.13 | [5 empty] | 83.82 |  |  | 89.32 |  |  |  | 5.12 |  | 4.60 | [8 empty] | 10.27 |  |  |  |  | 1.31
2000 |  |  |  | 6885.42 |  |  | 8221 |  |  |  | 881 | [10 empty] | 88.97 |  |  |  | 90.14 | [5 empty] | 88.97 |  |  | 93.59 |  |  |  | 9.86 |  | 9.86 | [8 empty] | 0.00 |  |  |  |  | 1.17
2001 |  |  |  | 5826.45 |  |  | 7030 |  |  |  | 881 | [10 empty] | 75.50 |  |  |  | 76.30 | [5 empty] | 75.50 |  |  | 80.25 |  |  |  | 6.64 |  | 5.43 | [8 empty] | 18.27 |  |  |  |  | 0.81
2002 |  |  |  | 7268.93 |  |  | 8627 |  |  |  | 881 | [10 empty] | 94.19 |  |  |  | 95.43 | [5 empty] | 94.19 |  |  | 98.48 |  |  |  | 4.57 |  | 4.57 | [8 empty] | 0.00 |  |  |  |  | 1.25
2003 |  |  |  | 6084.10 |  |  | 7245 |  |  |  | 881 | [10 empty] | 79.29 |  |  |  | 81.59 | [5 empty] | 78.83 |  |  | 82.71 |  |  |  | 5.71 |  | 4.94 | [8 empty] | 13.47 |  |  |  |  | 2.30
2004 |  |  |  | 7038.38 |  |  | 8737 |  |  |  | 881 | [10 empty] | 91.42 |  |  |  | 96.71 | [5 empty] | 90.95 |  |  | 99.46 |  |  |  | 3.29 |  | 3.29 | [8 empty] | 0.00 |  |  |  |  | 5.29
2005 |  |  |  | 6056.21 |  |  | 7031 |  |  |  | 878 | [10 empty] | 78.93 |  |  |  | 79.75 | [5 empty] | 78.67 |  |  | 80.26 |  |  |  | 0.98 |  | 4.72 | [8 empty] | 15.53 |  |  |  |  | 0.82
2006 |  |  |  | 7548.39 |  |  | 8745 |  |  |  | 878 | [10 empty] | 98.59 |  |  |  | 99.38 | [5 empty] | 98.14 |  |  | 99.83 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.00 |  |  |  |  | 0.79
2007 |  |  |  | 6364.83 |  |  | 7327 |  |  |  | 878 | [10 empty] | 82.85 |  |  |  | 83.37 | [5 empty] | 82.75 |  |  | 83.64 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 16.62 |  |  |  |  | 0.52
2008 |  |  |  | 7560.94 |  |  | 8696 |  |  |  | 878 | [10 empty] | 98.15 |  |  |  | 98.82 | [5 empty] | 98.04 |  |  | 99.00 |  |  |  | 1.18 |  | 1.18 | [8 empty] | 0.00 |  |  |  |  | 0.67
2009 |  |  |  | 6745.27 |  |  | 7769 |  |  |  | 878 | [10 empty] | 87.67 |  |  |  | 88.37 | [5 empty] | 87.70 |  |  | 88.69 |  |  |  | 2.03 |  | 2.71 | [8 empty] | 8.91 |  |  |  |  | 0.70
2010 |  |  |  | 6234.30 |  |  | 7248 |  |  |  | 878 | [10 empty] | 81.14 |  |  |  | 82.48 | [5 empty] | 81.06 |  |  | 82.74 |  |  |  | 0.67 |  | 0.56 | [8 empty] | 16.96 |  |  |  |  | 1.34
2011 |  |  |  | 7503.51 |  |  | 8719 |  |  |  | 878 | [10 empty] | 97.74 |  |  |  | 98.90 | [5 empty] | 97.56 |  |  | 99.53 |  |  |  | 1.06 |  | 1.06 | [8 empty] | 0.04 |  |  |  |  | 1.16
2012 |  |  |  | 7157.95 |  |  | 8467 |  |  |  | 878 | [10 empty] | 92.97 |  |  |  | 93.92 | [5 empty] | 92.81 |  |  | 96.39 |  |  |  | 3.86 |  | 3.77 | [8 empty] | 2.30 |  |  |  |  | 0.96
2013 |  |  |  | 5138.76 |  |  | 6131 |  |  |  | 878 | [10 empty] | 66.97 |  |  |  | 67.33 | [5 empty] | 66.81 |  |  | 69.99 |  |  |  | 7.39 |  | 10.77 | [8 empty] | 21.91 |  |  |  |  | 0.36
2014 |  |  |  | 7412.53 |  |  | 8522 |  |  |  | 878 | [10 empty] | 96.38 |  |  |  | 96.90 | [5 empty] | 96.38 |  |  | 97.28 |  |  |  | 2.22 |  | 2.21 | [8 empty] | 0.89 |  |  |  |  | 0.52
2015 |  |  |  | 6405.95 |  |  | 7428 |  |  |  | 878 | [10 empty] | 83.41 |  |  |  | 84.28 | [5 empty] | 83.29 |  |  | 84.79 |  |  |  | 2.05 |  | 1.77 | [8 empty] | 13.95 |  |  |  |  | 0.87
2016 |  |  |  | 5728.84 |  |  | 6793 |  |  |  | 878 | [10 empty] | 74.41 |  |  |  | 75.73 | [5 empty] | 74.28 |  |  | 77.33 |  |  |  | 3.13 |  | 2.45 | [8 empty] | 21.82 |  |  |  |  | 1.32
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 4218.91 |  |  | 5144 |  |  |  | 878 | [10 empty] | 54.74 |  |  |  | 55.41 | [5 empty] | 54.70 |  |  | 58.56 |  |  |  | 5.06 |  | 2.95 | [8 empty] | 41.64 |  |  |  |  | 0.67
2021 |  |  |  | 7158.02 |  |  | 8568 |  |  |  | 878 | [10 empty] | 93.52 |  |  |  | 95.29 | [5 empty] | 93.07 |  |  | 97.81 |  |  |  | 4.67 |  | 4.66 | [8 empty] | 0.04 |  |  |  |  | 1.77
2022 |  |  |  | 5985.00 |  |  | 7018 |  |  |  | 878 | [10 empty] | 78.08 |  |  |  | 79.06 | [5 empty] | 77.82 |  |  | 80.11 |  |  |  | 9.49 |  | 8.29 | [8 empty] | 12.65 |  |  |  |  | 0.98
2023 |  |  |  | 7240.39 |  |  | 8621 |  |  |  | 878 | [10 empty] | 94.40 |  |  |  | 96.40 | [5 empty] | 94.14 |  |  | 98.41 |  |  |  | 1.94 |  | 1.91 | [8 empty] | 1.69 |  |  |  |  | 2.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1990 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 139 | [14 empty] | 486
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 488 |  |  |  | 10
E. |  | Testing of plant systems or components | [35 empty] | 12
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 943
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
Z. |  | Other | [39 empty] | 197
Subtotal | [26 empty] | 139 | [10 empty] | 1443 |  |  |  | 693 | [11 empty] | 2
Total | [22 empty] | 139 | [14 empty] | 2138
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1990 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 33
12. |  |  | Reactor I&C Systems | [34 empty] | 24
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [19 empty] | 139 | [14 empty] | 288
16. |  |  | Steam generation systems | [34 empty] | 37
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 20
31. |  |  | Turbine and auxiliaries | [34 empty] | 23
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 10
41. |  |  | Main Generator Systems | [34 empty] | 6
42. |  |  | Electrical Power Supply Systems | [34 empty] | 24
Total | [22 empty] | 139 | [14 empty] | 487
Highlights (2023)
In July 2023, there was an automatic reactor trip on U2. The turbine was manually tripped per procedure following the reactor trip.

## DARLINGTON-3
2023 Operating Experience
CA-24 | [8 empty] | DARLINGTON-3 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-09-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1992-12-07
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-02-14
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3440.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 44.74 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.94 %
Unit Capability Factor (UCF) | [18 empty] | : | 45.74 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 53.32 %
Load Factor (LF) | [18 empty] | : | 44.73 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1 %
Operating Factor (OF) | [18 empty] | : | 47.68 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4583 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 337.47 |  | 622.83 |  |  |  | 596.94 |  |  | 622.66 |  |  | 611.74 | [9 empty] | 648.78 |  |  | 3440.42
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 51.61 |  | 95.35 |  |  |  | 94.43 |  |  | 95.32 |  |  | 96.77 | [9 empty] | 99.50 |  |  | 44.74
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 54.74 |  | 99.49 |  |  |  | 98.97 |  |  | 95.43 |  |  | 96.77 | [9 empty] | 99.50 |  |  | 45.74
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 51.66 |  | 95.35 |  |  |  | 94.43 |  |  | 95.32 |  |  | 96.77 | [9 empty] | 99.32 |  |  | 44.73
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 67.88 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 47.68
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 16.62 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.14 |  |  | 2.01
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 10.91 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.14 |  |  | 0.94
PUF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 34.34 |  | 0.51 |  |  |  | 1.03 |  |  | 4.57 |  |  | 3.23 | [9 empty] | 0.36 |  |  | 53.32
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 3.13 |  | 4.15 |  |  |  | 4.54 |  |  | 0.11 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 186699.03 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.89 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.49 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.43 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.26 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.31 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.23 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.77 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.98 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 6003.39 |  |  | 7141 |  |  |  | 881 | [10 empty] | 89.24 |  |  |  | 89.81 | [5 empty] | 85.01 |  |  | 89.08 |  |  |  | 10.05 |  | 10.04 | [8 empty] | 0.15 |  |  |  |  | 0.57
1994 |  |  |  | 6528.54 |  |  | 7642 |  |  |  | 881 | [10 empty] | 85.26 |  |  |  | 85.64 | [5 empty] | 84.59 |  |  | 87.24 |  |  |  | 2.11 |  | 1.85 | [8 empty] | 12.51 |  |  |  |  | 0.38
1995 |  |  |  | 7061.53 |  |  | 8219 |  |  |  | 881 | [10 empty] | 92.22 |  |  |  | 92.93 | [5 empty] | 91.50 |  |  | 93.82 |  |  |  | 3.05 |  | 2.92 | [8 empty] | 4.15 |  |  |  |  | 0.71
1996 |  |  |  | 7391.57 |  |  | 8574 |  |  |  | 881 | [10 empty] | 96.66 |  |  |  | 97.34 | [5 empty] | 95.51 |  |  | 97.61 |  |  |  | 2.65 |  | 2.65 | [8 empty] | 0.01 |  |  |  |  | 0.68
1997 |  |  |  | 4010.78 |  |  | 6314 |  |  |  | 881 | [10 empty] | 52.10 |  |  |  | 52.35 | [5 empty] | 51.97 |  |  | 72.08 |  |  |  | 40.36 |  | 35.42 | [8 empty] | 12.22 |  |  |  |  | 0.25
1998 |  |  |  | 7244.91 |  |  | 8593 |  |  |  | 881 | [10 empty] | 93.88 |  |  |  | 94.68 | [5 empty] | 93.88 |  |  | 98.09 |  |  |  | 4.05 |  | 4.00 | [8 empty] | 1.32 |  |  |  |  | 0.80
1999 |  |  |  | 5629.08 |  |  | 6929 |  |  |  | 881 | [10 empty] | 72.94 |  |  |  | 75.09 | [5 empty] | 72.94 |  |  | 79.10 |  |  |  | 6.57 |  | 5.28 | [8 empty] | 19.63 |  |  |  |  | 2.15
2000 |  |  |  | 6517.02 |  |  | 7822 |  |  |  | 881 | [10 empty] | 84.22 |  |  |  | 85.10 | [5 empty] | 84.21 |  |  | 89.05 |  |  |  | 8.27 |  | 7.67 | [8 empty] | 7.23 |  |  |  |  | 0.88
2001 |  |  |  | 6577.97 |  |  | 7901 |  |  |  | 881 | [10 empty] | 85.23 |  |  |  | 86.30 | [5 empty] | 85.23 |  |  | 90.19 |  |  |  | 8.87 |  | 8.40 | [8 empty] | 5.30 |  |  |  |  | 1.07
2002 |  |  |  | 6371.77 |  |  | 7595 |  |  |  | 881 | [10 empty] | 82.58 |  |  |  | 83.68 | [5 empty] | 82.56 |  |  | 86.70 |  |  |  | 4.81 |  | 4.23 | [8 empty] | 12.09 |  |  |  |  | 1.10
2003 |  |  |  | 6827.19 |  |  | 8004 |  |  |  | 881 | [10 empty] | 88.62 |  |  |  | 89.45 | [5 empty] | 88.46 |  |  | 91.37 |  |  |  | 2.21 |  | 2.02 | [8 empty] | 8.53 |  |  |  |  | 0.83
2004 |  |  |  | 6601.58 |  |  | 7649 |  |  |  | 881 | [10 empty] | 85.59 |  |  |  | 86.88 | [5 empty] | 85.31 |  |  | 87.08 |  |  |  | 5.14 |  | 4.71 | [8 empty] | 8.41 |  |  |  |  | 1.29
2005 |  |  |  | 7562.05 |  |  | 8760 |  |  |  | 878 | [10 empty] | 98.26 |  |  |  | 99.08 | [5 empty] | 98.24 |  |  | 100.00 |  |  |  | 0.89 |  | 0.89 | [8 empty] | 0.02 |  |  |  |  | 0.83
2006 |  |  |  | 5573.10 |  |  | 6452 |  |  |  | 878 | [10 empty] | 72.50 |  |  |  | 73.12 | [5 empty] | 72.46 |  |  | 73.65 |  |  |  | 8.54 |  | 13.05 | [8 empty] | 13.84 |  |  |  |  | 0.62
2007 |  |  |  | 7221.13 |  |  | 8311 |  |  |  | 878 | [10 empty] | 93.90 |  |  |  | 94.75 | [5 empty] | 93.89 |  |  | 94.87 |  |  |  | 0.02 |  | 0.75 | [8 empty] | 4.49 |  |  |  |  | 0.85
2008 |  |  |  | 7654.59 |  |  | 8784 |  |  |  | 878 | [10 empty] | 99.15 |  |  |  | 99.93 | [5 empty] | 99.25 |  |  | 100.00 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.03 |  |  |  |  | 0.78
2009 |  |  |  | 5657.16 |  |  | 6590 |  |  |  | 878 | [10 empty] | 73.60 |  |  |  | 74.47 | [5 empty] | 73.55 |  |  | 75.23 |  |  |  | 2.00 |  | 3.62 | [8 empty] | 21.91 |  |  |  |  | 0.87
2010 |  |  |  | 7500.90 |  |  | 8643 |  |  |  | 878 | [10 empty] | 97.47 |  |  |  | 98.51 | [5 empty] | 97.52 |  |  | 98.66 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 1.43 |  |  |  |  | 1.04
2011 |  |  |  | 7558.56 |  |  | 8707 |  |  |  | 878 | [10 empty] | 98.37 |  |  |  | 99.17 | [5 empty] | 98.27 |  |  | 99.39 |  |  |  | 0.78 |  | 0.78 | [8 empty] | 0.04 |  |  |  |  | 0.81
2012 |  |  |  | 6377.61 |  |  | 7419 |  |  |  | 878 | [10 empty] | 83.03 |  |  |  | 83.97 | [5 empty] | 82.69 |  |  | 84.46 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 15.98 |  |  |  |  | 0.94
2013 |  |  |  | 7334.60 |  |  | 8470 |  |  |  | 878 | [10 empty] | 95.63 |  |  |  | 96.61 | [5 empty] | 95.36 |  |  | 96.69 |  |  |  | 3.35 |  | 3.35 | [8 empty] | 0.04 |  |  |  |  | 0.98
2014 |  |  |  | 7501.60 |  |  | 8708 |  |  |  | 878 | [10 empty] | 97.75 |  |  |  | 98.75 | [5 empty] | 97.53 |  |  | 99.41 |  |  |  | 1.23 |  | 1.23 | [8 empty] | 0.02 |  |  |  |  | 1.00
2015 |  |  |  | 4992.10 |  |  | 5787 |  |  |  | 878 | [10 empty] | 65.00 |  |  |  | 65.52 | [5 empty] | 64.91 |  |  | 66.06 |  |  |  | 8.58 |  | 7.75 | [8 empty] | 26.73 |  |  |  |  | 0.52
2016 |  |  |  | 6716.91 |  |  | 7832 |  |  |  | 878 | [10 empty] | 86.99 |  |  |  | 87.63 | [5 empty] | 87.09 |  |  | 89.16 |  |  |  | 5.93 |  | 5.53 | [8 empty] | 6.84 |  |  |  |  | 0.64
2017 |  |  |  | 7219.88 |  |  | 8442 |  |  |  | 878 | [10 empty] | 94.27 |  |  |  | 95.20 | [5 empty] | 93.87 |  |  | 96.37 |  |  |  | 1.42 |  | 1.37 | [8 empty] | 3.43 |  |  |  |  | 0.93
2018 |  |  |  | 5781.75 |  |  | 6718 |  |  |  | 878 | [10 empty] | 75.15 |  |  |  | 75.94 | [5 empty] | 75.17 |  |  | 76.69 |  |  |  | 1.62 |  | 1.25 | [8 empty] | 22.81 |  |  |  |  | 0.79
2019 |  |  |  | 7026.63 |  |  | 8178 |  |  |  | 878 | [10 empty] | 91.58 |  |  |  | 91.98 | [5 empty] | 91.36 |  |  | 93.36 |  |  |  | 7.52 |  | 7.48 | [8 empty] | 0.54 |  |  |  |  | 0.40
2020 |  |  |  | 4483.41 |  |  | 5087 |  |  |  | 878 | [10 empty] | 57.75 |  |  |  | 57.88 | [5 empty] | 58.13 |  |  | 57.91 |  |  |  | 0.04 |  | 0.37 | [8 empty] | 41.75 |  |  |  |  | 0.13
2021 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2022 |  |  |  | 0.00 |  |  | 0 |  |  |  | 878 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2023 |  |  |  | 3440.41 |  |  | 4177 |  |  |  | 878 | [10 empty] | 44.74 |  |  |  | 45.74 | [5 empty] | 44.73 |  |  | 47.68 |  |  |  | 2.01 |  | 0.94 | [8 empty] | 53.32 |  |  |  |  | 1.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1993 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 73 | [14 empty] | 238
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 64
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 539
E. |  | Testing of plant systems or components | [39 empty] | 5
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [20 empty] | 4511 | [14 empty] | 713
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 93
L. |  | Human factor related | [39 empty] | 3
Subtotal | [22 empty] | 4511 |  |  |  | 73 | [10 empty] | 1409 |  |  |  | 246
Total | [22 empty] | 4584 | [14 empty] | 1655
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1993 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 20
12. |  |  | Reactor I&C Systems | [34 empty] | 24
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 73 | [14 empty] | 31
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 39
16. |  |  | Steam generation systems | [34 empty] | 13
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 18
31. |  |  | Turbine and auxiliaries | [34 empty] | 51
32. |  |  | Feedwater and Main Steam System | [34 empty] | 13
34. |  |  | Miscellaneous Systems | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 17
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [22 empty] | 73 | [14 empty] | 245
Highlights (2023)
Commissioning activities continued in July 2023 . Official connection to the grid-July 17, 2023 Unit 3 was declared commercially in service on July 18, 2023 .

## DARLINGTON-4
2023 Operating Experience
CA-25 | [8 empty] | DARLINGTON-4 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 850 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-07-01
Thermal power | [12 empty] | : |  |  | 2776 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-04-17
Gross electrical power | [12 empty] | : |  |  | 934 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-06-14
Reference unit power (net) | [12 empty] | : |  |  | 878 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 10
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.0965
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.72 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | NA | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8625 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 7.068 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.93
| Active core height/length [m] | [13 empty] | : |  |  | 6.06 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 6240 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 24 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 4163.79 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.24 %
Energy Availability Factor (EAF) | [18 empty] | : | 54.25 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.13 %
Unit Capability Factor (UCF) | [18 empty] | : | 54.41 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 45.46 %
Load Factor (LF) | [18 empty] | : | 54.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.16 %
Operating Factor (OF) | [18 empty] | : | 54.54 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3982 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 653.23 | 585.72 |  |  |  | 645.54 |  | 628.20 | [8 empty] | 650.37 |  |  | 626.31 | [6 empty] | 374.42 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4163.79
EAF [%] |  |  |  |  | 100.00 | 99.46 |  |  |  | 98.79 |  | 100.00 | [8 empty] | 99.98 |  |  | 99.24 | [6 empty] | 57.31 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 54.25
UCF [%] |  |  |  |  | 100.00 | 99.59 |  |  |  | 98.99 |  | 100.00 | [8 empty] | 99.99 |  |  | 99.91 | [6 empty] | 58.28 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 54.41
LF [%] |  |  |  |  | 100.00 | 99.27 |  |  |  | 98.82 |  | 99.37 | [8 empty] | 99.56 |  |  | 99.07 | [6 empty] | 57.32 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 54.14
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 58.33 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 54.54
FLR [%] |  |  |  |  | 0.00 | 0.41 |  |  |  | 1.01 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.09 | [6 empty] | 0.10 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.24
UCL [%] |  |  |  |  | 0.00 | 0.41 |  |  |  | 1.01 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.09 | [6 empty] | 0.06 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.13
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 41.66 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 45.46
XUF [%] |  |  |  |  | 0.00 | 0.12 |  |  |  | 0.20 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.67 | [6 empty] | 0.97 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.16
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 200285.66 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.8 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.76 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.69 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.44 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.87 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.69 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.68 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.02 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 3528.78 |  |  | 4447 |  |  |  | 881 | [10 empty] | 73.87 |  |  |  | 74.02 | [5 empty] | 67.58 |  |  | 70.40 |  |  |  | 10.42 |  | 8.61 | [8 empty] | 17.37 |  |  |  |  | 0.15
1994 |  |  |  | 7038.67 |  |  | 8143 |  |  |  | 881 | [10 empty] | 91.85 |  |  |  | 92.19 | [5 empty] | 91.20 |  |  | 92.96 |  |  |  | 3.36 |  | 3.21 | [8 empty] | 4.60 |  |  |  |  | 0.35
1995 |  |  |  | 6750.56 |  |  | 7751 |  |  |  | 881 | [10 empty] | 87.72 |  |  |  | 88.14 | [5 empty] | 87.47 |  |  | 88.48 |  |  |  | 2.41 |  | 2.18 | [8 empty] | 9.68 |  |  |  |  | 0.43
1996 |  |  |  | 6105.35 |  |  | 7023 |  |  |  | 881 | [10 empty] | 79.14 |  |  |  | 79.37 | [5 empty] | 78.89 |  |  | 79.95 |  |  |  | 12.79 |  | 11.65 | [8 empty] | 8.98 |  |  |  |  | 0.23
1997 |  |  |  | 5069.64 |  |  | 7428 |  |  |  | 881 | [10 empty] | 65.71 |  |  |  | 65.97 | [5 empty] | 65.69 |  |  | 84.79 |  |  |  | 28.56 |  | 26.37 | [8 empty] | 7.65 |  |  |  |  | 0.27
1998 |  |  |  | 6520.88 |  |  | 7699 |  |  |  | 881 | [10 empty] | 84.49 |  |  |  | 85.32 | [5 empty] | 84.49 |  |  | 87.89 |  |  |  | 11.60 |  | 11.20 | [8 empty] | 3.48 |  |  |  |  | 0.83
1999 |  |  |  | 6216.13 |  |  | 7431 |  |  |  | 881 | [10 empty] | 80.55 |  |  |  | 81.60 | [5 empty] | 80.55 |  |  | 84.83 |  |  |  | 5.28 |  | 4.55 | [8 empty] | 13.85 |  |  |  |  | 1.05
2000 |  |  |  | 6975.02 |  |  | 8219 |  |  |  | 881 | [10 empty] | 90.13 |  |  |  | 90.78 | [5 empty] | 90.13 |  |  | 93.57 |  |  |  | 9.22 |  | 9.22 | [8 empty] | 0.00 |  |  |  |  | 0.65
2001 |  |  |  | 6836.35 |  |  | 8037 |  |  |  | 881 | [10 empty] | 88.58 |  |  |  | 89.62 | [5 empty] | 88.58 |  |  | 91.75 |  |  |  | 3.01 |  | 2.78 | [8 empty] | 7.59 |  |  |  |  | 1.04
2002 |  |  |  | 7449.79 |  |  | 8760 |  |  |  | 881 | [10 empty] | 96.53 |  |  |  | 97.33 | [5 empty] | 96.53 |  |  | 100.00 |  |  |  | 2.67 |  | 2.67 | [8 empty] | 0.00 |  |  |  |  | 0.80
2003 |  |  |  | 5428.86 |  |  | 6320 |  |  |  | 881 | [10 empty] | 70.64 |  |  |  | 72.28 | [5 empty] | 70.34 |  |  | 72.15 |  |  |  | 5.81 |  | 4.46 | [8 empty] | 23.26 |  |  |  |  | 1.64
2004 |  |  |  | 7321.13 |  |  | 8451 |  |  |  | 881 | [10 empty] | 94.60 |  |  |  | 95.25 | [5 empty] | 94.60 |  |  | 96.21 |  |  |  | 4.75 |  | 4.75 | [8 empty] | 0.00 |  |  |  |  | 0.65
2005 |  |  |  | 6569.70 |  |  | 7617 |  |  |  | 878 | [10 empty] | 85.63 |  |  |  | 86.47 | [5 empty] | 85.35 |  |  | 86.95 |  |  |  | 0.36 |  | 2.49 | [8 empty] | 11.04 |  |  |  |  | 0.84
2006 |  |  |  | 7449.44 |  |  | 8541 |  |  |  | 878 | [10 empty] | 96.54 |  |  |  | 97.08 | [5 empty] | 96.86 |  |  | 97.50 |  |  |  | 2.92 |  | 2.92 | [8 empty] | 0.00 |  |  |  |  | 0.54
2007 |  |  |  | 6210.23 |  |  | 7170 |  |  |  | 878 | [10 empty] | 80.77 |  |  |  | 81.44 | [5 empty] | 80.74 |  |  | 81.85 |  |  |  | 2.90 |  | 2.43 | [8 empty] | 16.13 |  |  |  |  | 0.67
2008 |  |  |  | 7525.46 |  |  | 8652 |  |  |  | 878 | [10 empty] | 97.35 |  |  |  | 98.39 | [5 empty] | 97.58 |  |  | 98.50 |  |  |  | 1.48 |  | 1.48 | [8 empty] | 0.13 |  |  |  |  | 1.05
2009 |  |  |  | 6836.15 |  |  | 7892 |  |  |  | 878 | [10 empty] | 88.71 |  |  |  | 89.71 | [5 empty] | 88.88 |  |  | 90.09 |  |  |  | 2.12 |  | 2.23 | [8 empty] | 8.06 |  |  |  |  | 1.00
2010 |  |  |  | 5633.65 |  |  | 6612 |  |  |  | 878 | [10 empty] | 73.26 |  |  |  | 73.62 | [5 empty] | 73.25 |  |  | 75.48 |  |  |  | 8.67 |  | 10.81 | [8 empty] | 15.57 |  |  |  |  | 0.36
2011 |  |  |  | 7617.80 |  |  | 8760 |  |  |  | 878 | [10 empty] | 98.89 |  |  |  | 99.73 | [5 empty] | 99.04 |  |  | 100.00 |  |  |  | 0.23 |  | 0.23 | [8 empty] | 0.04 |  |  |  |  | 0.85
2012 |  |  |  | 7557.72 |  |  | 8725 |  |  |  | 878 | [10 empty] | 97.88 |  |  |  | 98.99 | [5 empty] | 97.99 |  |  | 99.33 |  |  |  | 0.87 |  | 0.87 | [8 empty] | 0.14 |  |  |  |  | 1.11
2013 |  |  |  | 5237.45 |  |  | 6132 |  |  |  | 878 | [10 empty] | 68.25 |  |  |  | 68.83 | [5 empty] | 68.10 |  |  | 70.00 |  |  |  | 9.51 |  | 12.75 | [8 empty] | 18.42 |  |  |  |  | 0.58
2014 |  |  |  | 7302.71 |  |  | 8476 |  |  |  | 878 | [10 empty] | 95.24 |  |  |  | 95.97 | [5 empty] | 94.95 |  |  | 96.76 |  |  |  | 0.65 |  | 0.63 | [8 empty] | 3.40 |  |  |  |  | 0.73
2015 |  |  |  | 6532.11 |  |  | 7490 |  |  |  | 878 | [10 empty] | 84.72 |  |  |  | 85.13 | [5 empty] | 84.93 |  |  | 85.50 |  |  |  | 1.53 |  | 1.32 | [8 empty] | 13.55 |  |  |  |  | 0.40
2016 |  |  |  | 5774.65 |  |  | 6678 |  |  |  | 878 | [10 empty] | 74.66 |  |  |  | 75.46 | [5 empty] | 74.88 |  |  | 76.02 |  |  |  | 0.23 |  | 0.18 | [8 empty] | 24.36 |  |  |  |  | 0.80
2017 |  |  |  | 7593.09 |  |  | 8684 |  |  |  | 878 | [10 empty] | 98.10 |  |  |  | 98.77 | [5 empty] | 98.72 |  |  | 99.13 |  |  |  | 1.03 |  | 1.03 | [8 empty] | 0.20 |  |  |  |  | 0.67
2018 |  |  |  | 6993.41 |  |  | 8105 |  |  |  | 878 | [10 empty] | 90.71 |  |  |  | 91.56 | [5 empty] | 90.93 |  |  | 92.52 |  |  |  | 1.42 |  | 1.32 | [8 empty] | 7.12 |  |  |  |  | 0.85
2019 |  |  |  | 5423.69 |  |  | 6248 |  |  |  | 878 | [10 empty] | 70.07 |  |  |  | 70.44 | [5 empty] | 70.52 |  |  | 71.32 |  |  |  | 7.34 |  | 5.58 | [8 empty] | 23.99 |  |  |  |  | 0.37
2020 |  |  |  | 7294.39 |  |  | 8784 |  |  |  | 878 | [10 empty] | 94.26 |  |  |  | 94.87 | [5 empty] | 94.58 |  |  | 100.00 |  |  |  | 1.46 |  | 1.41 | [8 empty] | 3.72 |  |  |  |  | 0.61
2021 |  |  |  | 5970.37 |  |  | 6865 |  |  |  | 878 | [10 empty] | 77.24 |  |  |  | 78.00 | [5 empty] | 77.63 |  |  | 78.37 |  |  |  | 0.74 |  | 0.58 | [8 empty] | 21.42 |  |  |  |  | 0.76
2022 |  |  |  | 7159.58 |  |  | 8207 |  |  |  | 878 | [10 empty] | 92.53 |  |  |  | 93.02 | [5 empty] | 93.09 |  |  | 93.69 |  |  |  | 6.98 |  | 6.98 | [8 empty] | 0.00 |  |  |  |  | 0.49
2023 |  |  |  | 4163.79 |  |  | 4778 |  |  |  | 878 | [10 empty] | 54.25 |  |  |  | 54.41 | [5 empty] | 54.14 |  |  | 54.54 |  |  |  | 0.24 |  | 0.13 | [8 empty] | 45.46 |  |  |  |  | 0.16
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1993 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 274
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 86
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 615
E. |  | Testing of plant systems or components | [35 empty] | 11 |  |  |  | 2
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [20 empty] | 3982 | [14 empty] | 130
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 9
Subtotal | [22 empty] | 3982 | [14 empty] | 842 |  |  |  | 286 | [11 empty] | 4
Total | [22 empty] | 3982 | [14 empty] | 1132
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1993 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 4
12. |  |  | Reactor I&C Systems | [34 empty] | 38
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
14. |  |  | Safety Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 91
16. |  |  | Steam generation systems | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 15
31. |  |  | Turbine and auxiliaries | [34 empty] | 41
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 19
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 17
42. |  |  | Electrical Power Supply Systems | [34 empty] | 29
Total | [37 empty] | 289
Highlights (2023)
Unit 4 entered Refurbishment on July 19th,2023.

## PICKERING-1
2023 Operating Experience
CA-4 | [8 empty] | PICKERING-1 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500A | [11 empty] | Construction Date | [15 empty] | : |  |  | 1966-06-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1971-04-04
Gross electrical power | [12 empty] | : |  |  | 542 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1971-07-29
Reference unit power (net) | [12 empty] | : |  |  | 515 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 52 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 9080 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4680 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 26.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 6 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 4165.01 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.04 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.26 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 3.91 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.87 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 3.23 %
Load Factor (LF) | [18 empty] | : | 92.32 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.61 %
Operating Factor (OF) | [18 empty] | : | 95.18 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 422 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 129.35 | 343.55 |  |  |  | 383.67 |  | 359.09 | [8 empty] | 379.35 |  |  | 350.16 | [6 empty] | 371.29 |  | 372.02 |  |  |  | 358.61 |  |  | 362.29 |  |  | 372.62 | [9 empty] | 383.01 |  |  | 4165.01
EAF [%] |  |  |  |  | 33.81 | 99.26 |  |  |  | 100.00 |  | 96.96 | [8 empty] | 99.28 |  |  | 94.43 | [6 empty] | 96.90 |  | 97.19 |  |  |  | 96.71 |  |  | 94.62 |  |  | 99.95 | [9 empty] | 99.28 |  |  | 92.26
UCF [%] |  |  |  |  | 33.81 | 99.26 |  |  |  | 100.00 |  | 96.96 | [8 empty] | 99.28 |  |  | 95.64 | [6 empty] | 98.83 |  | 98.83 |  |  |  | 98.64 |  |  | 95.16 |  |  | 99.95 | [9 empty] | 99.28 |  |  | 92.87
LF [%] |  |  |  |  | 33.76 | 99.27 |  |  |  | 100.13 |  | 96.84 | [8 empty] | 99.01 |  |  | 94.43 | [6 empty] | 96.90 |  | 97.09 |  |  |  | 96.71 |  |  | 94.55 |  |  | 100.49 | [9 empty] | 99.96 |  |  | 92.32
OF [%] |  |  |  |  | 43.28 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.18
FLR [%] |  |  |  |  | 54.64 | 0.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.66 | [6 empty] | 1.17 |  | 1.17 |  |  |  | 1.36 |  |  | 0.33 |  |  | 0.05 | [9 empty] | 0.00 |  |  | 4.04
UCL [%] |  |  |  |  | 40.73 | 0.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.63 | [6 empty] | 1.17 |  | 1.17 |  |  |  | 1.36 |  |  | 0.31 |  |  | 0.05 | [9 empty] | 0.00 |  |  | 3.91
PUF [%] |  |  |  |  | 25.46 | 0.00 |  |  |  | 0.00 |  | 3.04 | [8 empty] | 0.72 |  |  | 3.72 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 4.53 |  |  | 0.00 | [9 empty] | 0.72 |  |  | 3.23
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.21 | [6 empty] | 1.93 |  | 1.64 |  |  |  | 1.93 |  |  | 0.53 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.61
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 134907.34 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 22.69 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 68.5 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 21.17 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 68.75 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.08 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 66.58 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.25 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 69.95 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1971 |  |  |  | 2302.30 |  |  | 4829 |  |  |  | 514 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 80.43 |  |  | 78.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1972 |  |  |  | 2207.90 |  |  | 4117 |  |  |  | 514 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 48.90 |  |  | 46.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 4222.40 |  |  | 8523 |  |  |  | 514 | [10 empty] | 93.98 |  |  |  | 93.98 | [5 empty] | 92.26 |  |  | 95.72 |  |  |  | 5.19 |  | 5.15 | [8 empty] | 0.88 |  |  |  |  | 0.00
1974 |  |  |  | 3232.00 |  |  | 6979 |  |  |  | 514 | [10 empty] | 71.92 |  |  |  | 71.92 | [5 empty] | 71.98 |  |  | 79.89 |  |  |  | 20.17 |  | 18.17 | [8 empty] | 9.91 |  |  |  |  | 0.00
1975 |  |  |  | 3592.80 |  |  | 7234 |  |  |  | 512 | [10 empty] | 80.17 |  |  |  | 80.17 | [5 empty] | 80.32 |  |  | 82.81 |  |  |  | 11.74 |  | 10.66 | [8 empty] | 9.17 |  |  |  |  | 0.00
1976 |  |  |  | 4169.70 |  |  | 8136 |  |  |  | 514 | [10 empty] | 92.73 |  |  |  | 92.73 | [5 empty] | 92.61 |  |  | 92.88 |  |  |  | 2.07 |  | 1.96 | [8 empty] | 5.31 |  |  |  |  | 0.00
1977 |  |  |  | 3852.80 |  |  | 7545 |  |  |  | 514 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 85.80 |  |  | 86.37 |  |  |  | 6.14 |  | 5.61 | [8 empty] | 8.59 |  |  |  |  | 0.00
1978 |  |  |  | 4273.70 |  |  | 8359 |  |  |  | 515 | [10 empty] | 95.09 |  |  |  | 95.09 | [5 empty] | 94.99 |  |  | 95.68 |  |  |  | 4.91 |  | 4.91 | [8 empty] | 0.00 |  |  |  |  | 0.00
1979 |  |  |  | 3781.40 |  |  | 7554 |  |  |  | 515 | [10 empty] | 85.29 |  |  |  | 85.29 | [5 empty] | 82.91 |  |  | 85.30 |  |  |  | 14.71 |  | 14.71 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 3356.90 |  |  | 6640 |  |  |  | 515 | [10 empty] | 73.68 |  |  |  | 73.68 | [5 empty] | 74.21 |  |  | 75.59 |  |  |  | 14.10 |  | 12.09 | [8 empty] | 14.23 |  |  |  |  | 0.00
1981 |  |  |  | 3947.70 |  |  | 7795 |  |  |  | 515 | [10 empty] | 88.05 |  |  |  | 88.05 | [5 empty] | 87.50 |  |  | 88.98 |  |  |  | 5.07 |  | 4.70 | [8 empty] | 7.25 |  |  |  |  | 0.00
1982 |  |  |  | 3499.30 |  |  | 6915 |  |  |  | 515 | [10 empty] | 77.80 |  |  |  | 77.80 | [5 empty] | 77.57 |  |  | 78.94 |  |  |  | 10.00 |  | 8.65 | [8 empty] | 13.55 |  |  |  |  | 0.00
1983 |  |  |  | 3070.80 |  |  | 6101 |  |  |  | 515 | [10 empty] | 68.11 |  |  |  | 68.11 | [5 empty] | 68.07 |  |  | 69.65 |  |  |  | 27.81 |  | 26.23 | [8 empty] | 5.66 |  |  |  |  | 0.00
1984 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 832.79 |  |  | 1981 |  |  |  | 515 | [10 empty] | 17.35 |  |  |  | 19.69 | [5 empty] | 18.46 |  |  | 22.61 |  |  |  | 78.69 |  | 72.71 | [8 empty] | 7.60 |  |  |  |  | 2.33
1988 |  |  |  | 3986.48 |  |  | 8224 |  |  |  | 515 | [10 empty] | 89.12 |  |  |  | 89.16 | [5 empty] | 88.12 |  |  | 93.62 |  |  |  | 10.81 |  | 10.81 | [8 empty] | 0.04 |  |  |  |  | 0.03
1989 |  |  |  | 3222.13 |  |  | 6943 |  |  |  | 515 | [10 empty] | 72.62 |  |  |  | 72.72 | [5 empty] | 71.42 |  |  | 79.26 |  |  |  | 20.54 |  | 18.80 | [8 empty] | 8.48 |  |  |  |  | 0.11
1990 |  |  |  | 3041.75 |  |  | 7435 |  |  |  | 515 | [10 empty] | 70.56 |  |  |  | 70.86 | [5 empty] | 67.42 |  |  | 84.87 |  |  |  | 22.19 |  | 20.21 | [8 empty] | 8.93 |  |  |  |  | 0.30
1991 |  |  |  | 3051.08 |  |  | 6525 |  |  |  | 515 | [10 empty] | 67.83 |  |  |  | 67.84 | [5 empty] | 67.63 |  |  | 74.49 |  |  |  | 18.36 |  | 15.26 | [8 empty] | 16.90 |  |  |  |  | 0.01
1992 |  |  |  | 2919.96 |  |  | 5798 |  |  |  | 515 | [10 empty] | 65.43 |  |  |  | 65.43 | [5 empty] | 64.55 |  |  | 66.01 |  |  |  | 22.58 |  | 19.09 | [8 empty] | 15.48 |  |  |  |  | 0.00
1993 |  |  |  | 3451.16 |  |  | 6908 |  |  |  | 515 | [10 empty] | 78.39 |  |  |  | 78.43 | [5 empty] | 76.50 |  |  | 78.86 |  |  |  | 8.82 |  | 7.59 | [8 empty] | 13.98 |  |  |  |  | 0.04
1994 |  |  |  | 897.64 |  |  | 1835 |  |  |  | 515 | [10 empty] | 20.12 |  |  |  | 20.12 | [5 empty] | 19.90 |  |  | 20.95 |  |  |  | 54.24 |  | 23.84 | [8 empty] | 56.04 |  |  |  |  | 0.00
1995 |  |  |  | 2013.23 |  |  | 4234 |  |  |  | 515 | [10 empty] | 44.85 |  |  |  | 45.71 | [5 empty] | 44.63 |  |  | 48.33 |  |  |  | 49.07 |  | 44.04 | [8 empty] | 10.25 |  |  |  |  | 0.86
1996 |  |  |  | 3011.76 |  |  | 6202 |  |  |  | 515 | [10 empty] | 66.83 |  |  |  | 66.83 | [5 empty] | 66.58 |  |  | 70.61 |  |  |  | 31.66 |  | 30.96 | [8 empty] | 2.22 |  |  |  |  | 0.00
1997 |  |  |  | 3950.80 |  |  | 8205 |  |  |  | 515 | [10 empty] | 89.68 |  |  |  | 89.68 | [5 empty] | 88.54 |  |  | 94.70 |  |  |  | 10.32 |  | 10.32 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | Data not available - Suspended Operation
1999 |  |  |  | "
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | "
2004 |  |  |  | "
2005 |  |  |  | 584.96 |  |  | 1230 |  |  |  | 515 | [10 empty] | 95.88 |  |  |  | 95.88 | [5 empty] | 51.42 |  |  | 55.68 |  |  |  | 4.12 |  | 4.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 3470.49 |  |  | 7260 |  |  |  | 515 | [10 empty] | 77.02 |  |  |  | 77.22 | [5 empty] | 76.93 |  |  | 82.88 |  |  |  | 19.42 |  | 18.85 | [8 empty] | 3.92 |  |  |  |  | 0.21
2007 |  |  |  | 1750.26 |  |  | 3447 |  |  |  | 515 | [10 empty] | 38.91 |  |  |  | 38.94 | [5 empty] | 38.80 |  |  | 39.35 |  |  |  | 50.80 |  | 43.22 | [8 empty] | 17.84 |  |  |  |  | 0.04
2008 |  |  |  | 2792.10 |  |  | 6221 |  |  |  | 515 | [10 empty] | 61.72 |  |  |  | 61.78 | [5 empty] | 61.72 |  |  | 70.82 |  |  |  | 37.71 |  | 37.70 | [8 empty] | 0.52 |  |  |  |  | 0.06
2009 |  |  |  | 4108.77 |  |  | 8436 |  |  |  | 515 | [10 empty] | 91.15 |  |  |  | 91.45 | [5 empty] | 91.08 |  |  | 96.30 |  |  |  | 8.50 |  | 8.50 | [8 empty] | 0.05 |  |  |  |  | 0.30
2010 |  |  |  | 2376.13 |  |  | 4983 |  |  |  | 515 | [10 empty] | 52.73 |  |  |  | 52.90 | [5 empty] | 52.67 |  |  | 56.88 |  |  |  | 22.60 |  | 18.82 | [8 empty] | 28.28 |  |  |  |  | 0.17
2011 |  |  |  | 3669.17 |  |  | 7382 |  |  |  | 515 | [10 empty] | 81.49 |  |  |  | 81.79 | [5 empty] | 81.33 |  |  | 84.27 |  |  |  | 18.21 |  | 18.21 | [8 empty] | 0.00 |  |  |  |  | 0.30
2012 |  |  |  | 2912.37 |  |  | 5799 |  |  |  | 515 | [10 empty] | 64.48 |  |  |  | 65.11 | [5 empty] | 64.38 |  |  | 66.02 |  |  |  | 4.03 |  | 5.44 | [8 empty] | 29.45 |  |  |  |  | 0.64
2013 |  |  |  | 2074.98 |  |  | 4344 |  |  |  | 515 | [10 empty] | 45.99 |  |  |  | 46.20 | [5 empty] | 45.99 |  |  | 49.59 |  |  |  | 33.45 |  | 53.27 | [8 empty] | 0.53 |  |  |  |  | 0.21
2014 |  |  |  | 3871.29 |  |  | 7855 |  |  |  | 515 | [10 empty] | 86.08 |  |  |  | 87.40 | [5 empty] | 85.81 |  |  | 89.67 |  |  |  | 12.55 |  | 12.55 | [8 empty] | 0.05 |  |  |  |  | 1.32
2015 |  |  |  | 2599.85 |  |  | 5263 |  |  |  | 515 | [10 empty] | 57.80 |  |  |  | 57.92 | [5 empty] | 57.63 |  |  | 60.08 |  |  |  | 2.63 |  | 6.31 | [8 empty] | 35.77 |  |  |  |  | 0.12
2016 |  |  |  | 4212.67 |  |  | 8784 |  |  |  | 515 | [10 empty] | 93.41 |  |  |  | 94.28 | [5 empty] | 93.12 |  |  | 100.00 |  |  |  | 5.25 |  | 5.22 | [8 empty] | 0.50 |  |  |  |  | 0.87
2017 |  |  |  | 2608.49 |  |  | 5323 |  |  |  | 515 | [10 empty] | 57.91 |  |  |  | 58.07 | [5 empty] | 57.82 |  |  | 60.76 |  |  |  | 8.48 |  | 5.38 | [8 empty] | 36.56 |  |  |  |  | 0.16
2018 |  |  |  | 4206.18 |  |  | 8503 |  |  |  | 515 | [10 empty] | 93.41 |  |  |  | 94.09 | [5 empty] | 93.23 |  |  | 97.07 |  |  |  | 4.63 |  | 4.57 | [8 empty] | 1.34 |  |  |  |  | 0.68
2019 |  |  |  | 4299.59 |  |  | 8583 |  |  |  | 515 | [10 empty] | 95.53 |  |  |  | 95.91 | [5 empty] | 95.30 |  |  | 97.98 |  |  |  | 3.30 |  | 3.27 | [8 empty] | 0.82 |  |  |  |  | 0.38
2020 |  |  |  | 2244.06 |  |  | 4660 |  |  |  | 515 | [10 empty] | 49.73 |  |  |  | 50.11 | [5 empty] | 49.61 |  |  | 53.05 |  |  |  | 9.73 |  | 5.40 | [8 empty] | 44.49 |  |  |  |  | 0.38
2021 |  |  |  | 4183.00 |  |  | 8407 |  |  |  | 515 | [10 empty] | 92.81 |  |  |  | 93.35 | [5 empty] | 92.72 |  |  | 95.97 |  |  |  | 6.01 |  | 5.97 | [8 empty] | 0.68 |  |  |  |  | 0.54
2022 |  |  |  | 2986.96 |  |  | 6046 |  |  |  | 515 | [10 empty] | 66.29 |  |  |  | 66.78 | [5 empty] | 66.21 |  |  | 69.02 |  |  |  | 2.09 |  | 1.42 | [8 empty] | 31.79 |  |  |  |  | 0.50
2023 |  |  |  | 4165.01 |  |  | 8338 |  |  |  | 515 | [10 empty] | 92.26 |  |  |  | 92.87 | [5 empty] | 92.32 |  |  | 95.18 |  |  |  | 4.04 |  | 3.91 | [8 empty] | 3.23 |  |  |  |  | 0.61
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1971 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 292 | [14 empty] | 1557
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 130 | [14 empty] | 885
E. |  | Testing of plant systems or components | [35 empty] | 5 |  |  |  | 5
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 52
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
P. |  | Fire | [39 empty] | 32
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 67
Z. |  | Other | [39 empty] | 10
Subtotal | [22 empty] | 130 |  |  |  | 292 | [10 empty] | 890 |  |  |  | 1656 | [11 empty] | 70
Total | [22 empty] | 422 | [14 empty] | 2616
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1971 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 806
12. |  |  | Reactor I&C Systems | [34 empty] | 73
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 57
14. |  |  | Safety Systems | [34 empty] | 55
15. |  |  | Reactor Cooling Systems | [34 empty] | 130
16. |  |  | Steam generation systems | [34 empty] | 56
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 71
31. |  |  | Turbine and auxiliaries | [19 empty] | 292 | [14 empty] | 118
32. |  |  | Feedwater and Main Steam System | [34 empty] | 47
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 47
42. |  |  | Electrical Power Supply Systems | [34 empty] | 108
Total | [22 empty] | 292 | [14 empty] | 1586
Highlights (2023)
Forced Outage due to governor valve oscillations. Manual turbine trip.

## PICKERING-4
2023 Operating Experience
CA-7 | [8 empty] | PICKERING-4 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500A | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-05-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-05-21
Gross electrical power | [12 empty] | : |  |  | 542 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-06-17
Reference unit power (net) | [12 empty] | : |  |  | 515 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 50 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 9080 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 26.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 6 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3284.29 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.93 %
Energy Availability Factor (EAF) | [18 empty] | : | 72.89 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.24 %
Unit Capability Factor (UCF) | [18 empty] | : | 73.46 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.3 %
Load Factor (LF) | [18 empty] | : | 72.8 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.57 %
Operating Factor (OF) | [18 empty] | : | 75.84 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2116 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 372.93 | 344.02 |  |  |  | 295.09 |  | 0.00 | [8 empty] | 0.00 |  |  | 97.73 | [6 empty] | 362.91 |  | 357.32 |  |  |  | 336.60 |  |  | 377.76 |  |  | 356.88 | [9 empty] | 383.05 |  |  | 3284.29
EAF [%] |  |  |  |  | 97.34 | 99.60 |  |  |  | 76.91 |  | 0.00 | [8 empty] | 0.00 |  |  | 26.36 | [6 empty] | 94.71 |  | 93.38 |  |  |  | 90.78 |  |  | 99.20 |  |  | 96.41 | [9 empty] | 100.00 |  |  | 72.89
UCF [%] |  |  |  |  | 97.34 | 99.60 |  |  |  | 76.91 |  | 0.00 | [8 empty] | 0.00 |  |  | 26.51 | [6 empty] | 96.65 |  | 95.80 |  |  |  | 92.38 |  |  | 99.88 |  |  | 96.41 | [9 empty] | 100.00 |  |  | 73.46
LF [%] |  |  |  |  | 97.33 | 99.40 |  |  |  | 77.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 26.36 | [6 empty] | 94.71 |  | 93.26 |  |  |  | 90.78 |  |  | 98.59 |  |  | 96.25 | [9 empty] | 99.97 |  |  | 72.80
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 80.24 |  | 0.00 | [8 empty] | 0.00 |  |  | 29.86 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 75.84
FLR [%] |  |  |  |  | 0.17 | 0.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.13 | [6 empty] | 3.23 |  | 4.20 |  |  |  | 0.00 |  |  | 0.12 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.93
UCL [%] |  |  |  |  | 0.17 | 0.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 6.78 | [6 empty] | 3.22 |  | 4.20 |  |  |  | 0.00 |  |  | 0.12 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.24
PUF [%] |  |  |  |  | 2.49 | 0.00 |  |  |  | 23.09 |  | 100.00 | [8 empty] | 100.00 |  |  | 66.71 | [6 empty] | 0.13 |  | 0.00 |  |  |  | 7.62 |  |  | 0.00 |  |  | 3.59 | [9 empty] | 0.00 |  |  | 25.30
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.16 | [6 empty] | 1.94 |  | 2.41 |  |  |  | 1.61 |  |  | 0.68 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.57
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 139083.77 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 16.67 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 68.71 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 15.06 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 69.13 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.8 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 68.58 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.42 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 71.7 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 2226.60 |  |  | 4402 |  |  |  | 514 | [10 empty] | 90.59 |  |  |  | 90.59 | [5 empty] | 90.40 |  |  | 91.75 |  |  |  | 6.12 |  | 5.91 | [8 empty] | 3.50 |  |  |  |  | 0.00
1974 |  |  |  | 4221.00 |  |  | 8356 |  |  |  | 514 | [10 empty] | 94.00 |  |  |  | 94.00 | [5 empty] | 94.00 |  |  | 95.65 |  |  |  | 5.22 |  | 5.18 | [8 empty] | 0.82 |  |  |  |  | 0.00
1975 |  |  |  | 1094.20 |  |  | 2201 |  |  |  | 513 | [10 empty] | 24.24 |  |  |  | 24.24 | [5 empty] | 24.42 |  |  | 25.19 |  |  |  | 73.53 |  | 67.34 | [8 empty] | 8.42 |  |  |  |  | 0.00
1976 |  |  |  | 3089.00 |  |  | 6063 |  |  |  | 514 | [10 empty] | 68.23 |  |  |  | 68.23 | [5 empty] | 68.60 |  |  | 69.21 |  |  |  | 31.44 |  | 31.29 | [8 empty] | 0.49 |  |  |  |  | 0.00
1977 |  |  |  | 4107.20 |  |  | 7975 |  |  |  | 514 | [10 empty] | 90.30 |  |  |  | 90.30 | [5 empty] | 91.47 |  |  | 91.29 |  |  |  | 4.38 |  | 4.13 | [8 empty] | 5.57 |  |  |  |  | 0.00
1978 |  |  |  | 4033.90 |  |  | 7876 |  |  |  | 515 | [10 empty] | 89.70 |  |  |  | 89.70 | [5 empty] | 89.66 |  |  | 90.16 |  |  |  | 3.07 |  | 2.84 | [8 empty] | 7.46 |  |  |  |  | 0.00
1979 |  |  |  | 4102.20 |  |  | 8059 |  |  |  | 515 | [10 empty] | 91.00 |  |  |  | 91.00 | [5 empty] | 89.94 |  |  | 91.00 |  |  |  | 4.67 |  | 4.45 | [8 empty] | 4.55 |  |  |  |  | 0.00
1980 |  |  |  | 3700.50 |  |  | 7321 |  |  |  | 515 | [10 empty] | 81.76 |  |  |  | 81.76 | [5 empty] | 81.80 |  |  | 83.34 |  |  |  | 8.38 |  | 7.48 | [8 empty] | 10.77 |  |  |  |  | 0.00
1981 |  |  |  | 4142.00 |  |  | 8078 |  |  |  | 515 | [10 empty] | 91.65 |  |  |  | 91.65 | [5 empty] | 91.81 |  |  | 92.21 |  |  |  | 3.83 |  | 3.65 | [8 empty] | 4.70 |  |  |  |  | 0.00
1982 |  |  |  | 4137.90 |  |  | 8087 |  |  |  | 515 | [10 empty] | 91.76 |  |  |  | 91.76 | [5 empty] | 91.72 |  |  | 92.32 |  |  |  | 2.61 |  | 2.46 | [8 empty] | 5.78 |  |  |  |  | 0.00
1983 |  |  |  | 4170.20 |  |  | 8183 |  |  |  | 515 | [10 empty] | 92.32 |  |  |  | 92.32 | [5 empty] | 92.44 |  |  | 93.41 |  |  |  | 5.55 |  | 5.43 | [8 empty] | 2.25 |  |  |  |  | 0.00
1984 |  |  |  | 3733.30 |  |  | 7425 |  |  |  | 515 | [10 empty] | 82.75 |  |  |  | 82.75 | [5 empty] | 82.53 |  |  | 84.53 |  |  |  | 4.49 |  | 3.89 | [8 empty] | 13.36 |  |  |  |  | 0.00
1985 |  |  |  | 3438.86 |  |  | 6824 |  |  |  | 515 | [10 empty] | 77.47 |  |  |  | 83.50 | [5 empty] | 76.23 |  |  | 77.90 |  |  |  | 16.50 |  | 16.50 | [8 empty] | 0.00 |  |  |  |  | 6.03
1986 |  |  |  | 3687.37 |  |  | 7410 |  |  |  | 515 | [10 empty] | 83.16 |  |  |  | 83.16 | [5 empty] | 81.73 |  |  | 84.59 |  |  |  | 7.06 |  | 6.32 | [8 empty] | 10.52 |  |  |  |  | 0.00
1987 |  |  |  | 3770.41 |  |  | 7495 |  |  |  | 515 | [10 empty] | 83.96 |  |  |  | 84.33 | [5 empty] | 83.58 |  |  | 85.56 |  |  |  | 2.74 |  | 2.37 | [8 empty] | 13.29 |  |  |  |  | 0.37
1988 |  |  |  | 3166.17 |  |  | 6525 |  |  |  | 515 | [10 empty] | 70.11 |  |  |  | 70.11 | [5 empty] | 69.99 |  |  | 74.28 |  |  |  | 17.91 |  | 15.29 | [8 empty] | 14.60 |  |  |  |  | 0.00
1989 |  |  |  | 2255.49 |  |  | 5468 |  |  |  | 515 | [10 empty] | 50.00 |  |  |  | 50.00 | [5 empty] | 50.00 |  |  | 62.42 |  |  |  | 34.52 |  | 26.35 | [8 empty] | 23.65 |  |  |  |  | 0.00
1990 |  |  |  | 1070.83 |  |  | 2851 |  |  |  | 515 | [10 empty] | 23.74 |  |  |  | 23.74 | [5 empty] | 23.74 |  |  | 32.55 |  |  |  | 43.49 |  | 18.27 | [8 empty] | 58.00 |  |  |  |  | 0.00
1991 |  |  |  | 2130.76 |  |  | 5185 |  |  |  | 515 | [10 empty] | 47.34 |  |  |  | 47.34 | [5 empty] | 47.23 |  |  | 59.19 |  |  |  | 21.40 |  | 12.89 | [8 empty] | 39.77 |  |  |  |  | 0.00
1992 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1993 |  |  |  | 3309.63 |  |  | 6711 |  |  |  | 515 | [10 empty] | 73.76 |  |  |  | 74.21 | [5 empty] | 73.36 |  |  | 76.61 |  |  |  | 7.77 |  | 6.25 | [8 empty] | 19.55 |  |  |  |  | 0.45
1994 |  |  |  | 4009.64 |  |  | 7915 |  |  |  | 515 | [10 empty] | 89.51 |  |  |  | 89.71 | [5 empty] | 88.88 |  |  | 90.35 |  |  |  | 10.20 |  | 10.19 | [8 empty] | 0.09 |  |  |  |  | 0.21
1995 |  |  |  | 2806.96 |  |  | 5684 |  |  |  | 515 | [10 empty] | 63.33 |  |  |  | 63.84 | [5 empty] | 62.22 |  |  | 64.89 |  |  |  | 36.16 |  | 36.16 | [8 empty] | 0.00 |  |  |  |  | 0.50
1996 |  |  |  | 1134.91 |  |  | 2230 |  |  |  | 515 | [10 empty] | 25.13 |  |  |  | 25.13 | [5 empty] | 25.09 |  |  | 25.39 |  |  |  | 72.71 |  | 66.95 | [8 empty] | 7.92 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 515 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1998 |  |  |  | Data not provided
1999 |  |  |  | Data not available - Suspended Operation
2000 |  |  |  | "
2001 |  |  |  | "
2002 |  |  |  | "
2003 |  |  |  | 844.81 |  |  | 1880 |  |  |  | 515 | [10 empty] | 72.27 |  |  |  | 72.27 | [5 empty] | 72.27 |  |  | 82.70 |  |  |  | 27.73 |  | 27.73 | [8 empty] | 0.00 |  |  |  |  | 0.00
2004 |  |  |  | 3266.76 |  |  | 6739 |  |  |  | 515 | [10 empty] | 72.10 |  |  |  | 75.58 | [5 empty] | 72.21 |  |  | 76.72 |  |  |  | 19.76 |  | 18.61 | [8 empty] | 5.81 |  |  |  |  | 3.48
2005 |  |  |  | 2996.45 |  |  | 5900 |  |  |  | 515 | [10 empty] | 66.40 |  |  |  | 66.52 | [5 empty] | 66.42 |  |  | 67.35 |  |  |  | 33.48 |  | 33.48 | [8 empty] | 0.00 |  |  |  |  | 0.13
2006 |  |  |  | 2976.54 |  |  | 6149 |  |  |  | 515 | [10 empty] | 65.96 |  |  |  | 66.30 | [5 empty] | 65.98 |  |  | 70.19 |  |  |  | 15.05 |  | 17.26 | [8 empty] | 16.44 |  |  |  |  | 0.34
2007 |  |  |  | 1959.14 |  |  | 4086 |  |  |  | 515 | [10 empty] | 43.44 |  |  |  | 43.44 | [5 empty] | 43.43 |  |  | 46.64 |  |  |  | 49.23 |  | 55.59 | [8 empty] | 0.96 |  |  |  |  | 0.00
2008 |  |  |  | 3656.45 |  |  | 7765 |  |  |  | 515 | [10 empty] | 80.83 |  |  |  | 80.91 | [5 empty] | 80.83 |  |  | 88.40 |  |  |  | 19.04 |  | 19.03 | [8 empty] | 0.07 |  |  |  |  | 0.08
2009 |  |  |  | 1620.17 |  |  | 3845 |  |  |  | 515 | [10 empty] | 35.91 |  |  |  | 36.15 | [5 empty] | 35.91 |  |  | 43.89 |  |  |  | 48.47 |  | 42.90 | [8 empty] | 20.95 |  |  |  |  | 0.24
2010 |  |  |  | 3203.51 |  |  | 6583 |  |  |  | 515 | [10 empty] | 71.13 |  |  |  | 71.37 | [5 empty] | 71.01 |  |  | 75.15 |  |  |  | 17.89 |  | 15.55 | [8 empty] | 13.08 |  |  |  |  | 0.24
2011 |  |  |  | 2401.12 |  |  | 4919 |  |  |  | 515 | [10 empty] | 53.28 |  |  |  | 53.66 | [5 empty] | 53.22 |  |  | 56.15 |  |  |  | 29.34 |  | 24.15 | [8 empty] | 22.18 |  |  |  |  | 0.38
2012 |  |  |  | 3310.83 |  |  | 6592 |  |  |  | 515 | [10 empty] | 73.42 |  |  |  | 73.73 | [5 empty] | 73.19 |  |  | 75.05 |  |  |  | 20.62 |  | 21.17 | [8 empty] | 5.10 |  |  |  |  | 0.31
2013 |  |  |  | 3884.54 |  |  | 7798 |  |  |  | 515 | [10 empty] | 86.29 |  |  |  | 86.60 | [5 empty] | 86.10 |  |  | 89.02 |  |  |  | 7.00 |  | 7.76 | [8 empty] | 5.64 |  |  |  |  | 0.31
2014 |  |  |  | 2853.53 |  |  | 5772 |  |  |  | 515 | [10 empty] | 63.30 |  |  |  | 63.49 | [5 empty] | 63.25 |  |  | 65.89 |  |  |  | 5.37 |  | 13.00 | [8 empty] | 23.51 |  |  |  |  | 0.19
2015 |  |  |  | 4266.31 |  |  | 8604 |  |  |  | 515 | [10 empty] | 94.66 |  |  |  | 95.12 | [5 empty] | 94.57 |  |  | 98.22 |  |  |  | 4.87 |  | 4.87 | [8 empty] | 0.01 |  |  |  |  | 0.47
2016 |  |  |  | 2455.22 |  |  | 5169 |  |  |  | 515 | [10 empty] | 54.32 |  |  |  | 54.91 | [5 empty] | 54.27 |  |  | 58.85 |  |  |  | 10.39 |  | 15.07 | [8 empty] | 30.01 |  |  |  |  | 0.60
2017 |  |  |  | 3961.10 |  |  | 7978 |  |  |  | 515 | [10 empty] | 87.94 |  |  |  | 88.20 | [5 empty] | 87.80 |  |  | 91.07 |  |  |  | 3.91 |  | 3.59 | [8 empty] | 8.20 |  |  |  |  | 0.27
2018 |  |  |  | 2792.32 |  |  | 5901 |  |  |  | 515 | [10 empty] | 62.06 |  |  |  | 62.92 | [5 empty] | 61.89 |  |  | 67.36 |  |  |  | 8.24 |  | 5.65 | [8 empty] | 31.43 |  |  |  |  | 0.87
2019 |  |  |  | 4421.44 |  |  | 8760 |  |  |  | 515 | [10 empty] | 98.17 |  |  |  | 98.52 | [5 empty] | 98.01 |  |  | 100.00 |  |  |  | 1.21 |  | 1.20 | [8 empty] | 0.27 |  |  |  |  | 0.36
2020 |  |  |  | 2755.54 |  |  | 5555 |  |  |  | 515 | [10 empty] | 60.92 |  |  |  | 61.42 | [5 empty] | 60.91 |  |  | 63.24 |  |  |  | 1.20 |  | 4.29 | [8 empty] | 34.29 |  |  |  |  | 0.50
2021 |  |  |  | 4286.99 |  |  | 8684 |  |  |  | 515 | [10 empty] | 95.08 |  |  |  | 96.11 | [5 empty] | 95.03 |  |  | 99.13 |  |  |  | 2.91 |  | 2.88 | [8 empty] | 1.01 |  |  |  |  | 1.03
2022 |  |  |  | 3965.81 |  |  | 8020 |  |  |  | 515 | [10 empty] | 87.88 |  |  |  | 88.68 | [5 empty] | 87.91 |  |  | 91.55 |  |  |  | 1.90 |  | 1.71 | [8 empty] | 9.61 |  |  |  |  | 0.80
2023 |  |  |  | 3284.29 |  |  | 6644 |  |  |  | 515 | [10 empty] | 72.89 |  |  |  | 73.46 | [5 empty] | 72.80 |  |  | 75.84 |  |  |  | 0.93 |  | 1.24 | [8 empty] | 25.30 |  |  |  |  | 0.57
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1973 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 49 | [14 empty] | 1078
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 59
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2068 | [14 empty] | 1267
E. |  | Testing of plant systems or components | [35 empty] | 50
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 3
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 12
Z. |  | Other | [39 empty] | 6
Subtotal | [22 empty] | 2068 |  |  |  | 49 | [10 empty] | 1376 |  |  |  | 1087 | [11 empty] | 17
Total | [22 empty] | 2117 | [14 empty] | 2480
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1973 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 53
12. |  |  | Reactor I&C Systems | [34 empty] | 126
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 141
14. |  |  | Safety Systems | [34 empty] | 16
15. |  |  | Reactor Cooling Systems | [19 empty] | 49 | [14 empty] | 402
16. |  |  | Steam generation systems | [34 empty] | 37
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 104
32. |  |  | Feedwater and Main Steam System | [34 empty] | 26
34. |  |  | Miscellaneous Systems | [34 empty] | 15
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 42
42. |  |  | Electrical Power Supply Systems | [34 empty] | 99
Total | [22 empty] | 49 | [14 empty] | 1075

## PICKERING-5
2023 Operating Experience
CA-13 | [8 empty] | PICKERING-5 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-11-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-12-19
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-05-10
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 4208.08 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.53 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.47 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.5 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.68 %
Load Factor (LF) | [18 empty] | : | 93.1 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.35 %
Operating Factor (OF) | [18 empty] | : | 96.31 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 323 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 379.42 | 225.47 |  |  |  | 321.15 |  | 366.47 | [8 empty] | 377.39 |  |  | 340.74 | [6 empty] | 365.10 |  | 363.26 |  |  |  | 340.11 |  |  | 371.70 |  |  | 373.08 | [9 empty] | 384.19 |  |  | 4208.07
EAF [%] |  |  |  |  | 99.96 | 65.08 |  |  |  | 84.26 |  | 99.98 | [8 empty] | 98.81 |  |  | 91.72 | [6 empty] | 95.10 |  | 94.62 |  |  |  | 91.55 |  |  | 98.18 |  |  | 99.90 | [9 empty] | 99.99 |  |  | 93.47
UCF [%] |  |  |  |  | 99.96 | 65.08 |  |  |  | 84.26 |  | 99.98 | [8 empty] | 98.81 |  |  | 93.89 | [6 empty] | 98.33 |  | 97.88 |  |  |  | 97.38 |  |  | 99.86 |  |  | 99.90 | [9 empty] | 99.99 |  |  | 94.82
LF [%] |  |  |  |  | 98.83 | 65.02 |  |  |  | 83.65 |  | 98.64 | [8 empty] | 98.30 |  |  | 91.72 | [6 empty] | 95.10 |  | 94.62 |  |  |  | 91.55 |  |  | 96.82 |  |  | 100.42 | [9 empty] | 100.07 |  |  | 93.10
OF [%] |  |  |  |  | 100.00 | 65.18 |  |  |  | 88.04 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 96.31
FLR [%] |  |  |  |  | 0.04 | 0.05 |  |  |  | 0.10 |  | 0.02 | [8 empty] | 0.60 |  |  | 1.02 | [6 empty] | 0.93 |  | 1.40 |  |  |  | 2.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.53
UCL [%] |  |  |  |  | 0.04 | 0.03 |  |  |  | 0.08 |  | 0.02 | [8 empty] | 0.59 |  |  | 0.96 | [6 empty] | 0.92 |  | 1.39 |  |  |  | 1.99 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.50
PUF [%] |  |  |  |  | 0.00 | 34.89 |  |  |  | 15.65 |  | 0.00 | [8 empty] | 0.59 |  |  | 5.14 | [6 empty] | 0.74 |  | 0.73 |  |  |  | 0.63 |  |  | 0.14 |  |  | 0.10 | [9 empty] | 0.01 |  |  | 4.68
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.18 | [6 empty] | 3.23 |  | 3.26 |  |  |  | 5.84 |  |  | 1.68 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.35
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 137022.69 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 11.88 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.51 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 11.49 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.24 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.27 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.26 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.73 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.05 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 3202.40 |  |  | 6968 |  |  |  | 516 | [10 empty] | 90.29 |  |  |  | 90.29 | [5 empty] | 89.64 |  |  | 92.62 |  |  |  | 9.69 |  | 9.69 | [8 empty] | 0.02 |  |  |  |  | 0.00
1984 |  |  |  | 3517.52 |  |  | 7035 |  |  |  | 516 | [10 empty] | 77.75 |  |  |  | 77.75 | [5 empty] | 77.61 |  |  | 80.09 |  |  |  | 11.82 |  | 10.42 | [8 empty] | 11.83 |  |  |  |  | 0.00
1985 |  |  |  | 3366.50 |  |  | 6989 |  |  |  | 516 | [10 empty] | 77.74 |  |  |  | 83.10 | [5 empty] | 74.48 |  |  | 79.78 |  |  |  | 8.79 |  | 8.01 | [8 empty] | 8.89 |  |  |  |  | 5.36
1986 |  |  |  | 4068.64 |  |  | 8057 |  |  |  | 516 | [10 empty] | 90.70 |  |  |  | 91.16 | [5 empty] | 90.01 |  |  | 91.97 |  |  |  | 2.33 |  | 2.18 | [8 empty] | 6.66 |  |  |  |  | 0.46
1987 |  |  |  | 3600.10 |  |  | 7148 |  |  |  | 516 | [10 empty] | 79.56 |  |  |  | 80.33 | [5 empty] | 79.65 |  |  | 81.60 |  |  |  | 7.82 |  | 6.82 | [8 empty] | 12.85 |  |  |  |  | 0.77
1988 |  |  |  | 4397.16 |  |  | 8683 |  |  |  | 516 | [10 empty] | 97.52 |  |  |  | 97.55 | [5 empty] | 97.01 |  |  | 98.85 |  |  |  | 2.09 |  | 2.09 | [8 empty] | 0.37 |  |  |  |  | 0.03
1989 |  |  |  | 3400.76 |  |  | 6862 |  |  |  | 516 | [10 empty] | 75.42 |  |  |  | 75.67 | [5 empty] | 75.24 |  |  | 78.33 |  |  |  | 9.36 |  | 7.81 | [8 empty] | 16.52 |  |  |  |  | 0.25
1990 |  |  |  | 3885.00 |  |  | 7821 |  |  |  | 516 | [10 empty] | 86.36 |  |  |  | 86.44 | [5 empty] | 85.95 |  |  | 89.28 |  |  |  | 4.06 |  | 3.65 | [8 empty] | 9.90 |  |  |  |  | 0.08
1991 |  |  |  | 2887.06 |  |  | 5724 |  |  |  | 516 | [10 empty] | 64.36 |  |  |  | 64.56 | [5 empty] | 63.87 |  |  | 65.34 |  |  |  | 28.95 |  | 26.30 | [8 empty] | 9.14 |  |  |  |  | 0.20
1992 |  |  |  | 1345.25 |  |  | 2621 |  |  |  | 516 | [10 empty] | 29.76 |  |  |  | 29.76 | [5 empty] | 29.68 |  |  | 29.84 |  |  |  | 70.24 |  | 70.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
1993 |  |  |  | 3841.81 |  |  | 8307 |  |  |  | 516 | [10 empty] | 85.40 |  |  |  | 85.57 | [5 empty] | 84.99 |  |  | 94.83 |  |  |  | 14.25 |  | 14.22 | [8 empty] | 0.22 |  |  |  |  | 0.16
1994 |  |  |  | 3074.41 |  |  | 6196 |  |  |  | 516 | [10 empty] | 68.53 |  |  |  | 68.53 | [5 empty] | 68.02 |  |  | 70.73 |  |  |  | 9.15 |  | 6.90 | [8 empty] | 24.57 |  |  |  |  | 0.00
1995 |  |  |  | 3372.87 |  |  | 7008 |  |  |  | 516 | [10 empty] | 74.76 |  |  |  | 75.01 | [5 empty] | 74.62 |  |  | 80.00 |  |  |  | 13.00 |  | 11.21 | [8 empty] | 13.77 |  |  |  |  | 0.25
1996 |  |  |  | 3042.63 |  |  | 6429 |  |  |  | 516 | [10 empty] | 67.13 |  |  |  | 67.13 | [5 empty] | 67.13 |  |  | 73.19 |  |  |  | 32.87 |  | 32.87 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 3924.89 |  |  | 7908 |  |  |  | 516 | [10 empty] | 86.83 |  |  |  | 86.83 | [5 empty] | 86.83 |  |  | 90.27 |  |  |  | 13.17 |  | 13.17 | [8 empty] | 0.00 |  |  |  |  | 0.00
1998 |  |  |  | 3490.58 |  |  | 7296 |  |  |  | 516 | [10 empty] | 77.22 |  |  |  | 77.22 | [5 empty] | 77.22 |  |  | 83.29 |  |  |  | 8.70 |  | 7.36 | [8 empty] | 15.42 |  |  |  |  | 0.00
1999 |  |  |  | 2511.57 |  |  | 5302 |  |  |  | 516 | [10 empty] | 55.56 |  |  |  | 55.63 | [5 empty] | 55.56 |  |  | 60.53 |  |  |  | 20.16 |  | 14.04 | [8 empty] | 30.33 |  |  |  |  | 0.06
2000 |  |  |  | 2631.49 |  |  | 5457 |  |  |  | 516 | [10 empty] | 58.03 |  |  |  | 58.12 | [5 empty] | 58.06 |  |  | 62.12 |  |  |  | 32.58 |  | 28.09 | [8 empty] | 13.79 |  |  |  |  | 0.09
2001 |  |  |  | 2980.21 |  |  | 5986 |  |  |  | 516 | [10 empty] | 65.87 |  |  |  | 66.57 | [5 empty] | 65.93 |  |  | 68.33 |  |  |  | 6.95 |  | 4.97 | [8 empty] | 28.46 |  |  |  |  | 0.71
2002 |  |  |  | 2655.74 |  |  | 5565 |  |  |  | 516 | [10 empty] | 58.75 |  |  |  | 59.17 | [5 empty] | 58.75 |  |  | 63.53 |  |  |  | 11.96 |  | 8.03 | [8 empty] | 32.80 |  |  |  |  | 0.41
2003 |  |  |  | 3294.96 |  |  | 6566 |  |  |  | 516 | [10 empty] | 69.14 |  |  |  | 71.14 | [5 empty] | 72.89 |  |  | 74.95 |  |  |  | 28.29 |  | 28.07 | [8 empty] | 0.79 |  |  |  |  | 2.00
2004 |  |  |  | 4159.81 |  |  | 8264 |  |  |  | 516 | [10 empty] | 92.16 |  |  |  | 92.60 | [5 empty] | 91.78 |  |  | 94.08 |  |  |  | 4.45 |  | 4.31 | [8 empty] | 3.09 |  |  |  |  | 0.44
2005 |  |  |  | 2352.79 |  |  | 4818 |  |  |  | 516 | [10 empty] | 52.63 |  |  |  | 53.56 | [5 empty] | 52.05 |  |  | 55.00 |  |  |  | 9.80 |  | 8.30 | [8 empty] | 38.14 |  |  |  |  | 0.93
2006 |  |  |  | 4010.87 |  |  | 8113 |  |  |  | 516 | [10 empty] | 88.95 |  |  |  | 89.66 | [5 empty] | 88.73 |  |  | 92.61 |  |  |  | 10.34 |  | 10.34 | [8 empty] | 0.00 |  |  |  |  | 0.71
2007 |  |  |  | 2567.59 |  |  | 5637 |  |  |  | 516 | [10 empty] | 56.96 |  |  |  | 57.51 | [5 empty] | 56.80 |  |  | 64.35 |  |  |  | 21.85 |  | 22.84 | [8 empty] | 19.66 |  |  |  |  | 0.55
2008 |  |  |  | 4026.82 |  |  | 8357 |  |  |  | 516 | [10 empty] | 88.86 |  |  |  | 89.80 | [5 empty] | 88.84 |  |  | 95.14 |  |  |  | 7.64 |  | 8.89 | [8 empty] | 1.31 |  |  |  |  | 0.94
2009 |  |  |  | 3140.88 |  |  | 6631 |  |  |  | 516 | [10 empty] | 69.60 |  |  |  | 70.12 | [5 empty] | 69.49 |  |  | 75.70 |  |  |  | 7.81 |  | 13.53 | [8 empty] | 16.35 |  |  |  |  | 0.51
2010 |  |  |  | 3769.85 |  |  | 7645 |  |  |  | 516 | [10 empty] | 83.73 |  |  |  | 84.08 | [5 empty] | 83.40 |  |  | 87.27 |  |  |  | 4.21 |  | 3.69 | [8 empty] | 12.23 |  |  |  |  | 0.36
2011 |  |  |  | 1973.46 |  |  | 4258 |  |  |  | 516 | [10 empty] | 43.87 |  |  |  | 44.83 | [5 empty] | 43.66 |  |  | 48.61 |  |  |  | 10.88 |  | 22.97 | [8 empty] | 32.20 |  |  |  |  | 0.96
2012 |  |  |  | 4347.31 |  |  | 8725 |  |  |  | 516 | [10 empty] | 96.34 |  |  |  | 98.24 | [5 empty] | 95.91 |  |  | 99.33 |  |  |  | 1.69 |  | 1.69 | [8 empty] | 0.07 |  |  |  |  | 1.89
2013 |  |  |  | 2603.23 |  |  | 5371 |  |  |  | 516 | [10 empty] | 58.06 |  |  |  | 58.57 | [5 empty] | 57.59 |  |  | 61.31 |  |  |  | 1.98 |  | 15.82 | [8 empty] | 25.61 |  |  |  |  | 0.51
2014 |  |  |  | 4255.09 |  |  | 8760 |  |  |  | 516 | [10 empty] | 94.57 |  |  |  | 95.35 | [5 empty] | 94.14 |  |  | 100.00 |  |  |  | 4.50 |  | 4.49 | [8 empty] | 0.15 |  |  |  |  | 0.78
2015 |  |  |  | 2932.28 |  |  | 5865 |  |  |  | 516 | [10 empty] | 65.29 |  |  |  | 65.91 | [5 empty] | 64.87 |  |  | 66.95 |  |  |  | 0.62 |  | 4.44 | [8 empty] | 29.66 |  |  |  |  | 0.62
2016 |  |  |  | 4352.12 |  |  | 8784 |  |  |  | 516 | [10 empty] | 96.56 |  |  |  | 98.79 | [5 empty] | 96.02 |  |  | 100.00 |  |  |  | 1.11 |  | 1.10 | [8 empty] | 0.10 |  |  |  |  | 2.23
2017 |  |  |  | 2883.68 |  |  | 5841 |  |  |  | 516 | [10 empty] | 64.14 |  |  |  | 64.82 | [5 empty] | 63.80 |  |  | 66.68 |  |  |  | 1.92 |  | 1.27 | [8 empty] | 33.91 |  |  |  |  | 0.69
2018 |  |  |  | 4255.38 |  |  | 8615 |  |  |  | 516 | [10 empty] | 94.81 |  |  |  | 97.08 | [5 empty] | 94.14 |  |  | 98.34 |  |  |  | 2.88 |  | 2.87 | [8 empty] | 0.04 |  |  |  |  | 2.28
2019 |  |  |  | 2978.82 |  |  | 5934 |  |  |  | 516 | [10 empty] | 66.30 |  |  |  | 66.58 | [5 empty] | 65.90 |  |  | 67.74 |  |  |  | 1.67 |  | 1.13 | [8 empty] | 32.28 |  |  |  |  | 0.28
2020 |  |  |  | 4215.36 |  |  | 8520 |  |  |  | 516 | [10 empty] | 93.12 |  |  |  | 93.85 | [5 empty] | 93.00 |  |  | 96.99 |  |  |  | 5.72 |  | 5.70 | [8 empty] | 0.45 |  |  |  |  | 0.73
2021 |  |  |  | 3187.45 |  |  | 6438 |  |  |  | 516 | [10 empty] | 70.59 |  |  |  | 71.14 | [5 empty] | 70.52 |  |  | 73.49 |  |  |  | 21.62 |  | 19.62 | [8 empty] | 9.24 |  |  |  |  | 0.55
2022 |  |  |  | 2386.74 |  |  | 4852 |  |  |  | 516 | [10 empty] | 53.15 |  |  |  | 54.86 | [5 empty] | 52.80 |  |  | 55.39 |  |  |  | 0.88 |  | 0.78 | [8 empty] | 44.36 |  |  |  |  | 1.71
2023 |  |  |  | 4208.07 |  |  | 8437 |  |  |  | 516 | [10 empty] | 93.47 |  |  |  | 94.82 | [5 empty] | 93.10 |  |  | 96.31 |  |  |  | 0.53 |  | 0.50 | [8 empty] | 4.68 |  |  |  |  | 1.35
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1983 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 758
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 323 | [14 empty] | 1077
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 1
L. |  | Human factor related | [39 empty] | 47
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 7
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 14
Z. |  | Other | [35 empty] | 24 |  |  |  | 18
Subtotal | [22 empty] | 323 | [14 empty] | 1101 |  |  |  | 824 | [11 empty] | 21
Total | [22 empty] | 323 | [14 empty] | 1946
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1983 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 51
12. |  |  | Reactor I&C Systems | [34 empty] | 60
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 49
14. |  |  | Safety Systems | [34 empty] | 16
15. |  |  | Reactor Cooling Systems | [34 empty] | 104
16. |  |  | Steam generation systems | [34 empty] | 240
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 15
31. |  |  | Turbine and auxiliaries | [34 empty] | 41
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 101
42. |  |  | Electrical Power Supply Systems | [34 empty] | 76
Total | [37 empty] | 778

## PICKERING-6
2023 Operating Experience
CA-14 | [8 empty] | PICKERING-6 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-10-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-11-08
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-02-01
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2930.52 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.07 %
Energy Availability Factor (EAF) | [18 empty] | : | 65.12 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.05 %
Unit Capability Factor (UCF) | [18 empty] | : | 66.79 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 33.16 %
Load Factor (LF) | [18 empty] | : | 64.83 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.67 %
Operating Factor (OF) | [18 empty] | : | 66.51 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2934 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 146.36 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 221.51 |  |  | 365.81 | [6 empty] | 374.88 |  | 325.81 |  |  |  | 360.52 |  |  | 380.20 |  |  | 371.52 | [9 empty] | 383.90 |  |  | 2930.52
EAF [%] |  |  |  |  | 38.17 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 58.47 |  |  | 99.15 | [6 empty] | 97.65 |  | 85.31 |  |  |  | 98.28 |  |  | 99.37 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 65.12
UCF [%] |  |  |  |  | 38.17 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 58.47 |  |  | 99.99 | [6 empty] | 100.00 |  | 99.57 |  |  |  | 99.94 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 66.79
LF [%] |  |  |  |  | 38.12 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 57.70 |  |  | 98.46 | [6 empty] | 97.65 |  | 84.87 |  |  |  | 97.04 |  |  | 99.03 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 64.83
OF [%] |  |  |  |  | 39.11 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 62.10 |  |  | 100.00 | [6 empty] | 100.00 |  | 91.53 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 66.51
FLR [%] |  |  |  |  | 0.16 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.43 |  |  |  | 0.06 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.07
UCL [%] |  |  |  |  | 0.06 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.43 |  |  |  | 0.06 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
PUF [%] |  |  |  |  | 61.77 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 41.53 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 33.16
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.84 | [6 empty] | 2.35 |  | 14.26 |  |  |  | 1.66 |  |  | 0.63 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.67
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 142172.41 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 8.45 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.51 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.84 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.25 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.91 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.46 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.74 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 3816.08 |  |  | 7636 |  |  |  | 516 | [10 empty] | 86.09 |  |  |  | 86.09 | [5 empty] | 85.88 |  |  | 87.66 |  |  |  | 13.78 |  | 13.76 | [8 empty] | 0.16 |  |  |  |  | 0.00
1985 |  |  |  | 3289.09 |  |  | 6540 |  |  |  | 516 | [10 empty] | 73.11 |  |  |  | 79.48 | [5 empty] | 72.76 |  |  | 74.66 |  |  |  | 6.72 |  | 5.73 | [8 empty] | 14.80 |  |  |  |  | 6.37
1986 |  |  |  | 3395.22 |  |  | 6763 |  |  |  | 516 | [10 empty] | 75.84 |  |  |  | 76.11 | [5 empty] | 75.11 |  |  | 77.20 |  |  |  | 18.81 |  | 17.63 | [8 empty] | 6.25 |  |  |  |  | 0.28
1987 |  |  |  | 3949.93 |  |  | 7791 |  |  |  | 516 | [10 empty] | 86.60 |  |  |  | 88.53 | [5 empty] | 87.38 |  |  | 88.94 |  |  |  | 3.42 |  | 3.13 | [8 empty] | 8.33 |  |  |  |  | 1.94
1988 |  |  |  | 4496.76 |  |  | 8775 |  |  |  | 516 | [10 empty] | 98.42 |  |  |  | 98.49 | [5 empty] | 99.21 |  |  | 99.90 |  |  |  | 1.51 |  | 1.51 | [8 empty] | 0.00 |  |  |  |  | 0.07
1989 |  |  |  | 3950.21 |  |  | 7794 |  |  |  | 516 | [10 empty] | 87.57 |  |  |  | 87.89 | [5 empty] | 87.39 |  |  | 88.97 |  |  |  | 5.86 |  | 5.47 | [8 empty] | 6.64 |  |  |  |  | 0.31
1990 |  |  |  | 3473.45 |  |  | 7017 |  |  |  | 516 | [10 empty] | 76.92 |  |  |  | 77.74 | [5 empty] | 76.84 |  |  | 80.10 |  |  |  | 7.76 |  | 6.54 | [8 empty] | 15.72 |  |  |  |  | 0.82
1991 |  |  |  | 4469.68 |  |  | 8721 |  |  |  | 516 | [10 empty] | 98.97 |  |  |  | 99.21 | [5 empty] | 98.88 |  |  | 99.55 |  |  |  | 0.79 |  | 0.79 | [8 empty] | 0.00 |  |  |  |  | 0.24
1992 |  |  |  | 4050.47 |  |  | 7936 |  |  |  | 516 | [10 empty] | 89.29 |  |  |  | 89.32 | [5 empty] | 89.36 |  |  | 90.35 |  |  |  | 10.54 |  | 10.53 | [8 empty] | 0.15 |  |  |  |  | 0.03
1993 |  |  |  | 2689.19 |  |  | 5506 |  |  |  | 516 | [10 empty] | 59.88 |  |  |  | 60.38 | [5 empty] | 59.49 |  |  | 62.85 |  |  |  | 11.28 |  | 7.68 | [8 empty] | 31.94 |  |  |  |  | 0.50
1994 |  |  |  | 4043.00 |  |  | 8036 |  |  |  | 516 | [10 empty] | 90.14 |  |  |  | 90.15 | [5 empty] | 89.44 |  |  | 91.74 |  |  |  | 9.71 |  | 9.70 | [8 empty] | 0.15 |  |  |  |  | 0.01
1995 |  |  |  | 3493.34 |  |  | 6962 |  |  |  | 516 | [10 empty] | 77.19 |  |  |  | 77.51 | [5 empty] | 77.28 |  |  | 79.47 |  |  |  | 5.67 |  | 4.66 | [8 empty] | 17.83 |  |  |  |  | 0.32
1996 |  |  |  | 2591.65 |  |  | 5707 |  |  |  | 516 | [10 empty] | 57.18 |  |  |  | 57.18 | [5 empty] | 57.18 |  |  | 64.97 |  |  |  | 31.11 |  | 25.82 | [8 empty] | 17.00 |  |  |  |  | 0.00
1997 |  |  |  | 3386.16 |  |  | 6841 |  |  |  | 516 | [10 empty] | 74.91 |  |  |  | 74.91 | [5 empty] | 74.91 |  |  | 78.09 |  |  |  | 16.79 |  | 15.11 | [8 empty] | 9.98 |  |  |  |  | 0.00
1998 |  |  |  | 3130.15 |  |  | 6384 |  |  |  | 516 | [10 empty] | 69.25 |  |  |  | 69.73 | [5 empty] | 69.25 |  |  | 72.88 |  |  |  | 14.14 |  | 11.48 | [8 empty] | 18.78 |  |  |  |  | 0.49
1999 |  |  |  | 3353.71 |  |  | 6863 |  |  |  | 516 | [10 empty] | 74.18 |  |  |  | 74.42 | [5 empty] | 74.19 |  |  | 78.34 |  |  |  | 25.38 |  | 25.31 | [8 empty] | 0.27 |  |  |  |  | 0.24
2000 |  |  |  | 2738.74 |  |  | 6449 |  |  |  | 516 | [10 empty] | 60.46 |  |  |  | 60.60 | [5 empty] | 60.42 |  |  | 73.42 |  |  |  | 19.46 |  | 14.64 | [8 empty] | 24.76 |  |  |  |  | 0.14
2001 |  |  |  | 2618.08 |  |  | 5286 |  |  |  | 516 | [10 empty] | 57.68 |  |  |  | 57.68 | [5 empty] | 57.92 |  |  | 60.34 |  |  |  | 21.61 |  | 15.90 | [8 empty] | 26.42 |  |  |  |  | 0.00
2002 |  |  |  | 3982.31 |  |  | 7985 |  |  |  | 516 | [10 empty] | 88.29 |  |  |  | 88.90 | [5 empty] | 88.10 |  |  | 91.15 |  |  |  | 7.01 |  | 6.71 | [8 empty] | 4.39 |  |  |  |  | 0.61
2003 |  |  |  | 3267.37 |  |  | 6566 |  |  |  | 516 | [10 empty] | 72.46 |  |  |  | 74.27 | [5 empty] | 72.28 |  |  | 74.95 |  |  |  | 12.71 |  | 10.81 | [8 empty] | 14.92 |  |  |  |  | 1.81
2004 |  |  |  | 2780.80 |  |  | 5597 |  |  |  | 516 | [10 empty] | 61.51 |  |  |  | 61.68 | [5 empty] | 61.35 |  |  | 63.72 |  |  |  | 28.61 |  | 24.72 | [8 empty] | 13.60 |  |  |  |  | 0.17
2005 |  |  |  | 2850.13 |  |  | 5596 |  |  |  | 516 | [10 empty] | 63.14 |  |  |  | 64.25 | [5 empty] | 63.05 |  |  | 63.88 |  |  |  | 3.16 |  | 4.41 | [8 empty] | 31.34 |  |  |  |  | 1.12
2006 |  |  |  | 3899.46 |  |  | 7635 |  |  |  | 516 | [10 empty] | 86.05 |  |  |  | 86.14 | [5 empty] | 86.27 |  |  | 87.16 |  |  |  | 4.26 |  | 13.54 | [8 empty] | 0.32 |  |  |  |  | 0.10
2007 |  |  |  | 3216.52 |  |  | 6588 |  |  |  | 516 | [10 empty] | 70.75 |  |  |  | 71.26 | [5 empty] | 71.16 |  |  | 75.21 |  |  |  | 8.36 |  | 10.77 | [8 empty] | 17.97 |  |  |  |  | 0.51
2008 |  |  |  | 4323.78 |  |  | 8521 |  |  |  | 516 | [10 empty] | 95.64 |  |  |  | 95.79 | [5 empty] | 95.39 |  |  | 97.01 |  |  |  | 4.21 |  | 4.21 | [8 empty] | 0.00 |  |  |  |  | 0.15
2009 |  |  |  | 3493.23 |  |  | 7051 |  |  |  | 516 | [10 empty] | 77.60 |  |  |  | 77.97 | [5 empty] | 77.28 |  |  | 80.49 |  |  |  | 3.36 |  | 2.71 | [8 empty] | 19.32 |  |  |  |  | 0.36
2010 |  |  |  | 3865.26 |  |  | 7659 |  |  |  | 516 | [10 empty] | 85.83 |  |  |  | 86.01 | [5 empty] | 85.51 |  |  | 87.43 |  |  |  | 3.22 |  | 2.86 | [8 empty] | 11.12 |  |  |  |  | 0.19
2011 |  |  |  | 3195.82 |  |  | 6334 |  |  |  | 516 | [10 empty] | 70.96 |  |  |  | 71.33 | [5 empty] | 70.70 |  |  | 72.31 |  |  |  | 0.60 |  | 0.43 | [8 empty] | 28.24 |  |  |  |  | 0.38
2012 |  |  |  | 4333.57 |  |  | 8550 |  |  |  | 516 | [10 empty] | 95.50 |  |  |  | 97.08 | [5 empty] | 95.61 |  |  | 97.34 |  |  |  | 2.92 |  | 2.92 | [8 empty] | 0.00 |  |  |  |  | 1.58
2013 |  |  |  | 3027.43 |  |  | 6047 |  |  |  | 516 | [10 empty] | 67.19 |  |  |  | 67.42 | [5 empty] | 66.98 |  |  | 69.03 |  |  |  | 0.14 |  | 0.10 | [8 empty] | 32.49 |  |  |  |  | 0.23
2014 |  |  |  | 3979.30 |  |  | 8397 |  |  |  | 516 | [10 empty] | 87.91 |  |  |  | 88.18 | [5 empty] | 88.03 |  |  | 95.86 |  |  |  | 11.82 |  | 11.82 | [8 empty] | 0.00 |  |  |  |  | 0.27
2015 |  |  |  | 3037.96 |  |  | 6064 |  |  |  | 516 | [10 empty] | 67.32 |  |  |  | 67.86 | [5 empty] | 67.21 |  |  | 69.22 |  |  |  | 5.43 |  | 3.89 | [8 empty] | 28.25 |  |  |  |  | 0.54
2016 |  |  |  | 3995.28 |  |  | 8259 |  |  |  | 516 | [10 empty] | 88.20 |  |  |  | 91.33 | [5 empty] | 88.15 |  |  | 94.02 |  |  |  | 2.89 |  | 7.15 | [8 empty] | 1.52 |  |  |  |  | 3.13
2017 |  |  |  | 4434.18 |  |  | 8686 |  |  |  | 516 | [10 empty] | 98.31 |  |  |  | 98.57 | [5 empty] | 98.10 |  |  | 99.16 |  |  |  | 1.43 |  | 1.43 | [8 empty] | 0.00 |  |  |  |  | 0.27
2018 |  |  |  | 2652.58 |  |  | 5392 |  |  |  | 516 | [10 empty] | 58.68 |  |  |  | 61.18 | [5 empty] | 58.68 |  |  | 61.55 |  |  |  | 6.08 |  | 3.96 | [8 empty] | 34.87 |  |  |  |  | 2.49
2019 |  |  |  | 4461.28 |  |  | 8681 |  |  |  | 516 | [10 empty] | 98.28 |  |  |  | 98.40 | [5 empty] | 98.70 |  |  | 99.10 |  |  |  | 1.59 |  | 1.59 | [8 empty] | 0.01 |  |  |  |  | 0.12
2020 |  |  |  | 3027.01 |  |  | 5918 |  |  |  | 516 | [10 empty] | 66.72 |  |  |  | 67.10 | [5 empty] | 66.78 |  |  | 67.37 |  |  |  | 0.07 |  | 0.05 | [8 empty] | 32.85 |  |  |  |  | 0.39
2021 |  |  |  | 4206.84 |  |  | 8455 |  |  |  | 516 | [10 empty] | 92.99 |  |  |  | 93.52 | [5 empty] | 93.07 |  |  | 96.52 |  |  |  | 2.70 |  | 2.60 | [8 empty] | 3.88 |  |  |  |  | 0.53
2022 |  |  |  | 4022.03 |  |  | 7845 |  |  |  | 516 | [10 empty] | 88.91 |  |  |  | 90.17 | [5 empty] | 88.98 |  |  | 89.55 |  |  |  | 1.91 |  | 1.76 | [8 empty] | 8.07 |  |  |  |  | 1.26
2023 |  |  |  | 2930.52 |  |  | 5826 |  |  |  | 516 | [10 empty] | 65.12 |  |  |  | 66.79 | [5 empty] | 64.83 |  |  | 66.51 |  |  |  | 0.07 |  | 0.05 | [8 empty] | 33.16 |  |  |  |  | 1.67
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1984 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 483
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 75
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 2871 | [14 empty] | 1024
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 3
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 16
L. |  | Human factor related | [39 empty] | 33
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [31 empty] | 63 | [19 empty] | 12
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 15
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 2871 | [10 empty] | 63 |  |  |  | 1099 |  |  |  | 521 | [11 empty] | 43
Total | [22 empty] | 2934 | [14 empty] | 1663
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1984 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 52
12. |  |  | Reactor I&C Systems | [34 empty] | 43
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 27
14. |  |  | Safety Systems | [34 empty] | 35
15. |  |  | Reactor Cooling Systems | [34 empty] | 46
16. |  |  | Steam generation systems | [34 empty] | 91
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 12
31. |  |  | Turbine and auxiliaries | [34 empty] | 49
32. |  |  | Feedwater and Main Steam System | [34 empty] | 32
33. |  |  | Circulating Water System | [19 empty] | 63 | [14 empty] | 14
34. |  |  | Miscellaneous Systems | [34 empty] | 18
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 59
42. |  |  | Electrical Power Supply Systems | [34 empty] | 23
Total | [22 empty] | 63 | [14 empty] | 506
Highlights (2023)
Unit 6 experienced an outage due to debris run in the screenhouse through a manual Turbine trip.

## PICKERING-7
2023 Operating Experience
CA-15 | [8 empty] | PICKERING-7 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-03-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-11-17
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-01-01
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2/PuO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 4324.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.3 %
Energy Availability Factor (EAF) | [18 empty] | : | 94.4 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.3 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.7 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 95.67 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.3 %
Operating Factor (OF) | [18 empty] | : | 95.21 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 420 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 341.22 | 354.64 |  |  |  | 392.05 |  | 378.07 | [8 empty] | 300.05 |  |  | 373.60 | [6 empty] | 383.83 |  | 314.33 |  |  |  | 366.55 |  |  | 389.22 |  |  | 378.24 | [9 empty] | 352.46 |  |  | 4324.26
EAF [%] |  |  |  |  | 86.91 | 100.00 |  |  |  | 100.00 |  | 99.92 | [8 empty] | 76.72 |  |  | 100.00 | [6 empty] | 99.98 |  | 82.12 |  |  |  | 98.51 |  |  | 100.00 |  |  | 99.97 | [9 empty] | 89.92 |  |  | 94.40
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.92 | [8 empty] | 76.72 |  |  | 100.00 | [6 empty] | 99.98 |  | 82.84 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.97 | [9 empty] | 89.92 |  |  | 95.70
LF [%] |  |  |  |  | 88.88 | 102.28 |  |  |  | 102.12 |  | 101.76 | [8 empty] | 78.16 |  |  | 100.56 | [6 empty] | 99.98 |  | 81.88 |  |  |  | 98.66 |  |  | 101.38 |  |  | 101.81 | [9 empty] | 91.81 |  |  | 95.67
OF [%] |  |  |  |  | 88.71 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 79.30 |  |  | 100.00 | [6 empty] | 100.00 |  | 84.54 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 90.99 |  |  | 95.21
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.08 | [8 empty] | 23.28 |  |  | 0.00 | [6 empty] | 0.02 |  | 17.16 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.03 | [9 empty] | 10.08 |  |  | 4.30
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.08 | [8 empty] | 23.28 |  |  | 0.00 | [6 empty] | 0.02 |  | 17.16 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.03 | [9 empty] | 10.08 |  |  | 4.30
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 13.09 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.72 |  |  |  | 1.49 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.30
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 138955.43 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.78 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.67 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 9.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.28 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.32 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.56 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.61 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.29 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4093.95 |  |  | 8277 |  |  |  | 516 | [10 empty] | 92.65 |  |  |  | 99.03 | [5 empty] | 90.57 |  |  | 94.49 |  |  |  | 0.86 |  | 0.86 | [8 empty] | 0.11 |  |  |  |  | 6.39
1986 |  |  |  | 3373.30 |  |  | 7002 |  |  |  | 516 | [10 empty] | 75.20 |  |  |  | 75.45 | [5 empty] | 74.63 |  |  | 79.93 |  |  |  | 8.27 |  | 6.80 | [8 empty] | 17.75 |  |  |  |  | 0.25
1987 |  |  |  | 4339.89 |  |  | 8642 |  |  |  | 516 | [10 empty] | 95.99 |  |  |  | 97.44 | [5 empty] | 96.01 |  |  | 98.65 |  |  |  | 2.50 |  | 2.50 | [8 empty] | 0.05 |  |  |  |  | 1.45
1988 |  |  |  | 4340.42 |  |  | 8519 |  |  |  | 516 | [10 empty] | 95.39 |  |  |  | 95.94 | [5 empty] | 95.76 |  |  | 96.98 |  |  |  | 4.06 |  | 4.06 | [8 empty] | 0.00 |  |  |  |  | 0.55
1989 |  |  |  | 3408.69 |  |  | 6939 |  |  |  | 516 | [10 empty] | 75.37 |  |  |  | 77.13 | [5 empty] | 75.41 |  |  | 79.21 |  |  |  | 10.45 |  | 9.00 | [8 empty] | 13.87 |  |  |  |  | 1.76
1990 |  |  |  | 3500.80 |  |  | 7420 |  |  |  | 516 | [10 empty] | 77.73 |  |  |  | 78.35 | [5 empty] | 77.45 |  |  | 84.70 |  |  |  | 13.66 |  | 12.39 | [8 empty] | 9.25 |  |  |  |  | 0.62
1991 |  |  |  | 4258.77 |  |  | 8436 |  |  |  | 516 | [10 empty] | 94.52 |  |  |  | 94.93 | [5 empty] | 94.22 |  |  | 96.30 |  |  |  | 4.76 |  | 4.74 | [8 empty] | 0.33 |  |  |  |  | 0.42
1992 |  |  |  | 3727.45 |  |  | 7349 |  |  |  | 516 | [10 empty] | 82.40 |  |  |  | 82.41 | [5 empty] | 82.24 |  |  | 83.66 |  |  |  | 2.52 |  | 2.13 | [8 empty] | 15.46 |  |  |  |  | 0.01
1993 |  |  |  | 4415.95 |  |  | 8760 |  |  |  | 516 | [10 empty] | 99.01 |  |  |  | 99.88 | [5 empty] | 97.69 |  |  | 100.00 |  |  |  | 0.12 |  | 0.12 | [8 empty] | 0.00 |  |  |  |  | 0.87
1994 |  |  |  | 3709.91 |  |  | 7386 |  |  |  | 516 | [10 empty] | 83.40 |  |  |  | 83.40 | [5 empty] | 82.07 |  |  | 84.32 |  |  |  | 1.67 |  | 1.41 | [8 empty] | 15.18 |  |  |  |  | 0.00
1995 |  |  |  | 4056.79 |  |  | 8140 |  |  |  | 516 | [10 empty] | 90.05 |  |  |  | 90.43 | [5 empty] | 89.75 |  |  | 92.92 |  |  |  | 9.57 |  | 9.57 | [8 empty] | 0.00 |  |  |  |  | 0.38
1996 |  |  |  | 2050.69 |  |  | 4416 |  |  |  | 516 | [10 empty] | 45.37 |  |  |  | 45.37 | [5 empty] | 45.24 |  |  | 50.27 |  |  |  | 54.63 |  | 54.63 | [8 empty] | 0.00 |  |  |  |  | 0.00
1997 |  |  |  | 2936.16 |  |  | 6208 |  |  |  | 516 | [10 empty] | 64.96 |  |  |  | 64.96 | [5 empty] | 64.96 |  |  | 70.87 |  |  |  | 20.17 |  | 16.41 | [8 empty] | 18.63 |  |  |  |  | 0.00
1998 |  |  |  | 3084.73 |  |  | 6495 |  |  |  | 516 | [10 empty] | 68.24 |  |  |  | 68.87 | [5 empty] | 68.24 |  |  | 74.14 |  |  |  | 20.36 |  | 17.61 | [8 empty] | 13.52 |  |  |  |  | 0.63
1999 |  |  |  | 4433.82 |  |  | 8751 |  |  |  | 516 | [10 empty] | 98.04 |  |  |  | 98.82 | [5 empty] | 98.09 |  |  | 99.90 |  |  |  | 1.18 |  | 1.18 | [8 empty] | 0.00 |  |  |  |  | 0.78
2000 |  |  |  | 2099.00 |  |  | 4445 |  |  |  | 516 | [10 empty] | 46.29 |  |  |  | 46.37 | [5 empty] | 46.31 |  |  | 50.60 |  |  |  | 14.46 |  | 7.84 | [8 empty] | 45.79 |  |  |  |  | 0.08
2001 |  |  |  | 4020.78 |  |  | 7968 |  |  |  | 516 | [10 empty] | 88.71 |  |  |  | 89.03 | [5 empty] | 88.95 |  |  | 90.96 |  |  |  | 10.97 |  | 10.97 | [8 empty] | 0.00 |  |  |  |  | 0.32
2002 |  |  |  | 4246.89 |  |  | 8538 |  |  |  | 516 | [10 empty] | 93.85 |  |  |  | 94.45 | [5 empty] | 93.95 |  |  | 97.47 |  |  |  | 5.55 |  | 5.55 | [8 empty] | 0.00 |  |  |  |  | 0.59
2003 |  |  |  | 1790.66 |  |  | 3811 |  |  |  | 516 | [10 empty] | 39.66 |  |  |  | 39.81 | [5 empty] | 39.62 |  |  | 43.50 |  |  |  | 40.88 |  | 27.53 | [8 empty] | 32.67 |  |  |  |  | 0.15
2004 |  |  |  | 3116.06 |  |  | 6127 |  |  |  | 516 | [10 empty] | 68.86 |  |  |  | 68.93 | [5 empty] | 68.75 |  |  | 69.75 |  |  |  | 4.64 |  | 3.36 | [8 empty] | 27.72 |  |  |  |  | 0.07
2005 |  |  |  | 4390.76 |  |  | 8658 |  |  |  | 516 | [10 empty] | 97.44 |  |  |  | 97.79 | [5 empty] | 97.14 |  |  | 98.84 |  |  |  | 2.21 |  | 2.21 | [8 empty] | 0.00 |  |  |  |  | 0.34
2006 |  |  |  | 2652.57 |  |  | 5311 |  |  |  | 516 | [10 empty] | 59.06 |  |  |  | 59.11 | [5 empty] | 58.68 |  |  | 60.63 |  |  |  | 10.24 |  | 21.12 | [8 empty] | 19.77 |  |  |  |  | 0.05
2007 |  |  |  | 3667.91 |  |  | 7540 |  |  |  | 516 | [10 empty] | 81.69 |  |  |  | 82.04 | [5 empty] | 81.15 |  |  | 86.07 |  |  |  | 9.97 |  | 16.75 | [8 empty] | 1.21 |  |  |  |  | 0.35
2008 |  |  |  | 1530.27 |  |  | 3084 |  |  |  | 516 | [10 empty] | 33.98 |  |  |  | 33.99 | [5 empty] | 33.76 |  |  | 35.11 |  |  |  | 66.01 |  | 66.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
2009 |  |  |  | 4229.46 |  |  | 8492 |  |  |  | 516 | [10 empty] | 94.10 |  |  |  | 94.53 | [5 empty] | 93.57 |  |  | 96.94 |  |  |  | 5.47 |  | 5.47 | [8 empty] | 0.00 |  |  |  |  | 0.43
2010 |  |  |  | 2920.66 |  |  | 5895 |  |  |  | 516 | [10 empty] | 64.78 |  |  |  | 65.13 | [5 empty] | 64.61 |  |  | 67.29 |  |  |  | 1.64 |  | 1.69 | [8 empty] | 33.18 |  |  |  |  | 0.35
2011 |  |  |  | 4337.70 |  |  | 8673 |  |  |  | 516 | [10 empty] | 96.58 |  |  |  | 96.83 | [5 empty] | 95.96 |  |  | 99.01 |  |  |  | 3.17 |  | 3.17 | [8 empty] | 0.00 |  |  |  |  | 0.25
2012 |  |  |  | 2920.02 |  |  | 5965 |  |  |  | 516 | [10 empty] | 64.76 |  |  |  | 66.28 | [5 empty] | 64.42 |  |  | 67.91 |  |  |  | 6.84 |  | 4.87 | [8 empty] | 28.85 |  |  |  |  | 1.52
2013 |  |  |  | 4264.55 |  |  | 8760 |  |  |  | 516 | [10 empty] | 94.44 |  |  |  | 94.92 | [5 empty] | 94.35 |  |  | 100.00 |  |  |  | 5.04 |  | 5.04 | [8 empty] | 0.04 |  |  |  |  | 0.48
2014 |  |  |  | 2783.08 |  |  | 5489 |  |  |  | 516 | [10 empty] | 61.95 |  |  |  | 62.18 | [5 empty] | 61.57 |  |  | 62.66 |  |  |  | 6.72 |  | 6.53 | [8 empty] | 31.30 |  |  |  |  | 0.23
2015 |  |  |  | 4171.04 |  |  | 8336 |  |  |  | 516 | [10 empty] | 92.57 |  |  |  | 93.11 | [5 empty] | 92.28 |  |  | 95.16 |  |  |  | 3.43 |  | 5.65 | [8 empty] | 1.25 |  |  |  |  | 0.54
2016 |  |  |  | 2803.59 |  |  | 5574 |  |  |  | 516 | [10 empty] | 61.97 |  |  |  | 62.32 | [5 empty] | 61.85 |  |  | 63.46 |  |  |  | 6.62 |  | 5.50 | [8 empty] | 32.18 |  |  |  |  | 0.35
2017 |  |  |  | 3751.37 |  |  | 7512 |  |  |  | 516 | [10 empty] | 83.14 |  |  |  | 83.35 | [5 empty] | 82.99 |  |  | 85.75 |  |  |  | 13.44 |  | 16.11 | [8 empty] | 0.55 |  |  |  |  | 0.20
2018 |  |  |  | 4377.16 |  |  | 8687 |  |  |  | 516 | [10 empty] | 96.67 |  |  |  | 98.11 | [5 empty] | 96.84 |  |  | 99.17 |  |  |  | 1.89 |  | 1.89 | [8 empty] | 0.00 |  |  |  |  | 1.45
2019 |  |  |  | 3132.65 |  |  | 6131 |  |  |  | 516 | [10 empty] | 68.52 |  |  |  | 68.53 | [5 empty] | 69.30 |  |  | 69.99 |  |  |  | 1.03 |  | 0.71 | [8 empty] | 30.76 |  |  |  |  | 0.01
2020 |  |  |  | 4316.41 |  |  | 8321 |  |  |  | 516 | [10 empty] | 94.04 |  |  |  | 94.20 | [5 empty] | 95.23 |  |  | 94.73 |  |  |  | 0.35 |  | 0.33 | [8 empty] | 5.47 |  |  |  |  | 0.15
2021 |  |  |  | 2840.99 |  |  | 5532 |  |  |  | 516 | [10 empty] | 62.13 |  |  |  | 62.44 | [5 empty] | 62.85 |  |  | 63.15 |  |  |  | 0.14 |  | 0.09 | [8 empty] | 37.48 |  |  |  |  | 0.31
2022 |  |  |  | 4161.58 |  |  | 7970 |  |  |  | 516 | [10 empty] | 90.47 |  |  |  | 90.60 | [5 empty] | 92.07 |  |  | 90.98 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 9.13 |  |  |  |  | 0.13
2023 |  |  |  | 4324.26 |  |  | 8340 |  |  |  | 516 | [10 empty] | 94.40 |  |  |  | 95.70 | [5 empty] | 95.67 |  |  | 95.21 |  |  |  | 4.30 |  | 4.30 | [8 empty] | 0.00 |  |  |  |  | 1.30
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 337 | [14 empty] | 520
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 957
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 8
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 109
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [31 empty] | 84 | [19 empty] | 6
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 12
Z. |  | Other | [39 empty] | 30
Subtotal | [26 empty] | 337 | [6 empty] | 84 |  |  |  | 958 |  |  |  | 667 | [11 empty] | 20
Total | [22 empty] | 421 | [14 empty] | 1645
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 90
12. |  |  | Reactor I&C Systems | [34 empty] | 52
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 13
14. |  |  | Safety Systems | [34 empty] | 29
15. |  |  | Reactor Cooling Systems | [19 empty] | 67 | [14 empty] | 82
16. |  |  | Steam generation systems | [34 empty] | 52
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 21
31. |  |  | Turbine and auxiliaries | [34 empty] | 31
32. |  |  | Feedwater and Main Steam System | [34 empty] | 17
33. |  |  | Circulating Water System | [34 empty] | 12
34. |  |  | Miscellaneous Systems | [34 empty] | 42
41. |  |  | Main Generator Systems | [34 empty] | 62
42. |  |  | Electrical Power Supply Systems | [19 empty] | 270 | [14 empty] | 52
Total | [22 empty] | 337 | [14 empty] | 555
Highlights (2023)
Unit Outage due to an issue with line protection scheme on the 078 ring bus directed by the Independent Electricity System Operator (IESO)-manual turbine trip. 2 forced outages due to a gas protection relay trip on the Main Output Transformer-automatic turbine trip. One forced outage due to a gas protection relay trip on the Main Output Transformer-manual turbine trip.

## PICKERING-8
2023 Operating Experience
CA-16 | [8 empty] | PICKERING-8 | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OPG (Ontario Power Generation)
Owner | [7 empty] | : | OPG (Ontario Power Generation)
Reactor Supplier | [7 empty] | : | OH/AECL (ONTARIO HYDRO / ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI.P (NEI PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 500B | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-09-01
Thermal power | [12 empty] | : |  |  | 1744 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-01-21
Gross electrical power | [12 empty] | : |  |  | 540 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-02-28
Reference unit power (net) | [12 empty] | : |  |  | 516 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 293.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 12
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8330 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.8
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2630.89 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 7.12 %
Energy Availability Factor (EAF) | [18 empty] | : | 58.31 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.58 %
Unit Capability Factor (UCF) | [18 empty] | : | 59.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 35.6 %
Load Factor (LF) | [18 empty] | : | 58.2 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.5 %
Operating Factor (OF) | [18 empty] | : | 60.27 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3480 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 334.33 | 346.75 |  |  |  | 185.83 |  | 371.52 | [8 empty] | 380.62 |  |  | 346.19 | [6 empty] | 196.99 |  | 372.73 |  |  |  | 95.93 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2630.89
EAF [%] |  |  |  |  | 87.03 | 100.00 |  |  |  | 48.96 |  | 99.99 | [8 empty] | 99.27 |  |  | 93.66 | [6 empty] | 51.31 |  | 97.28 |  |  |  | 25.82 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 58.31
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 48.96 |  | 99.99 | [8 empty] | 99.27 |  |  | 94.52 | [6 empty] | 52.53 |  | 99.56 |  |  |  | 26.25 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 59.82
LF [%] |  |  |  |  | 87.09 | 100.00 |  |  |  | 48.41 |  | 100.00 | [8 empty] | 99.14 |  |  | 93.18 | [6 empty] | 51.31 |  | 97.09 |  |  |  | 25.82 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 58.20
OF [%] |  |  |  |  | 89.65 | 100.00 |  |  |  | 51.34 |  | 100.00 | [8 empty] | 100.00 |  |  | 94.86 | [6 empty] | 63.71 |  | 100.00 |  |  |  | 26.94 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 60.27
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 0.73 |  |  | 5.48 | [6 empty] | 47.47 |  | 0.44 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.12
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.73 |  |  | 5.48 | [6 empty] | 47.47 |  | 0.44 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.58
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 51.03 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 73.75 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 35.60
XUF [%] |  |  |  |  | 12.97 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.86 | [6 empty] | 1.22 |  | 2.28 |  |  |  | 0.43 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.50
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 128969.48 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 9.61 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.4 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.93 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.07 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.26 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.68 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.51 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 3792.31 |  |  | 8086 |  |  |  | 516 | [10 empty] | 96.32 |  |  |  | 96.67 | [5 empty] | 95.69 |  |  | 97.69 |  |  |  | 3.33 |  | 3.33 | [8 empty] | 0.00 |  |  |  |  | 0.35
1987 |  |  |  | 3759.36 |  |  | 7585 |  |  |  | 516 | [10 empty] | 83.31 |  |  |  | 84.70 | [5 empty] | 83.17 |  |  | 86.59 |  |  |  | 2.09 |  | 1.81 | [8 empty] | 13.49 |  |  |  |  | 1.38
1988 |  |  |  | 3710.38 |  |  | 7296 |  |  |  | 516 | [10 empty] | 82.25 |  |  |  | 82.50 | [5 empty] | 81.86 |  |  | 83.06 |  |  |  | 2.16 |  | 1.82 | [8 empty] | 15.68 |  |  |  |  | 0.25
1989 |  |  |  | 4295.19 |  |  | 8569 |  |  |  | 516 | [10 empty] | 95.37 |  |  |  | 96.61 | [5 empty] | 95.02 |  |  | 97.82 |  |  |  | 3.29 |  | 3.29 | [8 empty] | 0.10 |  |  |  |  | 1.24
1990 |  |  |  | 3014.65 |  |  | 6743 |  |  |  | 516 | [10 empty] | 66.63 |  |  |  | 66.72 | [5 empty] | 66.69 |  |  | 76.97 |  |  |  | 19.23 |  | 15.89 | [8 empty] | 17.39 |  |  |  |  | 0.09
1991 |  |  |  | 4484.97 |  |  | 8759 |  |  |  | 516 | [10 empty] | 98.89 |  |  |  | 99.52 | [5 empty] | 99.22 |  |  | 99.99 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.00 |  |  |  |  | 0.63
1992 |  |  |  | 4211.99 |  |  | 8280 |  |  |  | 516 | [10 empty] | 92.95 |  |  |  | 92.98 | [5 empty] | 92.93 |  |  | 94.26 |  |  |  | 6.81 |  | 6.79 | [8 empty] | 0.22 |  |  |  |  | 0.03
1993 |  |  |  | 3670.54 |  |  | 7233 |  |  |  | 516 | [10 empty] | 81.73 |  |  |  | 82.15 | [5 empty] | 81.20 |  |  | 82.57 |  |  |  | 2.50 |  | 2.11 | [8 empty] | 15.74 |  |  |  |  | 0.41
1994 |  |  |  | 4341.88 |  |  | 8579 |  |  |  | 516 | [10 empty] | 96.85 |  |  |  | 96.85 | [5 empty] | 96.06 |  |  | 97.93 |  |  |  | 3.14 |  | 3.14 | [8 empty] | 0.01 |  |  |  |  | 0.00
1995 |  |  |  | 4012.08 |  |  | 8066 |  |  |  | 516 | [10 empty] | 89.04 |  |  |  | 89.42 | [5 empty] | 88.76 |  |  | 92.08 |  |  |  | 10.58 |  | 10.58 | [8 empty] | 0.00 |  |  |  |  | 0.38
1996 |  |  |  | 1300.26 |  |  | 2597 |  |  |  | 516 | [10 empty] | 28.73 |  |  |  | 28.73 | [5 empty] | 28.69 |  |  | 29.57 |  |  |  | 68.79 |  | 63.34 | [8 empty] | 7.92 |  |  |  |  | 0.00
1997 |  |  |  | 360.81 |  |  | 995 |  |  |  | 516 | [10 empty] | 7.96 |  |  |  | 7.96 | [5 empty] | 7.96 |  |  | 11.33 |  |  |  | 44.06 |  | 6.27 | [8 empty] | 85.77 |  |  |  |  | 0.00
1998 |  |  |  | 3493.62 |  |  | 7009 |  |  |  | 516 | [10 empty] | 77.29 |  |  |  | 78.02 | [5 empty] | 77.29 |  |  | 80.01 |  |  |  | 10.55 |  | 9.20 | [8 empty] | 12.78 |  |  |  |  | 0.73
1999 |  |  |  | 3509.06 |  |  | 7077 |  |  |  | 516 | [10 empty] | 77.63 |  |  |  | 78.44 | [5 empty] | 77.63 |  |  | 80.79 |  |  |  | 2.49 |  | 2.00 | [8 empty] | 19.56 |  |  |  |  | 0.81
2000 |  |  |  | 2711.21 |  |  | 5508 |  |  |  | 516 | [10 empty] | 59.92 |  |  |  | 60.83 | [5 empty] | 59.82 |  |  | 62.70 |  |  |  | 16.52 |  | 12.04 | [8 empty] | 27.13 |  |  |  |  | 0.91
2001 |  |  |  | 3502.19 |  |  | 6999 |  |  |  | 516 | [10 empty] | 77.47 |  |  |  | 78.22 | [5 empty] | 77.48 |  |  | 79.90 |  |  |  | 8.46 |  | 7.23 | [8 empty] | 14.55 |  |  |  |  | 0.75
2002 |  |  |  | 3605.36 |  |  | 7244 |  |  |  | 516 | [10 empty] | 80.03 |  |  |  | 81.06 | [5 empty] | 79.76 |  |  | 82.69 |  |  |  | 9.27 |  | 8.28 | [8 empty] | 10.66 |  |  |  |  | 1.02
2003 |  |  |  | 3921.29 |  |  | 8026 |  |  |  | 516 | [10 empty] | 86.90 |  |  |  | 89.68 | [5 empty] | 86.75 |  |  | 91.62 |  |  |  | 10.32 |  | 10.32 | [8 empty] | 0.00 |  |  |  |  | 2.78
2004 |  |  |  | 2489.46 |  |  | 5182 |  |  |  | 516 | [10 empty] | 55.13 |  |  |  | 55.35 | [5 empty] | 54.92 |  |  | 58.99 |  |  |  | 23.42 |  | 16.93 | [8 empty] | 27.71 |  |  |  |  | 0.23
2005 |  |  |  | 4195.24 |  |  | 8431 |  |  |  | 516 | [10 empty] | 93.40 |  |  |  | 94.60 | [5 empty] | 92.81 |  |  | 96.24 |  |  |  | 5.40 |  | 5.40 | [8 empty] | 0.00 |  |  |  |  | 1.20
2006 |  |  |  | 2908.54 |  |  | 5853 |  |  |  | 516 | [10 empty] | 64.75 |  |  |  | 65.06 | [5 empty] | 64.35 |  |  | 66.82 |  |  |  | 3.38 |  | 11.22 | [8 empty] | 23.72 |  |  |  |  | 0.31
2007 |  |  |  | 3843.21 |  |  | 8015 |  |  |  | 516 | [10 empty] | 85.51 |  |  |  | 87.28 | [5 empty] | 85.02 |  |  | 91.50 |  |  |  | 12.72 |  | 12.72 | [8 empty] | 0.00 |  |  |  |  | 1.77
2008 |  |  |  | 2918.75 |  |  | 6116 |  |  |  | 516 | [10 empty] | 64.41 |  |  |  | 64.71 | [5 empty] | 64.40 |  |  | 69.63 |  |  |  | 18.42 |  | 18.21 | [8 empty] | 17.08 |  |  |  |  | 0.30
2009 |  |  |  | 4115.23 |  |  | 8520 |  |  |  | 516 | [10 empty] | 91.04 |  |  |  | 91.61 | [5 empty] | 91.04 |  |  | 97.26 |  |  |  | 8.39 |  | 8.39 | [8 empty] | 0.00 |  |  |  |  | 0.57
2010 |  |  |  | 3081.07 |  |  | 6427 |  |  |  | 516 | [10 empty] | 68.16 |  |  |  | 68.53 | [5 empty] | 68.16 |  |  | 73.37 |  |  |  | 9.60 |  | 9.19 | [8 empty] | 22.27 |  |  |  |  | 0.37
2011 |  |  |  | 4051.72 |  |  | 8345 |  |  |  | 516 | [10 empty] | 89.64 |  |  |  | 90.30 | [5 empty] | 89.64 |  |  | 95.26 |  |  |  | 9.61 |  | 9.60 | [8 empty] | 0.10 |  |  |  |  | 0.66
2012 |  |  |  | 2936.38 |  |  | 5967 |  |  |  | 516 | [10 empty] | 64.86 |  |  |  | 65.53 | [5 empty] | 64.78 |  |  | 67.93 |  |  |  | 6.71 |  | 7.15 | [8 empty] | 27.33 |  |  |  |  | 0.66
2013 |  |  |  | 3879.06 |  |  | 7979 |  |  |  | 516 | [10 empty] | 85.97 |  |  |  | 86.34 | [5 empty] | 85.82 |  |  | 91.08 |  |  |  | 13.57 |  | 13.55 | [8 empty] | 0.11 |  |  |  |  | 0.37
2014 |  |  |  | 2411.29 |  |  | 5223 |  |  |  | 516 | [10 empty] | 53.30 |  |  |  | 53.43 | [5 empty] | 53.35 |  |  | 59.62 |  |  |  | 26.12 |  | 22.62 | [8 empty] | 23.94 |  |  |  |  | 0.14
2015 |  |  |  | 4289.30 |  |  | 8440 |  |  |  | 516 | [10 empty] | 94.91 |  |  |  | 95.37 | [5 empty] | 94.89 |  |  | 96.35 |  |  |  | 0.76 |  | 0.73 | [8 empty] | 3.90 |  |  |  |  | 0.46
2016 |  |  |  | 2197.88 |  |  | 4367 |  |  |  | 516 | [10 empty] | 48.35 |  |  |  | 48.60 | [5 empty] | 48.49 |  |  | 49.72 |  |  |  | 0.61 |  | 11.62 | [8 empty] | 39.78 |  |  |  |  | 0.25
2017 |  |  |  | 3870.80 |  |  | 7787 |  |  |  | 516 | [10 empty] | 85.68 |  |  |  | 85.96 | [5 empty] | 85.63 |  |  | 88.89 |  |  |  | 2.90 |  | 2.57 | [8 empty] | 11.47 |  |  |  |  | 0.28
2018 |  |  |  | 2626.93 |  |  | 5427 |  |  |  | 516 | [10 empty] | 58.08 |  |  |  | 59.70 | [5 empty] | 58.12 |  |  | 61.95 |  |  |  | 13.69 |  | 9.47 | [8 empty] | 30.82 |  |  |  |  | 1.63
2019 |  |  |  | 4363.55 |  |  | 8571 |  |  |  | 516 | [10 empty] | 96.44 |  |  |  | 96.71 | [5 empty] | 96.54 |  |  | 97.84 |  |  |  | 1.03 |  | 1.01 | [8 empty] | 2.28 |  |  |  |  | 0.27
2020 |  |  |  | 4070.63 |  |  | 8022 |  |  |  | 516 | [10 empty] | 89.87 |  |  |  | 90.41 | [5 empty] | 89.81 |  |  | 91.33 |  |  |  | 0.65 |  | 0.59 | [8 empty] | 9.00 |  |  |  |  | 0.54
2021 |  |  |  | 2459.85 |  |  | 4932 |  |  |  | 516 | [10 empty] | 54.47 |  |  |  | 56.12 | [5 empty] | 54.42 |  |  | 56.30 |  |  |  | 1.38 |  | 0.78 | [8 empty] | 43.10 |  |  |  |  | 1.65
2022 |  |  |  | 3941.06 |  |  | 7789 |  |  |  | 516 | [10 empty] | 87.35 |  |  |  | 88.03 | [5 empty] | 87.19 |  |  | 88.92 |  |  |  | 4.31 |  | 3.97 | [8 empty] | 8.00 |  |  |  |  | 0.68
2023 |  |  |  | 2630.89 |  |  | 5280 |  |  |  | 516 | [10 empty] | 58.31 |  |  |  | 59.82 | [5 empty] | 58.20 |  |  | 60.27 |  |  |  | 7.12 |  | 4.58 | [8 empty] | 35.60 |  |  |  |  | 1.50
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1986 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 306 | [14 empty] | 444
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 70
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 3095 | [14 empty] | 1072
E. |  | Testing of plant systems or components | [35 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 279
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [31 empty] | 77 | [19 empty] | 13
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 3095 |  |  |  | 306 | [6 empty] | 77 |  |  |  | 1143 |  |  |  | 724 | [11 empty] | 17
Total | [22 empty] | 3478 | [14 empty] | 1884
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1986 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 31
12. |  |  | Reactor I&C Systems | [34 empty] | 33
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 34
15. |  |  | Reactor Cooling Systems | [34 empty] | 79
16. |  |  | Steam generation systems | [34 empty] | 28
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 89
31. |  |  | Turbine and auxiliaries | [19 empty] | 114 | [14 empty] | 48
32. |  |  | Feedwater and Main Steam System | [19 empty] | 192 | [14 empty] | 30
33. |  |  | Circulating Water System | [34 empty] | 24
34. |  |  | Miscellaneous Systems | [34 empty] | 12
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 15
42. |  |  | Electrical Power Supply Systems | [34 empty] | 27
Total | [22 empty] | 306 | [14 empty] | 454
Highlights (2023)
Unit Outage due to an issue with line protection scheme on the 078 ring bus directed by the Independent Electricity System Operator (IESO)-manual turbine trip. One forced outage due to condenser tube leak- manual turbine trip. the forced Outage due to boiler level transient-automatic reactor trip

## POINT LEPREAU
2023 Operating Experience
CA-17 | [8 empty] | POINT LEPREAU | [26 empty] | CANADA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NBEPC (NEW BRUNSWICK ELECTRIC POWER COMMISSION)
Owner | [7 empty] | : | NBEPC (NEW BRUNSWICK ELECTRIC POWER COMMISSION)
Reactor Supplier | [7 empty] | : | AECL (ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | NEI/PARS (NEI-PARSONS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-05-01
Thermal power | [12 empty] | : |  |  | 2180 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-09-11
Gross electrical power | [12 empty] | : |  |  | 705 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-02-01
Reference unit power (net) | [12 empty] | : |  |  | 660 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 11.55
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 1.3
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 8000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 6.28 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.64
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 59.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 4764.67 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.34 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.41 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 8.46 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.46 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.08 %
Load Factor (LF) | [18 empty] | : | 82.41 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.05 %
Operating Factor (OF) | [18 empty] | : | 84.09 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1394 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 207.80 | 443.52 |  |  |  | 491.04 |  | 229.02 | [8 empty] | 88.79 |  |  | 473.39 | [6 empty] | 489.82 |  | 488.03 |  |  |  | 472.28 |  |  | 488.26 |  |  | 401.69 | [9 empty] | 491.04 |  |  | 4764.67
EAF [%] |  |  |  |  | 42.32 | 100.00 |  |  |  | 100.00 |  | 48.19 | [8 empty] | 18.08 |  |  | 99.62 | [6 empty] | 99.75 |  | 99.39 |  |  |  | 99.39 |  |  | 99.43 |  |  | 84.53 | [9 empty] | 100.00 |  |  | 82.41
UCF [%] |  |  |  |  | 42.32 | 100.00 |  |  |  | 100.00 |  | 48.19 | [8 empty] | 18.08 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.39 |  |  |  | 99.39 |  |  | 99.43 |  |  | 84.53 | [9 empty] | 100.00 |  |  | 82.46
LF [%] |  |  |  |  | 42.32 | 100.00 |  |  |  | 100.00 |  | 48.19 | [8 empty] | 18.08 |  |  | 99.62 | [6 empty] | 99.75 |  | 99.39 |  |  |  | 99.39 |  |  | 99.43 |  |  | 84.53 | [9 empty] | 100.00 |  |  | 82.41
OF [%] |  |  |  |  | 55.91 | 100.00 |  |  |  | 100.00 |  | 48.19 | [8 empty] | 20.30 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 86.11 | [9 empty] | 100.00 |  |  | 84.09
FLR [%] |  |  |  |  | 51.02 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.34
UCL [%] |  |  |  |  | 44.09 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 55.51 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.46
PUF [%] |  |  |  |  | 13.60 | 0.00 |  |  |  | 0.00 |  | 51.81 | [8 empty] | 26.41 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.61 |  |  |  | 0.61 |  |  | 0.57 |  |  | 15.47 | [9 empty] | 0.00 |  |  | 9.08
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.38 | [6 empty] | 0.25 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 170346.71 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.19 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.37 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 73.08 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.88 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.8 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.71 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.51 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 4742.90 |  |  | 7875 |  |  |  | 640 | [10 empty] | 86.03 |  |  |  | 86.03 | [5 empty] | 85.85 |  |  | 89.37 |  |  |  | 8.10 |  | 7.58 | [8 empty] | 6.39 |  |  |  |  | 0.00
1984 |  |  |  | 5000.94 |  |  | 7927 |  |  |  | 635 | [10 empty] | 88.94 |  |  |  | 88.97 | [5 empty] | 89.66 |  |  | 90.24 |  |  |  | 3.03 |  | 2.78 | [8 empty] | 8.25 |  |  |  |  | 0.03
1985 |  |  |  | 5421.91 |  |  | 8547 |  |  |  | 635 | [10 empty] | 96.87 |  |  |  | 96.93 | [5 empty] | 97.47 |  |  | 97.57 |  |  |  | 1.25 |  | 1.23 | [8 empty] | 1.84 |  |  |  |  | 0.06
1986 |  |  |  | 5223.09 |  |  | 8257 |  |  |  | 635 | [10 empty] | 93.41 |  |  |  | 94.00 | [5 empty] | 93.90 |  |  | 94.26 |  |  |  | 0.90 |  | 0.85 | [8 empty] | 5.15 |  |  |  |  | 0.59
1987 |  |  |  | 5107.73 |  |  | 8110 |  |  |  | 635 | [10 empty] | 91.23 |  |  |  | 91.25 | [5 empty] | 91.82 |  |  | 92.58 |  |  |  | 3.32 |  | 3.14 | [8 empty] | 5.61 |  |  |  |  | 0.02
1988 |  |  |  | 5338.25 |  |  | 8383 |  |  |  | 635 | [10 empty] | 94.85 |  |  |  | 94.85 | [5 empty] | 95.70 |  |  | 95.43 |  |  |  | 0.38 |  | 0.36 | [8 empty] | 4.79 |  |  |  |  | 0.00
1989 |  |  |  | 5266.67 |  |  | 8271 |  |  |  | 635 | [10 empty] | 93.60 |  |  |  | 93.81 | [5 empty] | 94.68 |  |  | 94.42 |  |  |  | 0.89 |  | 0.84 | [8 empty] | 5.34 |  |  |  |  | 0.22
1990 |  |  |  | 5333.71 |  |  | 8384 |  |  |  | 635 | [10 empty] | 94.70 |  |  |  | 94.99 | [5 empty] | 95.89 |  |  | 95.71 |  |  |  | 2.92 |  | 2.86 | [8 empty] | 2.15 |  |  |  |  | 0.29
1991 |  |  |  | 5437.17 |  |  | 8500 |  |  |  | 635 | [10 empty] | 96.68 |  |  |  | 96.72 | [5 empty] | 97.75 |  |  | 97.03 |  |  |  | 0.55 |  | 0.54 | [8 empty] | 2.74 |  |  |  |  | 0.04
1992 |  |  |  | 4829.78 |  |  | 7748 |  |  |  | 635 | [10 empty] | 85.76 |  |  |  | 85.76 | [5 empty] | 86.59 |  |  | 88.21 |  |  |  | 3.99 |  | 3.57 | [8 empty] | 10.67 |  |  |  |  | 0.00
1993 |  |  |  | 5320.00 |  |  | 8391 |  |  |  | 635 | [10 empty] | 95.09 |  |  |  | 95.09 | [5 empty] | 95.64 |  |  | 95.79 |  |  |  | 1.42 |  | 1.37 | [8 empty] | 3.54 |  |  |  |  | 0.00
1994 |  |  |  | 5230.10 |  |  | 8270 |  |  |  | 635 | [10 empty] | 93.46 |  |  |  | 93.46 | [5 empty] | 94.02 |  |  | 94.41 |  |  |  | 0.34 |  | 0.32 | [8 empty] | 6.22 |  |  |  |  | 0.00
1995 |  |  |  | 1611.40 |  |  | 2615 |  |  |  | 635 | [10 empty] | 28.98 |  |  |  | 28.98 | [5 empty] | 28.97 |  |  | 29.85 |  |  |  | 43.54 |  | 22.34 | [8 empty] | 48.68 |  |  |  |  | 0.00
1996 |  |  |  | 4587.83 |  |  | 7363 |  |  |  | 635 | [10 empty] | 81.41 |  |  |  | 81.41 | [5 empty] | 82.25 |  |  | 83.82 |  |  |  | 13.97 |  | 13.22 | [8 empty] | 5.37 |  |  |  |  | 0.00
1997 |  |  |  | 3455.59 |  |  | 5564 |  |  |  | 635 | [10 empty] | 61.60 |  |  |  | 62.19 | [5 empty] | 62.12 |  |  | 63.52 |  |  |  | 24.86 |  | 20.57 | [8 empty] | 17.24 |  |  |  |  | 0.59
1998 |  |  |  | 3782.35 |  |  | 6111 |  |  |  | 635 | [10 empty] | 66.04 |  |  |  | 67.11 | [5 empty] | 68.00 |  |  | 69.76 |  |  |  | 20.20 |  | 16.99 | [8 empty] | 15.90 |  |  |  |  | 1.06
1999 |  |  |  | 4082.74 |  |  | 6797 |  |  |  | 635 | [10 empty] | 71.99 |  |  |  | 75.52 | [5 empty] | 73.40 |  |  | 77.59 |  |  |  | 11.47 |  | 9.78 | [8 empty] | 14.70 |  |  |  |  | 3.53
2000 |  |  |  | 3966.85 |  |  | 6792 |  |  |  | 635 | [10 empty] | 70.52 |  |  |  | 77.64 | [5 empty] | 71.12 |  |  | 77.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.36 |  |  |  |  | 7.12
2001 |  |  |  | 4451.33 |  |  | 7418 |  |  |  | 635 | [10 empty] | 79.08 |  |  |  | 84.61 | [5 empty] | 80.02 |  |  | 84.68 |  |  |  | 15.33 |  | 15.31 | [8 empty] | 0.08 |  |  |  |  | 5.53
2002 |  |  |  | 3760.64 |  |  | 6107 |  |  |  | 635 | [10 empty] | 67.59 |  |  |  | 71.59 | [5 empty] | 67.61 |  |  | 69.71 |  |  |  | 6.62 |  | 10.30 | [8 empty] | 18.12 |  |  |  |  | 4.00
2003 |  |  |  | 4739.52 |  |  | 7869 |  |  |  | 635 | [10 empty] | 84.39 |  |  |  | 89.77 | [5 empty] | 85.20 |  |  | 89.83 |  |  |  | 0.70 |  | 4.18 | [8 empty] | 6.05 |  |  |  |  | 5.38
2004 |  |  |  | 4299.74 |  |  | 7310 |  |  |  | 635 | [10 empty] | 82.58 |  |  |  | 83.32 | [5 empty] | 77.09 |  |  | 83.22 |  |  |  | 6.13 |  | 6.56 | [8 empty] | 10.12 |  |  |  |  | 0.74
2005 |  |  |  | 4372.64 |  |  | 7632 |  |  |  | 635 | [10 empty] | 86.79 |  |  |  | 86.79 | [5 empty] | 78.61 |  |  | 87.12 |  |  |  | 2.13 |  | 6.68 | [8 empty] | 6.53 |  |  |  |  | 0.00
2006 |  |  |  | 4361.99 |  |  | 7755 |  |  |  | 635 | [10 empty] | 88.74 |  |  |  | 88.74 | [5 empty] | 78.42 |  |  | 88.53 |  |  |  | 0.88 |  | 1.59 | [8 empty] | 9.67 |  |  |  |  | 0.00
2007 |  |  |  | 4121.82 |  |  | 7511 |  |  |  | 635 | [10 empty] | 85.95 |  |  |  | 85.95 | [5 empty] | 74.10 |  |  | 85.74 |  |  |  | 7.79 |  | 8.02 | [8 empty] | 6.04 |  |  |  |  | 0.00
2008 |  |  |  | 1150.56 |  |  | 2111 |  |  |  | 635 | [10 empty] | 24.03 |  |  |  | 24.03 | [5 empty] | 20.63 |  |  | 24.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 75.97 |  |  |  |  | 0.00
2009 |  |  |  | 0.00 |  |  | 0 |  |  |  | 635 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2010 |  |  |  | 0.00 |  |  | 0 |  |  |  | 635 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2011 |  |  |  | 0.00 |  |  | 0 |  |  |  | 635 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2012 |  |  |  | 411.48 |  |  | 966 |  |  |  | 660 | [10 empty] | 7.53 |  |  |  | 7.53 | [5 empty] | 7.30 |  |  | 11.00 |  |  |  | 39.71 |  | 4.96 | [8 empty] | 87.51 |  |  |  |  | 0.00
2013 |  |  |  | 4111.15 |  |  | 7879 |  |  |  | 660 | [10 empty] | 70.80 |  |  |  | 70.80 | [5 empty] | 71.12 |  |  | 89.95 |  |  |  | 25.07 |  | 24.92 | [8 empty] | 4.28 |  |  |  |  | 0.00
2014 |  |  |  | 4724.62 |  |  | 7229 |  |  |  | 660 | [10 empty] | 81.86 |  |  |  | 81.86 | [5 empty] | 81.72 |  |  | 82.52 |  |  |  | 1.50 |  | 6.29 | [8 empty] | 11.85 |  |  |  |  | 0.00
2015 |  |  |  | 4277.04 |  |  | 6993 |  |  |  | 660 | [10 empty] | 74.61 |  |  |  | 74.61 | [5 empty] | 73.98 |  |  | 79.83 |  |  |  | 20.21 |  | 18.89 | [8 empty] | 6.50 |  |  |  |  | 0.00
2016 |  |  |  | 4548.99 |  |  | 6989 |  |  |  | 660 | [10 empty] | 78.20 |  |  |  | 78.20 | [5 empty] | 78.47 |  |  | 79.57 |  |  |  | 2.65 |  | 10.10 | [8 empty] | 11.71 |  |  |  |  | 0.00
2017 |  |  |  | 5151.32 |  |  | 7928 |  |  |  | 660 | [10 empty] | 89.25 |  |  |  | 89.25 | [5 empty] | 89.10 |  |  | 90.50 |  |  |  | 2.44 |  | 3.65 | [8 empty] | 7.10 |  |  |  |  | 0.00
2018 |  |  |  | 4894.15 |  |  | 7469 |  |  |  | 660 | [10 empty] | 84.46 |  |  |  | 84.46 | [5 empty] | 84.65 |  |  | 85.26 |  |  |  | 0.53 |  | 5.32 | [8 empty] | 10.22 |  |  |  |  | 0.00
2019 |  |  |  | 5015.68 |  |  | 7663 |  |  |  | 660 | [10 empty] | 86.69 |  |  |  | 86.69 | [5 empty] | 86.75 |  |  | 87.48 |  |  |  | 4.50 |  | 4.08 | [8 empty] | 9.23 |  |  |  |  | 0.00
2020 |  |  |  | 4801.00 |  |  | 7302 |  |  |  | 660 | [10 empty] | 82.46 |  |  |  | 82.46 | [5 empty] | 82.81 |  |  | 83.13 |  |  |  | 0.23 |  | 3.08 | [8 empty] | 14.45 |  |  |  |  | 0.00
2021 |  |  |  | 4418.52 |  |  | 7038 |  |  |  | 660 | [10 empty] | 76.40 |  |  |  | 76.40 | [5 empty] | 76.42 |  |  | 80.34 |  |  |  | 17.86 |  | 16.61 | [8 empty] | 6.99 |  |  |  |  | 0.00
2022 |  |  |  | 3546.75 |  |  | 5499 |  |  |  | 660 | [10 empty] | 61.28 |  |  |  | 61.28 | [5 empty] | 61.35 |  |  | 62.77 |  |  |  | 12.21 |  | 19.70 | [8 empty] | 19.02 |  |  |  |  | 0.00
2023 |  |  |  | 4764.67 |  |  | 7366 |  |  |  | 660 | [10 empty] | 82.41 |  |  |  | 82.46 | [5 empty] | 82.41 |  |  | 84.09 |  |  |  | 4.34 |  | 8.46 | [8 empty] | 9.08 |  |  |  |  | 0.05
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1983 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 328 | [14 empty] | 330
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 119
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 553 | [14 empty] | 397
E. |  | Testing of plant systems or components | [35 empty] | 30 |  |  |  | 8
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 992
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 22
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [24 empty] | 413 | [14 empty] | 63
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 3
Z. |  | Other | [20 empty] | 100 | [14 empty] | 2 |  |  |  | 46
Subtotal | [22 empty] | 653 |  |  |  | 741 | [10 empty] | 1562 |  |  |  | 448 | [11 empty] | 4
Total | [22 empty] | 1394 | [14 empty] | 2014
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1983 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 19
12. |  |  | Reactor I&C Systems | [34 empty] | 17
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 10
14. |  |  | Safety Systems | [34 empty] | 20
15. |  |  | Reactor Cooling Systems | [34 empty] | 96
16. |  |  | Steam generation systems | [34 empty] | 38
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 4
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 22
31. |  |  | Turbine and auxiliaries | [34 empty] | 52
32. |  |  | Feedwater and Main Steam System | [34 empty] | 55
34. |  |  | Miscellaneous Systems | [19 empty] | 413 | [14 empty] | 26
41. |  |  | Main Generator Systems | [34 empty] | 29
42. |  |  | Electrical Power Supply Systems | [19 empty] | 328 | [14 empty] | 36
Total | [22 empty] | 741 | [14 empty] | 424