## CHANGJIANG-1
2023 Operating Experience
CN-36 | [8 empty] | CHANGJIANG-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | HNPC (Hainan Nuclear Power Company)
Owner | [7 empty] | : | HNPC (Hainan Nuclear Power Company)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-04-25
Thermal power | [12 empty] | : |  |  | 1930 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-11-07
Gross electrical power | [12 empty] | : |  |  | 650 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-12-25
Reference unit power (net) | [12 empty] | : |  |  | 601 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.35
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.53 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 29.75 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 2.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.09 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 4645.34 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.43 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.49 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.39 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.68 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.92 %
Load Factor (LF) | [18 empty] | : | 88.23 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.19 %
Operating Factor (OF) | [18 empty] | : | 91.23 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 768 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 413.99 | 88.41 |  |  |  | 303.75 |  | 414.14 | [8 empty] | 444.38 |  |  | 425.56 | [6 empty] | 437.15 |  | 420.93 |  |  |  | 429.03 |  |  | 443.77 |  |  | 409.91 | [9 empty] | 414.34 |  |  | 4645.34
EAF [%] |  |  |  |  | 100.00 | 20.94 |  |  |  | 67.93 |  | 100.00 | [8 empty] | 100.00 |  |  | 98.35 | [6 empty] | 97.76 |  | 95.39 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.49
UCF [%] |  |  |  |  | 100.00 | 20.94 |  |  |  | 67.93 |  | 100.00 | [8 empty] | 100.00 |  |  | 98.35 | [6 empty] | 100.00 |  | 95.39 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.68
LF [%] |  |  |  |  | 92.58 | 21.89 |  |  |  | 67.93 |  | 95.71 | [8 empty] | 99.38 |  |  | 98.35 | [6 empty] | 97.76 |  | 94.14 |  |  |  | 99.15 |  |  | 99.25 |  |  | 94.73 | [9 empty] | 92.66 |  |  | 88.23
OF [%] |  |  |  |  | 100.00 | 21.43 |  |  |  | 70.70 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 97.04 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.23
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 4.61 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.43
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 4.61 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.39
PUF [%] |  |  |  |  | 0.00 | 79.06 |  |  |  | 32.07 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.65 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.92
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 2.24 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.19
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 34155.23 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.22 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.43 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.45 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.35 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.97 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.37 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 43.73 |  |  | 1006 |  |  |  | 610 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 3617.23 |  |  | 8185 |  |  |  | 601 | [10 empty] | 93.96 |  |  |  | 93.96 | [5 empty] | 68.52 |  |  | 93.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.04 |  |  |  |  | 0.00
2017 |  |  |  | 3405.19 |  |  | 7006 |  |  |  | 601 | [10 empty] | 79.95 |  |  |  | 79.95 | [5 empty] | 64.68 |  |  | 79.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.05 |  |  |  |  | 0.00
2018 |  |  |  | 3909.29 |  |  | 7711 |  |  |  | 601 | [10 empty] | 87.53 |  |  |  | 87.53 | [5 empty] | 74.25 |  |  | 88.03 |  |  |  | 1.36 |  | 1.21 | [8 empty] | 11.26 |  |  |  |  | 0.00
2019 |  |  |  | 4352.30 |  |  | 7741 |  |  |  | 601 | [10 empty] | 87.46 |  |  |  | 87.46 | [5 empty] | 82.67 |  |  | 88.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.54 |  |  |  |  | 0.00
2020 |  |  |  | 4519.05 |  |  | 7933 |  |  |  | 601 | [10 empty] | 91.48 |  |  |  | 91.48 | [5 empty] | 85.86 |  |  | 90.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.52 |  |  |  |  | 0.00
2021 |  |  |  | 4467.67 |  |  | 8044 |  |  |  | 601 | [10 empty] | 92.65 |  |  |  | 92.65 | [5 empty] | 84.86 |  |  | 91.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.35 |  |  |  |  | 0.00
2022 |  |  |  | 5195.39 |  |  | 8760 |  |  |  | 601 | [10 empty] | 99.88 |  |  |  | 99.88 | [5 empty] | 98.68 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.12 |  |  |  |  | 0.00
2023 |  |  |  | 4645.34 |  |  | 7992 |  |  |  | 601 | [10 empty] | 90.49 |  |  |  | 90.68 | [5 empty] | 88.23 |  |  | 91.23 |  |  |  | 0.43 |  | 0.39 | [8 empty] | 8.92 |  |  |  |  | 0.19
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2015 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 22 | [14 empty] | 7
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 749 | [14 empty] | 702
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 77
I. |  | Grid capacity limitation | [51 empty] | 13
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 46
Subtotal | [22 empty] | 749 |  |  |  | 22 | [10 empty] | 779 |  |  |  | 7 | [11 empty] | 59
Total | [22 empty] | 771 | [14 empty] | 845
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2015 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [19 empty] | 22 | [14 empty] | 3
33. |  |  | Circulating Water System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 30
Total | [22 empty] | 22 | [14 empty] | 37

## CHANGJIANG-2
2023 Operating Experience
CN-37 | [8 empty] | CHANGJIANG-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | HNPC (Hainan Nuclear Power Company)
Owner | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-11-21
Thermal power | [12 empty] | : |  |  | 1930 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-06-20
Gross electrical power | [12 empty] | : |  |  | 650 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-08-12
Reference unit power (net) | [12 empty] | : |  |  | 601 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 326.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.35
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.53 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 29.75 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 2.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.09 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5110.99 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.12 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.9 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.1 %
Load Factor (LF) | [18 empty] | : | 97.08 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.77 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 396.25 | 410.53 |  |  |  | 446.83 |  | 413.53 | [8 empty] | 441.84 |  |  | 422.11 | [6 empty] | 433.63 |  | 433.43 |  |  |  | 425.92 |  |  | 440.92 |  |  | 418.19 | [9 empty] | 427.80 |  |  | 5110.99
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 97.55 | [6 empty] | 96.98 |  | 96.93 |  |  |  | 98.43 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.67 |  |  | 99.12
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.56 | [6 empty] | 100.00 |  | 99.54 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.67 |  |  | 99.90
LF [%] |  |  |  |  | 88.62 | 101.65 |  |  |  | 99.93 |  | 95.57 | [8 empty] | 98.81 |  |  | 97.55 | [6 empty] | 96.98 |  | 96.93 |  |  |  | 98.43 |  |  | 98.61 |  |  | 96.64 | [9 empty] | 95.67 |  |  | 97.08
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.44 | [6 empty] | 0.00 |  | 0.46 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.33 |  |  | 0.10
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.01 | [6 empty] | 3.02 |  | 2.60 |  |  |  | 1.57 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.77
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 31727.96 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.39 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.57 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.49 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.68 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.83 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.64 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.1 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.03 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 1831.25 |  |  | 4180 |  |  |  | 601 | [10 empty] | 95.30 |  |  |  | 95.30 | [5 empty] | 72.98 |  |  | 95.89 |  |  |  | 3.07 |  | 3.02 | [8 empty] | 1.68 |  |  |  |  | 0.00
2017 |  |  |  | 3417.22 |  |  | 7524 |  |  |  | 601 | [10 empty] | 88.44 |  |  |  | 88.44 | [5 empty] | 64.91 |  |  | 85.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.56 |  |  |  |  | 0.00
2018 |  |  |  | 3239.86 |  |  | 6531 |  |  |  | 601 | [10 empty] | 74.48 |  |  |  | 74.48 | [5 empty] | 61.54 |  |  | 74.55 |  |  |  | 1.82 |  | 2.40 | [8 empty] | 23.12 |  |  |  |  | 0.00
2019 |  |  |  | 4641.87 |  |  | 8483 |  |  |  | 601 | [10 empty] | 96.23 |  |  |  | 96.23 | [5 empty] | 88.17 |  |  | 96.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.77 |  |  |  |  | 0.00
2020 |  |  |  | 4328.28 |  |  | 7689 |  |  |  | 601 | [10 empty] | 92.11 |  |  |  | 92.11 | [5 empty] | 81.99 |  |  | 87.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.89 |  |  |  |  | 0.00
2021 |  |  |  | 4572.65 |  |  | 8147 |  |  |  | 601 | [10 empty] | 91.96 |  |  |  | 91.96 | [5 empty] | 86.85 |  |  | 93.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.04 |  |  |  |  | 0.00
2022 |  |  |  | 4587.19 |  |  | 7882 |  |  |  | 601 | [10 empty] | 89.67 |  |  |  | 89.67 | [5 empty] | 87.13 |  |  | 89.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.33 |  |  |  |  | 0.00
2023 |  |  |  | 5110.99 |  |  | 8760 |  |  |  | 601 | [10 empty] | 99.12 |  |  |  | 99.90 | [5 empty] | 97.08 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.10 |  |  |  |  | 0.77
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2016 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 40
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 730
E. |  | Testing of plant systems or components | [35 empty] | 43
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 107
Subtotal | [37 empty] | 773 |  |  |  | 40 | [11 empty] | 107
Total | [22 empty] | 0 | [14 empty] | 920
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2016 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 12
16. |  |  | Steam generation systems | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 18
34. |  |  | Miscellaneous Systems | [34 empty] | 51
Total | [37 empty] | 101

## DAYA BAY-1
2023 Operating Experience
CN-2 | [8 empty] | DAYA BAY-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | GNPJVC (GUANGDONG NUCLEAR POWER JOINT VENTURE COMPANY LIMITED)
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M310 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1987-08-07
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-08-31
Gross electrical power | [12 empty] | : |  |  | 984 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-02-01
Reference unit power (net) | [12 empty] | : |  |  | 944 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 46 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 26
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8307.47 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.64 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.64 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.36 %
Load Factor (LF) | [18 empty] | : | 100.46 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 716.52 | 647.09 |  |  |  | 715.22 |  | 690.52 | [8 empty] | 710.08 |  |  | 678.53 | [6 empty] | 702.66 |  | 704.29 |  |  |  | 681.40 |  |  | 705.38 |  |  | 685.61 | [9 empty] | 670.16 |  |  | 8307.47
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.94 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 95.86 |  |  | 99.64
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.94 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 95.86 |  |  | 99.64
LF [%] |  |  |  |  | 102.02 | 102.01 |  |  |  | 101.83 |  | 101.60 | [8 empty] | 101.10 |  |  | 99.83 | [6 empty] | 100.05 |  | 100.28 |  |  |  | 100.25 |  |  | 100.43 |  |  | 100.87 | [9 empty] | 95.42 |  |  | 100.46
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.06 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 4.14 |  |  | 0.36
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 215857.2 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.15 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.16 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.33 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.46 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.49 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.18 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.77 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 5917.39 |  |  | 6539 |  |  |  | 944 | [10 empty] | 76.26 |  |  |  | 77.44 | [5 empty] | 76.76 |  |  | 79.65 |  |  |  | 18.87 |  | 18.01 | [8 empty] | 4.55 |  |  |  |  | 1.18
1995 |  |  |  | 3723.63 |  |  | 4088 |  |  |  | 944 | [10 empty] | 46.21 |  |  |  | 84.61 | [5 empty] | 45.03 |  |  | 46.67 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 15.00 |  |  |  |  | 38.40
1996 |  |  |  | 6252.67 |  |  | 6847 |  |  |  | 944 | [10 empty] | 76.01 |  |  |  | 76.77 | [5 empty] | 75.41 |  |  | 77.95 |  |  |  | 5.09 |  | 4.12 | [8 empty] | 19.11 |  |  |  |  | 0.75
1997 |  |  |  | 6491.23 |  |  | 7272 |  |  |  | 944 | [10 empty] | 74.61 |  |  |  | 82.05 | [5 empty] | 78.50 |  |  | 83.01 |  |  |  | 0.26 |  | 0.21 | [8 empty] | 17.74 |  |  |  |  | 7.44
1998 |  |  |  | 6040.47 |  |  | 7344 |  |  |  | 944 | [10 empty] | 71.99 |  |  |  | 79.64 | [5 empty] | 73.05 |  |  | 83.84 |  |  |  | 5.64 |  | 4.76 | [8 empty] | 15.60 |  |  |  |  | 7.65
1999 |  |  |  | 6723.65 |  |  | 7680 |  |  |  | 944 | [10 empty] | 82.71 |  |  |  | 87.65 | [5 empty] | 81.30 |  |  | 87.66 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 12.33 |  |  |  |  | 4.94
2000 |  |  |  | 6986.58 |  |  | 7641 |  |  |  | 944 | [10 empty] | 85.18 |  |  |  | 85.44 | [5 empty] | 84.26 |  |  | 86.99 |  |  |  | 2.85 |  | 2.50 | [8 empty] | 12.06 |  |  |  |  | 0.26
2001 |  |  |  | 7009.34 |  |  | 7619 |  |  |  | 944 | [10 empty] | 84.81 |  |  |  | 87.49 | [5 empty] | 84.76 |  |  | 86.97 |  |  |  | 0.36 |  | 0.32 | [8 empty] | 12.19 |  |  |  |  | 2.68
2002 |  |  |  | 7387.25 |  |  | 7924 |  |  |  | 944 | [10 empty] | 89.52 |  |  |  | 89.62 | [5 empty] | 89.33 |  |  | 90.46 |  |  |  | 0.27 |  | 0.24 | [8 empty] | 10.13 |  |  |  |  | 0.10
2003 |  |  |  | 7400.76 |  |  | 7958 |  |  |  | 944 | [10 empty] | 90.42 |  |  |  | 90.95 | [5 empty] | 89.50 |  |  | 90.84 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 8.99 |  |  |  |  | 0.53
2004 |  |  |  | 7540.90 |  |  | 7789 |  |  |  | 944 | [10 empty] | 88.21 |  |  |  | 88.45 | [5 empty] | 90.94 |  |  | 88.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.55 |  |  |  |  | 0.24
2005 |  |  |  | 8260.49 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 99.89 |  |  | 100.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.01 |  |  |  |  | 0.00
2006 |  |  |  | 6635.15 |  |  | 7133 |  |  |  | 944 | [10 empty] | 79.86 |  |  |  | 79.86 | [5 empty] | 80.24 |  |  | 81.43 |  |  |  | 1.10 |  | 0.89 | [8 empty] | 19.26 |  |  |  |  | 0.00
2007 |  |  |  | 7542.13 |  |  | 8074 |  |  |  | 944 | [10 empty] | 91.20 |  |  |  | 91.20 | [5 empty] | 91.20 |  |  | 92.17 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 8.59 |  |  |  |  | 0.00
2008 |  |  |  | 8255.49 |  |  | 8774 |  |  |  | 944 | [10 empty] | 99.84 |  |  |  | 99.97 | [5 empty] | 99.56 |  |  | 99.89 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.02 |  |  |  |  | 0.13
2009 |  |  |  | 7439.13 |  |  | 8055 |  |  |  | 944 | [10 empty] | 90.81 |  |  |  | 90.86 | [5 empty] | 89.96 |  |  | 91.95 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 9.12 |  |  |  |  | 0.05
2010 |  |  |  | 7328.51 |  |  | 7876 |  |  |  | 944 | [10 empty] | 88.95 |  |  |  | 88.95 | [5 empty] | 88.62 |  |  | 89.91 |  |  |  | 0.00 |  | 1.61 | [8 empty] | 9.44 |  |  |  |  | 0.00
2011 |  |  |  | 8222.61 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 99.43 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
2012 |  |  |  | 6952.17 |  |  | 7452 |  |  |  | 944 | [10 empty] | 83.56 |  |  |  | 83.90 | [5 empty] | 83.84 |  |  | 84.84 |  |  |  | 0.14 |  | 1.36 | [8 empty] | 14.74 |  |  |  |  | 0.35
2013 |  |  |  | 7150.01 |  |  | 7682 |  |  |  | 944 | [10 empty] | 86.41 |  |  |  | 86.68 | [5 empty] | 86.46 |  |  | 87.69 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 13.31 |  |  |  |  | 0.26
2014 |  |  |  | 8247.51 |  |  | 8735 |  |  |  | 944 | [10 empty] | 99.33 |  |  |  | 99.53 | [5 empty] | 99.73 |  |  | 99.71 |  |  |  | 0.31 |  | 0.31 | [8 empty] | 0.15 |  |  |  |  | 0.20
2015 |  |  |  | 6581.67 |  |  | 6954 |  |  |  | 944 | [10 empty] | 78.84 |  |  |  | 78.84 | [5 empty] | 79.59 |  |  | 79.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.16 |  |  |  |  | 0.00
2016 |  |  |  | 7235.87 |  |  | 7671 |  |  |  | 944 | [10 empty] | 86.58 |  |  |  | 86.58 | [5 empty] | 87.26 |  |  | 87.33 |  |  |  | 0.04 |  | 1.24 | [8 empty] | 12.18 |  |  |  |  | 0.00
2017 |  |  |  | 8343.32 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 100.89 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2018 |  |  |  | 7444.51 |  |  | 7871 |  |  |  | 944 | [10 empty] | 89.18 |  |  |  | 89.25 | [5 empty] | 90.02 |  |  | 89.85 |  |  |  | 0.42 |  | 0.38 | [8 empty] | 10.37 |  |  |  |  | 0.07
2019 |  |  |  | 7771.68 |  |  | 8186 |  |  |  | 944 | [10 empty] | 92.94 |  |  |  | 92.94 | [5 empty] | 93.98 |  |  | 93.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.06 |  |  |  |  | 0.00
2020 |  |  |  | 8398.23 |  |  | 8784 |  |  |  | 944 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 101.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2021 |  |  |  | 7421.56 |  |  | 7834 |  |  |  | 944 | [10 empty] | 88.92 |  |  |  | 88.92 | [5 empty] | 89.75 |  |  | 89.43 |  |  |  | 0.00 |  | 0.84 | [8 empty] | 10.24 |  |  |  |  | 0.00
2022 |  |  |  | 7666.03 |  |  | 8101 |  |  |  | 944 | [10 empty] | 91.84 |  |  |  | 91.84 | [5 empty] | 92.70 |  |  | 92.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.16 |  |  |  |  | 0.00
2023 |  |  |  | 8307.47 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.64 |  |  |  | 99.64 | [5 empty] | 100.46 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.36 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1994 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 86
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 780
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 10
E. |  | Testing of plant systems or components | [39 empty] | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 10
Z. |  | Other | [51 empty] | 103
Subtotal | [37 empty] | 790 |  |  |  | 86 | [11 empty] | 113
Total | [22 empty] | 0 | [14 empty] | 989
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1994 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 32
42. |  |  | Electrical Power Supply Systems | [34 empty] | 19
Total | [37 empty] | 86

## DAYA BAY-2
2023 Operating Experience
CN-3 | [8 empty] | DAYA BAY-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | GNPJVC (GUANGDONG NUCLEAR POWER JOINT VENTURE COMPANY LIMITED)
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M310 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1988-04-07
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1994-02-07
Gross electrical power | [12 empty] | : |  |  | 984 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-05-06
Reference unit power (net) | [12 empty] | : |  |  | 944 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 29 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 46 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 26
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6181.83 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.25 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.25 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.75 %
Load Factor (LF) | [18 empty] | : | 74.76 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 74.33 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2249 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 715.04 | 646.05 |  |  |  | 714.31 |  | 687.95 | [8 empty] | 707.71 |  |  | 677.09 | [6 empty] | 700.76 |  | 701.39 |  |  |  | 631.53 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6181.83
EAF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.92 |  |  |  | 93.50 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 74.25
UCF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.92 |  |  |  | 93.50 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 74.25
LF [%] |  |  |  |  | 101.81 | 101.84 |  |  |  | 101.71 |  | 101.22 | [8 empty] | 100.77 |  |  | 99.62 | [6 empty] | 99.77 |  | 99.87 |  |  |  | 92.92 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 74.76
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 94.03 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.27 |  |  | 74.33
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.08 |  |  |  | 6.50 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 25.75
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 212019.23 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.41 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.41 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.99 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.43 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.58 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.6 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.81 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 5741.21 |  |  | 6889 |  |  |  | 944 | [10 empty] | 92.32 |  |  |  | 99.39 | [5 empty] | 90.33 |  |  | 97.98 |  |  |  | 0.60 |  | 0.60 | [8 empty] | 0.01 |  |  |  |  | 7.07
1995 |  |  |  | 6343.33 |  |  | 7146 |  |  |  | 944 | [10 empty] | 77.48 |  |  |  | 81.09 | [5 empty] | 76.71 |  |  | 81.58 |  |  |  | 1.35 |  | 1.11 | [8 empty] | 17.80 |  |  |  |  | 3.60
1996 |  |  |  | 5276.90 |  |  | 5740 |  |  |  | 944 | [10 empty] | 63.92 |  |  |  | 67.43 | [5 empty] | 63.64 |  |  | 65.35 |  |  |  | 13.49 |  | 10.51 | [8 empty] | 22.05 |  |  |  |  | 3.51
1997 |  |  |  | 5914.84 |  |  | 6194 |  |  |  | 944 | [10 empty] | 67.41 |  |  |  | 70.10 | [5 empty] | 71.53 |  |  | 70.71 |  |  |  | 2.15 |  | 1.54 | [8 empty] | 28.37 |  |  |  |  | 2.69
1998 |  |  |  | 6259.05 |  |  | 7302 |  |  |  | 944 | [10 empty] | 74.71 |  |  |  | 82.90 | [5 empty] | 75.69 |  |  | 83.36 |  |  |  | 2.15 |  | 1.82 | [8 empty] | 15.27 |  |  |  |  | 8.19
1999 |  |  |  | 6789.46 |  |  | 7594 |  |  |  | 944 | [10 empty] | 83.32 |  |  |  | 86.18 | [5 empty] | 82.10 |  |  | 86.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.82 |  |  |  |  | 2.87
2000 |  |  |  | 6995.52 |  |  | 7840 |  |  |  | 944 | [10 empty] | 88.39 |  |  |  | 89.13 | [5 empty] | 84.36 |  |  | 89.25 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 10.83 |  |  |  |  | 0.73
2001 |  |  |  | 7355.47 |  |  | 7986 |  |  |  | 944 | [10 empty] | 89.46 |  |  |  | 91.12 | [5 empty] | 88.95 |  |  | 91.16 |  |  |  | 0.19 |  | 0.18 | [8 empty] | 8.70 |  |  |  |  | 1.66
2002 |  |  |  | 6728.92 |  |  | 7224 |  |  |  | 944 | [10 empty] | 81.62 |  |  |  | 82.22 | [5 empty] | 81.37 |  |  | 82.47 |  |  |  | 15.12 |  | 14.64 | [8 empty] | 3.14 |  |  |  |  | 0.60
2003 |  |  |  | 6983.05 |  |  | 7503 |  |  |  | 944 | [10 empty] | 84.53 |  |  |  | 84.62 | [5 empty] | 84.44 |  |  | 85.65 |  |  |  | 0.53 |  | 1.17 | [8 empty] | 14.21 |  |  |  |  | 0.09
2004 |  |  |  | 6358.88 |  |  | 6580 |  |  |  | 944 | [10 empty] | 74.23 |  |  |  | 74.39 | [5 empty] | 76.69 |  |  | 74.91 |  |  |  | 0.10 |  | 16.74 | [8 empty] | 8.87 |  |  |  |  | 0.17
2005 |  |  |  | 6586.98 |  |  | 7075 |  |  |  | 944 | [10 empty] | 79.62 |  |  |  | 79.62 | [5 empty] | 79.65 |  |  | 80.76 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 20.36 |  |  |  |  | 0.00
2006 |  |  |  | 8222.79 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.89 |  |  |  | 99.89 | [5 empty] | 99.44 |  |  | 100.00 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.07 |  |  |  |  | 0.00
2007 |  |  |  | 7344.17 |  |  | 7858 |  |  |  | 944 | [10 empty] | 88.81 |  |  |  | 88.81 | [5 empty] | 88.81 |  |  | 89.70 |  |  |  | 0.90 |  | 2.27 | [8 empty] | 8.92 |  |  |  |  | 0.00
2008 |  |  |  | 7174.36 |  |  | 7667 |  |  |  | 944 | [10 empty] | 86.25 |  |  |  | 86.25 | [5 empty] | 86.52 |  |  | 87.28 |  |  |  | 5.20 |  | 4.73 | [8 empty] | 9.02 |  |  |  |  | 0.00
2009 |  |  |  | 8222.61 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.98 |  |  |  | 99.99 | [5 empty] | 99.43 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.01
2010 |  |  |  | 7685.64 |  |  | 8197 |  |  |  | 944 | [10 empty] | 92.50 |  |  |  | 92.50 | [5 empty] | 92.94 |  |  | 93.57 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 7.49 |  |  |  |  | 0.00
2011 |  |  |  | 7113.12 |  |  | 7649 |  |  |  | 944 | [10 empty] | 86.23 |  |  |  | 86.34 | [5 empty] | 86.02 |  |  | 87.32 |  |  |  | 0.00 |  | 2.65 | [8 empty] | 11.00 |  |  |  |  | 0.11
2012 |  |  |  | 8304.98 |  |  | 8784 |  |  |  | 944 | [10 empty] | 99.66 |  |  |  | 99.97 | [5 empty] | 100.16 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.31
2013 |  |  |  | 7091.41 |  |  | 7605 |  |  |  | 944 | [10 empty] | 85.58 |  |  |  | 85.81 | [5 empty] | 85.75 |  |  | 86.82 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 14.17 |  |  |  |  | 0.23
2014 |  |  |  | 6249.97 |  |  | 6629 |  |  |  | 944 | [10 empty] | 75.23 |  |  |  | 75.57 | [5 empty] | 75.58 |  |  | 75.67 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 24.41 |  |  |  |  | 0.34
2015 |  |  |  | 8193.18 |  |  | 8700 |  |  |  | 944 | [10 empty] | 98.65 |  |  |  | 98.65 | [5 empty] | 99.08 |  |  | 99.32 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 1.34 |  |  |  |  | 0.01
2016 |  |  |  | 7290.17 |  |  | 7750 |  |  |  | 944 | [10 empty] | 87.39 |  |  |  | 87.39 | [5 empty] | 87.92 |  |  | 88.23 |  |  |  | 0.30 |  | 0.30 | [8 empty] | 12.32 |  |  |  |  | 0.00
2017 |  |  |  | 7376.85 |  |  | 7819 |  |  |  | 944 | [10 empty] | 88.63 |  |  |  | 88.74 | [5 empty] | 89.21 |  |  | 89.26 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 11.25 |  |  |  |  | 0.11
2018 |  |  |  | 8306.97 |  |  | 8739 |  |  |  | 944 | [10 empty] | 99.65 |  |  |  | 99.72 | [5 empty] | 100.45 |  |  | 99.76 |  |  |  | 0.27 |  | 0.27 | [8 empty] | 0.01 |  |  |  |  | 0.06
2019 |  |  |  | 7704.07 |  |  | 8143 |  |  |  | 944 | [10 empty] | 92.35 |  |  |  | 92.35 | [5 empty] | 93.16 |  |  | 92.96 |  |  |  | 0.04 |  | 0.24 | [8 empty] | 7.40 |  |  |  |  | 0.00
2020 |  |  |  | 7475.32 |  |  | 7889 |  |  |  | 944 | [10 empty] | 89.21 |  |  |  | 89.21 | [5 empty] | 90.15 |  |  | 89.81 |  |  |  | 0.13 |  | 0.12 | [8 empty] | 10.67 |  |  |  |  | 0.00
2021 |  |  |  | 8321.42 |  |  | 8760 |  |  |  | 944 | [10 empty] | 99.89 |  |  |  | 99.98 | [5 empty] | 100.63 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.09
2022 |  |  |  | 7767.89 |  |  | 8209 |  |  |  | 944 | [10 empty] | 93.24 |  |  |  | 93.24 | [5 empty] | 93.93 |  |  | 93.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.76 |  |  |  |  | 0.00
2023 |  |  |  | 6181.83 |  |  | 6511 |  |  |  | 944 | [10 empty] | 74.25 |  |  |  | 74.25 | [5 empty] | 74.76 |  |  | 74.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.75 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1994 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 94
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1509 | [14 empty] | 835 |  |  |  | 8
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 9
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 744 | [14 empty] | 25
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 14
Subtotal | [22 empty] | 2253 | [14 empty] | 869 |  |  |  | 116 | [11 empty] | 11
Total | [22 empty] | 2253 | [14 empty] | 996
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1994 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 36
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 44
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [37 empty] | 106

## FANGCHENGGANG-1
2023 Operating Experience
CN-38 | [8 empty] | FANGCHENGGANG-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | GFNPC (Guangxi Fangchenggang Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | GFNPC (Guangxi Fangchenggang Nuclear Power Company, Ltd.)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-07-30
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-10-25
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-01-01
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7940.89 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.84 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.84 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.16 %
Load Factor (LF) | [18 empty] | : | 90.65 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.44 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 662 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 628.76 | 684.00 |  |  |  | 243.51 |  | 540.91 | [8 empty] | 746.70 |  |  | 719.50 | [6 empty] | 737.29 |  | 728.33 |  |  |  | 691.60 |  |  | 736.34 |  |  | 723.56 | [9 empty] | 760.38 |  |  | 7940.89
EAF [%] |  |  |  |  | 99.75 | 99.68 |  |  |  | 32.05 |  | 73.51 | [8 empty] | 99.73 |  |  | 99.75 | [6 empty] | 99.73 |  | 99.75 |  |  |  | 99.73 |  |  | 99.75 |  |  | 99.75 | [9 empty] | 99.85 |  |  | 91.84
UCF [%] |  |  |  |  | 99.75 | 99.68 |  |  |  | 32.05 |  | 73.51 | [8 empty] | 99.73 |  |  | 99.75 | [6 empty] | 99.73 |  | 99.75 |  |  |  | 99.73 |  |  | 99.75 |  |  | 99.75 | [9 empty] | 99.85 |  |  | 91.84
LF [%] |  |  |  |  | 84.51 | 101.79 |  |  |  | 32.73 |  | 75.13 | [8 empty] | 100.36 |  |  | 99.93 | [6 empty] | 99.10 |  | 97.89 |  |  |  | 96.06 |  |  | 98.97 |  |  | 100.49 | [9 empty] | 102.20 |  |  | 90.65
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 33.06 |  | 77.22 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.44
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.25 | 0.32 |  |  |  | 67.95 |  | 26.49 | [8 empty] | 0.27 |  |  | 0.25 | [6 empty] | 0.27 |  | 0.25 |  |  |  | 0.27 |  |  | 0.25 |  |  | 0.25 | [9 empty] | 0.15 |  |  | 8.16
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 61425.89 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.25 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.7 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.34 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.75 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.91 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.65 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.59 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 7141.83 |  |  | 7761 |  |  |  | 1000 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 81.30 |  |  | 88.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.01
2017 |  |  |  | 5212.98 |  |  | 5794 |  |  |  | 1000 | [10 empty] | 76.66 |  |  |  | 76.82 | [5 empty] | 59.51 |  |  | 66.14 |  |  |  | 0.00 |  | 0.91 | [8 empty] | 22.27 |  |  |  |  | 0.16
2018 |  |  |  | 7425.87 |  |  | 7622 |  |  |  | 1000 | [10 empty] | 90.01 |  |  |  | 90.19 | [5 empty] | 84.77 |  |  | 87.01 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.80 |  |  |  |  | 0.18
2019 |  |  |  | 8540.31 |  |  | 8736 |  |  |  | 1000 | [10 empty] | 99.62 |  |  |  | 99.62 | [5 empty] | 97.49 |  |  | 99.73 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.02 |  |  |  |  | 0.00
2020 |  |  |  | 7919.20 |  |  | 8140 |  |  |  | 1000 | [10 empty] | 91.43 |  |  |  | 91.43 | [5 empty] | 90.15 |  |  | 92.67 |  |  |  | 0.72 |  | 0.66 | [8 empty] | 7.91 |  |  |  |  | 0.00
2021 |  |  |  | 8168.79 |  |  | 8179 |  |  |  | 1000 | [10 empty] | 92.90 |  |  |  | 92.90 | [5 empty] | 93.25 |  |  | 93.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.09 |  |  |  |  | 0.00
2022 |  |  |  | 8414.60 |  |  | 8499 |  |  |  | 1000 | [10 empty] | 99.18 |  |  |  | 99.18 | [5 empty] | 96.06 |  |  | 97.02 |  |  |  | 0.81 |  | 0.81 | [8 empty] | 0.01 |  |  |  |  | 0.00
2023 |  |  |  | 7940.89 |  |  | 8098 |  |  |  | 1000 | [10 empty] | 91.84 |  |  |  | 91.84 | [5 empty] | 90.65 |  |  | 92.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.16 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2016 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 21
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 659 | [14 empty] | 573
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 319
Subtotal | [22 empty] | 659 | [14 empty] | 573 |  |  |  | 21 | [11 empty] | 319
Total | [22 empty] | 659 | [14 empty] | 913
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2016 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
14. |  |  | Safety Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 24
Total | [37 empty] | 45

## FANGCHENGGANG-2
2023 Operating Experience
CN-39 | [8 empty] | FANGCHENGGANG-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | GFNPC (Guangxi Fangchenggang Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | GFNPC (Guangxi Fangchenggang Nuclear Power Company, Ltd.)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-12-23
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-07-15
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-10-01
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8044.34 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.26 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.78 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.23 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.78 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.99 %
Load Factor (LF) | [18 empty] | : | 91.83 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.53 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 742 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 744.00 | 690.02 |  |  |  | 760.86 |  | 737.76 | [8 empty] | 754.22 |  |  | 721.77 | [6 empty] | 734.75 |  | 0.30 |  |  |  | 670.46 |  |  | 748.58 |  |  | 711.17 | [9 empty] | 770.45 |  |  | 8044.34
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.90 | [6 empty] | 99.56 |  | 0.08 |  |  |  | 94.55 |  |  | 99.98 |  |  | 97.16 | [9 empty] | 99.98 |  |  | 90.78
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.90 | [6 empty] | 99.56 |  | 0.08 |  |  |  | 94.55 |  |  | 99.98 |  |  | 97.16 | [9 empty] | 99.98 |  |  | 90.78
LF [%] |  |  |  |  | 100.00 | 102.68 |  |  |  | 102.27 |  | 102.47 | [8 empty] | 101.37 |  |  | 100.25 | [6 empty] | 98.76 |  | 0.04 |  |  |  | 93.12 |  |  | 100.62 |  |  | 98.77 | [9 empty] | 103.56 |  |  | 91.83
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 0.27 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.53
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.84 | [9 empty] | 0.00 |  |  | 0.26
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.84 | [9 empty] | 0.00 |  |  | 0.23
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.10 | [6 empty] | 0.44 |  | 99.92 |  |  |  | 5.45 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 8.99
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 57359.29 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.24 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.83 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.23 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.9 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.04 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.74 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 2648.30 |  |  | 3297 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 91.13 |  |  | 88.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6569.07 |  |  | 6827 |  |  |  | 1000 | [10 empty] | 80.27 |  |  |  | 80.38 | [5 empty] | 74.99 |  |  | 77.93 |  |  |  | 1.63 |  | 1.33 | [8 empty] | 18.29 |  |  |  |  | 0.12
2018 |  |  |  | 7655.73 |  |  | 7816 |  |  |  | 1000 | [10 empty] | 99.81 |  |  |  | 99.98 | [5 empty] | 87.39 |  |  | 89.22 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.01 |  |  |  |  | 0.18
2019 |  |  |  | 7579.32 |  |  | 7625 |  |  |  | 1000 | [10 empty] | 92.14 |  |  |  | 92.14 | [5 empty] | 86.52 |  |  | 87.04 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 7.78 |  |  |  |  | 0.00
2020 |  |  |  | 7901.00 |  |  | 7911 |  |  |  | 1000 | [10 empty] | 91.98 |  |  |  | 91.98 | [5 empty] | 89.95 |  |  | 90.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.02 |  |  |  |  | 0.00
2021 |  |  |  | 8888.26 |  |  | 8760 |  |  |  | 1000 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 101.46 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2022 |  |  |  | 8168.69 |  |  | 8129 |  |  |  | 1000 | [10 empty] | 93.04 |  |  |  | 93.04 | [5 empty] | 93.25 |  |  | 92.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.96 |  |  |  |  | 0.00
2023 |  |  |  | 8044.34 |  |  | 8018 |  |  |  | 1000 | [10 empty] | 90.78 |  |  |  | 90.78 | [5 empty] | 91.83 |  |  | 91.53 |  |  |  | 0.26 |  | 0.23 | [8 empty] | 8.99 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2016 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 17
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 742 | [14 empty] | 573
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 309
Subtotal | [22 empty] | 742 | [14 empty] | 573 |  |  |  | 17 | [11 empty] | 309
Total | [22 empty] | 742 | [14 empty] | 899
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2016 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
34. |  |  | Miscellaneous Systems | [34 empty] | 100
Total | [37 empty] | 116

## FANGCHENGGANG-3
2023 Operating Experience
CN-55 | [8 empty] | FANGCHENGGANG-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | GFNPC (Guangxi Fangchenggang Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | GFNPC (Guangxi Fangchenggang Nuclear Power Company, Ltd.)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / HPR1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2015-12-24
Thermal power | [12 empty] | : |  |  | 3150 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2023-01-10
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2023-03-25
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 0 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 324.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.7 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47400 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.23 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.45
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.95 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 68 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7569.94 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.79 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.19 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.79 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.19 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.02 %
Load Factor (LF) | [18 empty] | : | 106.57 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 98.18 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1903 hours
Annual Summary
[5 empty] | Mar | Jan |  |  |  | Feb |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [11 empty] | 792.00 | [8 empty] | 700.23 |  |  | 791.96 | [6 empty] | 816.45 |  | 811.37 |  |  |  | 766.88 |  |  | 814.02 |  |  | 722.47 | [9 empty] | 818.17 |  |  | 7033.55
EAF [%] | [11 empty] | 100.00 | [8 empty] | 84.12 |  |  | 99.99 | [6 empty] | 99.95 |  | 99.98 |  |  |  | 99.96 |  |  | 99.97 |  |  | 99.97 | [9 empty] | 99.97 |  |  | 98.19
UCF [%] | [11 empty] | 100.00 | [8 empty] | 84.12 |  |  | 99.99 | [6 empty] | 99.95 |  | 99.98 |  |  |  | 99.96 |  |  | 99.97 |  |  | 99.97 | [9 empty] | 99.97 |  |  | 98.19
LF [%] | [11 empty] | 110.00 | [8 empty] | 94.12 |  |  | 109.99 | [6 empty] | 109.74 |  | 109.06 |  |  |  | 106.51 |  |  | 109.41 |  |  | 100.34 | [9 empty] | 109.97 |  |  | 106.57
OF [%] | [11 empty] | 100.00 | [8 empty] | 83.87 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.18
FLR [%] | [11 empty] | 0.00 | [8 empty] | 15.87 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.79
UCL [%] | [11 empty] | 0.00 | [8 empty] | 15.86 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.79
PUF [%] | [11 empty] | 0.00 | [8 empty] | 0.02 |  |  | 0.01 | [6 empty] | 0.02 |  | 0.02 |  |  |  | 0.04 |  |  | 0.03 |  |  | 0.03 | [9 empty] | 0.03 |  |  | 0.02
XUF [%] | [11 empty] | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 7215.47 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.79 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 98.19 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.79 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 98.19 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0.02 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 106.57 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 98.18 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2023 |  |  |  | 7569.94 |  |  | 6641 |  |  |  | 1000 | [10 empty] | 98.19 |  |  |  | 98.19 | [5 empty] | 106.57 |  |  | 98.18 |  |  |  | 1.79 |  | 1.79 | [8 empty] | 0.02 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2023 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 120 | [14 empty] | 160
Subtotal | [26 empty] | 120 | [14 empty] | 160
Total | [22 empty] | 120 | [14 empty] | 160
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2023 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [19 empty] | 120 | [14 empty] | 120
Total | [22 empty] | 120 | [14 empty] | 120
Highlights (2023)
1.CN55 was officially put into commercial operation on March 25, 2023,Unplanned shutdown and retreat once.2.At the request of grid system,CN55 deloaded for some holidays and weekends and other reasons.

## FANGJIASHAN-1
2023 Operating Experience
CN-24 | [8 empty] | FANGJIASHAN-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CNNO (CNNC Nuclear Operation Management Company Limited)
Owner | [7 empty] | : | QNPC (QINSHAN NUCLEAR POWER COMPANY)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-12-26
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-11-04
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2014-12-15
Reference unit power (net) | [12 empty] | : |  |  | 1012 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8364.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.49 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.03 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.26 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.71 %
Load Factor (LF) | [18 empty] | : | 94.35 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.77 %
Operating Factor (OF) | [18 empty] | : | 94.71 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 463 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 723.68 | 690.44 |  |  |  | 764.70 |  | 740.00 | [8 empty] | 762.40 |  |  | 729.08 | [6 empty] | 737.82 |  | 738.32 |  |  |  | 303.60 |  |  | 672.76 |  |  | 738.82 | [9 empty] | 762.96 |  |  | 8364.58
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.75 |  |  | 98.79 | [6 empty] | 96.95 |  | 96.99 |  |  |  | 41.24 |  |  | 87.82 |  |  | 99.90 | [9 empty] | 100.00 |  |  | 93.49
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.64 |  | 100.00 |  |  |  | 42.25 |  |  | 88.64 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.26
LF [%] |  |  |  |  | 96.12 | 101.53 |  |  |  | 101.56 |  | 101.56 | [8 empty] | 101.26 |  |  | 100.06 | [6 empty] | 97.99 |  | 98.06 |  |  |  | 41.67 |  |  | 89.35 |  |  | 101.40 | [9 empty] | 101.33 |  |  | 94.35
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 42.92 |  |  | 93.01 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.71
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.34 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.34 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.02 |  | 0.00 |  |  |  | 57.75 |  |  | 11.36 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.71
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.24 |  |  | 1.21 | [6 empty] | 2.70 |  | 3.01 |  |  |  | 1.01 |  |  | 0.83 |  |  | 0.10 | [9 empty] | 0.00 |  |  | 0.77
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 72864 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.06 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.04 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.06 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.55 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.39 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.51 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.52 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 7180.23 |  |  | 7289 |  |  |  | 1012 | [10 empty] | 84.47 |  |  |  | 84.47 | [5 empty] | 80.99 |  |  | 83.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.53 |  |  |  |  | 0.00
2016 |  |  |  | 7827.38 |  |  | 7910 |  |  |  | 1012 | [10 empty] | 91.68 |  |  |  | 91.68 | [5 empty] | 88.05 |  |  | 90.05 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 8.28 |  |  |  |  | 0.00
2017 |  |  |  | 7628.57 |  |  | 7676 |  |  |  | 1012 | [10 empty] | 88.54 |  |  |  | 89.14 | [5 empty] | 86.05 |  |  | 87.63 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 10.79 |  |  |  |  | 0.60
2018 |  |  |  | 8761.17 |  |  | 8732 |  |  |  | 1012 | [10 empty] | 99.06 |  |  |  | 99.61 | [5 empty] | 98.83 |  |  | 99.68 |  |  |  | 0.39 |  | 0.39 | [8 empty] | 0.00 |  |  |  |  | 0.55
2019 |  |  |  | 7992.84 |  |  | 8048 |  |  |  | 1012 | [10 empty] | 89.85 |  |  |  | 91.12 | [5 empty] | 90.16 |  |  | 91.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.88 |  |  |  |  | 1.28
2020 |  |  |  | 7214.92 |  |  | 7218 |  |  |  | 1012 | [10 empty] | 89.30 |  |  |  | 89.77 | [5 empty] | 81.16 |  |  | 82.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.23 |  |  |  |  | 0.46
2021 |  |  |  | 8862.47 |  |  | 8760 |  |  |  | 1012 | [10 empty] | 99.76 |  |  |  | 99.86 | [5 empty] | 99.97 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.14 |  |  |  |  | 0.09
2022 |  |  |  | 8212.68 |  |  | 8150 |  |  |  | 1012 | [10 empty] | 91.55 |  |  |  | 92.46 | [5 empty] | 92.64 |  |  | 93.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.54 |  |  |  |  | 0.90
2023 |  |  |  | 8364.58 |  |  | 8297 |  |  |  | 1012 | [10 empty] | 93.49 |  |  |  | 94.26 | [5 empty] | 94.35 |  |  | 94.71 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 5.71 |  |  |  |  | 0.77
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2014 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 566
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 463 | [14 empty] | 51
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 135
L. |  | Human factor related | [39 empty] | 3
Subtotal | [22 empty] | 463 | [14 empty] | 617 |  |  |  | 3 | [11 empty] | 135
Total | [22 empty] | 463 | [14 empty] | 755
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2014 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [34 empty] | 81
Total | [37 empty] | 81
Highlights (2023)
The unit was shutdown for 107 refuelling outage from September 13 to October 3.

## FANGJIASHAN-2
2023 Operating Experience
CN-25 | [8 empty] | FANGJIASHAN-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CNNO (CNNC Nuclear Operation Management Company Limited)
Owner | [7 empty] | : | QNPC (QINSHAN NUCLEAR POWER COMPANY)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-07-17
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-01-12
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-02-12
Reference unit power (net) | [12 empty] | : |  |  | 1012 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8882.44 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.03 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 100.2 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.97 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 734.52 | 692.78 |  |  |  | 767.78 |  | 742.06 | [8 empty] | 762.44 |  |  | 727.92 | [6 empty] | 739.30 |  | 737.98 |  |  |  | 715.84 |  |  | 756.26 |  |  | 739.68 | [9 empty] | 765.88 |  |  | 8882.44
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.61 |  |  | 98.48 | [6 empty] | 96.98 |  | 96.78 |  |  |  | 97.64 |  |  | 99.17 |  |  | 99.81 | [9 empty] | 100.00 |  |  | 99.03
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 97.56 | 101.87 |  |  |  | 101.97 |  | 101.84 | [8 empty] | 101.26 |  |  | 99.90 | [6 empty] | 98.19 |  | 98.01 |  |  |  | 98.24 |  |  | 100.44 |  |  | 101.52 | [9 empty] | 101.72 |  |  | 100.20
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.39 |  |  | 1.52 | [6 empty] | 3.02 |  | 3.22 |  |  |  | 2.36 |  |  | 0.83 |  |  | 0.19 | [9 empty] | 0.00 |  |  | 0.97
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 71805 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.24 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.23 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.9 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 90.86 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.59 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 92.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 7400.55 |  |  | 7747 |  |  |  | 1012 | [10 empty] | 93.22 |  |  |  | 93.22 | [5 empty] | 89.98 |  |  | 92.90 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 6.76 |  |  |  |  | 0.00
2016 |  |  |  | 7324.84 |  |  | 7529 |  |  |  | 1012 | [10 empty] | 87.29 |  |  |  | 87.29 | [5 empty] | 82.40 |  |  | 85.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.71 |  |  |  |  | 0.00
2017 |  |  |  | 7521.75 |  |  | 7563 |  |  |  | 1012 | [10 empty] | 84.95 |  |  |  | 85.72 | [5 empty] | 84.85 |  |  | 86.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.28 |  |  |  |  | 0.77
2018 |  |  |  | 8472.42 |  |  | 8483 |  |  |  | 1012 | [10 empty] | 97.62 |  |  |  | 98.08 | [5 empty] | 95.57 |  |  | 96.84 |  |  |  | 0.48 |  | 0.47 | [8 empty] | 1.45 |  |  |  |  | 0.46
2019 |  |  |  | 7965.85 |  |  | 7963 |  |  |  | 1012 | [10 empty] | 90.97 |  |  |  | 91.45 | [5 empty] | 89.86 |  |  | 90.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.55 |  |  |  |  | 0.48
2020 |  |  |  | 8418.73 |  |  | 8376 |  |  |  | 1012 | [10 empty] | 99.62 |  |  |  | 99.93 | [5 empty] | 94.71 |  |  | 95.36 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.03 |  |  |  |  | 0.31
2021 |  |  |  | 7663.47 |  |  | 7704 |  |  |  | 1012 | [10 empty] | 85.78 |  |  |  | 86.96 | [5 empty] | 86.45 |  |  | 87.95 |  |  |  | 1.70 |  | 1.50 | [8 empty] | 11.54 |  |  |  |  | 1.18
2022 |  |  |  | 8301.13 |  |  | 8219 |  |  |  | 1012 | [10 empty] | 92.15 |  |  |  | 93.24 | [5 empty] | 93.64 |  |  | 93.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.76 |  |  |  |  | 1.09
2023 |  |  |  | 8882.44 |  |  | 8760 |  |  |  | 1012 | [10 empty] | 99.03 |  |  |  | 100.00 | [5 empty] | 100.20 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.97
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2015 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 17
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 565
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 9
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 88
Subtotal | [37 empty] | 574 |  |  |  | 17 | [11 empty] | 88
Total | [22 empty] | 0 | [14 empty] | 679
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2015 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 42
41. |  |  | Main Generator Systems | [34 empty] | 13
Total | [37 empty] | 58

## FUQING-1
2023 Operating Experience
CN-20 | [8 empty] | FUQING-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-11-21
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-08-20
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2014-11-22
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8746.94 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.59 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 99.85 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.41 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 748.45 | 675.85 |  |  |  | 748.24 |  | 723.87 | [8 empty] | 744.43 |  |  | 712.07 | [6 empty] | 733.86 |  | 733.94 |  |  |  | 713.39 |  |  | 742.24 |  |  | 722.39 | [9 empty] | 748.21 |  |  | 8746.94
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 98.90 | [6 empty] | 98.64 |  | 98.65 |  |  |  | 99.08 |  |  | 99.78 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.59
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 100.60 | 100.57 |  |  |  | 100.57 |  | 100.54 | [8 empty] | 100.06 |  |  | 98.90 | [6 empty] | 98.64 |  | 98.65 |  |  |  | 99.08 |  |  | 99.76 |  |  | 100.33 | [9 empty] | 100.57 |  |  | 99.85
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.10 | [6 empty] | 1.36 |  | 1.35 |  |  |  | 0.92 |  |  | 0.22 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.41
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 67943.45 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.2 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.08 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.44 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.19 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.04 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.29 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.29 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2014 |  |  |  | 1033.07 |  |  | 949 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 109.00 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 6032.38 |  |  | 6514 |  |  |  | 1000 | [10 empty] | 74.11 |  |  |  | 74.11 | [5 empty] | 68.86 |  |  | 74.36 |  |  |  | 1.98 |  | 3.77 | [8 empty] | 22.12 |  |  |  |  | 0.00
2016 |  |  |  | 6662.04 |  |  | 7511 |  |  |  | 1000 | [10 empty] | 99.31 |  |  |  | 99.31 | [5 empty] | 75.84 |  |  | 85.51 |  |  |  | 0.20 |  | 0.20 | [8 empty] | 0.50 |  |  |  |  | 0.00
2017 |  |  |  | 7535.41 |  |  | 7930 |  |  |  | 1000 | [10 empty] | 89.81 |  |  |  | 89.81 | [5 empty] | 86.02 |  |  | 90.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.19 |  |  |  |  | 0.00
2018 |  |  |  | 7398.98 |  |  | 7702 |  |  |  | 1000 | [10 empty] | 86.59 |  |  |  | 86.78 | [5 empty] | 84.46 |  |  | 87.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.22 |  |  |  |  | 0.19
2019 |  |  |  | 6417.64 |  |  | 7072 |  |  |  | 1000 | [10 empty] | 88.64 |  |  |  | 89.03 | [5 empty] | 73.26 |  |  | 80.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.97 |  |  |  |  | 0.39
2020 |  |  |  | 8222.85 |  |  | 8706 |  |  |  | 1000 | [10 empty] | 98.58 |  |  |  | 99.30 | [5 empty] | 93.61 |  |  | 99.11 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.70 |  |  |  |  | 0.72
2021 |  |  |  | 7967.88 |  |  | 8166 |  |  |  | 1000 | [10 empty] | 91.98 |  |  |  | 92.54 | [5 empty] | 90.96 |  |  | 93.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.46 |  |  |  |  | 0.56
2022 |  |  |  | 7927.14 |  |  | 8001 |  |  |  | 1000 | [10 empty] | 90.32 |  |  |  | 90.73 | [5 empty] | 90.49 |  |  | 91.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.27 |  |  |  |  | 0.40
2023 |  |  |  | 8746.94 |  |  | 8760 |  |  |  | 1000 | [10 empty] | 99.59 |  |  |  | 100.00 | [5 empty] | 99.85 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.41
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2014 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 36
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 672
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 238
Subtotal | [37 empty] | 672 |  |  |  | 36 | [11 empty] | 238
Total | [22 empty] | 0 | [14 empty] | 946
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2014 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 7
16. |  |  | Steam generation systems | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 22
Total | [37 empty] | 45

## FUQING-2
2023 Operating Experience
CN-21 | [8 empty] | FUQING-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-06-17
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-08-06
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-10-16
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7775.95 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.19 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.93 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.07 %
Load Factor (LF) | [18 empty] | : | 88.77 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.73 %
Operating Factor (OF) | [18 empty] | : | 90.1 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 867 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 438.83 | 665.34 |  |  |  | 747.53 |  | 723.53 | [8 empty] | 476.80 |  |  | 357.11 | [6 empty] | 728.22 |  | 735.91 |  |  |  | 688.69 |  |  | 742.81 |  |  | 723.08 | [9 empty] | 748.10 |  |  | 7775.95
EAF [%] |  |  |  |  | 100.00 | 98.60 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 63.93 |  |  | 49.60 | [6 empty] | 97.88 |  | 98.91 |  |  |  | 97.62 |  |  | 99.72 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.19
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 64.90 |  |  | 50.20 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.93
LF [%] |  |  |  |  | 58.98 | 99.01 |  |  |  | 100.47 |  | 100.49 | [8 empty] | 64.09 |  |  | 49.60 | [6 empty] | 97.88 |  | 98.91 |  |  |  | 95.65 |  |  | 99.84 |  |  | 100.43 | [9 empty] | 100.55 |  |  | 88.77
OF [%] |  |  |  |  | 66.94 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 60.48 |  |  | 54.58 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.10
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 35.10 |  |  | 49.80 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.07
XUF [%] |  |  |  |  | 0.00 | 1.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.97 |  |  | 0.60 | [6 empty] | 2.12 |  | 1.09 |  |  |  | 2.38 |  |  | 0.28 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.73
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 61825.3 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.84 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.48 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.77 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.35 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.35 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.4 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.27 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 2017.22 |  |  | 3487 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 87.75 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6070.84 |  |  | 6807 |  |  |  | 1000 | [10 empty] | 81.46 |  |  |  | 81.46 | [5 empty] | 69.11 |  |  | 77.49 |  |  |  | 0.34 |  | 0.27 | [8 empty] | 18.26 |  |  |  |  | 0.00
2017 |  |  |  | 7416.83 |  |  | 7659 |  |  |  | 1000 | [10 empty] | 86.58 |  |  |  | 86.58 | [5 empty] | 84.67 |  |  | 87.43 |  |  |  | 3.03 |  | 2.71 | [8 empty] | 10.71 |  |  |  |  | 0.00
2018 |  |  |  | 7255.87 |  |  | 7587 |  |  |  | 1000 | [10 empty] | 84.82 |  |  |  | 84.97 | [5 empty] | 82.83 |  |  | 86.61 |  |  |  | 3.06 |  | 2.68 | [8 empty] | 12.34 |  |  |  |  | 0.16
2019 |  |  |  | 7893.35 |  |  | 8685 |  |  |  | 1000 | [10 empty] | 98.89 |  |  |  | 99.35 | [5 empty] | 90.11 |  |  | 99.14 |  |  |  | 0.65 |  | 0.65 | [8 empty] | 0.00 |  |  |  |  | 0.46
2020 |  |  |  | 7726.34 |  |  | 8137 |  |  |  | 1000 | [10 empty] | 91.54 |  |  |  | 92.02 | [5 empty] | 87.96 |  |  | 92.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.98 |  |  |  |  | 0.49
2021 |  |  |  | 7482.49 |  |  | 7781 |  |  |  | 1000 | [10 empty] | 87.73 |  |  |  | 88.17 | [5 empty] | 85.42 |  |  | 88.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.83 |  |  |  |  | 0.43
2022 |  |  |  | 8194.52 |  |  | 8610 |  |  |  | 1000 | [10 empty] | 99.05 |  |  |  | 100.00 | [5 empty] | 93.54 |  |  | 98.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.95
2023 |  |  |  | 7775.95 |  |  | 7893 |  |  |  | 1000 | [10 empty] | 92.19 |  |  |  | 92.93 | [5 empty] | 88.77 |  |  | 90.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.07 |  |  |  |  | 0.73
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2015 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 59
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 583 | [14 empty] | 681
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 298 | [19 empty] | 117
Subtotal | [22 empty] | 583 | [10 empty] | 298 |  |  |  | 681 |  |  |  | 59 | [11 empty] | 117
Total | [22 empty] | 881 | [14 empty] | 857
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2015 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
33. |  |  | Circulating Water System | [34 empty] | 46
34. |  |  | Miscellaneous Systems | [34 empty] | 18
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [37 empty] | 74

## FUQING-3
2023 Operating Experience
CN-42 | [8 empty] | FUQING-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-12-31
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-09-07
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-10-24
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7576.01 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.42 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.46 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.54 %
Load Factor (LF) | [18 empty] | : | 86.48 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.04 %
Operating Factor (OF) | [18 empty] | : | 88.95 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 968 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 355.08 | 668.70 |  |  |  | 483.03 |  | 315.86 | [8 empty] | 701.97 |  |  | 710.63 | [6 empty] | 721.34 |  | 731.16 |  |  |  | 685.54 |  |  | 739.70 |  |  | 719.70 | [9 empty] | 743.30 |  |  | 7576.01
EAF [%] |  |  |  |  | 98.66 | 99.36 |  |  |  | 64.89 |  | 43.82 | [8 empty] | 100.00 |  |  | 98.68 | [6 empty] | 96.93 |  | 98.26 |  |  |  | 96.89 |  |  | 99.48 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.42
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 64.89 |  | 44.56 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.46
LF [%] |  |  |  |  | 47.73 | 99.51 |  |  |  | 64.92 |  | 43.87 | [8 empty] | 94.35 |  |  | 98.70 | [6 empty] | 96.95 |  | 98.27 |  |  |  | 95.21 |  |  | 99.42 |  |  | 99.96 | [9 empty] | 99.91 |  |  | 86.48
OF [%] |  |  |  |  | 54.03 | 100.00 |  |  |  | 65.59 |  | 48.61 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.95
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 35.11 |  | 55.44 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.54
XUF [%] |  |  |  |  | 1.34 | 0.64 |  |  |  | 0.00 |  | 0.73 | [8 empty] | 0.00 |  |  | 1.32 | [6 empty] | 3.07 |  | 1.74 |  |  |  | 3.11 |  |  | 0.52 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.04
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 50714.92 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.11 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.1 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.57 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.33 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.79 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.48 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.95 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 1628.31 |  |  | 1648 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 98.60 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6110.93 |  |  | 6592 |  |  |  | 1000 | [10 empty] | 82.12 |  |  |  | 82.12 | [5 empty] | 69.76 |  |  | 75.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.88 |  |  |  |  | 0.00
2018 |  |  |  | 7013.40 |  |  | 7357 |  |  |  | 1000 | [10 empty] | 88.67 |  |  |  | 88.88 | [5 empty] | 80.06 |  |  | 83.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.12 |  |  |  |  | 0.21
2019 |  |  |  | 7390.94 |  |  | 8107 |  |  |  | 1000 | [10 empty] | 95.23 |  |  |  | 95.78 | [5 empty] | 84.37 |  |  | 92.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.22 |  |  |  |  | 0.55
2020 |  |  |  | 7265.42 |  |  | 7724 |  |  |  | 1000 | [10 empty] | 88.61 |  |  |  | 89.24 | [5 empty] | 82.71 |  |  | 87.93 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 10.56 |  |  |  |  | 0.63
2021 |  |  |  | 7184.22 |  |  | 7835 |  |  |  | 1000 | [10 empty] | 90.97 |  |  |  | 91.13 | [5 empty] | 82.01 |  |  | 89.44 |  |  |  | 0.55 |  | 0.51 | [8 empty] | 8.36 |  |  |  |  | 0.17
2022 |  |  |  | 8011.27 |  |  | 8369 |  |  |  | 1000 | [10 empty] | 99.16 |  |  |  | 100.00 | [5 empty] | 91.45 |  |  | 95.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.84
2023 |  |  |  | 7576.01 |  |  | 7792 |  |  |  | 1000 | [10 empty] | 91.42 |  |  |  | 92.46 | [5 empty] | 86.48 |  |  | 88.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.54 |  |  |  |  | 1.04
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2016 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 6
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 626 | [14 empty] | 683
H. |  | Nuclear regulatory requirements | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 351 | [19 empty] | 367
Subtotal | [22 empty] | 626 | [10 empty] | 351 |  |  |  | 683 |  |  |  | 6 | [11 empty] | 368
Total | [22 empty] | 977 | [14 empty] | 1057
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2016 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [34 empty] | 115
Total | [37 empty] | 115

## FUQING-4
2023 Operating Experience
CN-43 | [8 empty] | FUQING-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2012-11-17
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2017-07-29
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2017-09-17
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 6 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5665.02 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 66.78 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.05 %
Unit Capability Factor (UCF) | [18 empty] | : | 67.26 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 32.68 %
Load Factor (LF) | [18 empty] | : | 64.67 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.48 %
Operating Factor (OF) | [18 empty] | : | 65.4 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3031 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 745.11 | 674.02 |  |  |  | 745.86 |  | 720.73 | [8 empty] | 742.65 |  |  | 710.37 | [6 empty] | 729.65 |  | 378.79 |  |  |  | 217.84 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5665.02
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 98.68 | [6 empty] | 98.06 |  | 50.92 |  |  |  | 43.25 |  |  | 12.90 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 66.78
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 51.99 |  |  |  | 44.64 |  |  | 12.90 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 67.26
LF [%] |  |  |  |  | 100.15 | 100.30 |  |  |  | 100.25 |  | 100.10 | [8 empty] | 99.82 |  |  | 98.66 | [6 empty] | 98.07 |  | 50.91 |  |  |  | 30.26 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 64.67
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 52.69 |  |  |  | 34.58 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 65.40
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.64 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 48.01 |  |  |  | 54.72 |  |  | 87.10 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 32.68
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.32 | [6 empty] | 1.94 |  | 1.07 |  |  |  | 1.39 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.48
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 44172.36 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.14 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.62 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.13 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.03 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.84 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.01 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.41 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.69 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2017 |  |  |  | 2540.07 |  |  | 2544 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.00 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 6682.09 |  |  | 6890 |  |  |  | 1000 | [10 empty] | 77.79 |  |  |  | 77.91 | [5 empty] | 76.28 |  |  | 78.65 |  |  |  | 0.98 |  | 0.77 | [8 empty] | 21.32 |  |  |  |  | 0.12
2019 |  |  |  | 6599.78 |  |  | 7215 |  |  |  | 1000 | [10 empty] | 91.31 |  |  |  | 91.68 | [5 empty] | 75.34 |  |  | 82.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.32 |  |  |  |  | 0.36
2020 |  |  |  | 6587.82 |  |  | 6953 |  |  |  | 1000 | [10 empty] | 92.01 |  |  |  | 92.47 | [5 empty] | 75.00 |  |  | 79.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.53 |  |  |  |  | 0.45
2021 |  |  |  | 8297.78 |  |  | 8407 |  |  |  | 1000 | [10 empty] | 99.44 |  |  |  | 100.00 | [5 empty] | 94.72 |  |  | 95.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.56
2022 |  |  |  | 7799.96 |  |  | 7904 |  |  |  | 1000 | [10 empty] | 88.99 |  |  |  | 89.60 | [5 empty] | 89.04 |  |  | 90.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.40 |  |  |  |  | 0.61
2023 |  |  |  | 5665.02 |  |  | 5729 |  |  |  | 1000 | [10 empty] | 66.78 |  |  |  | 67.26 | [5 empty] | 64.67 |  |  | 65.40 |  |  |  | 0.00 |  | 0.05 | [8 empty] | 32.68 |  |  |  |  | 0.48
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2017 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 9
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 725 | [14 empty] | 778
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 194 | [19 empty] | 443
Z. |  | Other | [20 empty] | 2112 | [14 empty] | 352
Subtotal | [22 empty] | 2837 | [10 empty] | 194 |  |  |  | 1130 |  |  |  | 9 | [11 empty] | 443
Total | [22 empty] | 3031 | [14 empty] | 1582
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2017 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 265
Total | [37 empty] | 274

## FUQING-5
2023 Operating Experience
CN-51 | [8 empty] | FUQING-5 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / HPR1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2015-05-07
Thermal power | [12 empty] | : |  |  | 3050 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-11-27
Gross electrical power | [12 empty] | : |  |  | 1161 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-01-30
Reference unit power (net) | [12 empty] | : |  |  | 1075 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.328 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | NA
| Active core height/length [m] | [13 empty] | : |  |  | 3.567 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.12 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 69 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8433.14 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.56 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8 %
Load Factor (LF) | [18 empty] | : | 89.55 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.45 %
Operating Factor (OF) | [18 empty] | : | 92.4 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 666 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 728.19 | 719.45 |  |  |  | 797.04 |  | 767.94 | [8 empty] | 428.87 |  |  | 367.82 | [6 empty] | 764.63 |  | 773.23 |  |  |  | 737.09 |  |  | 784.33 |  |  | 766.93 | [9 empty] | 797.62 |  |  | 8433.14
EAF [%] |  |  |  |  | 100.00 | 99.59 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 54.17 |  |  | 47.54 | [6 empty] | 95.57 |  | 96.68 |  |  |  | 95.29 |  |  | 98.08 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.56
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 55.02 |  |  | 49.15 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.00
LF [%] |  |  |  |  | 91.05 | 99.59 |  |  |  | 99.66 |  | 99.22 | [8 empty] | 53.62 |  |  | 47.52 | [6 empty] | 95.60 |  | 96.68 |  |  |  | 95.23 |  |  | 98.07 |  |  | 99.09 | [9 empty] | 99.73 |  |  | 89.55
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 55.91 |  |  | 53.06 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.40
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 44.98 |  |  | 50.85 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.00
XUF [%] |  |  |  |  | 0.00 | 0.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.85 |  |  | 1.62 | [6 empty] | 4.43 |  | 3.32 |  |  |  | 4.71 |  |  | 1.92 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.45
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 23708.58 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.7 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.47 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.59 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.56 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.85 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.13 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.09 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.2 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2021 |  |  |  | 8461.95 |  |  | 7965 |  |  |  | 1075 | [10 empty] | 91.50 |  |  |  | 92.11 | [5 empty] | 88.97 |  |  | 90.08 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 7.68 |  |  |  |  | 0.61
2022 |  |  |  | 6721.77 |  |  | 6441 |  |  |  | 1075 | [10 empty] | 74.86 |  |  |  | 76.03 | [5 empty] | 71.38 |  |  | 73.53 |  |  |  | 5.23 |  | 13.20 | [8 empty] | 10.78 |  |  |  |  | 1.17
2023 |  |  |  | 8433.14 |  |  | 8094 |  |  |  | 1075 | [10 empty] | 90.56 |  |  |  | 92.00 | [5 empty] | 89.55 |  |  | 92.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.00 |  |  |  |  | 1.45
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2021 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 115
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 666 | [14 empty] | 763
E. |  | Testing of plant systems or components | [35 empty] | 181
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 131
L. |  | Human factor related | [39 empty] | 11
Z. |  | Other | [39 empty] | 270
Subtotal | [22 empty] | 666 | [14 empty] | 944 |  |  |  | 396 | [11 empty] | 131
Total | [22 empty] | 666 | [14 empty] | 1471
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2021 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [34 empty] | 486
Total | [37 empty] | 486

## FUQING-6
2023 Operating Experience
CN-52 | [8 empty] | FUQING-6 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Owner | [7 empty] | : | FQNP (CNNC Fujian Fuqing Nuclear Power Co., LTD)
Reactor Supplier | [7 empty] | : | NPIC (Nuclear Power Institute of China)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / HPR1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2015-12-22
Thermal power | [12 empty] | : |  |  | 3060 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2022-01-01
Gross electrical power | [12 empty] | : |  |  | 1150 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2022-03-25
Reference unit power (net) | [12 empty] | : |  |  | 1075 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46410 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.228 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.5
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.38 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7371.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 79.29 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 81 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 17.97 %
Load Factor (LF) | [18 empty] | : | 78.28 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.72 %
Operating Factor (OF) | [18 empty] | : | 81.16 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1650 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 489.28 | 0.00 |  |  |  | 10.02 |  | 758.32 | [8 empty] | 756.98 |  |  | 745.78 | [6 empty] | 763.85 |  | 771.52 |  |  |  | 735.45 |  |  | 781.79 |  |  | 763.75 | [9 empty] | 794.67 |  |  | 7371.42
EAF [%] |  |  |  |  | 64.52 | 0.00 |  |  |  | 1.74 |  | 98.48 | [8 empty] | 100.00 |  |  | 96.68 | [6 empty] | 95.46 |  | 96.46 |  |  |  | 95.02 |  |  | 97.75 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 79.29
UCF [%] |  |  |  |  | 64.52 | 0.00 |  |  |  | 2.99 |  | 99.12 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.00
LF [%] |  |  |  |  | 61.18 | 0.00 |  |  |  | 1.25 |  | 97.97 | [8 empty] | 94.65 |  |  | 96.35 | [6 empty] | 95.51 |  | 96.46 |  |  |  | 95.02 |  |  | 97.75 |  |  | 98.68 | [9 empty] | 99.36 |  |  | 78.28
OF [%] |  |  |  |  | 64.52 | 0.00 |  |  |  | 4.03 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.16
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 11.22 |  | 0.88 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.02
PUF [%] |  |  |  |  | 35.48 | 100.00 |  |  |  | 85.80 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 17.97
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.25 |  | 0.64 | [8 empty] | 0.00 |  |  | 3.32 | [6 empty] | 4.54 |  | 3.54 |  |  |  | 4.98 |  |  | 2.25 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.72
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 14027.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.58 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.77 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.64 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.06 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.67 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.23 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2022 |  |  |  | 8810.67 |  |  | 8449 |  |  |  | 1075 | [10 empty] | 95.16 |  |  |  | 96.76 | [5 empty] | 91.74 |  |  | 95.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.24 |  |  |  |  | 1.60
2023 |  |  |  | 7371.42 |  |  | 7110 |  |  |  | 1075 | [10 empty] | 79.29 |  |  |  | 81.00 | [5 empty] | 78.28 |  |  | 81.16 |  |  |  | 0.00 |  | 1.02 | [8 empty] | 17.97 |  |  |  |  | 1.72
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2022 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1560 | [14 empty] | 891
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 61
Z. |  | Other | [24 empty] | 90 | [10 empty] | 117 |  |  |  | 51
Subtotal | [22 empty] | 1560 |  |  |  | 90 | [10 empty] | 1008 |  |  |  | 51 | [11 empty] | 61
Total | [22 empty] | 1650 | [14 empty] | 1120
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2022 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [19 empty] | 90 | [14 empty] | 98
Total | [22 empty] | 90 | [14 empty] | 98

## HAIYANG-1
2023 Operating Experience
CN-30 | [8 empty] | HAIYANG-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SDNPC (Shandong Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | CPIG (China Power Investment Group)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / AP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-09-24
Thermal power | [12 empty] | : |  |  | 3415 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-08-17
Gross electrical power | [12 empty] | : |  |  | 1250 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-10-22
Reference unit power (net) | [12 empty] | : |  |  | 1170 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.513
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321.11
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.407
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.7239 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.76 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 4.2672 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.76 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 69 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8971.59 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.65 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.95 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.04 %
Load Factor (LF) | [18 empty] | : | 87.53 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.31 %
Operating Factor (OF) | [18 empty] | : | 89.98 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 878 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 565.8 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 859.77 | 774.59 |  |  |  | 515.10 |  | 414.07 | [8 empty] | 827.43 |  |  | 830.63 | [6 empty] | 858.67 |  | 846.87 |  |  |  | 830.69 |  |  | 834.74 |  |  | 531.83 | [9 empty] | 847.21 |  |  | 8971.59
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 60.42 |  | 53.02 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 99.99 |  | 99.31 |  |  |  | 100.00 |  |  | 98.40 |  |  | 65.31 | [9 empty] | 99.03 |  |  | 89.65
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 60.42 |  | 53.02 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 100.00 |  |  | 99.60 |  |  | 66.11 | [9 empty] | 100.00 |  |  | 89.95
LF [%] |  |  |  |  | 98.77 | 98.52 |  |  |  | 59.17 |  | 49.15 | [8 empty] | 95.05 |  |  | 98.60 | [6 empty] | 98.64 |  | 97.29 |  |  |  | 98.61 |  |  | 95.89 |  |  | 63.13 | [9 empty] | 97.33 |  |  | 87.53
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 62.10 |  | 51.94 | [8 empty] | 96.51 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 68.89 | [9 empty] | 100.00 |  |  | 89.98
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 39.58 |  | 46.98 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.40 |  |  | 33.89 | [9 empty] | 0.00 |  |  | 10.04
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.69 |  |  |  | 0.00 |  |  | 1.19 |  |  | 0.80 | [9 empty] | 0.96 |  |  | 0.31
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 48591.31 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.78 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.71 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.73 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.62 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.56 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.93 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.94 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 2746.03 |  |  | 2870 |  |  |  | 1170 | [10 empty] | 94.20 |  |  |  | 94.20 | [5 empty] | 93.91 |  |  | 95.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.80 |  |  |  |  | 0.00
2019 |  |  |  | 9456.75 |  |  | 8221 |  |  |  | 1170 | [10 empty] | 96.46 |  |  |  | 97.39 | [5 empty] | 92.27 |  |  | 93.85 |  |  |  | 0.16 |  | 0.16 | [8 empty] | 2.45 |  |  |  |  | 0.93
2020 |  |  |  | 8762.30 |  |  | 7701 |  |  |  | 1170 | [10 empty] | 85.68 |  |  |  | 86.31 | [5 empty] | 85.26 |  |  | 87.67 |  |  |  | 0.31 |  | 0.27 | [8 empty] | 13.42 |  |  |  |  | 0.63
2021 |  |  |  | 9133.85 |  |  | 8030 |  |  |  | 1170 | [10 empty] | 91.78 |  |  |  | 92.90 | [5 empty] | 89.12 |  |  | 91.67 |  |  |  | 0.30 |  | 0.28 | [8 empty] | 6.82 |  |  |  |  | 1.12
2022 |  |  |  | 9520.82 |  |  | 8409 |  |  |  | 1170 | [10 empty] | 94.61 |  |  |  | 96.45 | [5 empty] | 92.89 |  |  | 95.99 |  |  |  | 3.08 |  | 3.06 | [8 empty] | 0.49 |  |  |  |  | 1.83
2023 |  |  |  | 8971.59 |  |  | 7882 |  |  |  | 1170 | [10 empty] | 89.65 |  |  |  | 89.95 | [5 empty] | 87.53 |  |  | 89.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.04 |  |  |  |  | 0.31
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2018 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 48
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 633 | [14 empty] | 436
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 123
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 247 | [14 empty] | 48
I. |  | Grid capacity limitation | [31 empty] | 48 | [19 empty] | 56
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 64
L. |  | Human factor related | [39 empty] | 1
Subtotal | [22 empty] | 880 | [10 empty] | 48 |  |  |  | 607 |  |  |  | 49 | [11 empty] | 120
Total | [22 empty] | 928 | [14 empty] | 776
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2018 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [19 empty] | 48 | [14 empty] | 53
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 46
Total | [22 empty] | 48 | [14 empty] | 100

## HAIYANG-2
2023 Operating Experience
CN-31 | [8 empty] | HAIYANG-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SDNPC (Shandong Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | CPIG (China Power Investment Group)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / AP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-06-20
Thermal power | [12 empty] | : |  |  | 3415 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-10-13
Gross electrical power | [12 empty] | : |  |  | 1250 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2019-01-09
Reference unit power (net) | [12 empty] | : |  |  | 1170 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.513
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321.11
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.407
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.7239 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.76 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 4.2672 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.76 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 69 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 9032.01 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.53 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.23 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.48 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.39 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.13 %
Load Factor (LF) | [18 empty] | : | 88.12 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.16 %
Operating Factor (OF) | [18 empty] | : | 90.18 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 860 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 161.7 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 530.20 | 360.95 |  |  |  | 863.61 |  | 834.69 | [8 empty] | 854.94 |  |  | 789.78 | [6 empty] | 859.30 |  | 849.64 |  |  |  | 771.12 |  |  | 686.75 |  |  | 783.24 | [9 empty] | 847.79 |  |  | 9032.01
EAF [%] |  |  |  |  | 61.54 | 42.04 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 95.08 | [6 empty] | 100.00 |  | 99.42 |  |  |  | 92.89 |  |  | 81.45 |  |  | 95.97 | [9 empty] | 98.67 |  |  | 89.23
UCF [%] |  |  |  |  | 61.54 | 42.04 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 95.08 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 92.89 |  |  | 81.45 |  |  | 95.97 | [9 empty] | 100.00 |  |  | 89.39
LF [%] |  |  |  |  | 60.91 | 45.91 |  |  |  | 99.21 |  | 99.08 | [8 empty] | 98.21 |  |  | 93.75 | [6 empty] | 98.72 |  | 97.61 |  |  |  | 91.54 |  |  | 78.89 |  |  | 92.98 | [9 empty] | 97.39 |  |  | 88.12
OF [%] |  |  |  |  | 62.37 | 44.49 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 96.39 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 96.11 |  |  | 81.18 |  |  | 98.19 | [9 empty] | 100.00 |  |  | 90.18
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.86 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 4.03 | [9 empty] | 0.00 |  |  | 0.53
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.81 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 4.03 | [9 empty] | 0.00 |  |  | 0.48
PUF [%] |  |  |  |  | 38.46 | 57.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 3.11 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 7.11 |  |  | 18.55 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.13
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.58 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 1.33 |  |  | 0.16
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 47894.25 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.64 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 93.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.61 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.99 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 5.4 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.7 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 94.13 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2019 |  |  |  | 9935.22 |  |  | 8711 |  |  |  | 1170 | [10 empty] | 97.38 |  |  |  | 98.43 | [5 empty] | 96.94 |  |  | 99.44 |  |  |  | 1.25 |  | 1.25 | [8 empty] | 0.32 |  |  |  |  | 1.05
2020 |  |  |  | 9066.38 |  |  | 7983 |  |  |  | 1170 | [10 empty] | 89.33 |  |  |  | 89.91 | [5 empty] | 88.22 |  |  | 90.88 |  |  |  | 0.44 |  | 0.40 | [8 empty] | 9.69 |  |  |  |  | 0.58
2021 |  |  |  | 9286.00 |  |  | 8139 |  |  |  | 1170 | [10 empty] | 92.49 |  |  |  | 93.32 | [5 empty] | 90.60 |  |  | 92.91 |  |  |  | 0.33 |  | 0.31 | [8 empty] | 6.38 |  |  |  |  | 0.83
2022 |  |  |  | 9773.92 |  |  | 8519 |  |  |  | 1170 | [10 empty] | 98.04 |  |  |  | 98.92 | [5 empty] | 95.36 |  |  | 97.25 |  |  |  | 0.61 |  | 0.61 | [8 empty] | 0.47 |  |  |  |  | 0.88
2023 |  |  |  | 9032.01 |  |  | 7900 |  |  |  | 1170 | [10 empty] | 89.23 |  |  |  | 89.39 | [5 empty] | 88.12 |  |  | 90.18 |  |  |  | 0.53 |  | 0.48 | [8 empty] | 10.13 |  |  |  |  | 0.16
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2019 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 40 | [14 empty] | 33
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 678 | [14 empty] | 387
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 92
E. |  | Testing of plant systems or components | [35 empty] | 19
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [20 empty] | 211 | [14 empty] | 42
I. |  | Grid capacity limitation | [51 empty] | 51
L. |  | Human factor related | [39 empty] | 66
Subtotal | [22 empty] | 889 |  |  |  | 40 | [10 empty] | 540 |  |  |  | 99 | [11 empty] | 51
Total | [22 empty] | 929 | [14 empty] | 690
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2019 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [19 empty] | 40 | [14 empty] | 19
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 65
34. |  |  | Miscellaneous Systems | [34 empty] | 49
Total | [22 empty] | 40 | [14 empty] | 142

## HONGYANHE-1
2023 Operating Experience
CN-16 | [8 empty] | HONGYANHE-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Owner | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-08-18
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2013-02-17
Gross electrical power | [12 empty] | : |  |  | 1119 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2013-06-06
Reference unit power (net) | [12 empty] | : |  |  | 1061 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 10 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.11
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7084.46 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.19 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.71 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.83 %
Unit Capability Factor (UCF) | [18 empty] | : | 80.5 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 14.67 %
Load Factor (LF) | [18 empty] | : | 76.22 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.79 %
Operating Factor (OF) | [18 empty] | : | 80.72 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1689 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 678.10 | 693.49 |  |  |  | 778.69 |  | 680.51 | [8 empty] | 758.10 |  |  | 739.32 | [6 empty] | 588.08 |  | 744.47 |  |  |  | 550.88 |  |  | 0.00 |  |  | 90.00 | [9 empty] | 782.81 |  |  | 7084.46
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 96.04 |  |  | 96.78 | [6 empty] | 74.50 |  | 94.31 |  |  |  | 72.11 |  |  | 0.00 |  |  | 11.78 | [9 empty] | 100.00 |  |  | 78.71
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 78.73 |  | 100.00 |  |  |  | 76.33 |  |  | 0.00 |  |  | 11.78 | [9 empty] | 100.00 |  |  | 80.50
LF [%] |  |  |  |  | 85.90 | 97.27 |  |  |  | 98.65 |  | 89.08 | [8 empty] | 96.04 |  |  | 96.78 | [6 empty] | 74.50 |  | 94.31 |  |  |  | 72.11 |  |  | 0.00 |  |  | 11.78 | [9 empty] | 99.17 |  |  | 76.22
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 96.94 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 79.30 |  | 100.00 |  |  |  | 76.67 |  |  | 0.00 |  |  | 16.53 | [9 empty] | 100.00 |  |  | 80.72
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 21.27 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.19
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 21.27 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 36.73 | [9 empty] | 0.00 |  |  | 4.83
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 23.67 |  |  | 100.00 |  |  | 51.49 | [9 empty] | 0.00 |  |  | 14.67
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.96 |  |  | 3.22 | [6 empty] | 4.23 |  | 5.69 |  |  |  | 4.22 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.79
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 81059.92 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.21 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.1 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.4 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.28 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.32 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.14 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.18 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.16 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2013 |  |  |  | 5683.38 |  |  | 7632 |  |  |  | 1061 | [10 empty] | 98.62 |  |  |  | 99.55 | [5 empty] | 102.41 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.44 |  |  |  |  | 0.94
2014 |  |  |  | 6093.20 |  |  | 6218 |  |  |  | 1061 | [10 empty] | 68.38 |  |  |  | 69.32 | [5 empty] | 65.56 |  |  | 70.98 |  |  |  | 9.71 |  | 7.65 | [8 empty] | 23.03 |  |  |  |  | 0.95
2015 |  |  |  | 7369.75 |  |  | 7756 |  |  |  | 1061 | [10 empty] | 87.80 |  |  |  | 87.80 | [5 empty] | 79.29 |  |  | 88.54 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 12.19 |  |  |  |  | 0.00
2016 |  |  |  | 6066.04 |  |  | 6694 |  |  |  | 1061 | [10 empty] | 86.62 |  |  |  | 86.62 | [5 empty] | 65.09 |  |  | 76.21 |  |  |  | 2.14 |  | 1.93 | [8 empty] | 11.45 |  |  |  |  | 0.00
2017 |  |  |  | 7304.12 |  |  | 7720 |  |  |  | 1061 | [10 empty] | 87.92 |  |  |  | 88.92 | [5 empty] | 78.59 |  |  | 88.13 |  |  |  | 0.43 |  | 0.38 | [8 empty] | 10.69 |  |  |  |  | 1.01
2018 |  |  |  | 8797.86 |  |  | 8760 |  |  |  | 1061 | [10 empty] | 98.55 |  |  |  | 99.98 | [5 empty] | 94.66 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 1.43
2019 |  |  |  | 8077.71 |  |  | 7954 |  |  |  | 1061 | [10 empty] | 88.51 |  |  |  | 90.20 | [5 empty] | 86.91 |  |  | 90.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.80 |  |  |  |  | 1.68
2020 |  |  |  | 7903.95 |  |  | 8033 |  |  |  | 1061 | [10 empty] | 89.65 |  |  |  | 91.10 | [5 empty] | 84.81 |  |  | 91.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.90 |  |  |  |  | 1.44
2021 |  |  |  | 8980.89 |  |  | 8760 |  |  |  | 1061 | [10 empty] | 98.15 |  |  |  | 100.00 | [5 empty] | 96.63 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 1.85
2022 |  |  |  | 7605.00 |  |  | 7696 |  |  |  | 1061 | [10 empty] | 90.56 |  |  |  | 92.32 | [5 empty] | 81.82 |  |  | 87.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.68 |  |  |  |  | 1.76
2023 |  |  |  | 7084.46 |  |  | 7071 |  |  |  | 1061 | [10 empty] | 78.71 |  |  |  | 80.50 | [5 empty] | 76.22 |  |  | 80.72 |  |  |  | 2.19 |  | 4.83 | [8 empty] | 14.67 |  |  |  |  | 1.79
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2013 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 428 | [14 empty] | 101
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1248 | [14 empty] | 772
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 22 | [19 empty] | 166
Subtotal | [22 empty] | 1248 |  |  |  | 428 | [6 empty] | 22 |  |  |  | 772 |  |  |  | 101 | [11 empty] | 166
Total | [22 empty] | 1698 | [14 empty] | 1039
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2013 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 286 | [14 empty] | 65
31. |  |  | Turbine and auxiliaries | [34 empty] | 0
33. |  |  | Circulating Water System | [19 empty] | 163 | [14 empty] | 27
41. |  |  | Main Generator Systems | [34 empty] | 45
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 449 | [14 empty] | 138
Highlights (2023)
At the request of the sate grid,the power was reduced separately for some pe of time

## HONGYANHE-2
2023 Operating Experience
CN-17 | [8 empty] | HONGYANHE-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Owner | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-03-28
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2013-11-23
Gross electrical power | [12 empty] | : |  |  | 1119 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2014-05-13
Reference unit power (net) | [12 empty] | : |  |  | 1061 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 10 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | NA
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8143.39 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.82 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.5 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.71 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.44 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.84 %
Load Factor (LF) | [18 empty] | : | 87.62 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.95 %
Operating Factor (OF) | [18 empty] | : | 92.92 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 620 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 686.38 | 698.15 |  |  |  | 503.19 |  | 494.17 | [8 empty] | 753.82 |  |  | 741.26 | [6 empty] | 571.31 |  | 730.60 |  |  |  | 715.38 |  |  | 722.06 |  |  | 749.83 | [9 empty] | 777.25 |  |  | 8143.39
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 63.74 |  | 66.35 | [8 empty] | 98.69 |  |  | 97.03 | [6 empty] | 75.90 |  | 94.78 |  |  |  | 93.65 |  |  | 96.55 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.50
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 63.74 |  | 66.35 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 79.85 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.44
LF [%] |  |  |  |  | 86.95 | 97.92 |  |  |  | 63.74 |  | 64.69 | [8 empty] | 95.49 |  |  | 97.03 | [6 empty] | 72.37 |  | 92.55 |  |  |  | 93.65 |  |  | 91.47 |  |  | 98.16 | [9 empty] | 98.46 |  |  | 87.62
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 64.52 |  | 70.97 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 80.24 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.92
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 20.15 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.82
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 20.15 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.71
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 36.26 |  | 33.65 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.84
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.31 |  |  | 2.97 | [6 empty] | 3.95 |  | 5.22 |  |  |  | 6.35 |  |  | 3.45 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.95
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 68421.51 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.8 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.75 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.97 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.09 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.94 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.49 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.34 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.56 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2014 |  |  |  | 4963.31 |  |  | 5053 |  |  |  | 1061 | [10 empty] | 81.06 |  |  |  | 81.06 | [5 empty] | 72.46 |  |  | 79.81 |  |  |  | 8.62 |  | 7.64 | [8 empty] | 11.29 |  |  |  |  | 0.00
2015 |  |  |  | 3496.01 |  |  | 3925 |  |  |  | 1061 | [10 empty] | 65.63 |  |  |  | 65.63 | [5 empty] | 37.61 |  |  | 44.81 |  |  |  | 0.16 |  | 0.34 | [8 empty] | 34.03 |  |  |  |  | 0.00
2016 |  |  |  | 5288.78 |  |  | 5542 |  |  |  | 1061 | [10 empty] | 87.53 |  |  |  | 87.53 | [5 empty] | 56.75 |  |  | 63.09 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 12.47 |  |  |  |  | 0.00
2017 |  |  |  | 5790.37 |  |  | 6250 |  |  |  | 1061 | [10 empty] | 95.98 |  |  |  | 98.08 | [5 empty] | 62.30 |  |  | 71.35 |  |  |  | 0.00 |  | 1.53 | [8 empty] | 0.40 |  |  |  |  | 2.10
2018 |  |  |  | 7737.78 |  |  | 7723 |  |  |  | 1061 | [10 empty] | 88.18 |  |  |  | 89.80 | [5 empty] | 83.25 |  |  | 88.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.20 |  |  |  |  | 1.63
2019 |  |  |  | 8077.34 |  |  | 8056 |  |  |  | 1061 | [10 empty] | 89.72 |  |  |  | 91.62 | [5 empty] | 86.91 |  |  | 91.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.38 |  |  |  |  | 1.89
2020 |  |  |  | 7767.35 |  |  | 8018 |  |  |  | 1061 | [10 empty] | 89.29 |  |  |  | 90.88 | [5 empty] | 83.34 |  |  | 91.28 |  |  |  | 0.00 |  | 0.70 | [8 empty] | 8.42 |  |  |  |  | 1.59
2021 |  |  |  | 8195.34 |  |  | 8027 |  |  |  | 1061 | [10 empty] | 89.41 |  |  |  | 91.17 | [5 empty] | 88.18 |  |  | 91.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.83 |  |  |  |  | 1.76
2022 |  |  |  | 8882.06 |  |  | 8760 |  |  |  | 1061 | [10 empty] | 97.96 |  |  |  | 100.00 | [5 empty] | 95.56 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 2.04
2023 |  |  |  | 8143.39 |  |  | 8140 |  |  |  | 1061 | [10 empty] | 90.50 |  |  |  | 92.44 | [5 empty] | 87.62 |  |  | 92.92 |  |  |  | 1.82 |  | 1.71 | [8 empty] | 5.84 |  |  |  |  | 1.95
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2014 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 155 | [14 empty] | 82
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 473 | [14 empty] | 834
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 690
Subtotal | [22 empty] | 473 |  |  |  | 155 | [10 empty] | 834 |  |  |  | 82 | [11 empty] | 690
Total | [22 empty] | 628 | [14 empty] | 1606
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2014 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 13
31. |  |  | Turbine and auxiliaries | [34 empty] | 18
33. |  |  | Circulating Water System | [19 empty] | 155 | [14 empty] | 42
Total | [22 empty] | 155 | [14 empty] | 79
Highlights (2023)
At the request of the sate grid,the power was reduced separately for some pe of time

## HONGYANHE-3
2023 Operating Experience
CN-26 | [8 empty] | HONGYANHE-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Owner | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-03-07
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-03-23
Gross electrical power | [12 empty] | : |  |  | 1119 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-08-16
Reference unit power (net) | [12 empty] | : |  |  | 1061 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.11
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8025.66 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.85 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.82 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.71 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.46 %
Load Factor (LF) | [18 empty] | : | 86.35 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2 %
Operating Factor (OF) | [18 empty] | : | 91.28 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 764 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 423.81 | 366.40 |  |  |  | 779.64 |  | 703.25 | [8 empty] | 751.70 |  |  | 738.98 | [6 empty] | 568.05 |  | 727.36 |  |  |  | 715.31 |  |  | 721.95 |  |  | 751.37 | [9 empty] | 777.84 |  |  | 8025.66
EAF [%] |  |  |  |  | 54.48 | 53.09 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 98.76 |  |  | 96.74 | [6 empty] | 75.64 |  | 94.43 |  |  |  | 93.64 |  |  | 96.76 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.82
UCF [%] |  |  |  |  | 54.48 | 53.09 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 79.84 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.82
LF [%] |  |  |  |  | 53.69 | 51.39 |  |  |  | 98.77 |  | 92.06 | [8 empty] | 95.23 |  |  | 96.74 | [6 empty] | 71.96 |  | 92.14 |  |  |  | 93.64 |  |  | 91.46 |  |  | 98.36 | [9 empty] | 98.54 |  |  | 86.35
OF [%] |  |  |  |  | 54.84 | 58.18 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 80.24 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.28
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 20.16 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.85
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 20.16 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.71
PUF [%] |  |  |  |  | 45.52 | 46.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.46
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.24 |  |  | 3.26 | [6 empty] | 4.20 |  | 5.57 |  |  |  | 6.36 |  |  | 3.24 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 57554.03 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.45 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.26 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.75 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.38 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 73.01 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.61 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.81 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 2322.53 |  |  | 2835 |  |  |  | 1061 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 43.20 |  |  | 47.98 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.01 |  |  |  |  | 0.00
2016 |  |  |  | 5483.99 |  |  | 5764 |  |  |  | 1061 | [10 empty] | 94.69 |  |  |  | 94.69 | [5 empty] | 58.84 |  |  | 65.62 |  |  |  | 0.55 |  | 0.52 | [8 empty] | 4.79 |  |  |  |  | 0.00
2017 |  |  |  | 5631.50 |  |  | 5975 |  |  |  | 1061 | [10 empty] | 80.94 |  |  |  | 82.61 | [5 empty] | 60.59 |  |  | 68.21 |  |  |  | 0.67 |  | 0.56 | [8 empty] | 16.83 |  |  |  |  | 1.67
2018 |  |  |  | 6535.98 |  |  | 6697 |  |  |  | 1061 | [10 empty] | 89.74 |  |  |  | 91.17 | [5 empty] | 70.32 |  |  | 76.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.82 |  |  |  |  | 1.44
2019 |  |  |  | 7491.34 |  |  | 7481 |  |  |  | 1061 | [10 empty] | 82.68 |  |  |  | 84.95 | [5 empty] | 80.60 |  |  | 85.40 |  |  |  | 0.60 |  | 0.51 | [8 empty] | 14.53 |  |  |  |  | 2.27
2020 |  |  |  | 6938.56 |  |  | 7116 |  |  |  | 1061 | [10 empty] | 98.05 |  |  |  | 99.73 | [5 empty] | 74.45 |  |  | 81.01 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 0.18 |  |  |  |  | 1.69
2021 |  |  |  | 7943.87 |  |  | 7670 |  |  |  | 1061 | [10 empty] | 85.80 |  |  |  | 88.06 | [5 empty] | 85.47 |  |  | 87.56 |  |  |  | 0.00 |  | 2.84 | [8 empty] | 9.10 |  |  |  |  | 2.26
2022 |  |  |  | 7198.11 |  |  | 7472 |  |  |  | 1061 | [10 empty] | 89.71 |  |  |  | 91.81 | [5 empty] | 77.45 |  |  | 85.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.19 |  |  |  |  | 2.10
2023 |  |  |  | 8025.66 |  |  | 7996 |  |  |  | 1061 | [10 empty] | 88.82 |  |  |  | 90.82 | [5 empty] | 86.35 |  |  | 91.28 |  |  |  | 1.85 |  | 1.71 | [8 empty] | 7.46 |  |  |  |  | 2.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2015 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 153 | [14 empty] | 58
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 617 | [14 empty] | 706
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1094
Subtotal | [22 empty] | 617 |  |  |  | 153 | [10 empty] | 706 |  |  |  | 58 | [11 empty] | 1094
Total | [22 empty] | 770 | [14 empty] | 1858
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2015 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 295
12. |  |  | Reactor I&C Systems | [34 empty] | 5
33. |  |  | Circulating Water System | [19 empty] | 153 | [14 empty] | 22
Total | [22 empty] | 153 | [14 empty] | 322
Highlights (2023)
At the request of the sate grid,the power was reduced separately for some pe of time

## HONGYANHE-4
2023 Operating Experience
CN-27 | [8 empty] | HONGYANHE-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Owner | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-08-15
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-04-01
Gross electrical power | [12 empty] | : |  |  | 1119 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-06-08
Reference unit power (net) | [12 empty] | : |  |  | 1061 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | NA
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7771.55 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.97 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.41 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.08 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.79 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.13 %
Load Factor (LF) | [18 empty] | : | 83.62 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.38 %
Operating Factor (OF) | [18 empty] | : | 87.39 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1105 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 678.87 | 693.63 |  |  |  | 780.73 |  | 576.90 | [8 empty] | 779.42 |  |  | 741.55 | [6 empty] | 590.60 |  | 526.10 |  |  |  | 114.80 |  |  | 753.79 |  |  | 750.04 | [9 empty] | 785.14 |  |  | 7771.55
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 98.74 |  |  | 97.07 | [6 empty] | 74.82 |  | 66.65 |  |  |  | 15.03 |  |  | 96.58 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.41
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 78.99 |  | 70.58 |  |  |  | 15.69 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.79
LF [%] |  |  |  |  | 86.00 | 97.28 |  |  |  | 98.90 |  | 75.52 | [8 empty] | 98.74 |  |  | 97.07 | [6 empty] | 74.82 |  | 66.65 |  |  |  | 15.03 |  |  | 95.49 |  |  | 98.18 | [9 empty] | 99.46 |  |  | 83.62
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 77.64 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 79.84 |  | 70.97 |  |  |  | 19.72 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.39
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 21.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.97
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 21.01 |  | 0.00 |  |  |  | 3.57 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.08
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 29.42 |  |  |  | 80.74 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.13
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.26 |  |  | 2.93 | [6 empty] | 4.17 |  | 3.94 |  |  |  | 0.66 |  |  | 3.42 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.38
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 49292.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.36 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.27 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.37 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.68 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.95 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 69.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.41 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.2 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 1130.44 |  |  | 1200 |  |  |  | 1000 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 22.01 |  |  | 23.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2017 |  |  |  | 3276.06 |  |  | 3638 |  |  |  | 1061 | [10 empty] | 85.13 |  |  |  | 85.76 | [5 empty] | 35.25 |  |  | 41.53 |  |  |  | 0.17 |  | 0.15 | [8 empty] | 14.10 |  |  |  |  | 0.63
2018 |  |  |  | 5198.53 |  |  | 5361 |  |  |  | 1061 | [10 empty] | 84.08 |  |  |  | 85.16 | [5 empty] | 55.93 |  |  | 61.20 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 14.82 |  |  |  |  | 1.08
2019 |  |  |  | 7117.14 |  |  | 7035 |  |  |  | 1061 | [10 empty] | 90.39 |  |  |  | 92.47 | [5 empty] | 76.57 |  |  | 80.31 |  |  |  | 0.21 |  | 0.20 | [8 empty] | 7.33 |  |  |  |  | 2.09
2020 |  |  |  | 7755.39 |  |  | 8183 |  |  |  | 1061 | [10 empty] | 91.28 |  |  |  | 92.78 | [5 empty] | 83.21 |  |  | 93.16 |  |  |  | 0.37 |  | 0.35 | [8 empty] | 6.87 |  |  |  |  | 1.50
2021 |  |  |  | 8327.55 |  |  | 8177 |  |  |  | 1061 | [10 empty] | 91.15 |  |  |  | 92.83 | [5 empty] | 89.60 |  |  | 93.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.17 |  |  |  |  | 1.68
2022 |  |  |  | 8000.10 |  |  | 8076 |  |  |  | 1061 | [10 empty] | 89.50 |  |  |  | 91.81 | [5 empty] | 86.07 |  |  | 92.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.19 |  |  |  |  | 2.30
2023 |  |  |  | 7771.55 |  |  | 7655 |  |  |  | 1061 | [10 empty] | 87.41 |  |  |  | 88.79 | [5 empty] | 83.62 |  |  | 87.39 |  |  |  | 1.97 |  | 2.08 | [8 empty] | 9.13 |  |  |  |  | 1.38
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2016 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 188 | [14 empty] | 31
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 768 | [14 empty] | 754
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 161 | [19 empty] | 1129
Subtotal | [22 empty] | 768 |  |  |  | 188 | [6 empty] | 161 |  |  |  | 754 |  |  |  | 31 | [11 empty] | 1129
Total | [22 empty] | 1117 | [14 empty] | 1914
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2016 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 187 | [14 empty] | 24
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
33. |  |  | Circulating Water System | [19 empty] | 162 | [14 empty] | 25
Total | [22 empty] | 349 | [14 empty] | 51
Highlights (2023)
At the request of the sate grid,the power was reduced separately for some pe of time

## HONGYANHE-5
2023 Operating Experience
CN-49 | [8 empty] | HONGYANHE-5 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Owner | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / ACPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2015-03-29
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2021-06-25
Gross electrical power | [12 empty] | : |  |  | 1119 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-07-31
Reference unit power (net) | [12 empty] | : |  |  | 1061 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8347.9 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.09 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.91 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.09 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.91 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 89.82 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2 %
Operating Factor (OF) | [18 empty] | : | 95.21 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 420 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 416.17 | 553.59 |  |  |  | 775.73 |  | 702.41 | [8 empty] | 749.19 |  |  | 738.96 | [6 empty] | 687.61 |  | 748.15 |  |  |  | 720.27 |  |  | 724.64 |  |  | 752.37 | [9 empty] | 778.81 |  |  | 8347.90
EAF [%] |  |  |  |  | 98.95 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 98.50 |  |  | 96.73 | [6 empty] | 94.60 |  | 94.78 |  |  |  | 94.29 |  |  | 97.23 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.91
UCF [%] |  |  |  |  | 98.95 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.91
LF [%] |  |  |  |  | 52.72 | 77.64 |  |  |  | 98.27 |  | 91.95 | [8 empty] | 94.91 |  |  | 96.73 | [6 empty] | 87.11 |  | 94.78 |  |  |  | 94.29 |  |  | 91.80 |  |  | 98.49 | [9 empty] | 98.66 |  |  | 89.82
OF [%] |  |  |  |  | 59.68 | 82.14 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.21
FLR [%] |  |  |  |  | 1.05 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.09
UCL [%] |  |  |  |  | 1.05 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.09
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.50 |  |  | 3.27 | [6 empty] | 5.40 |  | 5.22 |  |  |  | 5.71 |  |  | 2.77 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 18341.51 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.04 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 93.48 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 94.97 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 4.99 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.57 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.49 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.31 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2021 |  |  |  | 4718.48 |  |  | 4560 |  |  |  | 1061 | [10 empty] | 97.74 |  |  |  | 100.00 | [5 empty] | 96.93 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 2.26
2022 |  |  |  | 6217.30 |  |  | 6490 |  |  |  | 1061 | [10 empty] | 87.26 |  |  |  | 87.92 | [5 empty] | 66.89 |  |  | 74.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.08 |  |  |  |  | 0.66
2023 |  |  |  | 8347.90 |  |  | 8340 |  |  |  | 1061 | [10 empty] | 97.91 |  |  |  | 99.91 | [5 empty] | 89.82 |  |  | 95.21 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 0.00 |  |  |  |  | 2.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2021 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 424
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 413 | [19 empty] | 686
L. |  | Human factor related | [24 empty] | 8 | [14 empty] | 3
Subtotal | [26 empty] | 8 | [6 empty] | 413 |  |  |  | 424 |  |  |  | 3 | [11 empty] | 686
Total | [22 empty] | 421 | [14 empty] | 1113
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2021 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 420 | [14 empty] | 645
Total | [22 empty] | 420 | [14 empty] | 645
Highlights (2023)
At the request of the sate grid,the power was reduced separately for some pe of time

## HONGYANHE-6
2023 Operating Experience
CN-50 | [8 empty] | HONGYANHE-6 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Owner | [7 empty] | : | LHNPC (Liaoning Hongyanhe Nuclear Power Co. Ltd. (LHNPC))
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / ACPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2015-07-24
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2022-05-02
Gross electrical power | [12 empty] | : |  |  | 1119 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2022-06-23
Reference unit power (net) | [12 empty] | : |  |  | 1061 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7701.66 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.51 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.63 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.34 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.93 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.74 %
Load Factor (LF) | [18 empty] | : | 82.86 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.3 %
Operating Factor (OF) | [18 empty] | : | 87.45 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1099 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 679.35 | 703.61 |  |  |  | 663.31 |  | 743.24 | [8 empty] | 786.13 |  |  | 20.25 | [6 empty] | 362.48 |  | 754.94 |  |  |  | 722.56 |  |  | 728.34 |  |  | 755.65 | [9 empty] | 781.80 |  |  | 7701.66
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 84.28 |  | 100.00 | [8 empty] | 99.59 |  |  | 2.65 | [6 empty] | 53.09 |  | 95.64 |  |  |  | 94.59 |  |  | 97.66 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.63
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 84.28 |  | 100.00 | [8 empty] | 100.00 |  |  | 2.65 | [6 empty] | 56.02 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.93
LF [%] |  |  |  |  | 86.06 | 98.68 |  |  |  | 84.03 |  | 97.29 | [8 empty] | 99.59 |  |  | 2.65 | [6 empty] | 45.92 |  | 95.64 |  |  |  | 94.59 |  |  | 92.27 |  |  | 98.92 | [9 empty] | 99.04 |  |  | 82.86
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 85.22 |  | 100.00 | [8 empty] | 100.00 |  |  | 3.06 | [6 empty] | 60.89 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.45
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 15.72 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.51
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 15.72 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.34
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 97.35 | [6 empty] | 43.98 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 11.74
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.41 |  |  | 0.00 | [6 empty] | 2.93 |  | 4.36 |  |  |  | 5.41 |  |  | 2.34 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.30
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 11938.19 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.05 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.72 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.97 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.8 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.52 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.5 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.8 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2022 |  |  |  | 5000.45 |  |  | 5007 |  |  |  | 1061 | [10 empty] | 97.84 |  |  |  | 99.75 | [5 empty] | 81.83 |  |  | 88.50 |  |  |  | 0.25 |  | 0.25 | [8 empty] | 0.00 |  |  |  |  | 1.91
2023 |  |  |  | 7701.66 |  |  | 7661 |  |  |  | 1061 | [10 empty] | 85.63 |  |  |  | 86.93 | [5 empty] | 82.86 |  |  | 87.45 |  |  |  | 1.51 |  | 1.34 | [8 empty] | 11.74 |  |  |  |  | 1.30
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2022 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 123 | [14 empty] | 85
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 989 | [14 empty] | 659
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 563
Subtotal | [22 empty] | 989 |  |  |  | 123 | [10 empty] | 659 |  |  |  | 85 | [11 empty] | 563
Total | [22 empty] | 1112 | [14 empty] | 1307
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2022 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 507
32. |  |  | Feedwater and Main Steam System | [19 empty] | 123 | [14 empty] | 76
Total | [22 empty] | 123 | [14 empty] | 583
Highlights (2023)
At the request of the sate grid,the power was reduced separately for some pe of time

## LING AO-1
2023 Operating Experience
CN-6 | [8 empty] | LING AO-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | LANPC (LINGAO NUCLEAR POWER COMPANY LTD.)
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M310 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1997-05-15
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-02-26
Gross electrical power | [12 empty] | : |  |  | 990 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-05-28
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 21 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 26
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7899.06 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.53 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 95.53 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.47 %
Load Factor (LF) | [18 empty] | : | 94.92 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 96.21 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 332 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 655.09 | 645.64 |  |  |  | 712.34 |  | 684.47 | [8 empty] | 706.79 |  |  | 677.05 | [6 empty] | 702.57 |  | 703.56 |  |  |  | 308.94 |  |  | 705.06 |  |  | 685.31 | [9 empty] | 712.24 |  |  | 7899.06
EAF [%] |  |  |  |  | 99.94 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.96 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 45.78 |  |  | 99.94 |  |  | 99.98 | [9 empty] | 100.00 |  |  | 95.53
UCF [%] |  |  |  |  | 99.94 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.96 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 45.78 |  |  | 99.94 |  |  | 99.98 | [9 empty] | 100.00 |  |  | 95.53
LF [%] |  |  |  |  | 92.68 | 101.13 |  |  |  | 100.78 |  | 100.07 | [8 empty] | 100.00 |  |  | 98.98 | [6 empty] | 99.40 |  | 99.54 |  |  |  | 45.17 |  |  | 99.75 |  |  | 100.19 | [9 empty] | 100.77 |  |  | 94.92
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 53.89 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 96.21
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.06 | 0.00 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.04 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 54.22 |  |  | 0.06 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 4.47
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 158093.29 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.38 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.74 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.96 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.07 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.96 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.23 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.33 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.55 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 4583.85 |  |  | 5184 |  |  |  | 938 | [10 empty] | 95.06 |  |  |  | 95.06 | [5 empty] | 93.54 |  |  | 99.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.94 |  |  |  |  | 0.00
2003 |  |  |  | 6375.05 |  |  | 7215 |  |  |  | 938 | [10 empty] | 80.36 |  |  |  | 82.30 | [5 empty] | 77.58 |  |  | 82.36 |  |  |  | 6.17 |  | 5.41 | [8 empty] | 12.30 |  |  |  |  | 1.93
2004 |  |  |  | 7331.36 |  |  | 7884 |  |  |  | 938 | [10 empty] | 88.69 |  |  |  | 88.95 | [5 empty] | 88.98 |  |  | 89.75 |  |  |  | 0.51 |  | 0.91 | [8 empty] | 10.13 |  |  |  |  | 0.26
2005 |  |  |  | 6906.43 |  |  | 7424 |  |  |  | 938 | [10 empty] | 84.27 |  |  |  | 84.27 | [5 empty] | 84.05 |  |  | 84.75 |  |  |  | 0.46 |  | 0.39 | [8 empty] | 15.34 |  |  |  |  | 0.00
2006 |  |  |  | 7401.01 |  |  | 7964 |  |  |  | 938 | [10 empty] | 90.12 |  |  |  | 90.12 | [5 empty] | 90.07 |  |  | 90.91 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.87 |  |  |  |  | 0.00
2007 |  |  |  | 6835.04 |  |  | 7345 |  |  |  | 938 | [10 empty] | 83.18 |  |  |  | 83.18 | [5 empty] | 83.18 |  |  | 83.85 |  |  |  | 0.00 |  | 6.58 | [8 empty] | 10.24 |  |  |  |  | 0.00
2008 |  |  |  | 7542.85 |  |  | 8163 |  |  |  | 938 | [10 empty] | 91.20 |  |  |  | 92.11 | [5 empty] | 91.55 |  |  | 92.93 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 7.81 |  |  |  |  | 0.91
2009 |  |  |  | 7002.52 |  |  | 7997 |  |  |  | 938 | [10 empty] | 90.35 |  |  |  | 90.39 | [5 empty] | 85.22 |  |  | 91.29 |  |  |  | 0.69 |  | 0.63 | [8 empty] | 8.99 |  |  |  |  | 0.04
2010 |  |  |  | 7714.57 |  |  | 8288 |  |  |  | 938 | [10 empty] | 93.60 |  |  |  | 93.66 | [5 empty] | 93.89 |  |  | 94.61 |  |  |  | 0.18 |  | 0.17 | [8 empty] | 6.18 |  |  |  |  | 0.05
2011 |  |  |  | 7571.37 |  |  | 8072 |  |  |  | 938 | [10 empty] | 91.16 |  |  |  | 91.16 | [5 empty] | 92.14 |  |  | 92.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.84 |  |  |  |  | 0.00
2012 |  |  |  | 7657.29 |  |  | 8286 |  |  |  | 938 | [10 empty] | 93.35 |  |  |  | 93.47 | [5 empty] | 92.94 |  |  | 94.33 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 6.52 |  |  |  |  | 0.12
2013 |  |  |  | 6841.69 |  |  | 7340 |  |  |  | 950 | [10 empty] | 82.46 |  |  |  | 82.80 | [5 empty] | 82.30 |  |  | 83.79 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 17.18 |  |  |  |  | 0.34
2014 |  |  |  | 7361.90 |  |  | 7899 |  |  |  | 950 | [10 empty] | 89.37 |  |  |  | 90.44 | [5 empty] | 88.46 |  |  | 90.17 |  |  |  | 0.03 |  | 2.71 | [8 empty] | 6.86 |  |  |  |  | 1.06
2015 |  |  |  | 7180.10 |  |  | 7656 |  |  |  | 950 | [10 empty] | 86.80 |  |  |  | 86.80 | [5 empty] | 86.28 |  |  | 87.40 |  |  |  | 0.07 |  | 0.34 | [8 empty] | 12.86 |  |  |  |  | 0.00
2016 |  |  |  | 8253.13 |  |  | 8784 |  |  |  | 950 | [10 empty] | 99.66 |  |  |  | 99.98 | [5 empty] | 98.90 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.02 |  |  |  |  | 0.31
2017 |  |  |  | 7020.49 |  |  | 7538 |  |  |  | 950 | [10 empty] | 88.57 |  |  |  | 89.15 | [5 empty] | 84.36 |  |  | 86.05 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 10.84 |  |  |  |  | 0.58
2018 |  |  |  | 6990.81 |  |  | 7667 |  |  |  | 950 | [10 empty] | 86.52 |  |  |  | 87.40 | [5 empty] | 84.00 |  |  | 87.52 |  |  |  | 0.28 |  | 1.27 | [8 empty] | 11.33 |  |  |  |  | 0.88
2019 |  |  |  | 7518.48 |  |  | 8363 |  |  |  | 950 | [10 empty] | 94.72 |  |  |  | 95.04 | [5 empty] | 90.34 |  |  | 95.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.96 |  |  |  |  | 0.33
2020 |  |  |  | 7556.54 |  |  | 8784 |  |  |  | 950 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 90.55 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2021 |  |  |  | 7441.92 |  |  | 7896 |  |  |  | 950 | [10 empty] | 89.39 |  |  |  | 89.67 | [5 empty] | 89.42 |  |  | 90.14 |  |  |  | 0.00 |  | 2.32 | [8 empty] | 8.01 |  |  |  |  | 0.28
2022 |  |  |  | 6706.96 |  |  | 7226 |  |  |  | 950 | [10 empty] | 82.02 |  |  |  | 82.03 | [5 empty] | 80.59 |  |  | 82.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.97 |  |  |  |  | 0.01
2023 |  |  |  | 7899.06 |  |  | 8428 |  |  |  | 950 | [10 empty] | 95.53 |  |  |  | 95.53 | [5 empty] | 94.92 |  |  | 96.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.47 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2002 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 71
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 731 |  |  |  | 11
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 18
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Z. |  | Other | [20 empty] | 350 | [14 empty] | 17
Subtotal | [22 empty] | 350 | [14 empty] | 748 |  |  |  | 82 | [11 empty] | 21
Total | [22 empty] | 350 | [14 empty] | 851
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2002 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
12. |  |  | Reactor I&C Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 27
16. |  |  | Steam generation systems | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 28
Total | [37 empty] | 70

## LING AO-2
2023 Operating Experience
CN-7 | [8 empty] | LING AO-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | LANPC (LINGAO NUCLEAR POWER COMPANY LTD.)
Reactor Supplier | [7 empty] | : | FRAM (FRAMATOME)
Turbine Supplier | [7 empty] | : | GEC (GENERAL ELECTRIC COMPANY (UK))
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M310 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1997-11-28
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-09-14
Gross electrical power | [12 empty] | : |  |  | 990 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2003-01-08
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 21 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 26
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6968.32 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.56 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.56 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.44 %
Load Factor (LF) | [18 empty] | : | 83.73 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 85.08 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1307 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 657.18 | 642.45 |  |  |  | 706.52 |  | 45.58 | [8 empty] | 59.24 |  |  | 677.63 | [6 empty] | 701.96 |  | 703.63 |  |  |  | 669.99 |  |  | 704.63 |  |  | 686.77 | [9 empty] | 712.73 |  |  | 6968.32
EAF [%] |  |  |  |  | 99.98 | 100.00 |  |  |  | 99.97 |  | 6.77 | [8 empty] | 8.65 |  |  | 99.90 | [6 empty] | 99.96 |  | 100.00 |  |  |  | 100.00 |  |  | 99.98 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.56
UCF [%] |  |  |  |  | 99.98 | 100.00 |  |  |  | 99.97 |  | 6.77 | [8 empty] | 8.65 |  |  | 99.90 | [6 empty] | 99.96 |  | 100.00 |  |  |  | 100.00 |  |  | 99.98 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.56
LF [%] |  |  |  |  | 92.98 | 100.63 |  |  |  | 99.96 |  | 6.66 | [8 empty] | 8.38 |  |  | 99.07 | [6 empty] | 99.32 |  | 99.55 |  |  |  | 97.95 |  |  | 99.69 |  |  | 100.41 | [9 empty] | 100.84 |  |  | 83.73
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 7.22 | [8 empty] | 14.11 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.08
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.03 |  | 93.23 | [8 empty] | 91.35 |  |  | 0.10 | [6 empty] | 0.04 |  | 0.00 |  |  |  | 0.00 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.44
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 154414.23 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.38 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.24 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.39 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.55 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.06 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.8 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.31 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.59 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2003 |  |  |  | 6934.88 |  |  | 7494 |  |  |  | 938 | [10 empty] | 89.94 |  |  |  | 90.58 | [5 empty] | 84.40 |  |  | 85.55 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 9.35 |  |  |  |  | 0.64
2004 |  |  |  | 6669.41 |  |  | 7109 |  |  |  | 938 | [10 empty] | 79.80 |  |  |  | 79.85 | [5 empty] | 80.95 |  |  | 80.93 |  |  |  | 2.01 |  | 2.33 | [8 empty] | 17.82 |  |  |  |  | 0.05
2005 |  |  |  | 7530.93 |  |  | 8075 |  |  |  | 938 | [10 empty] | 91.25 |  |  |  | 91.55 | [5 empty] | 91.65 |  |  | 92.18 |  |  |  | 0.70 |  | 0.64 | [8 empty] | 7.81 |  |  |  |  | 0.30
2006 |  |  |  | 7660.99 |  |  | 8164 |  |  |  | 938 | [10 empty] | 92.08 |  |  |  | 92.08 | [5 empty] | 93.23 |  |  | 93.20 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 7.90 |  |  |  |  | 0.00
2007 |  |  |  | 7215.07 |  |  | 7796 |  |  |  | 938 | [10 empty] | 87.81 |  |  |  | 87.81 | [5 empty] | 87.81 |  |  | 89.00 |  |  |  | 3.81 |  | 3.47 | [8 empty] | 8.72 |  |  |  |  | 0.00
2008 |  |  |  | 7077.15 |  |  | 7577 |  |  |  | 938 | [10 empty] | 85.24 |  |  |  | 85.24 | [5 empty] | 85.89 |  |  | 86.26 |  |  |  | 0.20 |  | 0.17 | [8 empty] | 14.59 |  |  |  |  | 0.00
2009 |  |  |  | 7433.81 |  |  | 8052 |  |  |  | 938 | [10 empty] | 90.89 |  |  |  | 90.89 | [5 empty] | 90.47 |  |  | 91.92 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.09 |  |  |  |  | 0.00
2010 |  |  |  | 7505.55 |  |  | 8112 |  |  |  | 938 | [10 empty] | 90.84 |  |  |  | 90.84 | [5 empty] | 91.34 |  |  | 92.60 |  |  |  | 0.58 |  | 0.53 | [8 empty] | 8.63 |  |  |  |  | 0.00
2011 |  |  |  | 7734.34 |  |  | 8284 |  |  |  | 938 | [10 empty] | 93.74 |  |  |  | 93.74 | [5 empty] | 94.13 |  |  | 94.57 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 6.24 |  |  |  |  | 0.00
2012 |  |  |  | 7474.47 |  |  | 8113 |  |  |  | 938 | [10 empty] | 90.95 |  |  |  | 91.09 | [5 empty] | 90.72 |  |  | 92.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.91 |  |  |  |  | 0.15
2013 |  |  |  | 7261.33 |  |  | 7804 |  |  |  | 950 | [10 empty] | 87.91 |  |  |  | 88.62 | [5 empty] | 87.25 |  |  | 89.09 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 11.36 |  |  |  |  | 0.71
2014 |  |  |  | 7773.26 |  |  | 8363 |  |  |  | 950 | [10 empty] | 94.31 |  |  |  | 94.47 | [5 empty] | 93.41 |  |  | 95.47 |  |  |  | 0.21 |  | 0.20 | [8 empty] | 5.33 |  |  |  |  | 0.16
2015 |  |  |  | 7548.19 |  |  | 8114 |  |  |  | 950 | [10 empty] | 93.63 |  |  |  | 93.68 | [5 empty] | 90.70 |  |  | 92.63 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 6.29 |  |  |  |  | 0.05
2016 |  |  |  | 6969.06 |  |  | 7514 |  |  |  | 950 | [10 empty] | 88.13 |  |  |  | 88.66 | [5 empty] | 83.51 |  |  | 85.54 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 11.28 |  |  |  |  | 0.53
2017 |  |  |  | 7720.79 |  |  | 8404 |  |  |  | 950 | [10 empty] | 95.50 |  |  |  | 96.32 | [5 empty] | 92.78 |  |  | 95.94 |  |  |  | 0.48 |  | 0.46 | [8 empty] | 3.21 |  |  |  |  | 0.82
2018 |  |  |  | 7269.80 |  |  | 8108 |  |  |  | 950 | [10 empty] | 91.53 |  |  |  | 92.09 | [5 empty] | 87.36 |  |  | 92.56 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 7.90 |  |  |  |  | 0.57
2019 |  |  |  | 6863.24 |  |  | 7531 |  |  |  | 950 | [10 empty] | 88.63 |  |  |  | 89.17 | [5 empty] | 82.47 |  |  | 85.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.83 |  |  |  |  | 0.54
2020 |  |  |  | 7007.26 |  |  | 7907 |  |  |  | 950 | [10 empty] | 89.17 |  |  |  | 89.17 | [5 empty] | 83.97 |  |  | 90.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.83 |  |  |  |  | 0.00
2021 |  |  |  | 8143.18 |  |  | 8760 |  |  |  | 950 | [10 empty] | 98.00 |  |  |  | 99.98 | [5 empty] | 97.85 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 1.98
2022 |  |  |  | 7593.07 |  |  | 8030 |  |  |  | 950 | [10 empty] | 91.11 |  |  |  | 91.14 | [5 empty] | 91.24 |  |  | 91.67 |  |  |  | 0.00 |  | 0.12 | [8 empty] | 8.74 |  |  |  |  | 0.03
2023 |  |  |  | 6968.32 |  |  | 7453 |  |  |  | 950 | [10 empty] | 84.56 |  |  |  | 84.56 | [5 empty] | 83.73 |  |  | 85.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.44 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2003 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 20
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1308 | [14 empty] | 726
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 13
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 42
L. |  | Human factor related | [39 empty] | 0
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 0
Subtotal | [22 empty] | 1308 | [14 empty] | 739 |  |  |  | 20 | [11 empty] | 43
Total | [22 empty] | 1308 | [14 empty] | 802
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2003 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 0
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
33. |  |  | Circulating Water System | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 16
Total | [37 empty] | 21

## LING AO-3
2023 Operating Experience
CN-12 | [8 empty] | LING AO-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | LDNPC (Lingdong Nuclear Power Company Ltd.)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2005-12-15
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2010-07-15
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2010-09-15
Reference unit power (net) | [12 empty] | : |  |  | 1007 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 13 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8857.8 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.99 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.99 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 100.41 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 707.93 | 691.75 |  |  |  | 764.43 |  | 736.93 | [8 empty] | 757.43 |  |  | 723.43 | [6 empty] | 750.14 |  | 752.29 |  |  |  | 726.11 |  |  | 752.50 |  |  | 733.33 | [9 empty] | 761.51 |  |  | 8857.80
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 99.99 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.96 | [9 empty] | 100.00 |  |  | 99.99
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 99.99 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.96 | [9 empty] | 100.00 |  |  | 99.99
LF [%] |  |  |  |  | 94.49 | 102.22 |  |  |  | 102.03 |  | 101.64 | [8 empty] | 101.10 |  |  | 99.78 | [6 empty] | 100.12 |  | 100.41 |  |  |  | 100.15 |  |  | 100.44 |  |  | 101.14 | [9 empty] | 101.64 |  |  | 100.41
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.04 | [9 empty] | 0.00 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 102443.49 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.72 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.7 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.93 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.07 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.3 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.38 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2010 |  |  |  | 2164.44 |  |  | 2642 |  |  |  | 1007 | [10 empty] | 77.65 |  |  |  | 77.65 | [5 empty] | 62.01 |  |  | 64.34 |  |  |  | 1.39 |  | 1.09 | [8 empty] | 21.26 |  |  |  |  | 0.00
2011 |  |  |  | 6333.19 |  |  | 6866 |  |  |  | 1007 | [10 empty] | 71.31 |  |  |  | 71.31 | [5 empty] | 71.79 |  |  | 78.38 |  |  |  | 7.44 |  | 7.39 | [8 empty] | 21.30 |  |  |  |  | 0.00
2012 |  |  |  | 7720.90 |  |  | 7877 |  |  |  | 1020 | [10 empty] | 88.02 |  |  |  | 88.26 | [5 empty] | 86.82 |  |  | 89.67 |  |  |  | 1.18 |  | 1.06 | [8 empty] | 10.69 |  |  |  |  | 0.24
2013 |  |  |  | 7942.05 |  |  | 8017 |  |  |  | 1007 | [10 empty] | 89.63 |  |  |  | 90.10 | [5 empty] | 90.03 |  |  | 91.52 |  |  |  | 0.71 |  | 0.64 | [8 empty] | 9.26 |  |  |  |  | 0.48
2014 |  |  |  | 7854.08 |  |  | 7901 |  |  |  | 1007 | [10 empty] | 88.91 |  |  |  | 89.37 | [5 empty] | 89.04 |  |  | 90.19 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 10.58 |  |  |  |  | 0.46
2015 |  |  |  | 7958.52 |  |  | 7969 |  |  |  | 1007 | [10 empty] | 90.10 |  |  |  | 90.10 | [5 empty] | 90.22 |  |  | 90.97 |  |  |  | 0.23 |  | 0.35 | [8 empty] | 9.55 |  |  |  |  | 0.00
2016 |  |  |  | 7999.24 |  |  | 8004 |  |  |  | 1007 | [10 empty] | 91.09 |  |  |  | 91.63 | [5 empty] | 90.43 |  |  | 91.12 |  |  |  | 0.01 |  | 1.03 | [8 empty] | 7.34 |  |  |  |  | 0.53
2017 |  |  |  | 7519.94 |  |  | 7668 |  |  |  | 1007 | [10 empty] | 86.12 |  |  |  | 86.99 | [5 empty] | 85.25 |  |  | 87.53 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 12.99 |  |  |  |  | 0.86
2018 |  |  |  | 7903.44 |  |  | 7865 |  |  |  | 1007 | [10 empty] | 89.32 |  |  |  | 89.32 | [5 empty] | 89.59 |  |  | 89.78 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 10.67 |  |  |  |  | 0.00
2019 |  |  |  | 8329.82 |  |  | 8760 |  |  |  | 1007 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 94.43 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
2020 |  |  |  | 7539.38 |  |  | 7987 |  |  |  | 1007 | [10 empty] | 90.71 |  |  |  | 90.71 | [5 empty] | 85.23 |  |  | 90.93 |  |  |  | 0.56 |  | 0.51 | [8 empty] | 8.78 |  |  |  |  | 0.00
2021 |  |  |  | 7311.51 |  |  | 7347 |  |  |  | 1007 | [10 empty] | 82.09 |  |  |  | 83.40 | [5 empty] | 82.88 |  |  | 83.87 |  |  |  | 0.02 |  | 0.90 | [8 empty] | 15.70 |  |  |  |  | 1.31
2022 |  |  |  | 7556.80 |  |  | 7558 |  |  |  | 1007 | [10 empty] | 89.58 |  |  |  | 89.65 | [5 empty] | 85.67 |  |  | 86.28 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 10.32 |  |  |  |  | 0.07
2023 |  |  |  | 8857.80 |  |  | 8760 |  |  |  | 1007 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.41 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2010 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 30
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 782
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 73
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 25
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 12
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Subtotal | [37 empty] | 855 |  |  |  | 30 | [11 empty] | 39
Total | [22 empty] | 0 | [14 empty] | 924
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2010 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
34. |  |  | Miscellaneous Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 1
Total | [37 empty] | 35

## LING AO-4
2023 Operating Experience
CN-13 | [8 empty] | LING AO-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | DNMC (Daya Bay Nuclear Power Operations and Management Co, Ltd.)
Owner | [7 empty] | : | LDNPC (Lingdong Nuclear Power Company Ltd.)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2006-06-15
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2011-05-03
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2011-08-07
Reference unit power (net) | [12 empty] | : |  |  | 1007 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 12 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.81
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 16 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8260.89 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.15 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.15 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.85 %
Load Factor (LF) | [18 empty] | : | 93.65 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 93.94 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 531 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 369.88 | 466.26 |  |  |  | 763.03 |  | 733.57 | [8 empty] | 750.32 |  |  | 722.60 | [6 empty] | 749.55 |  | 751.54 |  |  |  | 715.97 |  |  | 740.80 |  |  | 733.46 | [9 empty] | 763.90 |  |  | 8260.89
EAF [%] |  |  |  |  | 48.55 | 67.85 |  |  |  | 99.97 |  | 99.99 | [8 empty] | 99.99 |  |  | 99.99 | [6 empty] | 99.99 |  | 99.99 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.96 | [9 empty] | 99.99 |  |  | 93.15
UCF [%] |  |  |  |  | 48.55 | 67.85 |  |  |  | 99.97 |  | 99.99 | [8 empty] | 99.99 |  |  | 99.99 | [6 empty] | 99.99 |  | 99.99 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.96 | [9 empty] | 99.99 |  |  | 93.15
LF [%] |  |  |  |  | 49.37 | 68.90 |  |  |  | 101.85 |  | 101.18 | [8 empty] | 100.15 |  |  | 99.66 | [6 empty] | 100.05 |  | 100.31 |  |  |  | 98.75 |  |  | 98.88 |  |  | 101.16 | [9 empty] | 101.96 |  |  | 93.65
OF [%] |  |  |  |  | 49.46 | 76.93 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.94
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 51.45 | 32.15 |  |  |  | 0.03 |  | 0.01 | [8 empty] | 0.01 |  |  | 0.01 | [6 empty] | 0.01 |  | 0.01 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.04 | [9 empty] | 0.01 |  |  | 6.85
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 96297.47 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.21 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.5 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.45 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.01 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.75 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.51 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.17 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2011 |  |  |  | 3914.72 |  |  | 5268 |  |  |  | 1007 | [10 empty] | 99.60 |  |  |  | 99.60 | [5 empty] | 96.00 |  |  | 100.00 |  |  |  | 0.35 |  | 0.35 | [8 empty] | 0.05 |  |  |  |  | 0.00
2012 |  |  |  | 7009.72 |  |  | 7156 |  |  |  | 1020 | [10 empty] | 80.10 |  |  |  | 80.55 | [5 empty] | 78.24 |  |  | 81.47 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 19.44 |  |  |  |  | 0.45
2013 |  |  |  | 7870.25 |  |  | 7880 |  |  |  | 1007 | [10 empty] | 88.42 |  |  |  | 88.99 | [5 empty] | 89.22 |  |  | 89.95 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 10.84 |  |  |  |  | 0.58
2014 |  |  |  | 7895.97 |  |  | 7972 |  |  |  | 1007 | [10 empty] | 89.82 |  |  |  | 90.25 | [5 empty] | 89.51 |  |  | 91.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.75 |  |  |  |  | 0.43
2015 |  |  |  | 7916.59 |  |  | 7963 |  |  |  | 1007 | [10 empty] | 90.29 |  |  |  | 90.29 | [5 empty] | 89.74 |  |  | 90.90 |  |  |  | 0.00 |  | 0.88 | [8 empty] | 8.83 |  |  |  |  | 0.00
2016 |  |  |  | 7211.42 |  |  | 7329 |  |  |  | 1007 | [10 empty] | 87.55 |  |  |  | 87.85 | [5 empty] | 81.53 |  |  | 83.44 |  |  |  | 0.18 |  | 2.39 | [8 empty] | 9.76 |  |  |  |  | 0.30
2017 |  |  |  | 7677.26 |  |  | 7668 |  |  |  | 1007 | [10 empty] | 91.24 |  |  |  | 91.33 | [5 empty] | 87.03 |  |  | 87.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.67 |  |  |  |  | 0.09
2018 |  |  |  | 8207.81 |  |  | 8447 |  |  |  | 1007 | [10 empty] | 97.86 |  |  |  | 98.34 | [5 empty] | 93.05 |  |  | 96.43 |  |  |  | 1.65 |  | 1.65 | [8 empty] | 0.01 |  |  |  |  | 0.48
2019 |  |  |  | 7157.30 |  |  | 7588 |  |  |  | 1007 | [10 empty] | 88.75 |  |  |  | 89.29 | [5 empty] | 81.14 |  |  | 86.62 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 10.65 |  |  |  |  | 0.55
2020 |  |  |  | 7333.57 |  |  | 8185 |  |  |  | 1007 | [10 empty] | 92.77 |  |  |  | 92.77 | [5 empty] | 82.91 |  |  | 93.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.23 |  |  |  |  | 0.00
2021 |  |  |  | 7366.90 |  |  | 7331 |  |  |  | 1007 | [10 empty] | 82.58 |  |  |  | 86.11 | [5 empty] | 83.51 |  |  | 83.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.89 |  |  |  |  | 3.52
2022 |  |  |  | 8841.24 |  |  | 8744 |  |  |  | 1007 | [10 empty] | 99.77 |  |  |  | 99.77 | [5 empty] | 100.23 |  |  | 99.82 |  |  |  | 0.22 |  | 0.22 | [8 empty] | 0.01 |  |  |  |  | 0.00
2023 |  |  |  | 8260.89 |  |  | 8229 |  |  |  | 1007 | [10 empty] | 93.15 |  |  |  | 93.15 | [5 empty] | 93.65 |  |  | 93.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.85 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2011 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 17
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 559 | [14 empty] | 706
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 105
L. |  | Human factor related | [39 empty] | 16
Z. |  | Other | [51 empty] | 21
Subtotal | [22 empty] | 559 | [14 empty] | 706 |  |  |  | 33 | [11 empty] | 126
Total | [22 empty] | 559 | [14 empty] | 865
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2011 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 24
Total | [37 empty] | 39

## NINGDE-1
2023 Operating Experience
CN-18 | [8 empty] | NINGDE-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Reactor Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-02-18
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2012-12-28
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2013-04-15
Reference unit power (net) | [12 empty] | : |  |  | 1018 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 11 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7443.81 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.47 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.47 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.53 %
Load Factor (LF) | [18 empty] | : | 83.47 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 85.09 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1306 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 468.23 | 146.59 |  |  |  | 219.84 |  | 732.27 | [8 empty] | 757.33 |  |  | 688.52 | [6 empty] | 757.30 |  | 757.38 |  |  |  | 732.87 |  |  | 757.38 |  |  | 732.88 | [9 empty] | 693.20 |  |  | 7443.81
EAF [%] |  |  |  |  | 61.82 | 21.43 |  |  |  | 29.03 |  | 99.91 | [8 empty] | 99.99 |  |  | 93.94 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 91.53 |  |  | 83.47
UCF [%] |  |  |  |  | 61.82 | 21.43 |  |  |  | 29.03 |  | 99.91 | [8 empty] | 99.99 |  |  | 93.94 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 91.53 |  |  | 83.47
LF [%] |  |  |  |  | 61.82 | 21.43 |  |  |  | 29.03 |  | 99.91 | [8 empty] | 99.99 |  |  | 93.94 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 91.53 |  |  | 83.47
OF [%] |  |  |  |  | 61.83 | 21.58 |  |  |  | 38.44 |  | 100.00 | [8 empty] | 100.00 |  |  | 94.86 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.09
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 38.18 | 78.57 |  |  |  | 70.97 |  | 0.09 | [8 empty] | 0.01 |  |  | 6.06 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 8.47 |  |  | 16.53
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 82967.84 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.53 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.58 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.75 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.6 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.07 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.5 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2013 |  |  |  | 6947.98 |  |  | 7369 |  |  |  | 1018 | [10 empty] | 99.94 |  |  |  | 99.94 | [5 empty] | 96.64 |  |  | 99.33 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.04 |  |  |  |  | 0.00
2014 |  |  |  | 5047.23 |  |  | 5119 |  |  |  | 1018 | [10 empty] | 56.73 |  |  |  | 56.73 | [5 empty] | 56.60 |  |  | 58.44 |  |  |  | 23.57 |  | 21.32 | [8 empty] | 21.96 |  |  |  |  | 0.00
2015 |  |  |  | 7583.95 |  |  | 7798 |  |  |  | 1018 | [10 empty] | 88.02 |  |  |  | 88.02 | [5 empty] | 85.04 |  |  | 89.02 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 11.80 |  |  |  |  | 0.00
2016 |  |  |  | 6764.98 |  |  | 7207 |  |  |  | 1018 | [10 empty] | 97.33 |  |  |  | 98.07 | [5 empty] | 75.65 |  |  | 82.05 |  |  |  | 1.93 |  | 1.93 | [8 empty] | 0.00 |  |  |  |  | 0.74
2017 |  |  |  | 7210.58 |  |  | 7177 |  |  |  | 1018 | [10 empty] | 83.79 |  |  |  | 83.79 | [5 empty] | 80.86 |  |  | 81.93 |  |  |  | 4.26 |  | 4.80 | [8 empty] | 11.40 |  |  |  |  | 0.00
2018 |  |  |  | 8116.45 |  |  | 7756 |  |  |  | 1018 | [10 empty] | 88.50 |  |  |  | 88.50 | [5 empty] | 91.02 |  |  | 88.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.50 |  |  |  |  | 0.00
2019 |  |  |  | 8608.23 |  |  | 8567 |  |  |  | 1018 | [10 empty] | 96.53 |  |  |  | 96.53 | [5 empty] | 96.53 |  |  | 97.80 |  |  |  | 1.09 |  | 1.07 | [8 empty] | 2.40 |  |  |  |  | 0.00
2020 |  |  |  | 8119.41 |  |  | 8007 |  |  |  | 1018 | [10 empty] | 90.80 |  |  |  | 90.80 | [5 empty] | 90.80 |  |  | 91.15 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 8.90 |  |  |  |  | 0.00
2021 |  |  |  | 8209.23 |  |  | 8070 |  |  |  | 1018 | [10 empty] | 92.06 |  |  |  | 92.06 | [5 empty] | 92.06 |  |  | 92.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.94 |  |  |  |  | 0.00
2022 |  |  |  | 8917.03 |  |  | 8760 |  |  |  | 1018 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 99.99 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2023 |  |  |  | 7443.81 |  |  | 7454 |  |  |  | 1018 | [10 empty] | 83.47 |  |  |  | 83.47 | [5 empty] | 83.47 |  |  | 85.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.53 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2013 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 193
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1263 | [14 empty] | 708
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 37 | [14 empty] | 3
H. |  | Nuclear regulatory requirements | [39 empty] | 29
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 152
M. |  | Governmental requirements or court decisions | [51 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 9
Subtotal | [22 empty] | 1300 | [14 empty] | 711 |  |  |  | 231 | [11 empty] | 153
Total | [22 empty] | 1300 | [14 empty] | 1095
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2013 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 136
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
41. |  |  | Main Generator Systems | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 23
Total | [37 empty] | 188

## NINGDE-2
2023 Operating Experience
CN-19 | [8 empty] | NINGDE-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Reactor Supplier | [7 empty] | : | SHE (Shanghai Electric)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-11-12
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-01-04
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2014-05-04
Reference unit power (net) | [12 empty] | : |  |  | 1018 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8874.52 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.48 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.48 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.52 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 99.52 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.52 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 42 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 757.33 | 684.09 |  |  |  | 757.29 |  | 690.47 | [8 empty] | 757.30 |  |  | 732.82 | [6 empty] | 757.37 |  | 757.31 |  |  |  | 732.96 |  |  | 757.30 |  |  | 732.96 | [9 empty] | 757.31 |  |  | 8874.52
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 94.20 | [8 empty] | 99.99 |  |  | 99.98 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 100.00 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 99.52
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 94.20 | [8 empty] | 99.99 |  |  | 99.98 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 100.00 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 99.52
LF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 99.99 |  | 94.20 | [8 empty] | 99.99 |  |  | 99.98 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 100.00 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 99.52
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 94.17 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.52
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 5.79 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.48
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 5.79 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.48
PUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.01 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.00 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 77259.23 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.29 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.54 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.41 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.56 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.03 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.69 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.09 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2014 |  |  |  | 6568.05 |  |  | 7044 |  |  |  | 1018 | [10 empty] | 99.85 |  |  |  | 99.85 | [5 empty] | 97.55 |  |  | 100.00 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 0.14 |  |  |  |  | 0.00
2015 |  |  |  | 6528.23 |  |  | 7145 |  |  |  | 1018 | [10 empty] | 80.58 |  |  |  | 80.58 | [5 empty] | 73.21 |  |  | 81.56 |  |  |  | 0.22 |  | 0.18 | [8 empty] | 19.24 |  |  |  |  | 0.00
2016 |  |  |  | 5714.85 |  |  | 6290 |  |  |  | 1018 | [10 empty] | 86.24 |  |  |  | 86.39 | [5 empty] | 63.91 |  |  | 71.61 |  |  |  | 0.32 |  | 1.62 | [8 empty] | 12.00 |  |  |  |  | 0.14
2017 |  |  |  | 8252.86 |  |  | 8371 |  |  |  | 1018 | [10 empty] | 98.72 |  |  |  | 98.72 | [5 empty] | 92.54 |  |  | 95.56 |  |  |  | 1.26 |  | 1.26 | [8 empty] | 0.02 |  |  |  |  | 0.00
2018 |  |  |  | 7953.87 |  |  | 7938 |  |  |  | 1018 | [10 empty] | 89.03 |  |  |  | 89.03 | [5 empty] | 89.19 |  |  | 90.62 |  |  |  | 0.44 |  | 0.40 | [8 empty] | 10.57 |  |  |  |  | 0.00
2019 |  |  |  | 8079.09 |  |  | 8026 |  |  |  | 1018 | [10 empty] | 90.60 |  |  |  | 90.60 | [5 empty] | 90.60 |  |  | 91.62 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 9.40 |  |  |  |  | 0.00
2020 |  |  |  | 8940.50 |  |  | 8784 |  |  |  | 1018 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 99.98 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2021 |  |  |  | 8043.49 |  |  | 7904 |  |  |  | 1018 | [10 empty] | 90.20 |  |  |  | 90.20 | [5 empty] | 90.20 |  |  | 90.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.80 |  |  |  |  | 0.00
2022 |  |  |  | 8303.72 |  |  | 8158 |  |  |  | 1018 | [10 empty] | 93.12 |  |  |  | 93.12 | [5 empty] | 93.12 |  |  | 93.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.88 |  |  |  |  | 0.00
2023 |  |  |  | 8874.52 |  |  | 8718 |  |  |  | 1018 | [10 empty] | 99.52 |  |  |  | 99.52 | [5 empty] | 99.52 |  |  | 99.52 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.01 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2014 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 42 | [14 empty] | 4
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 583
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 182
Z. |  | Other | [39 empty] | 12
Subtotal | [26 empty] | 42 | [10 empty] | 583 |  |  |  | 16 | [11 empty] | 182
Total | [22 empty] | 42 | [14 empty] | 781
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2014 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [19 empty] | 42 | [14 empty] | 4
Total | [22 empty] | 42 | [14 empty] | 4

## NINGDE-3
2023 Operating Experience
CN-34 | [8 empty] | NINGDE-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Owner | [7 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-01-08
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-03-21
Gross electrical power | [12 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-06-10
Reference unit power (net) | [12 empty] | : |  |  | 1018 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8595.73 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.39 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.39 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 3.61 %
Load Factor (LF) | [18 empty] | : | 96.39 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 96.47 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 309 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 757.38 | 684.03 |  |  |  | 757.33 |  | 732.95 | [8 empty] | 757.32 |  |  | 732.95 | [6 empty] | 757.34 |  | 757.02 |  |  |  | 732.89 |  |  | 757.35 |  |  | 732.93 | [9 empty] | 436.24 |  |  | 8595.73
EAF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.99 |  | 99.95 |  |  |  | 99.99 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 57.60 |  |  | 96.39
UCF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.99 |  | 99.95 |  |  |  | 99.99 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 57.60 |  |  | 96.39
LF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 99.99 |  | 100.00 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.99 |  | 99.95 |  |  |  | 99.99 |  |  | 99.99 |  |  | 100.00 | [9 empty] | 57.60 |  |  | 96.39
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 58.47 |  |  | 96.47
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.05 |  |  |  | 0.01 |  |  | 0.01 |  |  | 0.00 | [9 empty] | 42.40 |  |  | 3.61
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 68425.73 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.68 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.52 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.63 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.53 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.85 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.56 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.57 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 4638.75 |  |  | 5586 |  |  |  | 1018 | [10 empty] | 91.25 |  |  |  | 91.25 | [5 empty] | 80.88 |  |  | 92.85 |  |  |  | 8.74 |  | 8.74 | [8 empty] | 0.01 |  |  |  |  | 0.00
2016 |  |  |  | 6086.41 |  |  | 6514 |  |  |  | 1018 | [10 empty] | 81.37 |  |  |  | 81.37 | [5 empty] | 68.06 |  |  | 74.16 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 18.62 |  |  |  |  | 0.00
2017 |  |  |  | 7971.03 |  |  | 8107 |  |  |  | 1018 | [10 empty] | 95.64 |  |  |  | 95.64 | [5 empty] | 89.38 |  |  | 92.55 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 4.35 |  |  |  |  | 0.00
2018 |  |  |  | 8264.16 |  |  | 8141 |  |  |  | 1018 | [10 empty] | 92.40 |  |  |  | 92.44 | [5 empty] | 92.67 |  |  | 92.93 |  |  |  | 0.28 |  | 0.26 | [8 empty] | 7.29 |  |  |  |  | 0.05
2019 |  |  |  | 8167.27 |  |  | 8075 |  |  |  | 1018 | [10 empty] | 91.59 |  |  |  | 91.59 | [5 empty] | 91.59 |  |  | 92.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.41 |  |  |  |  | 0.00
2020 |  |  |  | 8650.70 |  |  | 8501 |  |  |  | 1018 | [10 empty] | 96.74 |  |  |  | 96.74 | [5 empty] | 96.74 |  |  | 96.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.26 |  |  |  |  | 0.00
2021 |  |  |  | 8418.61 |  |  | 8271 |  |  |  | 1018 | [10 empty] | 94.40 |  |  |  | 94.40 | [5 empty] | 94.40 |  |  | 94.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.60 |  |  |  |  | 0.00
2022 |  |  |  | 8239.00 |  |  | 8094 |  |  |  | 1018 | [10 empty] | 92.39 |  |  |  | 92.39 | [5 empty] | 92.39 |  |  | 92.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.61 |  |  |  |  | 0.00
2023 |  |  |  | 8595.73 |  |  | 8451 |  |  |  | 1018 | [10 empty] | 96.39 |  |  |  | 96.39 | [5 empty] | 96.39 |  |  | 96.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.61 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2015 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 17
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 309 | [14 empty] | 584
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 109
L. |  | Human factor related | [39 empty] | 32
Subtotal | [22 empty] | 309 | [14 empty] | 584 |  |  |  | 49 | [11 empty] | 109
Total | [22 empty] | 309 | [14 empty] | 742
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2015 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 32
31. |  |  | Turbine and auxiliaries | [34 empty] | 5
33. |  |  | Circulating Water System | [34 empty] | 11
Total | [37 empty] | 48

## NINGDE-4
2023 Operating Experience
CN-35 | [7 empty] | NINGDE-4 | [26 empty] | CHINA
Status at end of year | [6 empty] | : | Operational
Operator | [6 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Owner | [6 empty] | : | NDNP (Fujian Ningde Nuclear Power Company, Ltd.)
Reactor Supplier | [6 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [6 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [26 empty] | Key Dates
Reactor type and model | [11 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-09-29
Thermal power | [11 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-03-29
Gross electrical power | [11 empty] | : |  |  | 1089 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-07-21
Reference unit power (net) | [11 empty] | : |  |  | 1018 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [27 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [12 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 327.6
| Fuel material | [12 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [12 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [12 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [12 empty] | : |  |  | 2.43 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [12 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [12 empty] | : |  |  | 44.6 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [12 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [12 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [12 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [12 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [12 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [12 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [12 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [12 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [17 empty] | : | 7967.67 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [17 empty] | : | 89.35 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [17 empty] | : | 89.35 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.65 %
Load Factor (LF) | [17 empty] | : | 89.35 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [17 empty] | : | 90.34 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 846 hours
Annual Summary
|  |  |  | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  | 625.05 | 684.09 |  |  |  | 757.32 |  | 683.18 | [8 empty] | 757.37 |  |  | 732.92 | [6 empty] | 757.37 |  | 757.23 |  |  |  | 461.66 |  |  | 261.58 |  |  | 732.57 | [9 empty] | 757.34 |  |  | 7967.67
EAF [%] |  |  |  | 82.53 | 100.00 |  |  |  | 99.99 |  | 93.21 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 99.98 |  |  |  | 62.99 |  |  | 34.54 |  |  | 99.95 | [9 empty] | 99.99 |  |  | 89.35
UCF [%] |  |  |  | 82.53 | 100.00 |  |  |  | 99.99 |  | 93.21 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 99.98 |  |  |  | 62.99 |  |  | 34.54 |  |  | 99.95 | [9 empty] | 99.99 |  |  | 89.35
LF [%] |  |  |  | 82.53 | 100.00 |  |  |  | 99.99 |  | 93.21 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 99.98 |  |  |  | 62.99 |  |  | 34.54 |  |  | 99.95 | [9 empty] | 99.99 |  |  | 89.35
OF [%] |  |  |  | 82.53 | 100.00 |  |  |  | 100.00 |  | 93.19 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 63.89 |  |  | 45.30 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.34
FLR [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  | 17.47 | 0.00 |  |  |  | 0.01 |  | 6.79 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 37.01 |  |  | 65.46 |  |  | 0.05 | [9 empty] | 0.01 |  |  | 10.65
XUF [%] |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [12 empty] | : |  |  | 58999 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.02 %
Cumulative Energy Availability Factor (EAF) | [12 empty] | : |  |  | 92.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.02 %
Cumulative Unit Capability Factor (UCF) | [12 empty] | : |  |  | 92.55 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.43 %
Cumulative Load Factor (LF) | [12 empty] | : |  |  | 88.74 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [12 empty] | : |  |  | 90.29 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  | 3694.87 |  |  | 3786 |  |  |  | 1018 | [10 empty] | 99.87 |  |  |  | 99.87 | [5 empty] | 91.83 |  |  | 95.92 |  |  |  | 0.12 |  | 0.12 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  | 5303.77 |  |  | 5739 |  |  |  | 1018 | [10 empty] | 84.33 |  |  |  | 84.33 | [5 empty] | 59.47 |  |  | 65.51 |  |  |  | 0.12 |  | 0.10 | [8 empty] | 15.57 |  |  |  |  | 0.00
2018 |  |  | 8917.08 |  |  | 8760 |  |  |  | 1018 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 99.99 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2019 |  |  | 8074.33 |  |  | 7992 |  |  |  | 1018 | [10 empty] | 90.54 |  |  |  | 90.54 | [5 empty] | 90.54 |  |  | 91.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.46 |  |  |  |  | 0.00
2020 |  |  | 7998.17 |  |  | 8033 |  |  |  | 1018 | [10 empty] | 89.45 |  |  |  | 89.45 | [5 empty] | 89.44 |  |  | 91.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.55 |  |  |  |  | 0.00
2021 |  |  | 8916.45 |  |  | 8760 |  |  |  | 1018 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 99.99 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2022 |  |  | 8126.58 |  |  | 7984 |  |  |  | 1018 | [10 empty] | 91.13 |  |  |  | 91.13 | [5 empty] | 91.13 |  |  | 91.14 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.87 |  |  |  |  | 0.00
2023 |  |  | 7967.67 |  |  | 7914 |  |  |  | 1018 | [10 empty] | 89.35 |  |  |  | 89.35 | [5 empty] | 89.35 |  |  | 90.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.65 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[22 empty] | 2023 | [14 empty] | 2016 to 2023
Outage Cause | [21 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[22 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [19 empty] | 667 | [14 empty] | 575
D. |  | Inspection, maintenance or repair without refuelling | [19 empty] | 49 | [14 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [50 empty] | 141
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [50 empty] | 111
Z. |  | Other | [19 empty] | 130 | [14 empty] | 18
Subtotal | [21 empty] | 846 | [14 empty] | 600 | [15 empty] | 252
Total | [21 empty] | 846 | [14 empty] | 852
Equipment Related Unplanned Full Outages, Analysis by System
System | [21 empty] | 2023 | [14 empty] | 2016 to 2023
[22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
Total

## QINSHAN 2-1
2023 Operating Experience
CN-4 | [8 empty] | QINSHAN 2-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CNNO (CNNC Nuclear Operation Management Company Limited)
Owner | [7 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1996-06-02
Thermal power | [12 empty] | : |  |  | 1930 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-02-06
Gross electrical power | [12 empty] | : |  |  | 650 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-04-15
Reference unit power (net) | [12 empty] | : |  |  | 623 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 21 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.2
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.45
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.25 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 2.67 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.41
| Active core height/length [m] | [13 empty] | : |  |  | 3.6576 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.09 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 33 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5460.89 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.49 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.97 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.03 %
Load Factor (LF) | [18 empty] | : | 100.06 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.48 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 465.67 | 411.88 |  |  |  | 471.48 |  | 431.97 | [8 empty] | 470.89 |  |  | 453.66 | [6 empty] | 456.65 |  | 457.16 |  |  |  | 446.84 |  |  | 468.04 |  |  | 455.88 | [9 empty] | 470.79 |  |  | 5460.89
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.88 | [6 empty] | 97.29 |  | 97.53 |  |  |  | 99.32 |  |  | 99.96 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.49
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.66 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.97
LF [%] |  |  |  |  | 100.47 | 98.38 |  |  |  | 101.72 |  | 96.30 | [8 empty] | 101.59 |  |  | 101.14 | [6 empty] | 98.52 |  | 98.63 |  |  |  | 99.62 |  |  | 100.98 |  |  | 101.63 | [9 empty] | 101.57 |  |  | 100.06
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.34 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.12 | [6 empty] | 2.38 |  | 2.47 |  |  |  | 0.68 |  |  | 0.04 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.48
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 100272 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.8 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.33 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.66 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 85.41 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.93 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.89 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.08 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.36 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 2965.29 |  |  | 4631 |  |  |  | 610 | [10 empty] | 81.56 |  |  |  | 81.56 | [5 empty] | 73.64 |  |  | 70.16 |  |  |  | 18.44 |  | 18.44 | [8 empty] | 0.00 |  |  |  |  | 0.00
2003 |  |  |  | 4327.30 |  |  | 7123 |  |  |  | 610 | [10 empty] | 80.90 |  |  |  | 80.95 | [5 empty] | 80.98 |  |  | 81.31 |  |  |  | 2.61 |  | 2.17 | [8 empty] | 16.88 |  |  |  |  | 0.05
2004 |  |  |  | 4395.68 |  |  | 7117 |  |  |  | 610 | [10 empty] | 80.13 |  |  |  | 80.13 | [5 empty] | 82.04 |  |  | 81.02 |  |  |  | 3.25 |  | 2.69 | [8 empty] | 17.17 |  |  |  |  | 0.00
2005 |  |  |  | 4944.77 |  |  | 7982 |  |  |  | 610 | [10 empty] | 90.61 |  |  |  | 90.61 | [5 empty] | 92.54 |  |  | 91.12 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.37 |  |  |  |  | 0.00
2006 |  |  |  | 2938.16 |  |  | 4890 |  |  |  | 610 | [10 empty] | 55.23 |  |  |  | 55.23 | [5 empty] | 54.98 |  |  | 55.82 |  |  |  | 15.49 |  | 10.12 | [8 empty] | 34.65 |  |  |  |  | 0.00
2007 |  |  |  | 3503.00 |  |  | 5681 |  |  |  | 610 | [10 empty] | 64.12 |  |  |  | 64.12 | [5 empty] | 65.56 |  |  | 64.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 35.88 |  |  |  |  | 0.00
2008 |  |  |  | 4677.61 |  |  | 7554 |  |  |  | 610 | [10 empty] | 85.25 |  |  |  | 85.35 | [5 empty] | 87.30 |  |  | 86.00 |  |  |  | 0.18 |  | 0.48 | [8 empty] | 14.17 |  |  |  |  | 0.10
2009 |  |  |  | 4500.99 |  |  | 7256 |  |  |  | 610 | [10 empty] | 82.66 |  |  |  | 82.66 | [5 empty] | 84.23 |  |  | 82.83 |  |  |  | 0.74 |  | 0.62 | [8 empty] | 16.72 |  |  |  |  | 0.00
2010 |  |  |  | 4985.39 |  |  | 8095 |  |  |  | 610 | [10 empty] | 91.70 |  |  |  | 91.70 | [5 empty] | 93.30 |  |  | 92.41 |  |  |  | 0.21 |  | 0.19 | [8 empty] | 8.11 |  |  |  |  | 0.00
2011 |  |  |  | 4029.39 |  |  | 6521 |  |  |  | 610 | [10 empty] | 73.66 |  |  |  | 73.66 | [5 empty] | 75.41 |  |  | 74.44 |  |  |  | 2.90 |  | 3.97 | [8 empty] | 22.37 |  |  |  |  | 0.00
2012 |  |  |  | 4545.92 |  |  | 7543 |  |  |  | 610 | [10 empty] | 85.20 |  |  |  | 85.20 | [5 empty] | 84.84 |  |  | 85.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.80 |  |  |  |  | 0.00
2013 |  |  |  | 4680.90 |  |  | 7561 |  |  |  | 610 | [10 empty] | 85.75 |  |  |  | 85.75 | [5 empty] | 87.60 |  |  | 86.31 |  |  |  | 0.87 |  | 0.75 | [8 empty] | 13.50 |  |  |  |  | 0.00
2014 |  |  |  | 4579.16 |  |  | 7412 |  |  |  | 610 | [10 empty] | 83.68 |  |  |  | 83.68 | [5 empty] | 85.69 |  |  | 84.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.32 |  |  |  |  | 0.00
2015 |  |  |  | 4775.88 |  |  | 7859 |  |  |  | 610 | [10 empty] | 89.35 |  |  |  | 89.35 | [5 empty] | 89.38 |  |  | 89.71 |  |  |  | 0.84 |  | 0.76 | [8 empty] | 9.90 |  |  |  |  | 0.00
2016 |  |  |  | 4732.19 |  |  | 7825 |  |  |  | 610 | [10 empty] | 91.28 |  |  |  | 91.28 | [5 empty] | 88.32 |  |  | 89.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.72 |  |  |  |  | 0.00
2017 |  |  |  | 5385.37 |  |  | 8732 |  |  |  | 610 | [10 empty] | 99.32 |  |  |  | 99.52 | [5 empty] | 100.78 |  |  | 99.68 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.13 |  |  |  |  | 0.20
2018 |  |  |  | 4725.63 |  |  | 7682 |  |  |  | 610 | [10 empty] | 87.19 |  |  |  | 87.19 | [5 empty] | 88.44 |  |  | 87.69 |  |  |  | 0.16 |  | 0.14 | [8 empty] | 12.67 |  |  |  |  | 0.00
2019 |  |  |  | 4796.97 |  |  | 7781 |  |  |  | 610 | [10 empty] | 88.15 |  |  |  | 88.20 | [5 empty] | 89.77 |  |  | 88.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.80 |  |  |  |  | 0.06
2020 |  |  |  | 5228.19 |  |  | 8784 |  |  |  | 610 | [10 empty] | 99.88 |  |  |  | 99.95 | [5 empty] | 97.57 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  |  |  | 0.07
2021 |  |  |  | 5024.61 |  |  | 8118 |  |  |  | 610 | [10 empty] | 91.98 |  |  |  | 92.17 | [5 empty] | 94.03 |  |  | 92.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.83 |  |  |  |  | 0.19
2022 |  |  |  | 4897.42 |  |  | 7859 |  |  |  | 623 | [10 empty] | 88.76 |  |  |  | 89.36 | [5 empty] | 89.74 |  |  | 89.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.64 |  |  |  |  | 0.60
2023 |  |  |  | 5460.89 |  |  | 8760 |  |  |  | 623 | [10 empty] | 99.49 |  |  |  | 99.97 | [5 empty] | 100.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.48
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2002 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 77
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 938
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 21
E. |  | Testing of plant systems or components | [39 empty] | 1
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 187
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 9
Z. |  | Other | [39 empty] | 7
Subtotal | [37 empty] | 1146 |  |  |  | 85 | [11 empty] | 9
Total | [22 empty] | 0 | [14 empty] | 1240
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2002 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 34
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 14
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 24
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [37 empty] | 79

## QINSHAN 2-2
2023 Operating Experience
CN-5 | [9 empty] | QINSHAN 2-2 | [28 empty] | CHINA
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | CNNO (CNNC Nuclear Operation Management Company Limited)
Owner | [8 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Reactor Supplier | [8 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [8 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PWR / CNP-600 | [12 empty] | Construction Date | [16 empty] | : |  |  | 1997-04-01
Thermal power | [14 empty] | : |  |  | 1930 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 2004-03-11
Gross electrical power | [14 empty] | : |  |  | 650 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 2004-05-03
Reference unit power (net) | [14 empty] | : |  |  | 623 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 19 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Vertical | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 315.2
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 2
| Refuelling type | [15 empty] | : |  |  | OFF-line | [12 empty] | Containment type | [16 empty] | : |  |  | Single
| Moderator material | [15 empty] | : |  |  | H2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 0.450
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | 3.25 | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | 12 | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 1
| Part of the core refuelled [%] | [15 empty] | : |  |  | 33 | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | - | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | 3
| Active core diameter [m] | [15 empty] | : |  |  | 2.67 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 6.41
| Active core height/length [m] | [15 empty] | : |  |  | 3.6576 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 121 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 16.09 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | 3
| Number of control rod assemblies | [15 empty] | : |  |  | 33 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | 2
| Number of external reactor coolant loops | [15 empty] | : |  |  | 2 | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | 2
| Coolant type | [15 empty] | : |  |  | H2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [20 empty] | : | 5026.63 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [20 empty] | : | 94.58 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [20 empty] | : | 94.99 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 5.01 %
Load Factor (LF) | [20 empty] | : | 92.11 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0.41 %
Operating Factor (OF) | [20 empty] | : | 92.53 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 654 hours
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 320.39 |  | 403.91 |  |  |  |  | 468.50 |  | 430.89 | [8 empty] | 467.64 |  |  |  | 452.77 | [6 empty] | 456.65 |  | 456.49 |  |  |  |  | 175.61 |  |  | 469.70 |  |  | 454.68 | [9 empty] | 469.39 |  |  | 5026.63
EAF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 99.99 | [6 empty] | 97.76 |  | 97.64 |  |  |  |  | 38.89 |  |  | 99.98 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.58
UCF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  |  | 39.08 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.99
LF [%] |  |  |  |  | 69.12 |  | 96.48 |  |  |  |  | 101.08 |  | 96.06 | [8 empty] | 100.89 |  |  |  | 100.94 | [6 empty] | 98.52 |  | 98.48 |  |  |  |  | 39.15 |  |  | 101.33 |  |  | 101.36 | [9 empty] | 101.27 |  |  | 92.11
OF [%] |  |  |  |  | 68.82 |  | 99.11 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  |  | 42.22 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.53
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 60.92 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.01
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.01 | [6 empty] | 2.24 |  | 2.36 |  |  |  |  | 0.19 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.41
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 95276 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 1.26 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 89.42 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 1.14 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 89.55 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 9.32 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 90.25 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.13 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 89.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2004 |  |  |  | 3764.39 |  |  |  | 6381 |  |  |  |  | 610 | [10 empty] | 96.24 |  |  |  |  | 96.24 | [5 empty] | 97.96 |  |  | 96.62 |  |  |  |  | 0.90 |  | 0.87 | [8 empty] | 2.88 |  |  |  |  | 0.00
2005 |  |  |  | 4521.51 |  |  |  | 7331 |  |  |  |  | 610 | [10 empty] | 82.69 |  |  |  |  | 82.77 | [5 empty] | 84.62 |  |  | 83.69 |  |  |  |  | 1.65 |  | 1.39 | [8 empty] | 15.84 |  |  |  |  | 0.08
2006 |  |  |  | 4790.44 |  |  |  | 7822 |  |  |  |  | 610 | [10 empty] | 88.78 |  |  |  |  | 88.78 | [5 empty] | 89.65 |  |  | 89.29 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.21 |  |  |  |  | 0.00
2007 |  |  |  | 4817.01 |  |  |  | 7792 |  |  |  |  | 610 | [10 empty] | 88.30 |  |  |  |  | 88.30 | [5 empty] | 90.15 |  |  | 88.95 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.70 |  |  |  |  | 0.00
2008 |  |  |  | 4635.51 |  |  |  | 7545 |  |  |  |  | 610 | [10 empty] | 84.89 |  |  |  |  | 85.21 | [5 empty] | 86.51 |  |  | 85.89 |  |  |  |  | 0.36 |  | 0.31 | [8 empty] | 14.48 |  |  |  |  | 0.32
2009 |  |  |  | 4787.80 |  |  |  | 7821 |  |  |  |  | 610 | [10 empty] | 88.22 |  |  |  |  | 88.22 | [5 empty] | 89.60 |  |  | 89.28 |  |  |  |  | 0.62 |  | 0.55 | [8 empty] | 11.24 |  |  |  |  | 0.00
2010 |  |  |  | 4715.04 |  |  |  | 7645 |  |  |  |  | 610 | [10 empty] | 86.64 |  |  |  |  | 86.64 | [5 empty] | 88.24 |  |  | 87.27 |  |  |  |  | 0.43 |  | 0.37 | [8 empty] | 12.98 |  |  |  |  | 0.00
2011 |  |  |  | 4960.23 |  |  |  | 8014 |  |  |  |  | 610 | [10 empty] | 90.91 |  |  |  |  | 90.91 | [5 empty] | 92.83 |  |  | 91.48 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.09 |  |  |  |  | 0.00
2012 |  |  |  | 4335.54 |  |  |  | 7072 |  |  |  |  | 610 | [10 empty] | 79.63 |  |  |  |  | 79.63 | [5 empty] | 80.91 |  |  | 80.51 |  |  |  |  | 10.13 |  | 8.98 | [8 empty] | 11.39 |  |  |  |  | 0.00
2013 |  |  |  | 4818.51 |  |  |  | 7826 |  |  |  |  | 610 | [10 empty] | 88.70 |  |  |  |  | 88.70 | [5 empty] | 90.17 |  |  | 89.34 |  |  |  |  | 1.23 |  | 1.11 | [8 empty] | 10.19 |  |  |  |  | 0.00
2014 |  |  |  | 4626.25 |  |  |  | 7514 |  |  |  |  | 610 | [10 empty] | 85.00 |  |  |  |  | 85.00 | [5 empty] | 86.58 |  |  | 85.78 |  |  |  |  | 2.26 |  | 1.96 | [8 empty] | 13.04 |  |  |  |  | 0.00
2015 |  |  |  | 4872.99 |  |  |  | 7990 |  |  |  |  | 610 | [10 empty] | 95.14 |  |  |  |  | 95.14 | [5 empty] | 91.19 |  |  | 91.21 |  |  |  |  | 4.84 |  | 4.83 | [8 empty] | 0.03 |  |  |  |  | 0.00
2016 |  |  |  | 4525.57 |  |  |  | 7377 |  |  |  |  | 610 | [10 empty] | 83.79 |  |  |  |  | 83.79 | [5 empty] | 84.46 |  |  | 83.98 |  |  |  |  | 0.02 |  | 0.01 | [8 empty] | 16.20 |  |  |  |  | 0.00
2017 |  |  |  | 4803.39 |  |  |  | 7830 |  |  |  |  | 610 | [10 empty] | 88.83 |  |  |  |  | 88.83 | [5 empty] | 89.89 |  |  | 89.38 |  |  |  |  | 0.01 |  | 0.01 | [8 empty] | 11.16 |  |  |  |  | 0.00
2018 |  |  |  | 5306.28 |  |  |  | 8574 |  |  |  |  | 610 | [10 empty] | 97.65 |  |  |  |  | 97.65 | [5 empty] | 99.30 |  |  | 97.88 |  |  |  |  | 2.30 |  | 2.29 | [8 empty] | 0.05 |  |  |  |  | 0.00
2019 |  |  |  | 4735.26 |  |  |  | 7680 |  |  |  |  | 610 | [10 empty] | 87.10 |  |  |  |  | 87.16 | [5 empty] | 88.62 |  |  | 87.67 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.84 |  |  |  |  | 0.06
2020 |  |  |  | 4758.46 |  |  |  | 8156 |  |  |  |  | 610 | [10 empty] | 90.79 |  |  |  |  | 92.31 | [5 empty] | 88.81 |  |  | 92.85 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.69 |  |  |  |  | 1.52
2021 |  |  |  | 5406.39 |  |  |  | 8760 |  |  |  |  | 610 | [10 empty] | 99.91 |  |  |  |  | 99.91 | [5 empty] | 101.17 |  |  | 100.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.09 |  |  |  |  | 0.00
2022 |  |  |  | 5064.37 |  |  |  | 8159 |  |  |  |  | 610 | [10 empty] | 92.77 |  |  |  |  | 92.86 | [5 empty] | 94.77 |  |  | 93.14 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.14 |  |  |  |  | 0.09
2023 |  |  |  | 5026.63 |  |  |  | 8106 |  |  |  |  | 623 | [10 empty] | 94.58 |  |  |  |  | 94.99 | [5 empty] | 92.11 |  |  | 92.53 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.01 |  |  |  |  | 0.41
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2023 | [16 empty] | 2004 to 2023
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [43 empty] | 92
C. |  | Inspection, maintenance or repair combined with refuelling | [22 empty] | 414 | [16 empty] | 767
D. |  | Inspection, maintenance or repair without refuelling | [39 empty] | 19
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [39 empty] | 5
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [34 empty] | 238 | [20 empty] | 32
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [55 empty] | 1
Subtotal | [24 empty] | 414 | [11 empty] | 238 |  |  |  |  | 791 |  |  |  | 92 | [11 empty] | 33
Total | [24 empty] | 652 | [16 empty] | 916
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2023 | [16 empty] | 2004 to 2023
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [38 empty] | 5
15. |  |  | Reactor Cooling Systems | [38 empty] | 9
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [38 empty] | 1
31. |  |  | Turbine and auxiliaries | [38 empty] | 73
32. |  |  | Feedwater and Main Steam System | [38 empty] | 1
42. |  |  | Electrical Power Supply Systems | [38 empty] | 2
Total | [41 empty] | 91
RUP revision during the year (2023) due to power uprate
RUP at the end of previous year : 610 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
January | [5 empty] | 623 |  |  |  |  | Stretch power uprate (2-7%) | [14 empty] | Balance of plant | [13 empty] | Power Uprate
Highlights (2023)
The unit was shutdown for 216 refuelling outage from September 1 to September 18.

## QINSHAN 2-3
2023 Operating Experience
CN-14 | [9 empty] | QINSHAN 2-3 | [28 empty] | CHINA
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | CNNO (CNNC Nuclear Operation Management Company Limited)
Owner | [8 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Reactor Supplier | [8 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [8 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PWR / CNP-600 | [12 empty] | Construction Date | [16 empty] | : |  |  | 2006-04-28
Thermal power | [14 empty] | : |  |  | 1930 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 2010-08-01
Gross electrical power | [14 empty] | : |  |  | 660 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 2010-10-05
Reference unit power (net) | [14 empty] | : |  |  | 623 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 13 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Vertical | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 315.2
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 2
| Refuelling type | [15 empty] | : |  |  | OFF-line | [12 empty] | Containment type | [16 empty] | : |  |  | Single
| Moderator material | [15 empty] | : |  |  | H2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 0.45
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | 3.25 | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | 12 | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 1
| Part of the core refuelled [%] | [15 empty] | : |  |  | 33.3 | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | - | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | 3
| Active core diameter [m] | [15 empty] | : |  |  | 2.67 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 6.41
| Active core height/length [m] | [15 empty] | : |  |  | 3.6576 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 121 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 16.09 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | 3
| Number of control rod assemblies | [15 empty] | : |  |  | 33 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | 3
| Number of external reactor coolant loops | [15 empty] | : |  |  | 2 | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | 2
| Coolant type | [15 empty] | : |  |  | H2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [20 empty] | : | 5184.38 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [20 empty] | : | 94.92 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [20 empty] | : | 95.53 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 4.47 %
Load Factor (LF) | [20 empty] | : | 95 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0.61 %
Operating Factor (OF) | [20 empty] | : | 95.86 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 363 hours
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 447.47 |  | 410.61 |  |  |  |  | 470.06 |  | 186.76 | [8 empty] | 470.91 |  |  |  | 452.41 | [6 empty] | 454.22 |  | 453.61 |  |  |  |  | 445.77 |  |  | 468.74 |  |  | 454.71 | [9 empty] | 469.11 |  |  | 5184.38
EAF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 45.91 | [8 empty] | 100.00 |  |  |  | 99.67 | [6 empty] | 97.18 |  | 97.04 |  |  |  |  | 98.75 |  |  | 99.89 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.92
UCF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 45.91 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 99.74 |  | 100.00 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.53
LF [%] |  |  |  |  | 96.54 |  | 98.08 |  |  |  |  | 101.41 |  | 41.63 | [8 empty] | 101.60 |  |  |  | 100.86 | [6 empty] | 98.00 |  | 97.86 |  |  |  |  | 99.38 |  |  | 101.13 |  |  | 101.37 | [9 empty] | 101.21 |  |  | 95.00
OF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 49.58 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.86
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 54.09 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.26 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.47
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.33 | [6 empty] | 2.57 |  | 2.96 |  |  |  |  | 1.25 |  |  | 0.11 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.61
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 65540 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 0.9 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 91.65 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 0.83 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 91.79 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 7.38 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 91.29 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.14 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 91.85 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2010 |  |  |  | 1465.17 |  |  |  | 2685 |  |  |  |  | 610 | [10 empty] | 94.75 |  |  |  |  | 94.75 | [5 empty] | 96.66 |  |  | 97.55 |  |  |  |  | 5.22 |  | 5.21 | [8 empty] | 0.04 |  |  |  |  | 0.00
2011 |  |  |  | 4434.13 |  |  |  | 7226 |  |  |  |  | 610 | [10 empty] | 81.55 |  |  |  |  | 81.56 | [5 empty] | 82.98 |  |  | 82.49 |  |  |  |  | 0.21 |  | 0.17 | [8 empty] | 18.27 |  |  |  |  | 0.01
2012 |  |  |  | 4846.78 |  |  |  | 7977 |  |  |  |  | 610 | [10 empty] | 90.05 |  |  |  |  | 90.05 | [5 empty] | 90.45 |  |  | 90.81 |  |  |  |  | 0.50 |  | 0.45 | [8 empty] | 9.49 |  |  |  |  | 0.00
2013 |  |  |  | 5076.15 |  |  |  | 8243 |  |  |  |  | 610 | [10 empty] | 93.46 |  |  |  |  | 93.46 | [5 empty] | 94.99 |  |  | 94.10 |  |  |  |  | 0.17 |  | 0.16 | [8 empty] | 6.38 |  |  |  |  | 0.00
2014 |  |  |  | 4929.31 |  |  |  | 8078 |  |  |  |  | 619 | [10 empty] | 91.99 |  |  |  |  | 92.07 | [5 empty] | 90.91 |  |  | 92.21 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.93 |  |  |  |  | 0.08
2015 |  |  |  | 4519.98 |  |  |  | 7410 |  |  |  |  | 619 | [10 empty] | 86.17 |  |  |  |  | 86.17 | [5 empty] | 83.36 |  |  | 84.59 |  |  |  |  | 6.43 |  | 5.93 | [8 empty] | 7.91 |  |  |  |  | 0.00
2016 |  |  |  | 5259.45 |  |  |  | 8584 |  |  |  |  | 619 | [10 empty] | 99.80 |  |  |  |  | 99.80 | [5 empty] | 96.73 |  |  | 97.72 |  |  |  |  | 0.12 |  | 0.12 | [8 empty] | 0.09 |  |  |  |  | 0.00
2017 |  |  |  | 4768.41 |  |  |  | 7804 |  |  |  |  | 619 | [10 empty] | 87.96 |  |  |  |  | 88.41 | [5 empty] | 87.94 |  |  | 89.09 |  |  |  |  | 0.38 |  | 0.34 | [8 empty] | 11.25 |  |  |  |  | 0.45
2018 |  |  |  | 4767.33 |  |  |  | 7756 |  |  |  |  | 619 | [10 empty] | 87.93 |  |  |  |  | 87.93 | [5 empty] | 87.92 |  |  | 88.54 |  |  |  |  | 1.57 |  | 1.41 | [8 empty] | 10.67 |  |  |  |  | 0.00
2019 |  |  |  | 5341.24 |  |  |  | 8664 |  |  |  |  | 619 | [10 empty] | 98.82 |  |  |  |  | 98.82 | [5 empty] | 98.50 |  |  | 98.90 |  |  |  |  | 1.11 |  | 1.11 | [8 empty] | 0.07 |  |  |  |  | 0.00
2020 |  |  |  | 4753.88 |  |  |  | 7870 |  |  |  |  | 619 | [10 empty] | 90.05 |  |  |  |  | 90.36 | [5 empty] | 87.43 |  |  | 89.59 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.64 |  |  |  |  | 0.31
2021 |  |  |  | 4788.17 |  |  |  | 7768 |  |  |  |  | 619 | [10 empty] | 88.15 |  |  |  |  | 88.19 | [5 empty] | 88.30 |  |  | 88.68 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.81 |  |  |  |  | 0.04
2022 |  |  |  | 5468.09 |  |  |  | 8760 |  |  |  |  | 619 | [10 empty] | 99.67 |  |  |  |  | 100.00 | [5 empty] | 100.84 |  |  | 100.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.33
2023 |  |  |  | 5184.38 |  |  |  | 8397 |  |  |  |  | 623 | [10 empty] | 94.92 |  |  |  |  | 95.53 | [5 empty] | 95.00 |  |  | 95.86 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.47 |  |  |  |  | 0.61
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2023 | [16 empty] | 2010 to 2023
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [43 empty] | 64
C. |  | Inspection, maintenance or repair combined with refuelling | [22 empty] | 363 | [16 empty] | 627
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [55 empty] | 37
L. |  | Human factor related | [43 empty] | 0
Subtotal | [24 empty] | 363 | [16 empty] | 627 |  |  |  | 64 | [11 empty] | 37
Total | [24 empty] | 363 | [16 empty] | 728
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2023 | [16 empty] | 2010 to 2023
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [38 empty] | 9
16. |  |  | Steam generation systems | [38 empty] | 9
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [38 empty] | 2
31. |  |  | Turbine and auxiliaries | [38 empty] | 40
32. |  |  | Feedwater and Main Steam System | [38 empty] | 0
34. |  |  | Miscellaneous Systems | [38 empty] | 9
42. |  |  | Electrical Power Supply Systems | [38 empty] | 3
Total | [41 empty] | 72
RUP revision during the year (2023) due to power uprate
RUP at the end of previous year : 619 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
January | [5 empty] | 623 |  |  |  |  | Improved measurement (<2%) | [14 empty] | Balance of plant | [13 empty] | Power Uprate
Highlights (2023)
The unit was shutdown for 310 refuelling outage from April 1 to April 16.

## QINSHAN 2-4
2023 Operating Experience
CN-15 | [9 empty] | QINSHAN 2-4 | [28 empty] | CHINA
Status at end of year | [8 empty] | : | Operational
Operator | [8 empty] | : | CNNO (CNNC Nuclear Operation Management Company Limited)
Owner | [8 empty] | : | NPQJVC (NUCLEAR POWER PLANT QINSHAN JOINT VENTURE COMPANY LTD.)
Reactor Supplier | [8 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [8 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [30 empty] | Key Dates
Reactor type and model | [14 empty] | : |  |  | PWR / CNP-600 | [12 empty] | Construction Date | [16 empty] | : |  |  | 2007-01-28
Thermal power | [14 empty] | : |  |  | 1930 | [9 empty] | MWth |  |  | Grid Date | [16 empty] | : |  |  | 2011-11-25
Gross electrical power | [14 empty] | : |  |  | 660 | [9 empty] | MWe |  |  | Commercial Date | [16 empty] | : |  |  | 2011-12-30
Reference unit power (net) | [14 empty] | : |  |  | 623 | [9 empty] | MWe |  |  | Age at end of year | [16 empty] | : |  |  | 12 years
Design Characteristics
| Primary Systems | [31 empty] | Operating coolant pressure [MPa] | [16 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [15 empty] | : |  |  | Vertical | [12 empty] | Reactor outlet temperature [°C] | [16 empty] | : |  |  | 315.2
| Fuel material | [15 empty] | : |  |  | UO2 | [12 empty] | Number of SG | [16 empty] | : |  |  | 2
| Refuelling type | [15 empty] | : |  |  | OFF-line | [12 empty] | Containment type | [16 empty] | : |  |  | Single
| Moderator material | [15 empty] | : |  |  | H2O | [12 empty] | Containment design pressure [MPa] | [16 empty] | : |  |  | 0.45
| Average fuel enrichment [% of U235] | [15 empty] | : |  |  | 3.25 | [12 empty] | Secondary systems
| Refuelling frequency [month] | [15 empty] | : |  |  | 12 | [12 empty] | Number of turbine-generators per unit/reactor | [16 empty] | : |  |  | 1
| Part of the core refuelled [%] | [15 empty] | : |  |  | 33.3 | [12 empty] | Turbine speed [rpm] | [16 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [15 empty] | : |  |  | 50000 | [12 empty] | Number of LP cylinders per turbine | [16 empty] | : |  |  | 3
| Active core diameter [m] | [15 empty] | : |  |  | 2.67 | [12 empty] | HP cylinder inlet steam pressure [MPa] | [16 empty] | : |  |  | 6.41
| Active core height/length [m] | [15 empty] | : |  |  | 3.6576 | [12 empty] | Output voltage [kV] | [16 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [15 empty] | : |  |  | 121 | [12 empty] | Primary means of condenser cooling | [16 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [15 empty] | : |  |  | 16.09 | [12 empty] | Number of main condensate pumps | [16 empty] | : |  |  | 3
| Number of control rod assemblies | [15 empty] | : |  |  | 33 | [12 empty] | Number of FW pumps for full power operation | [16 empty] | : |  |  | 2
| Number of external reactor coolant loops | [15 empty] | : |  |  | 2 | [12 empty] | Number of on-site safety related diesel generators | [16 empty] | : |  |  | 2
| Coolant type | [15 empty] | : |  |  | H2O | [12 empty] | Non-electrical applications | [16 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [20 empty] | : | 5419.73 GW(e).h | [9 empty] | Forced Loss Rate (FLR) | [16 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [20 empty] | : | 99.35 % | [9 empty] | Unplanned Capability Loss Factor (UCL) | [16 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [20 empty] | : | 99.96 % | [9 empty] | Planned Unavailability Factor (PUF) | [16 empty] | : |  |  | 0.04 %
Load Factor (LF) | [20 empty] | : | 99.31 % | [9 empty] | Externally cause unavailability (XUF) | [16 empty] | : |  |  | 0.61 %
Operating Factor (OF) | [20 empty] | : | 100 % | [9 empty] | Total off-line time | [16 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan |  | Feb |  |  |  |  | Mar |  | Apr | [8 empty] | May |  |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 442.83 |  | 410.83 |  |  |  |  | 469.19 |  | 428.60 | [8 empty] | 467.74 |  |  |  | 452.93 | [6 empty] | 456.36 |  | 455.12 |  |  |  |  | 445.85 |  |  | 468.60 |  |  | 452.53 | [9 empty] | 469.16 |  |  | 5419.73
EAF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 99.92 | [6 empty] | 97.28 |  | 97.04 |  |  |  |  | 98.42 |  |  | 99.84 |  |  | 99.78 | [9 empty] | 100.00 |  |  | 99.35
UCF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 99.75 |  | 100.00 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.78 | [9 empty] | 100.00 |  |  | 99.96
LF [%] |  |  |  |  | 95.54 |  | 98.13 |  |  |  |  | 101.23 |  | 95.55 | [8 empty] | 100.91 |  |  |  | 100.97 | [6 empty] | 98.46 |  | 98.19 |  |  |  |  | 99.40 |  |  | 101.10 |  |  | 100.89 | [9 empty] | 101.22 |  |  | 99.31
OF [%] |  |  |  |  | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.00 | [6 empty] | 0.25 |  | 0.00 |  |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.22 | [9 empty] | 0.00 |  |  | 0.04
XUF [%] |  |  |  |  | 0.00 |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  | 0.08 | [6 empty] | 2.48 |  | 2.96 |  |  |  |  | 1.58 |  |  | 0.16 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.61
Historical Summary
Lifetime energy generation | [15 empty] | : |  |  | 59576 GW(e).h | [12 empty] | Cumulative Forced Loss Rate (FLR) | [22 empty] | : | 0.13 %
Cumulative Energy Availability Factor (EAF) | [15 empty] | : |  |  | 91.62 % | [12 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [22 empty] | : | 0.12 %
Cumulative Unit Capability Factor (UCF) | [15 empty] | : |  |  | 91.83 % | [12 empty] | Cumulative Planned Unavailability Factor (PUF) | [22 empty] | : | 8.06 %
Cumulative Load Factor (LF) | [15 empty] | : |  |  | 91.64 % | [12 empty] | Cumulative Externally cause unavailability (XUF) | [22 empty] | : | 0.21 %
Cumulative Operating Factor (OF) | [15 empty] | : |  |  | 91.99 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  |  | Time Online |  |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  |  | [Hours] |  |  |  |  | [MW] | [10 empty] | [%] |  |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2011 |  |  |  | 257.02 |  |  |  | 614 |  |  |  |  | 610 | [10 empty] | 0.00 |  |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 5195.81 |  |  |  | 8438 |  |  |  |  | 610 | [10 empty] | 95.79 |  |  |  |  | 95.79 | [5 empty] | 96.97 |  |  | 96.06 |  |  |  |  | 0.04 |  | 0.04 | [8 empty] | 4.17 |  |  |  |  | 0.00
2013 |  |  |  | 4591.39 |  |  |  | 7428 |  |  |  |  | 610 | [10 empty] | 84.25 |  |  |  |  | 84.25 | [5 empty] | 85.92 |  |  | 84.79 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.75 |  |  |  |  | 0.00
2014 |  |  |  | 4844.49 |  |  |  | 7905 |  |  |  |  | 610 | [10 empty] | 88.86 |  |  |  |  | 89.62 | [5 empty] | 90.66 |  |  | 90.24 |  |  |  |  | 1.32 |  | 1.20 | [8 empty] | 9.19 |  |  |  |  | 0.75
2015 |  |  |  | 4837.34 |  |  |  | 7994 |  |  |  |  | 610 | [10 empty] | 91.06 |  |  |  |  | 91.06 | [5 empty] | 90.53 |  |  | 91.26 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.94 |  |  |  |  | 0.00
2016 |  |  |  | 4983.82 |  |  |  | 8130 |  |  |  |  | 610 | [10 empty] | 91.93 |  |  |  |  | 91.93 | [5 empty] | 93.01 |  |  | 92.55 |  |  |  |  | 0.07 |  | 0.07 | [8 empty] | 8.00 |  |  |  |  | 0.00
2017 |  |  |  | 4899.45 |  |  |  | 7993 |  |  |  |  | 619 | [10 empty] | 90.14 |  |  |  |  | 90.61 | [5 empty] | 90.35 |  |  | 91.24 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.39 |  |  |  |  | 0.48
2018 |  |  |  | 4786.77 |  |  |  | 7760 |  |  |  |  | 619 | [10 empty] | 88.16 |  |  |  |  | 88.16 | [5 empty] | 88.28 |  |  | 88.58 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.84 |  |  |  |  | 0.00
2019 |  |  |  | 4812.21 |  |  |  | 7815 |  |  |  |  | 619 | [10 empty] | 91.91 |  |  |  |  | 91.91 | [5 empty] | 88.75 |  |  | 89.21 |  |  |  |  | 0.10 |  | 0.09 | [8 empty] | 8.00 |  |  |  |  | 0.00
2020 |  |  |  | 5276.68 |  |  |  | 8784 |  |  |  |  | 619 | [10 empty] | 99.97 |  |  |  |  | 99.97 | [5 empty] | 97.05 |  |  | 100.00 |  |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.03 |  |  |  |  | 0.00
2021 |  |  |  | 4882.83 |  |  |  | 7898 |  |  |  |  | 619 | [10 empty] | 88.97 |  |  |  |  | 89.04 | [5 empty] | 90.05 |  |  | 90.16 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.96 |  |  |  |  | 0.07
2022 |  |  |  | 4812.10 |  |  |  | 7861 |  |  |  |  | 619 | [10 empty] | 88.83 |  |  |  |  | 89.45 | [5 empty] | 88.74 |  |  | 89.74 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.55 |  |  |  |  | 0.62
2023 |  |  |  | 5419.73 |  |  |  | 8760 |  |  |  |  | 623 | [10 empty] | 99.35 |  |  |  |  | 99.96 | [5 empty] | 99.31 |  |  | 100.00 |  |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  |  |  | 0.61
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[25 empty] | 2023 | [16 empty] | 2011 to 2023
Outage Cause | [24 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
[25 empty] | Planned |  |  |  |  | Unplanned | [6 empty] | External |  |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [43 empty] | 1
C. |  | Inspection, maintenance or repair combined with refuelling | [39 empty] | 644
D. |  | Inspection, maintenance or repair without refuelling | [39 empty] | 22
E. |  | Testing of plant systems or components | [39 empty] | 7
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [55 empty] | 22
Subtotal | [41 empty] | 673 |  |  |  | 1 | [11 empty] | 22
Total | [24 empty] | 0 | [16 empty] | 696
Equipment Related Unplanned Full Outages, Analysis by System
System | [24 empty] | 2023 | [16 empty] | 2011 to 2023
[25 empty] | Hours Lost | [16 empty] | Average hours lost per reactor-year
35. |  |  | All other I&C Systems | [38 empty] | 1
Total | [41 empty] | 1
RUP revision during the year (2023) due to power uprate
RUP at the end of previous year : 619 [MWe]
Month | [5 empty] | Capacity [MWe] |  |  |  |  | Power Uprate | [14 empty] | Main modifications | [13 empty] | Description
January | [5 empty] | 623 |  |  |  |  | Improved measurement (<2%) | [14 empty] | Balance of plant | [13 empty] | Power Uprate

## QINSHAN 3-1
2023 Operating Experience
CN-8 | [8 empty] | QINSHAN 3-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CNNO (CNNC Nuclear Operation Management Company Limited)
Owner | [7 empty] | : | TQNPC (Qinshan Third nuclear power Co., LTD)
Reactor Supplier | [7 empty] | : | AECL (ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | Hit (Japan Hitachi Company.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1998-06-08
Thermal power | [12 empty] | : |  |  | 2064 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-11-19
Gross electrical power | [12 empty] | : |  |  | 728 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-12-31
Reference unit power (net) | [12 empty] | : |  |  | 677 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 21 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.89
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.124
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.71 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 60 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7186 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 6.28 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 25.35 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5291.35 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.69 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.32 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.64 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.74 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.62 %
Load Factor (LF) | [18 empty] | : | 89.22 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.42 %
Operating Factor (OF) | [18 empty] | : | 92.09 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 693 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 463.10 | 442.95 |  |  |  | 449.65 |  | 74.29 | [8 empty] | 495.57 |  |  | 470.76 | [6 empty] | 474.37 |  | 472.60 |  |  |  | 466.18 |  |  | 494.38 |  |  | 484.19 | [9 empty] | 503.32 |  |  | 5291.35
EAF [%] |  |  |  |  | 92.47 | 100.00 |  |  |  | 90.34 |  | 17.30 | [8 empty] | 98.57 |  |  | 97.35 | [6 empty] | 96.37 |  | 96.57 |  |  |  | 96.47 |  |  | 98.31 |  |  | 99.38 | [9 empty] | 100.00 |  |  | 90.32
UCF [%] |  |  |  |  | 92.47 | 100.00 |  |  |  | 90.34 |  | 17.30 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.74
LF [%] |  |  |  |  | 91.94 | 97.36 |  |  |  | 89.27 |  | 15.24 | [8 empty] | 98.39 |  |  | 96.58 | [6 empty] | 94.18 |  | 93.83 |  |  |  | 95.64 |  |  | 98.15 |  |  | 99.33 | [9 empty] | 99.93 |  |  | 89.22
OF [%] |  |  |  |  | 93.68 | 100.00 |  |  |  | 90.46 |  | 20.14 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.09
FLR [%] |  |  |  |  | 7.53 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.69
UCL [%] |  |  |  |  | 7.53 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.64
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 9.66 |  | 82.70 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.02 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.62
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.43 |  |  | 2.65 | [6 empty] | 3.61 |  | 3.43 |  |  |  | 3.53 |  |  | 1.69 |  |  | 0.62 | [9 empty] | 0.00 |  |  | 1.42
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 110243.35 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.43 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.17 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.31 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.72 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.96 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 90.34 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.55 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.9 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | Data not provided
2003 |  |  |  | 5174.75 |  |  | 7977 |  |  |  | 650 | [10 empty] | 86.59 |  |  |  | 89.65 | [5 empty] | 90.88 |  |  | 91.06 |  |  |  | 10.35 |  | 10.35 | [8 empty] | 0.00 |  |  |  |  | 3.06
2004 |  |  |  | 4405.52 |  |  | 6745 |  |  |  | 650 | [10 empty] | 75.60 |  |  |  | 75.61 | [5 empty] | 77.16 |  |  | 76.79 |  |  |  | 2.31 |  | 1.78 | [8 empty] | 22.61 |  |  |  |  | 0.01
2005 |  |  |  | 4781.60 |  |  | 7249 |  |  |  | 650 | [10 empty] | 82.43 |  |  |  | 82.50 | [5 empty] | 83.98 |  |  | 82.75 |  |  |  | 2.18 |  | 1.84 | [8 empty] | 15.66 |  |  |  |  | 0.07
2006 |  |  |  | 5577.79 |  |  | 8484 |  |  |  | 650 | [10 empty] | 96.34 |  |  |  | 96.34 | [5 empty] | 97.96 |  |  | 96.85 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 3.60 |  |  |  |  | 0.00
2007 |  |  |  | 5020.40 |  |  | 7597 |  |  |  | 650 | [10 empty] | 86.41 |  |  |  | 86.41 | [5 empty] | 88.17 |  |  | 86.72 |  |  |  | 0.95 |  | 0.82 | [8 empty] | 12.76 |  |  |  |  | 0.00
2008 |  |  |  | 5328.57 |  |  | 8051 |  |  |  | 650 | [10 empty] | 91.11 |  |  |  | 91.21 | [5 empty] | 93.33 |  |  | 91.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.79 |  |  |  |  | 0.10
2009 |  |  |  | 5326.22 |  |  | 8076 |  |  |  | 650 | [10 empty] | 91.91 |  |  |  | 91.91 | [5 empty] | 93.54 |  |  | 92.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.09 |  |  |  |  | 0.00
2010 |  |  |  | 5216.34 |  |  | 7884 |  |  |  | 650 | [10 empty] | 89.71 |  |  |  | 89.71 | [5 empty] | 91.61 |  |  | 90.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 10.27 |  |  |  |  | 0.00
2011 |  |  |  | 5388.51 |  |  | 8131 |  |  |  | 650 | [10 empty] | 92.55 |  |  |  | 92.55 | [5 empty] | 94.63 |  |  | 92.82 |  |  |  | 1.96 |  | 1.85 | [8 empty] | 5.60 |  |  |  |  | 0.00
2012 |  |  |  | 5544.58 |  |  | 8462 |  |  |  | 650 | [10 empty] | 96.25 |  |  |  | 96.25 | [5 empty] | 97.11 |  |  | 96.33 |  |  |  | 0.34 |  | 0.33 | [8 empty] | 3.41 |  |  |  |  | 0.00
2013 |  |  |  | 5237.40 |  |  | 7949 |  |  |  | 650 | [10 empty] | 89.89 |  |  |  | 89.89 | [5 empty] | 91.98 |  |  | 90.74 |  |  |  | 1.22 |  | 1.11 | [8 empty] | 9.00 |  |  |  |  | 0.00
2014 |  |  |  | 5594.85 |  |  | 8451 |  |  |  | 650 | [10 empty] | 96.13 |  |  |  | 96.13 | [5 empty] | 98.26 |  |  | 96.47 |  |  |  | 3.83 |  | 3.83 | [8 empty] | 0.04 |  |  |  |  | 0.00
2015 |  |  |  | 4758.34 |  |  | 7292 |  |  |  | 677 | [10 empty] | 83.19 |  |  |  | 83.19 | [5 empty] | 80.23 |  |  | 83.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.81 |  |  |  |  | 0.00
2016 |  |  |  | 5476.06 |  |  | 8351 |  |  |  | 677 | [10 empty] | 94.90 |  |  |  | 94.90 | [5 empty] | 92.08 |  |  | 95.07 |  |  |  | 5.08 |  | 5.08 | [8 empty] | 0.02 |  |  |  |  | 0.00
2017 |  |  |  | 4542.77 |  |  | 7000 |  |  |  | 677 | [10 empty] | 78.63 |  |  |  | 79.83 | [5 empty] | 76.60 |  |  | 79.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.17 |  |  |  |  | 1.20
2018 |  |  |  | 5729.05 |  |  | 8657 |  |  |  | 677 | [10 empty] | 98.76 |  |  |  | 99.96 | [5 empty] | 96.60 |  |  | 98.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  |  |  | 1.20
2019 |  |  |  | 5061.34 |  |  | 7709 |  |  |  | 677 | [10 empty] | 86.01 |  |  |  | 87.63 | [5 empty] | 85.34 |  |  | 88.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 12.34 |  |  |  |  | 1.62
2020 |  |  |  | 5714.70 |  |  | 8699 |  |  |  | 677 | [10 empty] | 98.95 |  |  |  | 99.92 | [5 empty] | 96.10 |  |  | 99.03 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 0.01 |  |  |  |  | 0.97
2021 |  |  |  | 5073.94 |  |  | 7745 |  |  |  | 677 | [10 empty] | 89.51 |  |  |  | 89.51 | [5 empty] | 85.56 |  |  | 88.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.49 |  |  |  |  | 0.00
2022 |  |  |  | 5778.63 |  |  | 8760 |  |  |  | 677 | [10 empty] | 98.11 |  |  |  | 99.90 | [5 empty] | 97.44 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.09 |  |  |  |  | 1.80
2023 |  |  |  | 5291.35 |  |  | 8067 |  |  |  | 677 | [10 empty] | 90.32 |  |  |  | 91.74 | [5 empty] | 89.22 |  |  | 92.09 |  |  |  | 0.69 |  | 0.64 | [8 empty] | 7.62 |  |  |  |  | 1.42
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2002 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 48 | [14 empty] | 100
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 646 | [14 empty] | 680
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
Z. |  | Other | [51 empty] | 4
Subtotal | [22 empty] | 646 |  |  |  | 48 | [10 empty] | 680 |  |  |  | 100 | [11 empty] | 15
Total | [22 empty] | 694 | [14 empty] | 795
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2002 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 33
16. |  |  | Steam generation systems | [34 empty] | 9
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [19 empty] | 48 | [14 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 10
42. |  |  | Electrical Power Supply Systems | [34 empty] | 35
Total | [22 empty] | 48 | [14 empty] | 109
Highlights (2023)
The unit was shutdown for 12th planned outage from March 29 to April 24.

## QINSHAN 3-2
2023 Operating Experience
CN-9 | [8 empty] | QINSHAN 3-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CNNO (CNNC Nuclear Operation Management Company Limited)
Owner | [7 empty] | : | TQNPC (Qinshan Third nuclear power Co., LTD)
Reactor Supplier | [7 empty] | : | AECL (ATOMIC ENERGY OF CANADA, LTD.)
Turbine Supplier | [7 empty] | : | Hit (Japan Hitachi Company.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PHWR / CANDU 6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1998-09-25
Thermal power | [12 empty] | : |  |  | 2064 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2003-06-12
Gross electrical power | [12 empty] | : |  |  | 728 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2003-07-24
Reference unit power (net) | [12 empty] | : |  |  | 677 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 20 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 9.89
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Horizontal | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 310
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | D2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.124
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 0.71 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 60 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 7186 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 6.28 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.51
| Active core height/length [m] | [13 empty] | : |  |  | 5.94 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 4560 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 25.35 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 21 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | D2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5737.33 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 98.61 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 96.74 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.39 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 499.11 | 443.20 |  |  |  | 498.94 |  | 456.21 | [8 empty] | 493.68 |  |  | 468.57 | [6 empty] | 471.17 |  | 469.98 |  |  |  | 463.56 |  |  | 491.78 |  |  | 480.84 | [9 empty] | 500.30 |  |  | 5737.33
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 98.77 |  |  | 97.43 | [6 empty] | 96.43 |  | 96.59 |  |  |  | 96.68 |  |  | 98.31 |  |  | 99.17 | [9 empty] | 100.00 |  |  | 98.61
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.97 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.98 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 99.09 | 97.42 |  |  |  | 99.06 |  | 93.59 | [8 empty] | 98.01 |  |  | 96.13 | [6 empty] | 93.54 |  | 93.31 |  |  |  | 95.10 |  |  | 97.64 |  |  | 98.65 | [9 empty] | 99.33 |  |  | 96.74
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.03 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.23 |  |  | 2.57 | [6 empty] | 3.54 |  | 3.41 |  |  |  | 3.32 |  |  | 1.69 |  |  | 0.81 | [9 empty] | 0.00 |  |  | 1.39
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 107901 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.52 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.46 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.54 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.92 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.46 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.91 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2003 |  |  |  | Data not provided
2004 |  |  |  | 5358.59 |  |  | 8236 |  |  |  | 665 | [10 empty] | 92.43 |  |  |  | 93.00 | [5 empty] | 91.74 |  |  | 93.76 |  |  |  | 2.84 |  | 2.72 | [8 empty] | 4.28 |  |  |  |  | 0.57
2005 |  |  |  | 4604.65 |  |  | 7014 |  |  |  | 665 | [10 empty] | 80.14 |  |  |  | 80.24 | [5 empty] | 79.04 |  |  | 80.07 |  |  |  | 0.90 |  | 0.73 | [8 empty] | 19.03 |  |  |  |  | 0.11
2006 |  |  |  | 5038.17 |  |  | 7721 |  |  |  | 650 | [10 empty] | 86.72 |  |  |  | 86.72 | [5 empty] | 88.48 |  |  | 88.14 |  |  |  | 0.25 |  | 0.22 | [8 empty] | 13.06 |  |  |  |  | 0.00
2007 |  |  |  | 5675.70 |  |  | 8559 |  |  |  | 650 | [10 empty] | 97.55 |  |  |  | 97.55 | [5 empty] | 99.68 |  |  | 97.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.45 |  |  |  |  | 0.00
2008 |  |  |  | 5083.41 |  |  | 7697 |  |  |  | 650 | [10 empty] | 87.21 |  |  |  | 87.32 | [5 empty] | 89.03 |  |  | 87.63 |  |  |  | 0.55 |  | 0.48 | [8 empty] | 12.20 |  |  |  |  | 0.11
2009 |  |  |  | 5523.74 |  |  | 8359 |  |  |  | 650 | [10 empty] | 95.36 |  |  |  | 95.36 | [5 empty] | 97.01 |  |  | 95.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.64 |  |  |  |  | 0.00
2010 |  |  |  | 5341.46 |  |  | 8099 |  |  |  | 650 | [10 empty] | 92.06 |  |  |  | 92.06 | [5 empty] | 93.81 |  |  | 92.45 |  |  |  | 1.93 |  | 1.82 | [8 empty] | 6.13 |  |  |  |  | 0.00
2011 |  |  |  | 5261.09 |  |  | 7951 |  |  |  | 650 | [10 empty] | 90.34 |  |  |  | 91.00 | [5 empty] | 92.40 |  |  | 90.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.00 |  |  |  |  | 0.66
2012 |  |  |  | 5210.75 |  |  | 7980 |  |  |  | 650 | [10 empty] | 90.44 |  |  |  | 90.44 | [5 empty] | 91.26 |  |  | 90.85 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 9.53 |  |  |  |  | 0.00
2013 |  |  |  | 5794.09 |  |  | 8760 |  |  |  | 650 | [10 empty] | 99.85 |  |  |  | 99.85 | [5 empty] | 101.76 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.15 |  |  |  |  | 0.00
2014 |  |  |  | 5223.32 |  |  | 7892 |  |  |  | 650 | [10 empty] | 89.99 |  |  |  | 89.99 | [5 empty] | 91.73 |  |  | 90.09 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 9.98 |  |  |  |  | 0.00
2015 |  |  |  | 5623.82 |  |  | 8553 |  |  |  | 677 | [10 empty] | 97.30 |  |  |  | 97.30 | [5 empty] | 94.83 |  |  | 97.64 |  |  |  | 2.69 |  | 2.69 | [8 empty] | 0.02 |  |  |  |  | 0.00
2016 |  |  |  | 4555.03 |  |  | 6979 |  |  |  | 677 | [10 empty] | 79.27 |  |  |  | 79.27 | [5 empty] | 76.60 |  |  | 79.45 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 20.71 |  |  |  |  | 0.00
2017 |  |  |  | 5598.62 |  |  | 8580 |  |  |  | 677 | [10 empty] | 98.19 |  |  |  | 99.96 | [5 empty] | 94.40 |  |  | 97.95 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.01 |  |  |  |  | 1.76
2018 |  |  |  | 4685.15 |  |  | 7183 |  |  |  | 677 | [10 empty] | 81.58 |  |  |  | 82.62 | [5 empty] | 79.00 |  |  | 82.00 |  |  |  | 0.94 |  | 0.78 | [8 empty] | 16.60 |  |  |  |  | 1.03
2019 |  |  |  | 5716.87 |  |  | 8686 |  |  |  | 677 | [10 empty] | 98.02 |  |  |  | 99.85 | [5 empty] | 96.40 |  |  | 99.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.15 |  |  |  |  | 1.83
2020 |  |  |  | 5261.05 |  |  | 8014 |  |  |  | 677 | [10 empty] | 91.04 |  |  |  | 91.04 | [5 empty] | 88.47 |  |  | 91.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.96 |  |  |  |  | 0.00
2021 |  |  |  | 5607.86 |  |  | 8540 |  |  |  | 677 | [10 empty] | 98.61 |  |  |  | 98.61 | [5 empty] | 94.56 |  |  | 97.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.39 |  |  |  |  | 0.00
2022 |  |  |  | 4979.49 |  |  | 7573 |  |  |  | 677 | [10 empty] | 84.62 |  |  |  | 86.31 | [5 empty] | 83.96 |  |  | 86.45 |  |  |  | 0.00 |  | 1.20 | [8 empty] | 12.49 |  |  |  |  | 1.69
2023 |  |  |  | 5737.33 |  |  | 8760 |  |  |  | 677 | [10 empty] | 98.61 |  |  |  | 100.00 | [5 empty] | 96.74 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 1.39
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2003 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 32
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 90
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 547
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 23
L. |  | Human factor related | [39 empty] | 5
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 5
Z. |  | Other | [39 empty] | 5
Subtotal | [37 empty] | 637 |  |  |  | 42 | [11 empty] | 28
Total | [22 empty] | 0 | [14 empty] | 707
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2003 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
12. |  |  | Reactor I&C Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 9
16. |  |  | Steam generation systems | [34 empty] | 3
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 44

## QINSHAN-1
2023 Operating Experience
CN-1 | [8 empty] | QINSHAN-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CNNO (CNNC Nuclear Operation Management Company Limited)
Owner | [7 empty] | : | QNPC (QINSHAN NUCLEAR POWER COMPANY)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-03-20
Thermal power | [12 empty] | : |  |  | 966 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1991-12-15
Gross electrical power | [12 empty] | : |  |  | 330 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-04-01
Reference unit power (net) | [12 empty] | : |  |  | 326 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 308.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 2.65
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.486 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.45
| Active core height/length [m] | [13 empty] | : |  |  | 2.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 18
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2659.67 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.61 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.72 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.28 %
Load Factor (LF) | [18 empty] | : | 93.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.1 %
Operating Factor (OF) | [18 empty] | : | 95.1 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 429 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 237.71 | 219.76 |  |  |  | 243.11 |  | 235.57 | [8 empty] | 90.08 |  |  | 230.55 | [6 empty] | 230.47 |  | 229.89 |  |  |  | 227.42 |  |  | 236.89 |  |  | 234.86 | [9 empty] | 243.35 |  |  | 2659.67
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 37.74 |  |  | 98.79 | [6 empty] | 95.70 |  | 95.46 |  |  |  | 97.51 |  |  | 99.56 |  |  | 99.92 | [9 empty] | 100.00 |  |  | 93.61
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 37.80 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.72
LF [%] |  |  |  |  | 98.01 | 100.32 |  |  |  | 100.23 |  | 100.36 | [8 empty] | 37.14 |  |  | 98.22 | [6 empty] | 95.02 |  | 94.78 |  |  |  | 96.89 |  |  | 97.67 |  |  | 100.06 | [9 empty] | 100.33 |  |  | 93.13
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 42.34 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.10
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 62.20 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.28
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.06 |  |  | 1.21 | [6 empty] | 4.30 |  | 4.54 |  |  |  | 2.49 |  |  | 0.44 |  |  | 0.08 | [9 empty] | 0.00 |  |  | 1.10
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 66886 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.53 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.06 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.37 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.05 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.59 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.33 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.98 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.62 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 1648.58 |  |  | 6439 |  |  |  | 279 | [10 empty] | 62.02 |  |  |  | 67.45 | [5 empty] | 62.67 |  |  | 70.06 |  |  |  | 3.98 |  | 2.80 | [8 empty] | 29.75 |  |  |  |  | 5.44
1995 |  |  |  | 2063.90 |  |  | 7886 |  |  |  | 300 | [10 empty] | 82.32 |  |  |  | 86.80 | [5 empty] | 78.53 |  |  | 90.02 |  |  |  | 2.25 |  | 2.00 | [8 empty] | 11.20 |  |  |  |  | 4.49
1996 |  |  |  | 2073.72 |  |  | 7479 |  |  |  | 279 | [10 empty] | 81.19 |  |  |  | 81.19 | [5 empty] | 84.62 |  |  | 85.14 |  |  |  | 1.17 |  | 0.96 | [8 empty] | 17.85 |  |  |  |  | 0.00
1997 |  |  |  | 2011.67 |  |  | 7185 |  |  |  | 300 | [10 empty] | 76.11 |  |  |  | 81.78 | [5 empty] | 76.55 |  |  | 82.02 |  |  |  | 2.87 |  | 2.42 | [8 empty] | 15.80 |  |  |  |  | 5.67
1998 |  |  |  | 1149.49 |  |  | 4331 |  |  |  | 279 | [10 empty] | 42.59 |  |  |  | 48.78 | [5 empty] | 47.03 |  |  | 49.44 |  |  |  | 0.98 |  | 0.48 | [8 empty] | 50.74 |  |  |  |  | 6.19
1999 |  |  |  | 680.88 |  |  | 2519 |  |  |  | 279 | [10 empty] | 27.76 |  |  |  | 27.76 | [5 empty] | 27.86 |  |  | 28.76 |  |  |  | 71.97 |  | 71.28 | [8 empty] | 0.96 |  |  |  |  | 0.00
2000 |  |  |  | 2035.48 |  |  | 6840 |  |  |  | 300 | [10 empty] | 77.61 |  |  |  | 77.61 | [5 empty] | 77.24 |  |  | 77.87 |  |  |  | 2.79 |  | 2.23 | [8 empty] | 20.16 |  |  |  |  | 0.00
2001 |  |  |  | 2319.37 |  |  | 8370 |  |  |  | 279 | [10 empty] | 92.82 |  |  |  | 93.47 | [5 empty] | 94.90 |  |  | 95.55 |  |  |  | 0.51 |  | 0.48 | [8 empty] | 6.05 |  |  |  |  | 0.64
2002 |  |  |  | 1783.25 |  |  | 5989 |  |  |  | 279 | [10 empty] | 66.31 |  |  |  | 69.21 | [5 empty] | 72.96 |  |  | 68.37 |  |  |  | 1.40 |  | 0.98 | [8 empty] | 29.81 |  |  |  |  | 2.90
2003 |  |  |  | 2256.57 |  |  | 7798 |  |  |  | 288 | [10 empty] | 88.44 |  |  |  | 88.46 | [5 empty] | 89.44 |  |  | 89.02 |  |  |  | 0.24 |  | 0.21 | [8 empty] | 11.33 |  |  |  |  | 0.01
2004 |  |  |  | 2565.24 |  |  | 8784 |  |  |  | 288 | [10 empty] | 99.08 |  |  |  | 99.79 | [5 empty] | 101.40 |  |  | 100.00 |  |  |  | 0.11 |  | 0.11 | [8 empty] | 0.10 |  |  |  |  | 0.71
2005 |  |  |  | 2194.56 |  |  | 7693 |  |  |  | 288 | [10 empty] | 86.83 |  |  |  | 87.02 | [5 empty] | 86.99 |  |  | 87.82 |  |  |  | 0.53 |  | 0.46 | [8 empty] | 12.52 |  |  |  |  | 0.19
2006 |  |  |  | 2310.41 |  |  | 8086 |  |  |  | 288 | [10 empty] | 91.81 |  |  |  | 91.81 | [5 empty] | 91.58 |  |  | 92.31 |  |  |  | 0.05 |  | 0.29 | [8 empty] | 7.89 |  |  |  |  | 0.00
2007 |  |  |  | 2061.43 |  |  | 7218 |  |  |  | 288 | [10 empty] | 81.99 |  |  |  | 82.22 | [5 empty] | 81.71 |  |  | 82.40 |  |  |  | 0.10 |  | 0.08 | [8 empty] | 17.70 |  |  |  |  | 0.23
2008 |  |  |  | 2430.72 |  |  | 8434 |  |  |  | 288 | [10 empty] | 95.38 |  |  |  | 95.54 | [5 empty] | 96.08 |  |  | 96.02 |  |  |  | 1.02 |  | 2.99 | [8 empty] | 1.47 |  |  |  |  | 0.16
2009 |  |  |  | 2195.44 |  |  | 7704 |  |  |  | 288 | [10 empty] | 87.33 |  |  |  | 87.41 | [5 empty] | 87.02 |  |  | 87.95 |  |  |  | 2.20 |  | 1.96 | [8 empty] | 10.62 |  |  |  |  | 0.08
2010 |  |  |  | 2169.32 |  |  | 7398 |  |  |  | 298 | [10 empty] | 83.24 |  |  |  | 83.33 | [5 empty] | 84.27 |  |  | 84.45 |  |  |  | 0.47 |  | 6.03 | [8 empty] | 10.64 |  |  |  |  | 0.09
2011 |  |  |  | 2332.64 |  |  | 7762 |  |  |  | 298 | [10 empty] | 87.88 |  |  |  | 88.06 | [5 empty] | 89.36 |  |  | 88.61 |  |  |  | 0.41 |  | 1.20 | [8 empty] | 10.75 |  |  |  |  | 0.18
2012 |  |  |  | 2659.07 |  |  | 8784 |  |  |  | 298 | [10 empty] | 99.80 |  |  |  | 99.94 | [5 empty] | 101.58 |  |  | 100.00 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 0.05 |  |  |  |  | 0.14
2013 |  |  |  | 2158.84 |  |  | 7199 |  |  |  | 298 | [10 empty] | 80.86 |  |  |  | 80.98 | [5 empty] | 82.70 |  |  | 82.18 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 19.00 |  |  |  |  | 0.12
2014 |  |  |  | 2461.14 |  |  | 8221 |  |  |  | 298 | [10 empty] | 92.93 |  |  |  | 92.93 | [5 empty] | 94.28 |  |  | 93.85 |  |  |  | 2.07 |  | 1.97 | [8 empty] | 5.10 |  |  |  |  | 0.00
2015 |  |  |  | 2413.17 |  |  | 8003 |  |  |  | 298 | [10 empty] | 91.14 |  |  |  | 91.14 | [5 empty] | 92.44 |  |  | 91.36 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 8.76 |  |  |  |  | 0.00
2016 |  |  |  | 2418.29 |  |  | 8084 |  |  |  | 298 | [10 empty] | 91.75 |  |  |  | 91.75 | [5 empty] | 92.38 |  |  | 92.03 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 8.23 |  |  |  |  | 0.00
2017 |  |  |  | 2615.97 |  |  | 8760 |  |  |  | 298 | [10 empty] | 99.37 |  |  |  | 99.96 | [5 empty] | 100.21 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  |  |  | 0.60
2018 |  |  |  | 1509.11 |  |  | 5147 |  |  |  | 298 | [10 empty] | 55.80 |  |  |  | 55.80 | [5 empty] | 57.81 |  |  | 58.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 44.20 |  |  |  |  | 0.00
2019 |  |  |  | 2447.78 |  |  | 7782 |  |  |  | 298 | [10 empty] | 88.27 |  |  |  | 88.27 | [5 empty] | 93.77 |  |  | 88.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.73 |  |  |  |  | 0.00
2020 |  |  |  | 2496.95 |  |  | 8132 |  |  |  | 308 | [10 empty] | 92.28 |  |  |  | 92.28 | [5 empty] | 92.29 |  |  | 92.58 |  |  |  | 5.67 |  | 5.54 | [8 empty] | 2.18 |  |  |  |  | 0.00
2021 |  |  |  | 2560.13 |  |  | 7982 |  |  |  | 308 | [10 empty] | 90.71 |  |  |  | 90.71 | [5 empty] | 94.89 |  |  | 91.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.29 |  |  |  |  | 0.00
2022 |  |  |  | 2603.50 |  |  | 8161 |  |  |  | 326 | [10 empty] | 91.09 |  |  |  | 92.97 | [5 empty] | 91.17 |  |  | 93.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.03 |  |  |  |  | 1.88
2023 |  |  |  | 2659.67 |  |  | 8331 |  |  |  | 326 | [10 empty] | 93.61 |  |  |  | 94.72 | [5 empty] | 93.13 |  |  | 95.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.28 |  |  |  |  | 1.10
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1994 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 70
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 437 | [14 empty] | 1012
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 42
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 2
L. |  | Human factor related | [39 empty] | 12
Z. |  | Other | [39 empty] | 208 | [11 empty] | 1
Subtotal | [22 empty] | 437 | [14 empty] | 1054 |  |  |  | 292 | [11 empty] | 1
Total | [22 empty] | 437 | [14 empty] | 1347
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1994 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 16
12. |  |  | Reactor I&C Systems | [34 empty] | 11
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 0
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 17
Total | [37 empty] | 72
Highlights (2023)
The unit was shutdown for 22th planned outage from May 1 to May 19.

## SANMEN-1
2023 Operating Experience
CN-28 | [8 empty] | SANMEN-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SMNPC (SANMEN NUCLEAR POWER CO., LTD.)
Owner | [7 empty] | : | SMNPC (SANMEN NUCLEAR POWER CO., LTD.)
Reactor Supplier | [7 empty] | : | WH/MHI (WESTINGHOUSE ELECTRIC CORPORATION / MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / AP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-04-19
Thermal power | [12 empty] | : |  |  | 3400 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-06-30
Gross electrical power | [12 empty] | : |  |  | 1251 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-09-21
Reference unit power (net) | [12 empty] | : |  |  | 1157 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.407
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.7239 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.8 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50558 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.77 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 69 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 9887.28 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.86 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.62 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.85 %
Unit Capability Factor (UCF) | [18 empty] | : | 98.63 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.52 %
Load Factor (LF) | [18 empty] | : | 97.55 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.01 %
Operating Factor (OF) | [18 empty] | : | 98.94 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 93 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 856.02 | 777.50 |  |  |  | 774.50 |  | 832.93 | [8 empty] | 859.51 |  |  | 767.58 | [6 empty] | 833.38 |  | 832.34 |  |  |  | 807.48 |  |  | 852.90 |  |  | 832.89 | [9 empty] | 860.24 |  |  | 9887.28
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 89.97 |  | 99.99 | [8 empty] | 100.00 |  |  | 92.14 | [6 empty] | 96.81 |  | 96.69 |  |  |  | 96.93 |  |  | 99.18 |  |  | 99.98 | [9 empty] | 99.93 |  |  | 97.62
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 89.97 |  | 99.99 | [8 empty] | 100.00 |  |  | 93.79 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.98 |  |  | 99.98 | [9 empty] | 99.93 |  |  | 98.63
LF [%] |  |  |  |  | 99.44 | 100.00 |  |  |  | 89.97 |  | 99.99 | [8 empty] | 99.85 |  |  | 92.14 | [6 empty] | 96.81 |  | 96.69 |  |  |  | 96.93 |  |  | 99.08 |  |  | 99.98 | [9 empty] | 99.93 |  |  | 97.55
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 91.80 |  | 100.00 | [8 empty] | 100.00 |  |  | 95.56 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 98.94
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 10.03 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.86
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 10.03 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.85
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 6.21 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.02 | [9 empty] | 0.07 |  |  | 0.52
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.65 | [6 empty] | 3.19 |  | 3.31 |  |  |  | 3.07 |  |  | 0.80 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.01
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 49147.96 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.89 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.88 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.78 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.8 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 5.41 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 90.79 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.93 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 92.77 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 3330.63 |  |  | 3840 |  |  |  | 1157 | [10 empty] | 99.85 |  |  |  | 99.98 | [5 empty] | 99.39 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.13
2019 |  |  |  | 8987.29 |  |  | 7909 |  |  |  | 1157 | [10 empty] | 91.14 |  |  |  | 92.26 | [5 empty] | 88.67 |  |  | 90.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.74 |  |  |  |  | 1.12
2020 |  |  |  | 8757.82 |  |  | 7832 |  |  |  | 1157 | [10 empty] | 87.29 |  |  |  | 88.13 | [5 empty] | 86.17 |  |  | 89.16 |  |  |  | 6.47 |  | 6.09 | [8 empty] | 5.78 |  |  |  |  | 0.84
2021 |  |  |  | 9379.74 |  |  | 8268 |  |  |  | 1157 | [10 empty] | 92.91 |  |  |  | 93.90 | [5 empty] | 92.55 |  |  | 94.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.10 |  |  |  |  | 0.99
2022 |  |  |  | 8805.20 |  |  | 7821 |  |  |  | 1157 | [10 empty] | 88.42 |  |  |  | 89.31 | [5 empty] | 86.88 |  |  | 89.28 |  |  |  | 2.63 |  | 2.41 | [8 empty] | 8.29 |  |  |  |  | 0.88
2023 |  |  |  | 9887.28 |  |  | 8667 |  |  |  | 1157 | [10 empty] | 97.62 |  |  |  | 98.63 | [5 empty] | 97.55 |  |  | 98.94 |  |  |  | 0.86 |  | 0.85 | [8 empty] | 0.52 |  |  |  |  | 1.01
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2018 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 61 | [14 empty] | 142
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 404
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 32 | [14 empty] | 60
E. |  | Testing of plant systems or components | [35 empty] | 59
I. |  | Grid capacity limitation | [51 empty] | 21
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 33
Z. |  | Other | [35 empty] | 27
Subtotal | [22 empty] | 32 |  |  |  | 61 | [10 empty] | 550 |  |  |  | 142 | [11 empty] | 54
Total | [22 empty] | 93 | [14 empty] | 746
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2018 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [19 empty] | 61 | [14 empty] | 126
41. |  |  | Main Generator Systems | [34 empty] | 20
Total | [22 empty] | 61 | [14 empty] | 153
Highlights (2023)
The overall operation of Unit 1 in 2023 is good, with a total of 7 peak shaving operations, 1 unplanned minor repair, and 1 planned minor repair.

## SANMEN-2
2023 Operating Experience
CN-29 | [8 empty] | SANMEN-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SMNPC (SANMEN NUCLEAR POWER CO., LTD.)
Owner | [7 empty] | : | SMNPC (SANMEN NUCLEAR POWER CO., LTD.)
Reactor Supplier | [7 empty] | : | WH/MHI (WESTINGHOUSE ELECTRIC CORPORATION / MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / AP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-12-15
Thermal power | [12 empty] | : |  |  | 3400 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-08-24
Gross electrical power | [12 empty] | : |  |  | 1251 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-11-05
Reference unit power (net) | [12 empty] | : |  |  | 1157 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.407
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.7239 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.8 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 50558 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.38
| Active core height/length [m] | [13 empty] | : |  |  | 4.267 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.77 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 69 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 9240.77 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.71 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.17 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.66 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.21 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.12 %
Load Factor (LF) | [18 empty] | : | 91.17 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.04 %
Operating Factor (OF) | [18 empty] | : | 92.58 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 650 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 860.76 | 777.48 |  |  |  | 860.80 |  | 832.89 | [8 empty] | 860.81 |  |  | 817.65 | [6 empty] | 832.71 |  | 831.85 |  |  |  | 806.78 |  |  | 787.01 |  |  | 741.82 | [9 empty] | 230.21 |  |  | 9240.77
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 99.98 | [8 empty] | 100.00 |  |  | 98.15 | [6 empty] | 96.74 |  | 96.64 |  |  |  | 96.85 |  |  | 91.43 |  |  | 89.05 | [9 empty] | 26.74 |  |  | 91.17
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 99.98 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 92.23 |  |  | 89.05 | [9 empty] | 26.74 |  |  | 92.21
LF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 99.98 | [8 empty] | 100.00 |  |  | 98.15 | [6 empty] | 96.74 |  | 96.64 |  |  |  | 96.85 |  |  | 91.43 |  |  | 89.05 | [9 empty] | 26.74 |  |  | 91.17
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 93.82 |  |  | 89.44 | [9 empty] | 29.03 |  |  | 92.58
FLR [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 7.77 |  |  | 0.00 | [9 empty] | 0.04 |  |  | 0.71
UCL [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 7.77 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 0.66
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.02 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 10.95 | [9 empty] | 73.25 |  |  | 7.12
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.85 | [6 empty] | 3.26 |  | 3.36 |  |  |  | 3.15 |  |  | 0.80 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.04
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 39579.91 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 19.02 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.09 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 18.36 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.22 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 4.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.01 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.13 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 75.55 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 2252.77 |  |  | 2381 |  |  |  | 1157 | [10 empty] | 85.14 |  |  |  | 85.14 | [5 empty] | 85.84 |  |  | 85.18 |  |  |  | 14.85 |  | 14.84 | [8 empty] | 0.02 |  |  |  |  | 0.00
2019 |  |  |  | 905.96 |  |  | 817 |  |  |  | 1157 | [10 empty] | 8.94 |  |  |  | 8.94 | [5 empty] | 8.94 |  |  | 9.33 |  |  |  | 91.02 |  | 90.64 | [8 empty] | 0.42 |  |  |  |  | 0.00
2020 |  |  |  | 8786.18 |  |  | 7871 |  |  |  | 1157 | [10 empty] | 97.25 |  |  |  | 99.99 | [5 empty] | 86.45 |  |  | 89.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 2.74
2021 |  |  |  | 9140.14 |  |  | 8085 |  |  |  | 1157 | [10 empty] | 90.21 |  |  |  | 91.48 | [5 empty] | 90.18 |  |  | 92.29 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.52 |  |  |  |  | 1.27
2022 |  |  |  | 9254.09 |  |  | 8087 |  |  |  | 1157 | [10 empty] | 91.31 |  |  |  | 92.09 | [5 empty] | 91.31 |  |  | 92.32 |  |  |  | 0.00 |  | 1.11 | [8 empty] | 6.80 |  |  |  |  | 0.78
2023 |  |  |  | 9240.77 |  |  | 8110 |  |  |  | 1157 | [10 empty] | 91.17 |  |  |  | 92.21 | [5 empty] | 91.17 |  |  | 92.58 |  |  |  | 0.71 |  | 0.66 | [8 empty] | 7.12 |  |  |  |  | 1.04
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2018 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 46 | [14 empty] | 1588
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 604 | [14 empty] | 359
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 61
E. |  | Testing of plant systems or components | [35 empty] | 37
O. |  | Load dispatching, prioritization | [51 empty] | 177
Z. |  | Other | [39 empty] | 19
Subtotal | [22 empty] | 604 |  |  |  | 46 | [10 empty] | 457 |  |  |  | 1607 | [11 empty] | 177
Total | [22 empty] | 650 | [14 empty] | 2241
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2018 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [19 empty] | 46 | [14 empty] | 1515
41. |  |  | Main Generator Systems | [34 empty] | 18
Total | [22 empty] | 46 | [14 empty] | 1533
Highlights (2023)
1. The overall operation of Unit 2 in 2023 is good, with one unplanned shutdown and minor repair. 2. At 23:45 on December 22, 2023, the outage of Unit 203 of Unit 2 was completed, lasting 25.17 days.

## SHIDAO BAY-1
2023 Operating Experience
CN-44 | [6 empty] | SHIDAO BAY-1 | [26 empty] | CHINA
Status at end of year | [5 empty] | : | Operational
Operator | [5 empty] | : | HSNPC (Huaneng Shandong Shidao Bay Nuclear Power Company, Ltd.)
Owner | [5 empty] | : | CHNG (China Huaneng Group)
Reactor Supplier | [5 empty] | : | TSINGHUA (Tsinghua university)
Turbine Supplier | [5 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [25 empty] | Key Dates
Reactor type and model | [10 empty] | : |  |  | HTGR / HTR-PM | [11 empty] | Construction Date | [15 empty] | : |  |  | 2012-12-09
Thermal power | [10 empty] | : |  |  | 500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2021-12-14
Gross electrical power | [10 empty] | : |  |  | 211 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2023-12-06
Reference unit power (net) | [10 empty] | : |  |  | 150 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [26 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [11 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 750
| Fuel material | [11 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [11 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [11 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.13
| Average fuel enrichment [% of U235] | [11 empty] | : |  |  | 8.5 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [11 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [11 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [11 empty] | : |  |  | 90000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [11 empty] | : |  |  | 3 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 13.24
| Active core height/length [m] | [11 empty] | : |  |  | 11 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 18
| Number of fissile fuel assemblies/bundles | [11 empty] | : |  |  | 420000 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [11 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [11 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [11 empty] | : |  |  | 1 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [11 empty] | : |  |  | Other | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [16 empty] | : | 112.09 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [16 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [16 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [16 empty] | : | 100.44 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [16 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
|  |  | Jan | Oct |  |  |  | Nov |  | Feb | [8 empty] | Mar |  |  | Apr | [6 empty] | May |  | Jun |  |  |  | Jul |  |  | Aug |  |  | Sep | [9 empty] | Dec |  |  | Annual
GW(e)-h | [50 empty] | 112.09 |  |  | 112.09
EAF [%] | [50 empty] | 100.00 |  |  | 100.00
UCF [%] | [50 empty] | 100.00 |  |  | 100.00
LF [%] | [50 empty] | 100.44 |  |  | 100.44
OF [%] | [50 empty] | 100.00 |  |  | 100.00
FLR [%] | [50 empty] | 0.00 |  |  | 0.00
UCL [%] | [50 empty] | 0.00 |  |  | 0.00
PUF [%] | [50 empty] | 0.00 |  |  | 0.00
XUF [%] | [50 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [11 empty] | : |  |  | 112.09 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [11 empty] | : |  |  | 100 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [11 empty] | : |  |  | 100 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0 %
Cumulative Load Factor (LF) | [11 empty] | : |  |  | 100.44 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [11 empty] | : |  |  | 100 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2023 |  | 112.09 |  |  | 744 |  |  |  | 150 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.44 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[21 empty] | 2023 | [14 empty] | 2023 to 2023
Outage Cause | [20 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[21 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
Subtotal
Total | [20 empty] | 0 | [14 empty] | 0
Equipment Related Unplanned Full Outages, Analysis by System
System | [20 empty] | 2023 | [14 empty] | 2023 to 2023
[21 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
Total
Highlights (2023)
During the year, Shidao Bay Nuclear Power Plant Unit 1 maintained power operation, and no manual or automatic emergency shutdown occurred.

## TAISHAN-1
2023 Operating Experience
CN-32 | [8 empty] | TAISHAN-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TNPJVC (Taishan Nuclear Power Joint Venture Company Limited)
Owner | [7 empty] | : | TNPJVC (Taishan Nuclear Power Joint Venture Company Limited)
Reactor Supplier | [7 empty] | : | ORANO (ORANO)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / EPR-1750 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-11-18
Thermal power | [12 empty] | : |  |  | 4590 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-06-29
Gross electrical power | [12 empty] | : |  |  | 1750 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-12-13
Reference unit power (net) | [12 empty] | : |  |  | 1660 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.55
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.98 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 29.88 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 59000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.657 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | NA
| Active core height/length [m] | [13 empty] | : |  |  | 4.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 6
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2068.28 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 15.18 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 15.45 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 84.54 %
Load Factor (LF) | [18 empty] | : | 14.22 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.27 %
Operating Factor (OF) | [18 empty] | : | 17.64 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 7215 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 984.49 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 23.99 | [9 empty] | 1059.80 |  |  | 2068.27
EAF [%] |  |  |  |  | 91.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.01 | [9 empty] | 85.81 |  |  | 15.18
UCF [%] |  |  |  |  | 92.45 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.43 | [9 empty] | 87.16 |  |  | 15.45
LF [%] |  |  |  |  | 79.71 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.01 | [9 empty] | 85.81 |  |  | 14.22
OF [%] |  |  |  |  | 97.72 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 10.28 | [9 empty] | 100.00 |  |  | 17.64
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 0.00
PUF [%] |  |  |  |  | 7.55 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 97.57 | [9 empty] | 12.83 |  |  | 84.54
XUF [%] |  |  |  |  | 1.45 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.43 | [9 empty] | 1.35 |  |  | 0.27
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 37924.66 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.16 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 52.52 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.35 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 53.05 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 45.59 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 48.59 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.53 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 55.55 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 3056.09 |  |  | 3958 |  |  |  | 1660 | [10 empty] | 84.52 |  |  |  | 84.52 | [5 empty] | 83.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.48 |  |  |  |  | 0.00
2019 |  |  |  | 11952.73 |  |  | 7836 |  |  |  | 1660 | [10 empty] | 90.77 |  |  |  | 90.77 | [5 empty] | 82.20 |  |  | 89.45 |  |  |  | 0.73 |  | 2.26 | [8 empty] | 6.97 |  |  |  |  | 0.00
2020 |  |  |  | 9169.83 |  |  | 6377 |  |  |  | 1660 | [10 empty] | 70.53 |  |  |  | 71.56 | [5 empty] | 62.89 |  |  | 72.60 |  |  |  | 0.53 |  | 2.49 | [8 empty] | 25.95 |  |  |  |  | 1.03
2021 |  |  |  | 7616.68 |  |  | 4933 |  |  |  | 1660 | [10 empty] | 55.07 |  |  |  | 55.79 | [5 empty] | 52.38 |  |  | 56.31 |  |  |  | 3.56 |  | 2.06 | [8 empty] | 42.15 |  |  |  |  | 0.72
2022 |  |  |  | 4113.09 |  |  | 3322 |  |  |  | 1660 | [10 empty] | 28.28 |  |  |  | 28.97 | [5 empty] | 28.28 |  |  | 37.92 |  |  |  | 0.23 |  | 0.07 | [8 empty] | 70.96 |  |  |  |  | 0.69
2023 |  |  |  | 2068.28 |  |  | 1545 |  |  |  | 1660 | [10 empty] | 15.18 |  |  |  | 15.45 | [5 empty] | 14.22 |  |  | 17.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 84.54 |  |  |  |  | 0.27
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2018 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 44
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 7215 | [14 empty] | 1797
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 1931
E. |  | Testing of plant systems or components | [35 empty] | 6
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 66
L. |  | Human factor related | [39 empty] | 113
Z. |  | Other | [39 empty] | 37
Subtotal | [22 empty] | 7215 | [14 empty] | 3734 |  |  |  | 194 | [11 empty] | 66
Total | [22 empty] | 7215 | [14 empty] | 3994
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2018 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 14
16. |  |  | Steam generation systems | [34 empty] | 15
31. |  |  | Turbine and auxiliaries | [34 empty] | 15
32. |  |  | Feedwater and Main Steam System | [34 empty] | 56
33. |  |  | Circulating Water System | [34 empty] | 17
34. |  |  | Miscellaneous Systems | [34 empty] | 90
Total | [37 empty] | 208
Highlights (2023)
There wasn't unplanned scram in CN32 in 2023

## TAISHAN-2
2023 Operating Experience
CN-33 | [8 empty] | TAISHAN-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TNPJVC (Taishan Nuclear Power Joint Venture Company Limited)
Owner | [7 empty] | : | TNPJVC (Taishan Nuclear Power Joint Venture Company Limited)
Reactor Supplier | [7 empty] | : | ORANO (ORANO)
Turbine Supplier | [7 empty] | : | ALSTOM (ALSTOM)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / EPR-1750 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-04-15
Thermal power | [12 empty] | : |  |  | 4590 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-06-23
Gross electrical power | [12 empty] | : |  |  | 1750 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2019-09-07
Reference unit power (net) | [12 empty] | : |  |  | 1660 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.55
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.98 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 29.8755 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 59000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.657 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | NA
| Active core height/length [m] | [13 empty] | : |  |  | 4.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 6
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 12884.09 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.17 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.55 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.45 %
Load Factor (LF) | [18 empty] | : | 88.6 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.38 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 952.36 | 1015.85 |  |  |  | 1120.76 |  | 1081.80 | [8 empty] | 1109.29 |  |  | 1060.76 | [6 empty] | 1097.14 |  | 1095.60 |  |  |  | 1055.45 |  |  | 1104.10 |  |  | 1074.14 | [9 empty] | 1116.84 |  |  | 12884.09
EAF [%] |  |  |  |  | 94.67 | 91.07 |  |  |  | 90.75 |  | 90.51 | [8 empty] | 89.82 |  |  | 88.75 | [6 empty] | 88.83 |  | 88.71 |  |  |  | 89.28 |  |  | 89.40 |  |  | 89.87 | [9 empty] | 90.43 |  |  | 90.17
UCF [%] |  |  |  |  | 96.23 | 92.28 |  |  |  | 92.01 |  | 91.81 | [8 empty] | 91.18 |  |  | 90.22 | [6 empty] | 90.27 |  | 90.23 |  |  |  | 90.76 |  |  | 90.79 |  |  | 91.17 | [9 empty] | 91.66 |  |  | 91.55
LF [%] |  |  |  |  | 77.11 | 91.07 |  |  |  | 90.75 |  | 90.51 | [8 empty] | 89.82 |  |  | 88.75 | [6 empty] | 88.83 |  | 88.71 |  |  |  | 88.31 |  |  | 89.40 |  |  | 89.87 | [9 empty] | 90.43 |  |  | 88.60
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 3.77 | 7.72 |  |  |  | 7.99 |  | 8.19 | [8 empty] | 8.82 |  |  | 9.78 | [6 empty] | 9.73 |  | 9.77 |  |  |  | 9.24 |  |  | 9.21 |  |  | 8.83 | [9 empty] | 8.34 |  |  | 8.45
XUF [%] |  |  |  |  | 1.57 | 1.22 |  |  |  | 1.26 |  | 1.30 | [8 empty] | 1.36 |  |  | 1.47 | [6 empty] | 1.44 |  | 1.52 |  |  |  | 1.48 |  |  | 1.39 |  |  | 1.30 | [9 empty] | 1.24 |  |  | 1.38
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 49863.38 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.37 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.94 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.31 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.91 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.78 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.69 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.96 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.12 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2019 |  |  |  | 5356.14 |  |  | 3817 |  |  |  | 1660 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 92.33 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 12454.80 |  |  | 8667 |  |  |  | 1660 | [10 empty] | 96.77 |  |  |  | 97.71 | [5 empty] | 85.42 |  |  | 98.67 |  |  |  | 1.03 |  | 1.02 | [8 empty] | 1.27 |  |  |  |  | 0.95
2021 |  |  |  | 10870.50 |  |  | 7089 |  |  |  | 1660 | [10 empty] | 77.70 |  |  |  | 78.97 | [5 empty] | 74.75 |  |  | 80.92 |  |  |  | 0.40 |  | 0.32 | [8 empty] | 20.72 |  |  |  |  | 1.27
2022 |  |  |  | 8297.85 |  |  | 5654 |  |  |  | 1660 | [10 empty] | 57.06 |  |  |  | 57.65 | [5 empty] | 57.06 |  |  | 64.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 42.35 |  |  |  |  | 0.58
2023 |  |  |  | 12884.09 |  |  | 8760 |  |  |  | 1660 | [10 empty] | 90.17 |  |  |  | 91.55 | [5 empty] | 88.60 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.45 |  |  |  |  | 1.38
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2019 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 20
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1098
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 15
E. |  | Testing of plant systems or components | [35 empty] | 163
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 12
Subtotal | [37 empty] | 1276 |  |  |  | 20 | [11 empty] | 12
Total | [22 empty] | 0 | [14 empty] | 1308
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2019 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [34 empty] | 27
41. |  |  | Main Generator Systems | [34 empty] | 4
Total | [37 empty] | 31
Highlights (2023)
There wasn't unplanned scram in CN33 in 2023.

## TIANWAN-1
2023 Operating Experience
CN-10 | [8 empty] | TIANWAN-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | IZ (Izhorskiye Zavody)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-428 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1999-10-20
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2006-05-12
Gross electrical power | [12 empty] | : |  |  | 1060 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2007-05-17
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 17 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 4
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.78
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 103 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7875.04 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.5 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.97 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.47 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.15 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.38 %
Load Factor (LF) | [18 empty] | : | 89.9 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.18 %
Operating Factor (OF) | [18 empty] | : | 93.44 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 575 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 667.74 | 665.01 |  |  |  | 742.50 |  | 701.06 | [8 empty] | 192.71 |  |  | 708.38 | [6 empty] | 731.43 |  | 726.95 |  |  |  | 706.77 |  |  | 695.91 |  |  | 675.86 | [9 empty] | 660.71 |  |  | 7875.04
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 98.93 | [8 empty] | 25.91 |  |  | 98.73 | [6 empty] | 98.66 |  | 99.77 |  |  |  | 100.00 |  |  | 95.11 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.97
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 98.93 | [8 empty] | 25.91 |  |  | 99.33 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 95.11 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.15
LF [%] |  |  |  |  | 89.75 | 98.96 |  |  |  | 99.80 |  | 97.37 | [8 empty] | 25.90 |  |  | 98.39 | [6 empty] | 98.31 |  | 97.71 |  |  |  | 98.16 |  |  | 93.54 |  |  | 93.87 | [9 empty] | 88.81 |  |  | 89.90
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.72 | [8 empty] | 27.82 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 95.16 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.44
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.67 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 4.89 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.50
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.67 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 4.89 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.47
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 1.07 | [8 empty] | 74.09 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.38
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.60 | [6 empty] | 1.34 |  | 0.23 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.18
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 126335.84 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.68 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.02 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.62 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.17 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.21 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.95 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.15 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.68 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2007 |  |  |  | 5311.00 |  |  | 5688 |  |  |  | 933 | [10 empty] | 82.44 |  |  |  | 82.44 | [5 empty] | 84.77 |  |  | 82.71 |  |  |  | 0.44 |  | 0.36 | [8 empty] | 17.20 |  |  |  |  | 0.00
2008 |  |  |  | 6116.16 |  |  | 6270 |  |  |  | 933 | [10 empty] | 70.97 |  |  |  | 70.97 | [5 empty] | 74.63 |  |  | 71.38 |  |  |  | 3.60 |  | 2.65 | [8 empty] | 26.38 |  |  |  |  | 0.00
2009 |  |  |  | 6337.71 |  |  | 6553 |  |  |  | 933 | [10 empty] | 74.12 |  |  |  | 74.12 | [5 empty] | 77.54 |  |  | 74.81 |  |  |  | 0.97 |  | 0.73 | [8 empty] | 25.16 |  |  |  |  | 0.00
2010 |  |  |  | 7539.59 |  |  | 7643 |  |  |  | 933 | [10 empty] | 87.02 |  |  |  | 87.02 | [5 empty] | 92.25 |  |  | 87.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.98 |  |  |  |  | 0.00
2011 |  |  |  | 7470.08 |  |  | 7606 |  |  |  | 990 | [10 empty] | 86.55 |  |  |  | 86.55 | [5 empty] | 86.14 |  |  | 86.83 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 13.39 |  |  |  |  | 0.00
2012 |  |  |  | 7550.16 |  |  | 7635 |  |  |  | 990 | [10 empty] | 86.78 |  |  |  | 86.78 | [5 empty] | 86.82 |  |  | 86.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.22 |  |  |  |  | 0.00
2013 |  |  |  | 7869.05 |  |  | 7959 |  |  |  | 990 | [10 empty] | 90.71 |  |  |  | 90.71 | [5 empty] | 90.74 |  |  | 90.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.29 |  |  |  |  | 0.00
2014 |  |  |  | 7766.80 |  |  | 7888 |  |  |  | 990 | [10 empty] | 89.83 |  |  |  | 89.83 | [5 empty] | 89.56 |  |  | 90.05 |  |  |  | 0.09 |  | 0.44 | [8 empty] | 9.73 |  |  |  |  | 0.00
2015 |  |  |  | 7894.21 |  |  | 7996 |  |  |  | 990 | [10 empty] | 91.07 |  |  |  | 91.07 | [5 empty] | 91.03 |  |  | 91.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.92 |  |  |  |  | 0.00
2016 |  |  |  | 7027.54 |  |  | 7295 |  |  |  | 990 | [10 empty] | 81.71 |  |  |  | 81.71 | [5 empty] | 80.81 |  |  | 83.05 |  |  |  | 0.90 |  | 0.74 | [8 empty] | 17.54 |  |  |  |  | 0.00
2017 |  |  |  | 7869.01 |  |  | 8081 |  |  |  | 990 | [10 empty] | 91.25 |  |  |  | 92.05 | [5 empty] | 90.74 |  |  | 92.25 |  |  |  | 0.40 |  | 0.37 | [8 empty] | 7.58 |  |  |  |  | 0.80
2018 |  |  |  | 7074.55 |  |  | 7450 |  |  |  | 990 | [10 empty] | 89.28 |  |  |  | 89.91 | [5 empty] | 81.58 |  |  | 85.05 |  |  |  | 3.66 |  | 3.42 | [8 empty] | 6.67 |  |  |  |  | 0.64
2019 |  |  |  | 8254.54 |  |  | 8501 |  |  |  | 990 | [10 empty] | 98.43 |  |  |  | 98.68 | [5 empty] | 95.18 |  |  | 97.04 |  |  |  | 0.52 |  | 0.52 | [8 empty] | 0.80 |  |  |  |  | 0.25
2020 |  |  |  | 7424.97 |  |  | 7854 |  |  |  | 990 | [10 empty] | 89.31 |  |  |  | 89.31 | [5 empty] | 85.38 |  |  | 89.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.69 |  |  |  |  | 0.00
2021 |  |  |  | 7528.83 |  |  | 7686 |  |  |  | 1000 | [10 empty] | 89.35 |  |  |  | 89.96 | [5 empty] | 85.95 |  |  | 87.74 |  |  |  | 0.87 |  | 0.78 | [8 empty] | 9.26 |  |  |  |  | 0.61
2022 |  |  |  | 8167.00 |  |  | 8630 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 93.23 |  |  | 98.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2023 |  |  |  | 7875.04 |  |  | 8185 |  |  |  | 1000 | [10 empty] | 92.97 |  |  |  | 93.15 | [5 empty] | 89.90 |  |  | 93.44 |  |  |  | 0.50 |  | 0.47 | [8 empty] | 6.38 |  |  |  |  | 0.18
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2007 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 36 | [14 empty] | 44
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 540 | [14 empty] | 892
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 84
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 59
L. |  | Human factor related | [39 empty] | 2
Subtotal | [22 empty] | 540 |  |  |  | 36 | [10 empty] | 976 |  |  |  | 46 | [11 empty] | 59
Total | [22 empty] | 576 | [14 empty] | 1081
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2007 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 6
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [19 empty] | 36 | [14 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 22
41. |  |  | Main Generator Systems | [34 empty] | 17
42. |  |  | Electrical Power Supply Systems | [34 empty] | 15
Total | [22 empty] | 36 | [14 empty] | 66
Highlights (2023)
This year, Unit 1 underwent a unit outage and one minor power reduction repair, and cooperated with the power grid to reduce power multiple times. At other times, it maintained power operation and experienced an automatic emergency shutdown event. On April 30th at 21:50, the steam turbine generator of Unit 1 was disconnected and the OT114 refueling outage began. On May 23rd at 09:35, Unit 1 was reconnected to the grid for operation after completing major repairs. On May 25th at 20:30, the unit rose to full power operation. On June 20th at 08:30, due to the shutdown and maintenance of 1PAC21AP001, Unit 1 reduced its power to 900MW for operation. On June 21st at 09:30, the maintenance of the circulating cooling water pump 1PAC21AP001 was completed, and the unit was put into full power operation. On October 29th at 23:29, the condensate control valve in the second circuit of Unit 1 malfunctioned and closed, causing fluctuations in feedwater flow and resulting in low steam generator liquid level. This triggered a shutdown protection action and caused the unit to shut down. The unit was reconnected to the grid after completing defect elimination at 05:40 on October 31st.

## TIANWAN-2
2023 Operating Experience
CN-11 | [8 empty] | TIANWAN-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | IZ (Izhorskiye Zavody)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-428 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2000-09-20
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2007-05-14
Gross electrical power | [12 empty] | : |  |  | 1060 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2007-08-16
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 16 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 40.49 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 4
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.78
| Active core height/length [m] | [13 empty] | : |  |  | 3.68 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 103 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8015.09 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.7 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 91.5 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.3 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 499.73 | 649.70 |  |  |  | 685.30 |  | 557.97 | [8 empty] | 696.34 |  |  | 705.20 | [6 empty] | 729.00 |  | 726.21 |  |  |  | 704.26 |  |  | 727.97 |  |  | 674.13 | [9 empty] | 659.29 |  |  | 8015.09
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.26 | [6 empty] | 99.08 |  | 98.10 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.70
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 67.17 | 96.68 |  |  |  | 92.11 |  | 77.50 | [8 empty] | 93.59 |  |  | 97.94 | [6 empty] | 97.98 |  | 97.61 |  |  |  | 97.81 |  |  | 97.84 |  |  | 93.63 | [9 empty] | 88.61 |  |  | 91.50
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.74 | [6 empty] | 0.92 |  | 1.90 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.30
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 125778.72 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.17 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.13 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.15 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.36 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.48 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.83 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.23 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.04 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2007 |  |  |  | 3974.00 |  |  | 4471 |  |  |  | 958 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.13 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 7003.03 |  |  | 7193 |  |  |  | 933 | [10 empty] | 81.20 |  |  |  | 81.20 | [5 empty] | 85.45 |  |  | 81.89 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 18.77 |  |  |  |  | 0.00
2009 |  |  |  | 6943.40 |  |  | 7054 |  |  |  | 933 | [10 empty] | 80.69 |  |  |  | 80.69 | [5 empty] | 84.95 |  |  | 80.53 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 19.29 |  |  |  |  | 0.00
2010 |  |  |  | 7131.13 |  |  | 7260 |  |  |  | 933 | [10 empty] | 82.28 |  |  |  | 82.28 | [5 empty] | 87.25 |  |  | 82.88 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 17.65 |  |  |  |  | 0.00
2011 |  |  |  | 7546.20 |  |  | 7658 |  |  |  | 990 | [10 empty] | 87.05 |  |  |  | 87.05 | [5 empty] | 87.01 |  |  | 87.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.95 |  |  |  |  | 0.00
2012 |  |  |  | 7640.12 |  |  | 7722 |  |  |  | 990 | [10 empty] | 87.77 |  |  |  | 87.77 | [5 empty] | 87.86 |  |  | 87.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.23 |  |  |  |  | 0.00
2013 |  |  |  | 7741.45 |  |  | 7837 |  |  |  | 990 | [10 empty] | 89.14 |  |  |  | 89.14 | [5 empty] | 89.27 |  |  | 89.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.86 |  |  |  |  | 0.00
2014 |  |  |  | 7901.45 |  |  | 7950 |  |  |  | 990 | [10 empty] | 91.10 |  |  |  | 91.10 | [5 empty] | 91.11 |  |  | 90.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.90 |  |  |  |  | 0.00
2015 |  |  |  | 7666.57 |  |  | 7790 |  |  |  | 990 | [10 empty] | 88.22 |  |  |  | 88.22 | [5 empty] | 88.40 |  |  | 88.93 |  |  |  | 0.87 |  | 0.77 | [8 empty] | 11.01 |  |  |  |  | 0.00
2016 |  |  |  | 7326.45 |  |  | 7705 |  |  |  | 990 | [10 empty] | 87.36 |  |  |  | 87.36 | [5 empty] | 84.25 |  |  | 87.72 |  |  |  | 0.50 |  | 0.44 | [8 empty] | 12.20 |  |  |  |  | 0.00
2017 |  |  |  | 8201.96 |  |  | 8430 |  |  |  | 990 | [10 empty] | 98.97 |  |  |  | 99.90 | [5 empty] | 94.58 |  |  | 96.23 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.07 |  |  |  |  | 0.93
2018 |  |  |  | 7661.18 |  |  | 8007 |  |  |  | 990 | [10 empty] | 91.64 |  |  |  | 92.22 | [5 empty] | 88.34 |  |  | 91.40 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 7.72 |  |  |  |  | 0.58
2019 |  |  |  | 7644.10 |  |  | 7833 |  |  |  | 990 | [10 empty] | 91.13 |  |  |  | 91.30 | [5 empty] | 88.14 |  |  | 89.42 |  |  |  | 0.09 |  | 0.09 | [8 empty] | 8.62 |  |  |  |  | 0.17
2020 |  |  |  | 7991.08 |  |  | 8683 |  |  |  | 990 | [10 empty] | 98.32 |  |  |  | 98.32 | [5 empty] | 91.89 |  |  | 98.85 |  |  |  | 0.25 |  | 0.25 | [8 empty] | 1.43 |  |  |  |  | 0.00
2021 |  |  |  | 7972.07 |  |  | 8253 |  |  |  | 1000 | [10 empty] | 92.34 |  |  |  | 93.24 | [5 empty] | 91.01 |  |  | 94.21 |  |  |  | 0.77 |  | 0.72 | [8 empty] | 6.03 |  |  |  |  | 0.90
2022 |  |  |  | 7420.49 |  |  | 7861 |  |  |  | 1000 | [10 empty] | 90.46 |  |  |  | 91.32 | [5 empty] | 84.71 |  |  | 89.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.68 |  |  |  |  | 0.86
2023 |  |  |  | 8015.09 |  |  | 8760 |  |  |  | 1000 | [10 empty] | 99.70 |  |  |  | 100.00 | [5 empty] | 91.50 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.30
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2007 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 3
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 730
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 105
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 50
L. |  | Human factor related | [39 empty] | 3
Subtotal | [37 empty] | 835 |  |  |  | 6 | [11 empty] | 50
Total | [22 empty] | 0 | [14 empty] | 891
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2007 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 2
Total | [37 empty] | 16
Highlights (2023)
This year, Unit 2 has cooperated with the power grid multiple times to reduce power, while maintaining power operation at other times without any emergency shutdown incidents.

## TIANWAN-3
2023 Operating Experience
CN-45 | [8 empty] | TIANWAN-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | IZ (Izhorskiye Zavody)
Turbine Supplier | [7 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-428M | [11 empty] | Construction Date | [15 empty] | : |  |  | 2012-12-27
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2017-12-30
Gross electrical power | [12 empty] | : |  |  | 1126 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-02-14
Reference unit power (net) | [12 empty] | : |  |  | 1060 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 6 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.49
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | NA | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.88
| Active core height/length [m] | [13 empty] | : |  |  | NA | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | NA | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 103 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7013.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.06 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 78.7 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.3 %
Load Factor (LF) | [18 empty] | : | 75.53 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.64 %
Operating Factor (OF) | [18 empty] | : | 79.02 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1838 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 788.27 | 712.32 |  |  |  | 413.46 |  | 0.38 | [8 empty] | 0.00 |  |  | 687.98 | [6 empty] | 754.36 |  | 752.68 |  |  |  | 736.88 |  |  | 763.70 |  |  | 708.31 | [9 empty] | 694.93 |  |  | 7013.26
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 52.74 |  | 0.05 | [8 empty] | 0.00 |  |  | 91.90 | [6 empty] | 98.02 |  | 95.45 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.06
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 52.75 |  | 0.05 | [8 empty] | 0.00 |  |  | 92.96 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.70
LF [%] |  |  |  |  | 99.95 | 100.00 |  |  |  | 52.43 |  | 0.05 | [8 empty] | 0.00 |  |  | 90.14 | [6 empty] | 95.65 |  | 95.44 |  |  |  | 96.55 |  |  | 96.84 |  |  | 92.81 | [9 empty] | 88.12 |  |  | 75.53
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 53.23 |  | 1.39 | [8 empty] | 0.00 |  |  | 95.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 79.02
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 47.25 |  | 99.95 | [8 empty] | 100.00 |  |  | 7.04 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 21.30
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.06 | [6 empty] | 1.98 |  | 4.55 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.64
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 44660.01 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.22 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.65 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.1 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.34 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.56 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.26 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.69 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.9 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 6922.47 |  |  | 7704 |  |  |  | 1045 | [10 empty] | 90.85 |  |  |  | 91.48 | [5 empty] | 78.83 |  |  | 86.83 |  |  |  | 7.27 |  | 7.18 | [8 empty] | 1.34 |  |  |  |  | 0.63
2019 |  |  |  | 7149.36 |  |  | 7055 |  |  |  | 1045 | [10 empty] | 81.24 |  |  |  | 81.29 | [5 empty] | 78.10 |  |  | 80.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.71 |  |  |  |  | 0.05
2020 |  |  |  | 6896.21 |  |  | 7611 |  |  |  | 1045 | [10 empty] | 90.70 |  |  |  | 91.29 | [5 empty] | 75.13 |  |  | 86.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.71 |  |  |  |  | 0.58
2021 |  |  |  | 7919.12 |  |  | 7790 |  |  |  | 1060 | [10 empty] | 92.29 |  |  |  | 93.41 | [5 empty] | 85.28 |  |  | 88.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.59 |  |  |  |  | 1.11
2022 |  |  |  | 8757.42 |  |  | 8709 |  |  |  | 1060 | [10 empty] | 98.89 |  |  |  | 100.00 | [5 empty] | 94.31 |  |  | 99.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 1.11
2023 |  |  |  | 7013.26 |  |  | 6922 |  |  |  | 1060 | [10 empty] | 78.06 |  |  |  | 78.70 | [5 empty] | 75.53 |  |  | 79.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.30 |  |  |  |  | 0.64
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2018 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 84
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 581 | [14 empty] | 588
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 1258 | [14 empty] | 213
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 265
Subtotal | [22 empty] | 1839 | [14 empty] | 801 |  |  |  | 84 | [11 empty] | 265
Total | [22 empty] | 1839 | [14 empty] | 1150
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2018 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 61
16. |  |  | Steam generation systems | [34 empty] | 22
34. |  |  | Miscellaneous Systems | [34 empty] | 158
Total | [37 empty] | 241
Highlights (2023)
This year, Unit 3 has cooperated with the power grid multiple times to reduce power, while maintaining power operation at other times; This year, Unit 3 underwent a outage, one minor maintenance shutdown, and multiple power reductions in coordination with the power grid, while maintaining power operation at other times. On March 17th at 12:05, the steam turbine generator of Unit 3 was disconnected and the OT304 material replacement overhaul began. At 16:10 on April 10th, Unit 1 was reconnected to the grid for operation after completing major repairs. At 17:55 on April 21st, Unit 3 underwent maintenance and defect elimination of the primary low-pressure safety injection system containment isolation valve, as well as reactor disassembly inspection. It began to shut down for minor repairs and was reconnected to the grid at 12:20 on June 2nd.

## TIANWAN-4
2023 Operating Experience
CN-46 | [8 empty] | TIANWAN-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | IZ (Izhorskiye Zavody)
Turbine Supplier | [7 empty] | : | HTC (HARBIN TURBINE COMPANY LIMITED)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-428M | [11 empty] | Construction Date | [15 empty] | : |  |  | 2013-09-27
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-10-27
Gross electrical power | [12 empty] | : |  |  | 1126 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-12-22
Reference unit power (net) | [12 empty] | : |  |  | 1060 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.49
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | NA | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | NA | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | NA | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.88
| Active core height/length [m] | [13 empty] | : |  |  | NA | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | NA | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 103 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | NA
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7630.39 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.04 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.35 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.04 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.35 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.61 %
Load Factor (LF) | [18 empty] | : | 82.17 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.55 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 828 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 533.61 | 668.99 |  |  |  | 729.06 |  | 524.65 | [8 empty] | 725.94 |  |  | 703.35 | [6 empty] | 741.38 |  | 745.83 |  |  |  | 681.08 |  |  | 744.40 |  |  | 645.84 | [9 empty] | 186.26 |  |  | 7630.39
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 85.64 | [9 empty] | 23.80 |  |  | 92.35
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 85.64 | [9 empty] | 23.80 |  |  | 92.35
LF [%] |  |  |  |  | 67.66 | 93.92 |  |  |  | 92.45 |  | 68.74 | [8 empty] | 92.05 |  |  | 92.16 | [6 empty] | 94.01 |  | 94.57 |  |  |  | 89.24 |  |  | 94.39 |  |  | 84.62 | [9 empty] | 23.62 |  |  | 82.17
OF [%] |  |  |  |  | 75.40 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 86.67 | [9 empty] | 26.21 |  |  | 90.55
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.55 | [9 empty] | 0.00 |  |  | 0.04
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.47 | [9 empty] | 0.00 |  |  | 0.04
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 13.89 | [9 empty] | 76.20 |  |  | 7.61
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 39799.82 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.05 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.25 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.31 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.65 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.58 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.05 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.14 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 732.62 |  |  | 1035 |  |  |  | 1045 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7519.47 |  |  | 7462 |  |  |  | 1045 | [10 empty] | 84.63 |  |  |  | 84.71 | [5 empty] | 82.14 |  |  | 85.18 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 15.13 |  |  |  |  | 0.09
2020 |  |  |  | 7033.68 |  |  | 7003 |  |  |  | 1045 | [10 empty] | 95.17 |  |  |  | 95.17 | [5 empty] | 76.63 |  |  | 79.72 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 4.80 |  |  |  |  | 0.00
2021 |  |  |  | 8610.04 |  |  | 8422 |  |  |  | 1060 | [10 empty] | 95.87 |  |  |  | 95.87 | [5 empty] | 92.72 |  |  | 96.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.13 |  |  |  |  | 0.00
2022 |  |  |  | 8273.71 |  |  | 8244 |  |  |  | 1060 | [10 empty] | 93.18 |  |  |  | 93.35 | [5 empty] | 89.10 |  |  | 94.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.65 |  |  |  |  | 0.17
2023 |  |  |  | 7630.39 |  |  | 7932 |  |  |  | 1060 | [10 empty] | 92.35 |  |  |  | 92.35 | [5 empty] | 82.17 |  |  | 90.55 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 7.61 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2018 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 1
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 645 | [14 empty] | 637
E. |  | Testing of plant systems or components | [35 empty] | 106
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 183 | [19 empty] | 316
Subtotal | [22 empty] | 645 | [10 empty] | 183 |  |  |  | 743 |  |  |  | 1 | [11 empty] | 316
Total | [22 empty] | 828 | [14 empty] | 1060
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2018 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [19 empty] | 183 | [14 empty] | 301
Total | [22 empty] | 183 | [14 empty] | 302
Highlights (2023)
This year, Unit 4 underwent a major overhaul and experienced an unplanned power reduction event (on November 22, during the maintenance process of Unit 4's start-up transformer, backup was used) During the power switch transmission test, triggering the logic resulted in a decrease in reactor power. In addition, we have cooperated with the power grid multiple times this year to reduce power, while maintaining power operation for others The detailed information is as follows: On November 26th at 3:00 PM, Unit 4 began to reduce power, and on the 27th at 00:00 PM, it disconnected from the power grid and began the OT404 refueling overhaul. At 21:28 on December 23rd, the major overhaul was completed and the unit was connected to the grid.

## TIANWAN-5
2023 Operating Experience
CN-53 | [8 empty] | TIANWAN-5 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | SHE (Shanghai Electric)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2015-12-27
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-08-08
Gross electrical power | [12 empty] | : |  |  | 1118 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2020-09-08
Reference unit power (net) | [12 empty] | : |  |  | 1060 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.8
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 3.2 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8038.07 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.46 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.34 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.66 %
Load Factor (LF) | [18 empty] | : | 86.56 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.88 %
Operating Factor (OF) | [18 empty] | : | 89.77 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 896 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 77.03 | 699.90 |  |  |  | 786.32 |  | 714.46 | [8 empty] | 460.93 |  |  | 745.34 | [6 empty] | 757.73 |  | 752.92 |  |  |  | 735.51 |  |  | 762.05 |  |  | 756.81 | [9 empty] | 789.07 |  |  | 8038.07
EAF [%] |  |  |  |  | 9.77 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 97.66 | [6 empty] | 100.00 |  | 95.47 |  |  |  | 96.37 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.46
UCF [%] |  |  |  |  | 9.77 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.34
LF [%] |  |  |  |  | 9.77 | 98.26 |  |  |  | 99.71 |  | 93.61 | [8 empty] | 58.45 |  |  | 97.66 | [6 empty] | 96.08 |  | 95.47 |  |  |  | 96.37 |  |  | 96.63 |  |  | 99.16 | [9 empty] | 100.05 |  |  | 86.56
OF [%] |  |  |  |  | 21.77 | 100.00 |  |  |  | 100.00 |  | 94.58 | [8 empty] | 63.04 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.77
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 90.23 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.66
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.34 | [6 empty] | 0.00 |  | 4.53 |  |  |  | 3.63 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.88
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 27411.54 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.59 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.66 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.34 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.3 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.07 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2020 |  |  |  | 2901.91 |  |  | 3383 |  |  |  | 1000 | [10 empty] | 93.34 |  |  |  | 93.34 | [5 empty] | 91.31 |  |  | 95.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.66 |  |  |  |  | 0.00
2021 |  |  |  | 7538.34 |  |  | 7400 |  |  |  | 1060 | [10 empty] | 84.35 |  |  |  | 85.46 | [5 empty] | 81.18 |  |  | 84.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.54 |  |  |  |  | 1.11
2022 |  |  |  | 8933.22 |  |  | 8760 |  |  |  | 1060 | [10 empty] | 98.41 |  |  |  | 99.97 | [5 empty] | 96.21 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 1.56
2023 |  |  |  | 8038.07 |  |  | 7864 |  |  |  | 1060 | [10 empty] | 91.46 |  |  |  | 92.34 | [5 empty] | 86.56 |  |  | 89.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.66 |  |  |  |  | 0.88
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2020 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 582 | [14 empty] | 532
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 314 | [19 empty] | 187
Subtotal | [22 empty] | 582 | [10 empty] | 314 |  |  |  | 532 | [15 empty] | 187
Total | [22 empty] | 896 | [14 empty] | 719
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2020 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [19 empty] | 314 | [14 empty] | 183
Total | [22 empty] | 314 | [14 empty] | 183
Highlights (2023)
This year, Unit 5 has cooperated with the power grid multiple times to reduce power, while others have maintained power operation. No manual emergency shutdown events have occurred, and the detailed situation is as follows: On January 1, 2023 at 00:09, Unit 5 tripped and shut down, starting the OT502 overhaul. On January 25 at 06:36, the unit was connected to the grid, and the OT502 overhaul was completed.

## TIANWAN-6
2023 Operating Experience
CN-54 | [8 empty] | TIANWAN-6 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Owner | [7 empty] | : | JNPC (Jiangsu Nuclear Power Corporation)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | DEC (Dongfang Electric Corporation )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2016-09-07
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2021-05-11
Gross electrical power | [12 empty] | : |  |  | 1118 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-06-02
Reference unit power (net) | [12 empty] | : |  |  | 1060 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 329.8
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.2 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 3.2 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 33000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8344 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.6 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.49 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.51 %
Load Factor (LF) | [18 empty] | : | 89.86 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.89 %
Operating Factor (OF) | [18 empty] | : | 94.22 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 506 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 713.85 | 687.50 |  |  |  | 741.76 |  | 727.96 | [8 empty] | 763.52 |  |  | 737.82 | [6 empty] | 758.28 |  | 753.72 |  |  |  | 691.32 |  |  | 247.00 |  |  | 731.97 | [9 empty] | 789.31 |  |  | 8344.00
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 97.70 | [6 empty] | 96.15 |  | 95.57 |  |  |  | 90.58 |  |  | 32.52 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.60
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 90.58 |  |  | 32.52 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.49
LF [%] |  |  |  |  | 90.52 | 96.52 |  |  |  | 94.06 |  | 95.38 | [8 empty] | 96.81 |  |  | 96.67 | [6 empty] | 96.15 |  | 95.57 |  |  |  | 90.58 |  |  | 31.32 |  |  | 95.91 | [9 empty] | 100.08 |  |  | 89.86
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 94.86 |  |  | 36.96 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 94.22
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 9.42 |  |  | 67.48 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.51
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.30 | [6 empty] | 3.85 |  | 4.43 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.89
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 21668.64 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.03 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.79 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.03 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.38 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.59 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.59 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 92.84 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2021 |  |  |  | 5786.59 |  |  | 5636 |  |  |  | 1060 | [10 empty] | 98.89 |  |  |  | 99.98 | [5 empty] | 96.48 |  |  | 100.00 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 0.00 |  |  |  |  | 1.09
2022 |  |  |  | 7538.05 |  |  | 7643 |  |  |  | 1060 | [10 empty] | 86.81 |  |  |  | 86.81 | [5 empty] | 81.18 |  |  | 87.25 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 13.12 |  |  |  |  | 0.00
2023 |  |  |  | 8344.00 |  |  | 8254 |  |  |  | 1060 | [10 empty] | 92.60 |  |  |  | 93.49 | [5 empty] | 89.86 |  |  | 94.22 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.51 |  |  |  |  | 0.89
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2021 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 498 | [14 empty] | 617
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 9 | [19 empty] | 3
Subtotal | [22 empty] | 498 | [10 empty] | 9 |  |  |  | 617 | [15 empty] | 3
Total | [22 empty] | 507 | [14 empty] | 620
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2021 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
34. |  |  | Miscellaneous Systems | [19 empty] | 9 | [14 empty] | 3
Total | [22 empty] | 9 | [14 empty] | 3
Highlights (2023)
This year, Unit 6 has cooperated with the power grid multiple times to reduce power, while others have maintained power operation. No manual emergency shutdown events have occurred, and the detailed situation is as follows: Unit 6 began power reduction at 00:00 on September 29th, disconnected from the power grid at 11:02 on September 29th, and began material replacement and overhaul On September 29, 2023 at 11:02, Unit 6 tripped and shut down, starting the OT602 overhaul; At 04:52 on October 20th, the grid connection conditions were met, and the OT602 material replacement overhaul was completed. The actual construction period was 20.74 days. Due to the large amount of new energy generation and difficulties in balancing the power grid, the unit was actually reconnected to the grid for operation at 13:48 on October 20th, and rose to full power operation at 05:40 on October 23rd

## YANGJIANG-1
2023 Operating Experience
CN-22 | [8 empty] | YANGJIANG-1 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-12-16
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2013-12-31
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2014-03-25
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 10 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8868.11 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.38 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.61 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.38 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.61 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 101.23 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.67 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 29 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 718.56 | 700.84 |  |  |  | 774.36 |  | 661.61 | [8 empty] | 766.40 |  |  | 732.77 | [6 empty] | 761.06 |  | 757.49 |  |  |  | 718.33 |  |  | 763.09 |  |  | 743.90 | [9 empty] | 769.70 |  |  | 8868.11
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 95.36 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.95 | [9 empty] | 100.00 |  |  | 99.61
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 95.36 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.95 | [9 empty] | 100.00 |  |  | 99.61
LF [%] |  |  |  |  | 96.58 | 104.29 |  |  |  | 104.08 |  | 91.89 | [8 empty] | 103.01 |  |  | 101.77 | [6 empty] | 102.29 |  | 101.81 |  |  |  | 99.77 |  |  | 102.57 |  |  | 103.32 | [9 empty] | 103.45 |  |  | 101.23
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 95.97 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.67
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 4.64 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.38
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 4.64 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.38
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.05 | [9 empty] | 0.00 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 79218.18 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.28 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.71 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.26 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.78 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.97 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.75 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.07 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.8 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2014 |  |  |  | 6793.37 |  |  | 6753 |  |  |  | 1000 | [10 empty] | 99.93 |  |  |  | 99.93 | [5 empty] | 100.54 |  |  | 100.00 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 0.02 |  |  |  |  | 0.00
2015 |  |  |  | 7025.37 |  |  | 7021 |  |  |  | 1000 | [10 empty] | 79.73 |  |  |  | 79.73 | [5 empty] | 80.20 |  |  | 80.15 |  |  |  | 0.74 |  | 0.59 | [8 empty] | 19.68 |  |  |  |  | 0.00
2016 |  |  |  | 7077.81 |  |  | 6989 |  |  |  | 1000 | [10 empty] | 81.52 |  |  |  | 81.56 | [5 empty] | 80.58 |  |  | 79.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.44 |  |  |  |  | 0.04
2017 |  |  |  | 8699.83 |  |  | 8677 |  |  |  | 1000 | [10 empty] | 99.75 |  |  |  | 99.99 | [5 empty] | 99.31 |  |  | 99.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.24
2018 |  |  |  | 7715.76 |  |  | 7789 |  |  |  | 1000 | [10 empty] | 88.20 |  |  |  | 88.24 | [5 empty] | 88.08 |  |  | 88.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.76 |  |  |  |  | 0.03
2019 |  |  |  | 7988.46 |  |  | 7861 |  |  |  | 1000 | [10 empty] | 89.09 |  |  |  | 89.09 | [5 empty] | 91.19 |  |  | 89.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.91 |  |  |  |  | 0.00
2020 |  |  |  | 8122.92 |  |  | 8665 |  |  |  | 1000 | [10 empty] | 98.42 |  |  |  | 98.51 | [5 empty] | 92.47 |  |  | 98.65 |  |  |  | 1.49 |  | 1.49 | [8 empty] | 0.00 |  |  |  |  | 0.09
2021 |  |  |  | 7930.66 |  |  | 7834 |  |  |  | 1000 | [10 empty] | 88.69 |  |  |  | 88.72 | [5 empty] | 90.53 |  |  | 89.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.28 |  |  |  |  | 0.03
2022 |  |  |  | 8373.86 |  |  | 8312 |  |  |  | 1000 | [10 empty] | 94.17 |  |  |  | 94.41 | [5 empty] | 95.59 |  |  | 94.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.58 |  |  |  |  | 0.25
2023 |  |  |  | 8868.11 |  |  | 8731 |  |  |  | 1000 | [10 empty] | 99.61 |  |  |  | 99.61 | [5 empty] | 101.23 |  |  | 99.67 |  |  |  | 0.38 |  | 0.38 | [8 empty] | 0.01 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2014 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 29 | [14 empty] | 22
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 723
E. |  | Testing of plant systems or components | [35 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 34
Subtotal | [26 empty] | 29 | [10 empty] | 723 |  |  |  | 22 | [11 empty] | 34
Total | [22 empty] | 29 | [14 empty] | 779
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2014 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [19 empty] | 29 | [14 empty] | 9
33. |  |  | Circulating Water System | [34 empty] | 13
Total | [22 empty] | 29 | [14 empty] | 22
Highlights (2023)
Unit 1 of Yangjiang Nuclear Power Plant had a turbine trip on April 12,2023, and re-connected to the grid on April 13. The unit operated at full power at all times except during holidays and grid line maintenance in which it operated at reduced power in order to cooperate with peak shaving of the grid. No scrams has occurred throughout the year.

## YANGJIANG-2
2023 Operating Experience
CN-23 | [8 empty] | YANGJIANG-2 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-06-04
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-03-10
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-06-05
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8111.96 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.94 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 94.04 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.95 %
Load Factor (LF) | [18 empty] | : | 92.6 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.11 %
Operating Factor (OF) | [18 empty] | : | 93.89 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 535 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 697.47 | 676.90 |  |  |  | 766.20 |  | 621.29 | [8 empty] | 754.63 |  |  | 727.53 | [6 empty] | 754.22 |  | 673.74 |  |  |  | 271.78 |  |  | 758.71 |  |  | 739.08 | [9 empty] | 670.41 |  |  | 8111.96
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 89.10 |  |  |  | 37.60 |  |  | 100.00 |  |  | 99.98 | [9 empty] | 99.96 |  |  | 93.94
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 90.33 |  |  |  | 37.60 |  |  | 100.00 |  |  | 99.98 | [9 empty] | 99.96 |  |  | 94.04
LF [%] |  |  |  |  | 93.75 | 100.73 |  |  |  | 102.98 |  | 86.29 | [8 empty] | 101.43 |  |  | 101.05 | [6 empty] | 101.37 |  | 90.56 |  |  |  | 37.75 |  |  | 101.98 |  |  | 102.65 | [9 empty] | 90.11 |  |  | 92.60
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 92.22 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 90.73 |  |  |  | 43.06 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.89
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.04 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.04 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 9.67 |  |  |  | 62.40 |  |  | 0.00 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 5.95
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 1.24 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.11
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 68073.1 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.4 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.79 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.37 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.85 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.77 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.87 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.06 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.49 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 5683.72 |  |  | 6017 |  |  |  | 1000 | [10 empty] | 99.79 |  |  |  | 99.79 | [5 empty] | 102.21 |  |  | 100.00 |  |  |  | 0.20 |  | 0.20 | [8 empty] | 0.01 |  |  |  |  | 0.00
2016 |  |  |  | 6911.71 |  |  | 6874 |  |  |  | 1000 | [10 empty] | 77.59 |  |  |  | 77.69 | [5 empty] | 78.69 |  |  | 78.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.31 |  |  |  |  | 0.10
2017 |  |  |  | 7497.38 |  |  | 7476 |  |  |  | 1000 | [10 empty] | 87.99 |  |  |  | 87.99 | [5 empty] | 85.59 |  |  | 85.34 |  |  |  | 0.52 |  | 0.46 | [8 empty] | 11.55 |  |  |  |  | 0.00
2018 |  |  |  | 8910.12 |  |  | 8760 |  |  |  | 1000 | [10 empty] | 99.95 |  |  |  | 99.98 | [5 empty] | 101.71 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.04
2019 |  |  |  | 7478.07 |  |  | 7943 |  |  |  | 1000 | [10 empty] | 89.97 |  |  |  | 90.27 | [5 empty] | 85.37 |  |  | 90.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.73 |  |  |  |  | 0.30
2020 |  |  |  | 6539.67 |  |  | 6854 |  |  |  | 1000 | [10 empty] | 88.49 |  |  |  | 88.49 | [5 empty] | 74.45 |  |  | 78.03 |  |  |  | 2.84 |  | 2.59 | [8 empty] | 8.92 |  |  |  |  | 0.00
2021 |  |  |  | 8783.89 |  |  | 8760 |  |  |  | 1000 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.27 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2022 |  |  |  | 8156.58 |  |  | 8077 |  |  |  | 1000 | [10 empty] | 91.78 |  |  |  | 91.78 | [5 empty] | 93.11 |  |  | 92.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.21 |  |  |  |  | 0.00
2023 |  |  |  | 8111.96 |  |  | 8225 |  |  |  | 1000 | [10 empty] | 93.94 |  |  |  | 94.04 | [5 empty] | 92.60 |  |  | 93.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.95 |  |  |  |  | 0.11
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2015 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 5
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 479 | [14 empty] | 645
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 3
I. |  | Grid capacity limitation | [31 empty] | 53 | [19 empty] | 120
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 34
Z. |  | Other | [35 empty] | 1 |  |  |  | 26
Subtotal | [22 empty] | 479 | [10 empty] | 53 |  |  |  | 649 |  |  |  | 31 | [11 empty] | 154
Total | [22 empty] | 532 | [14 empty] | 834
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2015 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
33. |  |  | Circulating Water System | [34 empty] | 25
42. |  |  | Electrical Power Supply Systems | [19 empty] | 53 | [14 empty] | 117
Total | [22 empty] | 53 | [14 empty] | 146
Highlights (2023)
Unit 2 of Yangjiang Nuclear Power Plant was disconnected from the grid for Y206 outage on August 29,2023, and re-connected to the grid on September 18. The unit operated at full power at all times except during holidays and grid line maintenance in which it operated at reduced power in order to cooperate with peak shaving of the grid (including 1 shutdown for standby to cooperate with the grid). No scrams has occurred throughout the year.

## YANGJIANG-3
2023 Operating Experience
CN-40 | [8 empty] | YANGJIANG-3 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-11-15
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-10-18
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-01-01
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8071.11 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.93 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.93 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.06 %
Load Factor (LF) | [18 empty] | : | 92.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.32 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 673 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 472.93 | 260.38 |  |  |  | 769.13 |  | 690.82 | [8 empty] | 755.35 |  |  | 728.71 | [6 empty] | 755.42 |  | 754.19 |  |  |  | 712.61 |  |  | 759.52 |  |  | 739.91 | [9 empty] | 672.14 |  |  | 8071.11
EAF [%] |  |  |  |  | 61.39 | 37.73 |  |  |  | 99.98 |  | 99.95 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.93
UCF [%] |  |  |  |  | 61.39 | 37.73 |  |  |  | 99.98 |  | 99.95 | [8 empty] | 99.99 |  |  | 100.00 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.93
LF [%] |  |  |  |  | 63.57 | 38.75 |  |  |  | 103.38 |  | 95.95 | [8 empty] | 101.53 |  |  | 101.21 | [6 empty] | 101.53 |  | 101.37 |  |  |  | 98.97 |  |  | 102.09 |  |  | 102.77 | [9 empty] | 90.34 |  |  | 92.14
OF [%] |  |  |  |  | 61.69 | 42.26 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.32
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 38.61 | 62.27 |  |  |  | 0.02 |  | 0.05 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.02 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.06
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 63485.22 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.38 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.36 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.73 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.91 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.18 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.76 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 7593.85 |  |  | 7559 |  |  |  | 1000 | [10 empty] | 91.12 |  |  |  | 91.24 | [5 empty] | 86.45 |  |  | 86.05 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.75 |  |  |  |  | 0.12
2017 |  |  |  | 7396.07 |  |  | 7435 |  |  |  | 1000 | [10 empty] | 86.14 |  |  |  | 86.87 | [5 empty] | 84.43 |  |  | 84.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.13 |  |  |  |  | 0.72
2018 |  |  |  | 7926.66 |  |  | 8028 |  |  |  | 1000 | [10 empty] | 91.09 |  |  |  | 91.51 | [5 empty] | 90.49 |  |  | 91.64 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 8.30 |  |  |  |  | 0.41
2019 |  |  |  | 8621.67 |  |  | 8760 |  |  |  | 1000 | [10 empty] | 99.96 |  |  |  | 99.99 | [5 empty] | 98.42 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.04
2020 |  |  |  | 6600.21 |  |  | 7039 |  |  |  | 1000 | [10 empty] | 86.76 |  |  |  | 86.91 | [5 empty] | 75.14 |  |  | 80.13 |  |  |  | 2.70 |  | 2.41 | [8 empty] | 10.68 |  |  |  |  | 0.15
2021 |  |  |  | 7804.98 |  |  | 7978 |  |  |  | 1000 | [10 empty] | 93.41 |  |  |  | 93.41 | [5 empty] | 89.10 |  |  | 91.07 |  |  |  | 0.24 |  | 0.23 | [8 empty] | 6.36 |  |  |  |  | 0.00
2022 |  |  |  | 8991.99 |  |  | 8760 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.65 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2023 |  |  |  | 8071.11 |  |  | 8087 |  |  |  | 1000 | [10 empty] | 91.93 |  |  |  | 91.93 | [5 empty] | 92.14 |  |  | 92.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.06 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2016 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 2
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 673 | [14 empty] | 577
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 3
I. |  | Grid capacity limitation | [51 empty] | 113
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 85
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 4
Z. |  | Other | [39 empty] | 26
Subtotal | [22 empty] | 673 | [14 empty] | 580 |  |  |  | 28 | [11 empty] | 202
Total | [22 empty] | 673 | [14 empty] | 810
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2016 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
33. |  |  | Circulating Water System | [34 empty] | 26
42. |  |  | Electrical Power Supply Systems | [34 empty] | 113
Total | [37 empty] | 141
Highlights (2023)
Unit 3 of Yangjiang Nuclear Power Plant was disconnected from the grid for Y305 outage on January 20,2023, and re-connected to the grid on February 17. The unit operated at full power at all times except during holidays and grid line maintenance in which it operated at reduced power in order to cooperate with peak shaving of the grid. No scrams has occurred throughout the year.

## YANGJIANG-4
2023 Operating Experience
CN-41 | [8 empty] | YANGJIANG-4 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2012-11-17
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2017-01-08
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2017-03-15
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 6 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8978.18 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.99 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.99 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 102.49 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 773.76 | 688.64 |  |  |  | 772.11 |  | 743.27 | [8 empty] | 762.95 |  |  | 728.53 | [6 empty] | 754.59 |  | 756.21 |  |  |  | 729.97 |  |  | 761.34 |  |  | 741.04 | [9 empty] | 765.77 |  |  | 8978.18
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.93 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 99.99
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.93 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.98 |  |  | 99.99
LF [%] |  |  |  |  | 104.00 | 102.48 |  |  |  | 103.78 |  | 103.23 | [8 empty] | 102.55 |  |  | 101.18 | [6 empty] | 101.42 |  | 101.64 |  |  |  | 101.38 |  |  | 102.33 |  |  | 102.92 | [9 empty] | 102.93 |  |  | 102.49
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.07 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.02 |  |  | 0.01
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 53001.67 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.81 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.22 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.31 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 5.99 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.22 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.09 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.43 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2017 |  |  |  | 6759.71 |  |  | 6353 |  |  |  | 1000 | [10 empty] | 90.72 |  |  |  | 91.02 | [5 empty] | 90.26 |  |  | 86.51 |  |  |  | 8.98 |  | 8.98 | [8 empty] | 0.01 |  |  |  |  | 0.30
2018 |  |  |  | 6591.93 |  |  | 6695 |  |  |  | 1000 | [10 empty] | 83.35 |  |  |  | 83.43 | [5 empty] | 75.25 |  |  | 76.43 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 16.57 |  |  |  |  | 0.07
2019 |  |  |  | 6915.91 |  |  | 7164 |  |  |  | 1000 | [10 empty] | 91.88 |  |  |  | 91.88 | [5 empty] | 78.95 |  |  | 81.78 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.11 |  |  |  |  | 0.00
2020 |  |  |  | 7954.62 |  |  | 8216 |  |  |  | 1000 | [10 empty] | 97.02 |  |  |  | 97.11 | [5 empty] | 90.56 |  |  | 93.53 |  |  |  | 2.88 |  | 2.88 | [8 empty] | 0.00 |  |  |  |  | 0.09
2021 |  |  |  | 7977.13 |  |  | 7880 |  |  |  | 1000 | [10 empty] | 89.45 |  |  |  | 89.45 | [5 empty] | 91.06 |  |  | 89.95 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 10.48 |  |  |  |  | 0.00
2022 |  |  |  | 7820.95 |  |  | 7927 |  |  |  | 1000 | [10 empty] | 92.87 |  |  |  | 93.08 | [5 empty] | 89.28 |  |  | 90.49 |  |  |  | 1.18 |  | 1.11 | [8 empty] | 5.81 |  |  |  |  | 0.21
2023 |  |  |  | 8978.18 |  |  | 8760 |  |  |  | 1000 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 102.49 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2017 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 96
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 501
I. |  | Grid capacity limitation | [51 empty] | 101
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 231
Z. |  | Other | [39 empty] | 36
Subtotal | [37 empty] | 501 |  |  |  | 132 | [11 empty] | 332
Total | [22 empty] | 0 | [14 empty] | 965
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2017 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
33. |  |  | Circulating Water System | [34 empty] | 36
42. |  |  | Electrical Power Supply Systems | [34 empty] | 192
Total | [37 empty] | 228
Highlights (2023)
Unit 4 of Yangjiang Nuclear Power operated at full power at all times except during holidays and grid line maintenance in which it operated at reduced power in order to cooperate with peak shaving of the grid. No scrams has occurred throughout the year.

## YANGJIANG-5
2023 Operating Experience
CN-47 | [8 empty] | YANGJIANG-5 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / ACPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2013-09-18
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-05-23
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-07-12
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7988.19 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.19 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.68 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.34 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.98 %
Load Factor (LF) | [18 empty] | : | 91.19 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.15 %
Operating Factor (OF) | [18 empty] | : | 92.33 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 672 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 698.84 | 674.92 |  |  |  | 769.69 |  | 644.19 | [8 empty] | 755.96 |  |  | 729.96 | [6 empty] | 753.34 |  | 753.17 |  |  |  | 523.48 |  |  | 272.10 |  |  | 742.75 | [9 empty] | 669.79 |  |  | 7988.19
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.98 |  | 99.99 |  |  |  | 71.46 |  |  | 35.73 |  |  | 99.97 | [9 empty] | 100.00 |  |  | 92.19
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.98 |  | 100.00 |  |  |  | 73.29 |  |  | 35.73 |  |  | 99.97 | [9 empty] | 100.00 |  |  | 92.34
LF [%] |  |  |  |  | 93.93 | 100.43 |  |  |  | 103.45 |  | 89.47 | [8 empty] | 101.61 |  |  | 101.38 | [6 empty] | 101.26 |  | 101.23 |  |  |  | 72.71 |  |  | 36.57 |  |  | 103.16 | [9 empty] | 90.03 |  |  | 91.19
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 95.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 73.75 |  |  | 39.92 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.33
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 8.04 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.68
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.02 |  | 0.00 |  |  |  | 26.71 |  |  | 56.23 |  |  | 0.03 | [9 empty] | 0.00 |  |  | 6.98
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 1.83 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.15
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 42803.68 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.7 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.98 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.77 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.11 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.11 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.32 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.13 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 4365.35 |  |  | 4847 |  |  |  | 1000 | [10 empty] | 99.11 |  |  |  | 99.94 | [5 empty] | 94.36 |  |  | 97.26 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 0.00 |  |  |  |  | 0.83
2019 |  |  |  | 6699.42 |  |  | 6927 |  |  |  | 1000 | [10 empty] | 82.36 |  |  |  | 82.36 | [5 empty] | 76.48 |  |  | 79.08 |  |  |  | 0.68 |  | 0.56 | [8 empty] | 17.08 |  |  |  |  | 0.00
2020 |  |  |  | 7318.68 |  |  | 7706 |  |  |  | 1000 | [10 empty] | 94.64 |  |  |  | 94.79 | [5 empty] | 83.32 |  |  | 87.73 |  |  |  | 2.83 |  | 2.76 | [8 empty] | 2.45 |  |  |  |  | 0.15
2021 |  |  |  | 8195.95 |  |  | 8314 |  |  |  | 1000 | [10 empty] | 94.39 |  |  |  | 94.40 | [5 empty] | 93.56 |  |  | 94.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.60 |  |  |  |  | 0.01
2022 |  |  |  | 8236.09 |  |  | 8177 |  |  |  | 1000 | [10 empty] | 92.72 |  |  |  | 92.72 | [5 empty] | 94.02 |  |  | 93.34 |  |  |  | 0.24 |  | 0.22 | [8 empty] | 7.06 |  |  |  |  | 0.00
2023 |  |  |  | 7988.19 |  |  | 8088 |  |  |  | 1000 | [10 empty] | 92.19 |  |  |  | 92.34 | [5 empty] | 91.19 |  |  | 92.33 |  |  |  | 0.00 |  | 0.68 | [8 empty] | 6.98 |  |  |  |  | 0.15
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2018 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 60 | [14 empty] | 22
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 576 | [14 empty] | 593
I. |  | Grid capacity limitation | [31 empty] | 33 | [19 empty] | 121
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 61
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 6
Z. |  | Other | [39 empty] | 43
Subtotal | [22 empty] | 576 |  |  |  | 60 | [6 empty] | 33 |  |  |  | 593 |  |  |  | 65 | [11 empty] | 188
Total | [22 empty] | 669 | [14 empty] | 846
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2018 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
14. |  |  | Safety Systems | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
33. |  |  | Circulating Water System | [34 empty] | 42
34. |  |  | Miscellaneous Systems | [19 empty] | 60 | [14 empty] | 11
42. |  |  | Electrical Power Supply Systems | [19 empty] | 33 | [14 empty] | 117
Total | [22 empty] | 93 | [14 empty] | 181
Highlights (2023)
Unit 5 of Yangjiang Nuclear Power Plant was disconnected from the grid for Y504 outage on September 23, 2023, and re-connected to the grid on October 19, 2023. The unit operated at full power at all times except during holidays and grid line maintenance in which it operated at reduced power in order to cooperate with peak shaving of the grid (including 1 shutdown for standby to cooperate with the grid). No scrams has occurred throughout the year.

## YANGJIANG-6
2023 Operating Experience
CN-48 | [8 empty] | YANGJIANG-6 | [26 empty] | CHINA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Owner | [7 empty] | : | YJNPC (Yangjiang Nuclear Power Company)
Reactor Supplier | [7 empty] | : | CFHI (China First Heavy Industries)
Turbine Supplier | [7 empty] | : | SEG (Shanghai Electric Group)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / ACPR-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2013-12-23
Thermal power | [12 empty] | : |  |  | 2905 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-06-29
Gross electrical power | [12 empty] | : |  |  | 1086 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2019-07-24
Reference unit power (net) | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 328.4
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.52
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.45 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 4.45 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.43
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8015.33 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.92 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.92 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.08 %
Load Factor (LF) | [18 empty] | : | 91.5 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 91.21 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 770 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 700.89 | 681.82 |  |  |  | 766.54 |  | 689.28 | [8 empty] | 756.93 |  |  | 723.69 | [6 empty] | 137.87 |  | 752.31 |  |  |  | 540.26 |  |  | 758.19 |  |  | 739.68 | [9 empty] | 767.87 |  |  | 8015.33
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 18.69 |  | 99.60 |  |  |  | 74.03 |  |  | 99.98 |  |  | 100.00 | [9 empty] | 99.97 |  |  | 90.92
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.98 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 18.69 |  | 99.60 |  |  |  | 74.03 |  |  | 99.98 |  |  | 100.00 | [9 empty] | 99.97 |  |  | 90.92
LF [%] |  |  |  |  | 94.21 | 101.46 |  |  |  | 103.03 |  | 95.73 | [8 empty] | 101.74 |  |  | 100.51 | [6 empty] | 18.53 |  | 101.12 |  |  |  | 75.04 |  |  | 101.91 |  |  | 102.73 | [9 empty] | 103.21 |  |  | 91.50
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 22.85 |  | 100.00 |  |  |  | 72.78 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.21
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.02 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 81.31 |  | 0.40 |  |  |  | 25.97 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.03 |  |  | 9.08
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 34778.15 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.87 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.81 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.35 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.84 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.27 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.7 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2019 |  |  |  | 3934.18 |  |  | 3915 |  |  |  | 1000 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 92.83 |  |  | 93.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 5896.66 |  |  | 6526 |  |  |  | 1000 | [10 empty] | 82.41 |  |  |  | 82.41 | [5 empty] | 67.13 |  |  | 74.29 |  |  |  | 4.15 |  | 3.57 | [8 empty] | 14.02 |  |  |  |  | 0.00
2021 |  |  |  | 8522.45 |  |  | 8571 |  |  |  | 1000 | [10 empty] | 99.31 |  |  |  | 99.31 | [5 empty] | 97.29 |  |  | 97.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.69 |  |  |  |  | 0.00
2022 |  |  |  | 8349.54 |  |  | 8234 |  |  |  | 1000 | [10 empty] | 93.56 |  |  |  | 93.56 | [5 empty] | 95.31 |  |  | 94.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.44 |  |  |  |  | 0.00
2023 |  |  |  | 8015.33 |  |  | 7990 |  |  |  | 1000 | [10 empty] | 90.92 |  |  |  | 90.92 | [5 empty] | 91.50 |  |  | 91.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.08 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2019 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 574 | [14 empty] | 519
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 182 | [14 empty] | 54
I. |  | Grid capacity limitation | [51 empty] | 223
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 56
Z. |  | Other | [39 empty] | 49
Subtotal | [22 empty] | 756 | [14 empty] | 573 |  |  |  | 49 | [11 empty] | 279
Total | [22 empty] | 756 | [14 empty] | 901
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2019 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
33. |  |  | Circulating Water System | [34 empty] | 47
42. |  |  | Electrical Power Supply Systems | [34 empty] | 215
Total | [37 empty] | 262
Highlights (2023)
Unit 6 of Yangjiang Nuclear Power Plant was disconnected from the grid for Y603 outage on July 6, 2023, and re-connected to the grid on July 30. Unit 6 shut down for maintenance from September 6 to September 14. The unit operated at full power at all times except during holidays and grid line maintenance in which it operated at reduced power in order to cooperate with peak shaving of the grid. No scrams has occurred throughout the year.