## DUKOVANY-1
2023 Operating Experience
CZ-4 | [8 empty] | DUKOVANY-1 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-01-01
Thermal power | [12 empty] | : |  |  | 1444 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-02-24
Gross electrical power | [12 empty] | : |  |  | 500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-05-03
Reference unit power (net) | [12 empty] | : |  |  | 468 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.26
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 297
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.3
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3207.28 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.52 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.03 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.42 %
Unit Capability Factor (UCF) | [18 empty] | : | 80.64 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 18.94 %
Load Factor (LF) | [18 empty] | : | 78.23 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.62 %
Operating Factor (OF) | [18 empty] | : | 81.11 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1655 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 344.60 | 313.91 |  |  |  | 347.03 |  | 325.61 | [8 empty] | 285.07 |  |  | 11.41 | [6 empty] | 0.00 |  | 216.15 |  |  |  | 328.70 |  |  | 345.68 |  |  | 338.79 | [9 empty] | 350.33 |  |  | 3207.28
EAF [%] |  |  |  |  | 98.53 | 99.36 |  |  |  | 99.35 |  | 96.31 | [8 empty] | 82.38 |  |  | 3.48 | [6 empty] | 0.00 |  | 62.25 |  |  |  | 97.47 |  |  | 98.89 |  |  | 99.87 | [9 empty] | 100.00 |  |  | 78.03
UCF [%] |  |  |  |  | 100.00 | 99.97 |  |  |  | 99.97 |  | 99.83 | [8 empty] | 100.00 |  |  | 4.77 | [6 empty] | 0.00 |  | 64.49 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 80.64
LF [%] |  |  |  |  | 98.97 | 99.81 |  |  |  | 99.67 |  | 96.63 | [8 empty] | 81.87 |  |  | 3.39 | [6 empty] | 0.00 |  | 62.08 |  |  |  | 97.55 |  |  | 99.28 |  |  | 100.54 | [9 empty] | 100.62 |  |  | 78.23
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 5.42 | [6 empty] | 0.00 |  | 69.09 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.11
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 7.13 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.52
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 4.95 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.42
PUF [%] |  |  |  |  | 0.00 | 0.03 |  |  |  | 0.03 |  | 0.17 | [8 empty] | 0.00 |  |  | 95.23 | [6 empty] | 100.00 |  | 30.56 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 18.94
XUF [%] |  |  |  |  | 1.47 | 0.61 |  |  |  | 0.62 |  | 3.52 | [8 empty] | 17.62 |  |  | 1.29 | [6 empty] | 0.00 |  | 2.24 |  |  |  | 2.53 |  |  | 1.11 |  |  | 0.12 | [9 empty] | 0.00 |  |  | 2.62
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 122229.56 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.25 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.05 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.28 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.98 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.85 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.93 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.38 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 1993.92 |  |  | 5418 |  |  |  | 396 | [10 empty] | 88.11 |  |  |  | 88.11 | [5 empty] | 86.73 |  |  | 88.06 |  |  |  | 2.36 |  | 2.13 | [8 empty] | 9.77 |  |  |  |  | 0.00
1986 |  |  |  | 2658.35 |  |  | 7094 |  |  |  | 403 | [10 empty] | 76.12 |  |  |  | 76.15 | [5 empty] | 75.30 |  |  | 80.98 |  |  |  | 1.22 |  | 0.94 | [8 empty] | 22.91 |  |  |  |  | 0.03
1987 |  |  |  | 2575.95 |  |  | 6867 |  |  |  | 408 | [10 empty] | 70.74 |  |  |  | 74.73 | [5 empty] | 72.07 |  |  | 78.39 |  |  |  | 0.79 |  | 0.60 | [8 empty] | 24.68 |  |  |  |  | 3.99
1988 |  |  |  | 2523.99 |  |  | 6996 |  |  |  | 408 | [10 empty] | 71.53 |  |  |  | 74.17 | [5 empty] | 70.43 |  |  | 79.64 |  |  |  | 1.48 |  | 1.11 | [8 empty] | 24.72 |  |  |  |  | 2.64
1989 |  |  |  | 2940.57 |  |  | 7579 |  |  |  | 408 | [10 empty] | 82.01 |  |  |  | 82.60 | [5 empty] | 82.27 |  |  | 86.52 |  |  |  | 2.05 |  | 1.72 | [8 empty] | 15.68 |  |  |  |  | 0.59
1990 |  |  |  | 2965.55 |  |  | 7658 |  |  |  | 408 | [10 empty] | 82.49 |  |  |  | 84.34 | [5 empty] | 82.97 |  |  | 87.42 |  |  |  | 3.02 |  | 2.62 | [8 empty] | 13.04 |  |  |  |  | 1.85
1991 |  |  |  | 2581.09 |  |  | 6751 |  |  |  | 408 | [10 empty] | 70.50 |  |  |  | 70.68 | [5 empty] | 72.22 |  |  | 77.07 |  |  |  | 9.25 |  | 7.20 | [8 empty] | 22.12 |  |  |  |  | 0.18
1992 |  |  |  | 3172.77 |  |  | 7537 |  |  |  | 408 | [10 empty] | 80.45 |  |  |  | 80.90 | [5 empty] | 88.53 |  |  | 85.80 |  |  |  | 3.16 |  | 2.64 | [8 empty] | 16.46 |  |  |  |  | 0.44
1993 |  |  |  | 3239.65 |  |  | 7649 |  |  |  | 442 | [10 empty] | 83.67 |  |  |  | 83.67 | [5 empty] | 83.67 |  |  | 87.32 |  |  |  | 2.87 |  | 2.47 | [8 empty] | 13.86 |  |  |  |  | 0.00
1994 |  |  |  | 3278.54 |  |  | 7656 |  |  |  | 442 | [10 empty] | 84.64 |  |  |  | 84.64 | [5 empty] | 84.67 |  |  | 87.40 |  |  |  | 3.15 |  | 2.76 | [8 empty] | 12.60 |  |  |  |  | 0.00
1995 |  |  |  | 2966.06 |  |  | 7022 |  |  |  | 442 | [10 empty] | 76.78 |  |  |  | 76.78 | [5 empty] | 76.60 |  |  | 80.16 |  |  |  | 4.40 |  | 3.53 | [8 empty] | 19.69 |  |  |  |  | 0.00
1996 |  |  |  | 3144.62 |  |  | 7592 |  |  |  | 412 | [10 empty] | 85.36 |  |  |  | 86.01 | [5 empty] | 86.89 |  |  | 86.43 |  |  |  | 2.73 |  | 2.42 | [8 empty] | 11.57 |  |  |  |  | 0.65
1997 |  |  |  | 3295.57 |  |  | 7678 |  |  |  | 440 | [10 empty] | 85.26 |  |  |  | 86.76 | [5 empty] | 85.50 |  |  | 87.65 |  |  |  | 1.01 |  | 0.88 | [8 empty] | 12.36 |  |  |  |  | 1.50
1998 |  |  |  | 2973.35 |  |  | 7518 |  |  |  | 412 | [10 empty] | 82.62 |  |  |  | 85.44 | [5 empty] | 82.38 |  |  | 85.82 |  |  |  | 3.29 |  | 2.91 | [8 empty] | 11.65 |  |  |  |  | 2.82
1999 |  |  |  | 2901.08 |  |  | 7034 |  |  |  | 412 | [10 empty] | 79.23 |  |  |  | 79.75 | [5 empty] | 80.38 |  |  | 80.30 |  |  |  | 0.46 |  | 0.37 | [8 empty] | 19.88 |  |  |  |  | 0.52
2000 |  |  |  | 3327.93 |  |  | 7934 |  |  |  | 412 | [10 empty] | 89.73 |  |  |  | 89.84 | [5 empty] | 91.96 |  |  | 90.32 |  |  |  | 0.48 |  | 0.44 | [8 empty] | 9.72 |  |  |  |  | 0.11
2001 |  |  |  | 3328.90 |  |  | 7996 |  |  |  | 412 | [10 empty] | 90.16 |  |  |  | 90.57 | [5 empty] | 92.24 |  |  | 91.28 |  |  |  | 0.77 |  | 0.70 | [8 empty] | 8.73 |  |  |  |  | 0.42
2002 |  |  |  | 3267.45 |  |  | 7926 |  |  |  | 412 | [10 empty] | 88.92 |  |  |  | 89.63 | [5 empty] | 90.53 |  |  | 90.48 |  |  |  | 1.03 |  | 0.94 | [8 empty] | 9.43 |  |  |  |  | 0.71
2003 |  |  |  | 3032.00 |  |  | 7261 |  |  |  | 412 | [10 empty] | 82.63 |  |  |  | 82.89 | [5 empty] | 84.01 |  |  | 82.89 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 17.06 |  |  |  |  | 0.25
2004 |  |  |  | 3035.50 |  |  | 7349 |  |  |  | 412 | [10 empty] | 82.91 |  |  |  | 83.65 | [5 empty] | 83.88 |  |  | 83.66 |  |  |  | 0.01 |  | 1.17 | [8 empty] | 15.18 |  |  |  |  | 0.73
2005 |  |  |  | 3324.55 |  |  | 8015 |  |  |  | 412 | [10 empty] | 90.62 |  |  |  | 91.26 | [5 empty] | 92.12 |  |  | 91.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.74 |  |  |  |  | 0.64
2006 |  |  |  | 3271.63 |  |  | 8014 |  |  |  | 412 | [10 empty] | 89.73 |  |  |  | 91.20 | [5 empty] | 90.65 |  |  | 91.48 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.79 |  |  |  |  | 1.46
2007 |  |  |  | 2967.32 |  |  | 7198 |  |  |  | 427 | [10 empty] | 80.92 |  |  |  | 81.36 | [5 empty] | 81.72 |  |  | 82.17 |  |  |  | 1.23 |  | 1.01 | [8 empty] | 17.63 |  |  |  |  | 0.45
2008 |  |  |  | 3485.30 |  |  | 8090 |  |  |  | 427 | [10 empty] | 91.59 |  |  |  | 91.80 | [5 empty] | 92.92 |  |  | 92.10 |  |  |  | 1.66 |  | 1.55 | [8 empty] | 6.65 |  |  |  |  | 0.21
2009 |  |  |  | 3518.64 |  |  | 8186 |  |  |  | 427 | [10 empty] | 92.48 |  |  |  | 92.68 | [5 empty] | 94.07 |  |  | 93.45 |  |  |  | 0.49 |  | 0.68 | [8 empty] | 6.65 |  |  |  |  | 0.20
2010 |  |  |  | 3573.83 |  |  | 8256 |  |  |  | 427 | [10 empty] | 93.76 |  |  |  | 93.98 | [5 empty] | 95.54 |  |  | 94.25 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 5.96 |  |  |  |  | 0.21
2011 |  |  |  | 2939.01 |  |  | 6877 |  |  |  | 468 | [10 empty] | 76.93 |  |  |  | 77.28 | [5 empty] | 77.94 |  |  | 78.50 |  |  |  | 0.43 |  | 0.33 | [8 empty] | 22.39 |  |  |  |  | 0.35
2012 |  |  |  | 3733.44 |  |  | 8049 |  |  |  | 468 | [10 empty] | 90.24 |  |  |  | 91.13 | [5 empty] | 90.82 |  |  | 91.63 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 8.82 |  |  |  |  | 0.89
2013 |  |  |  | 3778.58 |  |  | 8142 |  |  |  | 468 | [10 empty] | 91.72 |  |  |  | 92.63 | [5 empty] | 92.17 |  |  | 92.95 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 7.27 |  |  |  |  | 0.91
2014 |  |  |  | 3785.47 |  |  | 8141 |  |  |  | 468 | [10 empty] | 91.74 |  |  |  | 92.55 | [5 empty] | 92.34 |  |  | 92.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.45 |  |  |  |  | 0.80
2015 |  |  |  | 2655.64 |  |  | 5753 |  |  |  | 468 | [10 empty] | 64.66 |  |  |  | 65.63 | [5 empty] | 64.78 |  |  | 65.67 |  |  |  | 0.00 |  | 17.81 | [8 empty] | 16.56 |  |  |  |  | 0.97
2016 |  |  |  | 3579.05 |  |  | 7721 |  |  |  | 468 | [10 empty] | 86.69 |  |  |  | 87.58 | [5 empty] | 87.07 |  |  | 87.91 |  |  |  | 0.00 |  | 12.35 | [8 empty] | 0.07 |  |  |  |  | 0.89
2017 |  |  |  | 2642.46 |  |  | 5780 |  |  |  | 468 | [10 empty] | 64.32 |  |  |  | 65.46 | [5 empty] | 64.46 |  |  | 65.98 |  |  |  | 0.30 |  | 0.19 | [8 empty] | 34.35 |  |  |  |  | 1.13
2018 |  |  |  | 3370.83 |  |  | 7305 |  |  |  | 468 | [10 empty] | 81.91 |  |  |  | 82.82 | [5 empty] | 82.22 |  |  | 83.39 |  |  |  | 2.36 |  | 2.00 | [8 empty] | 15.18 |  |  |  |  | 0.91
2019 |  |  |  | 3430.94 |  |  | 7462 |  |  |  | 468 | [10 empty] | 83.62 |  |  |  | 84.83 | [5 empty] | 83.69 |  |  | 85.18 |  |  |  | 0.18 |  | 2.68 | [8 empty] | 12.50 |  |  |  |  | 1.21
2020 |  |  |  | 3526.21 |  |  | 7620 |  |  |  | 468 | [10 empty] | 85.48 |  |  |  | 86.67 | [5 empty] | 85.78 |  |  | 86.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.33 |  |  |  |  | 1.19
2021 |  |  |  | 3571.79 |  |  | 7761 |  |  |  | 468 | [10 empty] | 86.90 |  |  |  | 88.15 | [5 empty] | 87.12 |  |  | 88.60 |  |  |  | 0.10 |  | 9.57 | [8 empty] | 2.28 |  |  |  |  | 1.25
2022 |  |  |  | 3490.34 |  |  | 7673 |  |  |  | 468 | [10 empty] | 85.11 |  |  |  | 87.12 | [5 empty] | 85.14 |  |  | 87.59 |  |  |  | 0.15 |  | 0.13 | [8 empty] | 12.75 |  |  |  |  | 2.01
2023 |  |  |  | 3207.28 |  |  | 7105 |  |  |  | 468 | [10 empty] | 78.03 |  |  |  | 80.64 | [5 empty] | 78.23 |  |  | 81.11 |  |  |  | 0.52 |  | 0.42 | [8 empty] | 18.94 |  |  |  |  | 2.62
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 36 | [14 empty] | 72
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1619 | [14 empty] | 1103
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 71
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 68
Subtotal | [22 empty] | 1619 |  |  |  | 36 | [10 empty] | 1174 |  |  |  | 140 | [11 empty] | 4
Total | [22 empty] | 1655 | [14 empty] | 1318
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 0
12. |  |  | Reactor I&C Systems | [34 empty] | 3
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 36 | [14 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 5
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
16. |  |  | Steam generation systems | [34 empty] | 34
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [22 empty] | 36 | [14 empty] | 69

## DUKOVANY-2
2023 Operating Experience
CZ-5 | [8 empty] | DUKOVANY-2 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-01-01
Thermal power | [12 empty] | : |  |  | 1444 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-01-30
Gross electrical power | [12 empty] | : |  |  | 500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-03-21
Reference unit power (net) | [12 empty] | : |  |  | 471 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.26
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 297
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.3
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3115.8 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 75.91 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 77.75 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 22.24 %
Load Factor (LF) | [18 empty] | : | 75.52 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.84 %
Operating Factor (OF) | [18 empty] | : | 78.36 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1896 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 345.55 | 106.48 |  |  |  | 0.00 |  | 214.29 | [8 empty] | 339.20 |  |  | 328.41 | [6 empty] | 102.41 |  | 331.37 |  |  |  | 325.50 |  |  | 341.15 |  |  | 334.68 | [9 empty] | 346.75 |  |  | 3115.80
EAF [%] |  |  |  |  | 98.87 | 33.72 |  |  |  | 0.00 |  | 64.44 | [8 empty] | 97.09 |  |  | 97.08 | [6 empty] | 29.60 |  | 95.29 |  |  |  | 96.54 |  |  | 97.64 |  |  | 99.02 | [9 empty] | 99.26 |  |  | 75.91
UCF [%] |  |  |  |  | 100.00 | 33.85 |  |  |  | 0.00 |  | 67.41 | [8 empty] | 100.00 |  |  | 99.66 | [6 empty] | 30.30 |  | 99.43 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.94 |  |  | 77.75
LF [%] |  |  |  |  | 98.61 | 33.64 |  |  |  | 0.00 |  | 63.19 | [8 empty] | 96.80 |  |  | 96.84 | [6 empty] | 29.22 |  | 94.56 |  |  |  | 95.98 |  |  | 97.35 |  |  | 98.69 | [9 empty] | 98.95 |  |  | 75.52
OF [%] |  |  |  |  | 100.00 | 34.67 |  |  |  | 0.00 |  | 70.69 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 32.53 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.36
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.06 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.03 |  |  | 0.01
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.06 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.03 |  |  | 0.01
PUF [%] |  |  |  |  | 0.00 | 66.15 |  |  |  | 100.00 |  | 32.59 | [8 empty] | 0.00 |  |  | 0.34 | [6 empty] | 69.70 |  | 0.51 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.03 |  |  | 22.24
XUF [%] |  |  |  |  | 1.13 | 0.13 |  |  |  | 0.00 |  | 2.97 | [8 empty] | 2.91 |  |  | 2.58 | [6 empty] | 0.70 |  | 4.14 |  |  |  | 3.46 |  |  | 2.36 |  |  | 0.98 | [9 empty] | 0.68 |  |  | 1.84
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 117421.22 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.54 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.57 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.2 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.57 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.23 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.23 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.08 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 2792.72 |  |  | 7615 |  |  |  | 408 | [10 empty] | 93.71 |  |  |  | 93.71 | [5 empty] | 93.32 |  |  | 96.65 |  |  |  | 0.83 |  | 0.78 | [8 empty] | 5.50 |  |  |  |  | 0.00
1987 |  |  |  | 2668.61 |  |  | 6997 |  |  |  | 408 | [10 empty] | 71.57 |  |  |  | 76.57 | [5 empty] | 74.67 |  |  | 79.87 |  |  |  | 0.21 |  | 0.16 | [8 empty] | 23.28 |  |  |  |  | 5.00
1988 |  |  |  | 2771.27 |  |  | 6963 |  |  |  | 408 | [10 empty] | 74.59 |  |  |  | 74.89 | [5 empty] | 77.33 |  |  | 79.27 |  |  |  | 5.14 |  | 4.06 | [8 empty] | 21.06 |  |  |  |  | 0.30
1989 |  |  |  | 3011.03 |  |  | 7713 |  |  |  | 408 | [10 empty] | 82.23 |  |  |  | 82.68 | [5 empty] | 84.25 |  |  | 88.05 |  |  |  | 1.71 |  | 1.43 | [8 empty] | 15.89 |  |  |  |  | 0.45
1990 |  |  |  | 2822.65 |  |  | 7566 |  |  |  | 408 | [10 empty] | 76.46 |  |  |  | 80.06 | [5 empty] | 78.98 |  |  | 86.37 |  |  |  | 5.38 |  | 4.55 | [8 empty] | 15.39 |  |  |  |  | 3.60
1991 |  |  |  | 2901.44 |  |  | 7600 |  |  |  | 408 | [10 empty] | 81.18 |  |  |  | 81.60 | [5 empty] | 81.18 |  |  | 86.76 |  |  |  | 3.41 |  | 2.88 | [8 empty] | 15.52 |  |  |  |  | 0.42
1992 |  |  |  | 2830.61 |  |  | 6551 |  |  |  | 408 | [10 empty] | 71.42 |  |  |  | 71.59 | [5 empty] | 78.98 |  |  | 74.58 |  |  |  | 0.74 |  | 0.53 | [8 empty] | 27.88 |  |  |  |  | 0.16
1993 |  |  |  | 3256.93 |  |  | 7496 |  |  |  | 440 | [10 empty] | 84.16 |  |  |  | 84.16 | [5 empty] | 84.50 |  |  | 85.57 |  |  |  | 1.34 |  | 1.14 | [8 empty] | 14.70 |  |  |  |  | 0.00
1994 |  |  |  | 3094.32 |  |  | 7315 |  |  |  | 440 | [10 empty] | 79.64 |  |  |  | 80.75 | [5 empty] | 80.28 |  |  | 83.50 |  |  |  | 6.29 |  | 5.42 | [8 empty] | 13.82 |  |  |  |  | 1.11
1995 |  |  |  | 3263.35 |  |  | 7720 |  |  |  | 440 | [10 empty] | 84.35 |  |  |  | 85.52 | [5 empty] | 84.67 |  |  | 88.13 |  |  |  | 3.54 |  | 3.13 | [8 empty] | 11.34 |  |  |  |  | 1.17
1996 |  |  |  | 2831.01 |  |  | 6917 |  |  |  | 412 | [10 empty] | 77.31 |  |  |  | 78.32 | [5 empty] | 78.23 |  |  | 78.75 |  |  |  | 1.82 |  | 1.45 | [8 empty] | 20.22 |  |  |  |  | 1.02
1997 |  |  |  | 3144.83 |  |  | 7179 |  |  |  | 440 | [10 empty] | 81.11 |  |  |  | 81.11 | [5 empty] | 81.59 |  |  | 81.95 |  |  |  | 0.89 |  | 0.73 | [8 empty] | 18.16 |  |  |  |  | 0.00
1998 |  |  |  | 3209.23 |  |  | 7803 |  |  |  | 412 | [10 empty] | 87.73 |  |  |  | 88.24 | [5 empty] | 88.92 |  |  | 89.08 |  |  |  | 0.63 |  | 0.56 | [8 empty] | 11.20 |  |  |  |  | 0.51
1999 |  |  |  | 3198.15 |  |  | 7812 |  |  |  | 412 | [10 empty] | 87.81 |  |  |  | 88.44 | [5 empty] | 88.61 |  |  | 89.18 |  |  |  | 2.04 |  | 1.84 | [8 empty] | 9.71 |  |  |  |  | 0.63
2000 |  |  |  | 2954.10 |  |  | 7223 |  |  |  | 412 | [10 empty] | 81.18 |  |  |  | 81.80 | [5 empty] | 81.63 |  |  | 82.23 |  |  |  | 0.78 |  | 0.64 | [8 empty] | 17.56 |  |  |  |  | 0.62
2001 |  |  |  | 3121.12 |  |  | 7646 |  |  |  | 412 | [10 empty] | 86.35 |  |  |  | 86.92 | [5 empty] | 86.48 |  |  | 87.28 |  |  |  | 0.71 |  | 0.62 | [8 empty] | 12.46 |  |  |  |  | 0.56
2002 |  |  |  | 3159.64 |  |  | 7716 |  |  |  | 412 | [10 empty] | 87.83 |  |  |  | 88.30 | [5 empty] | 87.55 |  |  | 88.08 |  |  |  | 0.40 |  | 0.35 | [8 empty] | 11.35 |  |  |  |  | 0.47
2003 |  |  |  | 3252.55 |  |  | 7939 |  |  |  | 412 | [10 empty] | 89.20 |  |  |  | 89.85 | [5 empty] | 90.12 |  |  | 90.63 |  |  |  | 1.01 |  | 0.92 | [8 empty] | 9.23 |  |  |  |  | 0.65
2004 |  |  |  | 3087.75 |  |  | 7439 |  |  |  | 412 | [10 empty] | 84.19 |  |  |  | 84.36 | [5 empty] | 85.31 |  |  | 84.68 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 15.48 |  |  |  |  | 0.16
2005 |  |  |  | 3313.22 |  |  | 8048 |  |  |  | 412 | [10 empty] | 90.75 |  |  |  | 91.25 | [5 empty] | 91.80 |  |  | 91.87 |  |  |  | 0.49 |  | 0.45 | [8 empty] | 8.30 |  |  |  |  | 0.50
2006 |  |  |  | 3294.69 |  |  | 8017 |  |  |  | 412 | [10 empty] | 90.59 |  |  |  | 91.15 | [5 empty] | 91.29 |  |  | 91.52 |  |  |  | 0.29 |  | 0.27 | [8 empty] | 8.58 |  |  |  |  | 0.56
2007 |  |  |  | 3274.74 |  |  | 7983 |  |  |  | 412 | [10 empty] | 90.12 |  |  |  | 90.88 | [5 empty] | 90.74 |  |  | 91.13 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 9.07 |  |  |  |  | 0.77
2008 |  |  |  | 3040.36 |  |  | 7228 |  |  |  | 427 | [10 empty] | 81.60 |  |  |  | 82.08 | [5 empty] | 82.01 |  |  | 82.29 |  |  |  | 0.49 |  | 0.40 | [8 empty] | 17.52 |  |  |  |  | 0.48
2009 |  |  |  | 3507.86 |  |  | 8209 |  |  |  | 427 | [10 empty] | 92.78 |  |  |  | 93.15 | [5 empty] | 93.78 |  |  | 93.71 |  |  |  | 0.41 |  | 0.61 | [8 empty] | 6.24 |  |  |  |  | 0.38
2010 |  |  |  | 3535.93 |  |  | 8250 |  |  |  | 427 | [10 empty] | 93.39 |  |  |  | 93.81 | [5 empty] | 94.53 |  |  | 94.18 |  |  |  | 0.00 |  | 0.06 | [8 empty] | 6.14 |  |  |  |  | 0.42
2011 |  |  |  | 3254.83 |  |  | 7676 |  |  |  | 427 | [10 empty] | 86.33 |  |  |  | 86.73 | [5 empty] | 87.04 |  |  | 87.65 |  |  |  | 0.66 |  | 1.04 | [8 empty] | 12.23 |  |  |  |  | 0.40
2012 |  |  |  | 3047.28 |  |  | 6918 |  |  |  | 471 | [10 empty] | 76.80 |  |  |  | 78.31 | [5 empty] | 76.63 |  |  | 78.76 |  |  |  | 0.82 |  | 0.65 | [8 empty] | 21.04 |  |  |  |  | 1.51
2013 |  |  |  | 3690.57 |  |  | 7984 |  |  |  | 471 | [10 empty] | 89.75 |  |  |  | 90.61 | [5 empty] | 89.45 |  |  | 91.14 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 9.28 |  |  |  |  | 0.85
2014 |  |  |  | 3672.64 |  |  | 8033 |  |  |  | 471 | [10 empty] | 89.25 |  |  |  | 91.15 | [5 empty] | 89.01 |  |  | 91.70 |  |  |  | 0.34 |  | 0.32 | [8 empty] | 8.54 |  |  |  |  | 1.90
2015 |  |  |  | 2495.87 |  |  | 5426 |  |  |  | 471 | [10 empty] | 60.74 |  |  |  | 61.63 | [5 empty] | 60.49 |  |  | 61.94 |  |  |  | 31.80 |  | 32.58 | [8 empty] | 5.79 |  |  |  |  | 0.89
2016 |  |  |  | 2361.31 |  |  | 5194 |  |  |  | 471 | [10 empty] | 57.39 |  |  |  | 58.80 | [5 empty] | 57.07 |  |  | 59.13 |  |  |  | 17.04 |  | 12.08 | [8 empty] | 29.12 |  |  |  |  | 1.41
2017 |  |  |  | 3089.36 |  |  | 6782 |  |  |  | 471 | [10 empty] | 75.20 |  |  |  | 76.32 | [5 empty] | 74.88 |  |  | 77.42 |  |  |  | 3.04 |  | 2.90 | [8 empty] | 20.78 |  |  |  |  | 1.12
2018 |  |  |  | 3384.99 |  |  | 7359 |  |  |  | 471 | [10 empty] | 82.35 |  |  |  | 83.55 | [5 empty] | 82.04 |  |  | 84.01 |  |  |  | 1.80 |  | 1.53 | [8 empty] | 14.92 |  |  |  |  | 1.20
2019 |  |  |  | 2636.32 |  |  | 5751 |  |  |  | 471 | [10 empty] | 64.14 |  |  |  | 65.15 | [5 empty] | 63.90 |  |  | 65.65 |  |  |  | 27.32 |  | 24.94 | [8 empty] | 9.91 |  |  |  |  | 1.01
2020 |  |  |  | 3346.78 |  |  | 7359 |  |  |  | 471 | [10 empty] | 81.25 |  |  |  | 82.83 | [5 empty] | 80.89 |  |  | 83.78 |  |  |  | 0.80 |  | 1.21 | [8 empty] | 15.95 |  |  |  |  | 1.58
2021 |  |  |  | 3546.52 |  |  | 7744 |  |  |  | 471 | [10 empty] | 86.20 |  |  |  | 88.05 | [5 empty] | 85.96 |  |  | 88.40 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 11.81 |  |  |  |  | 1.85
2022 |  |  |  | 3401.12 |  |  | 7448 |  |  |  | 471 | [10 empty] | 82.83 |  |  |  | 84.55 | [5 empty] | 82.43 |  |  | 85.02 |  |  |  | 5.28 |  | 4.71 | [8 empty] | 10.74 |  |  |  |  | 1.73
2023 |  |  |  | 3115.80 |  |  | 6864 |  |  |  | 471 | [10 empty] | 75.91 |  |  |  | 77.75 | [5 empty] | 75.52 |  |  | 78.36 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 22.24 |  |  |  |  | 1.84
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1986 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 92
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1394 | [14 empty] | 1007
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 502 | [14 empty] | 76
E. |  | Testing of plant systems or components | [39 empty] | 2
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 115
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 122
Subtotal | [22 empty] | 1896 | [14 empty] | 1198 |  |  |  | 216 | [11 empty] | 4
Total | [22 empty] | 1896 | [14 empty] | 1418
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1986 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 9
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 18
16. |  |  | Steam generation systems | [34 empty] | 62
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [37 empty] | 112

## DUKOVANY-3
2023 Operating Experience
CZ-8 | [8 empty] | DUKOVANY-3 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-03-01
Thermal power | [12 empty] | : |  |  | 1444 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-11-14
Gross electrical power | [12 empty] | : |  |  | 500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-12-20
Reference unit power (net) | [12 empty] | : |  |  | 468 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.26
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 297
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.3
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3936.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.09 %
Energy Availability Factor (EAF) | [18 empty] | : | 95.62 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.09 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.85 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.06 %
Load Factor (LF) | [18 empty] | : | 96.02 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.23 %
Operating Factor (OF) | [18 empty] | : | 98.6 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 123 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 349.72 | 315.38 |  |  |  | 347.48 |  | 335.82 | [8 empty] | 341.60 |  |  | 325.24 | [6 empty] | 332.22 |  | 331.41 |  |  |  | 323.52 |  |  | 341.06 |  |  | 335.30 | [9 empty] | 257.82 |  |  | 3936.58
EAF [%] |  |  |  |  | 99.77 | 99.64 |  |  |  | 99.30 |  | 99.08 | [8 empty] | 97.70 |  |  | 96.15 | [6 empty] | 95.13 |  | 94.99 |  |  |  | 95.60 |  |  | 97.37 |  |  | 99.03 | [9 empty] | 74.26 |  |  | 95.62
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.81 |  | 100.00 |  |  |  | 100.00 |  |  | 99.89 |  |  | 100.00 | [9 empty] | 74.96 |  |  | 97.85
LF [%] |  |  |  |  | 100.44 | 100.28 |  |  |  | 99.80 |  | 99.66 | [8 empty] | 98.11 |  |  | 96.52 | [6 empty] | 95.41 |  | 95.18 |  |  |  | 96.01 |  |  | 97.95 |  |  | 99.51 | [9 empty] | 74.04 |  |  | 96.02
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 83.47 |  |  | 98.60
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 24.74 |  |  | 2.09
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 24.64 |  |  | 2.09
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.19 |  | 0.00 |  |  |  | 0.00 |  |  | 0.11 |  |  | 0.00 | [9 empty] | 0.40 |  |  | 0.06
XUF [%] |  |  |  |  | 0.23 | 0.36 |  |  |  | 0.70 |  | 0.92 | [8 empty] | 2.30 |  |  | 3.85 | [6 empty] | 4.68 |  | 5.01 |  |  |  | 4.40 |  |  | 2.52 |  |  | 0.97 | [9 empty] | 0.70 |  |  | 2.23
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 116999.07 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.99 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.72 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.22 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.25 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.53 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.62 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.53 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.66 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 280.19 |  |  | 1356 |  |  |  | 408 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1987 |  |  |  | 3109.91 |  |  | 7644 |  |  |  | 408 | [10 empty] | 84.32 |  |  |  | 86.35 | [5 empty] | 87.01 |  |  | 87.26 |  |  |  | 0.46 |  | 0.40 | [8 empty] | 13.25 |  |  |  |  | 2.03
1988 |  |  |  | 2988.88 |  |  | 7672 |  |  |  | 408 | [10 empty] | 79.96 |  |  |  | 81.44 | [5 empty] | 83.40 |  |  | 87.34 |  |  |  | 0.40 |  | 0.33 | [8 empty] | 18.22 |  |  |  |  | 1.48
1989 |  |  |  | 2685.66 |  |  | 6678 |  |  |  | 408 | [10 empty] | 71.04 |  |  |  | 71.39 | [5 empty] | 75.14 |  |  | 76.23 |  |  |  | 1.53 |  | 1.11 | [8 empty] | 27.50 |  |  |  |  | 0.35
1990 |  |  |  | 2981.97 |  |  | 7763 |  |  |  | 408 | [10 empty] | 80.32 |  |  |  | 84.97 | [5 empty] | 83.43 |  |  | 88.62 |  |  |  | 2.80 |  | 2.44 | [8 empty] | 12.58 |  |  |  |  | 4.65
1991 |  |  |  | 2987.03 |  |  | 7784 |  |  |  | 408 | [10 empty] | 81.28 |  |  |  | 81.59 | [5 empty] | 83.57 |  |  | 88.86 |  |  |  | 6.94 |  | 6.09 | [8 empty] | 12.33 |  |  |  |  | 0.31
1992 |  |  |  | 2917.94 |  |  | 6678 |  |  |  | 408 | [10 empty] | 72.27 |  |  |  | 72.59 | [5 empty] | 81.42 |  |  | 76.02 |  |  |  | 8.86 |  | 7.06 | [8 empty] | 20.36 |  |  |  |  | 0.32
1993 |  |  |  | 3190.49 |  |  | 7259 |  |  |  | 452 | [10 empty] | 80.51 |  |  |  | 80.51 | [5 empty] | 80.58 |  |  | 82.87 |  |  |  | 3.63 |  | 3.03 | [8 empty] | 16.46 |  |  |  |  | 0.00
1994 |  |  |  | 3343.93 |  |  | 7870 |  |  |  | 452 | [10 empty] | 84.45 |  |  |  | 84.45 | [5 empty] | 84.45 |  |  | 89.84 |  |  |  | 13.39 |  | 13.05 | [8 empty] | 2.49 |  |  |  |  | 0.00
1995 |  |  |  | 2689.63 |  |  | 7788 |  |  |  | 452 | [10 empty] | 70.02 |  |  |  | 87.40 | [5 empty] | 67.93 |  |  | 88.90 |  |  |  | 1.70 |  | 1.51 | [8 empty] | 11.08 |  |  |  |  | 17.38
1996 |  |  |  | 2871.23 |  |  | 7114 |  |  |  | 412 | [10 empty] | 78.29 |  |  |  | 80.39 | [5 empty] | 79.34 |  |  | 80.99 |  |  |  | 2.57 |  | 2.12 | [8 empty] | 17.48 |  |  |  |  | 2.10
1997 |  |  |  | 2904.58 |  |  | 6774 |  |  |  | 440 | [10 empty] | 74.88 |  |  |  | 75.46 | [5 empty] | 75.36 |  |  | 77.33 |  |  |  | 2.29 |  | 1.77 | [8 empty] | 22.77 |  |  |  |  | 0.57
1998 |  |  |  | 3090.14 |  |  | 7564 |  |  |  | 412 | [10 empty] | 85.02 |  |  |  | 85.70 | [5 empty] | 85.62 |  |  | 86.35 |  |  |  | 3.01 |  | 2.66 | [8 empty] | 11.64 |  |  |  |  | 0.67
1999 |  |  |  | 3246.18 |  |  | 7849 |  |  |  | 412 | [10 empty] | 89.28 |  |  |  | 89.86 | [5 empty] | 89.94 |  |  | 89.60 |  |  |  | 0.39 |  | 0.35 | [8 empty] | 9.79 |  |  |  |  | 0.58
2000 |  |  |  | 3187.89 |  |  | 7776 |  |  |  | 412 | [10 empty] | 87.40 |  |  |  | 88.75 | [5 empty] | 88.09 |  |  | 88.52 |  |  |  | 0.42 |  | 0.37 | [8 empty] | 10.88 |  |  |  |  | 1.35
2001 |  |  |  | 3005.99 |  |  | 7309 |  |  |  | 412 | [10 empty] | 82.67 |  |  |  | 83.78 | [5 empty] | 83.29 |  |  | 83.44 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 16.16 |  |  |  |  | 1.12
2002 |  |  |  | 3259.39 |  |  | 7880 |  |  |  | 412 | [10 empty] | 89.56 |  |  |  | 89.89 | [5 empty] | 90.31 |  |  | 89.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.11 |  |  |  |  | 0.33
2003 |  |  |  | 3280.09 |  |  | 7934 |  |  |  | 412 | [10 empty] | 89.83 |  |  |  | 90.50 | [5 empty] | 90.88 |  |  | 90.57 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 9.47 |  |  |  |  | 0.68
2004 |  |  |  | 3302.47 |  |  | 7957 |  |  |  | 412 | [10 empty] | 90.17 |  |  |  | 90.27 | [5 empty] | 91.24 |  |  | 90.57 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 9.64 |  |  |  |  | 0.10
2005 |  |  |  | 2964.87 |  |  | 7034 |  |  |  | 427 | [10 empty] | 79.55 |  |  |  | 80.00 | [5 empty] | 80.19 |  |  | 80.30 |  |  |  | 0.85 |  | 0.68 | [8 empty] | 19.32 |  |  |  |  | 0.45
2006 |  |  |  | 3396.20 |  |  | 8004 |  |  |  | 427 | [10 empty] | 90.01 |  |  |  | 90.83 | [5 empty] | 90.79 |  |  | 91.37 |  |  |  | 0.41 |  | 0.38 | [8 empty] | 8.79 |  |  |  |  | 0.82
2007 |  |  |  | 3427.86 |  |  | 8068 |  |  |  | 427 | [10 empty] | 90.90 |  |  |  | 91.41 | [5 empty] | 91.64 |  |  | 92.10 |  |  |  | 0.49 |  | 0.45 | [8 empty] | 8.13 |  |  |  |  | 0.51
2008 |  |  |  | 3548.84 |  |  | 8273 |  |  |  | 427 | [10 empty] | 93.15 |  |  |  | 93.66 | [5 empty] | 94.62 |  |  | 94.18 |  |  |  | 0.02 |  | 0.37 | [8 empty] | 5.97 |  |  |  |  | 0.50
2009 |  |  |  | 2944.75 |  |  | 6688 |  |  |  | 468 | [10 empty] | 73.96 |  |  |  | 74.69 | [5 empty] | 73.96 |  |  | 76.35 |  |  |  | 0.99 |  | 0.80 | [8 empty] | 24.51 |  |  |  |  | 0.74
2010 |  |  |  | 3283.52 |  |  | 7146 |  |  |  | 468 | [10 empty] | 79.93 |  |  |  | 80.87 | [5 empty] | 80.09 |  |  | 81.58 |  |  |  | 1.99 |  | 3.01 | [8 empty] | 16.13 |  |  |  |  | 0.94
2011 |  |  |  | 3643.88 |  |  | 7940 |  |  |  | 468 | [10 empty] | 89.03 |  |  |  | 89.93 | [5 empty] | 88.88 |  |  | 90.64 |  |  |  | 0.60 |  | 1.10 | [8 empty] | 8.97 |  |  |  |  | 0.90
2012 |  |  |  | 3691.31 |  |  | 8040 |  |  |  | 468 | [10 empty] | 89.82 |  |  |  | 91.09 | [5 empty] | 89.79 |  |  | 91.53 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 8.84 |  |  |  |  | 1.28
2013 |  |  |  | 3542.84 |  |  | 7714 |  |  |  | 468 | [10 empty] | 86.36 |  |  |  | 87.37 | [5 empty] | 86.42 |  |  | 88.06 |  |  |  | 0.31 |  | 0.68 | [8 empty] | 11.95 |  |  |  |  | 1.01
2014 |  |  |  | 3500.03 |  |  | 7639 |  |  |  | 468 | [10 empty] | 85.15 |  |  |  | 86.61 | [5 empty] | 85.37 |  |  | 87.20 |  |  |  | 5.52 |  | 5.81 | [8 empty] | 7.59 |  |  |  |  | 1.46
2015 |  |  |  | 2673.32 |  |  | 5870 |  |  |  | 468 | [10 empty] | 65.48 |  |  |  | 66.71 | [5 empty] | 65.21 |  |  | 67.01 |  |  |  | 29.23 |  | 27.65 | [8 empty] | 5.64 |  |  |  |  | 1.23
2016 |  |  |  | 2336.18 |  |  | 5021 |  |  |  | 468 | [10 empty] | 56.57 |  |  |  | 56.75 | [5 empty] | 56.83 |  |  | 57.16 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 43.24 |  |  |  |  | 0.18
2017 |  |  |  | 2813.49 |  |  | 6072 |  |  |  | 468 | [10 empty] | 68.37 |  |  |  | 68.86 | [5 empty] | 68.63 |  |  | 69.32 |  |  |  | 0.07 |  | 1.68 | [8 empty] | 29.47 |  |  |  |  | 0.48
2018 |  |  |  | 3630.68 |  |  | 7947 |  |  |  | 468 | [10 empty] | 88.45 |  |  |  | 90.37 | [5 empty] | 88.56 |  |  | 90.72 |  |  |  | 3.09 |  | 2.88 | [8 empty] | 6.75 |  |  |  |  | 1.92
2019 |  |  |  | 3521.99 |  |  | 7691 |  |  |  | 468 | [10 empty] | 85.94 |  |  |  | 87.65 | [5 empty] | 85.91 |  |  | 87.80 |  |  |  | 0.04 |  | 3.86 | [8 empty] | 8.49 |  |  |  |  | 1.71
2020 |  |  |  | 2919.55 |  |  | 6452 |  |  |  | 468 | [10 empty] | 70.76 |  |  |  | 72.50 | [5 empty] | 71.02 |  |  | 73.45 |  |  |  | 5.75 |  | 16.72 | [8 empty] | 10.78 |  |  |  |  | 1.74
2021 |  |  |  | 3387.51 |  |  | 7412 |  |  |  | 468 | [10 empty] | 82.32 |  |  |  | 83.75 | [5 empty] | 82.63 |  |  | 84.61 |  |  |  | 3.91 |  | 4.76 | [8 empty] | 11.49 |  |  |  |  | 1.43
2022 |  |  |  | 3477.43 |  |  | 7638 |  |  |  | 468 | [10 empty] | 84.35 |  |  |  | 86.76 | [5 empty] | 84.83 |  |  | 87.20 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.24 |  |  |  |  | 2.41
2023 |  |  |  | 3936.58 |  |  | 8637 |  |  |  | 468 | [10 empty] | 95.62 |  |  |  | 97.85 | [5 empty] | 96.02 |  |  | 98.60 |  |  |  | 2.09 |  | 2.09 | [8 empty] | 0.06 |  |  |  |  | 2.23
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1986 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 123 | [14 empty] | 114
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1007
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 33
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 102
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 97
Z. |  | Other | [39 empty] | 5
Subtotal | [26 empty] | 123 | [10 empty] | 1142 |  |  |  | 216 | [11 empty] | 3
Total | [22 empty] | 123 | [14 empty] | 1361
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1986 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 1
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 44
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 14
33. |  |  | Circulating Water System | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [19 empty] | 123 | [14 empty] | 25
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [22 empty] | 123 | [14 empty] | 115

## DUKOVANY-4
2023 Operating Experience
CZ-9 | [8 empty] | DUKOVANY-4 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-03-01
Thermal power | [12 empty] | : |  |  | 1444 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-06-11
Gross electrical power | [12 empty] | : |  |  | 500 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-07-19
Reference unit power (net) | [12 empty] | : |  |  | 471 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.26
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 297
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.15
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.3
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3189.39 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 77.31 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 79.59 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.4 %
Load Factor (LF) | [18 empty] | : | 77.3 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.28 %
Operating Factor (OF) | [18 empty] | : | 79.91 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1760 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 352.94 | 318.28 |  |  |  | 350.90 |  | 339.25 | [8 empty] | 346.37 |  |  | 331.14 | [6 empty] | 338.77 |  | 337.83 |  |  |  | 306.96 |  |  | 115.07 |  |  | 0.00 | [9 empty] | 51.88 |  |  | 3189.39
EAF [%] |  |  |  |  | 100.00 | 99.95 |  |  |  | 99.83 |  | 99.77 | [8 empty] | 98.85 |  |  | 97.70 | [6 empty] | 96.80 |  | 96.75 |  |  |  | 91.26 |  |  | 33.24 |  |  | 0.00 | [9 empty] | 15.09 |  |  | 77.31
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 40.48 |  |  | 0.00 | [9 empty] | 16.01 |  |  | 79.59
LF [%] |  |  |  |  | 100.72 | 100.56 |  |  |  | 100.14 |  | 100.04 | [8 empty] | 98.84 |  |  | 97.65 | [6 empty] | 96.67 |  | 96.41 |  |  |  | 90.52 |  |  | 32.84 |  |  | 0.00 | [9 empty] | 14.80 |  |  | 77.30
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 41.13 |  |  | 0.00 | [9 empty] | 19.09 |  |  | 79.91
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.57 |  |  | 0.01
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.09 |  |  | 0.01
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 59.52 |  |  | 100.00 | [9 empty] | 83.90 |  |  | 20.40
XUF [%] |  |  |  |  | 0.00 | 0.05 |  |  |  | 0.17 |  | 0.23 | [8 empty] | 1.15 |  |  | 2.30 | [6 empty] | 3.20 |  | 3.25 |  |  |  | 8.74 |  |  | 7.24 |  |  | 0.00 | [9 empty] | 0.92 |  |  | 2.28
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 117499.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.01 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 83.37 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.91 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.3 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 13.79 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.41 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.93 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.85 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 1624.94 |  |  | 4643 |  |  |  | 408 | [10 empty] | 97.85 |  |  |  | 99.92 | [5 empty] | 90.09 |  |  | 94.34 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 0.00 |  |  |  |  | 2.08
1988 |  |  |  | 2764.01 |  |  | 7092 |  |  |  | 408 | [10 empty] | 73.78 |  |  |  | 74.45 | [5 empty] | 77.12 |  |  | 80.74 |  |  |  | 3.05 |  | 2.34 | [8 empty] | 23.20 |  |  |  |  | 0.67
1989 |  |  |  | 2984.55 |  |  | 7314 |  |  |  | 408 | [10 empty] | 80.41 |  |  |  | 80.81 | [5 empty] | 83.51 |  |  | 83.49 |  |  |  | 0.54 |  | 0.44 | [8 empty] | 18.74 |  |  |  |  | 0.41
1990 |  |  |  | 2995.30 |  |  | 7836 |  |  |  | 408 | [10 empty] | 79.96 |  |  |  | 82.75 | [5 empty] | 83.81 |  |  | 89.45 |  |  |  | 2.21 |  | 1.87 | [8 empty] | 15.38 |  |  |  |  | 2.79
1991 |  |  |  | 2671.99 |  |  | 7301 |  |  |  | 408 | [10 empty] | 77.93 |  |  |  | 78.03 | [5 empty] | 74.76 |  |  | 83.34 |  |  |  | 4.57 |  | 3.74 | [8 empty] | 18.23 |  |  |  |  | 0.10
1992 |  |  |  | 3328.41 |  |  | 7614 |  |  |  | 408 | [10 empty] | 83.66 |  |  |  | 84.48 | [5 empty] | 92.87 |  |  | 86.68 |  |  |  | 2.81 |  | 2.45 | [8 empty] | 13.07 |  |  |  |  | 0.82
1993 |  |  |  | 2939.81 |  |  | 6859 |  |  |  | 448 | [10 empty] | 62.05 |  |  |  | 62.05 | [5 empty] | 74.91 |  |  | 78.30 |  |  |  | 21.40 |  | 16.90 | [8 empty] | 21.05 |  |  |  |  | 0.00
1994 |  |  |  | 3259.81 |  |  | 7538 |  |  |  | 448 | [10 empty] | 83.06 |  |  |  | 84.51 | [5 empty] | 83.06 |  |  | 86.05 |  |  |  | 2.85 |  | 2.48 | [8 empty] | 13.01 |  |  |  |  | 1.45
1995 |  |  |  | 3311.14 |  |  | 7712 |  |  |  | 448 | [10 empty] | 85.35 |  |  |  | 85.46 | [5 empty] | 84.37 |  |  | 88.04 |  |  |  | 3.74 |  | 3.32 | [8 empty] | 11.23 |  |  |  |  | 0.11
1996 |  |  |  | 3202.13 |  |  | 7762 |  |  |  | 412 | [10 empty] | 87.13 |  |  |  | 88.19 | [5 empty] | 88.48 |  |  | 88.37 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 11.64 |  |  |  |  | 1.06
1997 |  |  |  | 3149.15 |  |  | 7202 |  |  |  | 440 | [10 empty] | 80.89 |  |  |  | 80.89 | [5 empty] | 81.70 |  |  | 82.21 |  |  |  | 0.50 |  | 0.41 | [8 empty] | 18.70 |  |  |  |  | 0.00
1998 |  |  |  | 3078.56 |  |  | 7536 |  |  |  | 412 | [10 empty] | 83.85 |  |  |  | 85.66 | [5 empty] | 85.30 |  |  | 86.03 |  |  |  | 0.28 |  | 0.24 | [8 empty] | 14.09 |  |  |  |  | 1.81
1999 |  |  |  | 3179.42 |  |  | 7792 |  |  |  | 412 | [10 empty] | 86.60 |  |  |  | 88.64 | [5 empty] | 88.09 |  |  | 88.95 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 11.20 |  |  |  |  | 2.04
2000 |  |  |  | 3234.52 |  |  | 7839 |  |  |  | 412 | [10 empty] | 88.12 |  |  |  | 89.46 | [5 empty] | 89.38 |  |  | 89.24 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 10.45 |  |  |  |  | 1.34
2001 |  |  |  | 3258.06 |  |  | 7946 |  |  |  | 412 | [10 empty] | 89.25 |  |  |  | 90.40 | [5 empty] | 90.27 |  |  | 90.71 |  |  |  | 0.24 |  | 0.21 | [8 empty] | 9.39 |  |  |  |  | 1.15
2002 |  |  |  | 2748.24 |  |  | 6745 |  |  |  | 412 | [10 empty] | 75.57 |  |  |  | 77.29 | [5 empty] | 76.15 |  |  | 77.00 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 22.68 |  |  |  |  | 1.72
2003 |  |  |  | 3309.80 |  |  | 8009 |  |  |  | 412 | [10 empty] | 90.66 |  |  |  | 91.35 | [5 empty] | 91.71 |  |  | 91.43 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 8.63 |  |  |  |  | 0.70
2004 |  |  |  | 3335.38 |  |  | 8029 |  |  |  | 412 | [10 empty] | 90.87 |  |  |  | 91.09 | [5 empty] | 92.16 |  |  | 91.40 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 8.85 |  |  |  |  | 0.23
2005 |  |  |  | 3267.00 |  |  | 8008 |  |  |  | 412 | [10 empty] | 89.62 |  |  |  | 90.27 | [5 empty] | 90.52 |  |  | 91.42 |  |  |  | 0.98 |  | 0.89 | [8 empty] | 8.83 |  |  |  |  | 0.66
2006 |  |  |  | 3159.49 |  |  | 7704 |  |  |  | 412 | [10 empty] | 86.92 |  |  |  | 87.79 | [5 empty] | 87.54 |  |  | 87.95 |  |  |  | 0.16 |  | 0.14 | [8 empty] | 12.07 |  |  |  |  | 0.88
2007 |  |  |  | 3318.99 |  |  | 7854 |  |  |  | 427 | [10 empty] | 88.05 |  |  |  | 88.70 | [5 empty] | 88.73 |  |  | 89.66 |  |  |  | 0.37 |  | 0.33 | [8 empty] | 10.96 |  |  |  |  | 0.65
2008 |  |  |  | 3438.67 |  |  | 8010 |  |  |  | 427 | [10 empty] | 90.35 |  |  |  | 90.74 | [5 empty] | 91.68 |  |  | 91.19 |  |  |  | 0.62 |  | 0.56 | [8 empty] | 8.70 |  |  |  |  | 0.39
2009 |  |  |  | 3100.50 |  |  | 7247 |  |  |  | 427 | [10 empty] | 81.82 |  |  |  | 81.99 | [5 empty] | 82.89 |  |  | 82.73 |  |  |  | 0.31 |  | 0.25 | [8 empty] | 17.75 |  |  |  |  | 0.18
2010 |  |  |  | 2895.11 |  |  | 6846 |  |  |  | 427 | [10 empty] | 76.74 |  |  |  | 77.31 | [5 empty] | 77.40 |  |  | 78.15 |  |  |  | 0.32 |  | 0.24 | [8 empty] | 22.44 |  |  |  |  | 0.57
2011 |  |  |  | 3630.71 |  |  | 8001 |  |  |  | 471 | [10 empty] | 88.78 |  |  |  | 89.87 | [5 empty] | 88.00 |  |  | 91.34 |  |  |  | 4.28 |  | 4.02 | [8 empty] | 6.11 |  |  |  |  | 1.09
2012 |  |  |  | 3620.96 |  |  | 7850 |  |  |  | 471 | [10 empty] | 87.65 |  |  |  | 88.75 | [5 empty] | 87.52 |  |  | 89.37 |  |  |  | 0.14 |  | 2.37 | [8 empty] | 8.87 |  |  |  |  | 1.11
2013 |  |  |  | 3727.91 |  |  | 8009 |  |  |  | 471 | [10 empty] | 90.45 |  |  |  | 91.36 | [5 empty] | 90.35 |  |  | 91.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.63 |  |  |  |  | 0.91
2014 |  |  |  | 3494.80 |  |  | 7591 |  |  |  | 471 | [10 empty] | 84.79 |  |  |  | 86.06 | [5 empty] | 84.70 |  |  | 86.66 |  |  |  | 4.68 |  | 4.23 | [8 empty] | 9.71 |  |  |  |  | 1.27
2015 |  |  |  | 4004.79 |  |  | 8623 |  |  |  | 471 | [10 empty] | 97.05 |  |  |  | 98.00 | [5 empty] | 97.06 |  |  | 98.44 |  |  |  | 1.89 |  | 1.89 | [8 empty] | 0.11 |  |  |  |  | 0.96
2016 |  |  |  | 2936.27 |  |  | 6423 |  |  |  | 471 | [10 empty] | 71.26 |  |  |  | 72.43 | [5 empty] | 70.97 |  |  | 73.12 |  |  |  | 0.44 |  | 0.32 | [8 empty] | 27.25 |  |  |  |  | 1.17
2017 |  |  |  | 2576.88 |  |  | 5542 |  |  |  | 471 | [10 empty] | 62.47 |  |  |  | 62.75 | [5 empty] | 62.46 |  |  | 63.26 |  |  |  | 6.37 |  | 4.27 | [8 empty] | 32.98 |  |  |  |  | 0.28
2018 |  |  |  | 2979.28 |  |  | 6498 |  |  |  | 471 | [10 empty] | 72.22 |  |  |  | 72.99 | [5 empty] | 72.22 |  |  | 74.19 |  |  |  | 10.97 |  | 8.99 | [8 empty] | 18.01 |  |  |  |  | 0.77
2019 |  |  |  | 4009.33 |  |  | 8576 |  |  |  | 471 | [10 empty] | 96.97 |  |  |  | 97.73 | [5 empty] | 97.17 |  |  | 97.90 |  |  |  | 0.21 |  | 0.20 | [8 empty] | 2.07 |  |  |  |  | 0.76
2020 |  |  |  | 3624.27 |  |  | 7800 |  |  |  | 471 | [10 empty] | 87.66 |  |  |  | 88.53 | [5 empty] | 87.60 |  |  | 88.80 |  |  |  | 0.00 |  | 1.73 | [8 empty] | 9.73 |  |  |  |  | 0.88
2021 |  |  |  | 3454.30 |  |  | 7452 |  |  |  | 471 | [10 empty] | 83.80 |  |  |  | 84.65 | [5 empty] | 83.72 |  |  | 85.07 |  |  |  | 0.02 |  | 1.93 | [8 empty] | 13.42 |  |  |  |  | 0.85
2022 |  |  |  | 3456.36 |  |  | 7454 |  |  |  | 471 | [10 empty] | 83.78 |  |  |  | 84.76 | [5 empty] | 83.77 |  |  | 85.09 |  |  |  | 0.00 |  | 0.32 | [8 empty] | 14.92 |  |  |  |  | 0.99
2023 |  |  |  | 3189.39 |  |  | 7000 |  |  |  | 471 | [10 empty] | 77.31 |  |  |  | 79.59 | [5 empty] | 77.30 |  |  | 79.91 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 20.40 |  |  |  |  | 2.28
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1987 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 71
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1760 | [14 empty] | 1006
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 51
E. |  | Testing of plant systems or components | [39 empty] | 4
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 65
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 7
Subtotal | [22 empty] | 1760 | [14 empty] | 1122 |  |  |  | 82 | [11 empty] | 6
Total | [22 empty] | 1760 | [14 empty] | 1210
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1987 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 5
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 18
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 10
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
33. |  |  | Circulating Water System | [34 empty] | 10
35. |  |  | All other I&C Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 76

## TEMELIN-1
2023 Operating Experience
CZ-23 | [8 empty] | TEMELIN-1 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1987-02-01
Thermal power | [12 empty] | : |  |  | 3120 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2000-12-21
Gross electrical power | [12 empty] | : |  |  | 1082 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2002-06-10
Reference unit power (net) | [12 empty] | : |  |  | 1027 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 23 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.6 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25.7 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.2
| Active core height/length [m] | [13 empty] | : |  |  | 3.63 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7542.49 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.71 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.18 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16 %
Load Factor (LF) | [18 empty] | : | 83.84 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.11 %
Operating Factor (OF) | [18 empty] | : | 83.14 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1477 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 4.72 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 779.32 | 704.62 |  |  |  | 777.43 |  | 170.31 | [8 empty] | 0.00 |  |  | 536.56 | [6 empty] | 761.93 |  | 762.27 |  |  |  | 740.56 |  |  | 773.58 |  |  | 754.93 | [9 empty] | 780.98 |  |  | 7542.49
EAF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 22.52 | [8 empty] | 0.00 |  |  | 71.79 | [6 empty] | 99.54 |  | 99.41 |  |  |  | 99.82 |  |  | 99.93 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.71
UCF [%] |  |  |  |  | 99.99 | 100.00 |  |  |  | 100.00 |  | 22.54 | [8 empty] | 0.00 |  |  | 71.96 | [6 empty] | 99.94 |  | 99.96 |  |  |  | 99.98 |  |  | 99.96 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.82
LF [%] |  |  |  |  | 101.99 | 102.10 |  |  |  | 101.75 |  | 23.03 | [8 empty] | 0.00 |  |  | 72.56 | [6 empty] | 99.72 |  | 99.76 |  |  |  | 100.15 |  |  | 101.24 |  |  | 102.09 | [9 empty] | 102.21 |  |  | 83.84
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 23.33 | [8 empty] | 0.00 |  |  | 74.86 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.14
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.22 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 14.33 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.18
PUF [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 77.46 | [8 empty] | 100.00 |  |  | 13.71 | [6 empty] | 0.06 |  | 0.04 |  |  |  | 0.02 |  |  | 0.04 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.03 | [8 empty] | 0.00 |  |  | 0.17 | [6 empty] | 0.40 |  | 0.56 |  |  |  | 0.15 |  |  | 0.03 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.11
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 146131.16 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.05 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.77 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76.8 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.91 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.26 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.22 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2002 |  |  |  | 5147.87 |  |  | 5961 |  |  |  | 930 | [10 empty] | 76.06 |  |  |  | 76.06 | [5 empty] | 76.96 |  |  | 82.42 |  |  |  | 5.17 |  | 4.15 | [8 empty] | 19.80 |  |  |  |  | 0.00
2003 |  |  |  | 5455.32 |  |  | 5861 |  |  |  | 912 | [10 empty] | 65.30 |  |  |  | 65.30 | [5 empty] | 68.28 |  |  | 66.91 |  |  |  | 4.15 |  | 4.71 | [8 empty] | 29.99 |  |  |  |  | 0.00
2004 |  |  |  | 5715.82 |  |  | 6029 |  |  |  | 950 | [10 empty] | 68.01 |  |  |  | 68.09 | [5 empty] | 68.50 |  |  | 68.64 |  |  |  | 7.98 |  | 6.07 | [8 empty] | 25.84 |  |  |  |  | 0.08
2005 |  |  |  | 5443.97 |  |  | 5846 |  |  |  | 950 | [10 empty] | 66.30 |  |  |  | 66.33 | [5 empty] | 66.35 |  |  | 66.74 |  |  |  | 16.34 |  | 20.25 | [8 empty] | 13.42 |  |  |  |  | 0.03
2006 |  |  |  | 6124.86 |  |  | 6731 |  |  |  | 930 | [10 empty] | 75.68 |  |  |  | 75.69 | [5 empty] | 75.18 |  |  | 76.84 |  |  |  | 4.39 |  | 3.48 | [8 empty] | 20.83 |  |  |  |  | 0.01
2007 |  |  |  | 4901.35 |  |  | 5282 |  |  |  | 963 | [10 empty] | 60.02 |  |  |  | 60.02 | [5 empty] | 59.63 |  |  | 60.30 |  |  |  | 4.05 |  | 8.54 | [8 empty] | 31.44 |  |  |  |  | 0.01
2008 |  |  |  | 4526.45 |  |  | 4745 |  |  |  | 963 | [10 empty] | 53.50 |  |  |  | 53.57 | [5 empty] | 53.51 |  |  | 54.02 |  |  |  | 11.75 |  | 25.06 | [8 empty] | 21.36 |  |  |  |  | 0.07
2009 |  |  |  | 6229.78 |  |  | 6527 |  |  |  | 963 | [10 empty] | 73.81 |  |  |  | 73.88 | [5 empty] | 73.85 |  |  | 74.51 |  |  |  | 4.22 |  | 6.00 | [8 empty] | 20.12 |  |  |  |  | 0.07
2010 |  |  |  | 6305.63 |  |  | 6594 |  |  |  | 963 | [10 empty] | 74.50 |  |  |  | 74.83 | [5 empty] | 74.75 |  |  | 75.27 |  |  |  | 0.65 |  | 6.49 | [8 empty] | 18.68 |  |  |  |  | 0.33
2011 |  |  |  | 6915.59 |  |  | 7205 |  |  |  | 963 | [10 empty] | 81.80 |  |  |  | 81.82 | [5 empty] | 81.98 |  |  | 82.25 |  |  |  | 0.53 |  | 0.44 | [8 empty] | 17.75 |  |  |  |  | 0.02
2012 |  |  |  | 7159.77 |  |  | 7515 |  |  |  | 963 | [10 empty] | 84.68 |  |  |  | 84.99 | [5 empty] | 84.64 |  |  | 85.55 |  |  |  | 1.59 |  | 1.38 | [8 empty] | 13.63 |  |  |  |  | 0.31
2013 |  |  |  | 7018.65 |  |  | 7252 |  |  |  | 1003 | [10 empty] | 82.22 |  |  |  | 82.26 | [5 empty] | 82.06 |  |  | 82.79 |  |  |  | 1.18 |  | 4.07 | [8 empty] | 13.68 |  |  |  |  | 0.04
2014 |  |  |  | 7194.59 |  |  | 7092 |  |  |  | 1023 | [10 empty] | 80.85 |  |  |  | 80.85 | [5 empty] | 81.34 |  |  | 80.96 |  |  |  | 0.02 |  | 0.10 | [8 empty] | 19.04 |  |  |  |  | 0.01
2015 |  |  |  | 7581.24 |  |  | 7400 |  |  |  | 1026 | [10 empty] | 83.88 |  |  |  | 84.22 | [5 empty] | 84.35 |  |  | 84.47 |  |  |  | 3.28 |  | 2.86 | [8 empty] | 12.92 |  |  |  |  | 0.34
2016 |  |  |  | 5786.94 |  |  | 5868 |  |  |  | 1026 | [10 empty] | 64.07 |  |  |  | 66.48 | [5 empty] | 64.21 |  |  | 66.80 |  |  |  | 0.59 |  | 5.72 | [8 empty] | 27.79 |  |  |  |  | 2.42
2017 |  |  |  | 8410.14 |  |  | 8205 |  |  |  | 1026 | [10 empty] | 93.27 |  |  |  | 93.60 | [5 empty] | 93.57 |  |  | 93.66 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 6.37 |  |  |  |  | 0.33
2018 |  |  |  | 7487.60 |  |  | 7321 |  |  |  | 1027 | [10 empty] | 83.11 |  |  |  | 83.34 | [5 empty] | 83.24 |  |  | 83.57 |  |  |  | 0.11 |  | 0.09 | [8 empty] | 16.57 |  |  |  |  | 0.23
2019 |  |  |  | 7169.40 |  |  | 7088 |  |  |  | 1027 | [10 empty] | 79.65 |  |  |  | 80.21 | [5 empty] | 79.69 |  |  | 80.91 |  |  |  | 4.17 |  | 3.49 | [8 empty] | 16.30 |  |  |  |  | 0.56
2020 |  |  |  | 7294.10 |  |  | 7178 |  |  |  | 1027 | [10 empty] | 80.89 |  |  |  | 81.08 | [5 empty] | 80.86 |  |  | 81.72 |  |  |  | 3.08 |  | 2.58 | [8 empty] | 16.34 |  |  |  |  | 0.19
2021 |  |  |  | 7605.99 |  |  | 7403 |  |  |  | 1027 | [10 empty] | 83.92 |  |  |  | 84.02 | [5 empty] | 84.54 |  |  | 84.51 |  |  |  | 0.25 |  | 0.33 | [8 empty] | 15.65 |  |  |  |  | 0.10
2022 |  |  |  | 7733.58 |  |  | 7459 |  |  |  | 1027 | [10 empty] | 84.84 |  |  |  | 84.93 | [5 empty] | 85.96 |  |  | 85.15 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 15.03 |  |  |  |  | 0.10
2023 |  |  |  | 7542.49 |  |  | 7283 |  |  |  | 1027 | [10 empty] | 82.71 |  |  |  | 82.82 | [5 empty] | 83.84 |  |  | 83.14 |  |  |  | 0.02 |  | 1.18 | [8 empty] | 16.00 |  |  |  |  | 0.11
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2002 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 102 | [14 empty] | 401
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1375 | [14 empty] | 1378
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 49
E. |  | Testing of plant systems or components | [35 empty] | 29 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 112
L. |  | Human factor related | [39 empty] | 71
M. |  | Governmental requirements or court decisions | [39 empty] | 31
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 62
Subtotal | [22 empty] | 1375 |  |  |  | 102 | [10 empty] | 1630 |  |  |  | 504
Total | [22 empty] | 1477 | [14 empty] | 2134
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2002 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 59
12. |  |  | Reactor I&C Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [19 empty] | 102 | [14 empty] | 72
16. |  |  | Steam generation systems | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 165
32. |  |  | Feedwater and Main Steam System | [34 empty] | 28
33. |  |  | Circulating Water System | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 49
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 102 | [14 empty] | 400
Highlights (2023)
The Temelín Nuclear Power Plant will enter the final phase of approval of an extension of the outage cycle to 18 months. CEZ put into trial operation the third longest hot water piping in Czechia, connecting the Temelín Nuclear Power Plant and the regional city of Ceské Budejovice; the expected annual supply of 750 TJ of emission-free heat corresponds to approximately one-third of the city’s heat consumption and should be available for at least 20 years.

## TEMELIN-2
2023 Operating Experience
CZ-24 | [8 empty] | TEMELIN-2 | [26 empty] | CZECH REPUBLIC
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Owner | [7 empty] | : | CEZ (CZECH POWER Co., CEZ a.s.)
Reactor Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1987-02-01
Thermal power | [12 empty] | : |  |  | 3120 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2002-12-29
Gross electrical power | [12 empty] | : |  |  | 1082 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2003-04-18
Reference unit power (net) | [12 empty] | : |  |  | 1029 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 21 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 318
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.46
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.6 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25.7 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.2
| Active core height/length [m] | [13 empty] | : |  |  | 3.63 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling Towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7736.61 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.36 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.93 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.17 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.84 %
Load Factor (LF) | [18 empty] | : | 85.83 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.05 %
Operating Factor (OF) | [18 empty] | : | 85.32 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1286 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 58.27 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 779.81 | 704.76 |  |  |  | 778.22 |  | 752.91 | [8 empty] | 774.75 |  |  | 689.80 | [6 empty] | 745.43 |  | 400.20 |  |  |  | 0.00 |  |  | 587.04 |  |  | 749.70 | [9 empty] | 773.99 |  |  | 7736.61
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.95 |  |  | 93.05 | [6 empty] | 97.26 |  | 52.55 |  |  |  | 0.00 |  |  | 76.33 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.93
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.95 |  |  | 93.21 | [6 empty] | 97.57 |  | 52.70 |  |  |  | 0.00 |  |  | 76.33 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.98
LF [%] |  |  |  |  | 101.86 | 101.92 |  |  |  | 101.65 |  | 101.62 | [8 empty] | 101.20 |  |  | 93.11 | [6 empty] | 97.37 |  | 52.27 |  |  |  | 0.00 |  |  | 76.68 |  |  | 101.19 | [9 empty] | 101.10 |  |  | 85.83
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 94.17 | [6 empty] | 98.25 |  | 53.49 |  |  |  | 0.00 |  |  | 77.82 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.32
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  | 6.76 | [6 empty] | 2.43 |  | 8.31 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.36
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.05 |  |  | 6.76 | [6 empty] | 2.43 |  | 4.78 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.17
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.04 | [6 empty] | 0.00 |  | 42.52 |  |  |  | 100.00 |  |  | 23.67 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.84
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.16 | [6 empty] | 0.30 |  | 0.15 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 142140.68 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.44 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.72 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.74 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.99 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.19 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.16 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2003 |  |  |  | 6033.03 |  |  | 6934 |  |  |  | 930 | [10 empty] | 84.23 |  |  |  | 84.23 | [5 empty] | 86.59 |  |  | 86.52 |  |  |  | 15.60 |  | 15.57 | [8 empty] | 0.21 |  |  |  |  | 0.00
2004 |  |  |  | 6340.09 |  |  | 6678 |  |  |  | 950 | [10 empty] | 75.22 |  |  |  | 75.22 | [5 empty] | 75.98 |  |  | 76.02 |  |  |  | 8.49 |  | 6.98 | [8 empty] | 17.80 |  |  |  |  | 0.00
2005 |  |  |  | 4941.36 |  |  | 6135 |  |  |  | 780 | [10 empty] | 65.10 |  |  |  | 65.25 | [5 empty] | 65.27 |  |  | 70.03 |  |  |  | 6.34 |  | 10.21 | [8 empty] | 24.54 |  |  |  |  | 0.15
2006 |  |  |  | 5251.85 |  |  | 5765 |  |  |  | 930 | [10 empty] | 65.28 |  |  |  | 65.82 | [5 empty] | 65.36 |  |  | 65.81 |  |  |  | 3.01 |  | 8.85 | [8 empty] | 25.33 |  |  |  |  | 0.54
2007 |  |  |  | 6745.10 |  |  | 7051 |  |  |  | 963 | [10 empty] | 79.93 |  |  |  | 80.05 | [5 empty] | 80.50 |  |  | 80.49 |  |  |  | 0.85 |  | 2.44 | [8 empty] | 17.50 |  |  |  |  | 0.12
2008 |  |  |  | 6978.75 |  |  | 7420 |  |  |  | 963 | [10 empty] | 82.65 |  |  |  | 83.23 | [5 empty] | 82.50 |  |  | 84.47 |  |  |  | 3.05 |  | 2.62 | [8 empty] | 14.15 |  |  |  |  | 0.58
2009 |  |  |  | 6363.18 |  |  | 6756 |  |  |  | 963 | [10 empty] | 75.39 |  |  |  | 76.80 | [5 empty] | 75.43 |  |  | 77.12 |  |  |  | 0.25 |  | 0.19 | [8 empty] | 23.00 |  |  |  |  | 1.41
2010 |  |  |  | 6847.34 |  |  | 7135 |  |  |  | 963 | [10 empty] | 80.95 |  |  |  | 81.10 | [5 empty] | 81.18 |  |  | 81.46 |  |  |  | 1.55 |  | 2.78 | [8 empty] | 16.12 |  |  |  |  | 0.15
2011 |  |  |  | 6311.62 |  |  | 6589 |  |  |  | 963 | [10 empty] | 74.77 |  |  |  | 74.85 | [5 empty] | 74.82 |  |  | 75.22 |  |  |  | 3.32 |  | 9.69 | [8 empty] | 15.46 |  |  |  |  | 0.08
2012 |  |  |  | 7349.91 |  |  | 7656 |  |  |  | 963 | [10 empty] | 86.84 |  |  |  | 86.91 | [5 empty] | 86.89 |  |  | 87.16 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 13.05 |  |  |  |  | 0.06
2013 |  |  |  | 7246.82 |  |  | 7448 |  |  |  | 1003 | [10 empty] | 84.48 |  |  |  | 84.79 | [5 empty] | 84.43 |  |  | 85.02 |  |  |  | 1.06 |  | 1.92 | [8 empty] | 13.29 |  |  |  |  | 0.31
2014 |  |  |  | 6989.25 |  |  | 6980 |  |  |  | 1003 | [10 empty] | 79.32 |  |  |  | 79.33 | [5 empty] | 79.55 |  |  | 79.68 |  |  |  | 8.27 |  | 7.15 | [8 empty] | 13.52 |  |  |  |  | 0.01
2015 |  |  |  | 5926.47 |  |  | 5813 |  |  |  | 1026 | [10 empty] | 66.23 |  |  |  | 66.24 | [5 empty] | 66.84 |  |  | 66.36 |  |  |  | 7.35 |  | 17.25 | [8 empty] | 16.51 |  |  |  |  | 0.00
2016 |  |  |  | 5730.12 |  |  | 5617 |  |  |  | 1026 | [10 empty] | 62.87 |  |  |  | 62.87 | [5 empty] | 63.58 |  |  | 63.95 |  |  |  | 14.72 |  | 14.93 | [8 empty] | 22.20 |  |  |  |  | 0.00
2017 |  |  |  | 7252.35 |  |  | 7024 |  |  |  | 1026 | [10 empty] | 79.85 |  |  |  | 79.87 | [5 empty] | 80.69 |  |  | 80.18 |  |  |  | 0.08 |  | 0.06 | [8 empty] | 20.07 |  |  |  |  | 0.01
2018 |  |  |  | 7402.41 |  |  | 7208 |  |  |  | 1027 | [10 empty] | 81.65 |  |  |  | 82.00 | [5 empty] | 82.34 |  |  | 82.29 |  |  |  | 1.30 |  | 1.37 | [8 empty] | 16.63 |  |  |  |  | 0.35
2019 |  |  |  | 7813.14 |  |  | 7555 |  |  |  | 1027 | [10 empty] | 85.98 |  |  |  | 86.04 | [5 empty] | 86.85 |  |  | 86.24 |  |  |  | 0.16 |  | 0.13 | [8 empty] | 13.82 |  |  |  |  | 0.06
2020 |  |  |  | 7660.96 |  |  | 7398 |  |  |  | 1029 | [10 empty] | 83.98 |  |  |  | 84.03 | [5 empty] | 84.89 |  |  | 84.22 |  |  |  | 0.02 |  | 0.19 | [8 empty] | 15.78 |  |  |  |  | 0.05
2021 |  |  |  | 7477.64 |  |  | 7198 |  |  |  | 1029 | [10 empty] | 84.18 |  |  |  | 84.19 | [5 empty] | 82.96 |  |  | 82.17 |  |  |  | 0.34 |  | 0.29 | [8 empty] | 15.52 |  |  |  |  | 0.02
2022 |  |  |  | 7751.47 |  |  | 7455 |  |  |  | 1029 | [10 empty] | 84.84 |  |  |  | 84.86 | [5 empty] | 85.99 |  |  | 85.10 |  |  |  | 0.63 |  | 0.54 | [8 empty] | 14.60 |  |  |  |  | 0.03
2023 |  |  |  | 7736.61 |  |  | 7474 |  |  |  | 1029 | [10 empty] | 84.93 |  |  |  | 84.98 | [5 empty] | 85.83 |  |  | 85.32 |  |  |  | 1.36 |  | 1.17 | [8 empty] | 13.84 |  |  |  |  | 0.05
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2003 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 86 | [14 empty] | 378
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1200 | [14 empty] | 1287
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 44
E. |  | Testing of plant systems or components | [35 empty] | 19 |  |  |  | 3
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 93
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 11
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 45
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Subtotal | [22 empty] | 1200 |  |  |  | 86 | [10 empty] | 1443 |  |  |  | 426 | [11 empty] | 12
Total | [22 empty] | 1286 | [14 empty] | 1881
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2003 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 80
12. |  |  | Reactor I&C Systems | [34 empty] | 9
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 14
15. |  |  | Reactor Cooling Systems | [34 empty] | 17
16. |  |  | Steam generation systems | [34 empty] | 66
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [19 empty] | 86 | [14 empty] | 98
32. |  |  | Feedwater and Main Steam System | [34 empty] | 21
33. |  |  | Circulating Water System | [34 empty] | 7
35. |  |  | All other I&C Systems | [34 empty] | 28
41. |  |  | Main Generator Systems | [34 empty] | 30
42. |  |  | Electrical Power Supply Systems | [34 empty] | 25
Total | [22 empty] | 86 | [14 empty] | 397