## LOVIISA-1
2023 Operating Experience
FI-1 | [8 empty] | LOVIISA-1 | [26 empty] | FINLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FORTUMPH (FORTUM POWER AND HEAT OY (former IVO))
Owner | [7 empty] | : | FORTUMPH (FORTUM POWER AND HEAT OY (former IVO))
Reactor Supplier | [7 empty] | : | AEE (ATOMENERGOEXPORT)
Turbine Supplier | [7 empty] | : | AEE (ATOMENERGOEXPORT)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-05-01
Thermal power | [12 empty] | : |  |  | 1500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1977-02-08
Gross electrical power | [12 empty] | : |  |  | 531 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-05-09
Reference unit power (net) | [12 empty] | : |  |  | 507 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 46 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.25
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 301
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.07
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.73 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.42 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 313 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3987.98 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.34 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.47 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.79 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.65 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.56 %
Load Factor (LF) | [18 empty] | : | 89.79 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.18 %
Operating Factor (OF) | [18 empty] | : | 93.61 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 560 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 374.87 | 338.54 |  |  |  | 374.50 |  | 362.24 | [8 empty] | 365.97 |  |  | 356.32 | [6 empty] | 365.57 |  | 340.27 |  |  |  | 75.40 |  |  | 318.62 |  |  | 341.23 | [9 empty] | 374.45 |  |  | 3987.99
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 98.81 |  |  | 97.61 | [6 empty] | 97.50 |  | 91.04 |  |  |  | 20.65 |  |  | 85.01 |  |  | 94.43 | [9 empty] | 99.92 |  |  | 90.47
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 95.86 |  |  |  | 22.17 |  |  | 86.57 |  |  | 94.43 | [9 empty] | 99.92 |  |  | 91.65
LF [%] |  |  |  |  | 99.38 | 99.36 |  |  |  | 99.42 |  | 99.23 | [8 empty] | 97.02 |  |  | 97.61 | [6 empty] | 96.91 |  | 90.21 |  |  |  | 20.65 |  |  | 84.35 |  |  | 93.48 | [9 empty] | 99.27 |  |  | 89.79
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 28.47 |  |  | 97.72 |  |  | 96.11 | [9 empty] | 100.00 |  |  | 93.61
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 4.14 |  |  |  | 21.67 |  |  | 10.64 |  |  | 5.57 | [9 empty] | 0.08 |  |  | 2.34
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 4.14 |  |  |  | 10.99 |  |  | 12.59 |  |  | 5.57 | [9 empty] | 0.08 |  |  | 2.79
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 66.83 |  |  | 0.85 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.56
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.19 |  |  | 2.39 | [6 empty] | 2.50 |  | 4.82 |  |  |  | 1.52 |  |  | 1.56 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.18
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 169621.16 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.39 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.12 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.62 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.76 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.62 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.87 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.64 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.92 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 2505.50 |  |  | 7192 |  |  |  | 431 | [10 empty] | 83.79 |  |  |  | 83.79 | [5 empty] | 83.79 |  |  | 95.09 |  |  |  | 12.65 |  | 12.13 | [8 empty] | 4.08 |  |  |  |  | 0.00
1978 |  |  |  | 2975.80 |  |  | 7531 |  |  |  | 430 | [10 empty] | 78.93 |  |  |  | 78.93 | [5 empty] | 79.00 |  |  | 85.97 |  |  |  | 9.27 |  | 8.06 | [8 empty] | 13.01 |  |  |  |  | 0.00
1979 |  |  |  | 2901.70 |  |  | 7404 |  |  |  | 405 | [10 empty] | 81.76 |  |  |  | 81.76 | [5 empty] | 81.79 |  |  | 84.52 |  |  |  | 9.09 |  | 8.17 | [8 empty] | 10.07 |  |  |  |  | 0.00
1980 |  |  |  | 1407.80 |  |  | 3482 |  |  |  | 445 | [10 empty] | 36.65 |  |  |  | 36.65 | [5 empty] | 36.02 |  |  | 39.64 |  |  |  | 55.36 |  | 45.45 | [8 empty] | 17.90 |  |  |  |  | 0.00
1981 |  |  |  | 3105.10 |  |  | 7642 |  |  |  | 440 | [10 empty] | 81.94 |  |  |  | 81.94 | [5 empty] | 80.56 |  |  | 87.24 |  |  |  | 2.74 |  | 2.31 | [8 empty] | 15.75 |  |  |  |  | 0.00
1982 |  |  |  | 3245.40 |  |  | 7576 |  |  |  | 440 | [10 empty] | 84.19 |  |  |  | 84.19 | [5 empty] | 84.20 |  |  | 86.48 |  |  |  | 4.46 |  | 3.93 | [8 empty] | 11.88 |  |  |  |  | 0.00
1983 |  |  |  | 3337.40 |  |  | 7982 |  |  |  | 445 | [10 empty] | 86.68 |  |  |  | 86.68 | [5 empty] | 85.61 |  |  | 91.12 |  |  |  | 3.01 |  | 2.69 | [8 empty] | 10.63 |  |  |  |  | 0.00
1984 |  |  |  | 3343.86 |  |  | 7653 |  |  |  | 445 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 85.55 |  |  | 87.12 |  |  |  | 0.31 |  | 0.27 | [8 empty] | 13.94 |  |  |  |  | 0.00
1985 |  |  |  | 3599.97 |  |  | 8248 |  |  |  | 440 | [10 empty] | 92.54 |  |  |  | 92.54 | [5 empty] | 93.40 |  |  | 94.16 |  |  |  | 0.45 |  | 0.42 | [8 empty] | 7.05 |  |  |  |  | 0.00
1986 |  |  |  | 3522.37 |  |  | 8093 |  |  |  | 445 | [10 empty] | 91.10 |  |  |  | 91.10 | [5 empty] | 90.36 |  |  | 92.39 |  |  |  | 2.67 |  | 2.49 | [8 empty] | 6.40 |  |  |  |  | 0.00
1987 |  |  |  | 3600.36 |  |  | 8257 |  |  |  | 445 | [10 empty] | 94.55 |  |  |  | 94.55 | [5 empty] | 92.36 |  |  | 94.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.45 |  |  |  |  | 0.00
1988 |  |  |  | 3354.63 |  |  | 7678 |  |  |  | 445 | [10 empty] | 87.03 |  |  |  | 87.03 | [5 empty] | 85.82 |  |  | 87.41 |  |  |  | 1.21 |  | 1.07 | [8 empty] | 11.90 |  |  |  |  | 0.00
1989 |  |  |  | 3575.75 |  |  | 8183 |  |  |  | 445 | [10 empty] | 92.61 |  |  |  | 92.80 | [5 empty] | 91.73 |  |  | 93.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.20 |  |  |  |  | 0.19
1990 |  |  |  | 3271.13 |  |  | 7605 |  |  |  | 445 | [10 empty] | 85.48 |  |  |  | 85.50 | [5 empty] | 83.91 |  |  | 86.82 |  |  |  | 4.46 |  | 3.99 | [8 empty] | 10.50 |  |  |  |  | 0.03
1991 |  |  |  | 3360.90 |  |  | 7927 |  |  |  | 445 | [10 empty] | 88.58 |  |  |  | 88.84 | [5 empty] | 86.22 |  |  | 90.49 |  |  |  | 2.52 |  | 2.29 | [8 empty] | 8.86 |  |  |  |  | 0.26
1992 |  |  |  | 3108.41 |  |  | 7186 |  |  |  | 445 | [10 empty] | 80.19 |  |  |  | 80.30 | [5 empty] | 79.52 |  |  | 81.81 |  |  |  | 0.44 |  | 0.35 | [8 empty] | 19.35 |  |  |  |  | 0.11
1993 |  |  |  | 3443.16 |  |  | 8052 |  |  |  | 445 | [10 empty] | 89.47 |  |  |  | 89.49 | [5 empty] | 88.40 |  |  | 91.99 |  |  |  | 1.77 |  | 1.61 | [8 empty] | 8.91 |  |  |  |  | 0.02
1994 |  |  |  | 3497.57 |  |  | 8017 |  |  |  | 445 | [10 empty] | 90.70 |  |  |  | 90.76 | [5 empty] | 89.72 |  |  | 91.52 |  |  |  | 2.31 |  | 2.15 | [8 empty] | 7.09 |  |  |  |  | 0.06
1995 |  |  |  | 3389.06 |  |  | 7834 |  |  |  | 445 | [10 empty] | 87.66 |  |  |  | 88.50 | [5 empty] | 86.94 |  |  | 89.43 |  |  |  | 6.50 |  | 6.16 | [8 empty] | 5.34 |  |  |  |  | 0.84
1996 |  |  |  | 3203.49 |  |  | 7281 |  |  |  | 445 | [10 empty] | 82.04 |  |  |  | 82.51 | [5 empty] | 81.95 |  |  | 82.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.49 |  |  |  |  | 0.47
1997 |  |  |  | 3794.83 |  |  | 8309 |  |  |  | 445 | [10 empty] | 93.02 |  |  |  | 93.87 | [5 empty] | 97.35 |  |  | 94.85 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 6.11 |  |  |  |  | 0.86
1998 |  |  |  | 3852.35 |  |  | 8234 |  |  |  | 488 | [10 empty] | 91.35 |  |  |  | 93.39 | [5 empty] | 90.12 |  |  | 94.00 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 6.56 |  |  |  |  | 2.04
1999 |  |  |  | 3883.28 |  |  | 8304 |  |  |  | 488 | [10 empty] | 91.63 |  |  |  | 92.37 | [5 empty] | 90.84 |  |  | 94.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.63 |  |  |  |  | 0.74
2000 |  |  |  | 3618.00 |  |  | 7720 |  |  |  | 488 | [10 empty] | 84.91 |  |  |  | 86.50 | [5 empty] | 84.40 |  |  | 87.89 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 13.45 |  |  |  |  | 1.59
2001 |  |  |  | 3920.99 |  |  | 8233 |  |  |  | 488 | [10 empty] | 92.38 |  |  |  | 93.41 | [5 empty] | 91.72 |  |  | 93.98 |  |  |  | 0.67 |  | 0.63 | [8 empty] | 5.97 |  |  |  |  | 1.02
2002 |  |  |  | 3790.07 |  |  | 8095 |  |  |  | 488 | [10 empty] | 89.27 |  |  |  | 91.40 | [5 empty] | 88.66 |  |  | 92.41 |  |  |  | 0.72 |  | 0.66 | [8 empty] | 7.94 |  |  |  |  | 2.13
2003 |  |  |  | 3938.98 |  |  | 8194 |  |  |  | 488 | [10 empty] | 92.40 |  |  |  | 93.22 | [5 empty] | 92.14 |  |  | 93.54 |  |  |  | 0.16 |  | 2.01 | [8 empty] | 4.77 |  |  |  |  | 0.83
2004 |  |  |  | 3715.03 |  |  | 7647 |  |  |  | 488 | [10 empty] | 86.51 |  |  |  | 86.91 | [5 empty] | 86.66 |  |  | 87.05 |  |  |  | 0.24 |  | 1.55 | [8 empty] | 11.54 |  |  |  |  | 0.40
2005 |  |  |  | 4062.43 |  |  | 8351 |  |  |  | 488 | [10 empty] | 94.61 |  |  |  | 95.02 | [5 empty] | 95.03 |  |  | 95.33 |  |  |  | 0.28 |  | 0.27 | [8 empty] | 4.71 |  |  |  |  | 0.41
2006 |  |  |  | 3964.84 |  |  | 8138 |  |  |  | 488 | [10 empty] | 92.08 |  |  |  | 92.63 | [5 empty] | 92.74 |  |  | 92.89 |  |  |  | 0.18 |  | 0.95 | [8 empty] | 6.42 |  |  |  |  | 0.55
2007 |  |  |  | 4028.12 |  |  | 8285 |  |  |  | 488 | [10 empty] | 93.49 |  |  |  | 94.00 | [5 empty] | 94.23 |  |  | 94.58 |  |  |  | 0.32 |  | 1.19 | [8 empty] | 4.82 |  |  |  |  | 0.50
2008 |  |  |  | 3671.84 |  |  | 7571 |  |  |  | 488 | [10 empty] | 84.51 |  |  |  | 84.87 | [5 empty] | 85.66 |  |  | 86.19 |  |  |  | 0.09 |  | 3.25 | [8 empty] | 11.88 |  |  |  |  | 0.36
2009 |  |  |  | 4084.91 |  |  | 8345 |  |  |  | 488 | [10 empty] | 94.80 |  |  |  | 94.83 | [5 empty] | 95.56 |  |  | 95.26 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 5.14 |  |  |  |  | 0.03
2010 |  |  |  | 3955.59 |  |  | 8123 |  |  |  | 488 | [10 empty] | 91.95 |  |  |  | 92.33 | [5 empty] | 92.53 |  |  | 92.73 |  |  |  | 0.53 |  | 0.61 | [8 empty] | 7.07 |  |  |  |  | 0.38
2011 |  |  |  | 4026.87 |  |  | 8295 |  |  |  | 488 | [10 empty] | 93.82 |  |  |  | 94.32 | [5 empty] | 94.20 |  |  | 94.69 |  |  |  | 0.80 |  | 0.76 | [8 empty] | 4.92 |  |  |  |  | 0.51
2012 |  |  |  | 3653.04 |  |  | 7473 |  |  |  | 496 | [10 empty] | 84.08 |  |  |  | 84.86 | [5 empty] | 83.86 |  |  | 85.08 |  |  |  | 0.00 |  | 3.32 | [8 empty] | 11.82 |  |  |  |  | 0.78
2013 |  |  |  | 4000.24 |  |  | 8219 |  |  |  | 496 | [10 empty] | 92.00 |  |  |  | 93.02 | [5 empty] | 92.07 |  |  | 93.82 |  |  |  | 1.33 |  | 1.25 | [8 empty] | 5.73 |  |  |  |  | 1.02
2014 |  |  |  | 4010.58 |  |  | 8262 |  |  |  | 496 | [10 empty] | 92.60 |  |  |  | 93.38 | [5 empty] | 92.30 |  |  | 94.32 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 6.57 |  |  |  |  | 0.78
2015 |  |  |  | 4025.96 |  |  | 8248 |  |  |  | 496 | [10 empty] | 92.68 |  |  |  | 93.76 | [5 empty] | 92.66 |  |  | 94.16 |  |  |  | 0.07 |  | 0.99 | [8 empty] | 5.25 |  |  |  |  | 1.08
2016 |  |  |  | 3862.81 |  |  | 7873 |  |  |  | 502 | [10 empty] | 88.45 |  |  |  | 89.43 | [5 empty] | 88.48 |  |  | 89.63 |  |  |  | 0.07 |  | 1.58 | [8 empty] | 8.99 |  |  |  |  | 0.98
2017 |  |  |  | 4087.37 |  |  | 8246 |  |  |  | 507 | [10 empty] | 92.71 |  |  |  | 93.85 | [5 empty] | 92.71 |  |  | 94.13 |  |  |  | 0.15 |  | 0.55 | [8 empty] | 5.59 |  |  |  |  | 1.15
2018 |  |  |  | 4021.00 |  |  | 8124 |  |  |  | 507 | [10 empty] | 90.64 |  |  |  | 92.47 | [5 empty] | 90.54 |  |  | 92.74 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 7.43 |  |  |  |  | 1.82
2019 |  |  |  | 4109.79 |  |  | 8270 |  |  |  | 507 | [10 empty] | 92.90 |  |  |  | 94.10 | [5 empty] | 92.54 |  |  | 94.41 |  |  |  | 0.05 |  | 0.71 | [8 empty] | 5.19 |  |  |  |  | 1.20
2020 |  |  |  | 3709.11 |  |  | 7483 |  |  |  | 507 | [10 empty] | 83.47 |  |  |  | 84.86 | [5 empty] | 83.29 |  |  | 85.19 |  |  |  | 0.08 |  | 2.57 | [8 empty] | 12.56 |  |  |  |  | 1.39
2021 |  |  |  | 4137.39 |  |  | 8325 |  |  |  | 507 | [10 empty] | 93.40 |  |  |  | 94.66 | [5 empty] | 93.16 |  |  | 95.03 |  |  |  | 0.13 |  | 0.17 | [8 empty] | 5.17 |  |  |  |  | 1.26
2022 |  |  |  | 3995.96 |  |  | 8060 |  |  |  | 507 | [10 empty] | 90.22 |  |  |  | 91.80 | [5 empty] | 89.98 |  |  | 92.02 |  |  |  | 0.01 |  | 1.96 | [8 empty] | 6.24 |  |  |  |  | 1.58
2023 |  |  |  | 3987.99 |  |  | 8200 |  |  |  | 507 | [10 empty] | 90.47 |  |  |  | 91.65 | [5 empty] | 89.79 |  |  | 93.61 |  |  |  | 2.34 |  | 2.79 | [8 empty] | 5.56 |  |  |  |  | 1.18
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1977 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 51 | [14 empty] | 167
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 480 | [14 empty] | 690 |  |  |  | 7
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 14
E. |  | Testing of plant systems or components | [35 empty] | 2
L. |  | Human factor related | [39 empty] | 1
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [51 empty] | 4
Z. |  | Other | [24 empty] | 52 | [14 empty] | 13
Subtotal | [22 empty] | 480 |  |  |  | 103 | [10 empty] | 706 |  |  |  | 188 | [11 empty] | 4
Total | [22 empty] | 583 | [14 empty] | 898
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1977 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 11
14. |  |  | Safety Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 122
16. |  |  | Steam generation systems | [19 empty] | 51 | [14 empty] | 6
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 12
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 51 | [14 empty] | 167

## LOVIISA-2
2023 Operating Experience
FI-2 | [8 empty] | LOVIISA-2 | [26 empty] | FINLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FORTUMPH (FORTUM POWER AND HEAT OY (former IVO))
Owner | [7 empty] | : | FORTUMPH (FORTUM POWER AND HEAT OY (former IVO))
Reactor Supplier | [7 empty] | : | AEE (ATOMENERGOEXPORT)
Turbine Supplier | [7 empty] | : | AEE (ATOMENERGOEXPORT)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-08-01
Thermal power | [12 empty] | : |  |  | 1500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-11-04
Gross electrical power | [12 empty] | : |  |  | 531 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-01-05
Reference unit power (net) | [12 empty] | : |  |  | 507 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.25
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.07
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.73 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.42 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15.75
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 313 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.7 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 4100.21 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.89 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.28 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.82 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.91 %
Load Factor (LF) | [18 empty] | : | 92.32 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.93 %
Operating Factor (OF) | [18 empty] | : | 95.06 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 433 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 377.49 | 340.73 |  |  |  | 376.91 |  | 364.69 | [8 empty] | 367.57 |  |  | 358.70 | [6 empty] | 368.55 |  | 215.83 |  |  |  | 227.01 |  |  | 363.02 |  |  | 362.72 | [9 empty] | 376.99 |  |  | 4100.21
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.51 |  |  | 98.26 | [6 empty] | 98.05 |  | 57.22 |  |  |  | 63.51 |  |  | 98.45 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.89
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 59.77 |  |  |  | 66.32 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.82
LF [%] |  |  |  |  | 100.07 | 100.01 |  |  |  | 100.06 |  | 99.90 | [8 empty] | 97.45 |  |  | 98.26 | [6 empty] | 97.70 |  | 57.22 |  |  |  | 62.19 |  |  | 96.11 |  |  | 99.36 | [9 empty] | 99.94 |  |  | 92.32
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 63.04 |  |  |  | 78.06 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.06
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.07 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 3.38 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.28
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 40.23 |  |  |  | 30.30 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5.91
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.49 |  |  | 1.74 | [6 empty] | 1.95 |  | 2.55 |  |  |  | 2.81 |  |  | 1.55 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.93
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 160281.45 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.33 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.52 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.35 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.13 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.45 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.8 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 91.3 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 2714.20 |  |  | 7062 |  |  |  | 440 | [10 empty] | 72.18 |  |  |  | 72.18 | [5 empty] | 70.42 |  |  | 80.62 |  |  |  | 9.96 |  | 7.99 | [8 empty] | 19.83 |  |  |  |  | 0.00
1982 |  |  |  | 2997.40 |  |  | 7046 |  |  |  | 440 | [10 empty] | 78.00 |  |  |  | 78.00 | [5 empty] | 77.77 |  |  | 80.43 |  |  |  | 0.30 |  | 0.23 | [8 empty] | 21.76 |  |  |  |  | 0.00
1983 |  |  |  | 3474.50 |  |  | 8063 |  |  |  | 445 | [10 empty] | 90.09 |  |  |  | 90.09 | [5 empty] | 89.13 |  |  | 92.04 |  |  |  | 0.72 |  | 0.66 | [8 empty] | 9.25 |  |  |  |  | 0.00
1984 |  |  |  | 3608.63 |  |  | 8251 |  |  |  | 445 | [10 empty] | 92.57 |  |  |  | 92.57 | [5 empty] | 92.32 |  |  | 93.93 |  |  |  | 0.93 |  | 0.87 | [8 empty] | 6.56 |  |  |  |  | 0.00
1985 |  |  |  | 3549.84 |  |  | 8162 |  |  |  | 440 | [10 empty] | 92.15 |  |  |  | 92.15 | [5 empty] | 92.10 |  |  | 93.17 |  |  |  | 1.79 |  | 1.68 | [8 empty] | 6.17 |  |  |  |  | 0.00
1986 |  |  |  | 3174.87 |  |  | 7273 |  |  |  | 445 | [10 empty] | 81.46 |  |  |  | 81.46 | [5 empty] | 81.44 |  |  | 83.03 |  |  |  | 3.74 |  | 3.17 | [8 empty] | 15.37 |  |  |  |  | 0.00
1987 |  |  |  | 3572.08 |  |  | 8242 |  |  |  | 445 | [10 empty] | 93.37 |  |  |  | 93.37 | [5 empty] | 91.63 |  |  | 94.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.63 |  |  |  |  | 0.00
1988 |  |  |  | 3602.27 |  |  | 8305 |  |  |  | 445 | [10 empty] | 94.69 |  |  |  | 94.69 | [5 empty] | 92.16 |  |  | 94.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.31 |  |  |  |  | 0.00
1989 |  |  |  | 3550.96 |  |  | 8128 |  |  |  | 445 | [10 empty] | 91.69 |  |  |  | 91.76 | [5 empty] | 91.09 |  |  | 92.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.24 |  |  |  |  | 0.07
1990 |  |  |  | 3251.05 |  |  | 7584 |  |  |  | 445 | [10 empty] | 85.28 |  |  |  | 85.32 | [5 empty] | 83.40 |  |  | 86.58 |  |  |  | 4.24 |  | 3.78 | [8 empty] | 10.90 |  |  |  |  | 0.04
1991 |  |  |  | 3442.19 |  |  | 7941 |  |  |  | 445 | [10 empty] | 88.98 |  |  |  | 89.85 | [5 empty] | 88.30 |  |  | 90.65 |  |  |  | 0.25 |  | 0.22 | [8 empty] | 9.93 |  |  |  |  | 0.87
1992 |  |  |  | 3468.45 |  |  | 7931 |  |  |  | 445 | [10 empty] | 89.10 |  |  |  | 89.53 | [5 empty] | 88.73 |  |  | 90.29 |  |  |  | 0.66 |  | 0.60 | [8 empty] | 9.88 |  |  |  |  | 0.43
1993 |  |  |  | 3550.79 |  |  | 8050 |  |  |  | 445 | [10 empty] | 91.25 |  |  |  | 91.29 | [5 empty] | 91.16 |  |  | 91.97 |  |  |  | 2.29 |  | 2.14 | [8 empty] | 6.57 |  |  |  |  | 0.04
1994 |  |  |  | 3124.71 |  |  | 7170 |  |  |  | 445 | [10 empty] | 80.50 |  |  |  | 81.20 | [5 empty] | 80.16 |  |  | 81.85 |  |  |  | 1.87 |  | 1.55 | [8 empty] | 17.25 |  |  |  |  | 0.70
1995 |  |  |  | 3060.25 |  |  | 7064 |  |  |  | 445 | [10 empty] | 77.57 |  |  |  | 78.41 | [5 empty] | 78.50 |  |  | 80.64 |  |  |  | 17.16 |  | 16.25 | [8 empty] | 5.34 |  |  |  |  | 0.84
1996 |  |  |  | 3621.33 |  |  | 8227 |  |  |  | 445 | [10 empty] | 92.73 |  |  |  | 93.08 | [5 empty] | 92.64 |  |  | 93.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.92 |  |  |  |  | 0.35
1997 |  |  |  | 3804.70 |  |  | 8267 |  |  |  | 445 | [10 empty] | 91.96 |  |  |  | 92.87 | [5 empty] | 97.60 |  |  | 94.37 |  |  |  | 2.30 |  | 2.19 | [8 empty] | 4.94 |  |  |  |  | 0.91
1998 |  |  |  | 3687.90 |  |  | 7892 |  |  |  | 488 | [10 empty] | 86.41 |  |  |  | 88.55 | [5 empty] | 86.27 |  |  | 90.09 |  |  |  | 0.70 |  | 0.63 | [8 empty] | 10.82 |  |  |  |  | 2.14
1999 |  |  |  | 3974.34 |  |  | 8281 |  |  |  | 488 | [10 empty] | 93.53 |  |  |  | 94.19 | [5 empty] | 92.97 |  |  | 94.53 |  |  |  | 0.14 |  | 0.13 | [8 empty] | 5.69 |  |  |  |  | 0.65
2000 |  |  |  | 3885.10 |  |  | 8314 |  |  |  | 488 | [10 empty] | 90.90 |  |  |  | 94.11 | [5 empty] | 90.63 |  |  | 94.65 |  |  |  | 0.25 |  | 0.23 | [8 empty] | 5.66 |  |  |  |  | 3.21
2001 |  |  |  | 3781.06 |  |  | 8149 |  |  |  | 488 | [10 empty] | 89.58 |  |  |  | 92.30 | [5 empty] | 88.45 |  |  | 93.03 |  |  |  | 1.25 |  | 1.17 | [8 empty] | 6.53 |  |  |  |  | 2.72
2002 |  |  |  | 3498.66 |  |  | 7463 |  |  |  | 488 | [10 empty] | 82.56 |  |  |  | 84.51 | [5 empty] | 81.84 |  |  | 85.19 |  |  |  | 1.54 |  | 4.75 | [8 empty] | 10.74 |  |  |  |  | 1.94
2003 |  |  |  | 3736.65 |  |  | 8358 |  |  |  | 488 | [10 empty] | 90.00 |  |  |  | 90.14 | [5 empty] | 87.41 |  |  | 95.41 |  |  |  | 0.08 |  | 0.20 | [8 empty] | 9.66 |  |  |  |  | 0.14
2004 |  |  |  | 4009.18 |  |  | 8231 |  |  |  | 488 | [10 empty] | 93.11 |  |  |  | 93.59 | [5 empty] | 93.53 |  |  | 93.70 |  |  |  | 0.25 |  | 0.23 | [8 empty] | 6.18 |  |  |  |  | 0.47
2005 |  |  |  | 4076.12 |  |  | 8376 |  |  |  | 488 | [10 empty] | 94.55 |  |  |  | 95.36 | [5 empty] | 95.35 |  |  | 95.62 |  |  |  | 0.16 |  | 0.15 | [8 empty] | 4.49 |  |  |  |  | 0.81
2006 |  |  |  | 3766.55 |  |  | 7863 |  |  |  | 488 | [10 empty] | 87.47 |  |  |  | 88.49 | [5 empty] | 88.11 |  |  | 89.76 |  |  |  | 0.51 |  | 0.45 | [8 empty] | 11.06 |  |  |  |  | 1.01
2007 |  |  |  | 4090.87 |  |  | 8403 |  |  |  | 488 | [10 empty] | 94.85 |  |  |  | 95.47 | [5 empty] | 95.70 |  |  | 95.92 |  |  |  | 0.24 |  | 0.23 | [8 empty] | 4.30 |  |  |  |  | 0.61
2008 |  |  |  | 3997.95 |  |  | 8240 |  |  |  | 488 | [10 empty] | 92.52 |  |  |  | 93.47 | [5 empty] | 93.27 |  |  | 93.81 |  |  |  | 0.02 |  | 0.22 | [8 empty] | 6.32 |  |  |  |  | 0.95
2009 |  |  |  | 4063.83 |  |  | 8318 |  |  |  | 488 | [10 empty] | 94.26 |  |  |  | 94.59 | [5 empty] | 95.06 |  |  | 94.95 |  |  |  | 0.18 |  | 0.17 | [8 empty] | 5.24 |  |  |  |  | 0.33
2010 |  |  |  | 3789.14 |  |  | 7797 |  |  |  | 488 | [10 empty] | 88.09 |  |  |  | 88.80 | [5 empty] | 88.64 |  |  | 89.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.20 |  |  |  |  | 0.70
2011 |  |  |  | 4035.30 |  |  | 8290 |  |  |  | 488 | [10 empty] | 93.70 |  |  |  | 94.48 | [5 empty] | 94.40 |  |  | 94.63 |  |  |  | 0.07 |  | 0.77 | [8 empty] | 4.75 |  |  |  |  | 0.77
2012 |  |  |  | 3959.19 |  |  | 8141 |  |  |  | 496 | [10 empty] | 91.02 |  |  |  | 92.04 | [5 empty] | 90.87 |  |  | 92.68 |  |  |  | 2.12 |  | 1.99 | [8 empty] | 5.97 |  |  |  |  | 1.02
2013 |  |  |  | 4040.04 |  |  | 8250 |  |  |  | 496 | [10 empty] | 92.40 |  |  |  | 93.69 | [5 empty] | 92.98 |  |  | 94.18 |  |  |  | 1.58 |  | 1.50 | [8 empty] | 4.81 |  |  |  |  | 1.29
2014 |  |  |  | 3872.75 |  |  | 7912 |  |  |  | 496 | [10 empty] | 88.91 |  |  |  | 89.73 | [5 empty] | 89.13 |  |  | 90.32 |  |  |  | 0.29 |  | 0.64 | [8 empty] | 9.63 |  |  |  |  | 0.82
2015 |  |  |  | 4039.11 |  |  | 8276 |  |  |  | 496 | [10 empty] | 92.60 |  |  |  | 93.20 | [5 empty] | 92.96 |  |  | 94.47 |  |  |  | 2.07 |  | 1.97 | [8 empty] | 4.84 |  |  |  |  | 0.60
2016 |  |  |  | 4068.96 |  |  | 8304 |  |  |  | 502 | [10 empty] | 92.94 |  |  |  | 93.97 | [5 empty] | 93.30 |  |  | 94.54 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 5.94 |  |  |  |  | 1.04
2017 |  |  |  | 4071.92 |  |  | 8255 |  |  |  | 502 | [10 empty] | 92.51 |  |  |  | 93.96 | [5 empty] | 92.60 |  |  | 94.24 |  |  |  | 1.16 |  | 1.10 | [8 empty] | 4.94 |  |  |  |  | 1.45
2018 |  |  |  | 3770.71 |  |  | 7639 |  |  |  | 507 | [10 empty] | 85.52 |  |  |  | 86.92 | [5 empty] | 85.60 |  |  | 87.20 |  |  |  | 0.26 |  | 1.44 | [8 empty] | 11.64 |  |  |  |  | 1.41
2019 |  |  |  | 4053.97 |  |  | 8142 |  |  |  | 507 | [10 empty] | 91.58 |  |  |  | 92.48 | [5 empty] | 91.28 |  |  | 92.95 |  |  |  | 0.19 |  | 2.56 | [8 empty] | 4.96 |  |  |  |  | 0.91
2020 |  |  |  | 4058.51 |  |  | 8171 |  |  |  | 507 | [10 empty] | 91.22 |  |  |  | 92.53 | [5 empty] | 91.13 |  |  | 93.02 |  |  |  | 0.11 |  | 0.52 | [8 empty] | 6.96 |  |  |  |  | 1.30
2021 |  |  |  | 4071.02 |  |  | 8170 |  |  |  | 507 | [10 empty] | 91.81 |  |  |  | 93.01 | [5 empty] | 91.66 |  |  | 93.26 |  |  |  | 0.00 |  | 1.80 | [8 empty] | 5.20 |  |  |  |  | 1.19
2022 |  |  |  | 3894.87 |  |  | 7810 |  |  |  | 507 | [10 empty] | 87.80 |  |  |  | 88.76 | [5 empty] | 87.69 |  |  | 89.15 |  |  |  | 1.12 |  | 2.46 | [8 empty] | 8.78 |  |  |  |  | 0.97
2023 |  |  |  | 4100.21 |  |  | 8327 |  |  |  | 507 | [10 empty] | 92.89 |  |  |  | 93.82 | [5 empty] | 92.32 |  |  | 95.06 |  |  |  | 0.00 |  | 0.28 | [8 empty] | 5.91 |  |  |  |  | 0.93
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1981 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 82
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 408 | [14 empty] | 642 |  |  |  | 1
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 28
Z. |  | Other | [24 empty] | 24 | [10 empty] | 1 |  |  |  | 13
Subtotal | [22 empty] | 408 |  |  |  | 24 | [10 empty] | 671 |  |  |  | 96
Total | [22 empty] | 432 | [14 empty] | 767
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1981 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 9
12. |  |  | Reactor I&C Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 43
16. |  |  | Steam generation systems | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 12
34. |  |  | Miscellaneous Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 1
Total | [37 empty] | 83

## OLKILUOTO-1
2023 Operating Experience
FI-3 | [8 empty] | OLKILUOTO-1 | [26 empty] | FINLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVO (TEOLLISUUDEN VOIMA OYJ)
Owner | [7 empty] | : | TVO (TEOLLISUUDEN VOIMA OYJ)
Reactor Supplier | [7 empty] | : | ASEASTAL (ASEA-ATOM / STAL-LAVAL)
Turbine Supplier | [7 empty] | : | ASEASTAL (ASEA-ATOM / STAL-LAVAL)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / AA-III, BWR-2500 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-02-01
Thermal power | [12 empty] | : |  |  | 2500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1978-09-02
Gross electrical power | [12 empty] | : |  |  | 920 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-10-10
Reference unit power (net) | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 45 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.12
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.8
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.85 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 4
| Active core diameter [m] | [13 empty] | : |  |  | 3.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.7
| Active core height/length [m] | [13 empty] | : |  |  | 3.68 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 500 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 121 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7428.24 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.05 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.45 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.57 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.98 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.45 %
Load Factor (LF) | [18 empty] | : | 95.28 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.52 %
Operating Factor (OF) | [18 empty] | : | 97.23 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 243 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 667.53 | 600.99 |  |  |  | 666.14 |  | 409.77 | [8 empty] | 634.87 |  |  | 628.92 | [6 empty] | 641.52 |  | 639.43 |  |  |  | 597.28 |  |  | 629.70 |  |  | 644.68 | [9 empty] | 667.40 |  |  | 7428.24
EAF [%] |  |  |  |  | 100.00 | 99.73 |  |  |  | 100.00 |  | 63.77 | [8 empty] | 100.00 |  |  | 98.15 | [6 empty] | 98.27 |  | 98.20 |  |  |  | 98.91 |  |  | 100.00 |  |  | 99.93 | [9 empty] | 100.00 |  |  | 96.45
UCF [%] |  |  |  |  | 100.00 | 99.73 |  |  |  | 100.00 |  | 64.18 | [8 empty] | 100.00 |  |  | 99.42 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 99.95 |  |  | 100.00 |  |  | 99.93 | [9 empty] | 100.00 |  |  | 96.98
LF [%] |  |  |  |  | 100.81 | 100.49 |  |  |  | 100.74 |  | 63.95 | [8 empty] | 95.88 |  |  | 98.15 | [6 empty] | 96.88 |  | 96.57 |  |  |  | 93.21 |  |  | 94.97 |  |  | 100.60 | [9 empty] | 100.79 |  |  | 95.28
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 66.25 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.23
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.58 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 6.38 | [8 empty] | 0.00 |  |  | 0.58 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.57
PUF [%] |  |  |  |  | 0.00 | 0.27 |  |  |  | 0.00 |  | 29.45 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.05 |  |  | 0.00 |  |  | 0.07 | [9 empty] | 0.00 |  |  | 2.45
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.40 | [8 empty] | 0.00 |  |  | 1.27 | [6 empty] | 1.72 |  | 1.80 |  |  |  | 1.05 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.52
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 288862.97 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.38 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.75 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.55 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.21 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 5.25 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 92.58 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.46 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 93.77 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 3465.00 |  |  | 5614 |  |  |  | 660 | [10 empty] | 86.85 |  |  |  | 86.85 | [5 empty] | 86.82 |  |  | 90.40 |  |  |  | 12.45 |  | 12.35 | [8 empty] | 0.80 |  |  |  |  | 0.00
1980 |  |  |  | 4280.80 |  |  | 6849 |  |  |  | 658 | [10 empty] | 76.31 |  |  |  | 76.31 | [5 empty] | 74.06 |  |  | 77.97 |  |  |  | 3.12 |  | 2.46 | [8 empty] | 21.23 |  |  |  |  | 0.00
1981 |  |  |  | 4549.20 |  |  | 7353 |  |  |  | 660 | [10 empty] | 80.80 |  |  |  | 80.80 | [5 empty] | 78.68 |  |  | 83.94 |  |  |  | 8.82 |  | 7.82 | [8 empty] | 11.38 |  |  |  |  | 0.00
1982 |  |  |  | 4997.50 |  |  | 7903 |  |  |  | 658 | [10 empty] | 86.68 |  |  |  | 86.68 | [5 empty] | 86.70 |  |  | 90.22 |  |  |  | 3.90 |  | 3.51 | [8 empty] | 9.81 |  |  |  |  | 0.00
1983 |  |  |  | 4808.30 |  |  | 7651 |  |  |  | 669 | [10 empty] | 81.86 |  |  |  | 81.86 | [5 empty] | 82.01 |  |  | 87.34 |  |  |  | 0.96 |  | 0.79 | [8 empty] | 17.35 |  |  |  |  | 0.00
1984 |  |  |  | 5505.61 |  |  | 8247 |  |  |  | 694 | [10 empty] | 91.94 |  |  |  | 91.94 | [5 empty] | 90.30 |  |  | 93.89 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 7.76 |  |  |  |  | 0.00
1985 |  |  |  | 5414.51 |  |  | 8180 |  |  |  | 710 | [10 empty] | 88.75 |  |  |  | 88.75 | [5 empty] | 87.06 |  |  | 93.38 |  |  |  | 2.58 |  | 2.35 | [8 empty] | 8.90 |  |  |  |  | 0.00
1986 |  |  |  | 5463.21 |  |  | 8008 |  |  |  | 710 | [10 empty] | 90.08 |  |  |  | 90.08 | [5 empty] | 87.84 |  |  | 91.42 |  |  |  | 0.72 |  | 0.65 | [8 empty] | 9.27 |  |  |  |  | 0.00
1987 |  |  |  | 5636.46 |  |  | 8142 |  |  |  | 710 | [10 empty] | 92.05 |  |  |  | 92.05 | [5 empty] | 90.62 |  |  | 92.95 |  |  |  | 2.64 |  | 2.49 | [8 empty] | 5.45 |  |  |  |  | 0.00
1988 |  |  |  | 5778.87 |  |  | 8248 |  |  |  | 710 | [10 empty] | 94.07 |  |  |  | 94.29 | [5 empty] | 92.66 |  |  | 93.90 |  |  |  | 1.20 |  | 1.15 | [8 empty] | 4.56 |  |  |  |  | 0.22
1989 |  |  |  | 5056.20 |  |  | 7278 |  |  |  | 710 | [10 empty] | 83.18 |  |  |  | 83.18 | [5 empty] | 81.29 |  |  | 83.08 |  |  |  | 13.17 |  | 12.62 | [8 empty] | 4.20 |  |  |  |  | 0.00
1990 |  |  |  | 5857.31 |  |  | 8356 |  |  |  | 710 | [10 empty] | 95.60 |  |  |  | 95.60 | [5 empty] | 94.17 |  |  | 95.39 |  |  |  | 0.57 |  | 0.55 | [8 empty] | 3.86 |  |  |  |  | 0.00
1991 |  |  |  | 5873.22 |  |  | 8373 |  |  |  | 710 | [10 empty] | 94.85 |  |  |  | 95.72 | [5 empty] | 94.43 |  |  | 95.58 |  |  |  | 0.13 |  | 0.12 | [8 empty] | 4.16 |  |  |  |  | 0.87
1992 |  |  |  | 5803.04 |  |  | 8251 |  |  |  | 710 | [10 empty] | 93.23 |  |  |  | 93.72 | [5 empty] | 93.05 |  |  | 93.93 |  |  |  | 0.44 |  | 0.42 | [8 empty] | 5.87 |  |  |  |  | 0.49
1993 |  |  |  | 5944.92 |  |  | 8433 |  |  |  | 710 | [10 empty] | 95.33 |  |  |  | 95.78 | [5 empty] | 95.58 |  |  | 96.27 |  |  |  | 0.28 |  | 0.27 | [8 empty] | 3.95 |  |  |  |  | 0.45
1994 |  |  |  | 5978.04 |  |  | 8485 |  |  |  | 710 | [10 empty] | 96.01 |  |  |  | 96.50 | [5 empty] | 96.12 |  |  | 96.86 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 3.45 |  |  |  |  | 0.49
1995 |  |  |  | 5931.50 |  |  | 8427 |  |  |  | 710 | [10 empty] | 95.50 |  |  |  | 96.11 | [5 empty] | 95.37 |  |  | 96.20 |  |  |  | 0.84 |  | 0.81 | [8 empty] | 3.08 |  |  |  |  | 0.61
1996 |  |  |  | 5938.60 |  |  | 8212 |  |  |  | 710 | [10 empty] | 92.08 |  |  |  | 92.19 | [5 empty] | 95.22 |  |  | 93.49 |  |  |  | 1.22 |  | 1.14 | [8 empty] | 6.67 |  |  |  |  | 0.11
1997 |  |  |  | 6374.15 |  |  | 8254 |  |  |  | 772 | [10 empty] | 93.83 |  |  |  | 93.86 | [5 empty] | 94.18 |  |  | 94.22 |  |  |  | 1.24 |  | 1.18 | [8 empty] | 4.96 |  |  |  |  | 0.03
1998 |  |  |  | 6807.01 |  |  | 8384 |  |  |  | 840 | [10 empty] | 94.95 |  |  |  | 95.57 | [5 empty] | 92.51 |  |  | 95.71 |  |  |  | 0.22 |  | 0.21 | [8 empty] | 4.22 |  |  |  |  | 0.62
1999 |  |  |  | 7111.82 |  |  | 8542 |  |  |  | 840 | [10 empty] | 96.39 |  |  |  | 97.24 | [5 empty] | 96.65 |  |  | 97.51 |  |  |  | 0.26 |  | 0.25 | [8 empty] | 2.51 |  |  |  |  | 0.84
2000 |  |  |  | 7043.10 |  |  | 8448 |  |  |  | 840 | [10 empty] | 95.17 |  |  |  | 95.81 | [5 empty] | 95.45 |  |  | 96.17 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 4.06 |  |  |  |  | 0.65
2001 |  |  |  | 7163.80 |  |  | 8561 |  |  |  | 840 | [10 empty] | 97.16 |  |  |  | 97.64 | [5 empty] | 97.36 |  |  | 97.73 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 2.35 |  |  |  |  | 0.48
2002 |  |  |  | 6997.54 |  |  | 8377 |  |  |  | 840 | [10 empty] | 95.05 |  |  |  | 95.51 | [5 empty] | 95.09 |  |  | 95.62 |  |  |  | 0.65 |  | 0.63 | [8 empty] | 3.86 |  |  |  |  | 0.46
2003 |  |  |  | 7127.43 |  |  | 8515 |  |  |  | 840 | [10 empty] | 96.46 |  |  |  | 97.08 | [5 empty] | 96.86 |  |  | 97.20 |  |  |  | 0.18 |  | 0.51 | [8 empty] | 2.41 |  |  |  |  | 0.61
2004 |  |  |  | 7009.02 |  |  | 8329 |  |  |  | 840 | [10 empty] | 94.70 |  |  |  | 94.70 | [5 empty] | 94.99 |  |  | 94.82 |  |  |  | 0.80 |  | 1.19 | [8 empty] | 4.11 |  |  |  |  | 0.00
2005 |  |  |  | 7221.07 |  |  | 8588 |  |  |  | 840 | [10 empty] | 97.73 |  |  |  | 97.85 | [5 empty] | 98.13 |  |  | 98.04 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 2.13 |  |  |  |  | 0.12
2006 |  |  |  | 6973.38 |  |  | 8206 |  |  |  | 860 | [10 empty] | 92.64 |  |  |  | 93.34 | [5 empty] | 93.64 |  |  | 93.68 |  |  |  | 0.35 |  | 0.60 | [8 empty] | 6.06 |  |  |  |  | 0.71
2007 |  |  |  | 7334.94 |  |  | 8554 |  |  |  | 860 | [10 empty] | 96.75 |  |  |  | 97.37 | [5 empty] | 97.36 |  |  | 97.65 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 2.59 |  |  |  |  | 0.63
2008 |  |  |  | 7066.02 |  |  | 8288 |  |  |  | 860 | [10 empty] | 93.14 |  |  |  | 93.59 | [5 empty] | 93.54 |  |  | 94.35 |  |  |  | 0.78 |  | 2.09 | [8 empty] | 4.32 |  |  |  |  | 0.44
2009 |  |  |  | 7295.77 |  |  | 8548 |  |  |  | 860 | [10 empty] | 96.69 |  |  |  | 97.22 | [5 empty] | 96.84 |  |  | 97.58 |  |  |  | 0.30 |  | 0.37 | [8 empty] | 2.41 |  |  |  |  | 0.53
2010 |  |  |  | 6976.89 |  |  | 8120 |  |  |  | 880 | [10 empty] | 91.41 |  |  |  | 92.00 | [5 empty] | 91.54 |  |  | 92.69 |  |  |  | 0.65 |  | 0.90 | [8 empty] | 7.11 |  |  |  |  | 0.59
2011 |  |  |  | 7289.82 |  |  | 8410 |  |  |  | 880 | [10 empty] | 94.80 |  |  |  | 95.55 | [5 empty] | 94.56 |  |  | 96.00 |  |  |  | 1.91 |  | 2.38 | [8 empty] | 2.07 |  |  |  |  | 0.76
2012 |  |  |  | 6973.36 |  |  | 8013 |  |  |  | 880 | [10 empty] | 90.08 |  |  |  | 90.91 | [5 empty] | 90.21 |  |  | 91.22 |  |  |  | 2.52 |  | 2.35 | [8 empty] | 6.74 |  |  |  |  | 0.83
2013 |  |  |  | 7470.41 |  |  | 8555 |  |  |  | 880 | [10 empty] | 96.37 |  |  |  | 97.41 | [5 empty] | 96.91 |  |  | 97.66 |  |  |  | 0.36 |  | 0.58 | [8 empty] | 2.01 |  |  |  |  | 1.04
2014 |  |  |  | 7266.09 |  |  | 8337 |  |  |  | 880 | [10 empty] | 94.00 |  |  |  | 94.81 | [5 empty] | 94.26 |  |  | 95.17 |  |  |  | 0.38 |  | 0.89 | [8 empty] | 4.30 |  |  |  |  | 0.81
2015 |  |  |  | 7396.91 |  |  | 8506 |  |  |  | 880 | [10 empty] | 95.68 |  |  |  | 96.75 | [5 empty] | 95.95 |  |  | 97.10 |  |  |  | 0.24 |  | 0.66 | [8 empty] | 2.59 |  |  |  |  | 1.07
2016 |  |  |  | 7047.81 |  |  | 8146 |  |  |  | 880 | [10 empty] | 90.90 |  |  |  | 91.84 | [5 empty] | 91.18 |  |  | 92.74 |  |  |  | 2.29 |  | 3.46 | [8 empty] | 4.70 |  |  |  |  | 0.93
2017 |  |  |  | 7158.27 |  |  | 8289 |  |  |  | 880 | [10 empty] | 92.65 |  |  |  | 93.67 | [5 empty] | 92.86 |  |  | 94.62 |  |  |  | 3.26 |  | 3.82 | [8 empty] | 2.51 |  |  |  |  | 1.02
2018 |  |  |  | 6755.36 |  |  | 7731 |  |  |  | 880 | [10 empty] | 87.55 |  |  |  | 87.67 | [5 empty] | 87.63 |  |  | 88.25 |  |  |  | 0.65 |  | 2.73 | [8 empty] | 9.60 |  |  |  |  | 0.12
2019 |  |  |  | 7542.04 |  |  | 8539 |  |  |  | 890 | [10 empty] | 96.52 |  |  |  | 96.96 | [5 empty] | 96.74 |  |  | 97.48 |  |  |  | 0.27 |  | 0.32 | [8 empty] | 2.72 |  |  |  |  | 0.44
2020 |  |  |  | 7310.06 |  |  | 8391 |  |  |  | 890 | [10 empty] | 93.25 |  |  |  | 93.75 | [5 empty] | 93.51 |  |  | 95.53 |  |  |  | 2.12 |  | 2.30 | [8 empty] | 3.94 |  |  |  |  | 0.50
2021 |  |  |  | 7404.18 |  |  | 8375 |  |  |  | 890 | [10 empty] | 94.57 |  |  |  | 95.31 | [5 empty] | 94.97 |  |  | 95.61 |  |  |  | 0.19 |  | 0.34 | [8 empty] | 4.35 |  |  |  |  | 0.74
2022 |  |  |  | 6931.89 |  |  | 7827 |  |  |  | 890 | [10 empty] | 88.46 |  |  |  | 88.86 | [5 empty] | 88.91 |  |  | 89.35 |  |  |  | 2.30 |  | 2.09 | [8 empty] | 9.06 |  |  |  |  | 0.39
2023 |  |  |  | 7428.24 |  |  | 8517 |  |  |  | 890 | [10 empty] | 96.45 |  |  |  | 96.98 | [5 empty] | 95.28 |  |  | 97.23 |  |  |  | 0.05 |  | 0.57 | [8 empty] | 2.45 |  |  |  |  | 0.52
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1979 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 46 | [14 empty] | 97
B. |  | Refuelling without maintenance | [35 empty] | 36
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 197 | [14 empty] | 377 |  |  |  | 1
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 12
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 4
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 18
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
Z. |  | Other | [39 empty] | 24
Subtotal | [22 empty] | 197 |  |  |  | 46 | [10 empty] | 443 |  |  |  | 127 | [11 empty] | 12
Total | [22 empty] | 243 | [14 empty] | 582
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1979 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 17
12. |  |  | Reactor I&C Systems | [34 empty] | 5
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 46 | [14 empty] | 23
14. |  |  | Safety Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 14
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
33. |  |  | Circulating Water System | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 35
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 46 | [14 empty] | 122
Highlights (2023)
The electricity production of the Olkiluoto power plant units OL1, OL2 and OL3 during 2023 was 24,671 GWh. OL1's net production was 7,428 GWh. The annual outages of 2023 at the Olkiluoto nuclear power plant were carried out from April 16 to May 19, 2023. OL2 was performed a maintenance outage taking more than 17 days, and OL1 performed a refueling outage that lasted over 10 days. The annual outage period was about four days longer than expected. The schedule was affected mainly from relief system. In all other respects annual outages were implemented according to plans. The OL3 plant unit first annual outage starts on March 3, 2024.

## OLKILUOTO-2
2023 Operating Experience
FI-4 | [8 empty] | OLKILUOTO-2 | [26 empty] | FINLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVO (TEOLLISUUDEN VOIMA OYJ)
Owner | [7 empty] | : | TVO (TEOLLISUUDEN VOIMA OYJ)
Reactor Supplier | [7 empty] | : | ASEASTAL (ASEA-ATOM / STAL-LAVAL)
Turbine Supplier | [7 empty] | : | ASEASTAL (ASEA-ATOM / STAL-LAVAL)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / AA-III, BWR-2500 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-11-01
Thermal power | [12 empty] | : |  |  | 2500 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-02-18
Gross electrical power | [12 empty] | : |  |  | 920 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1982-07-10
Reference unit power (net) | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.12
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.8
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.66 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 21 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 45500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 4
| Active core diameter [m] | [13 empty] | : |  |  | 4.00 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.7
| Active core height/length [m] | [13 empty] | : |  |  | 3.68 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 500 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 15.0 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 121 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6871.08 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 6.45 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.12 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 6.59 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.71 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.7 %
Load Factor (LF) | [18 empty] | : | 88.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.6 %
Operating Factor (OF) | [18 empty] | : | 89.5 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 920 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 602.14 | 599.19 |  |  |  | 662.44 |  | 633.44 | [8 empty] | 227.96 |  |  | 631.55 | [6 empty] | 647.37 |  | 356.79 |  |  |  | 541.85 |  |  | 662.82 |  |  | 643.39 | [9 empty] | 662.15 |  |  | 6871.08
EAF [%] |  |  |  |  | 90.71 | 100.00 |  |  |  | 99.94 |  | 98.83 | [8 empty] | 35.39 |  |  | 98.56 | [6 empty] | 97.77 |  | 53.89 |  |  |  | 84.56 |  |  | 99.97 |  |  | 99.89 | [9 empty] | 100.00 |  |  | 88.12
UCF [%] |  |  |  |  | 90.71 | 100.00 |  |  |  | 99.94 |  | 100.00 | [8 empty] | 35.58 |  |  | 100.00 | [6 empty] | 99.92 |  | 55.08 |  |  |  | 85.54 |  |  | 100.00 |  |  | 99.89 | [9 empty] | 100.00 |  |  | 88.71
LF [%] |  |  |  |  | 90.94 | 100.19 |  |  |  | 100.18 |  | 98.85 | [8 empty] | 34.43 |  |  | 98.56 | [6 empty] | 97.77 |  | 53.88 |  |  |  | 84.56 |  |  | 99.97 |  |  | 100.40 | [9 empty] | 100.00 |  |  | 88.13
OF [%] |  |  |  |  | 94.22 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 39.11 |  |  | 100.00 | [6 empty] | 100.00 |  | 55.38 |  |  |  | 87.22 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.50
FLR [%] |  |  |  |  | 9.09 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.32 |  |  | 0.00 | [6 empty] | 0.00 |  | 44.92 |  |  |  | 14.46 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.45
UCL [%] |  |  |  |  | 9.07 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.59 |  |  | 0.00 | [6 empty] | 0.00 |  | 44.92 |  |  |  | 14.46 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.59
PUF [%] |  |  |  |  | 0.22 | 0.00 |  |  |  | 0.06 |  | 0.00 | [8 empty] | 54.83 |  |  | 0.00 | [6 empty] | 0.08 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.11 | [9 empty] | 0.00 |  |  | 4.70
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 1.17 | [8 empty] | 0.19 |  |  | 1.44 | [6 empty] | 2.15 |  | 1.19 |  |  |  | 0.98 |  |  | 0.03 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.60
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 278960.82 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.33 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 92.99 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.66 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.53 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 4.81 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 92.89 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.55 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 94.08 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1982 |  |  |  | 4587.10 |  |  | 7269 |  |  |  | 658 | [10 empty] | 77.65 |  |  |  | 77.65 | [5 empty] | 77.64 |  |  | 79.53 |  |  |  | 2.38 |  | 1.89 | [8 empty] | 20.45 |  |  |  |  | 0.00
1983 |  |  |  | 5087.20 |  |  | 8221 |  |  |  | 657 | [10 empty] | 86.75 |  |  |  | 86.75 | [5 empty] | 88.39 |  |  | 93.85 |  |  |  | 5.00 |  | 4.57 | [8 empty] | 8.69 |  |  |  |  | 0.00
1984 |  |  |  | 5341.30 |  |  | 8031 |  |  |  | 696 | [10 empty] | 89.57 |  |  |  | 89.57 | [5 empty] | 87.28 |  |  | 91.43 |  |  |  | 1.96 |  | 1.79 | [8 empty] | 8.64 |  |  |  |  | 0.00
1985 |  |  |  | 5415.79 |  |  | 7912 |  |  |  | 710 | [10 empty] | 88.16 |  |  |  | 88.16 | [5 empty] | 87.08 |  |  | 90.32 |  |  |  | 1.98 |  | 1.78 | [8 empty] | 10.06 |  |  |  |  | 0.00
1986 |  |  |  | 5840.21 |  |  | 8437 |  |  |  | 710 | [10 empty] | 95.07 |  |  |  | 95.07 | [5 empty] | 93.90 |  |  | 96.31 |  |  |  | 0.32 |  | 0.30 | [8 empty] | 4.63 |  |  |  |  | 0.00
1987 |  |  |  | 5725.03 |  |  | 8379 |  |  |  | 710 | [10 empty] | 93.71 |  |  |  | 93.71 | [5 empty] | 92.05 |  |  | 95.65 |  |  |  | 1.41 |  | 1.34 | [8 empty] | 4.95 |  |  |  |  | 0.00
1988 |  |  |  | 5713.20 |  |  | 8220 |  |  |  | 710 | [10 empty] | 92.73 |  |  |  | 92.73 | [5 empty] | 91.61 |  |  | 93.58 |  |  |  | 2.89 |  | 2.76 | [8 empty] | 4.51 |  |  |  |  | 0.00
1989 |  |  |  | 5827.02 |  |  | 8363 |  |  |  | 710 | [10 empty] | 94.94 |  |  |  | 94.94 | [5 empty] | 93.69 |  |  | 95.47 |  |  |  | 0.39 |  | 0.37 | [8 empty] | 4.69 |  |  |  |  | 0.00
1990 |  |  |  | 5749.87 |  |  | 8265 |  |  |  | 710 | [10 empty] | 93.78 |  |  |  | 93.78 | [5 empty] | 92.45 |  |  | 94.35 |  |  |  | 1.20 |  | 1.14 | [8 empty] | 5.09 |  |  |  |  | 0.00
1991 |  |  |  | 5730.95 |  |  | 8216 |  |  |  | 710 | [10 empty] | 92.96 |  |  |  | 93.67 | [5 empty] | 92.14 |  |  | 93.79 |  |  |  | 2.10 |  | 2.01 | [8 empty] | 4.32 |  |  |  |  | 0.71
1992 |  |  |  | 5790.44 |  |  | 8306 |  |  |  | 710 | [10 empty] | 93.31 |  |  |  | 94.54 | [5 empty] | 92.85 |  |  | 94.56 |  |  |  | 1.63 |  | 1.57 | [8 empty] | 3.89 |  |  |  |  | 1.23
1993 |  |  |  | 5861.56 |  |  | 8327 |  |  |  | 710 | [10 empty] | 94.38 |  |  |  | 95.14 | [5 empty] | 94.24 |  |  | 95.06 |  |  |  | 0.16 |  | 0.15 | [8 empty] | 4.71 |  |  |  |  | 0.76
1994 |  |  |  | 5732.63 |  |  | 8130 |  |  |  | 710 | [10 empty] | 92.30 |  |  |  | 93.15 | [5 empty] | 92.17 |  |  | 92.81 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 6.76 |  |  |  |  | 0.85
1995 |  |  |  | 5747.24 |  |  | 8236 |  |  |  | 710 | [10 empty] | 92.47 |  |  |  | 93.71 | [5 empty] | 92.42 |  |  | 94.03 |  |  |  | 1.88 |  | 1.79 | [8 empty] | 4.50 |  |  |  |  | 1.24
1996 |  |  |  | 5915.41 |  |  | 8413 |  |  |  | 710 | [10 empty] | 94.96 |  |  |  | 95.29 | [5 empty] | 94.85 |  |  | 95.78 |  |  |  | 1.49 |  | 1.44 | [8 empty] | 3.27 |  |  |  |  | 0.33
1997 |  |  |  | 6077.04 |  |  | 8258 |  |  |  | 736 | [10 empty] | 93.74 |  |  |  | 94.56 | [5 empty] | 94.14 |  |  | 94.27 |  |  |  | 0.22 |  | 0.21 | [8 empty] | 5.23 |  |  |  |  | 0.82
1998 |  |  |  | 6628.46 |  |  | 8207 |  |  |  | 840 | [10 empty] | 93.23 |  |  |  | 94.29 | [5 empty] | 90.08 |  |  | 93.69 |  |  |  | 0.51 |  | 0.48 | [8 empty] | 5.22 |  |  |  |  | 1.06
1999 |  |  |  | 7091.21 |  |  | 8505 |  |  |  | 840 | [10 empty] | 96.43 |  |  |  | 96.86 | [5 empty] | 96.37 |  |  | 97.09 |  |  |  | 0.17 |  | 0.17 | [8 empty] | 2.97 |  |  |  |  | 0.43
2000 |  |  |  | 7028.90 |  |  | 8457 |  |  |  | 840 | [10 empty] | 95.31 |  |  |  | 95.93 | [5 empty] | 95.26 |  |  | 96.28 |  |  |  | 0.15 |  | 0.15 | [8 empty] | 3.92 |  |  |  |  | 0.61
2001 |  |  |  | 6988.00 |  |  | 8387 |  |  |  | 840 | [10 empty] | 95.12 |  |  |  | 95.12 | [5 empty] | 94.97 |  |  | 95.74 |  |  |  | 0.52 |  | 0.49 | [8 empty] | 4.39 |  |  |  |  | 0.00
2002 |  |  |  | 7108.51 |  |  | 8472 |  |  |  | 840 | [10 empty] | 96.79 |  |  |  | 96.96 | [5 empty] | 96.59 |  |  | 96.70 |  |  |  | 0.47 |  | 0.46 | [8 empty] | 2.58 |  |  |  |  | 0.16
2003 |  |  |  | 7026.86 |  |  | 8378 |  |  |  | 840 | [10 empty] | 95.16 |  |  |  | 95.48 | [5 empty] | 95.49 |  |  | 95.64 |  |  |  | 0.39 |  | 0.62 | [8 empty] | 3.90 |  |  |  |  | 0.33
2004 |  |  |  | 7080.70 |  |  | 8485 |  |  |  | 840 | [10 empty] | 95.81 |  |  |  | 95.81 | [5 empty] | 95.96 |  |  | 96.60 |  |  |  | 1.23 |  | 1.55 | [8 empty] | 2.64 |  |  |  |  | 0.00
2005 |  |  |  | 6996.68 |  |  | 8248 |  |  |  | 860 | [10 empty] | 93.80 |  |  |  | 93.82 | [5 empty] | 93.96 |  |  | 94.16 |  |  |  | 0.05 |  | 0.41 | [8 empty] | 5.77 |  |  |  |  | 0.01
2006 |  |  |  | 7294.36 |  |  | 8562 |  |  |  | 860 | [10 empty] | 96.37 |  |  |  | 97.43 | [5 empty] | 96.82 |  |  | 97.74 |  |  |  | 0.21 |  | 0.28 | [8 empty] | 2.29 |  |  |  |  | 1.06
2007 |  |  |  | 7051.32 |  |  | 8258 |  |  |  | 860 | [10 empty] | 93.21 |  |  |  | 94.01 | [5 empty] | 93.60 |  |  | 94.27 |  |  |  | 1.01 |  | 1.53 | [8 empty] | 4.45 |  |  |  |  | 0.81
2008 |  |  |  | 7313.82 |  |  | 8579 |  |  |  | 860 | [10 empty] | 96.29 |  |  |  | 96.94 | [5 empty] | 96.82 |  |  | 97.67 |  |  |  | 0.80 |  | 0.85 | [8 empty] | 2.21 |  |  |  |  | 0.65
2009 |  |  |  | 7156.34 |  |  | 8365 |  |  |  | 860 | [10 empty] | 94.53 |  |  |  | 95.20 | [5 empty] | 94.99 |  |  | 95.49 |  |  |  | 0.14 |  | 0.58 | [8 empty] | 4.23 |  |  |  |  | 0.66
2010 |  |  |  | 7167.34 |  |  | 8386 |  |  |  | 860 | [10 empty] | 94.59 |  |  |  | 95.29 | [5 empty] | 95.14 |  |  | 95.73 |  |  |  | 1.45 |  | 2.03 | [8 empty] | 2.67 |  |  |  |  | 0.70
2011 |  |  |  | 6913.53 |  |  | 7987 |  |  |  | 880 | [10 empty] | 89.88 |  |  |  | 90.69 | [5 empty] | 90.71 |  |  | 91.18 |  |  |  | 0.39 |  | 1.31 | [8 empty] | 8.00 |  |  |  |  | 0.81
2012 |  |  |  | 7477.19 |  |  | 8561 |  |  |  | 880 | [10 empty] | 95.85 |  |  |  | 97.30 | [5 empty] | 96.73 |  |  | 97.46 |  |  |  | 0.00 |  | 0.37 | [8 empty] | 2.32 |  |  |  |  | 1.46
2013 |  |  |  | 7162.81 |  |  | 8171 |  |  |  | 880 | [10 empty] | 92.03 |  |  |  | 93.11 | [5 empty] | 92.92 |  |  | 93.28 |  |  |  | 1.98 |  | 2.15 | [8 empty] | 4.74 |  |  |  |  | 1.09
2014 |  |  |  | 7496.54 |  |  | 8567 |  |  |  | 880 | [10 empty] | 96.75 |  |  |  | 97.61 | [5 empty] | 97.25 |  |  | 97.80 |  |  |  | 0.15 |  | 0.20 | [8 empty] | 2.19 |  |  |  |  | 0.86
2015 |  |  |  | 6863.99 |  |  | 7856 |  |  |  | 880 | [10 empty] | 88.52 |  |  |  | 89.08 | [5 empty] | 89.04 |  |  | 89.68 |  |  |  | 6.32 |  | 6.70 | [8 empty] | 4.22 |  |  |  |  | 0.56
2016 |  |  |  | 7300.52 |  |  | 8381 |  |  |  | 880 | [10 empty] | 93.78 |  |  |  | 94.58 | [5 empty] | 94.45 |  |  | 95.41 |  |  |  | 2.81 |  | 3.03 | [8 empty] | 2.39 |  |  |  |  | 0.80
2017 |  |  |  | 6256.41 |  |  | 7132 |  |  |  | 880 | [10 empty] | 80.36 |  |  |  | 80.53 | [5 empty] | 81.16 |  |  | 81.42 |  |  |  | 1.89 |  | 7.84 | [8 empty] | 11.63 |  |  |  |  | 0.17
2018 |  |  |  | 7333.77 |  |  | 8350 |  |  |  | 890 | [10 empty] | 95.01 |  |  |  | 95.65 | [5 empty] | 94.07 |  |  | 95.32 |  |  |  | 0.45 |  | 1.27 | [8 empty] | 3.09 |  |  |  |  | 0.64
2019 |  |  |  | 7209.08 |  |  | 8162 |  |  |  | 890 | [10 empty] | 92.33 |  |  |  | 92.95 | [5 empty] | 92.47 |  |  | 93.17 |  |  |  | 1.16 |  | 1.16 | [8 empty] | 5.88 |  |  |  |  | 0.63
2020 |  |  |  | 7276.55 |  |  | 8289 |  |  |  | 890 | [10 empty] | 93.13 |  |  |  | 93.97 | [5 empty] | 93.08 |  |  | 94.36 |  |  |  | 2.87 |  | 3.58 | [8 empty] | 2.45 |  |  |  |  | 0.84
2021 |  |  |  | 7033.38 |  |  | 7941 |  |  |  | 890 | [10 empty] | 89.94 |  |  |  | 90.35 | [5 empty] | 90.21 |  |  | 90.65 |  |  |  | 0.58 |  | 1.41 | [8 empty] | 8.24 |  |  |  |  | 0.41
2022 |  |  |  | 7532.48 |  |  | 8539 |  |  |  | 890 | [10 empty] | 96.47 |  |  |  | 97.29 | [5 empty] | 96.61 |  |  | 97.48 |  |  |  | 0.00 |  | 0.42 | [8 empty] | 2.29 |  |  |  |  | 0.82
2023 |  |  |  | 6871.08 |  |  | 7840 |  |  |  | 890 | [10 empty] | 88.12 |  |  |  | 88.71 | [5 empty] | 88.13 |  |  | 89.50 |  |  |  | 6.45 |  | 6.59 | [8 empty] | 4.70 |  |  |  |  | 0.60
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1982 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 534 | [14 empty] | 306
B. |  | Refuelling without maintenance | [35 empty] | 33
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 387 | [14 empty] | 360
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 8
E. |  | Testing of plant systems or components | [35 empty] | 17 |  |  |  | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 24
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 7
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
P. |  | Fire | [39 empty] | 0
Z. |  | Other | [39 empty] | 1 | [11 empty] | 0
Subtotal | [22 empty] | 387 |  |  |  | 534 | [10 empty] | 442 |  |  |  | 315 | [11 empty] | 15
Total | [22 empty] | 921 | [14 empty] | 772
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1982 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 21
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 41 | [14 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 4
15. |  |  | Reactor Cooling Systems | [34 empty] | 21
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [19 empty] | 26 | [14 empty] | 7
32. |  |  | Feedwater and Main Steam System | [19 empty] | 43 | [14 empty] | 10
33. |  |  | Circulating Water System | [34 empty] | 1
34. |  |  | Miscellaneous Systems | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [19 empty] | 424 | [14 empty] | 218
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [22 empty] | 534 | [14 empty] | 290
Highlights (2023)
The electricity production of the Olkiluoto power plant units OL1, OL2 and OL3 during 2023 was 24,671 GWh. OL2´s net production was 6,871 GWh. OL2 plant unit was out of production from January 27 to January 29 due to repair of one main steam line valve. After annual outage during the start-up operation on May 19 there happened automatic scram due to high conductivity in condenser. There was cold shutdown due to leak in main generator cooling system from August 18 to September 4. The annual outages of 2023 at the Olkiluoto nuclear power plant were carried out from April 16 to May 19, 2023. OL2 was performed a maintenance outage taking more than 17 days, and OL1 performed a refueling outage that lasted over 10 days. The annual outage period was about four days longer than expected. The schedule was affected mainly from relief system. In all other respects annual outages were implemented according to plans. The OL3 plant unit first annual outage starts on March 3, 2024.

## OLKILUOTO-3
2023 Operating Experience
FI-5 | [8 empty] | OLKILUOTO-3 | [26 empty] | FINLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | TVO (TEOLLISUUDEN VOIMA OYJ)
Owner | [7 empty] | : | TVO (TEOLLISUUDEN VOIMA OYJ)
Reactor Supplier | [7 empty] | : | ORANO (ORANO)
Turbine Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / EPR | [11 empty] | Construction Date | [15 empty] | : |  |  | 2005-08-12
Thermal power | [12 empty] | : |  |  | 4300 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2022-03-12
Gross electrical power | [12 empty] | : |  |  | 1660 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2023-05-01
Reference unit power (net) | [12 empty] | : |  |  | 1600 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 312
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.53
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.54 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 47500 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.77 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 7
| Active core height/length [m] | [13 empty] | : |  |  | 4.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 89 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 6
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 10371.84 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.19 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.17 %
Unit Capability Factor (UCF) | [18 empty] | : | 96.85 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.98 %
Load Factor (LF) | [18 empty] | : | 88.76 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.57 %
Operating Factor (OF) | [18 empty] | : | 98.57 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1604 hours
Annual Summary
[5 empty] | Apr | Jan |  |  |  | Feb |  | Mar | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [20 empty] | 1065.69 |  |  | 980.14 | [6 empty] | 1122.28 |  | 1093.29 |  |  |  | 952.04 |  |  | 1044.85 |  |  | 965.31 | [9 empty] | 1128.76 |  |  | 8352.35
EAF [%] | [20 empty] | 98.87 |  |  | 93.55 | [6 empty] | 98.28 |  | 97.82 |  |  |  | 98.45 |  |  | 98.38 |  |  | 85.10 | [9 empty] | 99.42 |  |  | 96.28
UCF [%] | [20 empty] | 99.23 |  |  | 94.94 | [6 empty] | 99.30 |  | 98.61 |  |  |  | 99.28 |  |  | 98.60 |  |  | 85.10 | [9 empty] | 99.42 |  |  | 96.85
LF [%] | [20 empty] | 89.52 |  |  | 85.08 | [6 empty] | 94.28 |  | 91.84 |  |  |  | 82.64 |  |  | 87.66 |  |  | 83.79 | [9 empty] | 94.82 |  |  | 88.76
OF [%] | [20 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 88.33 | [9 empty] | 100.00 |  |  | 98.57
FLR [%] | [20 empty] | 0.03 |  |  | 0.00 | [6 empty] | 0.62 |  | 1.39 |  |  |  | 0.72 |  |  | 1.23 |  |  | 13.38 | [9 empty] | 0.45 |  |  | 2.19
UCL [%] | [20 empty] | 0.03 |  |  | 0.00 | [6 empty] | 0.62 |  | 1.39 |  |  |  | 0.72 |  |  | 1.22 |  |  | 13.15 | [9 empty] | 0.45 |  |  | 2.17
PUF [%] | [20 empty] | 0.74 |  |  | 5.06 | [6 empty] | 0.08 |  | 0.00 |  |  |  | 0.00 |  |  | 0.18 |  |  | 1.75 | [9 empty] | 0.13 |  |  | 0.98
XUF [%] | [20 empty] | 0.36 |  |  | 1.39 | [6 empty] | 1.02 |  | 0.79 |  |  |  | 0.83 |  |  | 0.21 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.57
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 12258.4 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.19 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 96.28 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.17 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 96.85 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 0.98 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.76 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.57 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 98.57 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2023 |  |  |  | 10371.84 |  |  | 7156 |  |  |  | 1600 | [10 empty] | 96.28 |  |  |  | 96.85 | [5 empty] | 88.76 |  |  | 98.57 |  |  |  | 2.19 |  | 2.17 | [8 empty] | 0.98 |  |  |  |  | 0.57
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2023 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 1572 | [14 empty] | 5849
E. |  | Testing of plant systems or components | [24 empty] | 30 | [14 empty] | 45
Z. |  | Other | [39 empty] | 3590
Subtotal | [26 empty] | 1602 | [14 empty] | 9484
Total | [22 empty] | 1602 | [14 empty] | 9484
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2023 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 916 | [14 empty] | 500
12. |  |  | Reactor I&C Systems | [34 empty] | 60
31. |  |  | Turbine and auxiliaries | [34 empty] | 197
32. |  |  | Feedwater and Main Steam System | [19 empty] | 602 | [14 empty] | 1324
41. |  |  | Main Generator Systems | [19 empty] | 53 | [14 empty] | 47
42. |  |  | Electrical Power Supply Systems | [19 empty] | 30 | [14 empty] | 16
Total | [22 empty] | 1601 | [14 empty] | 2144
Highlights (2023)
The electricity production of the Olkiluoto power plant units OL1, OL2 and OL3 during 2023 was 24,671 GWh. OL3's net production was 10,372 GWh. OL3 plant unit commissioning phase continued until January 10, when cold shutdown started due to feedwater pumps inspections. Cold shutdown due to feedwater pumps inspections and replacement of impellers ended February 5. February 12 the plant unit decided to run in cold shutdown due to inspections and maintenance of pressurizer valves. The maintenance works were completed in March 8th. Commissioning phase continued until April 16, when regular electricity production started. Commercial operation started May 1. The plant unit has produced electricity throughout the rest of the year expect for two turbine trips in November. The first happened on November 19 due to failure in temperature measurement of the generator cooling system. Production continued November 22. The second turbine trip happened on November 29 because of the near failure test. Production continued November 30. The power of the plant unit has been limited from time to time by the system protection, grid limitation and also low demand of electricity. The OL3 plant unit first annual outage starts on March 3, 2024.