## GENKAI-3
2023 Operating Experience
JP-45 | [8 empty] | GENKAI-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Owner | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (4-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1988-06-01
Thermal power | [12 empty] | : |  |  | 3423 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-06-15
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-03-18
Reference unit power (net) | [12 empty] | : |  |  | 1127 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 46 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.76
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8691.55 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.73 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.73 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 14.27 %
Load Factor (LF) | [18 empty] | : | 88.04 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 85.76 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1247 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 4.64 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 859.94 | 777.98 |  |  |  | 863.34 |  | 836.39 | [8 empty] | 864.11 |  |  | 834.74 | [6 empty] | 859.90 |  | 858.78 |  |  |  | 829.38 |  |  | 859.82 |  |  | 247.19 | [9 empty] | 0.00 |  |  | 8691.55
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 29.69 | [9 empty] | 0.00 |  |  | 85.73
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 29.69 | [9 empty] | 0.00 |  |  | 85.73
LF [%] |  |  |  |  | 102.56 | 102.72 |  |  |  | 102.96 |  | 103.07 | [8 empty] | 103.06 |  |  | 102.87 | [6 empty] | 102.55 |  | 102.42 |  |  |  | 102.21 |  |  | 102.54 |  |  | 30.46 | [9 empty] | 0.00 |  |  | 88.04
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 30.14 | [9 empty] | 0.00 |  |  | 85.76
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 70.31 | [9 empty] | 100.00 |  |  | 14.27
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 192671.9 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.29 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 62.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.18 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 62.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 37.52 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 63.31 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 62.56 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 8795.82 |  |  | 7828 |  |  |  | 1127 | [10 empty] | 96.91 |  |  |  | 96.91 | [5 empty] | 97.39 |  |  | 97.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.09 |  |  |  |  | 0.00
1995 |  |  |  | 7356.33 |  |  | 6588 |  |  |  | 1127 | [10 empty] | 74.14 |  |  |  | 74.14 | [5 empty] | 74.51 |  |  | 75.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.86 |  |  |  |  | 0.00
1996 |  |  |  | 7444.90 |  |  | 6663 |  |  |  | 1127 | [10 empty] | 74.86 |  |  |  | 74.86 | [5 empty] | 75.20 |  |  | 75.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.14 |  |  |  |  | 0.00
1997 |  |  |  | 8259.94 |  |  | 7358 |  |  |  | 1127 | [10 empty] | 83.29 |  |  |  | 83.29 | [5 empty] | 83.67 |  |  | 84.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.71 |  |  |  |  | 0.00
1998 |  |  |  | 9633.13 |  |  | 8514 |  |  |  | 1127 | [10 empty] | 97.14 |  |  |  | 97.14 | [5 empty] | 97.58 |  |  | 97.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.86 |  |  |  |  | 0.00
1999 |  |  |  | 7999.83 |  |  | 7068 |  |  |  | 1127 | [10 empty] | 80.67 |  |  |  | 80.67 | [5 empty] | 81.03 |  |  | 80.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.33 |  |  |  |  | 0.00
2000 |  |  |  | 8109.74 |  |  | 7164 |  |  |  | 1127 | [10 empty] | 81.55 |  |  |  | 81.55 | [5 empty] | 81.92 |  |  | 81.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.45 |  |  |  |  | 0.00
2001 |  |  |  | 8205.05 |  |  | 7249 |  |  |  | 1127 | [10 empty] | 82.74 |  |  |  | 82.74 | [5 empty] | 83.11 |  |  | 82.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.26 |  |  |  |  | 0.00
2002 |  |  |  | 9561.54 |  |  | 8446 |  |  |  | 1127 | [10 empty] | 96.40 |  |  |  | 96.40 | [5 empty] | 96.85 |  |  | 96.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.60 |  |  |  |  | 0.00
2003 |  |  |  | 8667.78 |  |  | 7497 |  |  |  | 1127 | [10 empty] | 85.59 |  |  |  | 85.59 | [5 empty] | 87.80 |  |  | 85.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.41 |  |  |  |  | 0.00
2004 |  |  |  | 8121.12 |  |  | 7015 |  |  |  | 1127 | [10 empty] | 79.87 |  |  |  | 79.87 | [5 empty] | 82.04 |  |  | 79.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.13 |  |  |  |  | 0.00
2005 |  |  |  | 8658.87 |  |  | 7523 |  |  |  | 1127 | [10 empty] | 85.32 |  |  |  | 85.32 | [5 empty] | 87.71 |  |  | 85.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.68 |  |  |  |  | 0.00
2006 |  |  |  | 9725.17 |  |  | 8401 |  |  |  | 1127 | [10 empty] | 95.86 |  |  |  | 95.86 | [5 empty] | 98.51 |  |  | 95.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.14 |  |  |  |  | 0.00
2007 |  |  |  | 7988.29 |  |  | 6987 |  |  |  | 1127 | [10 empty] | 79.11 |  |  |  | 79.11 | [5 empty] | 80.91 |  |  | 79.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.89 |  |  |  |  | 0.00
2008 |  |  |  | 8259.64 |  |  | 7211 |  |  |  | 1127 | [10 empty] | 81.57 |  |  |  | 81.57 | [5 empty] | 83.43 |  |  | 82.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.43 |  |  |  |  | 0.00
2009 |  |  |  | 8061.86 |  |  | 7043 |  |  |  | 1127 | [10 empty] | 79.87 |  |  |  | 79.87 | [5 empty] | 81.66 |  |  | 80.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.13 |  |  |  |  | 0.00
2010 |  |  |  | 9506.52 |  |  | 8257 |  |  |  | 1127 | [10 empty] | 94.22 |  |  |  | 94.22 | [5 empty] | 96.29 |  |  | 94.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.78 |  |  |  |  | 0.00
2011 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 7143.28 |  |  | 6313 |  |  |  | 1127 | [10 empty] | 70.82 |  |  |  | 70.82 | [5 empty] | 72.36 |  |  | 72.07 |  |  |  | 7.13 |  | 5.44 | [8 empty] | 23.74 |  |  |  |  | 0.00
2019 |  |  |  | 8106.36 |  |  | 7067 |  |  |  | 1127 | [10 empty] | 80.14 |  |  |  | 80.14 | [5 empty] | 82.11 |  |  | 80.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.86 |  |  |  |  | 0.00
2020 |  |  |  | 8236.08 |  |  | 7187 |  |  |  | 1127 | [10 empty] | 81.29 |  |  |  | 81.29 | [5 empty] | 83.20 |  |  | 81.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.71 |  |  |  |  | 0.00
2021 |  |  |  | 10083.48 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.14 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2022 |  |  |  | 1036.79 |  |  | 946 |  |  |  | 1127 | [10 empty] | 10.34 |  |  |  | 10.34 | [5 empty] | 10.50 |  |  | 10.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 89.66 |  |  |  |  | 0.00
2023 |  |  |  | 8691.55 |  |  | 7513 |  |  |  | 1127 | [10 empty] | 85.73 |  |  |  | 85.73 | [5 empty] | 88.04 |  |  | 85.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.27 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1994 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 15
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1247 | [14 empty] | 1219
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 2052
Subtotal | [22 empty] | 1247 | [14 empty] | 3271 |  |  |  | 15
Total | [22 empty] | 1247 | [14 empty] | 3286
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1994 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
Total | [37 empty] | 15

## GENKAI-4
2023 Operating Experience
JP-46 | [8 empty] | GENKAI-4 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Owner | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (4-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1992-07-15
Thermal power | [12 empty] | : |  |  | 3423 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1996-11-12
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1997-07-25
Reference unit power (net) | [12 empty] | : |  |  | 1127 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 27 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.39
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 46 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.76
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8916.52 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.72 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.72 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.28 %
Load Factor (LF) | [18 empty] | : | 90.32 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 89.14 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 951 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0.81 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 486.71 |  |  |  | 854.64 |  | 829.31 | [8 empty] | 857.01 |  |  | 828.47 | [6 empty] | 852.64 |  | 851.15 |  |  |  | 822.86 |  |  | 853.56 |  |  | 825.54 | [9 empty] | 854.62 |  |  | 8916.51
EAF [%] |  |  |  |  | 0.00 | 63.66 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.72
UCF [%] |  |  |  |  | 0.00 | 63.66 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.72
LF [%] |  |  |  |  | 0.00 | 64.27 |  |  |  | 101.93 |  | 102.20 | [8 empty] | 102.21 |  |  | 102.10 | [6 empty] | 101.69 |  | 101.51 |  |  |  | 101.41 |  |  | 101.80 |  |  | 101.74 | [9 empty] | 101.92 |  |  | 90.32
OF [%] |  |  |  |  | 0.00 | 69.20 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.14
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 100.00 | 36.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 11.28
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 170555.18 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.96 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 63.63 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.62 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 63.63 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 35.75 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 64.55 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 63.91 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1997 |  |  |  | 5841.01 |  |  | 5901 |  |  |  | 1127 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.73 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1998 |  |  |  | 7634.53 |  |  | 6783 |  |  |  | 1127 | [10 empty] | 76.75 |  |  |  | 76.75 | [5 empty] | 77.33 |  |  | 77.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.25 |  |  |  |  | 0.00
1999 |  |  |  | 9716.30 |  |  | 8559 |  |  |  | 1127 | [10 empty] | 97.69 |  |  |  | 97.69 | [5 empty] | 98.42 |  |  | 97.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.31 |  |  |  |  | 0.00
2000 |  |  |  | 8181.18 |  |  | 7205 |  |  |  | 1127 | [10 empty] | 82.02 |  |  |  | 82.02 | [5 empty] | 82.64 |  |  | 82.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.98 |  |  |  |  | 0.00
2001 |  |  |  | 8107.23 |  |  | 7142 |  |  |  | 1127 | [10 empty] | 81.51 |  |  |  | 81.51 | [5 empty] | 82.12 |  |  | 81.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.49 |  |  |  |  | 0.00
2002 |  |  |  | 8208.29 |  |  | 7217 |  |  |  | 1127 | [10 empty] | 82.37 |  |  |  | 82.37 | [5 empty] | 83.14 |  |  | 82.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.63 |  |  |  |  | 0.00
2003 |  |  |  | 9678.75 |  |  | 8422 |  |  |  | 1127 | [10 empty] | 96.12 |  |  |  | 96.12 | [5 empty] | 98.04 |  |  | 96.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.88 |  |  |  |  | 0.00
2004 |  |  |  | 8330.56 |  |  | 7243 |  |  |  | 1127 | [10 empty] | 82.44 |  |  |  | 82.44 | [5 empty] | 84.15 |  |  | 82.46 |  |  |  | 4.05 |  | 3.48 | [8 empty] | 14.09 |  |  |  |  | 0.00
2005 |  |  |  | 8572.52 |  |  | 7499 |  |  |  | 1127 | [10 empty] | 85.04 |  |  |  | 85.04 | [5 empty] | 86.83 |  |  | 85.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.96 |  |  |  |  | 0.00
2006 |  |  |  | 7765.58 |  |  | 6813 |  |  |  | 1127 | [10 empty] | 76.97 |  |  |  | 76.97 | [5 empty] | 78.66 |  |  | 77.77 |  |  |  | 3.64 |  | 2.91 | [8 empty] | 20.12 |  |  |  |  | 0.00
2007 |  |  |  | 10025.27 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.55 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2008 |  |  |  | 7695.98 |  |  | 6797 |  |  |  | 1127 | [10 empty] | 76.61 |  |  |  | 76.61 | [5 empty] | 77.74 |  |  | 77.38 |  |  |  | 2.15 |  | 1.69 | [8 empty] | 21.71 |  |  |  |  | 0.00
2009 |  |  |  | 8325.59 |  |  | 7331 |  |  |  | 1127 | [10 empty] | 83.07 |  |  |  | 83.07 | [5 empty] | 84.33 |  |  | 83.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.93 |  |  |  |  | 0.00
2010 |  |  |  | 8365.65 |  |  | 7355 |  |  |  | 1127 | [10 empty] | 83.43 |  |  |  | 83.43 | [5 empty] | 84.74 |  |  | 83.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.57 |  |  |  |  | 0.00
2011 |  |  |  | 8999.40 |  |  | 7918 |  |  |  | 1127 | [10 empty] | 90.09 |  |  |  | 90.09 | [5 empty] | 91.16 |  |  | 90.39 |  |  |  | 8.35 |  | 8.21 | [8 empty] | 1.70 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 5269.18 |  |  | 4706 |  |  |  | 1127 | [10 empty] | 52.56 |  |  |  | 52.56 | [5 empty] | 53.37 |  |  | 53.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 47.44 |  |  |  |  | 0.00
2019 |  |  |  | 8067.74 |  |  | 7091 |  |  |  | 1127 | [10 empty] | 80.41 |  |  |  | 80.41 | [5 empty] | 81.72 |  |  | 80.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.59 |  |  |  |  | 0.00
2020 |  |  |  | 9703.45 |  |  | 8473 |  |  |  | 1127 | [10 empty] | 96.42 |  |  |  | 96.42 | [5 empty] | 98.02 |  |  | 96.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.58 |  |  |  |  | 0.00
2021 |  |  |  | 7840.45 |  |  | 6897 |  |  |  | 1127 | [10 empty] | 78.22 |  |  |  | 78.22 | [5 empty] | 79.42 |  |  | 78.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.78 |  |  |  |  | 0.00
2022 |  |  |  | 4888.76 |  |  | 4319 |  |  |  | 1127 | [10 empty] | 48.81 |  |  |  | 48.81 | [5 empty] | 49.52 |  |  | 49.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 51.19 |  |  |  |  | 0.00
2023 |  |  |  | 8916.51 |  |  | 7809 |  |  |  | 1127 | [10 empty] | 88.72 |  |  |  | 88.72 | [5 empty] | 90.32 |  |  | 89.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.28 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1997 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 52
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 951 | [14 empty] | 1087
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 2079
Subtotal | [22 empty] | 951 | [14 empty] | 3166 |  |  |  | 52
Total | [22 empty] | 951 | [14 empty] | 3218
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1997 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 9
31. |  |  | Turbine and auxiliaries | [34 empty] | 27
41. |  |  | Main Generator Systems | [34 empty] | 17
Total | [37 empty] | 53

## IKATA-3
2023 Operating Experience
JP-47 | [8 empty] | IKATA-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | SHIKOKU (SHIKOKU ELECTRIC POWER CO., INC)
Owner | [7 empty] | : | SHIKOKU (SHIKOKU ELECTRIC POWER CO., INC)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1990-10-01
Thermal power | [12 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1994-03-29
Gross electrical power | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1994-12-15
Reference unit power (net) | [12 empty] | : |  |  | 846 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 29 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.283
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 48000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.1
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS / DS
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5715.39 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.24 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.33 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.24 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 25.43 %
Load Factor (LF) | [18 empty] | : | 77.12 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 74.53 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2231 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 1.57 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 656.22 | 463.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 83.38 |  |  | 635.49 | [6 empty] | 655.42 |  | 651.62 |  |  |  | 628.83 |  |  | 651.09 |  |  | 632.78 | [9 empty] | 656.56 |  |  | 5715.39
EAF [%] |  |  |  |  | 100.00 | 78.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.08 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 74.24
UCF [%] |  |  |  |  | 100.00 | 78.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.08 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 74.24
LF [%] |  |  |  |  | 104.26 | 81.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.25 |  |  | 104.33 | [6 empty] | 104.13 |  | 103.53 |  |  |  | 103.24 |  |  | 103.44 |  |  | 103.88 | [9 empty] | 104.31 |  |  | 77.12
OF [%] |  |  |  |  | 100.00 | 78.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.26 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 74.53
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.83 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.33
PUF [%] |  |  |  |  | 0.00 | 21.68 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 83.09 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 25.43
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 139484.58 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.72 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 65.66 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 65.66 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 33.63 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 64.8 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 63.04 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1994 |  |  |  | 2195.52 |  |  | 3669 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.17 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 7491.81 |  |  | 8760 |  |  |  | 846 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 101.09 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1996 |  |  |  | 5578.21 |  |  | 6621 |  |  |  | 846 | [10 empty] | 74.23 |  |  |  | 74.23 | [5 empty] | 75.06 |  |  | 75.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.76 |  |  |  |  | 0.00
1997 |  |  |  | 6134.74 |  |  | 7242 |  |  |  | 846 | [10 empty] | 81.87 |  |  |  | 81.87 | [5 empty] | 82.78 |  |  | 82.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.13 |  |  |  |  | 0.00
1998 |  |  |  | 6250.38 |  |  | 7374 |  |  |  | 846 | [10 empty] | 83.43 |  |  |  | 83.43 | [5 empty] | 84.34 |  |  | 84.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.57 |  |  |  |  | 0.00
1999 |  |  |  | 6298.35 |  |  | 7368 |  |  |  | 846 | [10 empty] | 84.09 |  |  |  | 84.09 | [5 empty] | 84.99 |  |  | 84.11 |  |  |  | 3.16 |  | 2.74 | [8 empty] | 13.17 |  |  |  |  | 0.00
2000 |  |  |  | 6660.35 |  |  | 7790 |  |  |  | 846 | [10 empty] | 88.68 |  |  |  | 88.68 | [5 empty] | 89.63 |  |  | 88.68 |  |  |  | 10.78 |  | 10.71 | [8 empty] | 0.61 |  |  |  |  | 0.00
2001 |  |  |  | 6210.74 |  |  | 7267 |  |  |  | 846 | [10 empty] | 82.94 |  |  |  | 82.94 | [5 empty] | 83.80 |  |  | 82.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.06 |  |  |  |  | 0.00
2002 |  |  |  | 6599.51 |  |  | 7518 |  |  |  | 846 | [10 empty] | 85.82 |  |  |  | 85.82 | [5 empty] | 89.05 |  |  | 85.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.18 |  |  |  |  | 0.00
2003 |  |  |  | 5862.10 |  |  | 6560 |  |  |  | 846 | [10 empty] | 74.86 |  |  |  | 74.86 | [5 empty] | 79.10 |  |  | 74.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.14 |  |  |  |  | 0.00
2004 |  |  |  | 7828.92 |  |  | 8784 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.35 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2005 |  |  |  | 6699.37 |  |  | 7637 |  |  |  | 846 | [10 empty] | 86.84 |  |  |  | 86.84 | [5 empty] | 90.40 |  |  | 87.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.16 |  |  |  |  | 0.00
2006 |  |  |  | 6134.56 |  |  | 6990 |  |  |  | 846 | [10 empty] | 79.53 |  |  |  | 79.53 | [5 empty] | 82.78 |  |  | 79.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.47 |  |  |  |  | 0.00
2007 |  |  |  | 6869.33 |  |  | 7813 |  |  |  | 846 | [10 empty] | 88.88 |  |  |  | 88.88 | [5 empty] | 92.69 |  |  | 89.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.12 |  |  |  |  | 0.00
2008 |  |  |  | 6392.97 |  |  | 7282 |  |  |  | 846 | [10 empty] | 82.57 |  |  |  | 82.57 | [5 empty] | 86.03 |  |  | 82.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.43 |  |  |  |  | 0.00
2009 |  |  |  | 7716.65 |  |  | 8760 |  |  |  | 846 | [10 empty] | 99.96 |  |  |  | 99.96 | [5 empty] | 104.12 |  |  | 100.00 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 6490.71 |  |  | 7410 |  |  |  | 846 | [10 empty] | 84.34 |  |  |  | 84.34 | [5 empty] | 87.58 |  |  | 84.59 |  |  |  | 0.00 |  | 1.71 | [8 empty] | 13.95 |  |  |  |  | 0.00
2011 |  |  |  | 2511.01 |  |  | 2852 |  |  |  | 846 | [10 empty] | 32.58 |  |  |  | 32.58 | [5 empty] | 33.88 |  |  | 32.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 67.42 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.06 |  |  |  | 0.06 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 99.94 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 2848.03 |  |  | 3322 |  |  |  | 846 | [10 empty] | 37.02 |  |  |  | 37.02 | [5 empty] | 38.32 |  |  | 37.82 |  |  |  | 0.00 |  | 4.53 | [8 empty] | 58.45 |  |  |  |  | 0.00
2017 |  |  |  | 5802.18 |  |  | 6600 |  |  |  | 846 | [10 empty] | 75.32 |  |  |  | 75.32 | [5 empty] | 78.29 |  |  | 75.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.68 |  |  |  |  | 0.00
2018 |  |  |  | 1306.34 |  |  | 1511 |  |  |  | 846 | [10 empty] | 99.72 |  |  |  | 99.72 | [5 empty] | 17.63 |  |  | 17.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.28 |  |  |  |  | 0.00
2019 |  |  |  | 7570.95 |  |  | 8616 |  |  |  | 846 | [10 empty] | 98.34 |  |  |  | 98.34 | [5 empty] | 102.16 |  |  | 98.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.66 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2021 |  |  |  | 468.08 |  |  | 606 |  |  |  | 846 | [10 empty] | 6.29 |  |  |  | 6.29 | [5 empty] | 6.32 |  |  | 6.92 |  |  |  | 5.33 |  | 0.35 | [8 empty] | 93.36 |  |  |  |  | 0.00
2022 |  |  |  | 7695.11 |  |  | 8760 |  |  |  | 846 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 103.83 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2023 |  |  |  | 5715.39 |  |  | 6529 |  |  |  | 846 | [10 empty] | 74.24 |  |  |  | 74.24 | [5 empty] | 77.12 |  |  | 74.53 |  |  |  | 0.00 |  | 0.33 | [8 empty] | 25.43 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1994 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 5 | [14 empty] | 42
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2203 | [14 empty] | 1452
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 1594
L. |  | Human factor related | [24 empty] | 24 | [14 empty] | 1
M. |  | Governmental requirements or court decisions | [51 empty] | 259
Z. |  | Other | [39 empty] | 20
Subtotal | [22 empty] | 2203 |  |  |  | 29 | [10 empty] | 3046 |  |  |  | 63 | [11 empty] | 259
Total | [22 empty] | 2232 | [14 empty] | 3368
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1994 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 24 | [14 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 14
41. |  |  | Main Generator Systems | [19 empty] | 5 | [14 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 34
Total | [22 empty] | 29 | [14 empty] | 58
Highlights (2023)
Operation at full power in base load mode Conduct the 16th periodical inspection of Ikata Unit 3

## MIHAMA-3
2023 Operating Experience
JP-14 | [8 empty] | MIHAMA-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-08-07
Thermal power | [12 empty] | : |  |  | 2440 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-02-19
Gross electrical power | [12 empty] | : |  |  | 826 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-12-01
Reference unit power (net) | [12 empty] | : |  |  | 780 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.24
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.0 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.64 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5823.48 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.44 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 81.44 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 18.56 %
Load Factor (LF) | [18 empty] | : | 85.23 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 81.5 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1621 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 611.33 | 551.85 |  |  |  | 611.10 |  | 591.36 | [8 empty] | 610.87 |  |  | 589.38 | [6 empty] | 603.16 |  | 599.57 |  |  |  | 581.02 |  |  | 473.84 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 5823.48
EAF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 100.00 |  |  | 78.30 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 81.44
UCF [%] |  |  |  |  | 100.00 | 99.99 |  |  |  | 100.00 |  | 99.99 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 100.00 |  |  | 78.30 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 81.44
LF [%] |  |  |  |  | 105.34 | 105.28 |  |  |  | 105.30 |  | 105.30 | [8 empty] | 105.26 |  |  | 104.95 | [6 empty] | 103.94 |  | 103.32 |  |  |  | 103.46 |  |  | 81.65 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 85.23
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 78.90 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 81.50
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.01 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 0.00 |  |  | 21.70 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 18.56
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 179228.41 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.79 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 54.98 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.37 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 54.99 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 43.64 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 55.67 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 55.7 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | 2615.00 |  |  | 5285 |  |  |  | 780 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 85.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.90 |  |  |  |  | 0.00
1977 |  |  |  | 4498.50 |  |  | 6159 |  |  |  | 780 | [10 empty] | 65.85 |  |  |  | 65.85 | [5 empty] | 65.84 |  |  | 70.31 |  |  |  | 1.27 |  | 0.85 | [8 empty] | 33.31 |  |  |  |  | 0.00
1978 |  |  |  | 4166.60 |  |  | 5537 |  |  |  | 780 | [10 empty] | 59.52 |  |  |  | 59.52 | [5 empty] | 60.98 |  |  | 63.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 40.48 |  |  |  |  | 0.00
1979 |  |  |  | 1697.40 |  |  | 2307 |  |  |  | 780 | [10 empty] | 24.85 |  |  |  | 24.85 | [5 empty] | 24.84 |  |  | 26.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 75.15 |  |  |  |  | 0.00
1980 |  |  |  | 4597.70 |  |  | 5964 |  |  |  | 780 | [10 empty] | 67.00 |  |  |  | 67.00 | [5 empty] | 67.10 |  |  | 67.90 |  |  |  | 1.17 |  | 0.79 | [8 empty] | 32.21 |  |  |  |  | 0.00
1981 |  |  |  | 5832.90 |  |  | 7607 |  |  |  | 780 | [10 empty] | 85.16 |  |  |  | 85.16 | [5 empty] | 85.37 |  |  | 86.84 |  |  |  | 0.33 |  | 0.28 | [8 empty] | 14.55 |  |  |  |  | 0.00
1982 |  |  |  | 5239.10 |  |  | 6952 |  |  |  | 780 | [10 empty] | 76.38 |  |  |  | 76.38 | [5 empty] | 76.68 |  |  | 79.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.62 |  |  |  |  | 0.00
1983 |  |  |  | 4818.00 |  |  | 6330 |  |  |  | 780 | [10 empty] | 70.63 |  |  |  | 70.63 | [5 empty] | 70.51 |  |  | 72.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.37 |  |  |  |  | 0.00
1984 |  |  |  | 5353.73 |  |  | 6906 |  |  |  | 780 | [10 empty] | 77.82 |  |  |  | 77.82 | [5 empty] | 78.14 |  |  | 78.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.18 |  |  |  |  | 0.00
1985 |  |  |  | 4971.94 |  |  | 6426 |  |  |  | 780 | [10 empty] | 72.65 |  |  |  | 72.65 | [5 empty] | 72.77 |  |  | 73.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.35 |  |  |  |  | 0.00
1986 |  |  |  | 6848.35 |  |  | 8760 |  |  |  | 780 | [10 empty] | 99.78 |  |  |  | 99.78 | [5 empty] | 100.23 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.22 |  |  |  |  | 0.00
1987 |  |  |  | 4822.71 |  |  | 6268 |  |  |  | 780 | [10 empty] | 71.55 |  |  |  | 71.55 | [5 empty] | 70.58 |  |  | 71.55 |  |  |  | 3.89 |  | 2.90 | [8 empty] | 25.55 |  |  |  |  | 0.00
1988 |  |  |  | 4261.32 |  |  | 5625 |  |  |  | 780 | [10 empty] | 64.04 |  |  |  | 64.04 | [5 empty] | 62.20 |  |  | 64.04 |  |  |  | 5.10 |  | 3.44 | [8 empty] | 32.53 |  |  |  |  | 0.00
1989 |  |  |  | 5299.69 |  |  | 6834 |  |  |  | 780 | [10 empty] | 78.01 |  |  |  | 78.01 | [5 empty] | 77.56 |  |  | 78.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.99 |  |  |  |  | 0.00
1990 |  |  |  | 6867.04 |  |  | 8760 |  |  |  | 780 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 100.50 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
1991 |  |  |  | 4246.18 |  |  | 5495 |  |  |  | 780 | [10 empty] | 59.68 |  |  |  | 59.68 | [5 empty] | 62.14 |  |  | 62.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 40.32 |  |  |  |  | 0.00
1992 |  |  |  | 4709.88 |  |  | 6095 |  |  |  | 780 | [10 empty] | 68.54 |  |  |  | 68.54 | [5 empty] | 68.74 |  |  | 69.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.46 |  |  |  |  | 0.00
1993 |  |  |  | 4526.62 |  |  | 5951 |  |  |  | 780 | [10 empty] | 66.11 |  |  |  | 66.42 | [5 empty] | 66.25 |  |  | 67.93 |  |  |  | 0.74 |  | 0.50 | [8 empty] | 33.08 |  |  |  |  | 0.31
1994 |  |  |  | 6623.04 |  |  | 8486 |  |  |  | 780 | [10 empty] | 96.81 |  |  |  | 96.83 | [5 empty] | 96.93 |  |  | 96.87 |  |  |  | 1.78 |  | 1.76 | [8 empty] | 1.42 |  |  |  |  | 0.01
1995 |  |  |  | 3389.17 |  |  | 4534 |  |  |  | 780 | [10 empty] | 49.61 |  |  |  | 49.74 | [5 empty] | 49.60 |  |  | 51.76 |  |  |  | 21.69 |  | 13.77 | [8 empty] | 36.49 |  |  |  |  | 0.13
1996 |  |  |  | 4491.42 |  |  | 5760 |  |  |  | 780 | [10 empty] | 65.30 |  |  |  | 65.50 | [5 empty] | 65.55 |  |  | 65.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 34.50 |  |  |  |  | 0.19
1997 |  |  |  | 6262.81 |  |  | 7963 |  |  |  | 780 | [10 empty] | 91.24 |  |  |  | 91.24 | [5 empty] | 91.66 |  |  | 90.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.76 |  |  |  |  | 0.00
1998 |  |  |  | 5979.86 |  |  | 7788 |  |  |  | 780 | [10 empty] | 87.10 |  |  |  | 87.10 | [5 empty] | 87.52 |  |  | 88.90 |  |  |  | 1.39 |  | 1.23 | [8 empty] | 11.66 |  |  |  |  | 0.00
1999 |  |  |  | 5795.30 |  |  | 7398 |  |  |  | 780 | [10 empty] | 84.44 |  |  |  | 84.44 | [5 empty] | 84.82 |  |  | 84.45 |  |  |  | 3.45 |  | 3.01 | [8 empty] | 12.54 |  |  |  |  | 0.00
2000 |  |  |  | 4784.98 |  |  | 6117 |  |  |  | 780 | [10 empty] | 69.60 |  |  |  | 69.61 | [5 empty] | 69.84 |  |  | 69.64 |  |  |  | 15.88 |  | 13.15 | [8 empty] | 17.25 |  |  |  |  | 0.00
2001 |  |  |  | 6853.68 |  |  | 8760 |  |  |  | 780 | [10 empty] | 99.96 |  |  |  | 99.99 | [5 empty] | 100.31 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.03
2002 |  |  |  | 5248.01 |  |  | 6732 |  |  |  | 780 | [10 empty] | 76.84 |  |  |  | 76.84 | [5 empty] | 76.81 |  |  | 76.85 |  |  |  | 5.19 |  | 4.21 | [8 empty] | 18.95 |  |  |  |  | 0.00
2003 |  |  |  | 6111.49 |  |  | 7701 |  |  |  | 780 | [10 empty] | 87.91 |  |  |  | 87.91 | [5 empty] | 89.44 |  |  | 87.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.09 |  |  |  |  | 0.00
2004 |  |  |  | 4301.26 |  |  | 5319 |  |  |  | 780 | [10 empty] | 60.48 |  |  |  | 60.48 | [5 empty] | 62.78 |  |  | 60.55 |  |  |  | 2.06 |  | 13.02 | [8 empty] | 26.50 |  |  |  |  | 0.00
2005 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2006 |  |  |  | 92.08 |  |  | 181 |  |  |  | 780 | [10 empty] | 1.35 |  |  |  | 1.35 | [5 empty] | 1.35 |  |  | 2.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 98.65 |  |  |  |  | 0.00
2007 |  |  |  | 4943.91 |  |  | 6190 |  |  |  | 780 | [10 empty] | 69.45 |  |  |  | 69.45 | [5 empty] | 72.36 |  |  | 70.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.55 |  |  |  |  | 0.00
2008 |  |  |  | 5725.55 |  |  | 7049 |  |  |  | 780 | [10 empty] | 79.72 |  |  |  | 79.72 | [5 empty] | 83.57 |  |  | 80.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.28 |  |  |  |  | 0.00
2009 |  |  |  | 6795.53 |  |  | 8315 |  |  |  | 780 | [10 empty] | 94.86 |  |  |  | 94.86 | [5 empty] | 99.45 |  |  | 94.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.14 |  |  |  |  | 0.00
2010 |  |  |  | 5541.00 |  |  | 6823 |  |  |  | 780 | [10 empty] | 77.39 |  |  |  | 77.39 | [5 empty] | 81.09 |  |  | 77.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.61 |  |  |  |  | 0.00
2011 |  |  |  | 2637.14 |  |  | 3203 |  |  |  | 780 | [10 empty] | 36.51 |  |  |  | 36.51 | [5 empty] | 38.60 |  |  | 36.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 63.49 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2021 |  |  |  | 2211.25 |  |  | 2804 |  |  |  | 780 | [10 empty] | 31.12 |  |  |  | 31.12 | [5 empty] | 32.36 |  |  | 32.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 68.88 |  |  |  |  | 0.00
2022 |  |  |  | 2343.68 |  |  | 2908 |  |  |  | 780 | [10 empty] | 32.70 |  |  |  | 32.70 | [5 empty] | 34.30 |  |  | 33.20 |  |  |  | 0.00 |  | 5.48 | [8 empty] | 61.82 |  |  |  |  | 0.00
2023 |  |  |  | 5823.48 |  |  | 7139 |  |  |  | 780 | [10 empty] | 81.44 |  |  |  | 81.44 | [5 empty] | 85.23 |  |  | 81.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.56 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1976 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 103
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1621 | [14 empty] | 2012
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 3
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 1764
L. |  | Human factor related | [39 empty] | 6
Subtotal | [22 empty] | 1621 | [14 empty] | 3776 |  |  |  | 112
Total | [22 empty] | 1621 | [14 empty] | 3888
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1976 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 23
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 23
32. |  |  | Feedwater and Main Steam System | [34 empty] | 43
34. |  |  | Miscellaneous Systems | [34 empty] | 3
Total | [37 empty] | 110

## OHI-3
2023 Operating Experience
JP-50 | [8 empty] | OHI-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (4-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1987-10-03
Thermal power | [12 empty] | : |  |  | 3423 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1991-06-07
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1991-12-18
Reference unit power (net) | [12 empty] | : |  |  | 1127 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 32 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 10162.58 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 100 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 102.94 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 16.83 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 870.37 | 788.49 |  |  |  | 874.43 |  | 843.27 | [8 empty] | 868.57 |  |  | 834.25 | [6 empty] | 852.24 |  | 848.02 |  |  |  | 819.93 |  |  | 856.82 |  |  | 836.37 | [9 empty] | 869.80 |  |  | 10162.58
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 103.80 | 104.11 |  |  |  | 104.29 |  | 103.92 | [8 empty] | 103.59 |  |  | 102.81 | [6 empty] | 101.64 |  | 101.14 |  |  |  | 101.05 |  |  | 102.19 |  |  | 103.07 | [9 empty] | 103.73 |  |  | 102.94
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 211335.37 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.82 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 65.73 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.22 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 65.75 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 30.03 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 66.71 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.02 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 66.03 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1991 |  |  |  | 2524.41 |  |  | 3228 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1992 |  |  |  | 9954.69 |  |  | 8784 |  |  |  | 1127 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 100.56 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
1993 |  |  |  | 7863.69 |  |  | 7025 |  |  |  | 1127 | [10 empty] | 79.43 |  |  |  | 79.43 | [5 empty] | 79.65 |  |  | 80.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.57 |  |  |  |  | 0.00
1994 |  |  |  | 8139.08 |  |  | 7265 |  |  |  | 1127 | [10 empty] | 82.53 |  |  |  | 82.53 | [5 empty] | 82.44 |  |  | 82.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.47 |  |  |  |  | 0.00
1995 |  |  |  | 7701.72 |  |  | 6887 |  |  |  | 1127 | [10 empty] | 77.82 |  |  |  | 77.82 | [5 empty] | 78.01 |  |  | 78.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.18 |  |  |  |  | 0.00
1996 |  |  |  | 9957.45 |  |  | 8784 |  |  |  | 1127 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.58 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1997 |  |  |  | 8333.01 |  |  | 7385 |  |  |  | 1127 | [10 empty] | 83.88 |  |  |  | 83.88 | [5 empty] | 84.41 |  |  | 84.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.12 |  |  |  |  | 0.00
1998 |  |  |  | 8872.74 |  |  | 7867 |  |  |  | 1127 | [10 empty] | 89.30 |  |  |  | 89.30 | [5 empty] | 89.87 |  |  | 89.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.70 |  |  |  |  | 0.00
1999 |  |  |  | 8892.35 |  |  | 7875 |  |  |  | 1127 | [10 empty] | 89.52 |  |  |  | 89.89 | [5 empty] | 90.07 |  |  | 89.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.11 |  |  |  |  | 0.37
2000 |  |  |  | 8868.86 |  |  | 7824 |  |  |  | 1127 | [10 empty] | 89.06 |  |  |  | 89.06 | [5 empty] | 89.59 |  |  | 89.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.94 |  |  |  |  | 0.00
2001 |  |  |  | 8474.65 |  |  | 7481 |  |  |  | 1127 | [10 empty] | 85.38 |  |  |  | 85.38 | [5 empty] | 85.84 |  |  | 85.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.62 |  |  |  |  | 0.01
2002 |  |  |  | 9918.68 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.47 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2003 |  |  |  | 8683.19 |  |  | 7525 |  |  |  | 1127 | [10 empty] | 85.89 |  |  |  | 85.89 | [5 empty] | 87.95 |  |  | 85.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.11 |  |  |  |  | 0.00
2004 |  |  |  | 3040.18 |  |  | 2634 |  |  |  | 1127 | [10 empty] | 30.01 |  |  |  | 30.01 | [5 empty] | 30.71 |  |  | 29.99 |  |  |  | 0.00 |  | 59.84 | [8 empty] | 10.15 |  |  |  |  | 0.00
2005 |  |  |  | 7834.00 |  |  | 6968 |  |  |  | 1127 | [10 empty] | 77.64 |  |  |  | 77.64 | [5 empty] | 79.35 |  |  | 79.54 |  |  |  | 7.12 |  | 9.73 | [8 empty] | 12.63 |  |  |  |  | 0.00
2006 |  |  |  | 8012.30 |  |  | 7001 |  |  |  | 1127 | [10 empty] | 79.62 |  |  |  | 79.62 | [5 empty] | 81.16 |  |  | 79.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.38 |  |  |  |  | 0.00
2007 |  |  |  | 10080.14 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 102.10 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2008 |  |  |  | 2355.61 |  |  | 2081 |  |  |  | 1127 | [10 empty] | 23.36 |  |  |  | 23.36 | [5 empty] | 23.80 |  |  | 23.69 |  |  |  | 0.00 |  | 53.75 | [8 empty] | 22.90 |  |  |  |  | 0.00
2009 |  |  |  | 8335.16 |  |  | 7282 |  |  |  | 1127 | [10 empty] | 83.08 |  |  |  | 83.08 | [5 empty] | 84.43 |  |  | 83.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.92 |  |  |  |  | 0.00
2010 |  |  |  | 8297.03 |  |  | 7299 |  |  |  | 1127 | [10 empty] | 82.76 |  |  |  | 82.76 | [5 empty] | 84.04 |  |  | 83.32 |  |  |  | 11.51 |  | 10.76 | [8 empty] | 6.48 |  |  |  |  | 0.00
2011 |  |  |  | 2104.70 |  |  | 1834 |  |  |  | 1127 | [10 empty] | 20.89 |  |  |  | 20.89 | [5 empty] | 21.32 |  |  | 20.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 79.11 |  |  |  |  | 0.00
2012 |  |  |  | 4925.65 |  |  | 4325 |  |  |  | 1127 | [10 empty] | 48.78 |  |  |  | 48.78 | [5 empty] | 49.76 |  |  | 49.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 51.22 |  |  |  |  | 0.00
2013 |  |  |  | 6779.28 |  |  | 5879 |  |  |  | 1127 | [10 empty] | 66.75 |  |  |  | 67.10 | [5 empty] | 68.67 |  |  | 67.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.90 |  |  |  |  | 0.36
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 8009.80 |  |  | 6967 |  |  |  | 1127 | [10 empty] | 79.13 |  |  |  | 79.13 | [5 empty] | 81.13 |  |  | 79.53 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.87 |  |  |  |  | 0.00
2019 |  |  |  | 7928.91 |  |  | 6881 |  |  |  | 1127 | [10 empty] | 78.12 |  |  |  | 78.12 | [5 empty] | 80.31 |  |  | 78.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.88 |  |  |  |  | 0.00
2020 |  |  |  | 5627.87 |  |  | 4834 |  |  |  | 1127 | [10 empty] | 54.99 |  |  |  | 54.99 | [5 empty] | 56.85 |  |  | 55.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 45.01 |  |  |  |  | 0.00
2021 |  |  |  | 4866.36 |  |  | 4303 |  |  |  | 1127 | [10 empty] | 48.13 |  |  |  | 48.13 | [5 empty] | 49.29 |  |  | 49.12 |  |  |  | 1.32 |  | 0.64 | [8 empty] | 51.22 |  |  |  |  | 0.00
2022 |  |  |  | 6869.56 |  |  | 5943 |  |  |  | 1127 | [10 empty] | 67.48 |  |  |  | 67.48 | [5 empty] | 69.58 |  |  | 67.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.52 |  |  |  |  | 0.00
2023 |  |  |  | 10162.58 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 102.94 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1991 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 349
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 1128
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 658
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 919
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 30
Subtotal | [37 empty] | 2705 |  |  |  | 379
Total | [22 empty] | 0 | [14 empty] | 3084
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1991 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 210
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 152
Total | [37 empty] | 379

## OHI-4
2023 Operating Experience
JP-51 | [8 empty] | OHI-4 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (4-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1988-06-13
Thermal power | [12 empty] | : |  |  | 3423 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1992-06-19
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-02-02
Reference unit power (net) | [12 empty] | : |  |  | 1127 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 31 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 325
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 44000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.37 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 24
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 193 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 53 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8554.07 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.06 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 84.06 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.94 %
Load Factor (LF) | [18 empty] | : | 86.65 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 84.42 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1365 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 870.65 | 786.73 |  |  |  | 871.50 |  | 843.31 | [8 empty] | 867.82 |  |  | 833.89 | [6 empty] | 851.76 |  | 839.00 |  |  |  | 0.00 |  |  | 85.45 |  |  | 834.35 | [9 empty] | 869.61 |  |  | 8554.07
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 98.98 |  |  |  | 0.00 |  |  | 10.08 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.06
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 98.98 |  |  |  | 0.00 |  |  | 10.08 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.06
LF [%] |  |  |  |  | 103.84 | 103.88 |  |  |  | 103.94 |  | 103.93 | [8 empty] | 103.50 |  |  | 102.77 | [6 empty] | 101.58 |  | 100.06 |  |  |  | 0.00 |  |  | 10.19 |  |  | 102.82 | [9 empty] | 103.71 |  |  | 86.65
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.46 |  |  |  | 0.00 |  |  | 13.84 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.42
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 1.02 |  |  |  | 100.00 |  |  | 89.92 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.94
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 216888.2 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.98 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 69.79 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.51 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 69.8 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 28.69 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.01 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 70 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 9923.46 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 99.98 |  |  |  | 99.98 | [5 empty] | 100.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.02 |  |  |  |  | 0.00
1994 |  |  |  | 7851.52 |  |  | 7063 |  |  |  | 1127 | [10 empty] | 79.68 |  |  |  | 79.68 | [5 empty] | 79.53 |  |  | 80.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.32 |  |  |  |  | 0.00
1995 |  |  |  | 7495.11 |  |  | 6695 |  |  |  | 1127 | [10 empty] | 75.63 |  |  |  | 75.63 | [5 empty] | 75.92 |  |  | 76.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.37 |  |  |  |  | 0.00
1996 |  |  |  | 7051.09 |  |  | 6221 |  |  |  | 1127 | [10 empty] | 70.81 |  |  |  | 70.81 | [5 empty] | 71.23 |  |  | 70.82 |  |  |  | 16.12 |  | 13.61 | [8 empty] | 15.58 |  |  |  |  | 0.00
1997 |  |  |  | 7660.20 |  |  | 6756 |  |  |  | 1127 | [10 empty] | 77.10 |  |  |  | 77.10 | [5 empty] | 77.59 |  |  | 77.12 |  |  |  | 22.89 |  | 22.89 | [8 empty] | 0.01 |  |  |  |  | 0.00
1998 |  |  |  | 8839.42 |  |  | 7835 |  |  |  | 1127 | [10 empty] | 88.96 |  |  |  | 88.96 | [5 empty] | 89.54 |  |  | 89.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.04 |  |  |  |  | 0.00
1999 |  |  |  | 8903.44 |  |  | 7872 |  |  |  | 1127 | [10 empty] | 89.54 |  |  |  | 89.85 | [5 empty] | 90.18 |  |  | 89.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.15 |  |  |  |  | 0.31
2000 |  |  |  | 8649.77 |  |  | 7629 |  |  |  | 1127 | [10 empty] | 86.83 |  |  |  | 86.83 | [5 empty] | 87.38 |  |  | 86.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.17 |  |  |  |  | 0.00
2001 |  |  |  | 9283.56 |  |  | 8179 |  |  |  | 1127 | [10 empty] | 93.36 |  |  |  | 93.36 | [5 empty] | 94.03 |  |  | 93.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.64 |  |  |  |  | 0.00
2002 |  |  |  | 9217.09 |  |  | 8017 |  |  |  | 1127 | [10 empty] | 91.50 |  |  |  | 91.50 | [5 empty] | 93.36 |  |  | 91.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.50 |  |  |  |  | 0.00
2003 |  |  |  | 8762.57 |  |  | 7557 |  |  |  | 1127 | [10 empty] | 86.26 |  |  |  | 86.26 | [5 empty] | 88.76 |  |  | 86.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.74 |  |  |  |  | 0.00
2004 |  |  |  | 8318.19 |  |  | 7186 |  |  |  | 1127 | [10 empty] | 81.78 |  |  |  | 81.78 | [5 empty] | 84.03 |  |  | 81.81 |  |  |  | 7.44 |  | 6.57 | [8 empty] | 11.65 |  |  |  |  | 0.00
2005 |  |  |  | 9929.00 |  |  | 8657 |  |  |  | 1127 | [10 empty] | 98.77 |  |  |  | 98.77 | [5 empty] | 100.57 |  |  | 98.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.23 |  |  |  |  | 0.00
2006 |  |  |  | 8163.92 |  |  | 7087 |  |  |  | 1127 | [10 empty] | 80.66 |  |  |  | 80.66 | [5 empty] | 82.69 |  |  | 80.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.34 |  |  |  |  | 0.00
2007 |  |  |  | 7978.56 |  |  | 6934 |  |  |  | 1127 | [10 empty] | 78.87 |  |  |  | 78.87 | [5 empty] | 80.82 |  |  | 79.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.13 |  |  |  |  | 0.00
2008 |  |  |  | 7642.69 |  |  | 6654 |  |  |  | 1127 | [10 empty] | 75.41 |  |  |  | 75.41 | [5 empty] | 77.20 |  |  | 75.75 |  |  |  | 0.79 |  | 0.60 | [8 empty] | 23.98 |  |  |  |  | 0.00
2009 |  |  |  | 10097.36 |  |  | 8760 |  |  |  | 1127 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 102.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2010 |  |  |  | 6977.31 |  |  | 6109 |  |  |  | 1127 | [10 empty] | 69.41 |  |  |  | 69.41 | [5 empty] | 70.67 |  |  | 69.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.59 |  |  |  |  | 0.00
2011 |  |  |  | 5599.90 |  |  | 4872 |  |  |  | 1127 | [10 empty] | 55.56 |  |  |  | 55.56 | [5 empty] | 56.72 |  |  | 55.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 44.44 |  |  |  |  | 0.00
2012 |  |  |  | 4486.58 |  |  | 3941 |  |  |  | 1127 | [10 empty] | 44.41 |  |  |  | 44.41 | [5 empty] | 45.32 |  |  | 44.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 55.59 |  |  |  |  | 0.00
2013 |  |  |  | 7167.72 |  |  | 6191 |  |  |  | 1127 | [10 empty] | 70.67 |  |  |  | 70.67 | [5 empty] | 72.60 |  |  | 70.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.33 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 1127 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2018 |  |  |  | 6428.38 |  |  | 5623 |  |  |  | 1127 | [10 empty] | 63.79 |  |  |  | 63.79 | [5 empty] | 65.11 |  |  | 64.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.21 |  |  |  |  | 0.00
2019 |  |  |  | 8077.29 |  |  | 7011 |  |  |  | 1127 | [10 empty] | 79.65 |  |  |  | 79.65 | [5 empty] | 81.82 |  |  | 80.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.35 |  |  |  |  | 0.00
2020 |  |  |  | 8481.35 |  |  | 7378 |  |  |  | 1127 | [10 empty] | 83.95 |  |  |  | 83.95 | [5 empty] | 85.67 |  |  | 83.99 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.05 |  |  |  |  | 0.00
2021 |  |  |  | 9636.22 |  |  | 8357 |  |  |  | 1127 | [10 empty] | 95.07 |  |  |  | 95.07 | [5 empty] | 97.61 |  |  | 95.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.93 |  |  |  |  | 0.00
2022 |  |  |  | 6536.56 |  |  | 5681 |  |  |  | 1127 | [10 empty] | 64.47 |  |  |  | 64.47 | [5 empty] | 66.21 |  |  | 64.85 |  |  |  | 0.00 |  | 3.01 | [8 empty] | 32.51 |  |  |  |  | 0.00
2023 |  |  |  | 8554.07 |  |  | 7395 |  |  |  | 1127 | [10 empty] | 84.06 |  |  |  | 84.06 | [5 empty] | 86.65 |  |  | 84.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.94 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1993 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 117
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1365 | [14 empty] | 999
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 670
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 906
Z. |  | Other | [39 empty] | 19
Subtotal | [22 empty] | 1365 | [14 empty] | 2575 |  |  |  | 136
Total | [22 empty] | 1365 | [14 empty] | 2711
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1993 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 19
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
41. |  |  | Main Generator Systems | [34 empty] | 107
Total | [37 empty] | 137

## SENDAI-1
2023 Operating Experience
JP-28 | [8 empty] | SENDAI-1 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Owner | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-12-15
Thermal power | [12 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-09-16
Gross electrical power | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-07-04
Reference unit power (net) | [12 empty] | : |  |  | 846 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.22
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 49000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.07
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6502.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.37 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 81.37 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 18.63 %
Load Factor (LF) | [18 empty] | : | 87.74 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 81.82 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1593 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 686.51 | 337.31 |  |  |  | 0.00 |  | 121.38 | [8 empty] | 683.35 |  |  | 658.13 | [6 empty] | 671.12 |  | 669.69 |  |  |  | 648.83 |  |  | 678.20 |  |  | 661.98 | [9 empty] | 685.92 |  |  | 6502.42
EAF [%] |  |  |  |  | 100.00 | 54.43 |  |  |  | 0.00 |  | 19.18 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.37
UCF [%] |  |  |  |  | 100.00 | 54.43 |  |  |  | 0.00 |  | 19.18 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.37
LF [%] |  |  |  |  | 109.07 | 59.33 |  |  |  | 0.00 |  | 19.93 | [8 empty] | 108.57 |  |  | 108.05 | [6 empty] | 106.63 |  | 106.40 |  |  |  | 106.52 |  |  | 107.75 |  |  | 108.68 | [9 empty] | 108.98 |  |  | 87.74
OF [%] |  |  |  |  | 100.00 | 54.91 |  |  |  | 0.00 |  | 24.17 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.82
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 45.57 |  |  |  | 100.00 |  | 80.82 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 18.63
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 225366.52 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.51 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.41 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 72.41 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 26.88 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.89 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 72.91 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 6069.77 |  |  | 7487 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.06 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 5890.27 |  |  | 6964 |  |  |  | 846 | [10 empty] | 78.68 |  |  |  | 78.68 | [5 empty] | 79.48 |  |  | 79.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.32 |  |  |  |  | 0.00
1986 |  |  |  | 6084.02 |  |  | 7224 |  |  |  | 846 | [10 empty] | 81.36 |  |  |  | 81.36 | [5 empty] | 82.09 |  |  | 82.47 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.64 |  |  |  |  | 0.00
1987 |  |  |  | 6113.36 |  |  | 7261 |  |  |  | 846 | [10 empty] | 81.74 |  |  |  | 81.74 | [5 empty] | 82.49 |  |  | 82.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.26 |  |  |  |  | 0.00
1988 |  |  |  | 5683.09 |  |  | 6756 |  |  |  | 846 | [10 empty] | 75.81 |  |  |  | 75.81 | [5 empty] | 76.48 |  |  | 76.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.19 |  |  |  |  | 0.00
1989 |  |  |  | 7381.33 |  |  | 8641 |  |  |  | 846 | [10 empty] | 98.69 |  |  |  | 98.69 | [5 empty] | 99.60 |  |  | 98.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.31 |  |  |  |  | 0.00
1990 |  |  |  | 6154.95 |  |  | 7307 |  |  |  | 846 | [10 empty] | 82.31 |  |  |  | 82.31 | [5 empty] | 83.05 |  |  | 83.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.69 |  |  |  |  | 0.00
1991 |  |  |  | 5590.69 |  |  | 6684 |  |  |  | 846 | [10 empty] | 74.76 |  |  |  | 74.76 | [5 empty] | 75.44 |  |  | 76.30 |  |  |  | 1.23 |  | 0.93 | [8 empty] | 24.31 |  |  |  |  | 0.00
1992 |  |  |  | 5713.89 |  |  | 6780 |  |  |  | 846 | [10 empty] | 76.08 |  |  |  | 76.08 | [5 empty] | 76.89 |  |  | 77.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.92 |  |  |  |  | 0.00
1993 |  |  |  | 6619.24 |  |  | 7753 |  |  |  | 846 | [10 empty] | 88.43 |  |  |  | 88.43 | [5 empty] | 89.32 |  |  | 88.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.57 |  |  |  |  | 0.00
1994 |  |  |  | 5778.34 |  |  | 6762 |  |  |  | 846 | [10 empty] | 77.17 |  |  |  | 77.17 | [5 empty] | 77.97 |  |  | 77.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.83 |  |  |  |  | 0.00
1995 |  |  |  | 5780.32 |  |  | 6863 |  |  |  | 846 | [10 empty] | 77.28 |  |  |  | 77.28 | [5 empty] | 78.00 |  |  | 78.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.72 |  |  |  |  | 0.00
1996 |  |  |  | 5185.37 |  |  | 6157 |  |  |  | 846 | [10 empty] | 69.09 |  |  |  | 69.09 | [5 empty] | 69.78 |  |  | 70.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 30.91 |  |  |  |  | 0.00
1997 |  |  |  | 7216.68 |  |  | 8449 |  |  |  | 846 | [10 empty] | 96.40 |  |  |  | 96.40 | [5 empty] | 97.38 |  |  | 96.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.60 |  |  |  |  | 0.00
1998 |  |  |  | 5291.22 |  |  | 6311 |  |  |  | 846 | [10 empty] | 70.64 |  |  |  | 70.64 | [5 empty] | 71.40 |  |  | 72.04 |  |  |  | 4.67 |  | 3.46 | [8 empty] | 25.90 |  |  |  |  | 0.00
1999 |  |  |  | 6057.57 |  |  | 7082 |  |  |  | 846 | [10 empty] | 80.83 |  |  |  | 80.83 | [5 empty] | 81.74 |  |  | 80.84 |  |  |  | 3.06 |  | 2.55 | [8 empty] | 16.62 |  |  |  |  | 0.00
2000 |  |  |  | 5654.00 |  |  | 6609 |  |  |  | 846 | [10 empty] | 75.23 |  |  |  | 75.23 | [5 empty] | 76.08 |  |  | 75.24 |  |  |  | 9.23 |  | 7.65 | [8 empty] | 17.12 |  |  |  |  | 0.00
2001 |  |  |  | 7367.04 |  |  | 8614 |  |  |  | 846 | [10 empty] | 98.31 |  |  |  | 98.31 | [5 empty] | 99.41 |  |  | 98.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.69 |  |  |  |  | 0.00
2002 |  |  |  | 6323.03 |  |  | 7333 |  |  |  | 846 | [10 empty] | 83.68 |  |  |  | 83.68 | [5 empty] | 85.32 |  |  | 83.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.32 |  |  |  |  | 0.00
2003 |  |  |  | 6282.06 |  |  | 7278 |  |  |  | 846 | [10 empty] | 83.08 |  |  |  | 83.08 | [5 empty] | 84.77 |  |  | 83.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.92 |  |  |  |  | 0.00
2004 |  |  |  | 6080.79 |  |  | 7043 |  |  |  | 846 | [10 empty] | 80.15 |  |  |  | 80.15 | [5 empty] | 81.83 |  |  | 80.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.85 |  |  |  |  | 0.00
2005 |  |  |  | 7155.81 |  |  | 8305 |  |  |  | 846 | [10 empty] | 94.74 |  |  |  | 94.74 | [5 empty] | 96.56 |  |  | 94.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.26 |  |  |  |  | 0.00
2006 |  |  |  | 6436.58 |  |  | 7330 |  |  |  | 846 | [10 empty] | 82.92 |  |  |  | 82.92 | [5 empty] | 86.85 |  |  | 83.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.08 |  |  |  |  | 0.00
2007 |  |  |  | 5868.86 |  |  | 6660 |  |  |  | 846 | [10 empty] | 75.21 |  |  |  | 75.21 | [5 empty] | 79.19 |  |  | 76.03 |  |  |  | 0.00 |  | 8.05 | [8 empty] | 16.74 |  |  |  |  | 0.00
2008 |  |  |  | 5665.09 |  |  | 6396 |  |  |  | 846 | [10 empty] | 71.92 |  |  |  | 71.92 | [5 empty] | 76.23 |  |  | 72.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.08 |  |  |  |  | 0.00
2009 |  |  |  | 7880.10 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 106.33 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2010 |  |  |  | 4919.57 |  |  | 5571 |  |  |  | 846 | [10 empty] | 62.67 |  |  |  | 62.67 | [5 empty] | 66.38 |  |  | 63.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.33 |  |  |  |  | 0.00
2011 |  |  |  | 2823.75 |  |  | 3097 |  |  |  | 846 | [10 empty] | 35.32 |  |  |  | 35.32 | [5 empty] | 38.10 |  |  | 35.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 64.68 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 2893.82 |  |  | 3351 |  |  |  | 846 | [10 empty] | 36.84 |  |  |  | 36.84 | [5 empty] | 39.05 |  |  | 38.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 63.16 |  |  |  |  | 0.00
2016 |  |  |  | 6452.27 |  |  | 7188 |  |  |  | 846 | [10 empty] | 81.16 |  |  |  | 81.16 | [5 empty] | 86.83 |  |  | 81.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.84 |  |  |  |  | 0.00
2017 |  |  |  | 8007.73 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 108.05 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 5186.62 |  |  | 5756 |  |  |  | 846 | [10 empty] | 65.03 |  |  |  | 65.03 | [5 empty] | 69.99 |  |  | 65.71 |  |  |  | 0.00 |  | 5.10 | [8 empty] | 29.87 |  |  |  |  | 0.00
2019 |  |  |  | 6434.71 |  |  | 7058 |  |  |  | 846 | [10 empty] | 80.07 |  |  |  | 80.07 | [5 empty] | 86.83 |  |  | 80.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.93 |  |  |  |  | 0.00
2020 |  |  |  | 2552.25 |  |  | 2818 |  |  |  | 846 | [10 empty] | 31.58 |  |  |  | 31.58 | [5 empty] | 34.34 |  |  | 32.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 68.42 |  |  |  |  | 0.00
2021 |  |  |  | 6563.52 |  |  | 7215 |  |  |  | 846 | [10 empty] | 81.90 |  |  |  | 81.90 | [5 empty] | 88.57 |  |  | 82.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.10 |  |  |  |  | 0.00
2022 |  |  |  | 8012.33 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 108.11 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2023 |  |  |  | 6502.42 |  |  | 7167 |  |  |  | 846 | [10 empty] | 81.37 |  |  |  | 81.37 | [5 empty] | 87.74 |  |  | 81.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.63 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1984 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 59
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1593 | [14 empty] | 1449
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 914
Subtotal | [22 empty] | 1593 | [14 empty] | 2363 |  |  |  | 59
Total | [22 empty] | 1593 | [14 empty] | 2422
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1984 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 11
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
16. |  |  | Steam generation systems | [34 empty] | 17
31. |  |  | Turbine and auxiliaries | [34 empty] | 6
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
Total | [37 empty] | 58

## SENDAI-2
2023 Operating Experience
JP-37 | [8 empty] | SENDAI-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Owner | [7 empty] | : | KYUSHU (Kyushu Electric Power Co., Inc.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | SIEMENS (Siemens AG, Power Generation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-10-12
Thermal power | [12 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-04-05
Gross electrical power | [12 empty] | : |  |  | 890 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-11-28
Reference unit power (net) | [12 empty] | : |  |  | 846 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.4
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.22
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.8 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 49000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.07
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6518.1 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.37 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 81.37 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 18.63 %
Load Factor (LF) | [18 empty] | : | 87.95 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 81.82 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1593 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 686.50 | 619.78 |  |  |  | 685.75 |  | 662.42 | [8 empty] | 270.09 |  |  | 0.00 | [6 empty] | 248.92 |  | 669.34 |  |  |  | 648.49 |  |  | 678.23 |  |  | 662.01 | [9 empty] | 686.57 |  |  | 6518.10
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 39.48 |  |  | 0.00 | [6 empty] | 37.91 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.37
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 39.48 |  |  | 0.00 | [6 empty] | 37.91 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.37
LF [%] |  |  |  |  | 109.07 | 109.02 |  |  |  | 108.95 |  | 108.75 | [8 empty] | 42.91 |  |  | 0.00 | [6 empty] | 39.55 |  | 106.34 |  |  |  | 106.46 |  |  | 107.75 |  |  | 108.68 | [9 empty] | 109.08 |  |  | 87.95
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 39.92 |  |  | 0.00 | [6 empty] | 42.74 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.82
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 60.52 |  |  | 100.00 | [6 empty] | 62.09 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 18.63
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 211260.85 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.04 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.16 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.03 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 73.16 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 26.82 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.28 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 73.58 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 2816.07 |  |  | 4327 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.22 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 5996.37 |  |  | 7112 |  |  |  | 846 | [10 empty] | 80.14 |  |  |  | 80.14 | [5 empty] | 80.91 |  |  | 81.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.86 |  |  |  |  | 0.00
1987 |  |  |  | 6080.60 |  |  | 7211 |  |  |  | 846 | [10 empty] | 81.18 |  |  |  | 81.18 | [5 empty] | 82.05 |  |  | 82.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.82 |  |  |  |  | 0.00
1988 |  |  |  | 7409.79 |  |  | 8665 |  |  |  | 846 | [10 empty] | 98.70 |  |  |  | 98.70 | [5 empty] | 99.71 |  |  | 98.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.30 |  |  |  |  | 0.00
1989 |  |  |  | 4999.37 |  |  | 5950 |  |  |  | 846 | [10 empty] | 66.84 |  |  |  | 66.84 | [5 empty] | 67.46 |  |  | 67.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.16 |  |  |  |  | 0.00
1990 |  |  |  | 6160.14 |  |  | 7309 |  |  |  | 846 | [10 empty] | 82.37 |  |  |  | 82.37 | [5 empty] | 83.12 |  |  | 83.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.63 |  |  |  |  | 0.00
1991 |  |  |  | 5665.26 |  |  | 6732 |  |  |  | 846 | [10 empty] | 75.72 |  |  |  | 75.72 | [5 empty] | 76.44 |  |  | 76.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.28 |  |  |  |  | 0.00
1992 |  |  |  | 7385.32 |  |  | 8639 |  |  |  | 846 | [10 empty] | 98.30 |  |  |  | 98.30 | [5 empty] | 99.38 |  |  | 98.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.70 |  |  |  |  | 0.00
1993 |  |  |  | 5821.98 |  |  | 6632 |  |  |  | 846 | [10 empty] | 77.69 |  |  |  | 77.69 | [5 empty] | 78.56 |  |  | 75.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.31 |  |  |  |  | 0.00
1994 |  |  |  | 5568.78 |  |  | 6557 |  |  |  | 846 | [10 empty] | 74.30 |  |  |  | 74.30 | [5 empty] | 75.14 |  |  | 74.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.70 |  |  |  |  | 0.00
1995 |  |  |  | 5658.40 |  |  | 6709 |  |  |  | 846 | [10 empty] | 75.50 |  |  |  | 75.50 | [5 empty] | 76.35 |  |  | 76.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.50 |  |  |  |  | 0.00
1996 |  |  |  | 7359.31 |  |  | 8617 |  |  |  | 846 | [10 empty] | 98.05 |  |  |  | 98.05 | [5 empty] | 99.03 |  |  | 98.10 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.95 |  |  |  |  | 0.00
1997 |  |  |  | 5950.29 |  |  | 7034 |  |  |  | 846 | [10 empty] | 79.44 |  |  |  | 79.44 | [5 empty] | 80.29 |  |  | 80.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.56 |  |  |  |  | 0.00
1998 |  |  |  | 5899.10 |  |  | 6973 |  |  |  | 846 | [10 empty] | 78.72 |  |  |  | 78.72 | [5 empty] | 79.60 |  |  | 79.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.28 |  |  |  |  | 0.00
1999 |  |  |  | 5658.29 |  |  | 6612 |  |  |  | 846 | [10 empty] | 75.47 |  |  |  | 75.47 | [5 empty] | 76.35 |  |  | 75.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.53 |  |  |  |  | 0.00
2000 |  |  |  | 7370.17 |  |  | 8614 |  |  |  | 846 | [10 empty] | 98.04 |  |  |  | 98.04 | [5 empty] | 99.18 |  |  | 98.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.96 |  |  |  |  | 0.00
2001 |  |  |  | 6210.15 |  |  | 7260 |  |  |  | 846 | [10 empty] | 82.86 |  |  |  | 82.86 | [5 empty] | 83.80 |  |  | 82.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.14 |  |  |  |  | 0.00
2002 |  |  |  | 6255.46 |  |  | 7257 |  |  |  | 846 | [10 empty] | 82.83 |  |  |  | 82.83 | [5 empty] | 84.41 |  |  | 82.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.17 |  |  |  |  | 0.00
2003 |  |  |  | 6348.77 |  |  | 7315 |  |  |  | 846 | [10 empty] | 83.38 |  |  |  | 83.38 | [5 empty] | 85.67 |  |  | 83.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.62 |  |  |  |  | 0.00
2004 |  |  |  | 6762.55 |  |  | 7774 |  |  |  | 846 | [10 empty] | 88.48 |  |  |  | 88.48 | [5 empty] | 91.00 |  |  | 88.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.52 |  |  |  |  | 0.00
2005 |  |  |  | 6752.80 |  |  | 7895 |  |  |  | 846 | [10 empty] | 88.94 |  |  |  | 88.94 | [5 empty] | 91.12 |  |  | 90.13 |  |  |  | 1.17 |  | 1.05 | [8 empty] | 10.01 |  |  |  |  | 0.00
2006 |  |  |  | 6464.16 |  |  | 7548 |  |  |  | 846 | [10 empty] | 85.35 |  |  |  | 85.35 | [5 empty] | 87.22 |  |  | 86.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.65 |  |  |  |  | 0.00
2007 |  |  |  | 5989.31 |  |  | 6996 |  |  |  | 846 | [10 empty] | 79.05 |  |  |  | 79.05 | [5 empty] | 80.82 |  |  | 79.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.95 |  |  |  |  | 0.00
2008 |  |  |  | 6824.28 |  |  | 7897 |  |  |  | 846 | [10 empty] | 89.86 |  |  |  | 89.86 | [5 empty] | 91.83 |  |  | 89.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.14 |  |  |  |  | 0.00
2009 |  |  |  | 6320.24 |  |  | 7355 |  |  |  | 846 | [10 empty] | 83.19 |  |  |  | 83.19 | [5 empty] | 85.28 |  |  | 83.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.81 |  |  |  |  | 0.00
2010 |  |  |  | 5767.52 |  |  | 6630 |  |  |  | 846 | [10 empty] | 74.78 |  |  |  | 74.78 | [5 empty] | 77.82 |  |  | 75.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.22 |  |  |  |  | 0.00
2011 |  |  |  | 5216.82 |  |  | 5833 |  |  |  | 846 | [10 empty] | 66.55 |  |  |  | 66.55 | [5 empty] | 70.39 |  |  | 66.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.45 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 846 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 1452.66 |  |  | 1729 |  |  |  | 846 | [10 empty] | 18.63 |  |  |  | 18.63 | [5 empty] | 19.60 |  |  | 19.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 81.37 |  |  |  |  | 0.00
2016 |  |  |  | 7468.59 |  |  | 8401 |  |  |  | 846 | [10 empty] | 95.60 |  |  |  | 95.60 | [5 empty] | 100.50 |  |  | 95.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.40 |  |  |  |  | 0.00
2017 |  |  |  | 6554.16 |  |  | 7401 |  |  |  | 846 | [10 empty] | 83.87 |  |  |  | 83.87 | [5 empty] | 88.44 |  |  | 84.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.13 |  |  |  |  | 0.00
2018 |  |  |  | 5016.93 |  |  | 5618 |  |  |  | 846 | [10 empty] | 63.46 |  |  |  | 63.46 | [5 empty] | 67.70 |  |  | 64.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.54 |  |  |  |  | 0.00
2019 |  |  |  | 6381.17 |  |  | 7082 |  |  |  | 846 | [10 empty] | 80.38 |  |  |  | 80.38 | [5 empty] | 86.10 |  |  | 80.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.62 |  |  |  |  | 0.00
2020 |  |  |  | 3197.98 |  |  | 3538 |  |  |  | 846 | [10 empty] | 39.82 |  |  |  | 39.82 | [5 empty] | 43.03 |  |  | 40.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 60.18 |  |  |  |  | 0.00
2021 |  |  |  | 8012.55 |  |  | 8760 |  |  |  | 846 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 108.12 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2022 |  |  |  | 5488.22 |  |  | 6063 |  |  |  | 846 | [10 empty] | 68.71 |  |  |  | 68.71 | [5 empty] | 74.06 |  |  | 69.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.29 |  |  |  |  | 0.00
2023 |  |  |  | 6518.10 |  |  | 7167 |  |  |  | 846 | [10 empty] | 81.37 |  |  |  | 81.37 | [5 empty] | 87.95 |  |  | 81.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.63 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 3
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1545 | [14 empty] | 1439
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 900
Subtotal | [22 empty] | 1545 | [14 empty] | 2339 |  |  |  | 3
Total | [22 empty] | 1545 | [14 empty] | 2342
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
Total | [37 empty] | 3

## TAKAHAMA-1
2023 Operating Experience
JP-8 | [8 empty] | TAKAHAMA-1 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | WH/MHI (WESTINGHOUSE ELECTRIC CORPORATION / MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-04-25
Thermal power | [12 empty] | : |  |  | 2440 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-03-27
Gross electrical power | [12 empty] | : |  |  | 826 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1974-11-14
Reference unit power (net) | [12 empty] | : |  |  | 780 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.24
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.0 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.64 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2936.1 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.13 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.13 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.87 %
Load Factor (LF) | [18 empty] | : | 103.19 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 99.59 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 15 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | Jul |  |  | May | [6 empty] | Jun |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [32 empty] | 545.18 |  |  |  | 580.23 |  |  | 607.36 |  |  | 591.12 | [9 empty] | 612.21 |  |  | 2936.11
EAF [%] | [32 empty] | 95.62 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 99.13
UCF [%] | [32 empty] | 95.62 |  |  |  | 99.99 |  |  | 100.00 |  |  | 99.99 | [9 empty] | 100.00 |  |  | 99.13
LF [%] | [32 empty] | 97.08 |  |  |  | 103.32 |  |  | 104.66 |  |  | 105.26 | [9 empty] | 105.50 |  |  | 103.19
OF [%] | [32 empty] | 97.92 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.59
FLR [%] | [32 empty] | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] | [32 empty] | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] | [32 empty] | 4.38 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.01 | [9 empty] | 0.00 |  |  | 0.87
XUF [%] | [32 empty] | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 177250.1 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.31 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 69.81 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.78 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 69.84 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 25.38 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.84 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 70.99 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1974 |  |  |  | 2660.40 |  |  | 4392 |  |  |  | 780 | [10 empty] | 94.03 |  |  |  | 94.03 | [5 empty] | 92.81 |  |  | 93.99 |  |  |  | 5.08 |  | 5.03 | [8 empty] | 0.93 |  |  |  |  | 0.00
1975 |  |  |  | 4980.40 |  |  | 6938 |  |  |  | 780 | [10 empty] | 72.81 |  |  |  | 72.81 | [5 empty] | 72.89 |  |  | 79.20 |  |  |  | 12.81 |  | 10.70 | [8 empty] | 16.49 |  |  |  |  | 0.00
1976 |  |  |  | 3170.10 |  |  | 4900 |  |  |  | 780 | [10 empty] | 46.19 |  |  |  | 46.19 | [5 empty] | 46.27 |  |  | 55.78 |  |  |  | 19.20 |  | 10.98 | [8 empty] | 42.83 |  |  |  |  | 0.00
1977 |  |  |  | 383.80 |  |  | 569 |  |  |  | 780 | [10 empty] | 5.61 |  |  |  | 5.61 | [5 empty] | 5.62 |  |  | 6.50 |  |  |  | 94.39 |  | 94.39 | [8 empty] | 0.00 |  |  |  |  | 0.00
1978 |  |  |  | 2762.50 |  |  | 4088 |  |  |  | 780 | [10 empty] | 40.42 |  |  |  | 40.42 | [5 empty] | 40.43 |  |  | 46.67 |  |  |  | 5.59 |  | 2.39 | [8 empty] | 57.18 |  |  |  |  | 0.00
1979 |  |  |  | 1648.90 |  |  | 2269 |  |  |  | 780 | [10 empty] | 24.14 |  |  |  | 24.14 | [5 empty] | 24.13 |  |  | 25.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 75.86 |  |  |  |  | 0.00
1980 |  |  |  | 2705.10 |  |  | 3604 |  |  |  | 780 | [10 empty] | 39.42 |  |  |  | 39.42 | [5 empty] | 39.48 |  |  | 41.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 60.58 |  |  |  |  | 0.00
1981 |  |  |  | 3990.20 |  |  | 5180 |  |  |  | 780 | [10 empty] | 58.33 |  |  |  | 58.33 | [5 empty] | 58.40 |  |  | 59.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 41.67 |  |  |  |  | 0.00
1982 |  |  |  | 3872.10 |  |  | 5085 |  |  |  | 780 | [10 empty] | 56.50 |  |  |  | 56.50 | [5 empty] | 56.67 |  |  | 58.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 43.50 |  |  |  |  | 0.00
1983 |  |  |  | 5716.20 |  |  | 7403 |  |  |  | 780 | [10 empty] | 83.72 |  |  |  | 83.72 | [5 empty] | 83.66 |  |  | 84.51 |  |  |  | 0.65 |  | 0.54 | [8 empty] | 15.74 |  |  |  |  | 0.00
1984 |  |  |  | 3537.44 |  |  | 4586 |  |  |  | 780 | [10 empty] | 51.41 |  |  |  | 51.41 | [5 empty] | 51.63 |  |  | 52.21 |  |  |  | 0.54 |  | 0.28 | [8 empty] | 48.31 |  |  |  |  | 0.00
1985 |  |  |  | 5000.77 |  |  | 6473 |  |  |  | 780 | [10 empty] | 72.84 |  |  |  | 72.84 | [5 empty] | 73.19 |  |  | 73.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.16 |  |  |  |  | 0.00
1986 |  |  |  | 5070.31 |  |  | 6507 |  |  |  | 780 | [10 empty] | 73.86 |  |  |  | 73.86 | [5 empty] | 74.21 |  |  | 74.28 |  |  |  | 1.25 |  | 0.94 | [8 empty] | 25.21 |  |  |  |  | 0.00
1987 |  |  |  | 4701.39 |  |  | 6148 |  |  |  | 780 | [10 empty] | 70.18 |  |  |  | 70.18 | [5 empty] | 68.81 |  |  | 70.18 |  |  |  | 18.82 |  | 16.27 | [8 empty] | 13.55 |  |  |  |  | 0.00
1988 |  |  |  | 4147.14 |  |  | 5351 |  |  |  | 780 | [10 empty] | 60.92 |  |  |  | 60.92 | [5 empty] | 60.53 |  |  | 60.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 39.08 |  |  |  |  | 0.00
1989 |  |  |  | 4877.26 |  |  | 6311 |  |  |  | 780 | [10 empty] | 72.04 |  |  |  | 72.04 | [5 empty] | 71.38 |  |  | 72.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.96 |  |  |  |  | 0.00
1990 |  |  |  | 6265.50 |  |  | 8002 |  |  |  | 780 | [10 empty] | 90.76 |  |  |  | 90.76 | [5 empty] | 91.70 |  |  | 91.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.24 |  |  |  |  | 0.00
1991 |  |  |  | 4795.05 |  |  | 6202 |  |  |  | 780 | [10 empty] | 68.25 |  |  |  | 68.25 | [5 empty] | 70.18 |  |  | 70.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.75 |  |  |  |  | 0.00
1992 |  |  |  | 4644.96 |  |  | 6051 |  |  |  | 780 | [10 empty] | 67.62 |  |  |  | 67.62 | [5 empty] | 67.79 |  |  | 68.89 |  |  |  | 1.28 |  | 0.88 | [8 empty] | 31.50 |  |  |  |  | 0.00
1993 |  |  |  | 3299.67 |  |  | 4458 |  |  |  | 780 | [10 empty] | 48.36 |  |  |  | 48.36 | [5 empty] | 48.29 |  |  | 50.89 |  |  |  | 30.51 |  | 21.23 | [8 empty] | 30.41 |  |  |  |  | 0.00
1994 |  |  |  | 4024.04 |  |  | 5146 |  |  |  | 780 | [10 empty] | 58.84 |  |  |  | 58.84 | [5 empty] | 58.89 |  |  | 58.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 41.16 |  |  |  |  | 0.00
1995 |  |  |  | 6585.13 |  |  | 8485 |  |  |  | 780 | [10 empty] | 96.05 |  |  |  | 96.05 | [5 empty] | 96.38 |  |  | 96.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.95 |  |  |  |  | 0.00
1996 |  |  |  | 3358.80 |  |  | 4331 |  |  |  | 780 | [10 empty] | 48.81 |  |  |  | 48.82 | [5 empty] | 49.02 |  |  | 49.31 |  |  |  | 8.78 |  | 4.70 | [8 empty] | 46.48 |  |  |  |  | 0.01
1997 |  |  |  | 4674.40 |  |  | 6000 |  |  |  | 780 | [10 empty] | 68.10 |  |  |  | 68.10 | [5 empty] | 68.41 |  |  | 68.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.90 |  |  |  |  | 0.00
1998 |  |  |  | 6856.82 |  |  | 8760 |  |  |  | 780 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 100.35 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1999 |  |  |  | 5704.24 |  |  | 7291 |  |  |  | 780 | [10 empty] | 83.22 |  |  |  | 84.30 | [5 empty] | 83.48 |  |  | 83.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.70 |  |  |  |  | 1.08
2000 |  |  |  | 6008.07 |  |  | 7716 |  |  |  | 780 | [10 empty] | 87.42 |  |  |  | 87.42 | [5 empty] | 87.69 |  |  | 87.84 |  |  |  | 0.47 |  | 0.41 | [8 empty] | 12.17 |  |  |  |  | 0.00
2001 |  |  |  | 6005.80 |  |  | 7731 |  |  |  | 780 | [10 empty] | 87.62 |  |  |  | 87.62 | [5 empty] | 87.90 |  |  | 88.25 |  |  |  | 0.70 |  | 0.62 | [8 empty] | 11.76 |  |  |  |  | 0.00
2002 |  |  |  | 6056.31 |  |  | 7749 |  |  |  | 780 | [10 empty] | 88.44 |  |  |  | 88.44 | [5 empty] | 88.64 |  |  | 88.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.56 |  |  |  |  | 0.00
2003 |  |  |  | 6247.16 |  |  | 7637 |  |  |  | 780 | [10 empty] | 87.17 |  |  |  | 87.17 | [5 empty] | 91.43 |  |  | 87.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.83 |  |  |  |  | 0.00
2004 |  |  |  | 5539.92 |  |  | 6785 |  |  |  | 780 | [10 empty] | 77.21 |  |  |  | 77.21 | [5 empty] | 80.86 |  |  | 77.24 |  |  |  | 4.89 |  | 3.97 | [8 empty] | 18.81 |  |  |  |  | 0.00
2005 |  |  |  | 6222.49 |  |  | 7659 |  |  |  | 780 | [10 empty] | 87.07 |  |  |  | 87.07 | [5 empty] | 91.07 |  |  | 87.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.93 |  |  |  |  | 0.00
2006 |  |  |  | 6347.13 |  |  | 7811 |  |  |  | 780 | [10 empty] | 89.16 |  |  |  | 89.16 | [5 empty] | 92.89 |  |  | 89.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.84 |  |  |  |  | 0.00
2007 |  |  |  | 6012.94 |  |  | 7399 |  |  |  | 780 | [10 empty] | 84.15 |  |  |  | 84.15 | [5 empty] | 88.00 |  |  | 84.46 |  |  |  | 0.00 |  | 2.66 | [8 empty] | 13.19 |  |  |  |  | 0.00
2008 |  |  |  | 4935.75 |  |  | 6077 |  |  |  | 780 | [10 empty] | 68.84 |  |  |  | 68.84 | [5 empty] | 72.04 |  |  | 69.18 |  |  |  | 4.11 |  | 2.95 | [8 empty] | 28.21 |  |  |  |  | 0.00
2009 |  |  |  | 5870.09 |  |  | 7193 |  |  |  | 780 | [10 empty] | 81.73 |  |  |  | 81.73 | [5 empty] | 85.91 |  |  | 82.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.27 |  |  |  |  | 0.00
2010 |  |  |  | 7193.46 |  |  | 8760 |  |  |  | 780 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 105.28 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2011 |  |  |  | 183.43 |  |  | 226 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2021 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2022 |  |  |  | Data not available - Suspended Operation
2023 |  |  |  | 2936.11 |  |  | 3633 |  |  |  | 780 | [10 empty] | 99.13 |  |  |  | 99.13 | [5 empty] | 103.19 |  |  | 99.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.87 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1974 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 375
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 5127 | [14 empty] | 2110
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 194
E. |  | Testing of plant systems or components | [35 empty] | 0
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 50
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 2580
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 1
Z. |  | Other | [39 empty] | 10
Subtotal | [22 empty] | 5127 | [14 empty] | 4934 |  |  |  | 386 | [11 empty] | 3
Total | [22 empty] | 5127 | [14 empty] | 5323
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1974 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 95
16. |  |  | Steam generation systems | [34 empty] | 219
31. |  |  | Turbine and auxiliaries | [34 empty] | 25
32. |  |  | Feedwater and Main Steam System | [34 empty] | 24
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 378

## TAKAHAMA-2
2023 Operating Experience
JP-13 | [8 empty] | TAKAHAMA-2 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1971-03-09
Thermal power | [12 empty] | : |  |  | 2440 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-01-17
Gross electrical power | [12 empty] | : |  |  | 826 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-11-14
Reference unit power (net) | [12 empty] | : |  |  | 780 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.24
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.0 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.8
| Active core height/length [m] | [13 empty] | : |  |  | 3.64 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 22
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 20.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 1987.78 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.99 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.99 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0.01 %
Load Factor (LF) | [18 empty] | : | 105.21 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 15 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [39 empty] | 607.43 |  |  | 591.89 | [9 empty] | 612.62 |  |  | 1811.95
EAF [%] | [39 empty] | 99.99 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 99.99
UCF [%] | [39 empty] | 99.99 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 99.99
LF [%] | [39 empty] | 104.67 |  |  | 105.39 | [9 empty] | 105.57 |  |  | 105.21
OF [%] | [39 empty] | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] | [39 empty] | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] | [39 empty] | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] | [39 empty] | 0.01 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 0.01
XUF [%] | [39 empty] | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 174645.78 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.64 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 68.93 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.72 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 69.03 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 27.25 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.29 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.1 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 70.38 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 3168.50 |  |  | 5532 |  |  |  | 780 | [10 empty] | 99.55 |  |  |  | 99.55 | [5 empty] | 100.44 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.45 |  |  |  |  | 0.00
1976 |  |  |  | 3728.80 |  |  | 6214 |  |  |  | 780 | [10 empty] | 54.17 |  |  |  | 54.17 | [5 empty] | 54.42 |  |  | 70.74 |  |  |  | 23.83 |  | 16.94 | [8 empty] | 28.89 |  |  |  |  | 0.00
1977 |  |  |  | 4742.00 |  |  | 6429 |  |  |  | 780 | [10 empty] | 69.40 |  |  |  | 69.40 | [5 empty] | 69.40 |  |  | 73.39 |  |  |  | 0.11 |  | 0.08 | [8 empty] | 30.52 |  |  |  |  | 0.00
1978 |  |  |  | 4170.30 |  |  | 5751 |  |  |  | 780 | [10 empty] | 61.04 |  |  |  | 61.04 | [5 empty] | 61.03 |  |  | 65.65 |  |  |  | 0.59 |  | 0.37 | [8 empty] | 38.59 |  |  |  |  | 0.00
1979 |  |  |  | 1281.00 |  |  | 1826 |  |  |  | 780 | [10 empty] | 18.75 |  |  |  | 18.75 | [5 empty] | 18.75 |  |  | 20.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 81.25 |  |  |  |  | 0.00
1980 |  |  |  | 5751.10 |  |  | 7450 |  |  |  | 780 | [10 empty] | 83.72 |  |  |  | 83.72 | [5 empty] | 83.94 |  |  | 84.81 |  |  |  | 0.92 |  | 0.78 | [8 empty] | 15.51 |  |  |  |  | 0.00
1981 |  |  |  | 4763.20 |  |  | 6198 |  |  |  | 780 | [10 empty] | 69.55 |  |  |  | 69.55 | [5 empty] | 69.71 |  |  | 70.75 |  |  |  | 0.30 |  | 0.21 | [8 empty] | 30.23 |  |  |  |  | 0.00
1982 |  |  |  | 4133.90 |  |  | 5407 |  |  |  | 780 | [10 empty] | 60.26 |  |  |  | 60.26 | [5 empty] | 60.50 |  |  | 61.72 |  |  |  | 0.62 |  | 0.37 | [8 empty] | 39.36 |  |  |  |  | 0.00
1983 |  |  |  | 3549.40 |  |  | 4645 |  |  |  | 780 | [10 empty] | 51.74 |  |  |  | 51.74 | [5 empty] | 51.95 |  |  | 53.03 |  |  |  | 0.80 |  | 0.42 | [8 empty] | 47.84 |  |  |  |  | 0.00
1984 |  |  |  | 4503.14 |  |  | 5746 |  |  |  | 780 | [10 empty] | 65.38 |  |  |  | 65.38 | [5 empty] | 65.72 |  |  | 65.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 34.62 |  |  |  |  | 0.00
1985 |  |  |  | 4967.39 |  |  | 6466 |  |  |  | 780 | [10 empty] | 72.38 |  |  |  | 72.38 | [5 empty] | 72.70 |  |  | 73.81 |  |  |  | 18.83 |  | 16.79 | [8 empty] | 10.83 |  |  |  |  | 0.00
1986 |  |  |  | 3997.83 |  |  | 5183 |  |  |  | 780 | [10 empty] | 58.37 |  |  |  | 58.37 | [5 empty] | 58.51 |  |  | 59.17 |  |  |  | 0.81 |  | 0.48 | [8 empty] | 41.16 |  |  |  |  | 0.00
1987 |  |  |  | 4621.76 |  |  | 6154 |  |  |  | 780 | [10 empty] | 67.31 |  |  |  | 70.25 | [5 empty] | 67.64 |  |  | 70.25 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.75 |  |  |  |  | 2.94
1988 |  |  |  | 3071.35 |  |  | 4001 |  |  |  | 780 | [10 empty] | 45.55 |  |  |  | 45.55 | [5 empty] | 44.83 |  |  | 45.55 |  |  |  | 10.15 |  | 5.15 | [8 empty] | 49.31 |  |  |  |  | 0.00
1989 |  |  |  | 3991.50 |  |  | 5213 |  |  |  | 780 | [10 empty] | 59.51 |  |  |  | 59.51 | [5 empty] | 58.42 |  |  | 59.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 40.49 |  |  |  |  | 0.00
1990 |  |  |  | 1727.89 |  |  | 2218 |  |  |  | 780 | [10 empty] | 20.85 |  |  |  | 20.85 | [5 empty] | 25.29 |  |  | 25.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 79.15 |  |  |  |  | 0.00
1991 |  |  |  | 2265.80 |  |  | 3054 |  |  |  | 780 | [10 empty] | 32.25 |  |  |  | 32.25 | [5 empty] | 33.16 |  |  | 34.86 |  |  |  | 23.38 |  | 9.84 | [8 empty] | 57.91 |  |  |  |  | 0.00
1992 |  |  |  | 4873.75 |  |  | 6226 |  |  |  | 780 | [10 empty] | 70.80 |  |  |  | 70.80 | [5 empty] | 71.13 |  |  | 70.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.20 |  |  |  |  | 0.00
1993 |  |  |  | 5757.04 |  |  | 7426 |  |  |  | 780 | [10 empty] | 83.96 |  |  |  | 83.96 | [5 empty] | 84.26 |  |  | 84.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.04 |  |  |  |  | 0.00
1994 |  |  |  | 3357.26 |  |  | 4299 |  |  |  | 780 | [10 empty] | 49.29 |  |  |  | 49.29 | [5 empty] | 49.13 |  |  | 49.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 50.71 |  |  |  |  | 0.00
1995 |  |  |  | 4458.67 |  |  | 5906 |  |  |  | 780 | [10 empty] | 65.12 |  |  |  | 65.12 | [5 empty] | 65.25 |  |  | 67.42 |  |  |  | 5.98 |  | 4.14 | [8 empty] | 30.74 |  |  |  |  | 0.00
1996 |  |  |  | 6709.05 |  |  | 8629 |  |  |  | 780 | [10 empty] | 97.34 |  |  |  | 97.66 | [5 empty] | 97.92 |  |  | 98.24 |  |  |  | 2.33 |  | 2.33 | [8 empty] | 0.01 |  |  |  |  | 0.32
1997 |  |  |  | 4981.24 |  |  | 6306 |  |  |  | 780 | [10 empty] | 72.51 |  |  |  | 72.51 | [5 empty] | 72.90 |  |  | 71.99 |  |  |  | 0.54 |  | 0.39 | [8 empty] | 27.10 |  |  |  |  | 0.00
1998 |  |  |  | 5972.92 |  |  | 7657 |  |  |  | 780 | [10 empty] | 86.96 |  |  |  | 86.96 | [5 empty] | 87.42 |  |  | 87.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.04 |  |  |  |  | 0.00
1999 |  |  |  | 5989.80 |  |  | 7717 |  |  |  | 780 | [10 empty] | 87.17 |  |  |  | 87.20 | [5 empty] | 87.66 |  |  | 88.09 |  |  |  | 0.99 |  | 0.87 | [8 empty] | 11.93 |  |  |  |  | 0.03
2000 |  |  |  | 6849.93 |  |  | 8784 |  |  |  | 780 | [10 empty] | 99.50 |  |  |  | 99.50 | [5 empty] | 99.98 |  |  | 100.00 |  |  |  | 0.49 |  | 0.49 | [8 empty] | 0.01 |  |  |  |  | 0.00
2001 |  |  |  | 5900.98 |  |  | 7572 |  |  |  | 780 | [10 empty] | 85.99 |  |  |  | 85.99 | [5 empty] | 86.36 |  |  | 86.44 |  |  |  | 0.50 |  | 0.43 | [8 empty] | 13.57 |  |  |  |  | 0.00
2002 |  |  |  | 6097.67 |  |  | 7626 |  |  |  | 780 | [10 empty] | 87.04 |  |  |  | 87.04 | [5 empty] | 89.24 |  |  | 87.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.96 |  |  |  |  | 0.00
2003 |  |  |  | 5470.78 |  |  | 6717 |  |  |  | 780 | [10 empty] | 76.40 |  |  |  | 76.40 | [5 empty] | 80.07 |  |  | 76.68 |  |  |  | 1.39 |  | 1.33 | [8 empty] | 22.27 |  |  |  |  | 0.00
2004 |  |  |  | 6346.62 |  |  | 7839 |  |  |  | 780 | [10 empty] | 88.87 |  |  |  | 89.33 | [5 empty] | 92.63 |  |  | 89.24 |  |  |  | 7.07 |  | 6.80 | [8 empty] | 3.87 |  |  |  |  | 0.46
2005 |  |  |  | 6249.51 |  |  | 7625 |  |  |  | 780 | [10 empty] | 86.74 |  |  |  | 86.74 | [5 empty] | 91.46 |  |  | 87.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.26 |  |  |  |  | 0.00
2006 |  |  |  | 5653.43 |  |  | 6890 |  |  |  | 780 | [10 empty] | 78.31 |  |  |  | 78.31 | [5 empty] | 82.74 |  |  | 78.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.69 |  |  |  |  | 0.00
2007 |  |  |  | 4521.77 |  |  | 5483 |  |  |  | 780 | [10 empty] | 62.53 |  |  |  | 62.53 | [5 empty] | 66.18 |  |  | 62.59 |  |  |  | 0.00 |  | 23.29 | [8 empty] | 14.18 |  |  |  |  | 0.00
2008 |  |  |  | 4042.51 |  |  | 4949 |  |  |  | 780 | [10 empty] | 56.05 |  |  |  | 56.05 | [5 empty] | 59.00 |  |  | 56.34 |  |  |  | 0.00 |  | 43.66 | [8 empty] | 0.29 |  |  |  |  | 0.00
2009 |  |  |  | 5720.06 |  |  | 6978 |  |  |  | 780 | [10 empty] | 79.28 |  |  |  | 79.28 | [5 empty] | 83.71 |  |  | 79.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.72 |  |  |  |  | 0.00
2010 |  |  |  | 4935.20 |  |  | 6017 |  |  |  | 780 | [10 empty] | 68.28 |  |  |  | 68.28 | [5 empty] | 72.23 |  |  | 68.69 |  |  |  | 0.08 |  | 0.05 | [8 empty] | 31.66 |  |  |  |  | 0.00
2011 |  |  |  | 6502.50 |  |  | 7895 |  |  |  | 780 | [10 empty] | 98.42 |  |  |  | 98.42 | [5 empty] | 104.00 |  |  | 98.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 1.58 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2021 |  |  |  | 0.00 |  |  | 0 |  |  |  | 780 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2022 |  |  |  | Data not available - Suspended Operation
2023 |  |  |  | 1987.78 |  |  | 2457 |  |  |  | 780 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 105.21 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1975 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 282
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 6303 | [14 empty] | 2457
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 9
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 55
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 2393
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 16
Subtotal | [22 empty] | 6303 | [14 empty] | 4914 |  |  |  | 303
Total | [22 empty] | 6303 | [14 empty] | 5217
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1975 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 197
16. |  |  | Steam generation systems | [34 empty] | 74
31. |  |  | Turbine and auxiliaries | [34 empty] | 18
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
42. |  |  | Electrical Power Supply Systems | [34 empty] | 6
Total | [37 empty] | 302

## TAKAHAMA-3
2023 Operating Experience
JP-29 | [8 empty] | TAKAHAMA-3 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-12-12
Thermal power | [12 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-05-09
Gross electrical power | [12 empty] | : |  |  | 870 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-01-17
Reference unit power (net) | [12 empty] | : |  |  | 830 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.28
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.1
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5552.8 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 72.75 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 72.75 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 27.25 %
Load Factor (LF) | [18 empty] | : | 76.37 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 73.08 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2358 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 8.67 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 657.45 | 590.98 |  |  |  | 653.94 |  | 633.38 | [8 empty] | 652.12 |  |  | 625.16 | [6 empty] | 637.79 |  | 637.57 |  |  |  | 355.46 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 108.94 |  |  | 5552.80
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 57.69 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 16.87 |  |  | 72.75
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.99 |  |  |  | 57.69 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 16.87 |  |  | 72.75
LF [%] |  |  |  |  | 106.47 | 105.96 |  |  |  | 105.90 |  | 105.99 | [8 empty] | 105.60 |  |  | 104.61 | [6 empty] | 103.28 |  | 103.25 |  |  |  | 59.48 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 17.64 |  |  | 76.37
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 58.19 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 20.30 |  |  | 73.08
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.01 |  |  |  | 42.31 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 83.13 |  |  | 27.25
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 201395.56 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.27 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 70.79 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.45 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 70.81 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 28.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 69.19 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 6199.46 |  |  | 7426 |  |  |  | 830 | [10 empty] | 83.31 |  |  |  | 83.31 | [5 empty] | 84.14 |  |  | 83.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.69 |  |  |  |  | 0.00
1986 |  |  |  | 6833.58 |  |  | 8215 |  |  |  | 830 | [10 empty] | 93.08 |  |  |  | 93.08 | [5 empty] | 93.99 |  |  | 93.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.92 |  |  |  |  | 0.00
1987 |  |  |  | 6030.38 |  |  | 7265 |  |  |  | 830 | [10 empty] | 82.93 |  |  |  | 82.93 | [5 empty] | 82.94 |  |  | 82.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.07 |  |  |  |  | 0.00
1988 |  |  |  | 5743.18 |  |  | 6948 |  |  |  | 830 | [10 empty] | 79.10 |  |  |  | 79.10 | [5 empty] | 78.77 |  |  | 79.10 |  |  |  | 0.42 |  | 0.33 | [8 empty] | 20.57 |  |  |  |  | 0.00
1989 |  |  |  | 5987.22 |  |  | 7138 |  |  |  | 830 | [10 empty] | 81.48 |  |  |  | 81.48 | [5 empty] | 82.35 |  |  | 81.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.52 |  |  |  |  | 0.00
1990 |  |  |  | 6775.04 |  |  | 8143 |  |  |  | 830 | [10 empty] | 91.88 |  |  |  | 91.88 | [5 empty] | 93.18 |  |  | 92.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.12 |  |  |  |  | 0.00
1991 |  |  |  | 5513.55 |  |  | 6641 |  |  |  | 830 | [10 empty] | 73.86 |  |  |  | 73.86 | [5 empty] | 75.83 |  |  | 75.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.14 |  |  |  |  | 0.00
1992 |  |  |  | 6059.91 |  |  | 7292 |  |  |  | 830 | [10 empty] | 82.22 |  |  |  | 82.22 | [5 empty] | 83.12 |  |  | 83.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.78 |  |  |  |  | 0.00
1993 |  |  |  | 5804.78 |  |  | 6983 |  |  |  | 830 | [10 empty] | 77.57 |  |  |  | 77.57 | [5 empty] | 79.84 |  |  | 79.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.43 |  |  |  |  | 0.00
1994 |  |  |  | 7361.14 |  |  | 8760 |  |  |  | 830 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.24 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 5662.92 |  |  | 6809 |  |  |  | 830 | [10 empty] | 77.00 |  |  |  | 77.00 | [5 empty] | 77.89 |  |  | 77.73 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.00 |  |  |  |  | 0.00
1996 |  |  |  | 5479.31 |  |  | 6576 |  |  |  | 830 | [10 empty] | 74.24 |  |  |  | 74.24 | [5 empty] | 75.15 |  |  | 74.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.76 |  |  |  |  | 0.00
1997 |  |  |  | 6028.89 |  |  | 7206 |  |  |  | 830 | [10 empty] | 81.88 |  |  |  | 81.88 | [5 empty] | 82.92 |  |  | 82.26 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.12 |  |  |  |  | 0.00
1998 |  |  |  | 6853.72 |  |  | 8161 |  |  |  | 830 | [10 empty] | 93.11 |  |  |  | 93.11 | [5 empty] | 94.26 |  |  | 93.16 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.89 |  |  |  |  | 0.00
1999 |  |  |  | 6833.42 |  |  | 8131 |  |  |  | 830 | [10 empty] | 92.80 |  |  |  | 93.85 | [5 empty] | 93.98 |  |  | 92.82 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.15 |  |  |  |  | 1.05
2000 |  |  |  | 5898.88 |  |  | 7023 |  |  |  | 830 | [10 empty] | 79.94 |  |  |  | 79.94 | [5 empty] | 80.91 |  |  | 79.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.06 |  |  |  |  | 0.00
2001 |  |  |  | 6167.20 |  |  | 7340 |  |  |  | 830 | [10 empty] | 83.77 |  |  |  | 83.77 | [5 empty] | 84.82 |  |  | 83.79 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.23 |  |  |  |  | 0.00
2002 |  |  |  | 6463.31 |  |  | 7654 |  |  |  | 830 | [10 empty] | 87.35 |  |  |  | 87.35 | [5 empty] | 88.89 |  |  | 87.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.65 |  |  |  |  | 0.00
2003 |  |  |  | 7355.67 |  |  | 8421 |  |  |  | 830 | [10 empty] | 96.11 |  |  |  | 96.11 | [5 empty] | 101.17 |  |  | 96.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.89 |  |  |  |  | 0.00
2004 |  |  |  | 5625.10 |  |  | 6512 |  |  |  | 830 | [10 empty] | 74.11 |  |  |  | 74.11 | [5 empty] | 77.15 |  |  | 74.13 |  |  |  | 8.83 |  | 11.68 | [8 empty] | 14.21 |  |  |  |  | 0.00
2005 |  |  |  | 5738.44 |  |  | 6656 |  |  |  | 830 | [10 empty] | 75.61 |  |  |  | 75.61 | [5 empty] | 78.92 |  |  | 75.98 |  |  |  | 0.00 |  | 4.58 | [8 empty] | 19.81 |  |  |  |  | 0.00
2006 |  |  |  | 5702.85 |  |  | 6604 |  |  |  | 830 | [10 empty] | 75.04 |  |  |  | 75.04 | [5 empty] | 78.43 |  |  | 75.39 |  |  |  | 0.02 |  | 0.82 | [8 empty] | 24.14 |  |  |  |  | 0.00
2007 |  |  |  | 6847.38 |  |  | 7834 |  |  |  | 830 | [10 empty] | 89.37 |  |  |  | 89.37 | [5 empty] | 94.18 |  |  | 89.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.63 |  |  |  |  | 0.00
2008 |  |  |  | 3102.63 |  |  | 3608 |  |  |  | 830 | [10 empty] | 40.65 |  |  |  | 40.65 | [5 empty] | 42.56 |  |  | 41.07 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 59.35 |  |  |  |  | 0.00
2009 |  |  |  | 5738.94 |  |  | 6525 |  |  |  | 830 | [10 empty] | 74.19 |  |  |  | 74.19 | [5 empty] | 78.93 |  |  | 74.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.81 |  |  |  |  | 0.00
2010 |  |  |  | 6212.08 |  |  | 7006 |  |  |  | 830 | [10 empty] | 79.70 |  |  |  | 79.70 | [5 empty] | 85.44 |  |  | 79.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.30 |  |  |  |  | 0.00
2011 |  |  |  | 7828.83 |  |  | 8760 |  |  |  | 830 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 107.67 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2012 |  |  |  | 1079.91 |  |  | 1223 |  |  |  | 830 | [10 empty] | 13.92 |  |  |  | 13.92 | [5 empty] | 14.81 |  |  | 13.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 86.08 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 768.25 |  |  | 915 |  |  |  | 830 | [10 empty] | 84.77 |  |  |  | 84.77 | [5 empty] | 10.54 |  |  | 10.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.23 |  |  |  |  | 0.00
2017 |  |  |  | 4284.64 |  |  | 4944 |  |  |  | 830 | [10 empty] | 56.03 |  |  |  | 56.03 | [5 empty] | 58.93 |  |  | 56.44 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 43.97 |  |  |  |  | 0.00
2018 |  |  |  | 5595.11 |  |  | 6402 |  |  |  | 830 | [10 empty] | 72.75 |  |  |  | 72.75 | [5 empty] | 76.95 |  |  | 73.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.25 |  |  |  |  | 0.00
2019 |  |  |  | 7651.68 |  |  | 8760 |  |  |  | 830 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 105.24 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2020 |  |  |  | 111.74 |  |  | 131 |  |  |  | 830 | [10 empty] | 1.45 |  |  |  | 1.45 | [5 empty] | 1.53 |  |  | 1.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 98.55 |  |  |  |  | 0.00
2021 |  |  |  | 6178.54 |  |  | 7111 |  |  |  | 830 | [10 empty] | 80.80 |  |  |  | 80.80 | [5 empty] | 84.98 |  |  | 81.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.20 |  |  |  |  | 0.00
2022 |  |  |  | 4534.48 |  |  | 5226 |  |  |  | 830 | [10 empty] | 59.24 |  |  |  | 59.24 | [5 empty] | 62.37 |  |  | 59.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 40.76 |  |  |  |  | 0.00
2023 |  |  |  | 5552.80 |  |  | 6402 |  |  |  | 830 | [10 empty] | 72.75 |  |  |  | 72.75 | [5 empty] | 76.37 |  |  | 73.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 27.25 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 3
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2358 | [14 empty] | 1613
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 17
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 872
H. |  | Nuclear regulatory requirements | [39 empty] | 10
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
M. |  | Governmental requirements or court decisions | [51 empty] | 169
Z. |  | Other | [39 empty] | 26
Subtotal | [22 empty] | 2358 | [14 empty] | 2502 |  |  |  | 39 | [11 empty] | 171
Total | [22 empty] | 2358 | [14 empty] | 2712
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 11
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
16. |  |  | Steam generation systems | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
Total | [37 empty] | 39

## TAKAHAMA-4
2023 Operating Experience
JP-30 | [8 empty] | TAKAHAMA-4 | [26 empty] | JAPAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Owner | [7 empty] | : | KEPCO (Kansai Electric Power Co.)
Reactor Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Turbine Supplier | [7 empty] | : | MHI (MITSUBISHI HEAVY INDUSTRIES, LTD.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / M (3-loop) | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-03-19
Thermal power | [12 empty] | : |  |  | 2660 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-11-01
Gross electrical power | [12 empty] | : |  |  | 870 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-06-05
Reference unit power (net) | [12 empty] | : |  |  | 830 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 321
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.28
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 13 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1800
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.21
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 23
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 48 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DS
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6177.84 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 15.69 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.68 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 15.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 80.68 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.3 %
Load Factor (LF) | [18 empty] | : | 84.97 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 80.92 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1671 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 629.66 | 0.00 |  |  |  | 116.63 |  | 636.80 | [8 empty] | 655.48 |  |  | 627.57 | [6 empty] | 642.20 |  | 642.43 |  |  |  | 620.77 |  |  | 649.96 |  |  | 632.76 | [9 empty] | 323.59 |  |  | 6177.84
EAF [%] |  |  |  |  | 95.61 | 0.00 |  |  |  | 17.89 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 99.99 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 49.38 |  |  | 80.68
UCF [%] |  |  |  |  | 95.61 | 0.00 |  |  |  | 17.89 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.99 |  | 100.00 |  |  |  | 99.99 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 49.38 |  |  | 80.68
LF [%] |  |  |  |  | 101.97 | 0.00 |  |  |  | 18.89 |  | 106.56 | [8 empty] | 106.15 |  |  | 105.02 | [6 empty] | 104.00 |  | 104.03 |  |  |  | 103.88 |  |  | 105.25 |  |  | 105.88 | [9 empty] | 52.40 |  |  | 84.97
OF [%] |  |  |  |  | 95.56 | 0.00 |  |  |  | 20.30 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 49.87 |  |  | 80.92
FLR [%] |  |  |  |  | 4.39 | 100.00 |  |  |  | 82.11 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.69
UCL [%] |  |  |  |  | 4.39 | 100.00 |  |  |  | 82.11 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.02
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.00 |  |  |  | 0.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 50.62 |  |  | 4.30
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 200221.43 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.88 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 71.95 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.82 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 71.98 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 27.19 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 71.32 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 69.54 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 5479.31 |  |  | 6887 |  |  |  | 830 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 101.21 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 5864.02 |  |  | 7073 |  |  |  | 830 | [10 empty] | 79.59 |  |  |  | 79.59 | [5 empty] | 80.65 |  |  | 80.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.41 |  |  |  |  | 0.00
1987 |  |  |  | 5588.52 |  |  | 6743 |  |  |  | 830 | [10 empty] | 76.97 |  |  |  | 76.97 | [5 empty] | 76.86 |  |  | 76.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.03 |  |  |  |  | 0.00
1988 |  |  |  | 6437.90 |  |  | 7666 |  |  |  | 830 | [10 empty] | 87.27 |  |  |  | 87.27 | [5 empty] | 88.30 |  |  | 87.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.73 |  |  |  |  | 0.00
1989 |  |  |  | 6802.70 |  |  | 8167 |  |  |  | 830 | [10 empty] | 93.23 |  |  |  | 93.23 | [5 empty] | 93.56 |  |  | 93.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.77 |  |  |  |  | 0.00
1990 |  |  |  | 5174.56 |  |  | 6233 |  |  |  | 830 | [10 empty] | 68.98 |  |  |  | 68.98 | [5 empty] | 71.17 |  |  | 71.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.02 |  |  |  |  | 0.00
1991 |  |  |  | 6170.12 |  |  | 7409 |  |  |  | 830 | [10 empty] | 83.05 |  |  |  | 83.05 | [5 empty] | 84.86 |  |  | 84.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.95 |  |  |  |  | 0.00
1992 |  |  |  | 6048.41 |  |  | 7265 |  |  |  | 830 | [10 empty] | 81.93 |  |  |  | 81.93 | [5 empty] | 82.96 |  |  | 82.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.07 |  |  |  |  | 0.00
1993 |  |  |  | 7210.91 |  |  | 8578 |  |  |  | 830 | [10 empty] | 97.86 |  |  |  | 97.86 | [5 empty] | 99.18 |  |  | 97.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.14 |  |  |  |  | 0.00
1994 |  |  |  | 5767.17 |  |  | 6861 |  |  |  | 830 | [10 empty] | 78.51 |  |  |  | 78.51 | [5 empty] | 79.32 |  |  | 78.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.49 |  |  |  |  | 0.00
1995 |  |  |  | 5651.76 |  |  | 6785 |  |  |  | 830 | [10 empty] | 76.72 |  |  |  | 76.72 | [5 empty] | 77.73 |  |  | 77.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.28 |  |  |  |  | 0.00
1996 |  |  |  | 5666.52 |  |  | 6785 |  |  |  | 830 | [10 empty] | 76.68 |  |  |  | 76.68 | [5 empty] | 77.72 |  |  | 77.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.32 |  |  |  |  | 0.00
1997 |  |  |  | 7367.27 |  |  | 8760 |  |  |  | 830 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 101.33 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
1998 |  |  |  | 6470.18 |  |  | 7727 |  |  |  | 830 | [10 empty] | 87.79 |  |  |  | 87.79 | [5 empty] | 88.99 |  |  | 88.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.21 |  |  |  |  | 0.00
1999 |  |  |  | 5500.34 |  |  | 6542 |  |  |  | 830 | [10 empty] | 74.64 |  |  |  | 75.83 | [5 empty] | 75.65 |  |  | 74.68 |  |  |  | 3.70 |  | 2.92 | [8 empty] | 21.25 |  |  |  |  | 1.20
2000 |  |  |  | 6099.01 |  |  | 7254 |  |  |  | 830 | [10 empty] | 82.57 |  |  |  | 82.57 | [5 empty] | 83.65 |  |  | 82.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.43 |  |  |  |  | 0.00
2001 |  |  |  | 7364.55 |  |  | 8760 |  |  |  | 830 | [10 empty] | 99.99 |  |  |  | 99.99 | [5 empty] | 101.29 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  |  |  | 0.00
2002 |  |  |  | 6145.46 |  |  | 7316 |  |  |  | 830 | [10 empty] | 83.50 |  |  |  | 83.50 | [5 empty] | 84.52 |  |  | 83.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.50 |  |  |  |  | 0.00
2003 |  |  |  | 6490.21 |  |  | 7531 |  |  |  | 830 | [10 empty] | 85.98 |  |  |  | 85.98 | [5 empty] | 89.26 |  |  | 85.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.02 |  |  |  |  | 0.00
2004 |  |  |  | 5987.82 |  |  | 6868 |  |  |  | 830 | [10 empty] | 78.17 |  |  |  | 78.17 | [5 empty] | 82.13 |  |  | 78.19 |  |  |  | 0.00 |  | 3.71 | [8 empty] | 18.12 |  |  |  |  | 0.00
2005 |  |  |  | 6633.20 |  |  | 7657 |  |  |  | 830 | [10 empty] | 87.35 |  |  |  | 87.35 | [5 empty] | 91.23 |  |  | 87.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.65 |  |  |  |  | 0.00
2006 |  |  |  | 6589.83 |  |  | 7612 |  |  |  | 830 | [10 empty] | 86.56 |  |  |  | 86.56 | [5 empty] | 90.63 |  |  | 86.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.44 |  |  |  |  | 0.00
2007 |  |  |  | 5787.60 |  |  | 6688 |  |  |  | 830 | [10 empty] | 76.04 |  |  |  | 76.04 | [5 empty] | 79.60 |  |  | 76.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.96 |  |  |  |  | 0.00
2008 |  |  |  | 5009.76 |  |  | 5825 |  |  |  | 830 | [10 empty] | 65.56 |  |  |  | 65.56 | [5 empty] | 68.71 |  |  | 66.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 34.44 |  |  |  |  | 0.00
2009 |  |  |  | 7584.98 |  |  | 8760 |  |  |  | 830 | [10 empty] | 99.67 |  |  |  | 99.67 | [5 empty] | 104.32 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.33 |  |  |  |  | 0.00
2010 |  |  |  | 5379.61 |  |  | 6130 |  |  |  | 830 | [10 empty] | 69.45 |  |  |  | 69.45 | [5 empty] | 73.99 |  |  | 69.98 |  |  |  | 5.60 |  | 4.12 | [8 empty] | 26.43 |  |  |  |  | 0.00
2011 |  |  |  | 4320.16 |  |  | 4847 |  |  |  | 830 | [10 empty] | 55.29 |  |  |  | 55.29 | [5 empty] | 59.42 |  |  | 55.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 44.71 |  |  |  |  | 0.00
2012 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2013 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2014 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2015 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 830 | [10 empty] | 81.24 |  |  |  | 81.24 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 2.96 |  | 2.48 | [8 empty] | 16.28 |  |  |  |  | 0.00
2017 |  |  |  | 4636.34 |  |  | 5362 |  |  |  | 830 | [10 empty] | 84.51 |  |  |  | 84.51 | [5 empty] | 63.77 |  |  | 61.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.49 |  |  |  |  | 0.00
2018 |  |  |  | 5374.49 |  |  | 6167 |  |  |  | 830 | [10 empty] | 70.04 |  |  |  | 70.04 | [5 empty] | 73.92 |  |  | 70.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.96 |  |  |  |  | 0.00
2019 |  |  |  | 5463.11 |  |  | 6251 |  |  |  | 830 | [10 empty] | 71.31 |  |  |  | 71.31 | [5 empty] | 75.14 |  |  | 71.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.69 |  |  |  |  | 0.00
2020 |  |  |  | 5187.90 |  |  | 5969 |  |  |  | 830 | [10 empty] | 67.55 |  |  |  | 67.55 | [5 empty] | 71.16 |  |  | 67.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.45 |  |  |  |  | 0.00
2021 |  |  |  | 5443.67 |  |  | 6247 |  |  |  | 830 | [10 empty] | 70.94 |  |  |  | 70.94 | [5 empty] | 74.87 |  |  | 71.31 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.06 |  |  |  |  | 0.00
2022 |  |  |  | 4502.02 |  |  | 5132 |  |  |  | 830 | [10 empty] | 58.17 |  |  |  | 58.17 | [5 empty] | 61.92 |  |  | 58.58 |  |  |  | 0.00 |  | 3.54 | [8 empty] | 38.29 |  |  |  |  | 0.00
2023 |  |  |  | 6177.84 |  |  | 7089 |  |  |  | 830 | [10 empty] | 80.68 |  |  |  | 80.68 | [5 empty] | 84.97 |  |  | 80.92 |  |  |  | 15.69 |  | 15.02 | [8 empty] | 4.30 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 1338 | [14 empty] | 65
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 373 | [14 empty] | 1408
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 1000
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
M. |  | Governmental requirements or court decisions | [51 empty] | 243
Z. |  | Other | [39 empty] | 9
Subtotal | [22 empty] | 373 |  |  |  | 1338 | [10 empty] | 2408 |  |  |  | 74 | [11 empty] | 246
Total | [22 empty] | 1711 | [14 empty] | 2728
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [19 empty] | 1338 | [14 empty] | 42
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 9
41. |  |  | Main Generator Systems | [34 empty] | 15
Total | [22 empty] | 1338 | [14 empty] | 74