## CHASNUPP-1
2023 Operating Experience
PK-2 | [8 empty] | CHASNUPP-1 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | STW (Shanghai Turbine Works)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1993-08-01
Thermal power | [12 empty] | : |  |  | 999 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2000-06-13
Gross electrical power | [12 empty] | : |  |  | 325 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2000-09-15
Reference unit power (net) | [12 empty] | : |  |  | 300 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 23 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.26
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 14 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 30000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.486 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.34
| Active core height/length [m] | [13 empty] | : |  |  | 2.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.59 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2322.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.86 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.11 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 4.74 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.8 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.45 %
Load Factor (LF) | [18 empty] | : | 88.38 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 4.7 %
Operating Factor (OF) | [18 empty] | : | 92.82 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 629 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 209.17 | 191.63 |  |  |  | 170.94 |  | 211.26 | [8 empty] | 221.93 |  |  | 214.74 | [6 empty] | 193.82 |  | 147.08 |  |  |  | 209.55 |  |  | 196.44 |  |  | 214.77 | [9 empty] | 141.35 |  |  | 2322.68
EAF [%] |  |  |  |  | 93.12 | 94.45 |  |  |  | 75.75 |  | 97.81 | [8 empty] | 99.43 |  |  | 99.41 | [6 empty] | 86.84 |  | 65.90 |  |  |  | 97.01 |  |  | 87.66 |  |  | 98.93 | [9 empty] | 62.89 |  |  | 88.11
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 87.15 |  | 67.53 |  |  |  | 100.00 |  |  | 89.48 |  |  | 100.00 | [9 empty] | 71.11 |  |  | 92.80
LF [%] |  |  |  |  | 93.71 | 95.06 |  |  |  | 76.59 |  | 97.81 | [8 empty] | 99.43 |  |  | 99.41 | [6 empty] | 86.84 |  | 65.90 |  |  |  | 97.01 |  |  | 88.01 |  |  | 99.43 | [9 empty] | 63.33 |  |  | 88.38
OF [%] |  |  |  |  | 95.30 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 88.04 |  | 68.82 |  |  |  | 100.00 |  |  | 91.80 |  |  | 99.72 | [9 empty] | 71.77 |  |  | 92.82
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 12.85 |  | 32.47 |  |  |  | 0.00 |  |  | 10.52 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.86
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 12.85 |  | 32.47 |  |  |  | 0.00 |  |  | 10.52 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.74
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 28.89 |  |  | 2.45
XUF [%] |  |  |  |  | 6.88 | 5.55 |  |  |  | 24.25 |  | 2.19 | [8 empty] | 0.57 |  |  | 0.59 | [6 empty] | 0.32 |  | 1.63 |  |  |  | 2.99 |  |  | 1.82 |  |  | 1.07 | [9 empty] | 8.22 |  |  | 4.70
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 47998.31 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.62 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.99 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.48 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.55 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.97 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.02 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.56 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.05 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2000 |  |  |  | 529.15 |  |  | 1860 |  |  |  | 300 | [10 empty] | 72.19 |  |  |  | 72.19 | [5 empty] | 68.69 |  |  | 72.43 |  |  |  | 19.54 |  | 17.53 | [8 empty] | 10.28 |  |  |  |  | 0.00
2001 |  |  |  | 1581.75 |  |  | 5918 |  |  |  | 300 | [10 empty] | 60.06 |  |  |  | 62.44 | [5 empty] | 60.19 |  |  | 67.56 |  |  |  | 37.40 |  | 37.31 | [8 empty] | 0.25 |  |  |  |  | 2.38
2002 |  |  |  | 1356.00 |  |  | 4790 |  |  |  | 300 | [10 empty] | 52.25 |  |  |  | 53.69 | [5 empty] | 51.60 |  |  | 54.68 |  |  |  | 20.87 |  | 16.73 | [8 empty] | 29.58 |  |  |  |  | 1.44
2003 |  |  |  | 1809.80 |  |  | 6879 |  |  |  | 300 | [10 empty] | 68.85 |  |  |  | 68.85 | [5 empty] | 68.87 |  |  | 78.53 |  |  |  | 21.84 |  | 24.04 | [8 empty] | 7.11 |  |  |  |  | 0.00
2004 |  |  |  | 1750.71 |  |  | 5949 |  |  |  | 300 | [10 empty] | 66.35 |  |  |  | 68.12 | [5 empty] | 66.44 |  |  | 67.73 |  |  |  | 4.20 |  | 13.12 | [8 empty] | 18.76 |  |  |  |  | 1.77
2005 |  |  |  | 2155.19 |  |  | 7458 |  |  |  | 300 | [10 empty] | 81.92 |  |  |  | 81.92 | [5 empty] | 82.01 |  |  | 85.14 |  |  |  | 3.83 |  | 3.26 | [8 empty] | 14.82 |  |  |  |  | 0.00
2006 |  |  |  | 2532.91 |  |  | 8569 |  |  |  | 300 | [10 empty] | 98.19 |  |  |  | 98.19 | [5 empty] | 96.38 |  |  | 97.82 |  |  |  | 0.91 |  | 0.90 | [8 empty] | 0.91 |  |  |  |  | 0.00
2007 |  |  |  | 1949.13 |  |  | 6669 |  |  |  | 300 | [10 empty] | 75.22 |  |  |  | 75.55 | [5 empty] | 74.17 |  |  | 76.13 |  |  |  | 2.98 |  | 7.76 | [8 empty] | 16.69 |  |  |  |  | 0.33
2008 |  |  |  | 1356.45 |  |  | 4795 |  |  |  | 300 | [10 empty] | 52.25 |  |  |  | 52.40 | [5 empty] | 51.47 |  |  | 54.59 |  |  |  | 1.70 |  | 0.90 | [8 empty] | 46.69 |  |  |  |  | 0.15
2009 |  |  |  | 2145.87 |  |  | 7379 |  |  |  | 300 | [10 empty] | 82.80 |  |  |  | 82.82 | [5 empty] | 81.65 |  |  | 84.24 |  |  |  | 10.86 |  | 11.69 | [8 empty] | 5.49 |  |  |  |  | 0.02
2010 |  |  |  | 2095.76 |  |  | 7160 |  |  |  | 300 | [10 empty] | 80.66 |  |  |  | 80.66 | [5 empty] | 79.75 |  |  | 81.74 |  |  |  | 0.96 |  | 0.96 | [8 empty] | 18.37 |  |  |  |  | 0.00
2011 |  |  |  | 2061.67 |  |  | 7008 |  |  |  | 300 | [10 empty] | 79.31 |  |  |  | 79.31 | [5 empty] | 78.45 |  |  | 80.00 |  |  |  | 3.04 |  | 2.83 | [8 empty] | 17.87 |  |  |  |  | 0.00
2012 |  |  |  | 2489.25 |  |  | 8370 |  |  |  | 300 | [10 empty] | 94.74 |  |  |  | 94.79 | [5 empty] | 94.46 |  |  | 95.29 |  |  |  | 2.34 |  | 2.27 | [8 empty] | 2.94 |  |  |  |  | 0.05
2013 |  |  |  | 2189.64 |  |  | 7481 |  |  |  | 300 | [10 empty] | 84.04 |  |  |  | 84.04 | [5 empty] | 83.32 |  |  | 85.40 |  |  |  | 4.53 |  | 4.38 | [8 empty] | 11.59 |  |  |  |  | 0.00
2014 |  |  |  | 2178.22 |  |  | 7434 |  |  |  | 300 | [10 empty] | 85.57 |  |  |  | 85.61 | [5 empty] | 82.89 |  |  | 84.86 |  |  |  | 3.64 |  | 3.23 | [8 empty] | 11.16 |  |  |  |  | 0.04
2015 |  |  |  | 1627.53 |  |  | 5831 |  |  |  | 300 | [10 empty] | 64.28 |  |  |  | 65.44 | [5 empty] | 61.93 |  |  | 66.56 |  |  |  | 3.33 |  | 15.04 | [8 empty] | 19.52 |  |  |  |  | 1.17
2016 |  |  |  | 2326.46 |  |  | 8291 |  |  |  | 300 | [10 empty] | 89.27 |  |  |  | 89.27 | [5 empty] | 88.28 |  |  | 94.39 |  |  |  | 0.82 |  | 5.23 | [8 empty] | 5.50 |  |  |  |  | 0.00
2017 |  |  |  | 2157.86 |  |  | 7391 |  |  |  | 300 | [10 empty] | 82.53 |  |  |  | 82.55 | [5 empty] | 82.11 |  |  | 84.37 |  |  |  | 2.48 |  | 2.10 | [8 empty] | 15.36 |  |  |  |  | 0.01
2018 |  |  |  | 2017.02 |  |  | 6950 |  |  |  | 300 | [10 empty] | 79.42 |  |  |  | 79.52 | [5 empty] | 76.75 |  |  | 79.34 |  |  |  | 7.15 |  | 6.12 | [8 empty] | 14.36 |  |  |  |  | 0.10
2019 |  |  |  | 2335.20 |  |  | 7907 |  |  |  | 300 | [10 empty] | 90.23 |  |  |  | 90.33 | [5 empty] | 88.86 |  |  | 90.26 |  |  |  | 2.44 |  | 2.26 | [8 empty] | 7.41 |  |  |  |  | 0.10
2020 |  |  |  | 2277.56 |  |  | 7682 |  |  |  | 300 | [10 empty] | 86.43 |  |  |  | 86.65 | [5 empty] | 86.43 |  |  | 87.45 |  |  |  | 1.31 |  | 1.15 | [8 empty] | 12.20 |  |  |  |  | 0.22
2021 |  |  |  | 2209.57 |  |  | 7546 |  |  |  | 300 | [10 empty] | 85.84 |  |  |  | 85.89 | [5 empty] | 84.08 |  |  | 86.14 |  |  |  | 1.46 |  | 1.27 | [8 empty] | 12.84 |  |  |  |  | 0.05
2022 |  |  |  | 2330.60 |  |  | 8020 |  |  |  | 300 | [10 empty] | 90.46 |  |  |  | 90.99 | [5 empty] | 88.68 |  |  | 91.55 |  |  |  | 1.92 |  | 1.78 | [8 empty] | 7.23 |  |  |  |  | 0.53
2023 |  |  |  | 2322.68 |  |  | 8131 |  |  |  | 300 | [10 empty] | 88.11 |  |  |  | 92.80 | [5 empty] | 88.38 |  |  | 92.82 |  |  |  | 4.86 |  | 4.74 | [8 empty] | 2.45 |  |  |  |  | 4.70
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2000 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 382 | [14 empty] | 486
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 210 | [14 empty] | 990 |  |  |  | 6
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 58
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 37 | [19 empty] | 86
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 13
L. |  | Human factor related | [39 empty] | 5
P. |  | Fire | [39 empty] | 5
Z. |  | Other | [39 empty] | 20
Subtotal | [22 empty] | 210 |  |  |  | 382 | [6 empty] | 37 |  |  |  | 1051 |  |  |  | 523 | [11 empty] | 99
Total | [22 empty] | 629 | [14 empty] | 1673
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2000 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 38
12. |  |  | Reactor I&C Systems | [19 empty] | 61 | [14 empty] | 26
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 7
14. |  |  | Safety Systems | [34 empty] | 36
15. |  |  | Reactor Cooling Systems | [34 empty] | 109
16. |  |  | Steam generation systems | [34 empty] | 6
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 124
32. |  |  | Feedwater and Main Steam System | [19 empty] | 321 | [14 empty] | 40
33. |  |  | Circulating Water System | [34 empty] | 7
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 31
42. |  |  | Electrical Power Supply Systems | [34 empty] | 89
Total | [22 empty] | 382 | [14 empty] | 517
Highlights (2023)
2023 Q1 --- Plant remained critical for 85.33 days. --- Plant was started on 02-01-2022 after Manual shutdown (on 29-12-2022) due to abnormal degradation of Condenser Vacuum. --- Plant faced 02 automatic scrams while critical: 1) Reactor tripped on SG-A Hi Hi level signal due to malfunctioning of SMF-V03A. (January 18, 2022, 15:46 Hrs.) 2) Reactor tripped on RCP-B (SRC-004BRP) tripping. (March 30, 2022, 00:32 Hrs.) 2023 Q2 --- Plant remained critical for 91.0 days. 2023 Q3 --- Plant remained critical for 78.87 days. --- Plant faced Spurious Activation of the Containment Spray and Containment Phase–B Isolation during Monthly Functional Test of Reactor Protection and Engineering Safeguard System test of Channel B1 on July 27th, 2023 (1117 Hrs.). --- Plant faced 01 automatic scrams while critical: 1) Reactor tripped on Steam Generator (SG-B) Level Hi-Hi due to malfunction of SG-B level control. (July 28th, 2023, 06:42 Hrs.) 2023 Q4 --- Plant remained critical for 81.03 days. --- Plant faced power reduction and manual shutdown due to problem in control rod drive mechanism (A1-2 dropped to zero position) on October 6th, 2023 (21:05 Hrs.). --- Plant faced House load at over frequency of Grid on November 21st, 2023 (00:58 Hrs.). --- Plant entered in Refueling Outage (RFO-16) on December 23rd, 2023 (05:38 Hrs.).

## CHASNUPP-2
2023 Operating Experience
PK-3 | [8 empty] | CHASNUPP-2 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2005-12-28
Thermal power | [12 empty] | : |  |  | 999 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2011-03-14
Gross electrical power | [12 empty] | : |  |  | 325 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2011-05-18
Reference unit power (net) | [12 empty] | : |  |  | 300 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 12 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.26
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 14 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 32000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.486 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.34
| Active core height/length [m] | [13 empty] | : |  |  | 2.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.59 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.6 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.3 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.56 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.63 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.81 %
Load Factor (LF) | [18 empty] | : | 93.65 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.33 %
Operating Factor (OF) | [18 empty] | : | 92.97 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 210.95 | 201.35 |  |  |  | 208.65 |  | 59.27 | [8 empty] | 230.79 |  |  | 221.03 | [6 empty] | 229.50 |  | 230.02 |  |  |  | 218.69 |  |  | 225.17 |  |  | 209.33 | [9 empty] | 216.38 |  |  | 2461.13
EAF [%] |  |  |  |  | 90.26 | 95.50 |  |  |  | 90.18 |  | 26.77 | [8 empty] | 99.47 |  |  | 99.45 | [6 empty] | 99.33 |  | 99.53 |  |  |  | 98.45 |  |  | 97.22 |  |  | 93.06 | [9 empty] | 93.52 |  |  | 90.30
UCF [%] |  |  |  |  | 96.61 | 96.50 |  |  |  | 90.87 |  | 26.77 | [8 empty] | 99.99 |  |  | 99.98 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.85 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.63
LF [%] |  |  |  |  | 94.51 | 99.87 |  |  |  | 93.48 |  | 27.44 | [8 empty] | 103.40 |  |  | 102.33 | [6 empty] | 102.82 |  | 103.05 |  |  |  | 101.25 |  |  | 100.88 |  |  | 96.91 | [9 empty] | 96.95 |  |  | 93.65
OF [%] |  |  |  |  | 92.74 | 100.00 |  |  |  | 91.67 |  | 30.83 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.72 | [9 empty] | 100.00 |  |  | 92.97
FLR [%] |  |  |  |  | 3.39 | 3.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.60
UCL [%] |  |  |  |  | 3.39 | 3.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.56
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 9.13 |  | 73.23 | [8 empty] | 0.00 |  |  | 0.02 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.15 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.81
XUF [%] |  |  |  |  | 6.36 | 1.00 |  |  |  | 0.68 |  | 0.00 | [8 empty] | 0.52 |  |  | 0.54 | [6 empty] | 0.67 |  | 0.47 |  |  |  | 1.55 |  |  | 2.63 |  |  | 6.94 | [9 empty] | 6.48 |  |  | 2.33
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 0 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.08 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.87 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.31 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.16 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.44 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.32 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2011 |  |  |  | 1570.98 |  |  | 5766 |  |  |  | 300 | [10 empty] | 88.25 |  |  |  | 88.25 | [5 empty] | 85.28 |  |  | 86.94 |  |  |  | 7.81 |  | 9.56 | [8 empty] | 2.19 |  |  |  |  | 0.00
2012 |  |  |  | 2215.76 |  |  | 7864 |  |  |  | 300 | [10 empty] | 83.74 |  |  |  | 83.77 | [5 empty] | 84.08 |  |  | 89.53 |  |  |  | 12.44 |  | 11.96 | [8 empty] | 4.27 |  |  |  |  | 0.03
2013 |  |  |  | 1700.82 |  |  | 6308 |  |  |  | 300 | [10 empty] | 64.68 |  |  |  | 64.68 | [5 empty] | 64.72 |  |  | 72.01 |  |  |  | 7.80 |  | 13.73 | [8 empty] | 21.59 |  |  |  |  | 0.00
2014 |  |  |  | 2190.36 |  |  | 7546 |  |  |  | 300 | [10 empty] | 83.93 |  |  |  | 83.93 | [5 empty] | 83.35 |  |  | 86.14 |  |  |  | 3.49 |  | 3.04 | [8 empty] | 13.03 |  |  |  |  | 0.00
2015 |  |  |  | 2361.48 |  |  | 7855 |  |  |  | 300 | [10 empty] | 89.21 |  |  |  | 89.74 | [5 empty] | 89.86 |  |  | 89.67 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 10.24 |  |  |  |  | 0.54
2016 |  |  |  | 2335.43 |  |  | 7718 |  |  |  | 300 | [10 empty] | 88.18 |  |  |  | 88.18 | [5 empty] | 88.62 |  |  | 87.86 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.82 |  |  |  |  | 0.00
2017 |  |  |  | 2584.57 |  |  | 8520 |  |  |  | 300 | [10 empty] | 97.61 |  |  |  | 97.61 | [5 empty] | 98.35 |  |  | 97.26 |  |  |  | 0.87 |  | 0.86 | [8 empty] | 1.53 |  |  |  |  | 0.00
2018 |  |  |  | 2296.39 |  |  | 7679 |  |  |  | 300 | [10 empty] | 88.15 |  |  |  | 88.16 | [5 empty] | 87.38 |  |  | 87.66 |  |  |  | 1.05 |  | 0.94 | [8 empty] | 10.91 |  |  |  |  | 0.00
2019 |  |  |  | 2263.06 |  |  | 7573 |  |  |  | 300 | [10 empty] | 86.37 |  |  |  | 86.41 | [5 empty] | 86.11 |  |  | 86.45 |  |  |  | 1.79 |  | 1.57 | [8 empty] | 12.02 |  |  |  |  | 0.04
2020 |  |  |  | 2167.47 |  |  | 7379 |  |  |  | 300 | [10 empty] | 81.33 |  |  |  | 83.13 | [5 empty] | 82.25 |  |  | 84.01 |  |  |  | 4.82 |  | 4.21 | [8 empty] | 12.66 |  |  |  |  | 1.80
2021 |  |  |  | 2602.18 |  |  | 8493 |  |  |  | 300 | [10 empty] | 98.19 |  |  |  | 98.41 | [5 empty] | 99.02 |  |  | 96.95 |  |  |  | 1.54 |  | 1.54 | [8 empty] | 0.05 |  |  |  |  | 0.22
2022 |  |  |  | 2384.89 |  |  | 7902 |  |  |  | 300 | [10 empty] | 89.90 |  |  |  | 90.53 | [5 empty] | 90.75 |  |  | 90.21 |  |  |  | 0.39 |  | 0.35 | [8 empty] | 9.12 |  |  |  |  | 0.63
2023 |  |  |  | Data not provided
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2011 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 19 | [14 empty] | 269
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 561 | [14 empty] | 687
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 9
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 37 | [19 empty] | 72
Subtotal | [22 empty] | 561 |  |  |  | 19 | [6 empty] | 37 |  |  |  | 696 |  |  |  | 269 | [11 empty] | 72
Total | [22 empty] | 617 | [14 empty] | 1037
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2011 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 25
15. |  |  | Reactor Cooling Systems | [34 empty] | 66
16. |  |  | Steam generation systems | [19 empty] | 19 | [14 empty] | 16
31. |  |  | Turbine and auxiliaries | [34 empty] | 41
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
33. |  |  | Circulating Water System | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 41
42. |  |  | Electrical Power Supply Systems | [34 empty] | 62
Total | [22 empty] | 19 | [14 empty] | 264

## CHASNUPP-3
2023 Operating Experience
PK-4 | [8 empty] | CHASNUPP-3 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2011-05-28
Thermal power | [12 empty] | : |  |  | 999 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-10-15
Gross electrical power | [12 empty] | : |  |  | 340 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-12-06
Reference unit power (net) | [12 empty] | : |  |  | 315 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.26
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 14 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 32000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.486 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.34
| Active core height/length [m] | [13 empty] | : |  |  | 2.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.59 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.19 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.12 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.9 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.07 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.02 %
Load Factor (LF) | [18 empty] | : | 80.24 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 4.96 %
Operating Factor (OF) | [18 empty] | : | 85.47 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 216.72 | 200.70 |  |  |  | 231.21 |  | 225.59 | [8 empty] | 205.79 |  |  | 114.65 | [6 empty] | 0.00 |  | 100.04 |  |  |  | 226.19 |  |  | 234.36 |  |  | 224.36 | [9 empty] | 234.53 |  |  | 2214.14
EAF [%] |  |  |  |  | 92.09 | 94.19 |  |  |  | 98.66 |  | 99.82 | [8 empty] | 87.81 |  |  | 50.55 | [6 empty] | 0.00 |  | 42.68 |  |  |  | 99.73 |  |  | 100.00 |  |  | 98.43 | [9 empty] | 99.70 |  |  | 80.12
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.89 |  | 99.99 | [8 empty] | 99.99 |  |  | 80.41 | [6 empty] | 0.00 |  | 43.38 |  |  |  | 99.96 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.07
LF [%] |  |  |  |  | 92.47 | 94.81 |  |  |  | 98.66 |  | 99.47 | [8 empty] | 87.81 |  |  | 50.55 | [6 empty] | 0.00 |  | 42.68 |  |  |  | 99.73 |  |  | 100.00 |  |  | 98.92 | [9 empty] | 100.07 |  |  | 80.24
OF [%] |  |  |  |  | 95.16 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 81.25 | [6 empty] | 0.00 |  | 52.15 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.72 | [9 empty] | 100.00 |  |  | 85.47
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.11 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 33.96 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.19
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.11 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 22.31 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.90
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.01 |  |  | 19.59 | [6 empty] | 100.00 |  | 34.31 |  |  |  | 0.04 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.02
XUF [%] |  |  |  |  | 7.91 | 5.81 |  |  |  | 1.23 |  | 0.17 | [8 empty] | 12.18 |  |  | 29.86 | [6 empty] | 0.00 |  | 0.70 |  |  |  | 0.22 |  |  | 0.00 |  |  | 1.57 | [9 empty] | 0.30 |  |  | 4.96
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 0 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.39 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.21 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.27 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.67 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.06 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 85.71 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.46 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.87 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 344.98 |  |  | 1436 |  |  |  | 315 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.84 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 2542.08 |  |  | 8256 |  |  |  | 315 | [10 empty] | 93.53 |  |  |  | 94.13 | [5 empty] | 92.12 |  |  | 94.25 |  |  |  | 5.36 |  | 5.33 | [8 empty] | 0.54 |  |  |  |  | 0.60
2018 |  |  |  | 2145.22 |  |  | 7152 |  |  |  | 315 | [10 empty] | 80.37 |  |  |  | 81.52 | [5 empty] | 77.74 |  |  | 81.64 |  |  |  | 0.66 |  | 0.54 | [8 empty] | 17.94 |  |  |  |  | 1.16
2019 |  |  |  | 2247.57 |  |  | 7508 |  |  |  | 315 | [10 empty] | 85.26 |  |  |  | 86.16 | [5 empty] | 81.45 |  |  | 85.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.84 |  |  |  |  | 0.90
2020 |  |  |  | 2444.19 |  |  | 7931 |  |  |  | 315 | [10 empty] | 89.15 |  |  |  | 89.70 | [5 empty] | 88.33 |  |  | 90.29 |  |  |  | 0.49 |  | 0.44 | [8 empty] | 9.86 |  |  |  |  | 0.55
2021 |  |  |  | 2513.45 |  |  | 8649 |  |  |  | 315 | [10 empty] | 99.02 |  |  |  | 99.16 | [5 empty] | 91.09 |  |  | 98.73 |  |  |  | 0.73 |  | 0.73 | [8 empty] | 0.11 |  |  |  |  | 0.14
2022 |  |  |  | 2426.79 |  |  | 8071 |  |  |  | 315 | [10 empty] | 89.05 |  |  |  | 91.08 | [5 empty] | 87.95 |  |  | 92.13 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 8.88 |  |  |  |  | 2.03
2023 |  |  |  | Data not provided
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2016 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 137 | [14 empty] | 97
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1099 | [14 empty] | 748
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 38 | [19 empty] | 48
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 7
Subtotal | [22 empty] | 1099 |  |  |  | 137 | [6 empty] | 38 |  |  |  | 748 |  |  |  | 97 | [11 empty] | 55
Total | [22 empty] | 1274 | [14 empty] | 900
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2016 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 24
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 39
31. |  |  | Turbine and auxiliaries | [19 empty] | 137 | [14 empty] | 25
33. |  |  | Circulating Water System | [34 empty] | 4
Total | [22 empty] | 137 | [14 empty] | 97

## CHASNUPP-4
2023 Operating Experience
PK-5 | [8 empty] | CHASNUPP-4 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CNNC (CHINA NATIONAL NUCLEAR CORPORATION)
Turbine Supplier | [7 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / CNP-300 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2011-12-18
Thermal power | [12 empty] | : |  |  | 999 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2017-06-25
Gross electrical power | [12 empty] | : |  |  | 340 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2017-09-19
Reference unit power (net) | [12 empty] | : |  |  | 313 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 6 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.2
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 315.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.26
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.4 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 14 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 32000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.486 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.34
| Active core height/length [m] | [13 empty] | : |  |  | 2.9 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.59 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 34 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 0 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.44 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.97 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.03 %
Load Factor (LF) | [18 empty] | : | 90.89 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 3.53 %
Operating Factor (OF) | [18 empty] | : | 93.76 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 104.33 | 157.77 |  |  |  | 232.32 |  | 223.14 | [8 empty] | 231.36 |  |  | 223.30 | [6 empty] | 214.78 |  | 230.83 |  |  |  | 218.44 |  |  | 228.70 |  |  | 211.42 | [9 empty] | 215.75 |  |  | 2492.14
EAF [%] |  |  |  |  | 44.20 | 74.13 |  |  |  | 98.80 |  | 98.72 | [8 empty] | 99.32 |  |  | 99.09 | [6 empty] | 92.23 |  | 99.12 |  |  |  | 96.93 |  |  | 97.42 |  |  | 92.82 | [9 empty] | 91.69 |  |  | 90.44
UCF [%] |  |  |  |  | 48.55 | 78.43 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.99 | [6 empty] | 100.00 |  | 99.90 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.97
LF [%] |  |  |  |  | 44.80 | 75.01 |  |  |  | 99.77 |  | 99.01 | [8 empty] | 99.35 |  |  | 99.09 | [6 empty] | 92.23 |  | 99.12 |  |  |  | 96.93 |  |  | 98.21 |  |  | 93.81 | [9 empty] | 92.65 |  |  | 90.89
OF [%] |  |  |  |  | 49.06 | 82.74 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 93.41 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 99.58 | [9 empty] | 100.00 |  |  | 93.76
FLR [%] |  |  |  |  | 0.05 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 51.43 | 21.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.10 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.03
XUF [%] |  |  |  |  | 4.35 | 4.31 |  |  |  | 1.20 |  | 1.28 | [8 empty] | 0.68 |  |  | 0.91 | [6 empty] | 7.77 |  | 0.77 |  |  |  | 3.07 |  |  | 2.58 |  |  | 7.18 | [9 empty] | 8.31 |  |  | 3.53
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 0 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.93 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.19 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.86 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 91.44 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.71 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.11 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.25 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.23 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2017 |  |  |  | 484.17 |  |  | 1946 |  |  |  | 313 | [10 empty] | 95.21 |  |  |  | 95.22 | [5 empty] | 35.01 |  |  | 38.13 |  |  |  | 4.78 |  | 4.78 | [8 empty] | 0.00 |  |  |  |  | 0.01
2018 |  |  |  | 2557.08 |  |  | 8452 |  |  |  | 313 | [10 empty] | 95.74 |  |  |  | 97.25 | [5 empty] | 93.26 |  |  | 96.48 |  |  |  | 2.63 |  | 2.63 | [8 empty] | 0.12 |  |  |  |  | 1.51
2019 |  |  |  | 2181.00 |  |  | 7237 |  |  |  | 313 | [10 empty] | 81.52 |  |  |  | 81.88 | [5 empty] | 79.54 |  |  | 82.61 |  |  |  | 0.80 |  | 0.66 | [8 empty] | 17.46 |  |  |  |  | 0.36
2020 |  |  |  | 2474.85 |  |  | 8068 |  |  |  | 313 | [10 empty] | 90.76 |  |  |  | 91.09 | [5 empty] | 90.01 |  |  | 91.85 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 8.86 |  |  |  |  | 0.34
2021 |  |  |  | 2165.43 |  |  | 7407 |  |  |  | 313 | [10 empty] | 84.32 |  |  |  | 84.42 | [5 empty] | 78.98 |  |  | 84.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.58 |  |  |  |  | 0.11
2022 |  |  |  | 2654.75 |  |  | 8673 |  |  |  | 313 | [10 empty] | 97.10 |  |  |  | 99.04 | [5 empty] | 96.82 |  |  | 99.01 |  |  |  | 0.83 |  | 0.83 | [8 empty] | 0.13 |  |  |  |  | 1.94
2023 |  |  |  | Data not provided
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2017 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 0 | [14 empty] | 56
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 494 | [14 empty] | 641
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 52 | [19 empty] | 240
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 7
Subtotal | [22 empty] | 494 |  |  |  | 0 | [6 empty] | 52 |  |  |  | 641 |  |  |  | 56 | [11 empty] | 247
Total | [22 empty] | 546 | [14 empty] | 944
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2017 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 3
16. |  |  | Steam generation systems | [19 empty] | 0 | [14 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 19
41. |  |  | Main Generator Systems | [34 empty] | 31
Total | [22 empty] | 0 | [14 empty] | 53

## KANUPP-2
2023 Operating Experience
PK-6 | [8 empty] | KANUPP-2 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CZEC (China Zhongyuan Engineering Corporation)
Turbine Supplier | [7 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / ACP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2015-08-20
Thermal power | [12 empty] | : |  |  | 3060 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2021-03-18
Gross electrical power | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-05-21
Reference unit power (net) | [12 empty] | : |  |  | 1017 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6136.8 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.91 %
Energy Availability Factor (EAF) | [18 empty] | : | 71.67 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.84 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.08 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 18.08 %
Load Factor (LF) | [18 empty] | : | 68.88 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.41 %
Operating Factor (OF) | [18 empty] | : | 75 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2190 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 535.21 | 587.95 |  |  |  | 638.49 |  | 705.83 | [8 empty] | 654.61 |  |  | 679.59 | [6 empty] | 726.63 |  | 624.92 |  |  |  | 723.40 |  |  | 260.17 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6136.80
EAF [%] |  |  |  |  | 90.42 | 100.00 |  |  |  | 87.71 |  | 95.57 | [8 empty] | 84.40 |  |  | 92.09 | [6 empty] | 94.99 |  | 82.89 |  |  |  | 100.00 |  |  | 34.75 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 71.67
UCF [%] |  |  |  |  | 98.07 | 100.00 |  |  |  | 93.65 |  | 100.00 | [8 empty] | 92.75 |  |  | 92.41 | [6 empty] | 94.99 |  | 82.89 |  |  |  | 100.00 |  |  | 36.56 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 74.08
LF [%] |  |  |  |  | 70.73 | 86.03 |  |  |  | 84.38 |  | 96.39 | [8 empty] | 86.51 |  |  | 92.81 | [6 empty] | 96.03 |  | 82.59 |  |  |  | 98.79 |  |  | 34.38 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 68.88
OF [%] |  |  |  |  | 88.84 | 100.00 |  |  |  | 94.89 |  | 100.00 | [8 empty] | 94.22 |  |  | 95.28 | [6 empty] | 97.85 |  | 94.62 |  |  |  | 100.00 |  |  | 36.56 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 75.00
FLR [%] |  |  |  |  | 1.93 | 0.00 |  |  |  | 6.35 |  | 0.00 | [8 empty] | 7.25 |  |  | 7.59 | [6 empty] | 5.01 |  | 17.11 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.91
UCL [%] |  |  |  |  | 1.93 | 0.00 |  |  |  | 6.35 |  | 0.00 | [8 empty] | 7.25 |  |  | 7.59 | [6 empty] | 5.01 |  | 17.11 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 47.31 |  |  | 7.84
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 63.44 |  |  | 100.00 | [9 empty] | 52.69 |  |  | 18.08
XUF [%] |  |  |  |  | 7.65 | 0.00 |  |  |  | 5.94 |  | 4.43 | [8 empty] | 8.35 |  |  | 0.32 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 1.81 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.41
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 18586.05 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.6 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.25 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.18 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.53 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.09 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.93 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.72 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2021 |  |  |  | 6208.89 |  |  | 5910 |  |  |  | 1014 | [10 empty] | 98.64 |  |  |  | 98.64 | [5 empty] | 98.78 |  |  | 96.42 |  |  |  | 1.36 |  | 1.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
2022 |  |  |  | 6240.36 |  |  | 6540 |  |  |  | 1017 | [10 empty] | 70.32 |  |  |  | 72.91 | [5 empty] | 70.05 |  |  | 74.66 |  |  |  | 11.90 |  | 12.80 | [8 empty] | 14.30 |  |  |  |  | 2.59
2023 |  |  |  | 6136.80 |  |  | 6570 |  |  |  | 1017 | [10 empty] | 71.67 |  |  |  | 74.08 | [5 empty] | 68.88 |  |  | 75.00 |  |  |  | 4.91 |  | 7.84 | [8 empty] | 18.08 |  |  |  |  | 2.41
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2021 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 523 | [14 empty] | 349
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1576 | [14 empty] | 1072
H. |  | Nuclear regulatory requirements | [39 empty] | 234
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 73 | [19 empty] | 117
L. |  | Human factor related | [24 empty] | 10 | [14 empty] | 4
Subtotal | [22 empty] | 1576 |  |  |  | 533 | [6 empty] | 73 |  |  |  | 1072 |  |  |  | 587 | [11 empty] | 117
Total | [22 empty] | 2182 | [14 empty] | 1776
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2021 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [19 empty] | 53 | [14 empty] | 19
16. |  |  | Steam generation systems | [34 empty] | 213
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 8
31. |  |  | Turbine and auxiliaries | [19 empty] | 117 | [14 empty] | 76
32. |  |  | Feedwater and Main Steam System | [19 empty] | 362 | [14 empty] | 128
41. |  |  | Main Generator Systems | [34 empty] | 91
42. |  |  | Electrical Power Supply Systems | [34 empty] | 48
Total | [22 empty] | 532 | [14 empty] | 583
Highlights (2023)
RFO-2 planned from 12-10-2023 to 17-12-2023. RFO-2 extended till 04-01-2024 due to MSIV stem detachment issue.

## KANUPP-3
2023 Operating Experience
PK-7 | [8 empty] | KANUPP-3 | [26 empty] | PAKISTAN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Owner | [7 empty] | : | PAEC (PAKISTAN ATOMIC ENERGY COMMISSION)
Reactor Supplier | [7 empty] | : | CZEC (China Zhongyuan Engineering Corporation)
Turbine Supplier | [7 empty] | : | STC (Shanghai Turbine Co.)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / ACP-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2016-05-31
Thermal power | [12 empty] | : |  |  | 3060 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2022-03-04
Gross electrical power | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2022-04-18
Reference unit power (net) | [12 empty] | : |  |  | 1017 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6755.72 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.52 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.67 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.52 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.07 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.41 %
Load Factor (LF) | [18 empty] | : | 75.83 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.4 %
Operating Factor (OF) | [18 empty] | : | 85.73 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1250 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 599.27 | 543.87 |  |  |  | 520.42 |  | 492.16 | [8 empty] | 0.00 |  |  | 405.15 | [6 empty] | 743.45 |  | 708.87 |  |  |  | 692.19 |  |  | 682.20 |  |  | 711.72 | [9 empty] | 656.42 |  |  | 6755.72
EAF [%] |  |  |  |  | 100.00 | 99.96 |  |  |  | 95.33 |  | 90.09 | [8 empty] | 0.00 |  |  | 55.93 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.67
UCF [%] |  |  |  |  | 100.00 | 99.96 |  |  |  | 100.00 |  | 90.09 | [8 empty] | 0.00 |  |  | 55.93 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.07
LF [%] |  |  |  |  | 79.20 | 79.58 |  |  |  | 68.78 |  | 67.21 | [8 empty] | 0.00 |  |  | 55.33 | [6 empty] | 98.26 |  | 93.69 |  |  |  | 94.53 |  |  | 90.16 |  |  | 97.20 | [9 empty] | 86.75 |  |  | 75.83
OF [%] |  |  |  |  | 91.67 | 100.00 |  |  |  | 95.83 |  | 90.83 | [8 empty] | 0.00 |  |  | 61.81 | [6 empty] | 100.00 |  | 98.39 |  |  |  | 100.00 |  |  | 91.94 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.73
FLR [%] |  |  |  |  | 0.00 | 0.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 8.88 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.52
UCL [%] |  |  |  |  | 0.00 | 0.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 6.34 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.52
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 9.91 | [8 empty] | 100.00 |  |  | 37.73 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.41
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 4.67 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.40
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 12937.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.79 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 90.64 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.87 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.51 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.24 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.94 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2022 |  |  |  | 6181.90 |  |  | 6287 |  |  |  | 1017 | [10 empty] | 96.55 |  |  |  | 96.55 | [5 empty] | 89.98 |  |  | 91.24 |  |  |  | 3.45 |  | 3.45 | [8 empty] | 0.00 |  |  |  |  | 0.00
2023 |  |  |  | 6755.72 |  |  | 7510 |  |  |  | 1017 | [10 empty] | 86.67 |  |  |  | 87.07 | [5 empty] | 75.83 |  |  | 85.73 |  |  |  | 0.52 |  | 0.52 | [8 empty] | 12.41 |  |  |  |  | 0.40
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2022 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 35 | [14 empty] | 76
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1049 | [14 empty] | 629
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 132 | [19 empty] | 302
L. |  | Human factor related | [39 empty] | 31
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [31 empty] | 30 | [19 empty] | 18
Subtotal | [22 empty] | 1049 |  |  |  | 35 | [6 empty] | 162 |  |  |  | 629 |  |  |  | 107 | [11 empty] | 320
Total | [22 empty] | 1246 | [14 empty] | 1056
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2022 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [19 empty] | 29 | [14 empty] | 16
32. |  |  | Feedwater and Main Steam System | [34 empty] | 28
41. |  |  | Main Generator Systems | [19 empty] | 6 | [14 empty] | 54
Total | [22 empty] | 35 | [14 empty] | 98
Highlights (2023)
RFO-1 was planned from 28-4-2023 to 10-6-2023. RFO-1 extended till 11-6-2023 due to delay in identification and resolution of leakage in hydrogen purification system.