## AKADEMIK LOMONOSOV-1
2023 Operating Experience
RU-151 | [8 empty] | AKADEMIK LOMONOSOV-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / KLT-40S 'Floating' | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-04-15
Thermal power | [12 empty] | : |  |  | 150 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-12-19
Gross electrical power | [12 empty] | : |  |  | 35 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2020-05-22
Reference unit power (net) | [12 empty] | : |  |  | 32 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 316
| Fuel material | [13 empty] | : |  |  | Other | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 14.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 29 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 100 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 68700 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | NA
| Active core diameter [m] | [13 empty] | : |  |  | 1.220 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.43
| Active core height/length [m] | [13 empty] | : |  |  | 1.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 10.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 11 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 74.63 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.16 %
Energy Availability Factor (EAF) | [18 empty] | : | 33.02 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.73 %
Unit Capability Factor (UCF) | [18 empty] | : | 33.02 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 66.25 %
Load Factor (LF) | [18 empty] | : | 26.62 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 58.71 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3617 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 11.90 | 8.66 |  |  |  | 10.19 |  | 10.52 | [8 empty] | 10.70 |  |  | 10.10 | [6 empty] | 6.61 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 5.96 |  |  | 74.63
EAF [%] |  |  |  |  | 54.28 | 54.29 |  |  |  | 54.28 |  | 54.36 | [8 empty] | 54.28 |  |  | 52.25 | [6 empty] | 38.67 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 35.02 |  |  | 33.02
UCF [%] |  |  |  |  | 54.28 | 54.29 |  |  |  | 54.28 |  | 54.36 | [8 empty] | 54.28 |  |  | 52.25 | [6 empty] | 38.67 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 35.02 |  |  | 33.02
LF [%] |  |  |  |  | 50.00 | 40.26 |  |  |  | 42.80 |  | 45.64 | [8 empty] | 44.94 |  |  | 43.83 | [6 empty] | 27.74 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 25.03 |  |  | 26.62
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 96.11 | [6 empty] | 71.24 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 39.92 |  |  | 58.71
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 6.70 | [6 empty] | 11.39 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.16
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 3.75 | [6 empty] | 4.97 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.73
PUF [%] |  |  |  |  | 45.72 | 45.71 |  |  |  | 45.72 |  | 45.64 | [8 empty] | 45.72 |  |  | 44.00 | [6 empty] | 56.36 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 64.98 |  |  | 66.25
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 339.64 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.64 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 61.66 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 61.66 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 35.34 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 31.96 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 70.96 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2020 |  |  |  | 64.94 |  |  | 5138 |  |  |  | 32 | [10 empty] | 90.38 |  |  |  | 90.38 | [5 empty] | 28.76 |  |  | 71.63 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 9.34 |  |  |  |  | 0.00
2021 |  |  |  | 125.26 |  |  | 7104 |  |  |  | 32 | [10 empty] | 85.08 |  |  |  | 85.08 | [5 empty] | 44.69 |  |  | 81.10 |  |  |  | 8.98 |  | 8.39 | [8 empty] | 6.53 |  |  |  |  | 0.00
2022 |  |  |  | 74.13 |  |  | 6367 |  |  |  | 32 | [10 empty] | 50.04 |  |  |  | 50.04 | [5 empty] | 26.44 |  |  | 72.68 |  |  |  | 2.89 |  | 1.49 | [8 empty] | 48.47 |  |  |  |  | 0.00
2023 |  |  |  | 74.63 |  |  | 5143 |  |  |  | 32 | [10 empty] | 33.02 |  |  |  | 33.02 | [5 empty] | 26.62 |  |  | 58.71 |  |  |  | 2.16 |  | 0.73 | [8 empty] | 66.25 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2020 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 81 | [14 empty] | 265
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 3552 | [14 empty] | 991
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 511
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 56
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 226
L. |  | Human factor related | [39 empty] | 4
Z. |  | Other | [35 empty] | 224
Subtotal | [22 empty] | 3552 |  |  |  | 81 | [10 empty] | 1726 |  |  |  | 269 | [11 empty] | 282
Total | [22 empty] | 3633 | [14 empty] | 2277
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2020 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 185
31. |  |  | Turbine and auxiliaries | [19 empty] | 51 | [14 empty] | 16
32. |  |  | Feedwater and Main Steam System | [19 empty] | 30 | [14 empty] | 24
33. |  |  | Circulating Water System | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 81 | [14 empty] | 241
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. The unit was in the routine maintenance from 2023.07.24 to 2023.12.19. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## AKADEMIK LOMONOSOV-2
2023 Operating Experience
RU-152 | [8 empty] | AKADEMIK LOMONOSOV-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / KLT-40S 'Floating' | [11 empty] | Construction Date | [15 empty] | : |  |  | 2007-04-15
Thermal power | [12 empty] | : |  |  | 150 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-12-19
Gross electrical power | [12 empty] | : |  |  | 35 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2020-05-22
Reference unit power (net) | [12 empty] | : |  |  | 32 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 316
| Fuel material | [13 empty] | : |  |  | Other | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.4
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 14.1 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 29 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 100 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 68700 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | NA
| Active core diameter [m] | [13 empty] | : |  |  | 1.220 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 3.43
| Active core height/length [m] | [13 empty] | : |  |  | 1.2 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 10.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 11 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 121.54 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.73 %
Energy Availability Factor (EAF) | [18 empty] | : | 54.12 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.95 %
Unit Capability Factor (UCF) | [18 empty] | : | 54.12 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 44.93 %
Load Factor (LF) | [18 empty] | : | 43.36 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 88.96 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 967 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 12.70 | 9.92 |  |  |  | 11.40 |  | 9.01 | [8 empty] | 9.15 |  |  | 2.79 | [6 empty] | 3.27 |  | 13.12 |  |  |  | 13.13 |  |  | 13.28 |  |  | 12.39 | [9 empty] | 11.37 |  |  | 121.54
EAF [%] |  |  |  |  | 57.14 | 62.86 |  |  |  | 62.85 |  | 62.86 | [8 empty] | 62.86 |  |  | 20.69 | [6 empty] | 21.93 |  | 62.86 |  |  |  | 62.86 |  |  | 59.99 |  |  | 58.60 | [9 empty] | 54.38 |  |  | 54.12
UCF [%] |  |  |  |  | 57.14 | 62.86 |  |  |  | 62.85 |  | 62.86 | [8 empty] | 62.86 |  |  | 20.69 | [6 empty] | 21.93 |  | 62.86 |  |  |  | 62.86 |  |  | 59.99 |  |  | 58.60 | [9 empty] | 54.38 |  |  | 54.12
LF [%] |  |  |  |  | 53.36 | 46.14 |  |  |  | 47.90 |  | 39.11 | [8 empty] | 38.44 |  |  | 12.11 | [6 empty] | 13.75 |  | 55.11 |  |  |  | 56.97 |  |  | 55.76 |  |  | 53.77 | [9 empty] | 47.76 |  |  | 43.36
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 32.92 | [6 empty] | 34.95 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.96
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 32.89 |  | 0.00 |  |  |  | 0.00 |  |  | 0.78 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.73
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 10.75 |  | 0.00 |  |  |  | 0.00 |  |  | 0.47 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.95
PUF [%] |  |  |  |  | 42.86 | 37.14 |  |  |  | 37.14 |  | 37.14 | [8 empty] | 37.14 |  |  | 79.31 | [6 empty] | 67.32 |  | 37.14 |  |  |  | 37.14 |  |  | 39.54 |  |  | 41.40 | [9 empty] | 45.62 |  |  | 44.93
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 310.94 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.78 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 64.95 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.72 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 64.95 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 30.33 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 28.22 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 60.42 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2020 |  |  |  | 51.44 |  |  | 3942 |  |  |  | 32 | [10 empty] | 77.36 |  |  |  | 77.36 | [5 empty] | 15.99 |  |  | 38.32 |  |  |  | 14.66 |  | 13.29 | [8 empty] | 9.35 |  |  |  |  | 0.00
2021 |  |  |  | 50.36 |  |  | 2265 |  |  |  | 32 | [10 empty] | 87.11 |  |  |  | 87.11 | [5 empty] | 17.97 |  |  | 25.86 |  |  |  | 7.93 |  | 7.51 | [8 empty] | 5.39 |  |  |  |  | 0.00
2022 |  |  |  | 85.48 |  |  | 6956 |  |  |  | 32 | [10 empty] | 46.34 |  |  |  | 46.34 | [5 empty] | 30.50 |  |  | 79.41 |  |  |  | 1.44 |  | 0.68 | [8 empty] | 52.99 |  |  |  |  | 0.00
2023 |  |  |  | 121.54 |  |  | 7793 |  |  |  | 32 | [10 empty] | 54.12 |  |  |  | 54.12 | [5 empty] | 43.36 |  |  | 88.96 |  |  |  | 1.73 |  | 0.95 | [8 empty] | 44.93 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2020 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 80 | [14 empty] | 421
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 888 | [14 empty] | 910
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1614
L. |  | Human factor related | [39 empty] | 5
Subtotal | [22 empty] | 888 |  |  |  | 80 | [10 empty] | 910 |  |  |  | 426 | [11 empty] | 1614
Total | [22 empty] | 968 | [14 empty] | 2950
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2020 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [34 empty] | 320
31. |  |  | Turbine and auxiliaries | [34 empty] | 7
32. |  |  | Feedwater and Main Steam System | [19 empty] | 80 | [14 empty] | 20
33. |  |  | Circulating Water System | [34 empty] | 21
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [22 empty] | 80 | [14 empty] | 378
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-1
2023 Operating Experience
RU-96 | [8 empty] | BALAKOVO-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-12-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-12-28
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-05-23
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7943.1 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.63 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.81 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.58 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.43 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.99 %
Load Factor (LF) | [18 empty] | : | 95.45 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.62 %
Operating Factor (OF) | [18 empty] | : | 91.88 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 711 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 5.31 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 759.52 | 670.92 |  |  |  | 761.25 |  | 699.17 | [8 empty] | 229.07 |  |  | 469.20 | [6 empty] | 720.05 |  | 693.01 |  |  |  | 718.21 |  |  | 756.02 |  |  | 712.38 | [9 empty] | 754.30 |  |  | 7943.10
EAF [%] |  |  |  |  | 100.00 | 99.54 |  |  |  | 100.00 |  | 98.27 | [8 empty] | 33.04 |  |  | 66.13 | [6 empty] | 100.00 |  | 95.24 |  |  |  | 100.00 |  |  | 100.00 |  |  | 98.30 | [9 empty] | 100.00 |  |  | 90.81
UCF [%] |  |  |  |  | 100.00 | 99.54 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 38.71 |  |  | 66.13 | [6 empty] | 100.00 |  | 95.24 |  |  |  | 100.00 |  |  | 100.00 |  |  | 98.30 | [9 empty] | 100.00 |  |  | 91.43
LF [%] |  |  |  |  | 107.46 | 105.09 |  |  |  | 107.70 |  | 102.22 | [8 empty] | 32.41 |  |  | 68.60 | [6 empty] | 101.87 |  | 98.05 |  |  |  | 105.00 |  |  | 106.96 |  |  | 104.15 | [9 empty] | 106.72 |  |  | 95.45
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 38.71 |  |  | 66.81 | [6 empty] | 100.00 |  | 99.33 |  |  |  | 100.00 |  |  | 100.00 |  |  | 98.47 | [9 empty] | 100.00 |  |  | 91.88
FLR [%] |  |  |  |  | 0.00 | 0.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 4.76 |  |  |  | 0.00 |  |  | 0.00 |  |  | 1.70 | [9 empty] | 0.00 |  |  | 0.63
UCL [%] |  |  |  |  | 0.00 | 0.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 4.76 |  |  |  | 0.00 |  |  | 0.00 |  |  | 1.70 | [9 empty] | 0.00 |  |  | 0.58
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 61.29 |  |  | 33.87 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.99
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 1.73 | [8 empty] | 5.67 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.62
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 237935.74 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.97 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.63 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.98 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.29 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.73 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.43 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.65 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.63 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 4868.03 |  |  | 6082 |  |  |  | 950 | [10 empty] | 64.85 |  |  |  | 64.85 | [5 empty] | 64.46 |  |  | 69.51 |  |  |  | 17.62 |  | 13.87 | [8 empty] | 21.28 |  |  |  |  | 0.00
1987 |  |  |  | 4703.68 |  |  | 5302 |  |  |  | 1000 | [10 empty] | 57.40 |  |  |  | 57.40 | [5 empty] | 53.70 |  |  | 60.53 |  |  |  | 25.51 |  | 19.66 | [8 empty] | 22.95 |  |  |  |  | 0.00
1988 |  |  |  | 6476.87 |  |  | 7207 |  |  |  | 950 | [10 empty] | 80.93 |  |  |  | 80.93 | [5 empty] | 77.62 |  |  | 82.05 |  |  |  | 6.99 |  | 6.08 | [8 empty] | 12.99 |  |  |  |  | 0.00
1989 |  |  |  | 4473.90 |  |  | 5141 |  |  |  | 950 | [10 empty] | 56.34 |  |  |  | 56.37 | [5 empty] | 53.76 |  |  | 58.69 |  |  |  | 32.94 |  | 27.69 | [8 empty] | 15.95 |  |  |  |  | 0.03
1990 |  |  |  | 739.06 |  |  | 887 |  |  |  | 950 | [10 empty] | 9.09 |  |  |  | 9.09 | [5 empty] | 8.88 |  |  | 10.13 |  |  |  | 56.91 |  | 12.01 | [8 empty] | 78.90 |  |  |  |  | 0.00
1991 |  |  |  | 4951.60 |  |  | 5780 |  |  |  | 950 | [10 empty] | 59.85 |  |  |  | 60.19 | [5 empty] | 59.50 |  |  | 65.98 |  |  |  | 24.74 |  | 19.79 | [8 empty] | 20.02 |  |  |  |  | 0.35
1992 |  |  |  | 6352.28 |  |  | 7666 |  |  |  | 950 | [10 empty] | 76.31 |  |  |  | 76.38 | [5 empty] | 76.11 |  |  | 87.26 |  |  |  | 23.62 |  | 23.62 | [8 empty] | 0.00 |  |  |  |  | 0.07
1993 |  |  |  | 3326.09 |  |  | 4230 |  |  |  | 950 | [10 empty] | 39.88 |  |  |  | 46.10 | [5 empty] | 39.97 |  |  | 48.29 |  |  |  | 24.25 |  | 14.76 | [8 empty] | 39.14 |  |  |  |  | 6.22
1994 |  |  |  | 1759.54 |  |  | 2307 |  |  |  | 950 | [10 empty] | 77.30 |  |  |  | 77.30 | [5 empty] | 21.14 |  |  | 26.34 |  |  |  | 22.70 |  | 22.70 | [8 empty] | 0.00 |  |  |  |  | 0.00
1995 |  |  |  | 2017.98 |  |  | 4810 |  |  |  | 950 | [10 empty] | 28.57 |  |  |  | 28.57 | [5 empty] | 24.25 |  |  | 54.91 |  |  |  | 62.91 |  | 48.46 | [8 empty] | 22.97 |  |  |  |  | 0.00
1996 |  |  |  | 4872.54 |  |  | 5913 |  |  |  | 950 | [10 empty] | 59.00 |  |  |  | 86.47 | [5 empty] | 58.39 |  |  | 67.32 |  |  |  | 0.82 |  | 0.72 | [8 empty] | 12.81 |  |  |  |  | 27.47
1997 |  |  |  | 4728.99 |  |  | 5818 |  |  |  | 950 | [10 empty] | 57.24 |  |  |  | 60.37 | [5 empty] | 56.83 |  |  | 66.42 |  |  |  | 1.49 |  | 0.91 | [8 empty] | 38.72 |  |  |  |  | 3.13
1998 |  |  |  | 4329.83 |  |  | 5671 |  |  |  | 950 | [10 empty] | 52.16 |  |  |  | 55.84 | [5 empty] | 52.03 |  |  | 64.74 |  |  |  | 4.87 |  | 2.86 | [8 empty] | 41.30 |  |  |  |  | 3.68
1999 |  |  |  | 5141.31 |  |  | 6337 |  |  |  | 950 | [10 empty] | 62.09 |  |  |  | 65.56 | [5 empty] | 61.78 |  |  | 72.34 |  |  |  | 0.25 |  | 0.16 | [8 empty] | 34.28 |  |  |  |  | 3.47
2000 |  |  |  | 7247.37 |  |  | 7705 |  |  |  | 950 | [10 empty] | 86.49 |  |  |  | 87.54 | [5 empty] | 86.85 |  |  | 87.72 |  |  |  | 2.30 |  | 2.06 | [8 empty] | 10.40 |  |  |  |  | 1.05
2001 |  |  |  | 7407.90 |  |  | 8041 |  |  |  | 950 | [10 empty] | 88.19 |  |  |  | 91.57 | [5 empty] | 89.02 |  |  | 91.79 |  |  |  | 1.55 |  | 1.44 | [8 empty] | 6.98 |  |  |  |  | 3.38
2002 |  |  |  | 6785.73 |  |  | 7501 |  |  |  | 950 | [10 empty] | 80.48 |  |  |  | 86.52 | [5 empty] | 81.54 |  |  | 85.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.48 |  |  |  |  | 6.04
2003 |  |  |  | 7032.19 |  |  | 7460 |  |  |  | 950 | [10 empty] | 83.12 |  |  |  | 84.71 | [5 empty] | 84.50 |  |  | 85.16 |  |  |  | 0.75 |  | 0.64 | [8 empty] | 14.64 |  |  |  |  | 1.60
2004 |  |  |  | 6626.43 |  |  | 6901 |  |  |  | 950 | [10 empty] | 78.00 |  |  |  | 78.22 | [5 empty] | 79.41 |  |  | 78.56 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.78 |  |  |  |  | 0.22
2005 |  |  |  | 7312.72 |  |  | 7638 |  |  |  | 950 | [10 empty] | 86.24 |  |  |  | 86.58 | [5 empty] | 87.86 |  |  | 87.18 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 13.27 |  |  |  |  | 0.34
2006 |  |  |  | 7276.97 |  |  | 7517 |  |  |  | 950 | [10 empty] | 85.24 |  |  |  | 85.49 | [5 empty] | 87.44 |  |  | 85.81 |  |  |  | 0.70 |  | 0.60 | [8 empty] | 13.91 |  |  |  |  | 0.25
2007 |  |  |  | 7397.29 |  |  | 7731 |  |  |  | 950 | [10 empty] | 86.54 |  |  |  | 87.98 | [5 empty] | 88.89 |  |  | 88.25 |  |  |  | 0.39 |  | 0.34 | [8 empty] | 11.68 |  |  |  |  | 1.44
2008 |  |  |  | 6810.23 |  |  | 7283 |  |  |  | 950 | [10 empty] | 81.73 |  |  |  | 82.41 | [5 empty] | 81.61 |  |  | 82.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.59 |  |  |  |  | 0.68
2009 |  |  |  | 7948.45 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.61 |  |  |  | 99.74 | [5 empty] | 95.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.26 |  |  |  |  | 0.13
2010 |  |  |  | 6843.30 |  |  | 7069 |  |  |  | 950 | [10 empty] | 80.31 |  |  |  | 80.43 | [5 empty] | 82.23 |  |  | 80.70 |  |  |  | 0.00 |  | 7.09 | [8 empty] | 12.48 |  |  |  |  | 0.12
2011 |  |  |  | 7469.27 |  |  | 7573 |  |  |  | 950 | [10 empty] | 86.15 |  |  |  | 86.25 | [5 empty] | 89.76 |  |  | 86.46 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 13.73 |  |  |  |  | 0.10
2012 |  |  |  | 6322.13 |  |  | 6424 |  |  |  | 950 | [10 empty] | 72.90 |  |  |  | 73.02 | [5 empty] | 75.76 |  |  | 73.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.98 |  |  |  |  | 0.12
2013 |  |  |  | 8766.85 |  |  | 8726 |  |  |  | 950 | [10 empty] | 99.58 |  |  |  | 99.58 | [5 empty] | 105.35 |  |  | 99.61 |  |  |  | 0.42 |  | 0.42 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 7012.47 |  |  | 7077 |  |  |  | 950 | [10 empty] | 79.98 |  |  |  | 80.50 | [5 empty] | 84.25 |  |  | 80.78 |  |  |  | 0.09 |  | 0.07 | [8 empty] | 19.43 |  |  |  |  | 0.51
2015 |  |  |  | 7392.01 |  |  | 7481 |  |  |  | 950 | [10 empty] | 84.74 |  |  |  | 85.21 | [5 empty] | 88.82 |  |  | 85.40 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 14.77 |  |  |  |  | 0.47
2016 |  |  |  | 8880.23 |  |  | 8784 |  |  |  | 950 | [10 empty] | 99.94 |  |  |  | 99.94 | [5 empty] | 106.42 |  |  | 100.00 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7699.56 |  |  | 7887 |  |  |  | 950 | [10 empty] | 89.31 |  |  |  | 89.82 | [5 empty] | 92.52 |  |  | 90.03 |  |  |  | 1.64 |  | 1.50 | [8 empty] | 8.69 |  |  |  |  | 0.50
2018 |  |  |  | 6656.19 |  |  | 6737 |  |  |  | 950 | [10 empty] | 76.80 |  |  |  | 76.80 | [5 empty] | 79.98 |  |  | 76.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.20 |  |  |  |  | 0.00
2019 |  |  |  | 8783.41 |  |  | 8662 |  |  |  | 950 | [10 empty] | 98.87 |  |  |  | 98.87 | [5 empty] | 105.54 |  |  | 98.88 |  |  |  | 1.13 |  | 1.13 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7533.32 |  |  | 7842 |  |  |  | 950 | [10 empty] | 88.96 |  |  |  | 88.96 | [5 empty] | 90.28 |  |  | 89.28 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 10.87 |  |  |  |  | 0.00
2021 |  |  |  | 7475.86 |  |  | 7532 |  |  |  | 950 | [10 empty] | 85.51 |  |  |  | 85.74 | [5 empty] | 89.83 |  |  | 85.98 |  |  |  | 0.33 |  | 0.28 | [8 empty] | 13.98 |  |  |  |  | 0.23
2022 |  |  |  | 8788.05 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.96 |  |  |  | 99.96 | [5 empty] | 105.60 |  |  | 100.00 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 0.00 |  |  |  |  | 0.00
2023 |  |  |  | 7943.10 |  |  | 8049 |  |  |  | 950 | [10 empty] | 90.81 |  |  |  | 91.43 | [5 empty] | 95.45 |  |  | 91.88 |  |  |  | 0.63 |  | 0.58 | [8 empty] | 7.99 |  |  |  |  | 0.62
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1986 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 11 | [14 empty] | 288
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 700 | [14 empty] | 1195 |  |  |  | 10
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 244
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 128
L. |  | Human factor related | [39 empty] | 7
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 65
Z. |  | Other | [39 empty] | 21
Subtotal | [22 empty] | 700 |  |  |  | 11 | [10 empty] | 1440 |  |  |  | 327 | [11 empty] | 194
Total | [22 empty] | 711 | [14 empty] | 1961
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1986 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 2
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 10
16. |  |  | Steam generation systems | [34 empty] | 89
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 41
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 24
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [19 empty] | 11 | [14 empty] | 79
42. |  |  | Electrical Power Supply Systems | [34 empty] | 19
Total | [22 empty] | 11 | [14 empty] | 290
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-April, June-December. Additional electricity generation amounted to 376796 MWh. The unit was in the intermediate maintenance outage from 2023.05.13 to 2023.06.10. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-2
2023 Operating Experience
RU-97 | [8 empty] | BALAKOVO-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-08-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1987-10-08
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1988-01-18
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 36 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7964.89 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.69 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.25 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.63 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.25 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.12 %
Load Factor (LF) | [18 empty] | : | 95.71 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 90.95 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 793 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 4.77 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 627.00 |  |  |  | 763.75 |  | 731.00 | [8 empty] | 725.32 |  |  | 716.91 | [6 empty] | 691.80 |  | 733.19 |  |  |  | 721.11 |  |  | 757.41 |  |  | 739.69 | [9 empty] | 757.71 |  |  | 7964.89
EAF [%] |  |  |  |  | 0.00 | 91.77 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 96.90 |  |  | 100.00 | [6 empty] | 96.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.72 |  |  | 90.25
UCF [%] |  |  |  |  | 0.00 | 91.77 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 96.90 |  |  | 100.00 | [6 empty] | 96.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.72 |  |  | 90.25
LF [%] |  |  |  |  | 0.00 | 98.21 |  |  |  | 108.06 |  | 106.87 | [8 empty] | 102.62 |  |  | 104.81 | [6 empty] | 97.88 |  | 103.73 |  |  |  | 105.43 |  |  | 107.16 |  |  | 108.14 | [9 empty] | 107.20 |  |  | 95.71
OF [%] |  |  |  |  | 0.00 | 92.71 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.95
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.10 |  |  | 0.00 | [6 empty] | 4.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.28 |  |  | 0.69
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.10 |  |  | 0.00 | [6 empty] | 4.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.28 |  |  | 0.63
PUF [%] |  |  |  |  | 100.00 | 8.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.12
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 229692.53 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.67 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.13 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.53 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.32 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.29 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.19 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.06 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1988 |  |  |  | 5978.43 |  |  | 6928 |  |  |  | 950 | [10 empty] | 75.49 |  |  |  | 75.49 | [5 empty] | 70.63 |  |  | 77.66 |  |  |  | 6.59 |  | 5.33 | [8 empty] | 19.18 |  |  |  |  | 0.00
1989 |  |  |  | 6703.63 |  |  | 7626 |  |  |  | 950 | [10 empty] | 84.75 |  |  |  | 84.77 | [5 empty] | 80.55 |  |  | 87.05 |  |  |  | 9.33 |  | 8.72 | [8 empty] | 6.51 |  |  |  |  | 0.02
1990 |  |  |  | 5476.67 |  |  | 6165 |  |  |  | 950 | [10 empty] | 66.35 |  |  |  | 66.53 | [5 empty] | 65.81 |  |  | 70.38 |  |  |  | 15.71 |  | 12.40 | [8 empty] | 21.07 |  |  |  |  | 0.18
1991 |  |  |  | 4308.38 |  |  | 4845 |  |  |  | 950 | [10 empty] | 51.23 |  |  |  | 51.52 | [5 empty] | 51.77 |  |  | 55.31 |  |  |  | 10.81 |  | 6.25 | [8 empty] | 42.23 |  |  |  |  | 0.29
1992 |  |  |  | 5958.20 |  |  | 6601 |  |  |  | 950 | [10 empty] | 70.60 |  |  |  | 70.60 | [5 empty] | 71.39 |  |  | 75.14 |  |  |  | 9.39 |  | 7.32 | [8 empty] | 22.08 |  |  |  |  | 0.00
1993 |  |  |  | 3776.17 |  |  | 4147 |  |  |  | 950 | [10 empty] | 44.25 |  |  |  | 46.97 | [5 empty] | 45.38 |  |  | 47.34 |  |  |  | 38.44 |  | 29.33 | [8 empty] | 23.69 |  |  |  |  | 2.72
1994 |  |  |  | 4778.52 |  |  | 8020 |  |  |  | 950 | [10 empty] | 73.08 |  |  |  | 83.53 | [5 empty] | 57.42 |  |  | 91.55 |  |  |  | 12.39 |  | 11.81 | [8 empty] | 4.66 |  |  |  |  | 10.45
1995 |  |  |  | 2204.81 |  |  | 3261 |  |  |  | 950 | [10 empty] | 30.13 |  |  |  | 30.13 | [5 empty] | 26.49 |  |  | 37.23 |  |  |  | 27.40 |  | 11.37 | [8 empty] | 58.50 |  |  |  |  | 0.00
1996 |  |  |  | 2227.25 |  |  | 2604 |  |  |  | 950 | [10 empty] | 26.71 |  |  |  | 26.71 | [5 empty] | 26.69 |  |  | 29.64 |  |  |  | 66.37 |  | 52.71 | [8 empty] | 20.58 |  |  |  |  | 0.00
1997 |  |  |  | 4015.92 |  |  | 6158 |  |  |  | 950 | [10 empty] | 55.66 |  |  |  | 63.92 | [5 empty] | 48.26 |  |  | 70.30 |  |  |  | 27.93 |  | 24.77 | [8 empty] | 11.31 |  |  |  |  | 8.26
1998 |  |  |  | 3293.76 |  |  | 4984 |  |  |  | 950 | [10 empty] | 40.24 |  |  |  | 50.96 | [5 empty] | 39.58 |  |  | 56.89 |  |  |  | 0.11 |  | 0.05 | [8 empty] | 48.98 |  |  |  |  | 10.72
1999 |  |  |  | 2927.12 |  |  | 3942 |  |  |  | 950 | [10 empty] | 35.40 |  |  |  | 40.27 | [5 empty] | 35.17 |  |  | 45.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 59.73 |  |  |  |  | 4.87
2000 |  |  |  | 5730.07 |  |  | 7646 |  |  |  | 950 | [10 empty] | 68.89 |  |  |  | 83.21 | [5 empty] | 68.67 |  |  | 87.04 |  |  |  | 1.61 |  | 1.36 | [8 empty] | 15.43 |  |  |  |  | 14.32
2001 |  |  |  | 6678.82 |  |  | 7415 |  |  |  | 950 | [10 empty] | 79.86 |  |  |  | 83.90 | [5 empty] | 80.25 |  |  | 84.65 |  |  |  | 0.82 |  | 0.70 | [8 empty] | 15.40 |  |  |  |  | 4.05
2002 |  |  |  | 6756.53 |  |  | 7408 |  |  |  | 950 | [10 empty] | 80.40 |  |  |  | 84.43 | [5 empty] | 81.19 |  |  | 84.57 |  |  |  | 2.74 |  | 2.38 | [8 empty] | 13.19 |  |  |  |  | 4.03
2003 |  |  |  | 6171.76 |  |  | 6467 |  |  |  | 950 | [10 empty] | 72.70 |  |  |  | 73.99 | [5 empty] | 74.16 |  |  | 73.82 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 25.99 |  |  |  |  | 1.29
2004 |  |  |  | 7010.41 |  |  | 7514 |  |  |  | 950 | [10 empty] | 82.36 |  |  |  | 85.00 | [5 empty] | 84.01 |  |  | 85.54 |  |  |  | 0.72 |  | 0.62 | [8 empty] | 14.38 |  |  |  |  | 2.64
2005 |  |  |  | 6948.86 |  |  | 7688 |  |  |  | 950 | [10 empty] | 82.48 |  |  |  | 86.92 | [5 empty] | 83.49 |  |  | 87.75 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.08 |  |  |  |  | 4.44
2006 |  |  |  | 7237.48 |  |  | 7710 |  |  |  | 950 | [10 empty] | 84.59 |  |  |  | 87.38 | [5 empty] | 86.97 |  |  | 88.01 |  |  |  | 0.41 |  | 0.36 | [8 empty] | 12.26 |  |  |  |  | 2.79
2007 |  |  |  | 6657.18 |  |  | 7327 |  |  |  | 950 | [10 empty] | 78.71 |  |  |  | 83.46 | [5 empty] | 79.99 |  |  | 83.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.54 |  |  |  |  | 4.75
2008 |  |  |  | 7451.24 |  |  | 7750 |  |  |  | 950 | [10 empty] | 87.71 |  |  |  | 87.82 | [5 empty] | 89.29 |  |  | 88.23 |  |  |  | 1.21 |  | 1.07 | [8 empty] | 11.11 |  |  |  |  | 0.11
2009 |  |  |  | 7630.69 |  |  | 7797 |  |  |  | 950 | [10 empty] | 88.63 |  |  |  | 88.78 | [5 empty] | 91.69 |  |  | 89.01 |  |  |  | 0.28 |  | 0.25 | [8 empty] | 10.97 |  |  |  |  | 0.15
2010 |  |  |  | 8683.93 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.86 |  |  |  | 100.00 | [5 empty] | 104.35 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.14
2011 |  |  |  | 7288.41 |  |  | 7531 |  |  |  | 950 | [10 empty] | 85.42 |  |  |  | 85.76 | [5 empty] | 87.59 |  |  | 85.98 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.24 |  |  |  |  | 0.35
2012 |  |  |  | 7706.49 |  |  | 7829 |  |  |  | 950 | [10 empty] | 88.30 |  |  |  | 88.99 | [5 empty] | 92.35 |  |  | 89.13 |  |  |  | 1.35 |  | 1.22 | [8 empty] | 9.79 |  |  |  |  | 0.70
2013 |  |  |  | 8222.79 |  |  | 8509 |  |  |  | 950 | [10 empty] | 95.56 |  |  |  | 96.54 | [5 empty] | 98.81 |  |  | 97.13 |  |  |  | 0.45 |  | 0.44 | [8 empty] | 3.02 |  |  |  |  | 0.98
2014 |  |  |  | 6497.72 |  |  | 6672 |  |  |  | 950 | [10 empty] | 75.62 |  |  |  | 75.62 | [5 empty] | 78.07 |  |  | 76.16 |  |  |  | 10.92 |  | 9.27 | [8 empty] | 15.11 |  |  |  |  | 0.00
2015 |  |  |  | 6850.26 |  |  | 6845 |  |  |  | 950 | [10 empty] | 78.02 |  |  |  | 78.03 | [5 empty] | 82.32 |  |  | 78.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.97 |  |  |  |  | 0.01
2016 |  |  |  | 7922.42 |  |  | 7900 |  |  |  | 950 | [10 empty] | 89.79 |  |  |  | 89.79 | [5 empty] | 94.94 |  |  | 89.94 |  |  |  | 10.21 |  | 10.21 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 6880.73 |  |  | 6972 |  |  |  | 950 | [10 empty] | 79.07 |  |  |  | 79.07 | [5 empty] | 82.68 |  |  | 79.59 |  |  |  | 0.40 |  | 0.31 | [8 empty] | 20.61 |  |  |  |  | 0.00
2018 |  |  |  | 7858.92 |  |  | 7874 |  |  |  | 950 | [10 empty] | 89.46 |  |  |  | 89.82 | [5 empty] | 94.44 |  |  | 89.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.18 |  |  |  |  | 0.36
2019 |  |  |  | 8867.45 |  |  | 8760 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 106.55 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2020 |  |  |  | 7538.45 |  |  | 7590 |  |  |  | 950 | [10 empty] | 86.37 |  |  |  | 86.37 | [5 empty] | 90.34 |  |  | 86.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.63 |  |  |  |  | 0.00
2021 |  |  |  | 8043.86 |  |  | 7913 |  |  |  | 950 | [10 empty] | 90.15 |  |  |  | 90.25 | [5 empty] | 96.66 |  |  | 90.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.75 |  |  |  |  | 0.11
2022 |  |  |  | 8519.78 |  |  | 8472 |  |  |  | 950 | [10 empty] | 96.64 |  |  |  | 96.64 | [5 empty] | 102.38 |  |  | 96.71 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 3.33 |  |  |  |  | 0.00
2023 |  |  |  | 7964.89 |  |  | 7967 |  |  |  | 950 | [10 empty] | 90.25 |  |  |  | 90.25 | [5 empty] | 95.71 |  |  | 90.95 |  |  |  | 0.69 |  | 0.63 | [8 empty] | 9.12 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1988 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 318
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 793 | [14 empty] | 1336 |  |  |  | 76
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 83
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 24 | [19 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 6
L. |  | Human factor related | [39 empty] | 3
Z. |  | Other | [39 empty] | 12
Subtotal | [22 empty] | 793 | [10 empty] | 24 |  |  |  | 1419 |  |  |  | 409 | [11 empty] | 7
Total | [22 empty] | 817 | [14 empty] | 1835
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1988 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 222
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 15
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 63
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 318
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in February-December. Additional electricity generation amounted to 402761 MWh. The unit was in the overhaul outage from 2023.01.01 to 2023.02.03. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-3
2023 Operating Experience
RU-98 | [8 empty] | BALAKOVO-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-11-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1988-12-25
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1989-04-08
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 35 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8113.04 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.47 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.61 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.39 %
Load Factor (LF) | [18 empty] | : | 97.49 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.14 %
Operating Factor (OF) | [18 empty] | : | 91.67 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 730 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 4.22 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 764.07 | 555.34 |  |  |  | 98.54 |  | 735.96 | [8 empty] | 755.97 |  |  | 729.89 | [6 empty] | 740.74 |  | 738.68 |  |  |  | 730.09 |  |  | 758.88 |  |  | 739.87 | [9 empty] | 765.03 |  |  | 8113.04
EAF [%] |  |  |  |  | 100.00 | 83.93 |  |  |  | 14.13 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.47
UCF [%] |  |  |  |  | 100.00 | 85.72 |  |  |  | 14.13 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.61
LF [%] |  |  |  |  | 108.10 | 86.99 |  |  |  | 13.94 |  | 107.60 | [8 empty] | 106.96 |  |  | 106.71 | [6 empty] | 104.80 |  | 104.51 |  |  |  | 106.74 |  |  | 107.37 |  |  | 108.17 | [9 empty] | 108.24 |  |  | 97.49
OF [%] |  |  |  |  | 100.00 | 85.71 |  |  |  | 14.78 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.67
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 14.28 |  |  |  | 85.87 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.39
XUF [%] |  |  |  |  | 0.00 | 1.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.14
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 227995.02 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.77 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.55 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.28 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.27 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.44 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.38 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.72 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.46 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1989 |  |  |  | 6621.41 |  |  | 7792 |  |  |  | 950 | [10 empty] | 88.36 |  |  |  | 88.36 | [5 empty] | 87.44 |  |  | 91.12 |  |  |  | 6.11 |  | 5.75 | [8 empty] | 5.90 |  |  |  |  | 0.00
1990 |  |  |  | 5718.71 |  |  | 6696 |  |  |  | 950 | [10 empty] | 67.84 |  |  |  | 68.04 | [5 empty] | 68.72 |  |  | 76.44 |  |  |  | 13.53 |  | 10.65 | [8 empty] | 21.31 |  |  |  |  | 0.19
1991 |  |  |  | 5403.35 |  |  | 6124 |  |  |  | 950 | [10 empty] | 64.23 |  |  |  | 67.13 | [5 empty] | 64.93 |  |  | 69.91 |  |  |  | 12.68 |  | 9.75 | [8 empty] | 23.13 |  |  |  |  | 2.90
1992 |  |  |  | 5545.43 |  |  | 6202 |  |  |  | 950 | [10 empty] | 64.77 |  |  |  | 66.42 | [5 empty] | 66.45 |  |  | 70.60 |  |  |  | 17.40 |  | 14.00 | [8 empty] | 19.59 |  |  |  |  | 1.65
1993 |  |  |  | 4378.64 |  |  | 5461 |  |  |  | 950 | [10 empty] | 52.73 |  |  |  | 61.63 | [5 empty] | 52.62 |  |  | 62.34 |  |  |  | 13.51 |  | 9.63 | [8 empty] | 28.74 |  |  |  |  | 8.90
1994 |  |  |  | 3340.14 |  |  | 5389 |  |  |  | 950 | [10 empty] | 70.66 |  |  |  | 70.69 | [5 empty] | 40.14 |  |  | 61.52 |  |  |  | 10.93 |  | 8.68 | [8 empty] | 20.64 |  |  |  |  | 0.03
1995 |  |  |  | 2674.65 |  |  | 5511 |  |  |  | 950 | [10 empty] | 47.52 |  |  |  | 53.12 | [5 empty] | 32.14 |  |  | 62.91 |  |  |  | 20.77 |  | 13.93 | [8 empty] | 32.95 |  |  |  |  | 5.60
1996 |  |  |  | 5315.40 |  |  | 7085 |  |  |  | 950 | [10 empty] | 64.26 |  |  |  | 75.94 | [5 empty] | 63.70 |  |  | 80.66 |  |  |  | 1.93 |  | 1.49 | [8 empty] | 22.57 |  |  |  |  | 11.68
1997 |  |  |  | 2058.79 |  |  | 3395 |  |  |  | 950 | [10 empty] | 25.29 |  |  |  | 38.78 | [5 empty] | 24.74 |  |  | 38.76 |  |  |  | 0.58 |  | 0.22 | [8 empty] | 60.99 |  |  |  |  | 13.49
1998 |  |  |  | 5348.52 |  |  | 7136 |  |  |  | 950 | [10 empty] | 64.42 |  |  |  | 73.01 | [5 empty] | 64.27 |  |  | 81.46 |  |  |  | 0.09 |  | 0.06 | [8 empty] | 26.93 |  |  |  |  | 8.59
1999 |  |  |  | 5457.98 |  |  | 6552 |  |  |  | 950 | [10 empty] | 65.61 |  |  |  | 71.98 | [5 empty] | 65.59 |  |  | 74.79 |  |  |  | 0.16 |  | 0.12 | [8 empty] | 27.91 |  |  |  |  | 6.37
2000 |  |  |  | 6482.85 |  |  | 7327 |  |  |  | 950 | [10 empty] | 77.18 |  |  |  | 82.00 | [5 empty] | 77.69 |  |  | 83.41 |  |  |  | 1.10 |  | 0.91 | [8 empty] | 17.09 |  |  |  |  | 4.82
2001 |  |  |  | 6050.74 |  |  | 6927 |  |  |  | 950 | [10 empty] | 72.10 |  |  |  | 78.65 | [5 empty] | 72.71 |  |  | 79.08 |  |  |  | 0.15 |  | 0.12 | [8 empty] | 21.23 |  |  |  |  | 6.55
2002 |  |  |  | 6926.31 |  |  | 7478 |  |  |  | 950 | [10 empty] | 81.99 |  |  |  | 85.35 | [5 empty] | 83.23 |  |  | 85.37 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 14.64 |  |  |  |  | 3.36
2003 |  |  |  | 7016.14 |  |  | 7471 |  |  |  | 950 | [10 empty] | 83.19 |  |  |  | 85.05 | [5 empty] | 84.31 |  |  | 85.29 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 14.86 |  |  |  |  | 1.86
2004 |  |  |  | 7227.76 |  |  | 7607 |  |  |  | 950 | [10 empty] | 85.13 |  |  |  | 86.38 | [5 empty] | 86.61 |  |  | 86.60 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 13.56 |  |  |  |  | 1.25
2005 |  |  |  | 6244.44 |  |  | 7060 |  |  |  | 950 | [10 empty] | 74.50 |  |  |  | 79.90 | [5 empty] | 75.04 |  |  | 80.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.10 |  |  |  |  | 5.40
2006 |  |  |  | 7741.84 |  |  | 8354 |  |  |  | 950 | [10 empty] | 91.38 |  |  |  | 95.30 | [5 empty] | 93.03 |  |  | 95.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.70 |  |  |  |  | 3.92
2007 |  |  |  | 7407.10 |  |  | 8050 |  |  |  | 950 | [10 empty] | 87.59 |  |  |  | 91.82 | [5 empty] | 89.01 |  |  | 91.89 |  |  |  | 0.68 |  | 0.63 | [8 empty] | 7.56 |  |  |  |  | 4.23
2008 |  |  |  | 7384.34 |  |  | 7693 |  |  |  | 950 | [10 empty] | 86.99 |  |  |  | 87.15 | [5 empty] | 88.49 |  |  | 87.58 |  |  |  | 1.09 |  | 0.96 | [8 empty] | 11.89 |  |  |  |  | 0.16
2009 |  |  |  | 6932.73 |  |  | 7276 |  |  |  | 950 | [10 empty] | 82.56 |  |  |  | 82.63 | [5 empty] | 83.31 |  |  | 83.06 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.37 |  |  |  |  | 0.08
2010 |  |  |  | 7649.62 |  |  | 7710 |  |  |  | 950 | [10 empty] | 87.13 |  |  |  | 87.75 | [5 empty] | 91.92 |  |  | 88.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.25 |  |  |  |  | 0.63
2011 |  |  |  | 8579.15 |  |  | 8627 |  |  |  | 950 | [10 empty] | 98.26 |  |  |  | 98.26 | [5 empty] | 103.10 |  |  | 98.49 |  |  |  | 1.61 |  | 1.61 | [8 empty] | 0.13 |  |  |  |  | 0.00
2012 |  |  |  | 7716.23 |  |  | 7854 |  |  |  | 950 | [10 empty] | 89.32 |  |  |  | 89.34 | [5 empty] | 92.47 |  |  | 89.41 |  |  |  | 0.59 |  | 0.53 | [8 empty] | 10.13 |  |  |  |  | 0.02
2013 |  |  |  | 7378.17 |  |  | 7481 |  |  |  | 950 | [10 empty] | 84.53 |  |  |  | 84.94 | [5 empty] | 88.66 |  |  | 85.40 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 14.97 |  |  |  |  | 0.41
2014 |  |  |  | 7746.92 |  |  | 7827 |  |  |  | 950 | [10 empty] | 88.55 |  |  |  | 88.82 | [5 empty] | 93.08 |  |  | 89.34 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.18 |  |  |  |  | 0.26
2015 |  |  |  | 8250.27 |  |  | 8415 |  |  |  | 950 | [10 empty] | 95.78 |  |  |  | 95.78 | [5 empty] | 99.14 |  |  | 96.06 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 4.16 |  |  |  |  | 0.00
2016 |  |  |  | 7307.38 |  |  | 7331 |  |  |  | 950 | [10 empty] | 82.96 |  |  |  | 83.26 | [5 empty] | 87.57 |  |  | 83.46 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.74 |  |  |  |  | 0.30
2017 |  |  |  | 8653.43 |  |  | 8727 |  |  |  | 950 | [10 empty] | 99.16 |  |  |  | 99.48 | [5 empty] | 103.98 |  |  | 99.62 |  |  |  | 0.41 |  | 0.40 | [8 empty] | 0.11 |  |  |  |  | 0.32
2018 |  |  |  | 7167.75 |  |  | 7163 |  |  |  | 950 | [10 empty] | 81.59 |  |  |  | 81.71 | [5 empty] | 86.13 |  |  | 81.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.29 |  |  |  |  | 0.12
2019 |  |  |  | 4983.36 |  |  | 4979 |  |  |  | 950 | [10 empty] | 56.33 |  |  |  | 56.84 | [5 empty] | 59.88 |  |  | 56.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 43.16 |  |  |  |  | 0.51
2020 |  |  |  | 6845.49 |  |  | 6880 |  |  |  | 950 | [10 empty] | 78.34 |  |  |  | 78.34 | [5 empty] | 82.03 |  |  | 78.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.66 |  |  |  |  | 0.00
2021 |  |  |  | 7559.14 |  |  | 7634 |  |  |  | 950 | [10 empty] | 86.26 |  |  |  | 87.09 | [5 empty] | 90.83 |  |  | 87.15 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.91 |  |  |  |  | 0.82
2022 |  |  |  | 8734.40 |  |  | 8674 |  |  |  | 950 | [10 empty] | 98.99 |  |  |  | 98.99 | [5 empty] | 104.96 |  |  | 99.02 |  |  |  | 1.01 |  | 1.01 | [8 empty] | 0.00 |  |  |  |  | 0.00
2023 |  |  |  | 8113.04 |  |  | 8030 |  |  |  | 950 | [10 empty] | 91.47 |  |  |  | 91.61 | [5 empty] | 97.49 |  |  | 91.67 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.39 |  |  |  |  | 0.14
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1989 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 70
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 731 | [14 empty] | 1328 |  |  |  | 19
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 154
E. |  | Testing of plant systems or components | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 42
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 731 | [14 empty] | 1482 |  |  |  | 97 | [11 empty] | 43
Total | [22 empty] | 731 | [14 empty] | 1622
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1989 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 22
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
16. |  |  | Steam generation systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 8
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
33. |  |  | Circulating Water System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 5
35. |  |  | All other I&C Systems | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 11
Total | [37 empty] | 73
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-December. Additional electricity generation amounted to 433342 MWh. The unit was in the intermediate maintenance outage from 2023.02.25 to 2023.03.27. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BALAKOVO-4
2023 Operating Experience
RU-99 | [8 empty] | BALAKOVO-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-04-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1993-04-11
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1993-12-22
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 30 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7999.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.01 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.81 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.81 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.18 %
Load Factor (LF) | [18 empty] | : | 96.12 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 89.01 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 963 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 3.96 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 771.79 | 695.33 |  |  |  | 775.58 |  | 744.71 | [8 empty] | 768.14 |  |  | 738.14 | [6 empty] | 743.25 |  | 752.73 |  |  |  | 744.26 |  |  | 656.39 |  |  | 0.00 | [9 empty] | 608.94 |  |  | 7999.26
EAF [%] |  |  |  |  | 99.85 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 86.44 |  |  | 0.00 | [9 empty] | 78.70 |  |  | 88.81
UCF [%] |  |  |  |  | 99.85 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 86.44 |  |  | 0.00 | [9 empty] | 78.70 |  |  | 88.81
LF [%] |  |  |  |  | 109.20 | 108.92 |  |  |  | 109.73 |  | 108.88 | [8 empty] | 108.68 |  |  | 107.92 | [6 empty] | 105.16 |  | 106.50 |  |  |  | 108.81 |  |  | 92.87 |  |  | 0.00 | [9 empty] | 86.15 |  |  | 96.12
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 87.10 |  |  | 0.00 | [9 empty] | 80.24 |  |  | 89.01
FLR [%] |  |  |  |  | 0.15 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
UCL [%] |  |  |  |  | 0.15 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.01
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 13.56 |  |  | 100.00 | [9 empty] | 21.30 |  |  | 11.18
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 213006.56 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.27 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.59 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.09 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.48 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.43 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 83.79 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.89 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.61 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1993 |  |  |  | 3676.28 |  |  | 5206 |  |  |  | 950 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1994 |  |  |  | 3828.53 |  |  | 4604 |  |  |  | 950 | [10 empty] | 48.45 |  |  |  | 69.54 | [5 empty] | 46.00 |  |  | 52.56 |  |  |  | 1.58 |  | 1.12 | [8 empty] | 29.34 |  |  |  |  | 21.09
1995 |  |  |  | 5609.99 |  |  | 8760 |  |  |  | 950 | [10 empty] | 86.46 |  |  |  | 88.72 | [5 empty] | 67.41 |  |  | 100.00 |  |  |  | 11.28 |  | 11.28 | [8 empty] | 0.00 |  |  |  |  | 2.26
1996 |  |  |  | 4545.55 |  |  | 6652 |  |  |  | 950 | [10 empty] | 55.47 |  |  |  | 59.85 | [5 empty] | 54.47 |  |  | 75.73 |  |  |  | 13.90 |  | 9.66 | [8 empty] | 30.49 |  |  |  |  | 4.39
1997 |  |  |  | 4637.72 |  |  | 6637 |  |  |  | 950 | [10 empty] | 59.64 |  |  |  | 71.29 | [5 empty] | 55.73 |  |  | 75.76 |  |  |  | 0.16 |  | 0.11 | [8 empty] | 28.60 |  |  |  |  | 11.65
1998 |  |  |  | 5042.49 |  |  | 6936 |  |  |  | 950 | [10 empty] | 60.89 |  |  |  | 71.31 | [5 empty] | 60.59 |  |  | 79.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.69 |  |  |  |  | 10.42
1999 |  |  |  | 5803.91 |  |  | 7268 |  |  |  | 950 | [10 empty] | 69.59 |  |  |  | 77.55 | [5 empty] | 69.74 |  |  | 82.97 |  |  |  | 0.37 |  | 0.29 | [8 empty] | 22.17 |  |  |  |  | 7.95
2000 |  |  |  | 6665.85 |  |  | 7216 |  |  |  | 950 | [10 empty] | 78.95 |  |  |  | 80.96 | [5 empty] | 79.88 |  |  | 82.15 |  |  |  | 0.78 |  | 0.63 | [8 empty] | 18.40 |  |  |  |  | 2.01
2001 |  |  |  | 6578.09 |  |  | 7354 |  |  |  | 950 | [10 empty] | 78.30 |  |  |  | 83.91 | [5 empty] | 79.04 |  |  | 83.95 |  |  |  | 0.47 |  | 0.40 | [8 empty] | 15.69 |  |  |  |  | 5.61
2002 |  |  |  | 6292.92 |  |  | 6723 |  |  |  | 950 | [10 empty] | 72.80 |  |  |  | 77.28 | [5 empty] | 75.62 |  |  | 76.75 |  |  |  | 0.20 |  | 0.16 | [8 empty] | 22.57 |  |  |  |  | 4.47
2003 |  |  |  | 7223.84 |  |  | 7541 |  |  |  | 950 | [10 empty] | 84.64 |  |  |  | 85.84 | [5 empty] | 86.80 |  |  | 86.08 |  |  |  | 0.50 |  | 0.43 | [8 empty] | 13.73 |  |  |  |  | 1.20
2004 |  |  |  | 7022.94 |  |  | 7540 |  |  |  | 950 | [10 empty] | 82.51 |  |  |  | 85.37 | [5 empty] | 84.16 |  |  | 85.84 |  |  |  | 0.45 |  | 0.39 | [8 empty] | 14.24 |  |  |  |  | 2.86
2005 |  |  |  | 6938.28 |  |  | 7699 |  |  |  | 950 | [10 empty] | 82.14 |  |  |  | 87.62 | [5 empty] | 83.36 |  |  | 87.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.38 |  |  |  |  | 5.48
2006 |  |  |  | 6805.35 |  |  | 7230 |  |  |  | 950 | [10 empty] | 79.61 |  |  |  | 82.20 | [5 empty] | 81.78 |  |  | 82.53 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 17.74 |  |  |  |  | 2.58
2007 |  |  |  | 7153.35 |  |  | 7787 |  |  |  | 950 | [10 empty] | 84.70 |  |  |  | 88.53 | [5 empty] | 85.96 |  |  | 88.89 |  |  |  | 0.40 |  | 0.36 | [8 empty] | 11.11 |  |  |  |  | 3.83
2008 |  |  |  | 8330.42 |  |  | 8779 |  |  |  | 950 | [10 empty] | 99.71 |  |  |  | 99.73 | [5 empty] | 99.83 |  |  | 99.94 |  |  |  | 0.14 |  | 0.14 | [8 empty] | 0.13 |  |  |  |  | 0.02
2009 |  |  |  | 7409.95 |  |  | 7727 |  |  |  | 950 | [10 empty] | 87.83 |  |  |  | 87.83 | [5 empty] | 89.02 |  |  | 88.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.17 |  |  |  |  | 0.00
2010 |  |  |  | 7199.69 |  |  | 7168 |  |  |  | 950 | [10 empty] | 81.35 |  |  |  | 81.35 | [5 empty] | 86.51 |  |  | 81.83 |  |  |  | 2.02 |  | 1.68 | [8 empty] | 16.97 |  |  |  |  | 0.00
2011 |  |  |  | 7625.20 |  |  | 7619 |  |  |  | 950 | [10 empty] | 86.42 |  |  |  | 86.42 | [5 empty] | 91.64 |  |  | 86.98 |  |  |  | 2.50 |  | 2.22 | [8 empty] | 11.36 |  |  |  |  | 0.00
2012 |  |  |  | 8517.84 |  |  | 8608 |  |  |  | 950 | [10 empty] | 97.72 |  |  |  | 97.72 | [5 empty] | 102.07 |  |  | 98.00 |  |  |  | 2.08 |  | 2.07 | [8 empty] | 0.20 |  |  |  |  | 0.00
2013 |  |  |  | 7847.25 |  |  | 7847 |  |  |  | 950 | [10 empty] | 89.13 |  |  |  | 89.13 | [5 empty] | 94.30 |  |  | 89.58 |  |  |  | 0.61 |  | 0.54 | [8 empty] | 10.33 |  |  |  |  | 0.00
2014 |  |  |  | 7204.52 |  |  | 7173 |  |  |  | 950 | [10 empty] | 81.27 |  |  |  | 81.36 | [5 empty] | 86.56 |  |  | 81.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.64 |  |  |  |  | 0.09
2015 |  |  |  | 8800.05 |  |  | 8757 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.74 |  |  | 99.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 8006.24 |  |  | 8045 |  |  |  | 950 | [10 empty] | 91.07 |  |  |  | 91.58 | [5 empty] | 95.94 |  |  | 91.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.42 |  |  |  |  | 0.52
2017 |  |  |  | 7336.59 |  |  | 7386 |  |  |  | 950 | [10 empty] | 83.99 |  |  |  | 84.24 | [5 empty] | 88.16 |  |  | 84.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.76 |  |  |  |  | 0.25
2018 |  |  |  | 8777.02 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 105.47 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.03 |  |  |  |  | 0.00
2019 |  |  |  | 6075.81 |  |  | 5952 |  |  |  | 950 | [10 empty] | 67.76 |  |  |  | 67.76 | [5 empty] | 73.01 |  |  | 67.95 |  |  |  | 1.15 |  | 0.88 | [8 empty] | 31.36 |  |  |  |  | 0.00
2020 |  |  |  | 7368.35 |  |  | 7307 |  |  |  | 950 | [10 empty] | 83.11 |  |  |  | 83.11 | [5 empty] | 88.30 |  |  | 83.19 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 16.87 |  |  |  |  | 0.00
2021 |  |  |  | 8516.23 |  |  | 8296 |  |  |  | 950 | [10 empty] | 94.64 |  |  |  | 94.64 | [5 empty] | 102.33 |  |  | 94.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.36 |  |  |  |  | 0.00
2022 |  |  |  | 8167.11 |  |  | 7962 |  |  |  | 950 | [10 empty] | 90.70 |  |  |  | 90.76 | [5 empty] | 98.14 |  |  | 90.89 |  |  |  | 0.15 |  | 0.13 | [8 empty] | 9.11 |  |  |  |  | 0.05
2023 |  |  |  | 7999.26 |  |  | 7797 |  |  |  | 950 | [10 empty] | 88.81 |  |  |  | 88.81 | [5 empty] | 96.12 |  |  | 89.01 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 11.18 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1993 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 25
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 971 | [14 empty] | 1153
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 15
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 11
L. |  | Human factor related | [39 empty] | 0
Z. |  | Other | [51 empty] | 56
Subtotal | [22 empty] | 971 | [14 empty] | 1168 |  |  |  | 25 | [11 empty] | 67
Total | [22 empty] | 971 | [14 empty] | 1260
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1993 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 1
16. |  |  | Steam generation systems | [34 empty] | 7
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 27
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-October, December. Additional electricity generation amounted to 543695 MWh. The unit was in the overhaul outage from 2023.10.08 to 2023.12.07. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BELOYARSK-3
2023 Operating Experience
RU-21 | [8 empty] | BELOYARSK-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | LMZ (JOINT-STOCK COMPANY "LENINGRADSKIY METALLICHESKIY ZAVOD")
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | FBR / BN-600 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1969-01-01
Thermal power | [12 empty] | : |  |  | 1470 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-04-08
Gross electrical power | [12 empty] | : |  |  | 600 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-11-01
Reference unit power (net) | [12 empty] | : |  |  | 560 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 8.8
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 550
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 5 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 3
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 100000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.05 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 13
| Active core height/length [m] | [13 empty] | : |  |  | 1.03 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 369 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 38 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 19 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | Na | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2961.93 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.73 %
Energy Availability Factor (EAF) | [18 empty] | : | 59.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.05 %
Unit Capability Factor (UCF) | [18 empty] | : | 59.52 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 39.44 %
Load Factor (LF) | [18 empty] | : | 60.38 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 61.14 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3404 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 52.61 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 424.65 | 374.94 |  |  |  | 301.12 |  | 305.82 | [8 empty] | 432.11 |  |  | 413.72 | [6 empty] | 378.71 |  | 310.47 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 20.39 |  |  | 2961.93
EAF [%] |  |  |  |  | 100.00 | 98.41 |  |  |  | 71.76 |  | 73.45 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 89.84 |  | 74.74 |  |  |  | 0.04 |  |  | 0.04 |  |  | 0.04 | [9 empty] | 7.57 |  |  | 59.52
UCF [%] |  |  |  |  | 100.00 | 98.41 |  |  |  | 71.76 |  | 73.45 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 89.84 |  | 74.76 |  |  |  | 0.04 |  |  | 0.04 |  |  | 0.04 | [9 empty] | 7.57 |  |  | 59.52
LF [%] |  |  |  |  | 101.92 | 99.63 |  |  |  | 72.27 |  | 75.85 | [8 empty] | 103.71 |  |  | 102.61 | [6 empty] | 90.90 |  | 74.52 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 4.89 |  |  | 60.38
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 73.12 |  | 75.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 76.21 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 10.89 |  |  | 61.14
FLR [%] |  |  |  |  | 0.00 | 1.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 10.16 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 8.84 |  |  | 1.73
UCL [%] |  |  |  |  | 0.00 | 1.59 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 10.16 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.73 |  |  | 1.05
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 28.24 |  | 26.55 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 25.24 |  |  |  | 99.96 |  |  | 99.96 |  |  | 99.96 | [9 empty] | 91.70 |  |  | 39.44
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.02 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 159916.04 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.59 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.43 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.89 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.92 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.18 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 75.95 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.49 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.43 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | Data not provided
1982 |  |  |  | 2771.00 |  |  | 5555 |  |  |  | 560 | [10 empty] | 59.25 |  |  |  | 59.25 | [5 empty] | 56.49 |  |  | 63.41 |  |  |  | 11.50 |  | 7.70 | [8 empty] | 33.05 |  |  |  |  | 0.00
1983 |  |  |  | 3545.21 |  |  | 6737 |  |  |  | 560 | [10 empty] | 72.72 |  |  |  | 73.35 | [5 empty] | 72.27 |  |  | 76.91 |  |  |  | 3.71 |  | 2.82 | [8 empty] | 23.83 |  |  |  |  | 0.63
1984 |  |  |  | 3584.11 |  |  | 6848 |  |  |  | 560 | [10 empty] | 73.29 |  |  |  | 73.29 | [5 empty] | 72.86 |  |  | 77.96 |  |  |  | 5.70 |  | 4.43 | [8 empty] | 22.28 |  |  |  |  | 0.00
1985 |  |  |  | 3561.83 |  |  | 6544 |  |  |  | 560 | [10 empty] | 72.85 |  |  |  | 72.85 | [5 empty] | 72.61 |  |  | 74.70 |  |  |  | 2.47 |  | 1.85 | [8 empty] | 25.30 |  |  |  |  | 0.00
1986 |  |  |  | 3600.73 |  |  | 6818 |  |  |  | 560 | [10 empty] | 73.82 |  |  |  | 74.28 | [5 empty] | 73.40 |  |  | 77.83 |  |  |  | 4.78 |  | 3.73 | [8 empty] | 21.99 |  |  |  |  | 0.46
1987 |  |  |  | 3894.99 |  |  | 6714 |  |  |  | 600 | [10 empty] | 75.93 |  |  |  | 75.93 | [5 empty] | 74.11 |  |  | 76.64 |  |  |  | 2.64 |  | 2.05 | [8 empty] | 22.02 |  |  |  |  | 0.00
1988 |  |  |  | 3762.19 |  |  | 6810 |  |  |  | 560 | [10 empty] | 76.97 |  |  |  | 76.97 | [5 empty] | 76.48 |  |  | 77.53 |  |  |  | 0.38 |  | 0.30 | [8 empty] | 22.74 |  |  |  |  | 0.00
1989 |  |  |  | 3694.43 |  |  | 6800 |  |  |  | 560 | [10 empty] | 76.95 |  |  |  | 76.95 | [5 empty] | 75.31 |  |  | 77.63 |  |  |  | 1.21 |  | 0.94 | [8 empty] | 22.10 |  |  |  |  | 0.00
1990 |  |  |  | 3198.00 |  |  | 6627 |  |  |  | 560 | [10 empty] | 65.85 |  |  |  | 66.65 | [5 empty] | 65.19 |  |  | 75.65 |  |  |  | 11.05 |  | 8.28 | [8 empty] | 25.07 |  |  |  |  | 0.79
1991 |  |  |  | 3394.00 |  |  | 6631 |  |  |  | 560 | [10 empty] | 63.57 |  |  |  | 63.57 | [5 empty] | 69.19 |  |  | 75.70 |  |  |  | 13.75 |  | 10.14 | [8 empty] | 26.29 |  |  |  |  | 0.00
1992 |  |  |  | 4094.97 |  |  | 7449 |  |  |  | 560 | [10 empty] | 82.82 |  |  |  | 83.06 | [5 empty] | 83.26 |  |  | 84.81 |  |  |  | 0.34 |  | 0.28 | [8 empty] | 16.66 |  |  |  |  | 0.24
1993 |  |  |  | 3914.92 |  |  | 7065 |  |  |  | 560 | [10 empty] | 79.49 |  |  |  | 79.57 | [5 empty] | 79.81 |  |  | 80.65 |  |  |  | 7.18 |  | 6.15 | [8 empty] | 14.28 |  |  |  |  | 0.07
1994 |  |  |  | 3810.67 |  |  | 6977 |  |  |  | 560 | [10 empty] | 78.78 |  |  |  | 78.92 | [5 empty] | 77.68 |  |  | 79.65 |  |  |  | 0.90 |  | 0.71 | [8 empty] | 20.37 |  |  |  |  | 0.14
1995 |  |  |  | 3413.27 |  |  | 6953 |  |  |  | 560 | [10 empty] | 70.70 |  |  |  | 72.28 | [5 empty] | 69.58 |  |  | 79.37 |  |  |  | 9.36 |  | 7.46 | [8 empty] | 20.26 |  |  |  |  | 1.57
1996 |  |  |  | 3722.33 |  |  | 7010 |  |  |  | 560 | [10 empty] | 76.32 |  |  |  | 78.07 | [5 empty] | 75.67 |  |  | 79.80 |  |  |  | 1.72 |  | 1.37 | [8 empty] | 20.57 |  |  |  |  | 1.75
1997 |  |  |  | 3545.80 |  |  | 6596 |  |  |  | 560 | [10 empty] | 72.97 |  |  |  | 74.58 | [5 empty] | 72.28 |  |  | 75.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.42 |  |  |  |  | 1.61
1998 |  |  |  | 2335.33 |  |  | 4385 |  |  |  | 560 | [10 empty] | 47.67 |  |  |  | 49.23 | [5 empty] | 47.61 |  |  | 50.06 |  |  |  | 38.80 |  | 31.21 | [8 empty] | 19.55 |  |  |  |  | 1.56
1999 |  |  |  | 3720.99 |  |  | 6972 |  |  |  | 560 | [10 empty] | 76.18 |  |  |  | 77.96 | [5 empty] | 75.85 |  |  | 79.59 |  |  |  | 4.10 |  | 3.34 | [8 empty] | 18.71 |  |  |  |  | 1.78
2000 |  |  |  | 3565.82 |  |  | 6820 |  |  |  | 560 | [10 empty] | 72.49 |  |  |  | 75.49 | [5 empty] | 72.49 |  |  | 77.64 |  |  |  | 0.31 |  | 0.23 | [8 empty] | 24.27 |  |  |  |  | 3.00
2001 |  |  |  | 3891.10 |  |  | 7214 |  |  |  | 560 | [10 empty] | 79.90 |  |  |  | 80.72 | [5 empty] | 79.32 |  |  | 82.35 |  |  |  | 1.24 |  | 1.01 | [8 empty] | 18.27 |  |  |  |  | 0.82
2002 |  |  |  | 3774.40 |  |  | 7069 |  |  |  | 560 | [10 empty] | 77.30 |  |  |  | 79.34 | [5 empty] | 76.94 |  |  | 80.70 |  |  |  | 2.14 |  | 1.74 | [8 empty] | 18.93 |  |  |  |  | 2.04
2003 |  |  |  | 3693.28 |  |  | 6836 |  |  |  | 560 | [10 empty] | 75.74 |  |  |  | 76.81 | [5 empty] | 75.29 |  |  | 78.04 |  |  |  | 0.91 |  | 0.71 | [8 empty] | 22.48 |  |  |  |  | 1.07
2004 |  |  |  | 3927.64 |  |  | 7185 |  |  |  | 560 | [10 empty] | 80.02 |  |  |  | 80.81 | [5 empty] | 79.85 |  |  | 81.80 |  |  |  | 0.78 |  | 0.64 | [8 empty] | 18.56 |  |  |  |  | 0.78
2005 |  |  |  | 3802.75 |  |  | 6977 |  |  |  | 560 | [10 empty] | 77.76 |  |  |  | 78.77 | [5 empty] | 77.52 |  |  | 79.65 |  |  |  | 0.09 |  | 0.07 | [8 empty] | 21.16 |  |  |  |  | 1.02
2006 |  |  |  | 3844.94 |  |  | 7001 |  |  |  | 560 | [10 empty] | 78.38 |  |  |  | 79.02 | [5 empty] | 78.38 |  |  | 79.92 |  |  |  | 0.36 |  | 0.29 | [8 empty] | 20.69 |  |  |  |  | 0.65
2007 |  |  |  | 3798.42 |  |  | 7089 |  |  |  | 560 | [10 empty] | 77.52 |  |  |  | 77.80 | [5 empty] | 77.43 |  |  | 80.92 |  |  |  | 0.46 |  | 0.36 | [8 empty] | 21.84 |  |  |  |  | 0.28
2008 |  |  |  | 3781.03 |  |  | 6918 |  |  |  | 560 | [10 empty] | 76.85 |  |  |  | 76.95 | [5 empty] | 76.87 |  |  | 78.76 |  |  |  | 0.47 |  | 0.36 | [8 empty] | 22.69 |  |  |  |  | 0.10
2009 |  |  |  | 3736.60 |  |  | 6734 |  |  |  | 560 | [10 empty] | 75.58 |  |  |  | 75.61 | [5 empty] | 76.17 |  |  | 76.87 |  |  |  | 0.49 |  | 0.37 | [8 empty] | 24.01 |  |  |  |  | 0.03
2010 |  |  |  | 3669.75 |  |  | 6541 |  |  |  | 560 | [10 empty] | 73.51 |  |  |  | 73.56 | [5 empty] | 74.81 |  |  | 74.67 |  |  |  | 0.73 |  | 0.54 | [8 empty] | 25.90 |  |  |  |  | 0.05
2011 |  |  |  | 3968.73 |  |  | 7141 |  |  |  | 560 | [10 empty] | 79.17 |  |  |  | 79.17 | [5 empty] | 80.91 |  |  | 81.53 |  |  |  | 0.71 |  | 0.57 | [8 empty] | 20.26 |  |  |  |  | 0.00
2012 |  |  |  | 3975.50 |  |  | 7250 |  |  |  | 560 | [10 empty] | 78.84 |  |  |  | 78.84 | [5 empty] | 80.82 |  |  | 82.54 |  |  |  | 1.62 |  | 2.69 | [8 empty] | 18.47 |  |  |  |  | 0.00
2013 |  |  |  | 3841.06 |  |  | 7398 |  |  |  | 560 | [10 empty] | 77.62 |  |  |  | 77.80 | [5 empty] | 78.30 |  |  | 84.45 |  |  |  | 7.27 |  | 6.10 | [8 empty] | 16.11 |  |  |  |  | 0.18
2014 |  |  |  | 4222.91 |  |  | 7455 |  |  |  | 560 | [10 empty] | 83.77 |  |  |  | 83.77 | [5 empty] | 86.07 |  |  | 85.09 |  |  |  | 0.58 |  | 0.49 | [8 empty] | 15.75 |  |  |  |  | 0.00
2015 |  |  |  | 4220.16 |  |  | 7414 |  |  |  | 560 | [10 empty] | 83.78 |  |  |  | 83.78 | [5 empty] | 86.03 |  |  | 84.63 |  |  |  | 0.39 |  | 0.33 | [8 empty] | 15.89 |  |  |  |  | 0.00
2016 |  |  |  | 4307.17 |  |  | 7517 |  |  |  | 560 | [10 empty] | 84.66 |  |  |  | 84.66 | [5 empty] | 87.56 |  |  | 85.58 |  |  |  | 0.41 |  | 0.35 | [8 empty] | 14.98 |  |  |  |  | 0.00
2017 |  |  |  | 4323.23 |  |  | 7548 |  |  |  | 560 | [10 empty] | 85.36 |  |  |  | 85.36 | [5 empty] | 88.13 |  |  | 86.16 |  |  |  | 0.32 |  | 0.27 | [8 empty] | 14.36 |  |  |  |  | 0.00
2018 |  |  |  | 3809.52 |  |  | 6911 |  |  |  | 560 | [10 empty] | 75.28 |  |  |  | 75.28 | [5 empty] | 77.66 |  |  | 78.89 |  |  |  | 3.23 |  | 3.38 | [8 empty] | 21.34 |  |  |  |  | 0.00
2019 |  |  |  | 4184.26 |  |  | 7453 |  |  |  | 560 | [10 empty] | 82.22 |  |  |  | 82.22 | [5 empty] | 85.30 |  |  | 85.08 |  |  |  | 1.95 |  | 2.15 | [8 empty] | 15.63 |  |  |  |  | 0.00
2020 |  |  |  | 4169.76 |  |  | 7338 |  |  |  | 560 | [10 empty] | 81.60 |  |  |  | 81.60 | [5 empty] | 84.77 |  |  | 83.54 |  |  |  | 1.47 |  | 1.22 | [8 empty] | 17.19 |  |  |  |  | 0.00
2021 |  |  |  | 4152.25 |  |  | 7484 |  |  |  | 560 | [10 empty] | 82.23 |  |  |  | 82.23 | [5 empty] | 84.64 |  |  | 85.43 |  |  |  | 3.10 |  | 2.63 | [8 empty] | 15.14 |  |  |  |  | 0.00
2022 |  |  |  | 3670.83 |  |  | 6590 |  |  |  | 560 | [10 empty] | 72.84 |  |  |  | 72.84 | [5 empty] | 74.83 |  |  | 75.23 |  |  |  | 1.80 |  | 1.33 | [8 empty] | 25.83 |  |  |  |  | 0.00
2023 |  |  |  | 2961.93 |  |  | 5356 |  |  |  | 560 | [10 empty] | 59.52 |  |  |  | 59.52 | [5 empty] | 60.38 |  |  | 61.14 |  |  |  | 1.73 |  | 1.05 | [8 empty] | 39.44 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1981 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 113
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 3405 | [14 empty] | 1343
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 400 |  |  |  | 5
H. |  | Nuclear regulatory requirements | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 1
T. |  | Heat supply (on-site to support next unit or desalination and off-site distribution) | [51 empty] | 0
Subtotal | [22 empty] | 3405 | [14 empty] | 1743 |  |  |  | 120 | [11 empty] | 3
Total | [22 empty] | 3405 | [14 empty] | 1866
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1981 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 2
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 27
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 63
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 4
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [37 empty] | 115
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. Unit operation at power level above installed capacity took place in January-August. Additional electricity generation amounted to 56623 MWh. The unit was in the routine maintenance outage from 2023.03.23 to 2023.04.08 and the intermediate maintenance outage from 2023.08.24 to 2023.12.28. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BELOYARSK-4
2023 Operating Experience
RU-116 | [8 empty] | BELOYARSK-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | FBR / BN-800 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2006-07-18
Thermal power | [12 empty] | : |  |  | 2100 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2015-12-10
Gross electrical power | [12 empty] | : |  |  | 885 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2016-10-31
Reference unit power (net) | [12 empty] | : |  |  | 820 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 8 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 1.65
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 547
| Fuel material | [13 empty] | : |  |  | UO2/PuO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 6 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.56 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 13
| Active core height/length [m] | [13 empty] | : |  |  | 0.88 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 565 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 38 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 16 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | NA | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 4937.4 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 9.2 %
Energy Availability Factor (EAF) | [18 empty] | : | 68.68 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.23 %
Unit Capability Factor (UCF) | [18 empty] | : | 71.35 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.42 %
Load Factor (LF) | [18 empty] | : | 68.74 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.67 %
Operating Factor (OF) | [18 empty] | : | 76.45 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2063 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 587.10 | 270.98 |  |  |  | 318.55 |  | 588.93 | [8 empty] | 587.05 |  |  | 523.67 | [6 empty] | 596.28 |  | 288.09 |  |  |  | 0.00 |  |  | 171.05 |  |  | 540.04 | [9 empty] | 465.65 |  |  | 4937.40
EAF [%] |  |  |  |  | 95.42 | 49.53 |  |  |  | 52.58 |  | 98.86 | [8 empty] | 95.59 |  |  | 88.62 | [6 empty] | 97.18 |  | 47.87 |  |  |  | 0.06 |  |  | 29.58 |  |  | 90.85 | [9 empty] | 76.30 |  |  | 68.68
UCF [%] |  |  |  |  | 97.18 | 50.68 |  |  |  | 59.75 |  | 100.00 | [8 empty] | 97.18 |  |  | 90.86 | [6 empty] | 99.90 |  | 49.74 |  |  |  | 0.06 |  |  | 31.75 |  |  | 99.18 | [9 empty] | 78.08 |  |  | 71.35
LF [%] |  |  |  |  | 96.23 | 49.18 |  |  |  | 52.21 |  | 99.75 | [8 empty] | 96.23 |  |  | 88.70 | [6 empty] | 97.74 |  | 47.22 |  |  |  | 0.00 |  |  | 28.04 |  |  | 91.47 | [9 empty] | 76.33 |  |  | 68.74
OF [%] |  |  |  |  | 100.00 | 53.87 |  |  |  | 61.29 |  | 100.00 | [8 empty] | 100.00 |  |  | 92.78 | [6 empty] | 100.00 |  | 58.33 |  |  |  | 0.00 |  |  | 48.52 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 76.45
FLR [%] |  |  |  |  | 2.82 | 2.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.82 |  |  | 9.14 | [6 empty] | 0.10 |  | 13.57 |  |  |  | 0.00 |  |  | 55.09 |  |  | 0.64 | [9 empty] | 21.92 |  |  | 9.20
UCL [%] |  |  |  |  | 2.82 | 1.41 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.82 |  |  | 9.14 | [6 empty] | 0.10 |  | 7.81 |  |  |  | 0.00 |  |  | 38.96 |  |  | 0.64 | [9 empty] | 21.92 |  |  | 7.23
PUF [%] |  |  |  |  | 0.00 | 47.91 |  |  |  | 40.25 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 42.45 |  |  |  | 99.94 |  |  | 29.29 |  |  | 0.18 | [9 empty] | 0.00 |  |  | 21.42
XUF [%] |  |  |  |  | 1.76 | 1.15 |  |  |  | 7.16 |  | 1.14 | [8 empty] | 1.60 |  |  | 2.24 | [6 empty] | 2.72 |  | 1.87 |  |  |  | 0.00 |  |  | 2.18 |  |  | 8.33 | [9 empty] | 1.78 |  |  | 2.67
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 37108.78 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 7.01 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 67.06 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.93 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 68.44 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 25.63 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.38 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 71.12 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2016 |  |  |  | 3456.96 |  |  | 5453 |  |  |  | 820 | [10 empty] | 81.92 |  |  |  | 81.92 | [5 empty] | 81.96 |  |  | 96.45 |  |  |  | 18.08 |  | 18.08 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 5165.75 |  |  | 6551 |  |  |  | 820 | [10 empty] | 71.81 |  |  |  | 73.11 | [5 empty] | 71.91 |  |  | 74.78 |  |  |  | 1.71 |  | 4.59 | [8 empty] | 22.30 |  |  |  |  | 1.29
2018 |  |  |  | 4408.98 |  |  | 5680 |  |  |  | 820 | [10 empty] | 61.25 |  |  |  | 62.29 | [5 empty] | 61.38 |  |  | 64.84 |  |  |  | 5.45 |  | 3.59 | [8 empty] | 34.12 |  |  |  |  | 1.04
2019 |  |  |  | 4909.25 |  |  | 6196 |  |  |  | 820 | [10 empty] | 68.26 |  |  |  | 69.65 | [5 empty] | 68.34 |  |  | 70.73 |  |  |  | 3.35 |  | 4.61 | [8 empty] | 25.74 |  |  |  |  | 1.39
2020 |  |  |  | 5934.14 |  |  | 7373 |  |  |  | 820 | [10 empty] | 81.92 |  |  |  | 82.98 | [5 empty] | 82.39 |  |  | 83.94 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 16.64 |  |  |  |  | 1.06
2021 |  |  |  | 3087.27 |  |  | 4049 |  |  |  | 820 | [10 empty] | 43.31 |  |  |  | 44.47 | [5 empty] | 42.98 |  |  | 46.22 |  |  |  | 28.75 |  | 17.95 | [8 empty] | 37.58 |  |  |  |  | 1.15
2022 |  |  |  | 5174.47 |  |  | 6710 |  |  |  | 820 | [10 empty] | 71.64 |  |  |  | 72.91 | [5 empty] | 72.04 |  |  | 76.60 |  |  |  | 1.54 |  | 1.14 | [8 empty] | 25.95 |  |  |  |  | 1.28
2023 |  |  |  | 4937.40 |  |  | 6697 |  |  |  | 820 | [10 empty] | 68.68 |  |  |  | 71.35 | [5 empty] | 68.74 |  |  | 76.45 |  |  |  | 9.20 |  | 7.23 | [8 empty] | 21.42 |  |  |  |  | 2.67
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2016 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 225 | [14 empty] | 352
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1832 | [14 empty] | 1816
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 370
Subtotal | [22 empty] | 1832 |  |  |  | 225 | [10 empty] | 2186 |  |  |  | 352
Total | [22 empty] | 2057 | [14 empty] | 2538
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2016 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 177 | [14 empty] | 22
12. |  |  | Reactor I&C Systems | [19 empty] | 48 | [14 empty] | 30
14. |  |  | Safety Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 155
31. |  |  | Turbine and auxiliaries | [34 empty] | 57
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
41. |  |  | Main Generator Systems | [34 empty] | 29
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [22 empty] | 225 | [14 empty] | 316
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the routine maintenance outage from 2023.02.16 to 2023.03.12 and the overhaul from 2023.08.19 to 2023.10.09. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BILIBINO-2
2023 Operating Experience
RU-142 | [8 empty] | BILIBINO-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / EGP-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-01-01
Thermal power | [12 empty] | : |  |  | 62 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-12-30
Gross electrical power | [12 empty] | : |  |  | 12 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-02-01
Reference unit power (net) | [12 empty] | : |  |  | 11 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 280
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 3000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 273 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 36.43 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.26 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.23 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.52 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.25 %
Load Factor (LF) | [18 empty] | : | 37.8 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 88.81 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 980 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 13.35 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 2.75 | 4.07 |  |  |  | 1.90 |  | 2.99 | [8 empty] | 2.83 |  |  | 3.70 | [6 empty] | 0.95 |  | 2.07 |  |  |  | 1.70 |  |  | 2.42 |  |  | 5.97 | [9 empty] | 5.07 |  |  | 36.43
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 63.14 |  | 84.68 | [8 empty] | 100.00 |  |  | 97.15 | [6 empty] | 32.49 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 98.55 |  |  | 89.52
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 63.14 |  | 84.68 | [8 empty] | 100.00 |  |  | 97.15 | [6 empty] | 32.49 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 98.55 |  |  | 89.52
LF [%] |  |  |  |  | 33.54 | 55.01 |  |  |  | 23.22 |  | 37.79 | [8 empty] | 34.64 |  |  | 46.68 | [6 empty] | 11.66 |  | 25.27 |  |  |  | 21.50 |  |  | 29.57 |  |  | 75.40 | [9 empty] | 61.99 |  |  | 37.80
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 61.42 |  | 84.03 | [8 empty] | 100.00 |  |  | 94.31 | [6 empty] | 29.30 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 98.52 |  |  | 88.81
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.85 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.26
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.85 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.23
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 36.86 |  | 15.32 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 67.51 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 1.45 |  |  | 10.25
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 2344.32 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.49 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.44 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.81 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.75 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 51.13 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 8.32 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.66 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 63.76 |  |  | 7365 |  |  |  | 10 | [10 empty] | 88.97 |  |  |  | 94.67 | [5 empty] | 78.14 |  |  | 90.14 |  |  |  | 1.31 |  | 1.26 | [8 empty] | 4.07 |  |  |  |  | 5.70
1976 |  |  |  | 66.10 |  |  | 7901 |  |  |  | 10 | [10 empty] | 83.67 |  |  |  | 89.44 | [5 empty] | 75.25 |  |  | 89.95 |  |  |  | 1.10 |  | 0.99 | [8 empty] | 9.56 |  |  |  |  | 5.77
1977 |  |  |  | 57.04 |  |  | 7865 |  |  |  | 10 | [10 empty] | 81.34 |  |  |  | 90.50 | [5 empty] | 65.12 |  |  | 89.78 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 9.46 |  |  |  |  | 9.16
1978 |  |  |  | 60.61 |  |  | 7929 |  |  |  | 10 | [10 empty] | 94.81 |  |  |  | 94.81 | [5 empty] | 69.19 |  |  | 90.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.19 |  |  |  |  | 0.00
1979 |  |  |  | 69.85 |  |  | 8170 |  |  |  | 10 | [10 empty] | 88.17 |  |  |  | 92.93 | [5 empty] | 79.74 |  |  | 93.26 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 7.00 |  |  |  |  | 4.76
1980 |  |  |  | 44.05 |  |  | 5666 |  |  |  | 10 | [10 empty] | 59.82 |  |  |  | 62.73 | [5 empty] | 50.15 |  |  | 64.50 |  |  |  | 35.24 |  | 34.13 | [8 empty] | 3.14 |  |  |  |  | 2.91
1981 |  |  |  | 41.36 |  |  | 6520 |  |  |  | 10 | [10 empty] | 70.39 |  |  |  | 73.15 | [5 empty] | 47.21 |  |  | 74.43 |  |  |  | 4.87 |  | 3.74 | [8 empty] | 23.11 |  |  |  |  | 2.76
1982 |  |  |  | 63.92 |  |  | 7028 |  |  |  | 10 | [10 empty] | 79.24 |  |  |  | 79.24 | [5 empty] | 72.97 |  |  | 80.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.76 |  |  |  |  | 0.00
1983 |  |  |  | 73.76 |  |  | 7880 |  |  |  | 10 | [10 empty] | 86.92 |  |  |  | 90.06 | [5 empty] | 84.20 |  |  | 89.95 |  |  |  | 1.96 |  | 1.80 | [8 empty] | 8.14 |  |  |  |  | 3.14
1984 |  |  |  | 77.63 |  |  | 7891 |  |  |  | 10 | [10 empty] | 88.51 |  |  |  | 89.32 | [5 empty] | 88.38 |  |  | 89.83 |  |  |  | 0.29 |  | 0.26 | [8 empty] | 10.41 |  |  |  |  | 0.81
1985 |  |  |  | 78.00 |  |  | 7940 |  |  |  | 10 | [10 empty] | 88.57 |  |  |  | 90.29 | [5 empty] | 89.04 |  |  | 90.64 |  |  |  | 0.46 |  | 0.42 | [8 empty] | 9.29 |  |  |  |  | 1.73
1986 |  |  |  | 76.34 |  |  | 7679 |  |  |  | 10 | [10 empty] | 84.69 |  |  |  | 87.04 | [5 empty] | 87.14 |  |  | 87.66 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 12.93 |  |  |  |  | 2.35
1987 |  |  |  | 88.42 |  |  | 7794 |  |  |  | 12 | [10 empty] | 89.10 |  |  |  | 89.10 | [5 empty] | 84.12 |  |  | 88.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.90 |  |  |  |  | 0.00
1988 |  |  |  | 75.07 |  |  | 7927 |  |  |  | 11 | [10 empty] | 90.84 |  |  |  | 90.84 | [5 empty] | 77.69 |  |  | 90.24 |  |  |  | 0.64 |  | 0.58 | [8 empty] | 8.57 |  |  |  |  | 0.00
1989 |  |  |  | 74.81 |  |  | 7943 |  |  |  | 11 | [10 empty] | 91.38 |  |  |  | 91.38 | [5 empty] | 77.64 |  |  | 90.67 |  |  |  | 0.34 |  | 0.31 | [8 empty] | 8.31 |  |  |  |  | 0.00
1990 |  |  |  | 72.62 |  |  | 7274 |  |  |  | 11 | [10 empty] | 84.57 |  |  |  | 84.57 | [5 empty] | 75.36 |  |  | 83.04 |  |  |  | 3.23 |  | 2.83 | [8 empty] | 12.61 |  |  |  |  | 0.00
1991 |  |  |  | 57.83 |  |  | 4821 |  |  |  | 11 | [10 empty] | 64.92 |  |  |  | 64.92 | [5 empty] | 60.02 |  |  | 55.03 |  |  |  | 20.10 |  | 16.33 | [8 empty] | 18.74 |  |  |  |  | 0.00
1992 |  |  |  | 68.24 |  |  | 7857 |  |  |  | 11 | [10 empty] | 89.91 |  |  |  | 89.91 | [5 empty] | 70.63 |  |  | 89.45 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 9.99 |  |  |  |  | 0.00
1993 |  |  |  | 52.45 |  |  | 7072 |  |  |  | 11 | [10 empty] | 62.17 |  |  |  | 81.86 | [5 empty] | 54.43 |  |  | 80.73 |  |  |  | 1.69 |  | 1.41 | [8 empty] | 16.73 |  |  |  |  | 19.69
1994 |  |  |  | 47.83 |  |  | 6763 |  |  |  | 11 | [10 empty] | 77.31 |  |  |  | 78.74 | [5 empty] | 49.64 |  |  | 77.20 |  |  |  | 2.81 |  | 2.28 | [8 empty] | 18.98 |  |  |  |  | 1.43
1995 |  |  |  | 45.45 |  |  | 8677 |  |  |  | 11 | [10 empty] | 97.19 |  |  |  | 99.19 | [5 empty] | 47.16 |  |  | 99.05 |  |  |  | 0.69 |  | 0.69 | [8 empty] | 0.12 |  |  |  |  | 2.00
1996 |  |  |  | 16.83 |  |  | 2894 |  |  |  | 11 | [10 empty] | 33.47 |  |  |  | 33.47 | [5 empty] | 17.42 |  |  | 32.95 |  |  |  | 2.84 |  | 0.98 | [8 empty] | 65.55 |  |  |  |  | 0.00
1997 |  |  |  | 44.11 |  |  | 8050 |  |  |  | 11 | [10 empty] | 87.71 |  |  |  | 92.70 | [5 empty] | 45.78 |  |  | 91.89 |  |  |  | 0.36 |  | 0.34 | [8 empty] | 6.97 |  |  |  |  | 4.99
1998 |  |  |  | 18.16 |  |  | 3727 |  |  |  | 11 | [10 empty] | 23.30 |  |  |  | 42.91 | [5 empty] | 18.85 |  |  | 42.55 |  |  |  | 0.07 |  | 0.03 | [8 empty] | 57.06 |  |  |  |  | 19.61
1999 |  |  |  | 54.16 |  |  | 7355 |  |  |  | 11 | [10 empty] | 64.09 |  |  |  | 84.73 | [5 empty] | 56.21 |  |  | 83.96 |  |  |  | 0.45 |  | 0.39 | [8 empty] | 14.88 |  |  |  |  | 20.64
2000 |  |  |  | 48.46 |  |  | 6656 |  |  |  | 11 | [10 empty] | 56.35 |  |  |  | 78.15 | [5 empty] | 50.15 |  |  | 75.77 |  |  |  | 0.22 |  | 0.17 | [8 empty] | 21.68 |  |  |  |  | 21.80
2001 |  |  |  | 56.71 |  |  | 7439 |  |  |  | 11 | [10 empty] | 65.81 |  |  |  | 85.23 | [5 empty] | 58.86 |  |  | 84.92 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.77 |  |  |  |  | 19.42
2002 |  |  |  | 30.02 |  |  | 5744 |  |  |  | 11 | [10 empty] | 38.39 |  |  |  | 66.40 | [5 empty] | 31.16 |  |  | 65.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.60 |  |  |  |  | 28.01
2003 |  |  |  | 33.25 |  |  | 7162 |  |  |  | 11 | [10 empty] | 44.48 |  |  |  | 82.22 | [5 empty] | 34.51 |  |  | 81.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.78 |  |  |  |  | 37.74
2004 |  |  |  | 17.92 |  |  | 5851 |  |  |  | 11 | [10 empty] | 27.23 |  |  |  | 70.29 | [5 empty] | 18.55 |  |  | 66.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 29.71 |  |  |  |  | 43.05
2005 |  |  |  | 25.33 |  |  | 7351 |  |  |  | 11 | [10 empty] | 38.19 |  |  |  | 84.94 | [5 empty] | 26.29 |  |  | 83.92 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 15.03 |  |  |  |  | 46.76
2006 |  |  |  | 20.34 |  |  | 7248 |  |  |  | 11 | [10 empty] | 32.71 |  |  |  | 84.22 | [5 empty] | 21.11 |  |  | 82.74 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.78 |  |  |  |  | 51.52
2007 |  |  |  | 26.38 |  |  | 7478 |  |  |  | 11 | [10 empty] | 39.89 |  |  |  | 86.70 | [5 empty] | 27.37 |  |  | 85.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.30 |  |  |  |  | 46.80
2008 |  |  |  | 30.27 |  |  | 6490 |  |  |  | 11 | [10 empty] | 78.78 |  |  |  | 78.78 | [5 empty] | 31.33 |  |  | 73.88 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.22 |  |  |  |  | 0.00
2009 |  |  |  | 42.44 |  |  | 7388 |  |  |  | 11 | [10 empty] | 86.12 |  |  |  | 86.12 | [5 empty] | 44.04 |  |  | 84.34 |  |  |  | 0.89 |  | 0.78 | [8 empty] | 13.10 |  |  |  |  | 0.00
2010 |  |  |  | 48.08 |  |  | 7627 |  |  |  | 11 | [10 empty] | 88.09 |  |  |  | 88.09 | [5 empty] | 49.89 |  |  | 87.07 |  |  |  | 0.75 |  | 0.66 | [8 empty] | 11.25 |  |  |  |  | 0.00
2011 |  |  |  | 21.71 |  |  | 4977 |  |  |  | 11 | [10 empty] | 84.38 |  |  |  | 84.38 | [5 empty] | 22.53 |  |  | 56.82 |  |  |  | 1.45 |  | 1.24 | [8 empty] | 14.38 |  |  |  |  | 0.00
2012 |  |  |  | 28.27 |  |  | 5461 |  |  |  | 11 | [10 empty] | 72.73 |  |  |  | 72.73 | [5 empty] | 29.26 |  |  | 62.17 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 27.24 |  |  |  |  | 0.00
2013 |  |  |  | 43.12 |  |  | 6904 |  |  |  | 11 | [10 empty] | 85.84 |  |  |  | 85.84 | [5 empty] | 44.75 |  |  | 78.81 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.16 |  |  |  |  | 0.00
2014 |  |  |  | 40.96 |  |  | 6457 |  |  |  | 11 | [10 empty] | 84.92 |  |  |  | 84.92 | [5 empty] | 42.51 |  |  | 73.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.08 |  |  |  |  | 0.00
2015 |  |  |  | 39.78 |  |  | 6331 |  |  |  | 11 | [10 empty] | 73.73 |  |  |  | 73.73 | [5 empty] | 41.28 |  |  | 72.27 |  |  |  | 0.44 |  | 0.32 | [8 empty] | 25.95 |  |  |  |  | 0.00
2016 |  |  |  | 35.79 |  |  | 6506 |  |  |  | 11 | [10 empty] | 75.88 |  |  |  | 75.88 | [5 empty] | 37.04 |  |  | 74.07 |  |  |  | 0.86 |  | 0.66 | [8 empty] | 23.46 |  |  |  |  | 0.00
2017 |  |  |  | 44.31 |  |  | 7393 |  |  |  | 11 | [10 empty] | 85.12 |  |  |  | 85.12 | [5 empty] | 45.98 |  |  | 84.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.88 |  |  |  |  | 0.00
2018 |  |  |  | 54.16 |  |  | 7383 |  |  |  | 11 | [10 empty] | 84.99 |  |  |  | 84.99 | [5 empty] | 56.20 |  |  | 84.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.01 |  |  |  |  | 0.00
2019 |  |  |  | 57.78 |  |  | 7398 |  |  |  | 11 | [10 empty] | 85.16 |  |  |  | 85.16 | [5 empty] | 59.97 |  |  | 84.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.84 |  |  |  |  | 0.00
2020 |  |  |  | 32.42 |  |  | 6429 |  |  |  | 11 | [10 empty] | 74.40 |  |  |  | 74.40 | [5 empty] | 33.55 |  |  | 73.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.60 |  |  |  |  | 0.00
2021 |  |  |  | 28.85 |  |  | 7051 |  |  |  | 11 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 29.94 |  |  | 80.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.90 |  |  |  |  | 0.00
2022 |  |  |  | 32.58 |  |  | 7214 |  |  |  | 11 | [10 empty] | 82.42 |  |  |  | 82.42 | [5 empty] | 33.81 |  |  | 82.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.58 |  |  |  |  | 0.00
2023 |  |  |  | 36.43 |  |  | 7780 |  |  |  | 11 | [10 empty] | 89.52 |  |  |  | 89.52 | [5 empty] | 37.80 |  |  | 88.81 |  |  |  | 0.26 |  | 0.23 | [8 empty] | 10.25 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1975 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 41 | [14 empty] | 101
B. |  | Refuelling without maintenance | [35 empty] | 8
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 929 | [14 empty] | 1414 |  |  |  | 61
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 97
E. |  | Testing of plant systems or components | [20 empty] | 11 | [14 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 12
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 109
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [35 empty] | 4
Subtotal | [22 empty] | 940 |  |  |  | 41 | [10 empty] | 1530 |  |  |  | 167 | [11 empty] | 121
Total | [22 empty] | 981 | [14 empty] | 1818
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1975 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 52
12. |  |  | Reactor I&C Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [19 empty] | 41 | [14 empty] | 5
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 15
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
33. |  |  | Circulating Water System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 5
Total | [22 empty] | 41 | [14 empty] | 101
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. The unit was in the intermediate maintenance outage from 2023.07.08 to 2023.07.30 and routine maintenance from 2023.03.19 to 2023.04.05. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BILIBINO-3
2023 Operating Experience
RU-143 | [8 empty] | BILIBINO-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / EGP-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-01-01
Thermal power | [12 empty] | : |  |  | 62 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1975-12-22
Gross electrical power | [12 empty] | : |  |  | 12 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1976-02-01
Reference unit power (net) | [12 empty] | : |  |  | 11 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 48 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 280
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 3000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 273 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 37.87 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 93.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.28 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.72 %
Load Factor (LF) | [18 empty] | : | 39.3 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.85 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 626 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 23.79 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 2.51 | 3.24 |  |  |  | 3.83 |  | 2.34 | [8 empty] | 1.45 |  |  | 0.26 | [6 empty] | 3.66 |  | 2.69 |  |  |  | 2.78 |  |  | 5.07 |  |  | 5.59 | [9 empty] | 4.43 |  |  | 37.87
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 40.38 | [6 empty] | 78.62 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.28
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 40.38 | [6 empty] | 78.62 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.28
LF [%] |  |  |  |  | 30.71 | 43.83 |  |  |  | 46.77 |  | 29.56 | [8 empty] | 17.74 |  |  | 3.30 | [6 empty] | 44.70 |  | 32.92 |  |  |  | 35.15 |  |  | 61.93 |  |  | 70.64 | [9 empty] | 54.19 |  |  | 39.30
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 37.50 | [6 empty] | 77.55 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 98.75 | [9 empty] | 100.00 |  |  | 92.85
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 59.62 | [6 empty] | 21.38 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.72
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 2376.01 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.6 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.61 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.49 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.96 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.54 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 52.84 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 8.36 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.31 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1976 |  |  |  | 51.20 |  |  | 6655 |  |  |  | 10 | [10 empty] | 83.33 |  |  |  | 90.55 | [5 empty] | 62.19 |  |  | 77.39 |  |  |  | 2.85 |  | 2.65 | [8 empty] | 6.80 |  |  |  |  | 7.21
1977 |  |  |  | 46.50 |  |  | 7533 |  |  |  | 10 | [10 empty] | 78.21 |  |  |  | 92.83 | [5 empty] | 53.08 |  |  | 85.99 |  |  |  | 0.39 |  | 0.36 | [8 empty] | 6.81 |  |  |  |  | 14.62
1978 |  |  |  | 61.86 |  |  | 7514 |  |  |  | 10 | [10 empty] | 86.25 |  |  |  | 86.25 | [5 empty] | 70.61 |  |  | 85.78 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 13.74 |  |  |  |  | 0.00
1979 |  |  |  | 62.12 |  |  | 7837 |  |  |  | 10 | [10 empty] | 82.45 |  |  |  | 88.94 | [5 empty] | 70.92 |  |  | 89.46 |  |  |  | 0.16 |  | 0.14 | [8 empty] | 10.92 |  |  |  |  | 6.49
1980 |  |  |  | 79.43 |  |  | 8130 |  |  |  | 10 | [10 empty] | 90.99 |  |  |  | 92.18 | [5 empty] | 90.42 |  |  | 92.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.82 |  |  |  |  | 1.20
1981 |  |  |  | 89.78 |  |  | 8480 |  |  |  | 10 | [10 empty] | 96.64 |  |  |  | 96.64 | [5 empty] | 102.49 |  |  | 96.80 |  |  |  | 0.13 |  | 0.12 | [8 empty] | 3.24 |  |  |  |  | 0.00
1982 |  |  |  | 79.34 |  |  | 8323 |  |  |  | 10 | [10 empty] | 94.83 |  |  |  | 94.83 | [5 empty] | 90.57 |  |  | 95.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.17 |  |  |  |  | 0.00
1983 |  |  |  | 72.81 |  |  | 7782 |  |  |  | 10 | [10 empty] | 85.31 |  |  |  | 88.85 | [5 empty] | 83.11 |  |  | 88.84 |  |  |  | 0.34 |  | 0.31 | [8 empty] | 10.85 |  |  |  |  | 3.54
1984 |  |  |  | 76.48 |  |  | 7876 |  |  |  | 10 | [10 empty] | 87.36 |  |  |  | 89.14 | [5 empty] | 87.07 |  |  | 89.66 |  |  |  | 0.48 |  | 0.43 | [8 empty] | 10.42 |  |  |  |  | 1.79
1985 |  |  |  | 69.83 |  |  | 7119 |  |  |  | 10 | [10 empty] | 78.48 |  |  |  | 80.33 | [5 empty] | 79.72 |  |  | 81.27 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.67 |  |  |  |  | 1.85
1986 |  |  |  | 77.11 |  |  | 8001 |  |  |  | 10 | [10 empty] | 87.71 |  |  |  | 91.02 | [5 empty] | 88.03 |  |  | 91.34 |  |  |  | 0.66 |  | 0.60 | [8 empty] | 8.38 |  |  |  |  | 3.31
1987 |  |  |  | 89.09 |  |  | 7801 |  |  |  | 12 | [10 empty] | 89.09 |  |  |  | 89.09 | [5 empty] | 84.75 |  |  | 89.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.91 |  |  |  |  | 0.00
1988 |  |  |  | 76.71 |  |  | 7815 |  |  |  | 11 | [10 empty] | 89.47 |  |  |  | 89.47 | [5 empty] | 79.39 |  |  | 88.97 |  |  |  | 0.57 |  | 0.51 | [8 empty] | 10.02 |  |  |  |  | 0.00
1989 |  |  |  | 74.26 |  |  | 7756 |  |  |  | 11 | [10 empty] | 89.05 |  |  |  | 89.46 | [5 empty] | 77.06 |  |  | 88.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.54 |  |  |  |  | 0.40
1990 |  |  |  | 73.74 |  |  | 8024 |  |  |  | 11 | [10 empty] | 91.12 |  |  |  | 91.98 | [5 empty] | 76.53 |  |  | 91.60 |  |  |  | 6.83 |  | 6.75 | [8 empty] | 1.28 |  |  |  |  | 0.86
1991 |  |  |  | 66.19 |  |  | 6749 |  |  |  | 11 | [10 empty] | 76.59 |  |  |  | 78.08 | [5 empty] | 68.69 |  |  | 77.04 |  |  |  | 1.34 |  | 1.06 | [8 empty] | 20.86 |  |  |  |  | 1.50
1992 |  |  |  | 70.92 |  |  | 7727 |  |  |  | 11 | [10 empty] | 79.70 |  |  |  | 79.70 | [5 empty] | 73.40 |  |  | 87.97 |  |  |  | 0.40 |  | 0.32 | [8 empty] | 19.98 |  |  |  |  | 0.00
1993 |  |  |  | 52.59 |  |  | 7218 |  |  |  | 11 | [10 empty] | 61.50 |  |  |  | 83.21 | [5 empty] | 54.58 |  |  | 82.40 |  |  |  | 0.16 |  | 0.13 | [8 empty] | 16.66 |  |  |  |  | 21.71
1994 |  |  |  | 44.71 |  |  | 6342 |  |  |  | 11 | [10 empty] | 71.96 |  |  |  | 73.69 | [5 empty] | 46.39 |  |  | 72.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.31 |  |  |  |  | 1.73
1995 |  |  |  | 17.30 |  |  | 3293 |  |  |  | 11 | [10 empty] | 34.90 |  |  |  | 38.15 | [5 empty] | 17.95 |  |  | 37.59 |  |  |  | 9.46 |  | 3.99 | [8 empty] | 57.86 |  |  |  |  | 3.26
1996 |  |  |  | 52.62 |  |  | 7142 |  |  |  | 11 | [10 empty] | 82.27 |  |  |  | 82.27 | [5 empty] | 54.46 |  |  | 81.31 |  |  |  | 6.51 |  | 5.73 | [8 empty] | 12.00 |  |  |  |  | 0.00
1997 |  |  |  | 25.83 |  |  | 3769 |  |  |  | 11 | [10 empty] | 42.86 |  |  |  | 42.86 | [5 empty] | 26.80 |  |  | 43.03 |  |  |  | 0.86 |  | 0.37 | [8 empty] | 56.77 |  |  |  |  | 0.00
1998 |  |  |  | 23.16 |  |  | 4200 |  |  |  | 11 | [10 empty] | 29.11 |  |  |  | 49.13 | [5 empty] | 24.04 |  |  | 47.95 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 50.87 |  |  |  |  | 20.02
1999 |  |  |  | 51.44 |  |  | 6607 |  |  |  | 11 | [10 empty] | 59.91 |  |  |  | 75.85 | [5 empty] | 53.38 |  |  | 75.42 |  |  |  | 0.12 |  | 0.09 | [8 empty] | 24.06 |  |  |  |  | 15.94
2000 |  |  |  | 45.23 |  |  | 7569 |  |  |  | 11 | [10 empty] | 54.84 |  |  |  | 86.83 | [5 empty] | 46.81 |  |  | 86.17 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.17 |  |  |  |  | 31.99
2001 |  |  |  | 53.94 |  |  | 7383 |  |  |  | 11 | [10 empty] | 62.96 |  |  |  | 84.88 | [5 empty] | 55.98 |  |  | 84.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.12 |  |  |  |  | 21.91
2002 |  |  |  | 30.73 |  |  | 6250 |  |  |  | 11 | [10 empty] | 39.39 |  |  |  | 71.50 | [5 empty] | 31.90 |  |  | 71.35 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.50 |  |  |  |  | 32.11
2003 |  |  |  | 35.42 |  |  | 7097 |  |  |  | 11 | [10 empty] | 46.72 |  |  |  | 81.51 | [5 empty] | 36.75 |  |  | 81.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.49 |  |  |  |  | 34.79
2004 |  |  |  | 31.09 |  |  | 7166 |  |  |  | 11 | [10 empty] | 42.00 |  |  |  | 85.77 | [5 empty] | 32.18 |  |  | 81.58 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.23 |  |  |  |  | 43.77
2005 |  |  |  | 20.37 |  |  | 6102 |  |  |  | 11 | [10 empty] | 30.86 |  |  |  | 71.09 | [5 empty] | 21.14 |  |  | 69.66 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.91 |  |  |  |  | 40.23
2006 |  |  |  | 26.25 |  |  | 6542 |  |  |  | 11 | [10 empty] | 36.94 |  |  |  | 76.74 | [5 empty] | 27.24 |  |  | 74.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.26 |  |  |  |  | 39.80
2007 |  |  |  | 27.45 |  |  | 7257 |  |  |  | 11 | [10 empty] | 38.64 |  |  |  | 85.73 | [5 empty] | 28.49 |  |  | 82.84 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.27 |  |  |  |  | 47.09
2008 |  |  |  | 33.28 |  |  | 7335 |  |  |  | 11 | [10 empty] | 85.73 |  |  |  | 85.73 | [5 empty] | 34.44 |  |  | 83.50 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 14.20 |  |  |  |  | 0.00
2009 |  |  |  | 44.57 |  |  | 7972 |  |  |  | 11 | [10 empty] | 91.43 |  |  |  | 91.43 | [5 empty] | 46.25 |  |  | 91.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.57 |  |  |  |  | 0.00
2010 |  |  |  | 33.69 |  |  | 6035 |  |  |  | 11 | [10 empty] | 77.50 |  |  |  | 77.50 | [5 empty] | 34.96 |  |  | 68.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.50 |  |  |  |  | 0.00
2011 |  |  |  | 22.19 |  |  | 4885 |  |  |  | 11 | [10 empty] | 87.96 |  |  |  | 87.96 | [5 empty] | 23.03 |  |  | 55.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.04 |  |  |  |  | 0.00
2012 |  |  |  | 34.63 |  |  | 7253 |  |  |  | 11 | [10 empty] | 86.71 |  |  |  | 86.71 | [5 empty] | 35.84 |  |  | 82.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.29 |  |  |  |  | 0.00
2013 |  |  |  | 43.85 |  |  | 7436 |  |  |  | 11 | [10 empty] | 85.64 |  |  |  | 85.64 | [5 empty] | 45.51 |  |  | 84.89 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.36 |  |  |  |  | 0.00
2014 |  |  |  | 45.10 |  |  | 6615 |  |  |  | 11 | [10 empty] | 76.67 |  |  |  | 76.67 | [5 empty] | 46.80 |  |  | 75.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.33 |  |  |  |  | 0.00
2015 |  |  |  | 51.64 |  |  | 7337 |  |  |  | 11 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 53.60 |  |  | 83.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.90 |  |  |  |  | 0.00
2016 |  |  |  | 49.20 |  |  | 7410 |  |  |  | 11 | [10 empty] | 85.10 |  |  |  | 85.10 | [5 empty] | 50.92 |  |  | 84.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.90 |  |  |  |  | 0.00
2017 |  |  |  | 50.50 |  |  | 7377 |  |  |  | 11 | [10 empty] | 84.93 |  |  |  | 84.93 | [5 empty] | 52.41 |  |  | 84.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.07 |  |  |  |  | 0.00
2018 |  |  |  | 48.41 |  |  | 6626 |  |  |  | 11 | [10 empty] | 76.75 |  |  |  | 76.75 | [5 empty] | 50.24 |  |  | 75.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.25 |  |  |  |  | 0.00
2019 |  |  |  | 63.23 |  |  | 7849 |  |  |  | 11 | [10 empty] | 90.08 |  |  |  | 90.08 | [5 empty] | 65.62 |  |  | 89.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.92 |  |  |  |  | 0.00
2020 |  |  |  | 38.00 |  |  | 7380 |  |  |  | 11 | [10 empty] | 84.73 |  |  |  | 84.73 | [5 empty] | 39.33 |  |  | 84.02 |  |  |  | 0.21 |  | 0.18 | [8 empty] | 15.09 |  |  |  |  | 0.00
2021 |  |  |  | 21.89 |  |  | 6747 |  |  |  | 11 | [10 empty] | 80.29 |  |  |  | 80.29 | [5 empty] | 22.72 |  |  | 77.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.71 |  |  |  |  | 0.00
2022 |  |  |  | 23.07 |  |  | 6294 |  |  |  | 11 | [10 empty] | 71.85 |  |  |  | 71.85 | [5 empty] | 23.94 |  |  | 71.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.15 |  |  |  |  | 0.00
2023 |  |  |  | 37.87 |  |  | 8134 |  |  |  | 11 | [10 empty] | 93.28 |  |  |  | 93.28 | [5 empty] | 39.30 |  |  | 92.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.72 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1976 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 43
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 616 | [14 empty] | 1328
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 237
E. |  | Testing of plant systems or components | [20 empty] | 9 | [14 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 32
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 96
Z. |  | Other | [35 empty] | 11 |  |  |  | 1
Subtotal | [22 empty] | 625 | [14 empty] | 1582 |  |  |  | 44 | [11 empty] | 128
Total | [22 empty] | 625 | [14 empty] | 1754
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1976 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
31. |  |  | Turbine and auxiliaries | [34 empty] | 10
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 0
34. |  |  | Miscellaneous Systems | [34 empty] | 13
Total | [37 empty] | 43
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. The unit was in the intermediate maintenance outage from 2023.06.11 to 2023.07.07. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## BILIBINO-4
2023 Operating Experience
RU-144 | [8 empty] | BILIBINO-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | ŠKODA (ŠKODA CONCERN NUCLEAR POWER PLANT WORKS)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / EGP-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-01-01
Thermal power | [12 empty] | : |  |  | 62 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1976-12-27
Gross electrical power | [12 empty] | : |  |  | 12 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1977-01-01
Reference unit power (net) | [12 empty] | : |  |  | 11 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 47 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 6
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 280
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 3000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.1 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 273 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 27 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 34.45 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 83.59 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 83.59 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.41 %
Load Factor (LF) | [18 empty] | : | 35.75 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 82.8 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1507 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 21.56 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1.52 | 2.01 |  |  |  | 2.99 |  | 0.24 | [8 empty] | 0.00 |  |  | 2.71 | [6 empty] | 3.63 |  | 3.36 |  |  |  | 4.72 |  |  | 6.30 |  |  | 3.98 | [9 empty] | 3.01 |  |  | 34.45
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 30.18 | [8 empty] | 4.55 |  |  | 69.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.77 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.59
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 30.18 | [8 empty] | 4.55 |  |  | 69.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.77 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.59
LF [%] |  |  |  |  | 18.52 | 27.18 |  |  |  | 36.52 |  | 2.99 | [8 empty] | 0.00 |  |  | 34.15 | [6 empty] | 44.32 |  | 41.01 |  |  |  | 59.57 |  |  | 76.99 |  |  | 50.28 | [9 empty] | 36.80 |  |  | 35.75
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 26.81 | [8 empty] | 0.00 |  |  | 67.50 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.73 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.80
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 69.82 | [8 empty] | 95.45 |  |  | 31.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.23 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.41
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 2216.12 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.61 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.27 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.23 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 51.19 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 7.98 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 78.21 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1977 |  |  |  | 52.65 |  |  | 7392 |  |  |  | 10 | [10 empty] | 82.89 |  |  |  | 93.56 | [5 empty] | 60.10 |  |  | 84.38 |  |  |  | 0.28 |  | 0.27 | [8 empty] | 6.17 |  |  |  |  | 10.67
1978 |  |  |  | 58.30 |  |  | 7827 |  |  |  | 10 | [10 empty] | 91.06 |  |  |  | 91.06 | [5 empty] | 66.55 |  |  | 89.35 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.93 |  |  |  |  | 0.00
1979 |  |  |  | 74.46 |  |  | 7552 |  |  |  | 10 | [10 empty] | 83.88 |  |  |  | 85.52 | [5 empty] | 85.00 |  |  | 86.21 |  |  |  | 0.20 |  | 0.17 | [8 empty] | 14.31 |  |  |  |  | 1.64
1980 |  |  |  | 77.62 |  |  | 8347 |  |  |  | 10 | [10 empty] | 92.91 |  |  |  | 94.77 | [5 empty] | 88.37 |  |  | 95.03 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 5.18 |  |  |  |  | 1.86
1981 |  |  |  | 78.26 |  |  | 7734 |  |  |  | 10 | [10 empty] | 86.61 |  |  |  | 87.69 | [5 empty] | 89.33 |  |  | 88.29 |  |  |  | 0.80 |  | 0.71 | [8 empty] | 11.60 |  |  |  |  | 1.08
1982 |  |  |  | 77.61 |  |  | 7976 |  |  |  | 10 | [10 empty] | 90.71 |  |  |  | 90.71 | [5 empty] | 88.59 |  |  | 91.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.29 |  |  |  |  | 0.00
1983 |  |  |  | 75.53 |  |  | 7923 |  |  |  | 10 | [10 empty] | 86.88 |  |  |  | 89.97 | [5 empty] | 86.23 |  |  | 90.45 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 9.94 |  |  |  |  | 3.09
1984 |  |  |  | 79.01 |  |  | 7744 |  |  |  | 10 | [10 empty] | 86.77 |  |  |  | 87.57 | [5 empty] | 89.95 |  |  | 88.16 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 12.36 |  |  |  |  | 0.80
1985 |  |  |  | 81.23 |  |  | 7919 |  |  |  | 10 | [10 empty] | 89.53 |  |  |  | 90.33 | [5 empty] | 92.73 |  |  | 90.40 |  |  |  | 1.23 |  | 1.13 | [8 empty] | 8.55 |  |  |  |  | 0.79
1986 |  |  |  | 74.54 |  |  | 7083 |  |  |  | 10 | [10 empty] | 79.84 |  |  |  | 79.90 | [5 empty] | 85.09 |  |  | 80.86 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 20.09 |  |  |  |  | 0.06
1987 |  |  |  | 95.55 |  |  | 8154 |  |  |  | 12 | [10 empty] | 93.26 |  |  |  | 93.26 | [5 empty] | 90.89 |  |  | 93.08 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 6.54 |  |  |  |  | 0.00
1988 |  |  |  | 75.85 |  |  | 7617 |  |  |  | 11 | [10 empty] | 87.34 |  |  |  | 87.34 | [5 empty] | 78.50 |  |  | 86.71 |  |  |  | 0.86 |  | 0.76 | [8 empty] | 11.90 |  |  |  |  | 0.00
1989 |  |  |  | 71.37 |  |  | 7853 |  |  |  | 11 | [10 empty] | 93.22 |  |  |  | 93.22 | [5 empty] | 74.06 |  |  | 89.65 |  |  |  | 0.25 |  | 0.24 | [8 empty] | 6.54 |  |  |  |  | 0.00
1990 |  |  |  | 75.29 |  |  | 7588 |  |  |  | 11 | [10 empty] | 86.36 |  |  |  | 87.22 | [5 empty] | 78.13 |  |  | 86.62 |  |  |  | 5.48 |  | 5.06 | [8 empty] | 7.73 |  |  |  |  | 0.86
1991 |  |  |  | 61.32 |  |  | 6139 |  |  |  | 11 | [10 empty] | 69.89 |  |  |  | 71.43 | [5 empty] | 63.64 |  |  | 70.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 28.57 |  |  |  |  | 1.54
1992 |  |  |  | 69.84 |  |  | 7756 |  |  |  | 11 | [10 empty] | 87.82 |  |  |  | 87.82 | [5 empty] | 72.28 |  |  | 88.30 |  |  |  | 1.22 |  | 1.08 | [8 empty] | 11.10 |  |  |  |  | 0.00
1993 |  |  |  | 56.00 |  |  | 6918 |  |  |  | 11 | [10 empty] | 64.39 |  |  |  | 80.22 | [5 empty] | 58.12 |  |  | 78.97 |  |  |  | 0.82 |  | 0.66 | [8 empty] | 19.11 |  |  |  |  | 15.83
1994 |  |  |  | 38.46 |  |  | 5266 |  |  |  | 11 | [10 empty] | 61.82 |  |  |  | 61.99 | [5 empty] | 39.91 |  |  | 60.11 |  |  |  | 9.18 |  | 6.27 | [8 empty] | 31.75 |  |  |  |  | 0.17
1995 |  |  |  | 29.88 |  |  | 5083 |  |  |  | 11 | [10 empty] | 62.73 |  |  |  | 63.94 | [5 empty] | 31.01 |  |  | 58.03 |  |  |  | 0.53 |  | 0.34 | [8 empty] | 35.72 |  |  |  |  | 1.21
1996 |  |  |  | 35.18 |  |  | 5109 |  |  |  | 11 | [10 empty] | 59.13 |  |  |  | 59.13 | [5 empty] | 36.41 |  |  | 58.16 |  |  |  | 1.36 |  | 0.81 | [8 empty] | 40.06 |  |  |  |  | 0.00
1997 |  |  |  | 15.13 |  |  | 2490 |  |  |  | 11 | [10 empty] | 28.42 |  |  |  | 37.04 | [5 empty] | 15.70 |  |  | 28.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 62.96 |  |  |  |  | 8.61
1998 |  |  |  | 37.29 |  |  | 5510 |  |  |  | 11 | [10 empty] | 44.52 |  |  |  | 63.14 | [5 empty] | 38.70 |  |  | 62.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.86 |  |  |  |  | 18.62
1999 |  |  |  | 28.69 |  |  | 3993 |  |  |  | 11 | [10 empty] | 34.77 |  |  |  | 46.74 | [5 empty] | 29.77 |  |  | 45.58 |  |  |  | 6.39 |  | 3.19 | [8 empty] | 50.07 |  |  |  |  | 11.97
2000 |  |  |  | 55.85 |  |  | 7740 |  |  |  | 11 | [10 empty] | 64.20 |  |  |  | 88.68 | [5 empty] | 57.80 |  |  | 88.11 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 11.29 |  |  |  |  | 24.48
2001 |  |  |  | 35.44 |  |  | 5931 |  |  |  | 11 | [10 empty] | 43.17 |  |  |  | 68.01 | [5 empty] | 36.78 |  |  | 67.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.99 |  |  |  |  | 24.84
2002 |  |  |  | 33.12 |  |  | 6419 |  |  |  | 11 | [10 empty] | 46.34 |  |  |  | 73.76 | [5 empty] | 34.37 |  |  | 73.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 26.24 |  |  |  |  | 27.42
2003 |  |  |  | 24.52 |  |  | 5849 |  |  |  | 11 | [10 empty] | 34.04 |  |  |  | 67.51 | [5 empty] | 25.45 |  |  | 66.77 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 32.49 |  |  |  |  | 33.47
2004 |  |  |  | 26.10 |  |  | 7303 |  |  |  | 11 | [10 empty] | 36.71 |  |  |  | 83.90 | [5 empty] | 27.01 |  |  | 83.14 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.10 |  |  |  |  | 47.19
2005 |  |  |  | 24.95 |  |  | 7300 |  |  |  | 11 | [10 empty] | 36.29 |  |  |  | 84.32 | [5 empty] | 25.89 |  |  | 83.33 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.68 |  |  |  |  | 48.03
2006 |  |  |  | 25.22 |  |  | 6626 |  |  |  | 11 | [10 empty] | 36.44 |  |  |  | 76.86 | [5 empty] | 26.18 |  |  | 75.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.14 |  |  |  |  | 40.42
2007 |  |  |  | 19.57 |  |  | 5983 |  |  |  | 11 | [10 empty] | 30.89 |  |  |  | 76.55 | [5 empty] | 20.31 |  |  | 68.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.45 |  |  |  |  | 45.65
2008 |  |  |  | 29.55 |  |  | 7023 |  |  |  | 11 | [10 empty] | 87.66 |  |  |  | 87.66 | [5 empty] | 30.59 |  |  | 79.95 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 12.25 |  |  |  |  | 0.00
2009 |  |  |  | 42.14 |  |  | 7663 |  |  |  | 11 | [10 empty] | 88.40 |  |  |  | 88.40 | [5 empty] | 43.74 |  |  | 87.48 |  |  |  | 0.14 |  | 0.12 | [8 empty] | 11.48 |  |  |  |  | 0.00
2010 |  |  |  | 37.48 |  |  | 7272 |  |  |  | 11 | [10 empty] | 86.93 |  |  |  | 86.93 | [5 empty] | 38.90 |  |  | 83.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.07 |  |  |  |  | 0.00
2011 |  |  |  | 32.79 |  |  | 5944 |  |  |  | 11 | [10 empty] | 77.29 |  |  |  | 77.29 | [5 empty] | 34.03 |  |  | 67.85 |  |  |  | 0.21 |  | 0.16 | [8 empty] | 22.55 |  |  |  |  | 0.00
2012 |  |  |  | 24.50 |  |  | 5886 |  |  |  | 11 | [10 empty] | 86.69 |  |  |  | 86.69 | [5 empty] | 25.36 |  |  | 67.01 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 13.28 |  |  |  |  | 0.00
2013 |  |  |  | 45.48 |  |  | 7472 |  |  |  | 11 | [10 empty] | 87.40 |  |  |  | 87.40 | [5 empty] | 47.19 |  |  | 85.30 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.60 |  |  |  |  | 0.00
2014 |  |  |  | 45.89 |  |  | 7187 |  |  |  | 11 | [10 empty] | 84.56 |  |  |  | 84.56 | [5 empty] | 47.63 |  |  | 82.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.44 |  |  |  |  | 0.00
2015 |  |  |  | 40.59 |  |  | 6307 |  |  |  | 11 | [10 empty] | 76.02 |  |  |  | 76.02 | [5 empty] | 42.12 |  |  | 72.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.98 |  |  |  |  | 0.00
2016 |  |  |  | 43.53 |  |  | 7163 |  |  |  | 11 | [10 empty] | 83.57 |  |  |  | 83.57 | [5 empty] | 45.05 |  |  | 81.55 |  |  |  | 1.87 |  | 1.59 | [8 empty] | 14.84 |  |  |  |  | 0.00
2017 |  |  |  | 46.22 |  |  | 7395 |  |  |  | 11 | [10 empty] | 85.13 |  |  |  | 85.13 | [5 empty] | 47.97 |  |  | 84.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.87 |  |  |  |  | 0.00
2018 |  |  |  | 54.77 |  |  | 7392 |  |  |  | 11 | [10 empty] | 85.09 |  |  |  | 85.09 | [5 empty] | 56.84 |  |  | 84.38 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.91 |  |  |  |  | 0.00
2019 |  |  |  | 50.73 |  |  | 6705 |  |  |  | 11 | [10 empty] | 77.60 |  |  |  | 77.60 | [5 empty] | 52.65 |  |  | 76.54 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 22.40 |  |  |  |  | 0.00
2020 |  |  |  | 38.06 |  |  | 7194 |  |  |  | 11 | [10 empty] | 82.72 |  |  |  | 82.72 | [5 empty] | 39.39 |  |  | 81.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.28 |  |  |  |  | 0.00
2021 |  |  |  | 22.23 |  |  | 6890 |  |  |  | 11 | [10 empty] | 80.19 |  |  |  | 80.19 | [5 empty] | 23.07 |  |  | 78.65 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.81 |  |  |  |  | 0.00
2022 |  |  |  | 27.07 |  |  | 7324 |  |  |  | 11 | [10 empty] | 83.61 |  |  |  | 83.61 | [5 empty] | 28.09 |  |  | 83.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.39 |  |  |  |  | 0.00
2023 |  |  |  | 34.45 |  |  | 7253 |  |  |  | 11 | [10 empty] | 83.59 |  |  |  | 83.59 | [5 empty] | 35.75 |  |  | 82.80 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.41 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1977 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 47
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1505 | [14 empty] | 1426
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 329
E. |  | Testing of plant systems or components | [20 empty] | 2 | [14 empty] | 7
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 41
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 100
L. |  | Human factor related | [39 empty] | 0
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 1507 | [14 empty] | 1762 |  |  |  | 48 | [11 empty] | 141
Total | [22 empty] | 1507 | [14 empty] | 1951
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1977 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 10
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 11
33. |  |  | Circulating Water System | [34 empty] | 4
41. |  |  | Main Generator Systems | [34 empty] | 12
Total | [37 empty] | 48
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. The unit was in the intermediate maintenance outage from 2023.04.08 to 2023.06.10. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-1
2023 Operating Experience
RU-30 | [8 empty] | KALININ-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-338 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-02-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-05-09
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-06-12
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7295.91 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 7.06 %
Energy Availability Factor (EAF) | [18 empty] | : | 82.46 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 6.26 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.46 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 11.28 %
Load Factor (LF) | [18 empty] | : | 87.67 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 83.32 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1461 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 34.11 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 310.26 | 114.61 |  |  |  | 747.60 |  | 694.92 | [8 empty] | 571.16 |  |  | 400.45 | [6 empty] | 732.65 |  | 746.61 |  |  |  | 718.47 |  |  | 755.37 |  |  | 739.11 | [9 empty] | 764.70 |  |  | 7295.91
EAF [%] |  |  |  |  | 41.52 | 17.72 |  |  |  | 98.12 |  | 95.41 | [8 empty] | 76.00 |  |  | 56.89 | [6 empty] | 98.28 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.46
UCF [%] |  |  |  |  | 41.52 | 17.72 |  |  |  | 98.12 |  | 95.41 | [8 empty] | 76.00 |  |  | 56.89 | [6 empty] | 98.28 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 82.46
LF [%] |  |  |  |  | 43.90 | 17.95 |  |  |  | 105.77 |  | 101.60 | [8 empty] | 80.81 |  |  | 58.55 | [6 empty] | 103.66 |  | 105.63 |  |  |  | 105.04 |  |  | 106.87 |  |  | 108.06 | [9 empty] | 108.19 |  |  | 87.67
OF [%] |  |  |  |  | 42.07 | 18.30 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 77.96 |  |  | 57.50 | [6 empty] | 98.52 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.32
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.88 |  | 4.59 | [8 empty] | 24.00 |  |  | 43.11 | [6 empty] | 1.72 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.06
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.88 |  | 4.59 | [8 empty] | 24.00 |  |  | 43.11 | [6 empty] | 1.72 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.26
PUF [%] |  |  |  |  | 58.48 | 82.28 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 11.28
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 252023.13 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.37 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.37 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.5 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 76 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 18.5 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.55 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.63 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.94 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4487.64 |  |  | 5824 |  |  |  | 950 | [10 empty] | 58.28 |  |  |  | 58.28 | [5 empty] | 57.38 |  |  | 60.38 |  |  |  | 10.99 |  | 7.20 | [8 empty] | 34.52 |  |  |  |  | 0.00
1986 |  |  |  | 5297.73 |  |  | 5946 |  |  |  | 950 | [10 empty] | 62.85 |  |  |  | 62.85 | [5 empty] | 63.66 |  |  | 67.88 |  |  |  | 28.18 |  | 24.65 | [8 empty] | 12.50 |  |  |  |  | 0.00
1987 |  |  |  | 6842.49 |  |  | 6972 |  |  |  | 1000 | [10 empty] | 78.71 |  |  |  | 78.71 | [5 empty] | 78.11 |  |  | 79.59 |  |  |  | 7.76 |  | 6.62 | [8 empty] | 14.67 |  |  |  |  | 0.00
1988 |  |  |  | 5891.61 |  |  | 6187 |  |  |  | 950 | [10 empty] | 70.12 |  |  |  | 70.12 | [5 empty] | 70.60 |  |  | 70.43 |  |  |  | 9.61 |  | 7.45 | [8 empty] | 22.43 |  |  |  |  | 0.00
1989 |  |  |  | 6129.71 |  |  | 6396 |  |  |  | 950 | [10 empty] | 71.91 |  |  |  | 71.94 | [5 empty] | 73.66 |  |  | 73.01 |  |  |  | 10.20 |  | 8.17 | [8 empty] | 19.89 |  |  |  |  | 0.03
1990 |  |  |  | 5192.31 |  |  | 5435 |  |  |  | 950 | [10 empty] | 61.53 |  |  |  | 61.56 | [5 empty] | 62.39 |  |  | 62.04 |  |  |  | 3.54 |  | 2.26 | [8 empty] | 36.18 |  |  |  |  | 0.03
1991 |  |  |  | 6482.72 |  |  | 7161 |  |  |  | 950 | [10 empty] | 77.09 |  |  |  | 78.06 | [5 empty] | 77.90 |  |  | 81.75 |  |  |  | 11.66 |  | 10.30 | [8 empty] | 11.64 |  |  |  |  | 0.97
1992 |  |  |  | 6781.35 |  |  | 7388 |  |  |  | 950 | [10 empty] | 80.33 |  |  |  | 80.36 | [5 empty] | 81.27 |  |  | 84.12 |  |  |  | 12.02 |  | 10.98 | [8 empty] | 8.66 |  |  |  |  | 0.03
1993 |  |  |  | 4927.21 |  |  | 6133 |  |  |  | 950 | [10 empty] | 59.38 |  |  |  | 66.61 | [5 empty] | 59.21 |  |  | 70.01 |  |  |  | 5.55 |  | 3.91 | [8 empty] | 29.48 |  |  |  |  | 7.23
1994 |  |  |  | 4437.58 |  |  | 5440 |  |  |  | 950 | [10 empty] | 54.09 |  |  |  | 54.37 | [5 empty] | 53.32 |  |  | 62.10 |  |  |  | 16.02 |  | 10.37 | [8 empty] | 35.26 |  |  |  |  | 0.29
1995 |  |  |  | 4699.05 |  |  | 6265 |  |  |  | 950 | [10 empty] | 56.75 |  |  |  | 57.00 | [5 empty] | 56.47 |  |  | 71.52 |  |  |  | 26.12 |  | 20.15 | [8 empty] | 22.85 |  |  |  |  | 0.25
1996 |  |  |  | 4431.67 |  |  | 5628 |  |  |  | 950 | [10 empty] | 53.22 |  |  |  | 53.31 | [5 empty] | 53.11 |  |  | 64.07 |  |  |  | 19.08 |  | 12.57 | [8 empty] | 34.11 |  |  |  |  | 0.09
1997 |  |  |  | 5197.08 |  |  | 6195 |  |  |  | 950 | [10 empty] | 63.23 |  |  |  | 65.00 | [5 empty] | 62.45 |  |  | 70.72 |  |  |  | 5.59 |  | 3.85 | [8 empty] | 31.16 |  |  |  |  | 1.77
1998 |  |  |  | 6100.97 |  |  | 6937 |  |  |  | 950 | [10 empty] | 73.04 |  |  |  | 73.33 | [5 empty] | 73.31 |  |  | 79.19 |  |  |  | 6.48 |  | 5.08 | [8 empty] | 21.59 |  |  |  |  | 0.29
1999 |  |  |  | 5775.11 |  |  | 6589 |  |  |  | 950 | [10 empty] | 69.32 |  |  |  | 73.06 | [5 empty] | 69.40 |  |  | 75.22 |  |  |  | 5.65 |  | 4.37 | [8 empty] | 22.56 |  |  |  |  | 3.74
2000 |  |  |  | 6289.72 |  |  | 6784 |  |  |  | 950 | [10 empty] | 75.00 |  |  |  | 76.79 | [5 empty] | 75.37 |  |  | 77.23 |  |  |  | 3.54 |  | 2.82 | [8 empty] | 20.39 |  |  |  |  | 1.79
2001 |  |  |  | 6627.54 |  |  | 7020 |  |  |  | 950 | [10 empty] | 78.18 |  |  |  | 79.37 | [5 empty] | 79.64 |  |  | 80.14 |  |  |  | 5.67 |  | 4.77 | [8 empty] | 15.86 |  |  |  |  | 1.19
2002 |  |  |  | 7248.38 |  |  | 7568 |  |  |  | 950 | [10 empty] | 84.66 |  |  |  | 86.10 | [5 empty] | 87.10 |  |  | 86.39 |  |  |  | 0.27 |  | 0.23 | [8 empty] | 13.66 |  |  |  |  | 1.44
2003 |  |  |  | 7155.92 |  |  | 7408 |  |  |  | 950 | [10 empty] | 83.10 |  |  |  | 83.75 | [5 empty] | 85.99 |  |  | 84.57 |  |  |  | 4.40 |  | 3.85 | [8 empty] | 12.40 |  |  |  |  | 0.65
2004 |  |  |  | 6936.97 |  |  | 7179 |  |  |  | 950 | [10 empty] | 80.69 |  |  |  | 81.55 | [5 empty] | 83.13 |  |  | 81.73 |  |  |  | 2.57 |  | 2.15 | [8 empty] | 16.30 |  |  |  |  | 0.86
2005 |  |  |  | 6836.33 |  |  | 7219 |  |  |  | 950 | [10 empty] | 80.39 |  |  |  | 81.50 | [5 empty] | 82.14 |  |  | 82.40 |  |  |  | 4.45 |  | 4.78 | [8 empty] | 13.72 |  |  |  |  | 1.11
2006 |  |  |  | 6743.58 |  |  | 7112 |  |  |  | 950 | [10 empty] | 79.48 |  |  |  | 80.58 | [5 empty] | 81.03 |  |  | 81.19 |  |  |  | 4.77 |  | 5.16 | [8 empty] | 14.26 |  |  |  |  | 1.10
2007 |  |  |  | 7150.35 |  |  | 7491 |  |  |  | 950 | [10 empty] | 84.04 |  |  |  | 85.24 | [5 empty] | 85.92 |  |  | 85.51 |  |  |  | 2.14 |  | 1.87 | [8 empty] | 12.90 |  |  |  |  | 1.20
2008 |  |  |  | 6953.55 |  |  | 7209 |  |  |  | 950 | [10 empty] | 81.53 |  |  |  | 81.53 | [5 empty] | 83.33 |  |  | 82.07 |  |  |  | 2.44 |  | 2.04 | [8 empty] | 16.43 |  |  |  |  | 0.00
2009 |  |  |  | 7234.70 |  |  | 7669 |  |  |  | 950 | [10 empty] | 87.27 |  |  |  | 87.27 | [5 empty] | 86.93 |  |  | 87.55 |  |  |  | 0.70 |  | 0.62 | [8 empty] | 12.11 |  |  |  |  | 0.00
2010 |  |  |  | 7006.14 |  |  | 7175 |  |  |  | 950 | [10 empty] | 82.65 |  |  |  | 82.74 | [5 empty] | 84.19 |  |  | 81.91 |  |  |  | 6.45 |  | 5.71 | [8 empty] | 11.55 |  |  |  |  | 0.09
2011 |  |  |  | 7516.88 |  |  | 7727 |  |  |  | 950 | [10 empty] | 87.91 |  |  |  | 87.91 | [5 empty] | 90.34 |  |  | 88.22 |  |  |  | 0.22 |  | 0.19 | [8 empty] | 11.89 |  |  |  |  | 0.00
2012 |  |  |  | 6648.33 |  |  | 6833 |  |  |  | 950 | [10 empty] | 77.49 |  |  |  | 77.49 | [5 empty] | 79.67 |  |  | 77.79 |  |  |  | 0.94 |  | 0.74 | [8 empty] | 21.77 |  |  |  |  | 0.00
2013 |  |  |  | 6963.99 |  |  | 6915 |  |  |  | 950 | [10 empty] | 78.67 |  |  |  | 78.67 | [5 empty] | 83.68 |  |  | 78.94 |  |  |  | 6.17 |  | 15.31 | [8 empty] | 6.03 |  |  |  |  | 0.00
2014 |  |  |  | 5892.14 |  |  | 6035 |  |  |  | 950 | [10 empty] | 67.51 |  |  |  | 67.51 | [5 empty] | 70.79 |  |  | 68.88 |  |  |  | 3.79 |  | 2.66 | [8 empty] | 29.83 |  |  |  |  | 0.00
2015 |  |  |  | 8036.64 |  |  | 7931 |  |  |  | 950 | [10 empty] | 90.46 |  |  |  | 90.46 | [5 empty] | 96.57 |  |  | 90.54 |  |  |  | 0.64 |  | 0.58 | [8 empty] | 8.96 |  |  |  |  | 0.00
2016 |  |  |  | 6966.43 |  |  | 6876 |  |  |  | 950 | [10 empty] | 78.17 |  |  |  | 78.17 | [5 empty] | 83.48 |  |  | 78.28 |  |  |  | 8.56 |  | 7.32 | [8 empty] | 14.52 |  |  |  |  | 0.00
2017 |  |  |  | 8025.20 |  |  | 7856 |  |  |  | 950 | [10 empty] | 89.63 |  |  |  | 89.63 | [5 empty] | 96.43 |  |  | 89.68 |  |  |  | 0.00 |  | 0.53 | [8 empty] | 9.84 |  |  |  |  | 0.00
2018 |  |  |  | 8802.94 |  |  | 8643 |  |  |  | 950 | [10 empty] | 98.20 |  |  |  | 98.21 | [5 empty] | 105.78 |  |  | 98.66 |  |  |  | 1.79 |  | 1.79 | [8 empty] | 0.00 |  |  |  |  | 0.01
2019 |  |  |  | 6650.32 |  |  | 6595 |  |  |  | 950 | [10 empty] | 75.05 |  |  |  | 75.10 | [5 empty] | 79.91 |  |  | 75.29 |  |  |  | 6.64 |  | 5.34 | [8 empty] | 19.56 |  |  |  |  | 0.05
2020 |  |  |  | 2709.37 |  |  | 2703 |  |  |  | 950 | [10 empty] | 30.56 |  |  |  | 30.56 | [5 empty] | 32.47 |  |  | 30.77 |  |  |  | 4.41 |  | 1.41 | [8 empty] | 68.03 |  |  |  |  | 0.00
2021 |  |  |  | 7970.06 |  |  | 7849 |  |  |  | 950 | [10 empty] | 89.44 |  |  |  | 89.49 | [5 empty] | 95.77 |  |  | 89.60 |  |  |  | 1.34 |  | 1.21 | [8 empty] | 9.30 |  |  |  |  | 0.05
2022 |  |  |  | 8863.93 |  |  | 8760 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 106.51 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2023 |  |  |  | 7295.91 |  |  | 7299 |  |  |  | 950 | [10 empty] | 82.46 |  |  |  | 82.46 | [5 empty] | 87.67 |  |  | 83.32 |  |  |  | 7.06 |  | 6.26 | [8 empty] | 11.28 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 504 | [14 empty] | 274
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 982 | [14 empty] | 1488 |  |  |  | 28
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 99 |  |  |  | 1
E. |  | Testing of plant systems or components | [39 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 6
Z. |  | Other | [39 empty] | 33
Subtotal | [22 empty] | 982 |  |  |  | 504 | [10 empty] | 1587 |  |  |  | 343 | [11 empty] | 3
Total | [22 empty] | 1486 | [14 empty] | 1933
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 33
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [19 empty] | 139 | [14 empty] | 9
16. |  |  | Steam generation systems | [34 empty] | 35
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [19 empty] | 34 | [14 empty] | 24
32. |  |  | Feedwater and Main Steam System | [34 empty] | 19
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 117
42. |  |  | Electrical Power Supply Systems | [19 empty] | 331 | [14 empty] | 15
Total | [22 empty] | 504 | [14 empty] | 281
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-December. Additional electricity generation amounted to 431205MWh. The unit was in the overhaul from 2023.01.14 to 2023.02.23. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-2
2023 Operating Experience
RU-31 | [8 empty] | KALININ-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-338 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1982-02-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1986-12-03
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1987-03-03
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 37 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8191.96 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.93 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.01 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.99 %
Load Factor (LF) | [18 empty] | : | 98.44 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.08 %
Operating Factor (OF) | [18 empty] | : | 92.09 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 693 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 43.1 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 764.15 | 682.00 |  |  |  | 766.11 |  | 733.71 | [8 empty] | 762.40 |  |  | 730.28 | [6 empty] | 754.29 |  | 750.48 |  |  |  | 686.65 |  |  | 60.16 |  |  | 735.12 | [9 empty] | 766.60 |  |  | 8191.96
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 95.78 |  |  | 9.05 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.93
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 96.74 |  |  | 9.05 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.01
LF [%] |  |  |  |  | 108.11 | 106.83 |  |  |  | 108.39 |  | 107.27 | [8 empty] | 107.87 |  |  | 106.77 | [6 empty] | 106.72 |  | 106.18 |  |  |  | 100.39 |  |  | 8.51 |  |  | 107.47 | [9 empty] | 108.46 |  |  | 98.44
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 96.81 |  |  | 9.95 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.09
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 3.26 |  |  | 90.95 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.99
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.96 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.08
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 249736.21 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.6 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.23 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.88 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.04 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.09 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.17 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.8 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.34 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1987 |  |  |  | 6494.00 |  |  | 7605 |  |  |  | 1000 | [10 empty] | 86.27 |  |  |  | 86.27 | [5 empty] | 79.18 |  |  | 87.96 |  |  |  | 9.13 |  | 8.67 | [8 empty] | 5.07 |  |  |  |  | 0.00
1988 |  |  |  | 5829.43 |  |  | 6446 |  |  |  | 950 | [10 empty] | 71.67 |  |  |  | 71.67 | [5 empty] | 69.86 |  |  | 73.38 |  |  |  | 9.64 |  | 7.64 | [8 empty] | 20.68 |  |  |  |  | 0.00
1989 |  |  |  | 6580.49 |  |  | 7034 |  |  |  | 950 | [10 empty] | 78.45 |  |  |  | 78.45 | [5 empty] | 79.07 |  |  | 80.30 |  |  |  | 5.86 |  | 4.88 | [8 empty] | 16.67 |  |  |  |  | 0.00
1990 |  |  |  | 6788.16 |  |  | 7083 |  |  |  | 950 | [10 empty] | 79.45 |  |  |  | 79.45 | [5 empty] | 81.57 |  |  | 80.86 |  |  |  | 5.85 |  | 4.94 | [8 empty] | 15.61 |  |  |  |  | 0.00
1991 |  |  |  | 4729.67 |  |  | 5154 |  |  |  | 950 | [10 empty] | 49.79 |  |  |  | 49.79 | [5 empty] | 56.83 |  |  | 58.84 |  |  |  | 30.08 |  | 21.42 | [8 empty] | 28.79 |  |  |  |  | 0.00
1992 |  |  |  | 5496.31 |  |  | 6145 |  |  |  | 950 | [10 empty] | 65.70 |  |  |  | 65.70 | [5 empty] | 65.87 |  |  | 69.96 |  |  |  | 5.58 |  | 3.88 | [8 empty] | 30.42 |  |  |  |  | 0.00
1993 |  |  |  | 5862.30 |  |  | 7078 |  |  |  | 950 | [10 empty] | 51.91 |  |  |  | 56.45 | [5 empty] | 70.44 |  |  | 80.80 |  |  |  | 28.07 |  | 22.03 | [8 empty] | 21.52 |  |  |  |  | 4.54
1994 |  |  |  | 4463.77 |  |  | 6989 |  |  |  | 950 | [10 empty] | 54.87 |  |  |  | 54.87 | [5 empty] | 53.64 |  |  | 79.78 |  |  |  | 31.92 |  | 25.73 | [8 empty] | 19.41 |  |  |  |  | 0.00
1995 |  |  |  | 5769.75 |  |  | 7283 |  |  |  | 950 | [10 empty] | 69.48 |  |  |  | 72.40 | [5 empty] | 69.33 |  |  | 83.14 |  |  |  | 15.96 |  | 13.75 | [8 empty] | 13.85 |  |  |  |  | 2.92
1996 |  |  |  | 4595.17 |  |  | 7501 |  |  |  | 950 | [10 empty] | 56.02 |  |  |  | 78.42 | [5 empty] | 55.07 |  |  | 85.39 |  |  |  | 2.81 |  | 2.26 | [8 empty] | 19.31 |  |  |  |  | 22.40
1997 |  |  |  | 3880.64 |  |  | 6117 |  |  |  | 950 | [10 empty] | 47.25 |  |  |  | 62.67 | [5 empty] | 46.63 |  |  | 69.83 |  |  |  | 2.47 |  | 1.59 | [8 empty] | 35.74 |  |  |  |  | 15.42
1998 |  |  |  | 4946.65 |  |  | 6839 |  |  |  | 950 | [10 empty] | 59.67 |  |  |  | 59.98 | [5 empty] | 59.44 |  |  | 78.07 |  |  |  | 26.91 |  | 22.08 | [8 empty] | 17.93 |  |  |  |  | 0.31
1999 |  |  |  | 6379.25 |  |  | 7155 |  |  |  | 950 | [10 empty] | 76.21 |  |  |  | 80.03 | [5 empty] | 76.66 |  |  | 81.68 |  |  |  | 0.26 |  | 0.21 | [8 empty] | 19.76 |  |  |  |  | 3.82
2000 |  |  |  | 6418.74 |  |  | 7441 |  |  |  | 950 | [10 empty] | 76.26 |  |  |  | 83.57 | [5 empty] | 76.92 |  |  | 84.71 |  |  |  | 0.55 |  | 0.46 | [8 empty] | 15.97 |  |  |  |  | 7.32
2001 |  |  |  | 6708.99 |  |  | 7070 |  |  |  | 950 | [10 empty] | 79.16 |  |  |  | 80.00 | [5 empty] | 80.62 |  |  | 80.71 |  |  |  | 2.26 |  | 1.85 | [8 empty] | 18.15 |  |  |  |  | 0.84
2002 |  |  |  | 7003.43 |  |  | 7554 |  |  |  | 950 | [10 empty] | 82.66 |  |  |  | 85.76 | [5 empty] | 84.16 |  |  | 86.23 |  |  |  | 1.00 |  | 0.86 | [8 empty] | 13.37 |  |  |  |  | 3.10
2003 |  |  |  | 7329.54 |  |  | 7541 |  |  |  | 950 | [10 empty] | 85.33 |  |  |  | 85.89 | [5 empty] | 88.07 |  |  | 86.08 |  |  |  | 0.77 |  | 0.67 | [8 empty] | 13.45 |  |  |  |  | 0.55
2004 |  |  |  | 7398.23 |  |  | 7674 |  |  |  | 950 | [10 empty] | 86.68 |  |  |  | 87.11 | [5 empty] | 88.66 |  |  | 87.36 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 12.79 |  |  |  |  | 0.44
2005 |  |  |  | 6116.27 |  |  | 6476 |  |  |  | 950 | [10 empty] | 72.11 |  |  |  | 73.62 | [5 empty] | 73.49 |  |  | 73.92 |  |  |  | 11.86 |  | 9.90 | [8 empty] | 16.48 |  |  |  |  | 1.51
2006 |  |  |  | 7074.89 |  |  | 7400 |  |  |  | 950 | [10 empty] | 82.73 |  |  |  | 84.26 | [5 empty] | 85.01 |  |  | 84.47 |  |  |  | 3.63 |  | 3.18 | [8 empty] | 12.56 |  |  |  |  | 1.53
2007 |  |  |  | 7231.43 |  |  | 7539 |  |  |  | 950 | [10 empty] | 84.16 |  |  |  | 85.49 | [5 empty] | 86.90 |  |  | 86.06 |  |  |  | 1.16 |  | 1.00 | [8 empty] | 13.51 |  |  |  |  | 1.33
2008 |  |  |  | 7474.79 |  |  | 7756 |  |  |  | 950 | [10 empty] | 88.19 |  |  |  | 88.19 | [5 empty] | 89.57 |  |  | 88.30 |  |  |  | 0.25 |  | 0.22 | [8 empty] | 11.59 |  |  |  |  | 0.00
2009 |  |  |  | 7004.16 |  |  | 7248 |  |  |  | 950 | [10 empty] | 82.51 |  |  |  | 82.51 | [5 empty] | 84.16 |  |  | 82.74 |  |  |  | 1.50 |  | 1.26 | [8 empty] | 16.23 |  |  |  |  | 0.00
2010 |  |  |  | 7423.50 |  |  | 7595 |  |  |  | 950 | [10 empty] | 87.77 |  |  |  | 87.77 | [5 empty] | 89.20 |  |  | 86.70 |  |  |  | 1.51 |  | 1.34 | [8 empty] | 10.89 |  |  |  |  | 0.00
2011 |  |  |  | 7570.61 |  |  | 7675 |  |  |  | 950 | [10 empty] | 86.98 |  |  |  | 86.98 | [5 empty] | 90.98 |  |  | 87.62 |  |  |  | 0.63 |  | 0.55 | [8 empty] | 12.47 |  |  |  |  | 0.00
2012 |  |  |  | 7164.85 |  |  | 7464 |  |  |  | 950 | [10 empty] | 84.47 |  |  |  | 84.47 | [5 empty] | 85.86 |  |  | 84.97 |  |  |  | 0.93 |  | 0.79 | [8 empty] | 14.74 |  |  |  |  | 0.00
2013 |  |  |  | 8635.13 |  |  | 8552 |  |  |  | 950 | [10 empty] | 97.57 |  |  |  | 97.57 | [5 empty] | 103.76 |  |  | 97.63 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.43 |  |  |  |  | 0.00
2014 |  |  |  | 7030.39 |  |  | 6984 |  |  |  | 950 | [10 empty] | 79.59 |  |  |  | 79.59 | [5 empty] | 84.47 |  |  | 79.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.41 |  |  |  |  | 0.00
2015 |  |  |  | 7883.15 |  |  | 7805 |  |  |  | 950 | [10 empty] | 88.94 |  |  |  | 88.94 | [5 empty] | 94.73 |  |  | 89.10 |  |  |  | 2.10 |  | 1.90 | [8 empty] | 9.16 |  |  |  |  | 0.00
2016 |  |  |  | 6776.88 |  |  | 6664 |  |  |  | 950 | [10 empty] | 75.75 |  |  |  | 75.75 | [5 empty] | 81.21 |  |  | 75.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 24.25 |  |  |  |  | 0.00
2017 |  |  |  | 7562.08 |  |  | 7439 |  |  |  | 950 | [10 empty] | 84.68 |  |  |  | 84.71 | [5 empty] | 90.87 |  |  | 84.92 |  |  |  | 1.93 |  | 6.54 | [8 empty] | 8.75 |  |  |  |  | 0.03
2018 |  |  |  | 8390.72 |  |  | 8224 |  |  |  | 950 | [10 empty] | 93.84 |  |  |  | 93.86 | [5 empty] | 100.83 |  |  | 93.88 |  |  |  | 6.14 |  | 6.14 | [8 empty] | 0.00 |  |  |  |  | 0.01
2019 |  |  |  | 7769.30 |  |  | 7721 |  |  |  | 950 | [10 empty] | 87.05 |  |  |  | 87.05 | [5 empty] | 93.36 |  |  | 88.14 |  |  |  | 1.94 |  | 1.73 | [8 empty] | 11.23 |  |  |  |  | 0.00
2020 |  |  |  | 7987.59 |  |  | 8031 |  |  |  | 950 | [10 empty] | 90.80 |  |  |  | 90.80 | [5 empty] | 95.72 |  |  | 91.43 |  |  |  | 0.52 |  | 0.48 | [8 empty] | 8.73 |  |  |  |  | 0.00
2021 |  |  |  | 8688.57 |  |  | 8645 |  |  |  | 950 | [10 empty] | 97.24 |  |  |  | 97.24 | [5 empty] | 104.40 |  |  | 98.69 |  |  |  | 2.76 |  | 2.76 | [8 empty] | 0.00 |  |  |  |  | 0.00
2022 |  |  |  | 7334.10 |  |  | 7262 |  |  |  | 950 | [10 empty] | 82.50 |  |  |  | 82.78 | [5 empty] | 88.13 |  |  | 82.90 |  |  |  | 0.21 |  | 0.18 | [8 empty] | 17.04 |  |  |  |  | 0.28
2023 |  |  |  | 8191.96 |  |  | 8067 |  |  |  | 950 | [10 empty] | 91.93 |  |  |  | 92.01 | [5 empty] | 98.44 |  |  | 92.09 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.99 |  |  |  |  | 0.08
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1987 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 170
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 695 | [14 empty] | 1193 |  |  |  | 6
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 63
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
L. |  | Human factor related | [39 empty] | 15
Z. |  | Other | [39 empty] | 3
Subtotal | [22 empty] | 695 | [14 empty] | 1256 |  |  |  | 194 | [11 empty] | 3
Total | [22 empty] | 695 | [14 empty] | 1453
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1987 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [34 empty] | 31
16. |  |  | Steam generation systems | [34 empty] | 4
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 28
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 7
35. |  |  | All other I&C Systems | [34 empty] | 6
41. |  |  | Main Generator Systems | [34 empty] | 67
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [37 empty] | 178
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-December. Additional electricity generation amounted to 511203 MWh. The unit was in the intermediate maintenance outage from 2023.09.30 to 2023.10.28. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-3
2023 Operating Experience
RU-36 | [8 empty] | KALININ-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | FAEA (Federal Atomic Energy Agency)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1985-10-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2004-12-16
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2005-11-08
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 19 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8833.38 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 99.97 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.03 %
Unit Capability Factor (UCF) | [18 empty] | : | 99.97 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 106.14 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 30.74 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 753.00 | 685.23 |  |  |  | 757.39 |  | 726.87 | [8 empty] | 753.93 |  |  | 725.13 | [6 empty] | 744.59 |  | 738.51 |  |  |  | 718.55 |  |  | 746.65 |  |  | 726.22 | [9 empty] | 757.30 |  |  | 8833.38
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.70 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.97
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.70 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 99.97
LF [%] |  |  |  |  | 106.54 | 107.34 |  |  |  | 107.16 |  | 106.27 | [8 empty] | 106.67 |  |  | 106.01 | [6 empty] | 105.35 |  | 104.49 |  |  |  | 105.05 |  |  | 105.64 |  |  | 106.17 | [9 empty] | 107.15 |  |  | 106.14
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.30 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.30 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 134503.78 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.57 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.85 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.29 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.93 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.78 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 86.97 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.08 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.34 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2005 |  |  |  | 4345.70 |  |  | 5686 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.84 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2006 |  |  |  | 6287.23 |  |  | 6692 |  |  |  | 950 | [10 empty] | 74.90 |  |  |  | 75.20 | [5 empty] | 75.55 |  |  | 76.39 |  |  |  | 5.71 |  | 6.62 | [8 empty] | 18.18 |  |  |  |  | 0.29
2007 |  |  |  | 7185.22 |  |  | 7505 |  |  |  | 950 | [10 empty] | 84.96 |  |  |  | 85.51 | [5 empty] | 86.34 |  |  | 85.67 |  |  |  | 0.91 |  | 0.81 | [8 empty] | 13.68 |  |  |  |  | 0.55
2008 |  |  |  | 7561.73 |  |  | 7737 |  |  |  | 950 | [10 empty] | 87.74 |  |  |  | 87.78 | [5 empty] | 90.62 |  |  | 88.08 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 12.06 |  |  |  |  | 0.03
2009 |  |  |  | 6806.52 |  |  | 7553 |  |  |  | 950 | [10 empty] | 85.96 |  |  |  | 85.96 | [5 empty] | 81.79 |  |  | 86.22 |  |  |  | 3.61 |  | 3.22 | [8 empty] | 10.82 |  |  |  |  | 0.00
2010 |  |  |  | 6902.21 |  |  | 7248 |  |  |  | 950 | [10 empty] | 82.13 |  |  |  | 82.44 | [5 empty] | 82.94 |  |  | 82.74 |  |  |  | 1.25 |  | 1.04 | [8 empty] | 16.52 |  |  |  |  | 0.31
2011 |  |  |  | 7088.32 |  |  | 7427 |  |  |  | 950 | [10 empty] | 84.82 |  |  |  | 84.85 | [5 empty] | 85.19 |  |  | 84.79 |  |  |  | 0.59 |  | 2.84 | [8 empty] | 12.31 |  |  |  |  | 0.04
2012 |  |  |  | 7765.07 |  |  | 8091 |  |  |  | 950 | [10 empty] | 91.78 |  |  |  | 91.78 | [5 empty] | 93.05 |  |  | 92.11 |  |  |  | 6.68 |  | 6.57 | [8 empty] | 1.65 |  |  |  |  | 0.01
2013 |  |  |  | 6505.71 |  |  | 6698 |  |  |  | 950 | [10 empty] | 76.18 |  |  |  | 76.18 | [5 empty] | 78.17 |  |  | 76.46 |  |  |  | 1.31 |  | 10.15 | [8 empty] | 13.67 |  |  |  |  | 0.00
2014 |  |  |  | 6599.48 |  |  | 6918 |  |  |  | 950 | [10 empty] | 78.27 |  |  |  | 78.27 | [5 empty] | 79.29 |  |  | 78.96 |  |  |  | 5.79 |  | 5.33 | [8 empty] | 16.40 |  |  |  |  | 0.00
2015 |  |  |  | 7665.20 |  |  | 8196 |  |  |  | 950 | [10 empty] | 92.28 |  |  |  | 92.28 | [5 empty] | 92.11 |  |  | 93.56 |  |  |  | 7.67 |  | 7.67 | [8 empty] | 0.05 |  |  |  |  | 0.00
2016 |  |  |  | 5233.15 |  |  | 5612 |  |  |  | 950 | [10 empty] | 62.43 |  |  |  | 62.43 | [5 empty] | 62.71 |  |  | 63.89 |  |  |  | 10.35 |  | 13.02 | [8 empty] | 24.55 |  |  |  |  | 0.00
2017 |  |  |  | 7892.37 |  |  | 7990 |  |  |  | 950 | [10 empty] | 91.11 |  |  |  | 91.11 | [5 empty] | 94.84 |  |  | 91.21 |  |  |  | 8.89 |  | 8.89 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 7504.45 |  |  | 7558 |  |  |  | 950 | [10 empty] | 85.85 |  |  |  | 85.95 | [5 empty] | 90.18 |  |  | 86.28 |  |  |  | 2.29 |  | 2.01 | [8 empty] | 12.04 |  |  |  |  | 0.10
2019 |  |  |  | 7322.22 |  |  | 7362 |  |  |  | 950 | [10 empty] | 83.69 |  |  |  | 83.76 | [5 empty] | 87.99 |  |  | 84.04 |  |  |  | 4.44 |  | 4.74 | [8 empty] | 11.50 |  |  |  |  | 0.07
2020 |  |  |  | 8807.69 |  |  | 8784 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 105.55 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2021 |  |  |  | 7321.23 |  |  | 7369 |  |  |  | 950 | [10 empty] | 83.73 |  |  |  | 83.78 | [5 empty] | 87.97 |  |  | 84.12 |  |  |  | 0.70 |  | 0.59 | [8 empty] | 15.64 |  |  |  |  | 0.05
2022 |  |  |  | 6877.28 |  |  | 6929 |  |  |  | 950 | [10 empty] | 78.94 |  |  |  | 79.00 | [5 empty] | 82.64 |  |  | 79.10 |  |  |  | 5.09 |  | 4.24 | [8 empty] | 16.76 |  |  |  |  | 0.06
2023 |  |  |  | 8833.38 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 106.14 |  |  | 100.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.00 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2005 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 322
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 931 |  |  |  | 10
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 16
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 2
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
L. |  | Human factor related | [39 empty] | 2
Z. |  | Other | [39 empty] | 11
Subtotal | [37 empty] | 947 |  |  |  | 351 | [11 empty] | 2
Total | [22 empty] | 0 | [14 empty] | 1300
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2005 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 11
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 9
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 52
32. |  |  | Feedwater and Main Steam System | [34 empty] | 10
33. |  |  | Circulating Water System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 143
42. |  |  | Electrical Power Supply Systems | [34 empty] | 101
Total | [37 empty] | 336
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-December. Additional electricity generation amounted to 509006 MWh. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KALININ-4
2023 Operating Experience
RU-37 | [8 empty] | KALININ-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1986-08-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2011-11-24
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2012-12-25
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 12 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 1.05
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8076.94 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 92.27 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 92.27 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 7.71 %
Load Factor (LF) | [18 empty] | : | 97.06 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 92.47 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 660 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 15.36 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 753.73 | 680.19 |  |  |  | 754.43 |  | 721.96 | [8 empty] | 739.32 |  |  | 539.52 | [6 empty] | 220.81 |  | 726.09 |  |  |  | 708.89 |  |  | 751.14 |  |  | 726.78 | [9 empty] | 754.07 |  |  | 8076.94
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 76.34 | [6 empty] | 31.88 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.27
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 76.34 | [6 empty] | 31.88 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.27
LF [%] |  |  |  |  | 106.64 | 106.55 |  |  |  | 106.74 |  | 105.55 | [8 empty] | 104.60 |  |  | 78.88 | [6 empty] | 31.24 |  | 102.73 |  |  |  | 103.64 |  |  | 106.27 |  |  | 106.25 | [9 empty] | 106.69 |  |  | 97.06
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 76.81 | [6 empty] | 33.74 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.47
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.91 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.29 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 23.66 | [6 empty] | 67.82 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 7.71
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 89888.52 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.5 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.13 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.13 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 8.17 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 92.32 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.55 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2012 |  |  |  | 5166.49 |  |  | 6858 |  |  |  | 950 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2013 |  |  |  | 6342.91 |  |  | 6662 |  |  |  | 950 | [10 empty] | 75.72 |  |  |  | 75.73 | [5 empty] | 76.22 |  |  | 76.05 |  |  |  | 6.89 |  | 8.42 | [8 empty] | 15.85 |  |  |  |  | 0.02
2014 |  |  |  | 7249.38 |  |  | 7691 |  |  |  | 950 | [10 empty] | 87.21 |  |  |  | 87.21 | [5 empty] | 87.10 |  |  | 87.79 |  |  |  | 1.23 |  | 1.08 | [8 empty] | 11.71 |  |  |  |  | 0.00
2015 |  |  |  | 8086.65 |  |  | 8346 |  |  |  | 950 | [10 empty] | 95.01 |  |  |  | 95.01 | [5 empty] | 97.17 |  |  | 95.27 |  |  |  | 4.99 |  | 4.99 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6704.20 |  |  | 7255 |  |  |  | 950 | [10 empty] | 80.15 |  |  |  | 80.15 | [5 empty] | 80.34 |  |  | 82.59 |  |  |  | 9.83 |  | 8.96 | [8 empty] | 10.89 |  |  |  |  | 0.00
2017 |  |  |  | 7535.97 |  |  | 7490 |  |  |  | 950 | [10 empty] | 86.52 |  |  |  | 86.52 | [5 empty] | 90.55 |  |  | 85.50 |  |  |  | 0.92 |  | 2.39 | [8 empty] | 11.09 |  |  |  |  | 0.00
2018 |  |  |  | 8736.46 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.76 |  |  |  | 99.76 | [5 empty] | 104.98 |  |  | 100.00 |  |  |  | 0.24 |  | 0.24 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7668.87 |  |  | 7745 |  |  |  | 950 | [10 empty] | 87.66 |  |  |  | 87.66 | [5 empty] | 92.15 |  |  | 88.41 |  |  |  | 0.70 |  | 0.61 | [8 empty] | 11.72 |  |  |  |  | 0.00
2020 |  |  |  | 7553.71 |  |  | 7638 |  |  |  | 950 | [10 empty] | 86.28 |  |  |  | 86.28 | [5 empty] | 90.52 |  |  | 86.95 |  |  |  | 1.93 |  | 1.69 | [8 empty] | 12.02 |  |  |  |  | 0.00
2021 |  |  |  | 8673.29 |  |  | 8657 |  |  |  | 950 | [10 empty] | 98.71 |  |  |  | 98.71 | [5 empty] | 104.22 |  |  | 98.82 |  |  |  | 1.29 |  | 1.29 | [8 empty] | 0.00 |  |  |  |  | 0.00
2022 |  |  |  | 7923.02 |  |  | 7987 |  |  |  | 950 | [10 empty] | 91.15 |  |  |  | 91.15 | [5 empty] | 95.21 |  |  | 91.18 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 8.84 |  |  |  |  | 0.00
2023 |  |  |  | 8076.94 |  |  | 8100 |  |  |  | 950 | [10 empty] | 92.27 |  |  |  | 92.27 | [5 empty] | 97.06 |  |  | 92.47 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 7.71 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2012 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 194
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 661 | [14 empty] | 702
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 12
L. |  | Human factor related | [39 empty] | 7
Subtotal | [22 empty] | 661 | [14 empty] | 714 |  |  |  | 201
Total | [22 empty] | 661 | [14 empty] | 915
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2012 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 12
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 63
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
33. |  |  | Circulating Water System | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 59
42. |  |  | Electrical Power Supply Systems | [34 empty] | 36
Total | [37 empty] | 184
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-December. Additional electricity generation amounted to 433342 MWh. The unit was in the intermediate maintenance outage from 2023.06.24 to 2023.07.21. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-1
2023 Operating Experience
RU-12 | [8 empty] | KOLA-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-230 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-05-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1973-06-29
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-12-28
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 50 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 1958.53 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.56 %
Energy Availability Factor (EAF) | [18 empty] | : | 84.54 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.35 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.22 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.43 %
Load Factor (LF) | [18 empty] | : | 54.4 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.67 %
Operating Factor (OF) | [18 empty] | : | 75.01 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2189 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 129.48 | 187.44 |  |  |  | 42.64 |  | 9.39 | [8 empty] | 153.49 |  |  | 279.79 | [6 empty] | 292.32 |  | 275.46 |  |  |  | 213.40 |  |  | 18.91 |  |  | 73.16 | [9 empty] | 283.04 |  |  | 1958.53
EAF [%] |  |  |  |  | 100.00 | 95.71 |  |  |  | 25.74 |  | 9.15 | [8 empty] | 84.07 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.54
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 29.79 |  | 9.15 | [8 empty] | 84.07 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.22
LF [%] |  |  |  |  | 42.34 | 67.87 |  |  |  | 13.95 |  | 3.17 | [8 empty] | 50.20 |  |  | 94.55 | [6 empty] | 95.60 |  | 90.08 |  |  |  | 72.11 |  |  | 6.19 |  |  | 24.72 | [9 empty] | 92.56 |  |  | 54.40
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 30.51 |  | 11.67 | [8 empty] | 86.96 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 17.47 |  |  | 54.86 | [9 empty] | 100.00 |  |  | 75.01
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.91 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.56
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.91 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.35
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 70.21 |  | 90.85 | [8 empty] | 0.02 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.43
XUF [%] |  |  |  |  | 0.00 | 4.29 |  |  |  | 4.05 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.67
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 115303.16 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.56 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 72.74 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.09 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.68 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.23 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 63.51 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 4.94 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 79.14 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 918.20 |  |  | 4180 |  |  |  | 411 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1974 |  |  |  | 1990.06 |  |  | 8463 |  |  |  | 411 | [10 empty] | 79.22 |  |  |  | 79.22 | [5 empty] | 55.27 |  |  | 96.61 |  |  |  | 0.90 |  | 0.72 | [8 empty] | 20.06 |  |  |  |  | 0.01
1975 |  |  |  | 1015.76 |  |  | 5426 |  |  |  | 411 | [10 empty] | 50.91 |  |  |  | 50.94 | [5 empty] | 28.21 |  |  | 61.94 |  |  |  | 1.27 |  | 0.66 | [8 empty] | 48.40 |  |  |  |  | 0.03
1976 |  |  |  | 2421.71 |  |  | 8247 |  |  |  | 411 | [10 empty] | 74.05 |  |  |  | 74.17 | [5 empty] | 67.08 |  |  | 93.89 |  |  |  | 0.97 |  | 0.73 | [8 empty] | 25.10 |  |  |  |  | 0.12
1977 |  |  |  | 2101.05 |  |  | 7462 |  |  |  | 411 | [10 empty] | 76.38 |  |  |  | 76.40 | [5 empty] | 58.36 |  |  | 85.18 |  |  |  | 6.73 |  | 5.52 | [8 empty] | 18.09 |  |  |  |  | 0.01
1978 |  |  |  | 2978.78 |  |  | 8074 |  |  |  | 411 | [10 empty] | 82.58 |  |  |  | 82.60 | [5 empty] | 82.74 |  |  | 92.17 |  |  |  | 1.55 |  | 1.30 | [8 empty] | 16.10 |  |  |  |  | 0.02
1979 |  |  |  | 2435.60 |  |  | 6232 |  |  |  | 411 | [10 empty] | 64.63 |  |  |  | 64.65 | [5 empty] | 67.65 |  |  | 71.14 |  |  |  | 2.14 |  | 1.41 | [8 empty] | 33.94 |  |  |  |  | 0.02
1980 |  |  |  | 3466.37 |  |  | 8072 |  |  |  | 411 | [10 empty] | 90.90 |  |  |  | 91.05 | [5 empty] | 96.02 |  |  | 91.89 |  |  |  | 0.33 |  | 0.30 | [8 empty] | 8.65 |  |  |  |  | 0.15
1981 |  |  |  | 2870.79 |  |  | 7448 |  |  |  | 411 | [10 empty] | 80.94 |  |  |  | 80.95 | [5 empty] | 79.74 |  |  | 85.02 |  |  |  | 2.81 |  | 2.34 | [8 empty] | 16.71 |  |  |  |  | 0.01
1982 |  |  |  | 2848.07 |  |  | 7875 |  |  |  | 411 | [10 empty] | 85.52 |  |  |  | 85.52 | [5 empty] | 79.11 |  |  | 89.90 |  |  |  | 1.80 |  | 1.56 | [8 empty] | 12.91 |  |  |  |  | 0.01
1983 |  |  |  | 3217.37 |  |  | 7884 |  |  |  | 411 | [10 empty] | 88.25 |  |  |  | 88.27 | [5 empty] | 89.36 |  |  | 90.00 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 11.57 |  |  |  |  | 0.02
1984 |  |  |  | 3112.02 |  |  | 8060 |  |  |  | 411 | [10 empty] | 84.90 |  |  |  | 84.92 | [5 empty] | 86.20 |  |  | 91.76 |  |  |  | 1.41 |  | 1.22 | [8 empty] | 13.87 |  |  |  |  | 0.01
1985 |  |  |  | 2388.76 |  |  | 6001 |  |  |  | 411 | [10 empty] | 67.02 |  |  |  | 67.05 | [5 empty] | 66.35 |  |  | 68.50 |  |  |  | 0.61 |  | 0.41 | [8 empty] | 32.54 |  |  |  |  | 0.03
1986 |  |  |  | 2805.84 |  |  | 8074 |  |  |  | 411 | [10 empty] | 85.08 |  |  |  | 85.08 | [5 empty] | 77.93 |  |  | 92.17 |  |  |  | 5.88 |  | 5.32 | [8 empty] | 9.60 |  |  |  |  | 0.00
1987 |  |  |  | 3268.23 |  |  | 7972 |  |  |  | 440 | [10 empty] | 86.00 |  |  |  | 86.00 | [5 empty] | 84.79 |  |  | 91.00 |  |  |  | 0.96 |  | 0.83 | [8 empty] | 13.17 |  |  |  |  | 0.00
1988 |  |  |  | 2925.01 |  |  | 7482 |  |  |  | 411 | [10 empty] | 82.67 |  |  |  | 82.73 | [5 empty] | 81.02 |  |  | 85.18 |  |  |  | 6.53 |  | 5.78 | [8 empty] | 11.49 |  |  |  |  | 0.06
1989 |  |  |  | 2675.48 |  |  | 6731 |  |  |  | 411 | [10 empty] | 75.44 |  |  |  | 76.23 | [5 empty] | 74.31 |  |  | 76.84 |  |  |  | 1.18 |  | 0.91 | [8 empty] | 22.86 |  |  |  |  | 0.79
1990 |  |  |  | 2735.50 |  |  | 6838 |  |  |  | 411 | [10 empty] | 75.95 |  |  |  | 75.95 | [5 empty] | 75.98 |  |  | 78.06 |  |  |  | 2.00 |  | 1.55 | [8 empty] | 22.50 |  |  |  |  | 0.00
1991 |  |  |  | 2773.12 |  |  | 6965 |  |  |  | 411 | [10 empty] | 77.27 |  |  |  | 77.27 | [5 empty] | 77.02 |  |  | 79.51 |  |  |  | 7.17 |  | 5.97 | [8 empty] | 16.76 |  |  |  |  | 0.00
1992 |  |  |  | 2271.37 |  |  | 6651 |  |  |  | 411 | [10 empty] | 63.44 |  |  |  | 63.70 | [5 empty] | 62.92 |  |  | 75.73 |  |  |  | 17.65 |  | 13.65 | [8 empty] | 22.65 |  |  |  |  | 0.26
1993 |  |  |  | 1992.62 |  |  | 5663 |  |  |  | 411 | [10 empty] | 56.14 |  |  |  | 59.56 | [5 empty] | 55.35 |  |  | 64.65 |  |  |  | 14.77 |  | 10.32 | [8 empty] | 30.11 |  |  |  |  | 3.42
1994 |  |  |  | 1971.62 |  |  | 5359 |  |  |  | 411 | [10 empty] | 56.50 |  |  |  | 58.63 | [5 empty] | 54.76 |  |  | 61.18 |  |  |  | 7.34 |  | 4.65 | [8 empty] | 36.72 |  |  |  |  | 2.13
1995 |  |  |  | 1581.37 |  |  | 5398 |  |  |  | 411 | [10 empty] | 62.24 |  |  |  | 62.24 | [5 empty] | 43.92 |  |  | 61.62 |  |  |  | 5.06 |  | 3.32 | [8 empty] | 34.44 |  |  |  |  | 0.00
1996 |  |  |  | 1409.96 |  |  | 4466 |  |  |  | 411 | [10 empty] | 46.43 |  |  |  | 47.44 | [5 empty] | 39.05 |  |  | 50.84 |  |  |  | 6.51 |  | 3.30 | [8 empty] | 49.26 |  |  |  |  | 1.00
1997 |  |  |  | 2404.12 |  |  | 7942 |  |  |  | 411 | [10 empty] | 88.48 |  |  |  | 88.48 | [5 empty] | 66.77 |  |  | 90.66 |  |  |  | 5.02 |  | 4.68 | [8 empty] | 6.84 |  |  |  |  | 0.00
1998 |  |  |  | 1291.73 |  |  | 5658 |  |  |  | 411 | [10 empty] | 37.66 |  |  |  | 59.27 | [5 empty] | 35.88 |  |  | 64.59 |  |  |  | 12.77 |  | 8.68 | [8 empty] | 32.05 |  |  |  |  | 21.61
1999 |  |  |  | 2028.49 |  |  | 7355 |  |  |  | 411 | [10 empty] | 58.01 |  |  |  | 86.57 | [5 empty] | 56.34 |  |  | 83.96 |  |  |  | 0.97 |  | 0.85 | [8 empty] | 12.58 |  |  |  |  | 28.56
2000 |  |  |  | 1298.85 |  |  | 4643 |  |  |  | 411 | [10 empty] | 37.17 |  |  |  | 84.13 | [5 empty] | 35.98 |  |  | 52.86 |  |  |  | 0.80 |  | 0.68 | [8 empty] | 15.19 |  |  |  |  | 46.96
2001 |  |  |  | 2243.22 |  |  | 7098 |  |  |  | 411 | [10 empty] | 63.27 |  |  |  | 81.60 | [5 empty] | 62.31 |  |  | 81.03 |  |  |  | 0.91 |  | 0.75 | [8 empty] | 17.65 |  |  |  |  | 18.33
2002 |  |  |  | 1841.48 |  |  | 5660 |  |  |  | 411 | [10 empty] | 51.65 |  |  |  | 68.90 | [5 empty] | 51.15 |  |  | 64.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 31.10 |  |  |  |  | 17.25
2003 |  |  |  | 2164.00 |  |  | 6444 |  |  |  | 411 | [10 empty] | 60.41 |  |  |  | 75.51 | [5 empty] | 60.11 |  |  | 73.56 |  |  |  | 0.73 |  | 0.55 | [8 empty] | 23.94 |  |  |  |  | 15.10
2004 |  |  |  | 2440.48 |  |  | 7326 |  |  |  | 411 | [10 empty] | 68.21 |  |  |  | 83.64 | [5 empty] | 67.60 |  |  | 83.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.36 |  |  |  |  | 15.43
2005 |  |  |  | 2151.67 |  |  | 6901 |  |  |  | 411 | [10 empty] | 60.60 |  |  |  | 90.57 | [5 empty] | 59.76 |  |  | 78.78 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.43 |  |  |  |  | 29.97
2006 |  |  |  | 2338.66 |  |  | 7661 |  |  |  | 411 | [10 empty] | 65.95 |  |  |  | 89.94 | [5 empty] | 64.96 |  |  | 87.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.06 |  |  |  |  | 23.98
2007 |  |  |  | 2658.02 |  |  | 7740 |  |  |  | 411 | [10 empty] | 74.43 |  |  |  | 90.96 | [5 empty] | 73.83 |  |  | 88.36 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.04 |  |  |  |  | 16.53
2008 |  |  |  | 2705.75 |  |  | 7397 |  |  |  | 411 | [10 empty] | 84.34 |  |  |  | 84.34 | [5 empty] | 74.95 |  |  | 84.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.66 |  |  |  |  | 0.00
2009 |  |  |  | 2277.43 |  |  | 7333 |  |  |  | 411 | [10 empty] | 83.76 |  |  |  | 83.77 | [5 empty] | 63.26 |  |  | 83.71 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.23 |  |  |  |  | 0.01
2010 |  |  |  | 2467.97 |  |  | 7912 |  |  |  | 411 | [10 empty] | 85.79 |  |  |  | 85.82 | [5 empty] | 68.55 |  |  | 90.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.18 |  |  |  |  | 0.03
2011 |  |  |  | 2465.32 |  |  | 7870 |  |  |  | 411 | [10 empty] | 83.47 |  |  |  | 83.62 | [5 empty] | 68.48 |  |  | 89.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.38 |  |  |  |  | 0.15
2012 |  |  |  | 2205.74 |  |  | 7021 |  |  |  | 411 | [10 empty] | 82.24 |  |  |  | 82.24 | [5 empty] | 61.10 |  |  | 79.93 |  |  |  | 1.67 |  | 1.39 | [8 empty] | 16.37 |  |  |  |  | 0.00
2013 |  |  |  | 2380.88 |  |  | 7811 |  |  |  | 411 | [10 empty] | 83.98 |  |  |  | 83.98 | [5 empty] | 66.13 |  |  | 89.17 |  |  |  | 4.60 |  | 4.05 | [8 empty] | 11.97 |  |  |  |  | 0.00
2014 |  |  |  | 1911.66 |  |  | 7536 |  |  |  | 411 | [10 empty] | 85.18 |  |  |  | 86.19 | [5 empty] | 53.09 |  |  | 86.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.81 |  |  |  |  | 1.01
2015 |  |  |  | 2112.22 |  |  | 7373 |  |  |  | 411 | [10 empty] | 83.10 |  |  |  | 84.00 | [5 empty] | 58.67 |  |  | 84.17 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 15.99 |  |  |  |  | 0.91
2016 |  |  |  | 2097.80 |  |  | 6386 |  |  |  | 411 | [10 empty] | 78.45 |  |  |  | 78.45 | [5 empty] | 58.11 |  |  | 72.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.55 |  |  |  |  | 0.00
2017 |  |  |  | 1982.33 |  |  | 7025 |  |  |  | 411 | [10 empty] | 77.78 |  |  |  | 78.62 | [5 empty] | 55.06 |  |  | 80.19 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.38 |  |  |  |  | 0.84
2018 |  |  |  | 688.02 |  |  | 2652 |  |  |  | 411 | [10 empty] | 28.92 |  |  |  | 30.25 | [5 empty] | 19.11 |  |  | 30.27 |  |  |  | 5.22 |  | 1.97 | [8 empty] | 67.78 |  |  |  |  | 1.33
2019 |  |  |  | 2796.96 |  |  | 7740 |  |  |  | 411 | [10 empty] | 80.24 |  |  |  | 80.62 | [5 empty] | 77.69 |  |  | 88.36 |  |  |  | 6.14 |  | 7.61 | [8 empty] | 11.77 |  |  |  |  | 0.38
2020 |  |  |  | 2327.08 |  |  | 7193 |  |  |  | 411 | [10 empty] | 84.03 |  |  |  | 84.03 | [5 empty] | 64.46 |  |  | 81.89 |  |  |  | 0.07 |  | 0.05 | [8 empty] | 15.92 |  |  |  |  | 0.00
2021 |  |  |  | 1849.44 |  |  | 6406 |  |  |  | 411 | [10 empty] | 87.16 |  |  |  | 87.16 | [5 empty] | 51.37 |  |  | 73.13 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.84 |  |  |  |  | 0.00
2022 |  |  |  | 2215.25 |  |  | 7356 |  |  |  | 411 | [10 empty] | 84.90 |  |  |  | 84.90 | [5 empty] | 61.53 |  |  | 83.97 |  |  |  | 0.26 |  | 0.22 | [8 empty] | 14.88 |  |  |  |  | 0.00
2023 |  |  |  | 1958.53 |  |  | 6571 |  |  |  | 411 | [10 empty] | 84.54 |  |  |  | 85.22 | [5 empty] | 54.40 |  |  | 75.01 |  |  |  | 1.56 |  | 1.35 | [8 empty] | 13.43 |  |  |  |  | 0.67
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1973 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 97 | [14 empty] | 48
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1153 | [14 empty] | 1473 |  |  |  | 3
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 72
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 52
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 38
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 939 | [19 empty] | 157
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 4
Z. |  | Other | [39 empty] | 8
Subtotal | [22 empty] | 1153 |  |  |  | 97 | [6 empty] | 939 |  |  |  | 1597 |  |  |  | 60 | [11 empty] | 201
Total | [22 empty] | 2189 | [14 empty] | 1858
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1973 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 6
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [19 empty] | 97 | [14 empty] | 14
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 13
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [22 empty] | 97 | [14 empty] | 50
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in June, December. Additional electricity generation amounted to 1071 MWh. The unit was in the intermediate maintenance outage from 2023.03.10 to 2023.04.27. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-2
2023 Operating Experience
RU-13 | [8 empty] | KOLA-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-230 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1970-05-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1974-12-09
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1975-02-21
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 49 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2488.57 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.5 %
Energy Availability Factor (EAF) | [18 empty] | : | 85.42 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.44 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.27 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.29 %
Load Factor (LF) | [18 empty] | : | 69.12 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.84 %
Operating Factor (OF) | [18 empty] | : | 86.24 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1205 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 284.47 | 180.27 |  |  |  | 301.65 |  | 255.09 | [8 empty] | 178.98 |  |  | 299.49 | [6 empty] | 209.13 |  | 122.23 |  |  |  | 0.00 |  |  | 116.80 |  |  | 264.55 | [9 empty] | 275.91 |  |  | 2488.57
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 98.55 |  | 96.16 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 93.25 |  | 59.23 |  |  |  | 0.01 |  |  | 77.81 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.42
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 98.55 |  | 96.16 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 74.20 |  |  |  | 0.01 |  |  | 77.81 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.27
LF [%] |  |  |  |  | 93.03 | 65.27 |  |  |  | 98.65 |  | 86.20 | [8 empty] | 58.53 |  |  | 101.21 | [6 empty] | 68.39 |  | 39.97 |  |  |  | 0.00 |  |  | 38.20 |  |  | 89.40 | [9 empty] | 90.23 |  |  | 69.12
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 98.52 |  | 97.22 | [8 empty] | 92.74 |  |  | 100.00 | [6 empty] | 100.00 |  | 57.93 |  |  |  | 0.00 |  |  | 88.31 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.24
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.45 |  | 3.84 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.50
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 1.45 |  | 3.84 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.44
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 25.80 |  |  |  | 99.99 |  |  | 22.19 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.29
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 6.75 |  | 14.96 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.84
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 112612.62 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.55 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.45 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 77.8 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.17 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 63.9 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 4.34 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.95 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1975 |  |  |  | 1383.07 |  |  | 6449 |  |  |  | 411 | [10 empty] | 88.23 |  |  |  | 88.23 | [5 empty] | 37.48 |  |  | 73.97 |  |  |  | 3.66 |  | 3.35 | [8 empty] | 8.41 |  |  |  |  | 0.00
1976 |  |  |  | 1943.15 |  |  | 7083 |  |  |  | 411 | [10 empty] | 70.82 |  |  |  | 70.82 | [5 empty] | 53.82 |  |  | 80.64 |  |  |  | 0.74 |  | 0.53 | [8 empty] | 28.65 |  |  |  |  | 0.00
1977 |  |  |  | 2627.24 |  |  | 7038 |  |  |  | 411 | [10 empty] | 76.90 |  |  |  | 77.05 | [5 empty] | 72.97 |  |  | 80.34 |  |  |  | 1.10 |  | 0.85 | [8 empty] | 22.09 |  |  |  |  | 0.15
1978 |  |  |  | 2982.47 |  |  | 7576 |  |  |  | 411 | [10 empty] | 82.71 |  |  |  | 82.71 | [5 empty] | 82.84 |  |  | 86.48 |  |  |  | 0.67 |  | 0.56 | [8 empty] | 16.73 |  |  |  |  | 0.00
1979 |  |  |  | 3057.59 |  |  | 7663 |  |  |  | 411 | [10 empty] | 82.40 |  |  |  | 83.51 | [5 empty] | 84.92 |  |  | 87.48 |  |  |  | 3.13 |  | 2.70 | [8 empty] | 13.79 |  |  |  |  | 1.11
1980 |  |  |  | 3266.85 |  |  | 7966 |  |  |  | 411 | [10 empty] | 85.80 |  |  |  | 85.99 | [5 empty] | 90.49 |  |  | 90.69 |  |  |  | 0.71 |  | 0.62 | [8 empty] | 13.40 |  |  |  |  | 0.19
1981 |  |  |  | 3146.68 |  |  | 8225 |  |  |  | 411 | [10 empty] | 87.78 |  |  |  | 87.78 | [5 empty] | 87.40 |  |  | 93.89 |  |  |  | 2.81 |  | 2.54 | [8 empty] | 9.68 |  |  |  |  | 0.00
1982 |  |  |  | 2462.96 |  |  | 6742 |  |  |  | 411 | [10 empty] | 71.24 |  |  |  | 71.24 | [5 empty] | 68.41 |  |  | 76.96 |  |  |  | 3.13 |  | 2.30 | [8 empty] | 26.46 |  |  |  |  | 0.00
1983 |  |  |  | 3072.64 |  |  | 7963 |  |  |  | 411 | [10 empty] | 85.27 |  |  |  | 85.30 | [5 empty] | 85.34 |  |  | 90.90 |  |  |  | 3.18 |  | 2.80 | [8 empty] | 11.90 |  |  |  |  | 0.03
1984 |  |  |  | 3034.45 |  |  | 8079 |  |  |  | 411 | [10 empty] | 86.75 |  |  |  | 86.76 | [5 empty] | 84.05 |  |  | 91.97 |  |  |  | 1.97 |  | 1.74 | [8 empty] | 11.50 |  |  |  |  | 0.00
1985 |  |  |  | 3055.56 |  |  | 7872 |  |  |  | 411 | [10 empty] | 84.90 |  |  |  | 84.94 | [5 empty] | 84.87 |  |  | 89.86 |  |  |  | 3.18 |  | 2.79 | [8 empty] | 12.27 |  |  |  |  | 0.04
1986 |  |  |  | 2844.15 |  |  | 7405 |  |  |  | 411 | [10 empty] | 79.74 |  |  |  | 79.78 | [5 empty] | 79.00 |  |  | 84.53 |  |  |  | 4.19 |  | 3.49 | [8 empty] | 16.73 |  |  |  |  | 0.04
1987 |  |  |  | 3345.38 |  |  | 7900 |  |  |  | 440 | [10 empty] | 89.59 |  |  |  | 89.59 | [5 empty] | 86.79 |  |  | 90.18 |  |  |  | 0.58 |  | 0.52 | [8 empty] | 9.89 |  |  |  |  | 0.00
1988 |  |  |  | 2873.27 |  |  | 7451 |  |  |  | 411 | [10 empty] | 80.46 |  |  |  | 80.49 | [5 empty] | 79.59 |  |  | 84.82 |  |  |  | 5.60 |  | 4.78 | [8 empty] | 14.73 |  |  |  |  | 0.03
1989 |  |  |  | 2707.27 |  |  | 6859 |  |  |  | 411 | [10 empty] | 74.79 |  |  |  | 78.05 | [5 empty] | 75.19 |  |  | 78.30 |  |  |  | 0.67 |  | 0.52 | [8 empty] | 21.43 |  |  |  |  | 3.26
1990 |  |  |  | 2610.91 |  |  | 6751 |  |  |  | 411 | [10 empty] | 72.72 |  |  |  | 72.86 | [5 empty] | 72.52 |  |  | 77.07 |  |  |  | 6.09 |  | 4.73 | [8 empty] | 22.42 |  |  |  |  | 0.14
1991 |  |  |  | 2701.86 |  |  | 6983 |  |  |  | 411 | [10 empty] | 75.33 |  |  |  | 75.41 | [5 empty] | 75.04 |  |  | 79.71 |  |  |  | 11.29 |  | 9.60 | [8 empty] | 14.99 |  |  |  |  | 0.08
1992 |  |  |  | 2133.04 |  |  | 5871 |  |  |  | 411 | [10 empty] | 61.85 |  |  |  | 61.85 | [5 empty] | 59.09 |  |  | 66.85 |  |  |  | 16.94 |  | 12.61 | [8 empty] | 25.54 |  |  |  |  | 0.00
1993 |  |  |  | 2138.83 |  |  | 6377 |  |  |  | 411 | [10 empty] | 60.68 |  |  |  | 65.73 | [5 empty] | 59.41 |  |  | 72.80 |  |  |  | 7.71 |  | 5.49 | [8 empty] | 28.77 |  |  |  |  | 5.05
1994 |  |  |  | 398.60 |  |  | 1466 |  |  |  | 411 | [10 empty] | 16.68 |  |  |  | 16.68 | [5 empty] | 11.07 |  |  | 16.74 |  |  |  | 18.79 |  | 3.86 | [8 empty] | 79.46 |  |  |  |  | 0.00
1995 |  |  |  | 2205.78 |  |  | 6846 |  |  |  | 411 | [10 empty] | 93.58 |  |  |  | 93.58 | [5 empty] | 61.27 |  |  | 78.15 |  |  |  | 2.08 |  | 1.99 | [8 empty] | 4.43 |  |  |  |  | 0.00
1996 |  |  |  | 1946.17 |  |  | 6243 |  |  |  | 411 | [10 empty] | 65.47 |  |  |  | 66.30 | [5 empty] | 53.91 |  |  | 71.07 |  |  |  | 3.53 |  | 2.43 | [8 empty] | 31.27 |  |  |  |  | 0.84
1997 |  |  |  | 1157.94 |  |  | 3955 |  |  |  | 411 | [10 empty] | 40.64 |  |  |  | 53.44 | [5 empty] | 32.16 |  |  | 45.15 |  |  |  | 3.35 |  | 1.85 | [8 empty] | 44.70 |  |  |  |  | 12.80
1998 |  |  |  | 2655.63 |  |  | 8029 |  |  |  | 411 | [10 empty] | 74.46 |  |  |  | 83.64 | [5 empty] | 73.76 |  |  | 91.66 |  |  |  | 8.88 |  | 8.15 | [8 empty] | 8.22 |  |  |  |  | 9.18
1999 |  |  |  | 1272.59 |  |  | 4423 |  |  |  | 411 | [10 empty] | 36.30 |  |  |  | 48.99 | [5 empty] | 35.35 |  |  | 50.49 |  |  |  | 17.19 |  | 10.17 | [8 empty] | 40.84 |  |  |  |  | 12.69
2000 |  |  |  | 2430.51 |  |  | 7626 |  |  |  | 411 | [10 empty] | 68.16 |  |  |  | 83.38 | [5 empty] | 67.32 |  |  | 86.82 |  |  |  | 2.56 |  | 2.19 | [8 empty] | 14.43 |  |  |  |  | 15.22
2001 |  |  |  | 1722.31 |  |  | 6574 |  |  |  | 411 | [10 empty] | 49.08 |  |  |  | 84.74 | [5 empty] | 47.84 |  |  | 75.05 |  |  |  | 1.21 |  | 1.03 | [8 empty] | 14.22 |  |  |  |  | 35.67
2002 |  |  |  | 1738.75 |  |  | 5564 |  |  |  | 411 | [10 empty] | 48.66 |  |  |  | 83.24 | [5 empty] | 48.29 |  |  | 63.52 |  |  |  | 0.30 |  | 0.25 | [8 empty] | 16.51 |  |  |  |  | 34.58
2003 |  |  |  | 1866.10 |  |  | 5459 |  |  |  | 411 | [10 empty] | 52.04 |  |  |  | 66.40 | [5 empty] | 51.83 |  |  | 62.32 |  |  |  | 0.54 |  | 0.36 | [8 empty] | 33.24 |  |  |  |  | 14.37
2004 |  |  |  | 1787.07 |  |  | 5731 |  |  |  | 411 | [10 empty] | 49.92 |  |  |  | 73.84 | [5 empty] | 49.50 |  |  | 65.24 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 26.12 |  |  |  |  | 23.93
2005 |  |  |  | 2889.18 |  |  | 7379 |  |  |  | 411 | [10 empty] | 78.59 |  |  |  | 84.24 | [5 empty] | 80.25 |  |  | 84.24 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.76 |  |  |  |  | 5.65
2006 |  |  |  | 2640.13 |  |  | 7597 |  |  |  | 411 | [10 empty] | 71.98 |  |  |  | 85.73 | [5 empty] | 73.33 |  |  | 86.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.27 |  |  |  |  | 13.75
2007 |  |  |  | 2508.92 |  |  | 7474 |  |  |  | 411 | [10 empty] | 70.10 |  |  |  | 85.69 | [5 empty] | 69.69 |  |  | 85.32 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 14.14 |  |  |  |  | 15.59
2008 |  |  |  | 2554.70 |  |  | 7762 |  |  |  | 411 | [10 empty] | 89.13 |  |  |  | 89.92 | [5 empty] | 70.76 |  |  | 88.37 |  |  |  | 1.32 |  | 1.20 | [8 empty] | 8.88 |  |  |  |  | 0.79
2009 |  |  |  | 2384.55 |  |  | 6872 |  |  |  | 411 | [10 empty] | 79.44 |  |  |  | 80.28 | [5 empty] | 66.23 |  |  | 78.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.72 |  |  |  |  | 0.84
2010 |  |  |  | 2531.18 |  |  | 7619 |  |  |  | 411 | [10 empty] | 90.18 |  |  |  | 90.41 | [5 empty] | 70.30 |  |  | 86.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.59 |  |  |  |  | 0.24
2011 |  |  |  | 2501.98 |  |  | 7752 |  |  |  | 411 | [10 empty] | 83.07 |  |  |  | 83.63 | [5 empty] | 69.50 |  |  | 88.50 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.37 |  |  |  |  | 0.56
2012 |  |  |  | 2192.07 |  |  | 7775 |  |  |  | 411 | [10 empty] | 81.85 |  |  |  | 81.85 | [5 empty] | 60.72 |  |  | 88.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.14 |  |  |  |  | 0.00
2013 |  |  |  | 2412.70 |  |  | 7233 |  |  |  | 411 | [10 empty] | 82.80 |  |  |  | 82.80 | [5 empty] | 67.01 |  |  | 82.57 |  |  |  | 1.51 |  | 1.27 | [8 empty] | 15.93 |  |  |  |  | 0.00
2014 |  |  |  | 2596.45 |  |  | 7823 |  |  |  | 411 | [10 empty] | 89.32 |  |  |  | 90.15 | [5 empty] | 72.11 |  |  | 89.29 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 9.82 |  |  |  |  | 0.83
2015 |  |  |  | 1463.78 |  |  | 5450 |  |  |  | 411 | [10 empty] | 85.32 |  |  |  | 85.32 | [5 empty] | 40.66 |  |  | 62.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.68 |  |  |  |  | 0.00
2016 |  |  |  | 2053.14 |  |  | 6416 |  |  |  | 411 | [10 empty] | 79.35 |  |  |  | 79.79 | [5 empty] | 56.87 |  |  | 73.04 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.21 |  |  |  |  | 0.43
2017 |  |  |  | 1787.16 |  |  | 5615 |  |  |  | 411 | [10 empty] | 83.48 |  |  |  | 83.48 | [5 empty] | 49.64 |  |  | 64.10 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 16.45 |  |  |  |  | 0.00
2018 |  |  |  | 2765.53 |  |  | 7437 |  |  |  | 411 | [10 empty] | 84.10 |  |  |  | 84.42 | [5 empty] | 76.81 |  |  | 84.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.58 |  |  |  |  | 0.32
2019 |  |  |  | 670.53 |  |  | 1904 |  |  |  | 411 | [10 empty] | 20.38 |  |  |  | 21.54 | [5 empty] | 18.62 |  |  | 21.74 |  |  |  | 8.76 |  | 2.07 | [8 empty] | 76.39 |  |  |  |  | 1.17
2020 |  |  |  | 1890.68 |  |  | 7188 |  |  |  | 411 | [10 empty] | 86.71 |  |  |  | 86.71 | [5 empty] | 52.37 |  |  | 81.83 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.29 |  |  |  |  | 0.01
2021 |  |  |  | 1752.15 |  |  | 6931 |  |  |  | 411 | [10 empty] | 80.43 |  |  |  | 81.40 | [5 empty] | 48.67 |  |  | 79.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 18.60 |  |  |  |  | 0.97
2022 |  |  |  | 2190.58 |  |  | 6498 |  |  |  | 411 | [10 empty] | 85.85 |  |  |  | 85.85 | [5 empty] | 60.84 |  |  | 74.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.15 |  |  |  |  | 0.00
2023 |  |  |  | 2488.57 |  |  | 7555 |  |  |  | 411 | [10 empty] | 85.42 |  |  |  | 87.27 | [5 empty] | 69.12 |  |  | 86.24 |  |  |  | 0.50 |  | 0.44 | [8 empty] | 12.29 |  |  |  |  | 1.84
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1975 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 32 | [14 empty] | 64
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 999 | [14 empty] | 1469
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 51
E. |  | Testing of plant systems or components | [35 empty] | 7
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 101
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 27
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 175 | [19 empty] | 258
L. |  | Human factor related | [39 empty] | 1
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Z. |  | Other | [39 empty] | 0
Subtotal | [22 empty] | 999 |  |  |  | 32 | [6 empty] | 175 |  |  |  | 1628 |  |  |  | 69 | [11 empty] | 287
Total | [22 empty] | 1206 | [14 empty] | 1984
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1975 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 37
12. |  |  | Reactor I&C Systems | [34 empty] | 1
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 15
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [19 empty] | 32 | [14 empty] | 2
Total | [22 empty] | 32 | [14 empty] | 65
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in March-July, November-December. Additional electricity generation amounted to 18602 MWh. The unit was in the intermediate maintenance outage from 2023.08.24 to 2023.10.04. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-3
2023 Operating Experience
RU-32 | [8 empty] | KOLA-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1977-04-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-03-24
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1982-12-03
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2534.41 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.16 %
Energy Availability Factor (EAF) | [18 empty] | : | 77.88 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.92 %
Unit Capability Factor (UCF) | [18 empty] | : | 78.16 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.92 %
Load Factor (LF) | [18 empty] | : | 70.39 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.28 %
Operating Factor (OF) | [18 empty] | : | 75.39 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2156 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 261.91 | 240.95 |  |  |  | 295.45 |  | 259.62 | [8 empty] | 161.41 |  |  | 0.00 | [6 empty] | 0.00 |  | 107.28 |  |  |  | 281.16 |  |  | 299.02 |  |  | 315.48 | [9 empty] | 312.13 |  |  | 2534.41
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 93.68 |  |  | 10.01 | [6 empty] | 0.01 |  | 37.83 |  |  |  | 94.99 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 77.88
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 96.94 |  |  | 10.01 | [6 empty] | 0.01 |  | 37.83 |  |  |  | 94.99 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.16
LF [%] |  |  |  |  | 85.65 | 87.24 |  |  |  | 96.62 |  | 87.73 | [8 empty] | 52.79 |  |  | 0.00 | [6 empty] | 0.00 |  | 35.08 |  |  |  | 95.01 |  |  | 97.79 |  |  | 106.61 | [9 empty] | 102.08 |  |  | 70.39
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 65.99 |  |  | 0.00 | [6 empty] | 0.00 |  | 45.83 |  |  |  | 95.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 75.39
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.06 |  |  | 0.00 | [6 empty] | 0.00 |  | 7.08 |  |  |  | 5.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.16
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.06 |  |  | 0.00 | [6 empty] | 0.00 |  | 2.88 |  |  |  | 5.01 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.92
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 89.99 | [6 empty] | 99.99 |  | 59.29 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 20.92
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.27 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.28
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 106306.02 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.26 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.81 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.93 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.33 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.75 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 70.18 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 5.52 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.17 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1982 |  |  |  | 1891.17 |  |  | 7252 |  |  |  | 411 | [10 empty] | 99.35 |  |  |  | 99.38 | [5 empty] | 98.74 |  |  | 100.00 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 0.54 |  |  |  |  | 0.03
1983 |  |  |  | 2459.86 |  |  | 6818 |  |  |  | 411 | [10 empty] | 71.98 |  |  |  | 71.99 | [5 empty] | 68.32 |  |  | 77.83 |  |  |  | 3.90 |  | 2.92 | [8 empty] | 25.09 |  |  |  |  | 0.01
1984 |  |  |  | 2830.67 |  |  | 7610 |  |  |  | 411 | [10 empty] | 82.71 |  |  |  | 82.71 | [5 empty] | 78.41 |  |  | 86.63 |  |  |  | 1.76 |  | 1.48 | [8 empty] | 15.80 |  |  |  |  | 0.01
1985 |  |  |  | 2972.56 |  |  | 7814 |  |  |  | 411 | [10 empty] | 86.68 |  |  |  | 86.77 | [5 empty] | 82.56 |  |  | 89.20 |  |  |  | 2.25 |  | 2.00 | [8 empty] | 11.23 |  |  |  |  | 0.09
1986 |  |  |  | 2627.25 |  |  | 7244 |  |  |  | 411 | [10 empty] | 74.11 |  |  |  | 74.11 | [5 empty] | 72.97 |  |  | 82.69 |  |  |  | 16.48 |  | 14.62 | [8 empty] | 11.27 |  |  |  |  | 0.00
1987 |  |  |  | 2837.81 |  |  | 7024 |  |  |  | 440 | [10 empty] | 74.79 |  |  |  | 74.79 | [5 empty] | 73.63 |  |  | 80.18 |  |  |  | 6.83 |  | 5.49 | [8 empty] | 19.73 |  |  |  |  | 0.00
1988 |  |  |  | 2933.19 |  |  | 7913 |  |  |  | 411 | [10 empty] | 81.43 |  |  |  | 81.52 | [5 empty] | 81.25 |  |  | 90.08 |  |  |  | 4.73 |  | 4.05 | [8 empty] | 14.44 |  |  |  |  | 0.08
1989 |  |  |  | 3186.68 |  |  | 8047 |  |  |  | 411 | [10 empty] | 87.85 |  |  |  | 90.50 | [5 empty] | 88.51 |  |  | 91.86 |  |  |  | 0.81 |  | 0.74 | [8 empty] | 8.76 |  |  |  |  | 2.65
1990 |  |  |  | 3256.91 |  |  | 8022 |  |  |  | 411 | [10 empty] | 89.72 |  |  |  | 89.77 | [5 empty] | 90.46 |  |  | 91.58 |  |  |  | 0.95 |  | 0.87 | [8 empty] | 9.37 |  |  |  |  | 0.05
1991 |  |  |  | 2935.21 |  |  | 7188 |  |  |  | 411 | [10 empty] | 79.78 |  |  |  | 79.78 | [5 empty] | 81.53 |  |  | 82.05 |  |  |  | 2.74 |  | 2.25 | [8 empty] | 17.97 |  |  |  |  | 0.00
1992 |  |  |  | 2806.37 |  |  | 7396 |  |  |  | 411 | [10 empty] | 87.75 |  |  |  | 87.95 | [5 empty] | 77.74 |  |  | 84.21 |  |  |  | 2.36 |  | 2.13 | [8 empty] | 9.93 |  |  |  |  | 0.20
1993 |  |  |  | 2548.00 |  |  | 6833 |  |  |  | 411 | [10 empty] | 70.46 |  |  |  | 81.91 | [5 empty] | 70.77 |  |  | 78.00 |  |  |  | 1.41 |  | 1.17 | [8 empty] | 16.93 |  |  |  |  | 11.45
1994 |  |  |  | 2466.01 |  |  | 6373 |  |  |  | 411 | [10 empty] | 70.82 |  |  |  | 70.90 | [5 empty] | 68.49 |  |  | 72.75 |  |  |  | 10.76 |  | 8.55 | [8 empty] | 20.55 |  |  |  |  | 0.08
1995 |  |  |  | 2526.12 |  |  | 7083 |  |  |  | 411 | [10 empty] | 80.64 |  |  |  | 81.00 | [5 empty] | 70.16 |  |  | 80.86 |  |  |  | 0.82 |  | 0.67 | [8 empty] | 18.33 |  |  |  |  | 0.36
1996 |  |  |  | 2327.31 |  |  | 6928 |  |  |  | 411 | [10 empty] | 79.77 |  |  |  | 79.77 | [5 empty] | 64.46 |  |  | 78.87 |  |  |  | 5.33 |  | 4.49 | [8 empty] | 15.74 |  |  |  |  | 0.00
1997 |  |  |  | 2340.50 |  |  | 7114 |  |  |  | 411 | [10 empty] | 74.96 |  |  |  | 78.46 | [5 empty] | 65.01 |  |  | 81.21 |  |  |  | 0.56 |  | 0.44 | [8 empty] | 21.11 |  |  |  |  | 3.49
1998 |  |  |  | 2006.34 |  |  | 6705 |  |  |  | 411 | [10 empty] | 56.35 |  |  |  | 86.29 | [5 empty] | 55.73 |  |  | 76.54 |  |  |  | 4.27 |  | 3.85 | [8 empty] | 9.86 |  |  |  |  | 29.94
1999 |  |  |  | 2140.57 |  |  | 7040 |  |  |  | 411 | [10 empty] | 59.90 |  |  |  | 72.59 | [5 empty] | 59.45 |  |  | 80.37 |  |  |  | 9.77 |  | 7.86 | [8 empty] | 19.55 |  |  |  |  | 12.69
2000 |  |  |  | 2244.74 |  |  | 7731 |  |  |  | 411 | [10 empty] | 62.46 |  |  |  | 87.91 | [5 empty] | 62.18 |  |  | 88.01 |  |  |  | 0.08 |  | 0.07 | [8 empty] | 12.02 |  |  |  |  | 25.46
2001 |  |  |  | 2543.29 |  |  | 7057 |  |  |  | 411 | [10 empty] | 70.64 |  |  |  | 85.28 | [5 empty] | 70.64 |  |  | 80.56 |  |  |  | 1.10 |  | 0.95 | [8 empty] | 13.77 |  |  |  |  | 14.64
2002 |  |  |  | 2742.35 |  |  | 7909 |  |  |  | 411 | [10 empty] | 75.89 |  |  |  | 91.39 | [5 empty] | 76.17 |  |  | 90.29 |  |  |  | 0.43 |  | 0.40 | [8 empty] | 8.21 |  |  |  |  | 15.51
2003 |  |  |  | 2740.72 |  |  | 7335 |  |  |  | 411 | [10 empty] | 75.61 |  |  |  | 83.69 | [5 empty] | 76.12 |  |  | 83.73 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 16.26 |  |  |  |  | 8.08
2004 |  |  |  | 2816.85 |  |  | 7688 |  |  |  | 411 | [10 empty] | 77.37 |  |  |  | 88.10 | [5 empty] | 78.02 |  |  | 87.52 |  |  |  | 0.57 |  | 0.51 | [8 empty] | 11.39 |  |  |  |  | 10.73
2005 |  |  |  | 2059.39 |  |  | 7672 |  |  |  | 411 | [10 empty] | 57.64 |  |  |  | 88.49 | [5 empty] | 57.19 |  |  | 87.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 11.51 |  |  |  |  | 30.85
2006 |  |  |  | 2294.60 |  |  | 7436 |  |  |  | 411 | [10 empty] | 64.00 |  |  |  | 89.99 | [5 empty] | 63.73 |  |  | 84.89 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 9.97 |  |  |  |  | 25.99
2007 |  |  |  | 1815.27 |  |  | 6506 |  |  |  | 411 | [10 empty] | 50.72 |  |  |  | 82.86 | [5 empty] | 50.42 |  |  | 74.27 |  |  |  | 1.49 |  | 1.25 | [8 empty] | 15.89 |  |  |  |  | 32.14
2008 |  |  |  | 1876.73 |  |  | 7405 |  |  |  | 411 | [10 empty] | 83.82 |  |  |  | 83.82 | [5 empty] | 51.98 |  |  | 84.30 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 16.15 |  |  |  |  | 0.00
2009 |  |  |  | 2050.45 |  |  | 7340 |  |  |  | 411 | [10 empty] | 83.13 |  |  |  | 83.85 | [5 empty] | 56.95 |  |  | 83.79 |  |  |  | 0.10 |  | 0.08 | [8 empty] | 16.07 |  |  |  |  | 0.71
2010 |  |  |  | 1979.23 |  |  | 6009 |  |  |  | 411 | [10 empty] | 71.48 |  |  |  | 71.48 | [5 empty] | 54.97 |  |  | 68.60 |  |  |  | 1.03 |  | 0.75 | [8 empty] | 27.78 |  |  |  |  | 0.00
2011 |  |  |  | 2288.62 |  |  | 6405 |  |  |  | 411 | [10 empty] | 71.67 |  |  |  | 71.67 | [5 empty] | 63.57 |  |  | 73.12 |  |  |  | 2.56 |  | 1.89 | [8 empty] | 26.45 |  |  |  |  | 0.00
2012 |  |  |  | 2226.17 |  |  | 6701 |  |  |  | 411 | [10 empty] | 78.13 |  |  |  | 78.13 | [5 empty] | 61.66 |  |  | 76.29 |  |  |  | 1.74 |  | 1.38 | [8 empty] | 20.49 |  |  |  |  | 0.00
2013 |  |  |  | 2264.33 |  |  | 6396 |  |  |  | 411 | [10 empty] | 73.80 |  |  |  | 73.80 | [5 empty] | 62.89 |  |  | 73.01 |  |  |  | 2.75 |  | 2.09 | [8 empty] | 24.11 |  |  |  |  | 0.00
2014 |  |  |  | 2636.67 |  |  | 7712 |  |  |  | 411 | [10 empty] | 87.60 |  |  |  | 87.60 | [5 empty] | 73.23 |  |  | 88.03 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 12.38 |  |  |  |  | 0.00
2015 |  |  |  | 2581.99 |  |  | 7364 |  |  |  | 411 | [10 empty] | 84.12 |  |  |  | 84.12 | [5 empty] | 71.71 |  |  | 84.06 |  |  |  | 0.45 |  | 0.38 | [8 empty] | 15.50 |  |  |  |  | 0.00
2016 |  |  |  | 2583.96 |  |  | 6573 |  |  |  | 411 | [10 empty] | 86.16 |  |  |  | 86.29 | [5 empty] | 71.57 |  |  | 74.83 |  |  |  | 0.41 |  | 0.36 | [8 empty] | 13.36 |  |  |  |  | 0.13
2017 |  |  |  | 2679.44 |  |  | 7494 |  |  |  | 411 | [10 empty] | 84.70 |  |  |  | 84.70 | [5 empty] | 74.42 |  |  | 85.55 |  |  |  | 0.31 |  | 0.27 | [8 empty] | 15.03 |  |  |  |  | 0.00
2018 |  |  |  | 3036.60 |  |  | 7433 |  |  |  | 411 | [10 empty] | 85.34 |  |  |  | 85.34 | [5 empty] | 84.34 |  |  | 84.85 |  |  |  | 2.24 |  | 2.62 | [8 empty] | 12.04 |  |  |  |  | 0.00
2019 |  |  |  | 2759.12 |  |  | 7606 |  |  |  | 411 | [10 empty] | 85.71 |  |  |  | 86.49 | [5 empty] | 76.63 |  |  | 86.83 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 13.47 |  |  |  |  | 0.78
2020 |  |  |  | 2527.89 |  |  | 7116 |  |  |  | 411 | [10 empty] | 81.99 |  |  |  | 82.81 | [5 empty] | 70.02 |  |  | 81.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 17.19 |  |  |  |  | 0.82
2021 |  |  |  | 2539.74 |  |  | 7038 |  |  |  | 411 | [10 empty] | 82.91 |  |  |  | 82.91 | [5 empty] | 70.54 |  |  | 80.34 |  |  |  | 0.53 |  | 0.44 | [8 empty] | 16.65 |  |  |  |  | 0.00
2022 |  |  |  | 2739.16 |  |  | 7514 |  |  |  | 411 | [10 empty] | 84.71 |  |  |  | 84.71 | [5 empty] | 76.08 |  |  | 85.78 |  |  |  | 0.68 |  | 0.79 | [8 empty] | 14.50 |  |  |  |  | 0.00
2023 |  |  |  | 2534.41 |  |  | 6604 |  |  |  | 411 | [10 empty] | 77.88 |  |  |  | 78.16 | [5 empty] | 70.39 |  |  | 75.39 |  |  |  | 1.16 |  | 0.92 | [8 empty] | 20.92 |  |  |  |  | 0.28
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1982 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 80 | [14 empty] | 66
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1774 | [14 empty] | 1270
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 60
E. |  | Testing of plant systems or components | [35 empty] | 10 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 47
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 302 | [19 empty] | 114
L. |  | Human factor related | [39 empty] | 2
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 3
Subtotal | [22 empty] | 1774 |  |  |  | 80 | [6 empty] | 302 |  |  |  | 1340 |  |  |  | 72 | [11 empty] | 162
Total | [22 empty] | 2156 | [14 empty] | 1574
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1982 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 6
12. |  |  | Reactor I&C Systems | [34 empty] | 22
15. |  |  | Reactor Cooling Systems | [34 empty] | 11
16. |  |  | Steam generation systems | [34 empty] | 8
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [19 empty] | 23 | [14 empty] | 4
32. |  |  | Feedwater and Main Steam System | [19 empty] | 57 | [14 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [22 empty] | 80 | [14 empty] | 68
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in August-December. Additional electricity generation amounted to 40285 MWh. The unit was in the overhaul outage from 2023.06.04 to 2023.08.21. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KOLA-4
2023 Operating Experience
RU-33 | [8 empty] | KOLA-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KALUGA (JSC "Kaluga turbine plant" 32, Glagoleva Street, Kaluga, 248021, Russia )
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-213 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-08-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-10-11
Gross electrical power | [12 empty] | : |  |  | 440 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-12-06
Reference unit power (net) | [12 empty] | : |  |  | 411 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 300
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Lake (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 37 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3102.73 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.39 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.39 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.61 %
Load Factor (LF) | [18 empty] | : | 86.18 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 86.37 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1194 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 297.98 | 267.95 |  |  |  | 325.23 |  | 290.99 | [8 empty] | 117.15 |  |  | 0.00 | [6 empty] | 279.38 |  | 303.86 |  |  |  | 301.39 |  |  | 295.36 |  |  | 318.16 | [9 empty] | 305.28 |  |  | 3102.73
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 48.39 |  |  | 0.01 | [6 empty] | 88.12 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.39
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 48.39 |  |  | 0.01 | [6 empty] | 88.12 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.39
LF [%] |  |  |  |  | 97.45 | 97.02 |  |  |  | 106.36 |  | 98.33 | [8 empty] | 38.31 |  |  | 0.00 | [6 empty] | 91.37 |  | 99.37 |  |  |  | 101.85 |  |  | 96.59 |  |  | 107.52 | [9 empty] | 99.83 |  |  | 86.18
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 44.49 |  |  | 0.00 | [6 empty] | 91.80 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 86.37
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 51.61 |  |  | 99.99 | [6 empty] | 11.88 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 13.61
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 101890.34 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.48 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.94 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.09 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.32 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 15.58 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.38 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 5.38 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.39 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 249.38 |  |  | 1605 |  |  |  | 411 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 55.09 |  |  | 98.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 2585.77 |  |  | 7751 |  |  |  | 411 | [10 empty] | 78.18 |  |  |  | 78.19 | [5 empty] | 71.82 |  |  | 88.48 |  |  |  | 3.31 |  | 2.68 | [8 empty] | 19.14 |  |  |  |  | 0.01
1986 |  |  |  | 2690.18 |  |  | 7230 |  |  |  | 411 | [10 empty] | 72.36 |  |  |  | 72.36 | [5 empty] | 74.72 |  |  | 82.53 |  |  |  | 6.11 |  | 4.71 | [8 empty] | 22.93 |  |  |  |  | 0.00
1987 |  |  |  | 3341.17 |  |  | 7861 |  |  |  | 440 | [10 empty] | 85.50 |  |  |  | 85.50 | [5 empty] | 86.68 |  |  | 89.74 |  |  |  | 0.91 |  | 0.79 | [8 empty] | 13.72 |  |  |  |  | 0.00
1988 |  |  |  | 3124.21 |  |  | 7762 |  |  |  | 411 | [10 empty] | 84.95 |  |  |  | 84.96 | [5 empty] | 86.54 |  |  | 88.37 |  |  |  | 4.04 |  | 3.58 | [8 empty] | 11.47 |  |  |  |  | 0.01
1989 |  |  |  | 3111.51 |  |  | 7793 |  |  |  | 411 | [10 empty] | 85.77 |  |  |  | 87.57 | [5 empty] | 86.42 |  |  | 88.96 |  |  |  | 1.33 |  | 1.18 | [8 empty] | 11.25 |  |  |  |  | 1.80
1990 |  |  |  | 2930.40 |  |  | 7142 |  |  |  | 411 | [10 empty] | 80.24 |  |  |  | 80.28 | [5 empty] | 81.39 |  |  | 81.53 |  |  |  | 0.76 |  | 0.62 | [8 empty] | 19.10 |  |  |  |  | 0.05
1991 |  |  |  | 2790.49 |  |  | 7429 |  |  |  | 411 | [10 empty] | 76.70 |  |  |  | 76.70 | [5 empty] | 77.51 |  |  | 84.81 |  |  |  | 8.47 |  | 7.09 | [8 empty] | 16.21 |  |  |  |  | 0.00
1992 |  |  |  | 2764.94 |  |  | 7253 |  |  |  | 411 | [10 empty] | 79.99 |  |  |  | 80.51 | [5 empty] | 76.60 |  |  | 82.58 |  |  |  | 2.77 |  | 2.29 | [8 empty] | 17.19 |  |  |  |  | 0.52
1993 |  |  |  | 2826.99 |  |  | 8247 |  |  |  | 411 | [10 empty] | 79.00 |  |  |  | 92.43 | [5 empty] | 78.52 |  |  | 94.14 |  |  |  | 5.98 |  | 5.88 | [8 empty] | 1.69 |  |  |  |  | 13.43
1994 |  |  |  | 1939.77 |  |  | 5915 |  |  |  | 411 | [10 empty] | 55.77 |  |  |  | 62.72 | [5 empty] | 53.88 |  |  | 67.52 |  |  |  | 20.29 |  | 15.97 | [8 empty] | 21.31 |  |  |  |  | 6.95
1995 |  |  |  | 2288.81 |  |  | 7022 |  |  |  | 411 | [10 empty] | 73.83 |  |  |  | 73.83 | [5 empty] | 63.57 |  |  | 80.16 |  |  |  | 7.04 |  | 5.59 | [8 empty] | 20.57 |  |  |  |  | 0.00
1996 |  |  |  | 2537.72 |  |  | 7792 |  |  |  | 411 | [10 empty] | 84.09 |  |  |  | 84.09 | [5 empty] | 70.29 |  |  | 88.71 |  |  |  | 4.39 |  | 3.86 | [8 empty] | 12.05 |  |  |  |  | 0.00
1997 |  |  |  | 2271.67 |  |  | 6848 |  |  |  | 411 | [10 empty] | 74.56 |  |  |  | 76.16 | [5 empty] | 63.10 |  |  | 78.17 |  |  |  | 6.93 |  | 5.67 | [8 empty] | 18.18 |  |  |  |  | 1.59
1998 |  |  |  | 1927.55 |  |  | 6336 |  |  |  | 411 | [10 empty] | 49.19 |  |  |  | 69.38 | [5 empty] | 53.54 |  |  | 72.33 |  |  |  | 8.64 |  | 6.56 | [8 empty] | 24.05 |  |  |  |  | 20.20
1999 |  |  |  | 2567.48 |  |  | 7193 |  |  |  | 411 | [10 empty] | 71.16 |  |  |  | 82.00 | [5 empty] | 71.31 |  |  | 82.11 |  |  |  | 1.51 |  | 1.26 | [8 empty] | 16.75 |  |  |  |  | 10.84
2000 |  |  |  | 2177.50 |  |  | 7096 |  |  |  | 411 | [10 empty] | 60.44 |  |  |  | 86.31 | [5 empty] | 60.31 |  |  | 80.78 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 13.63 |  |  |  |  | 25.86
2001 |  |  |  | 2447.14 |  |  | 7149 |  |  |  | 411 | [10 empty] | 67.98 |  |  |  | 87.38 | [5 empty] | 67.97 |  |  | 81.61 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.62 |  |  |  |  | 19.40
2002 |  |  |  | 2601.71 |  |  | 7281 |  |  |  | 411 | [10 empty] | 71.52 |  |  |  | 79.71 | [5 empty] | 72.26 |  |  | 83.12 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 20.29 |  |  |  |  | 8.19
2003 |  |  |  | 2480.80 |  |  | 6663 |  |  |  | 411 | [10 empty] | 68.69 |  |  |  | 90.88 | [5 empty] | 68.90 |  |  | 76.06 |  |  |  | 1.45 |  | 1.34 | [8 empty] | 7.78 |  |  |  |  | 22.20
2004 |  |  |  | 2391.59 |  |  | 7863 |  |  |  | 411 | [10 empty] | 66.38 |  |  |  | 86.78 | [5 empty] | 66.24 |  |  | 89.52 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.22 |  |  |  |  | 20.40
2005 |  |  |  | 2231.75 |  |  | 7879 |  |  |  | 411 | [10 empty] | 62.10 |  |  |  | 90.21 | [5 empty] | 61.98 |  |  | 89.93 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.79 |  |  |  |  | 28.11
2006 |  |  |  | 2573.11 |  |  | 7217 |  |  |  | 411 | [10 empty] | 71.26 |  |  |  | 84.11 | [5 empty] | 71.47 |  |  | 82.39 |  |  |  | 0.13 |  | 0.11 | [8 empty] | 15.79 |  |  |  |  | 12.85
2007 |  |  |  | 2584.08 |  |  | 7640 |  |  |  | 411 | [10 empty] | 71.52 |  |  |  | 89.77 | [5 empty] | 71.77 |  |  | 87.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.23 |  |  |  |  | 18.25
2008 |  |  |  | 2793.49 |  |  | 7794 |  |  |  | 411 | [10 empty] | 85.15 |  |  |  | 85.20 | [5 empty] | 77.38 |  |  | 88.73 |  |  |  | 0.05 |  | 0.04 | [8 empty] | 14.76 |  |  |  |  | 0.04
2009 |  |  |  | 2468.01 |  |  | 7538 |  |  |  | 411 | [10 empty] | 83.73 |  |  |  | 83.74 | [5 empty] | 68.55 |  |  | 86.05 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 16.25 |  |  |  |  | 0.02
2010 |  |  |  | 2956.73 |  |  | 7332 |  |  |  | 411 | [10 empty] | 84.73 |  |  |  | 84.73 | [5 empty] | 82.12 |  |  | 83.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 15.27 |  |  |  |  | 0.00
2011 |  |  |  | 2558.01 |  |  | 6803 |  |  |  | 411 | [10 empty] | 79.30 |  |  |  | 79.33 | [5 empty] | 71.06 |  |  | 77.67 |  |  |  | 5.98 |  | 5.05 | [8 empty] | 15.62 |  |  |  |  | 0.03
2012 |  |  |  | 2601.69 |  |  | 7459 |  |  |  | 411 | [10 empty] | 84.75 |  |  |  | 84.75 | [5 empty] | 72.06 |  |  | 84.92 |  |  |  | 0.11 |  | 0.09 | [8 empty] | 15.16 |  |  |  |  | 0.00
2013 |  |  |  | 2572.70 |  |  | 7084 |  |  |  | 411 | [10 empty] | 83.22 |  |  |  | 83.22 | [5 empty] | 71.46 |  |  | 80.87 |  |  |  | 0.26 |  | 0.22 | [8 empty] | 16.56 |  |  |  |  | 0.00
2014 |  |  |  | 2488.19 |  |  | 6241 |  |  |  | 411 | [10 empty] | 70.91 |  |  |  | 70.91 | [5 empty] | 69.10 |  |  | 71.24 |  |  |  | 2.61 |  | 1.90 | [8 empty] | 27.18 |  |  |  |  | 0.00
2015 |  |  |  | 2506.63 |  |  | 6870 |  |  |  | 411 | [10 empty] | 87.25 |  |  |  | 87.25 | [5 empty] | 69.62 |  |  | 78.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.75 |  |  |  |  | 0.00
2016 |  |  |  | 2425.95 |  |  | 6422 |  |  |  | 411 | [10 empty] | 83.44 |  |  |  | 83.44 | [5 empty] | 67.20 |  |  | 73.11 |  |  |  | 0.86 |  | 0.73 | [8 empty] | 15.83 |  |  |  |  | 0.00
2017 |  |  |  | 2994.93 |  |  | 7633 |  |  |  | 411 | [10 empty] | 84.56 |  |  |  | 84.56 | [5 empty] | 83.18 |  |  | 87.13 |  |  |  | 3.60 |  | 3.16 | [8 empty] | 12.28 |  |  |  |  | 0.00
2018 |  |  |  | 3058.96 |  |  | 7464 |  |  |  | 411 | [10 empty] | 84.97 |  |  |  | 84.97 | [5 empty] | 84.96 |  |  | 85.21 |  |  |  | 0.57 |  | 0.49 | [8 empty] | 14.54 |  |  |  |  | 0.00
2019 |  |  |  | 3188.15 |  |  | 7831 |  |  |  | 411 | [10 empty] | 87.41 |  |  |  | 87.48 | [5 empty] | 88.55 |  |  | 89.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.52 |  |  |  |  | 0.07
2020 |  |  |  | 1996.91 |  |  | 5992 |  |  |  | 411 | [10 empty] | 80.37 |  |  |  | 80.37 | [5 empty] | 55.31 |  |  | 68.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 19.63 |  |  |  |  | 0.00
2021 |  |  |  | 2516.21 |  |  | 6801 |  |  |  | 411 | [10 empty] | 82.77 |  |  |  | 82.77 | [5 empty] | 69.89 |  |  | 77.64 |  |  |  | 0.85 |  | 0.71 | [8 empty] | 16.52 |  |  |  |  | 0.00
2022 |  |  |  | 2512.64 |  |  | 6357 |  |  |  | 411 | [10 empty] | 77.84 |  |  |  | 77.84 | [5 empty] | 69.79 |  |  | 72.57 |  |  |  | 0.41 |  | 0.32 | [8 empty] | 21.84 |  |  |  |  | 0.00
2023 |  |  |  | 3102.73 |  |  | 7566 |  |  |  | 411 | [10 empty] | 86.39 |  |  |  | 86.39 | [5 empty] | 86.18 |  |  | 86.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 13.61 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1984 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 50
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1165 | [14 empty] | 1172 |  |  |  | 15
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 66
E. |  | Testing of plant systems or components | [35 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 39
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [31 empty] | 29 | [19 empty] | 178
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 0
Z. |  | Other | [39 empty] | 0
Subtotal | [22 empty] | 1165 | [10 empty] | 29 |  |  |  | 1242 |  |  |  | 68 | [11 empty] | 217
Total | [22 empty] | 1194 | [14 empty] | 1527
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1984 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 2
12. |  |  | Reactor I&C Systems | [34 empty] | 12
14. |  |  | Safety Systems | [34 empty] | 6
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
16. |  |  | Steam generation systems | [34 empty] | 9
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 13
Total | [37 empty] | 54
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-May, July-December. Additional electricity generation amounted to 97736 MWh. The unit was in the overhaul outage from 2023.05.16 to 2023.07.03. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-2
2023 Operating Experience
RU-22 | [8 empty] | KURSK-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Permanent Shutdown
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-01-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1979-01-28
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-08-17
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | NA
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1693 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 11.2 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 150 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6196.09 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.54 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.92 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.96 %
Unit Capability Factor (UCF) | [18 empty] | : | 75.23 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 22.81 %
Load Factor (LF) | [18 empty] | : | 76.47 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.31 %
Operating Factor (OF) | [18 empty] | : | 77.83 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1942 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 48.75 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 701.76 | 628.94 |  |  |  | 3.95 |  | 0.00 | [8 empty] | 181.66 |  |  | 659.46 | [6 empty] | 655.20 |  | 547.62 |  |  |  | 670.35 |  |  | 714.62 |  |  | 699.39 | [9 empty] | 733.14 |  |  | 6196.09
EAF [%] |  |  |  |  | 100.00 | 98.43 |  |  |  | 1.81 |  | 0.00 | [8 empty] | 27.75 |  |  | 98.26 | [6 empty] | 94.89 |  | 80.28 |  |  |  | 99.82 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 74.92
UCF [%] |  |  |  |  | 100.00 | 98.43 |  |  |  | 1.81 |  | 0.00 | [8 empty] | 27.91 |  |  | 98.38 | [6 empty] | 95.76 |  | 82.63 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 75.23
LF [%] |  |  |  |  | 101.97 | 101.18 |  |  |  | 0.57 |  | 0.00 | [8 empty] | 26.40 |  |  | 99.02 | [6 empty] | 95.21 |  | 79.57 |  |  |  | 100.65 |  |  | 103.84 |  |  | 105.01 | [9 empty] | 106.53 |  |  | 76.47
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 3.63 |  | 0.00 | [8 empty] | 32.12 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 77.83
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.62 | [6 empty] | 4.24 |  | 17.32 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.54
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 1.62 | [6 empty] | 4.24 |  | 17.31 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.96
PUF [%] |  |  |  |  | 0.00 | 1.57 |  |  |  | 98.19 |  | 100.00 | [8 empty] | 72.09 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.07 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 22.81
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.16 |  |  | 0.12 | [6 empty] | 0.86 |  | 2.35 |  |  |  | 0.18 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.31
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 236137.58 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.83 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 64.81 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 4.33 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 66.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 29.02 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 65.14 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.84 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.65 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 3613.90 |  |  | 6734 |  |  |  | 925 | [10 empty] | 62.36 |  |  |  | 62.36 | [5 empty] | 62.31 |  |  | 80.40 |  |  |  | 27.83 |  | 24.04 | [8 empty] | 13.59 |  |  |  |  | 0.00
1980 |  |  |  | 6404.32 |  |  | 7658 |  |  |  | 925 | [10 empty] | 78.45 |  |  |  | 79.02 | [5 empty] | 78.82 |  |  | 87.18 |  |  |  | 10.04 |  | 8.82 | [8 empty] | 12.15 |  |  |  |  | 0.58
1981 |  |  |  | 6385.88 |  |  | 7874 |  |  |  | 925 | [10 empty] | 78.71 |  |  |  | 78.71 | [5 empty] | 78.81 |  |  | 89.89 |  |  |  | 8.73 |  | 7.53 | [8 empty] | 13.77 |  |  |  |  | 0.00
1982 |  |  |  | 5875.79 |  |  | 6443 |  |  |  | 925 | [10 empty] | 71.11 |  |  |  | 71.11 | [5 empty] | 72.51 |  |  | 73.55 |  |  |  | 6.25 |  | 4.74 | [8 empty] | 24.14 |  |  |  |  | 0.00
1983 |  |  |  | 5707.64 |  |  | 7104 |  |  |  | 925 | [10 empty] | 70.07 |  |  |  | 70.07 | [5 empty] | 70.44 |  |  | 81.10 |  |  |  | 10.00 |  | 7.78 | [8 empty] | 22.15 |  |  |  |  | 0.00
1984 |  |  |  | 6326.50 |  |  | 7219 |  |  |  | 925 | [10 empty] | 77.06 |  |  |  | 77.10 | [5 empty] | 77.86 |  |  | 82.18 |  |  |  | 5.31 |  | 4.33 | [8 empty] | 18.57 |  |  |  |  | 0.05
1985 |  |  |  | 6459.94 |  |  | 7598 |  |  |  | 925 | [10 empty] | 79.41 |  |  |  | 79.41 | [5 empty] | 79.72 |  |  | 86.74 |  |  |  | 6.09 |  | 5.15 | [8 empty] | 15.43 |  |  |  |  | 0.00
1986 |  |  |  | 5617.31 |  |  | 6575 |  |  |  | 925 | [10 empty] | 69.08 |  |  |  | 69.08 | [5 empty] | 69.32 |  |  | 75.06 |  |  |  | 15.66 |  | 12.82 | [8 empty] | 18.10 |  |  |  |  | 0.00
1987 |  |  |  | 7196.69 |  |  | 7539 |  |  |  | 1000 | [10 empty] | 83.29 |  |  |  | 83.29 | [5 empty] | 82.15 |  |  | 86.06 |  |  |  | 3.73 |  | 3.23 | [8 empty] | 13.48 |  |  |  |  | 0.00
1988 |  |  |  | 5725.66 |  |  | 6609 |  |  |  | 925 | [10 empty] | 73.88 |  |  |  | 73.88 | [5 empty] | 70.47 |  |  | 75.24 |  |  |  | 3.50 |  | 2.68 | [8 empty] | 23.44 |  |  |  |  | 0.00
1989 |  |  |  | 6164.20 |  |  | 6797 |  |  |  | 925 | [10 empty] | 74.90 |  |  |  | 74.91 | [5 empty] | 76.07 |  |  | 77.59 |  |  |  | 14.58 |  | 12.79 | [8 empty] | 12.30 |  |  |  |  | 0.02
1990 |  |  |  | 4789.70 |  |  | 6874 |  |  |  | 925 | [10 empty] | 62.20 |  |  |  | 62.20 | [5 empty] | 59.11 |  |  | 78.47 |  |  |  | 26.17 |  | 22.05 | [8 empty] | 15.75 |  |  |  |  | 0.00
1991 |  |  |  | 4375.96 |  |  | 7361 |  |  |  | 925 | [10 empty] | 55.26 |  |  |  | 56.28 | [5 empty] | 54.00 |  |  | 84.03 |  |  |  | 0.70 |  | 0.40 | [8 empty] | 43.32 |  |  |  |  | 1.02
1992 |  |  |  | 2158.37 |  |  | 3552 |  |  |  | 925 | [10 empty] | 27.24 |  |  |  | 27.24 | [5 empty] | 26.57 |  |  | 40.44 |  |  |  | 3.87 |  | 1.10 | [8 empty] | 71.67 |  |  |  |  | 0.00
1993 |  |  |  | 4438.15 |  |  | 7432 |  |  |  | 925 | [10 empty] | 57.09 |  |  |  | 85.00 | [5 empty] | 54.77 |  |  | 84.84 |  |  |  | 2.25 |  | 1.95 | [8 empty] | 13.04 |  |  |  |  | 27.91
1994 |  |  |  | 4212.17 |  |  | 7385 |  |  |  | 925 | [10 empty] | 53.46 |  |  |  | 55.29 | [5 empty] | 51.98 |  |  | 84.30 |  |  |  | 37.66 |  | 33.40 | [8 empty] | 11.31 |  |  |  |  | 1.82
1995 |  |  |  | 4745.36 |  |  | 7708 |  |  |  | 925 | [10 empty] | 59.79 |  |  |  | 90.79 | [5 empty] | 58.56 |  |  | 87.99 |  |  |  | 0.91 |  | 0.83 | [8 empty] | 8.38 |  |  |  |  | 31.00
1996 |  |  |  | 4196.12 |  |  | 7099 |  |  |  | 925 | [10 empty] | 52.69 |  |  |  | 52.84 | [5 empty] | 51.64 |  |  | 80.82 |  |  |  | 7.80 |  | 4.47 | [8 empty] | 42.69 |  |  |  |  | 0.15
1997 |  |  |  | 4354.28 |  |  | 7076 |  |  |  | 925 | [10 empty] | 54.94 |  |  |  | 55.26 | [5 empty] | 53.74 |  |  | 80.78 |  |  |  | 7.36 |  | 4.39 | [8 empty] | 40.36 |  |  |  |  | 0.32
1998 |  |  |  | 1685.05 |  |  | 2805 |  |  |  | 925 | [10 empty] | 21.30 |  |  |  | 21.71 | [5 empty] | 20.80 |  |  | 32.02 |  |  |  | 5.62 |  | 1.29 | [8 empty] | 77.00 |  |  |  |  | 0.41
1999 |  |  |  | 3708.09 |  |  | 6066 |  |  |  | 925 | [10 empty] | 46.84 |  |  |  | 48.03 | [5 empty] | 45.76 |  |  | 69.25 |  |  |  | 4.72 |  | 2.38 | [8 empty] | 49.59 |  |  |  |  | 1.19
2000 |  |  |  | 3668.06 |  |  | 6211 |  |  |  | 925 | [10 empty] | 46.19 |  |  |  | 48.87 | [5 empty] | 45.14 |  |  | 70.71 |  |  |  | 3.97 |  | 2.02 | [8 empty] | 49.11 |  |  |  |  | 2.68
2001 |  |  |  | 4768.15 |  |  | 7667 |  |  |  | 925 | [10 empty] | 60.09 |  |  |  | 61.11 | [5 empty] | 58.84 |  |  | 87.52 |  |  |  | 0.33 |  | 0.20 | [8 empty] | 38.69 |  |  |  |  | 1.02
2002 |  |  |  | 3027.77 |  |  | 4770 |  |  |  | 925 | [10 empty] | 38.07 |  |  |  | 38.25 | [5 empty] | 37.37 |  |  | 54.45 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 61.75 |  |  |  |  | 0.19
2003 |  |  |  | 3756.24 |  |  | 5834 |  |  |  | 925 | [10 empty] | 46.36 |  |  |  | 47.10 | [5 empty] | 46.36 |  |  | 66.60 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 52.90 |  |  |  |  | 0.74
2004 |  |  |  | 3692.07 |  |  | 4318 |  |  |  | 925 | [10 empty] | 44.97 |  |  |  | 45.06 | [5 empty] | 45.44 |  |  | 49.16 |  |  |  | 3.87 |  | 1.82 | [8 empty] | 53.13 |  |  |  |  | 0.09
2005 |  |  |  | 6896.62 |  |  | 7782 |  |  |  | 925 | [10 empty] | 84.68 |  |  |  | 87.51 | [5 empty] | 85.10 |  |  | 88.83 |  |  |  | 0.58 |  | 0.51 | [8 empty] | 11.98 |  |  |  |  | 2.83
2006 |  |  |  | 6574.42 |  |  | 7320 |  |  |  | 925 | [10 empty] | 80.34 |  |  |  | 82.92 | [5 empty] | 81.14 |  |  | 83.56 |  |  |  | 1.28 |  | 1.07 | [8 empty] | 16.01 |  |  |  |  | 2.58
2007 |  |  |  | 5728.65 |  |  | 6207 |  |  |  | 925 | [10 empty] | 69.48 |  |  |  | 69.99 | [5 empty] | 70.70 |  |  | 70.86 |  |  |  | 1.70 |  | 1.21 | [8 empty] | 28.80 |  |  |  |  | 0.51
2008 |  |  |  | 6835.74 |  |  | 7351 |  |  |  | 925 | [10 empty] | 82.61 |  |  |  | 82.63 | [5 empty] | 84.13 |  |  | 83.69 |  |  |  | 0.80 |  | 0.66 | [8 empty] | 16.70 |  |  |  |  | 0.03
2009 |  |  |  | 6428.15 |  |  | 6778 |  |  |  | 925 | [10 empty] | 76.64 |  |  |  | 76.67 | [5 empty] | 79.33 |  |  | 77.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 23.33 |  |  |  |  | 0.03
2010 |  |  |  | 7448.67 |  |  | 8076 |  |  |  | 925 | [10 empty] | 87.81 |  |  |  | 88.09 | [5 empty] | 91.92 |  |  | 92.19 |  |  |  | 1.15 |  | 1.03 | [8 empty] | 10.88 |  |  |  |  | 0.28
2011 |  |  |  | 6368.67 |  |  | 6539 |  |  |  | 925 | [10 empty] | 75.31 |  |  |  | 75.39 | [5 empty] | 78.61 |  |  | 74.65 |  |  |  | 1.56 |  | 1.20 | [8 empty] | 23.41 |  |  |  |  | 0.09
2012 |  |  |  | 7401.98 |  |  | 7802 |  |  |  | 925 | [10 empty] | 87.76 |  |  |  | 88.01 | [5 empty] | 91.10 |  |  | 88.82 |  |  |  | 1.85 |  | 1.66 | [8 empty] | 10.33 |  |  |  |  | 0.25
2013 |  |  |  | 1584.36 |  |  | 1606 |  |  |  | 925 | [10 empty] | 18.25 |  |  |  | 18.25 | [5 empty] | 19.55 |  |  | 18.33 |  |  |  | 0.44 |  | 0.08 | [8 empty] | 81.67 |  |  |  |  | 0.00
2014 |  |  |  | 6299.77 |  |  | 7011 |  |  |  | 925 | [10 empty] | 77.67 |  |  |  | 78.52 | [5 empty] | 77.74 |  |  | 80.03 |  |  |  | 0.54 |  | 0.43 | [8 empty] | 21.05 |  |  |  |  | 0.86
2015 |  |  |  | 6556.20 |  |  | 7160 |  |  |  | 925 | [10 empty] | 79.38 |  |  |  | 80.44 | [5 empty] | 80.91 |  |  | 81.74 |  |  |  | 2.96 |  | 4.25 | [8 empty] | 15.31 |  |  |  |  | 1.06
2016 |  |  |  | 5678.19 |  |  | 6425 |  |  |  | 925 | [10 empty] | 68.85 |  |  |  | 69.57 | [5 empty] | 69.88 |  |  | 73.14 |  |  |  | 3.29 |  | 2.37 | [8 empty] | 28.06 |  |  |  |  | 0.72
2017 |  |  |  | 5437.61 |  |  | 6209 |  |  |  | 925 | [10 empty] | 66.14 |  |  |  | 66.59 | [5 empty] | 67.11 |  |  | 70.88 |  |  |  | 3.75 |  | 7.38 | [8 empty] | 26.03 |  |  |  |  | 0.45
2018 |  |  |  | 4702.96 |  |  | 5689 |  |  |  | 925 | [10 empty] | 56.25 |  |  |  | 56.48 | [5 empty] | 58.04 |  |  | 64.94 |  |  |  | 11.38 |  | 9.58 | [8 empty] | 33.94 |  |  |  |  | 0.22
2019 |  |  |  | 5207.62 |  |  | 5656 |  |  |  | 925 | [10 empty] | 62.03 |  |  |  | 62.17 | [5 empty] | 64.27 |  |  | 64.57 |  |  |  | 2.74 |  | 1.75 | [8 empty] | 36.08 |  |  |  |  | 0.13
2020 |  |  |  | 5532.83 |  |  | 5945 |  |  |  | 925 | [10 empty] | 66.59 |  |  |  | 66.89 | [5 empty] | 68.09 |  |  | 67.68 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 33.10 |  |  |  |  | 0.30
2021 |  |  |  | 5567.70 |  |  | 6162 |  |  |  | 925 | [10 empty] | 68.28 |  |  |  | 69.35 | [5 empty] | 68.71 |  |  | 70.34 |  |  |  | 2.85 |  | 2.04 | [8 empty] | 28.61 |  |  |  |  | 1.07
2022 |  |  |  | 7019.38 |  |  | 7651 |  |  |  | 925 | [10 empty] | 85.77 |  |  |  | 86.45 | [5 empty] | 86.63 |  |  | 87.34 |  |  |  | 0.65 |  | 0.56 | [8 empty] | 12.99 |  |  |  |  | 0.68
2023 |  |  |  | 6196.09 |  |  | 6818 |  |  |  | 925 | [10 empty] | 74.92 |  |  |  | 75.23 | [5 empty] | 76.47 |  |  | 77.83 |  |  |  | 2.54 |  | 1.96 | [8 empty] | 22.81 |  |  |  |  | 0.31
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1979 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 107
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1941 | [14 empty] | 1397
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 582
E. |  | Testing of plant systems or components | [35 empty] | 12
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 93
H. |  | Nuclear regulatory requirements | [39 empty] | 4
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 3
Z. |  | Other | [39 empty] | 27
Subtotal | [22 empty] | 1941 | [14 empty] | 2084 |  |  |  | 141 | [11 empty] | 5
Total | [22 empty] | 1941 | [14 empty] | 2230
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1979 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 41
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 16
16. |  |  | Steam generation systems | [34 empty] | 3
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 6
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [37 empty] | 106
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-March, June-December. Additional electricity generation amounted to 120580 MWh. The unit was in the unit overhaul from 2023.03.02 to 2023.05.22. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-3
2023 Operating Experience
RU-38 | [8 empty] | KURSK-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1978-04-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1983-10-17
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-03-30
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 40 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 170 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6186.94 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.48 %
Energy Availability Factor (EAF) | [18 empty] | : | 75.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.14 %
Unit Capability Factor (UCF) | [18 empty] | : | 75.96 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 22.9 %
Load Factor (LF) | [18 empty] | : | 76.35 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.44 %
Operating Factor (OF) | [18 empty] | : | 77.77 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1947 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 38.74 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 692.07 | 633.18 |  |  |  | 696.17 |  | 660.22 | [8 empty] | 491.54 |  |  | 0.00 | [6 empty] | 0.00 |  | 318.50 |  |  |  | 658.13 |  |  | 702.83 |  |  | 616.27 | [9 empty] | 718.02 |  |  | 6186.94
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.97 |  | 98.82 | [8 empty] | 72.15 |  |  | 0.00 | [6 empty] | 0.00 |  | 47.96 |  |  |  | 98.99 |  |  | 99.90 |  |  | 90.38 | [9 empty] | 99.94 |  |  | 75.52
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.97 |  | 99.08 | [8 empty] | 74.84 |  |  | 0.00 | [6 empty] | 0.00 |  | 49.19 |  |  |  | 100.00 |  |  | 99.96 |  |  | 90.38 | [9 empty] | 99.94 |  |  | 75.96
LF [%] |  |  |  |  | 100.56 | 101.86 |  |  |  | 101.16 |  | 99.13 | [8 empty] | 71.42 |  |  | 0.00 | [6 empty] | 0.00 |  | 46.28 |  |  |  | 98.82 |  |  | 102.13 |  |  | 92.53 | [9 empty] | 104.33 |  |  | 76.35
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 78.09 |  |  | 0.00 | [6 empty] | 0.00 |  | 63.04 |  |  |  | 100.00 |  |  | 100.00 |  |  | 93.75 | [9 empty] | 100.00 |  |  | 77.77
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.03 |  | 0.92 | [8 empty] | 4.09 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.04 |  |  | 9.57 | [9 empty] | 0.00 |  |  | 1.48
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.03 |  | 0.92 | [8 empty] | 3.19 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.04 |  |  | 9.57 | [9 empty] | 0.00 |  |  | 1.14
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 21.96 |  |  | 100.00 | [6 empty] | 100.00 |  | 50.81 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.06 | [9 empty] | 0.06 |  |  | 22.90
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.25 | [8 empty] | 2.70 |  |  | 0.00 | [6 empty] | 0.00 |  | 1.23 |  |  |  | 1.01 |  |  | 0.06 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.44
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 240876.17 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.69 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.99 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.25 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.23 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.52 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.09 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.24 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.77 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 5479.24 |  |  | 6830 |  |  |  | 925 | [10 empty] | 72.49 |  |  |  | 72.49 | [5 empty] | 72.15 |  |  | 76.71 |  |  |  | 9.02 |  | 7.18 | [8 empty] | 20.33 |  |  |  |  | 0.00
1985 |  |  |  | 6260.75 |  |  | 7250 |  |  |  | 925 | [10 empty] | 77.59 |  |  |  | 77.93 | [5 empty] | 77.26 |  |  | 82.76 |  |  |  | 7.60 |  | 6.41 | [8 empty] | 15.66 |  |  |  |  | 0.34
1986 |  |  |  | 4810.84 |  |  | 6269 |  |  |  | 925 | [10 empty] | 60.00 |  |  |  | 60.42 | [5 empty] | 59.37 |  |  | 71.56 |  |  |  | 15.08 |  | 10.73 | [8 empty] | 28.85 |  |  |  |  | 0.42
1987 |  |  |  | 5458.95 |  |  | 6185 |  |  |  | 1000 | [10 empty] | 66.40 |  |  |  | 69.01 | [5 empty] | 62.32 |  |  | 70.61 |  |  |  | 5.11 |  | 3.71 | [8 empty] | 27.28 |  |  |  |  | 2.61
1988 |  |  |  | 6693.64 |  |  | 7471 |  |  |  | 925 | [10 empty] | 83.64 |  |  |  | 83.64 | [5 empty] | 82.38 |  |  | 85.05 |  |  |  | 3.44 |  | 2.98 | [8 empty] | 13.38 |  |  |  |  | 0.00
1989 |  |  |  | 5900.50 |  |  | 7200 |  |  |  | 925 | [10 empty] | 74.29 |  |  |  | 74.32 | [5 empty] | 72.82 |  |  | 82.19 |  |  |  | 8.84 |  | 7.21 | [8 empty] | 18.48 |  |  |  |  | 0.03
1990 |  |  |  | 6889.42 |  |  | 8096 |  |  |  | 925 | [10 empty] | 86.52 |  |  |  | 86.52 | [5 empty] | 85.02 |  |  | 92.42 |  |  |  | 7.78 |  | 7.30 | [8 empty] | 6.18 |  |  |  |  | 0.00
1991 |  |  |  | 5138.96 |  |  | 5704 |  |  |  | 925 | [10 empty] | 63.17 |  |  |  | 63.42 | [5 empty] | 63.42 |  |  | 65.11 |  |  |  | 1.30 |  | 0.83 | [8 empty] | 35.74 |  |  |  |  | 0.25
1992 |  |  |  | 6630.50 |  |  | 8126 |  |  |  | 925 | [10 empty] | 82.13 |  |  |  | 82.13 | [5 empty] | 81.61 |  |  | 92.52 |  |  |  | 5.97 |  | 5.22 | [8 empty] | 12.66 |  |  |  |  | 0.00
1993 |  |  |  | 5562.30 |  |  | 6438 |  |  |  | 925 | [10 empty] | 70.34 |  |  |  | 71.22 | [5 empty] | 68.64 |  |  | 73.49 |  |  |  | 8.24 |  | 6.39 | [8 empty] | 22.39 |  |  |  |  | 0.88
1994 |  |  |  | 5077.86 |  |  | 6495 |  |  |  | 925 | [10 empty] | 66.69 |  |  |  | 73.60 | [5 empty] | 62.67 |  |  | 74.14 |  |  |  | 0.74 |  | 0.55 | [8 empty] | 25.84 |  |  |  |  | 6.92
1995 |  |  |  | 5318.13 |  |  | 5974 |  |  |  | 925 | [10 empty] | 65.40 |  |  |  | 65.70 | [5 empty] | 65.63 |  |  | 68.20 |  |  |  | 2.80 |  | 1.90 | [8 empty] | 32.41 |  |  |  |  | 0.30
1996 |  |  |  | 6739.27 |  |  | 7383 |  |  |  | 925 | [10 empty] | 82.67 |  |  |  | 82.89 | [5 empty] | 82.94 |  |  | 84.05 |  |  |  | 2.36 |  | 2.00 | [8 empty] | 15.11 |  |  |  |  | 0.22
1997 |  |  |  | 6548.72 |  |  | 7325 |  |  |  | 925 | [10 empty] | 81.56 |  |  |  | 82.46 | [5 empty] | 80.82 |  |  | 83.62 |  |  |  | 0.21 |  | 0.17 | [8 empty] | 17.37 |  |  |  |  | 0.89
1998 |  |  |  | 4528.32 |  |  | 5405 |  |  |  | 925 | [10 empty] | 56.53 |  |  |  | 60.26 | [5 empty] | 55.88 |  |  | 61.70 |  |  |  | 17.21 |  | 12.53 | [8 empty] | 27.20 |  |  |  |  | 3.74
1999 |  |  |  | 6006.85 |  |  | 6749 |  |  |  | 925 | [10 empty] | 74.33 |  |  |  | 75.32 | [5 empty] | 74.13 |  |  | 77.04 |  |  |  | 4.80 |  | 3.80 | [8 empty] | 20.87 |  |  |  |  | 0.99
2000 |  |  |  | 6382.33 |  |  | 7415 |  |  |  | 925 | [10 empty] | 78.26 |  |  |  | 78.85 | [5 empty] | 78.55 |  |  | 84.41 |  |  |  | 7.98 |  | 6.83 | [8 empty] | 14.32 |  |  |  |  | 0.59
2001 |  |  |  | 3535.20 |  |  | 3948 |  |  |  | 925 | [10 empty] | 43.53 |  |  |  | 44.65 | [5 empty] | 43.63 |  |  | 45.07 |  |  |  | 0.15 |  | 0.07 | [8 empty] | 55.28 |  |  |  |  | 1.12
2002 |  |  |  | 6699.77 |  |  | 7788 |  |  |  | 925 | [10 empty] | 85.07 |  |  |  | 88.23 | [5 empty] | 82.68 |  |  | 88.90 |  |  |  | 0.29 |  | 0.26 | [8 empty] | 11.51 |  |  |  |  | 3.16
2003 |  |  |  | 5100.59 |  |  | 5469 |  |  |  | 925 | [10 empty] | 61.84 |  |  |  | 62.23 | [5 empty] | 62.95 |  |  | 62.43 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 37.77 |  |  |  |  | 0.39
2004 |  |  |  | 6894.20 |  |  | 7660 |  |  |  | 925 | [10 empty] | 84.35 |  |  |  | 86.33 | [5 empty] | 84.85 |  |  | 87.20 |  |  |  | 0.82 |  | 0.71 | [8 empty] | 12.96 |  |  |  |  | 1.98
2005 |  |  |  | 4987.10 |  |  | 5598 |  |  |  | 925 | [10 empty] | 61.31 |  |  |  | 63.49 | [5 empty] | 61.55 |  |  | 63.90 |  |  |  | 0.59 |  | 0.37 | [8 empty] | 36.14 |  |  |  |  | 2.17
2006 |  |  |  | 6711.22 |  |  | 7353 |  |  |  | 925 | [10 empty] | 81.93 |  |  |  | 83.37 | [5 empty] | 82.82 |  |  | 83.94 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 16.63 |  |  |  |  | 1.44
2007 |  |  |  | 5765.28 |  |  | 6535 |  |  |  | 925 | [10 empty] | 71.07 |  |  |  | 73.75 | [5 empty] | 71.15 |  |  | 74.60 |  |  |  | 1.12 |  | 0.84 | [8 empty] | 25.41 |  |  |  |  | 2.68
2008 |  |  |  | 2117.39 |  |  | 2374 |  |  |  | 925 | [10 empty] | 26.82 |  |  |  | 26.82 | [5 empty] | 26.06 |  |  | 27.03 |  |  |  | 1.30 |  | 0.35 | [8 empty] | 72.83 |  |  |  |  | 0.00
2009 |  |  |  | 7620.95 |  |  | 8216 |  |  |  | 925 | [10 empty] | 93.77 |  |  |  | 93.87 | [5 empty] | 94.05 |  |  | 93.79 |  |  |  | 0.58 |  | 0.55 | [8 empty] | 5.58 |  |  |  |  | 0.10
2010 |  |  |  | 6048.61 |  |  | 6352 |  |  |  | 925 | [10 empty] | 71.67 |  |  |  | 71.78 | [5 empty] | 74.65 |  |  | 72.51 |  |  |  | 1.44 |  | 1.05 | [8 empty] | 27.17 |  |  |  |  | 0.11
2011 |  |  |  | 7574.35 |  |  | 8228 |  |  |  | 925 | [10 empty] | 90.44 |  |  |  | 90.80 | [5 empty] | 93.49 |  |  | 93.94 |  |  |  | 3.77 |  | 3.56 | [8 empty] | 5.64 |  |  |  |  | 0.36
2012 |  |  |  | 6207.22 |  |  | 6900 |  |  |  | 925 | [10 empty] | 74.78 |  |  |  | 75.44 | [5 empty] | 76.39 |  |  | 78.55 |  |  |  | 5.35 |  | 7.58 | [8 empty] | 16.98 |  |  |  |  | 0.66
2013 |  |  |  | 7264.06 |  |  | 8022 |  |  |  | 925 | [10 empty] | 87.02 |  |  |  | 87.23 | [5 empty] | 89.65 |  |  | 91.58 |  |  |  | 5.04 |  | 4.63 | [8 empty] | 8.14 |  |  |  |  | 0.21
2014 |  |  |  | 6969.97 |  |  | 7506 |  |  |  | 925 | [10 empty] | 84.29 |  |  |  | 84.49 | [5 empty] | 86.01 |  |  | 85.68 |  |  |  | 0.85 |  | 4.03 | [8 empty] | 11.48 |  |  |  |  | 0.21
2015 |  |  |  | 7338.33 |  |  | 8075 |  |  |  | 925 | [10 empty] | 89.24 |  |  |  | 89.93 | [5 empty] | 90.56 |  |  | 92.18 |  |  |  | 1.22 |  | 1.11 | [8 empty] | 8.97 |  |  |  |  | 0.68
2016 |  |  |  | 7001.08 |  |  | 7556 |  |  |  | 925 | [10 empty] | 84.05 |  |  |  | 85.12 | [5 empty] | 86.17 |  |  | 86.02 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 14.88 |  |  |  |  | 1.07
2017 |  |  |  | 7405.52 |  |  | 8018 |  |  |  | 925 | [10 empty] | 90.09 |  |  |  | 90.92 | [5 empty] | 91.39 |  |  | 91.53 |  |  |  | 0.10 |  | 0.09 | [8 empty] | 9.00 |  |  |  |  | 0.83
2018 |  |  |  | 6346.60 |  |  | 7060 |  |  |  | 925 | [10 empty] | 76.64 |  |  |  | 77.41 | [5 empty] | 78.32 |  |  | 80.59 |  |  |  | 4.10 |  | 8.89 | [8 empty] | 13.70 |  |  |  |  | 0.77
2019 |  |  |  | 4990.43 |  |  | 5623 |  |  |  | 925 | [10 empty] | 60.49 |  |  |  | 61.19 | [5 empty] | 61.59 |  |  | 64.19 |  |  |  | 2.25 |  | 2.92 | [8 empty] | 35.90 |  |  |  |  | 0.70
2020 |  |  |  | 6473.17 |  |  | 7464 |  |  |  | 925 | [10 empty] | 78.62 |  |  |  | 80.58 | [5 empty] | 79.67 |  |  | 84.97 |  |  |  | 4.13 |  | 4.32 | [8 empty] | 15.11 |  |  |  |  | 1.96
2021 |  |  |  | 5674.03 |  |  | 6517 |  |  |  | 925 | [10 empty] | 70.44 |  |  |  | 73.85 | [5 empty] | 70.02 |  |  | 74.39 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 26.12 |  |  |  |  | 3.41
2022 |  |  |  | 6036.60 |  |  | 7369 |  |  |  | 925 | [10 empty] | 74.89 |  |  |  | 81.43 | [5 empty] | 74.50 |  |  | 84.12 |  |  |  | 3.05 |  | 2.57 | [8 empty] | 16.01 |  |  |  |  | 6.53
2023 |  |  |  | 6186.94 |  |  | 6813 |  |  |  | 925 | [10 empty] | 75.52 |  |  |  | 75.96 | [5 empty] | 76.35 |  |  | 77.77 |  |  |  | 1.48 |  | 1.14 | [8 empty] | 22.90 |  |  |  |  | 0.44
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1984 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 45 | [14 empty] | 133
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1900 | [14 empty] | 1166
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 642
E. |  | Testing of plant systems or components | [35 empty] | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 8
L. |  | Human factor related | [39 empty] | 1
Subtotal | [22 empty] | 1900 |  |  |  | 45 | [10 empty] | 1809 |  |  |  | 134 | [11 empty] | 8
Total | [22 empty] | 1945 | [14 empty] | 1951
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1984 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 45 | [14 empty] | 22
12. |  |  | Reactor I&C Systems | [34 empty] | 15
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 10
15. |  |  | Reactor Cooling Systems | [34 empty] | 49
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 4
31. |  |  | Turbine and auxiliaries | [34 empty] | 4
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
41. |  |  | Main Generator Systems | [34 empty] | 9
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 45 | [14 empty] | 133
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-April, October-December. Additional electricity generation amounted to 95702 MWh. The unit was in the routine maintenance from 2023.05.25 to 2023.08.12. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## KURSK-4
2023 Operating Experience
RU-39 | [8 empty] | KURSK-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-05-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-12-02
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1986-02-05
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 10000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 167 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6760.71 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.14 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.64 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.95 %
Unit Capability Factor (UCF) | [18 empty] | : | 82.74 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.3 %
Load Factor (LF) | [18 empty] | : | 83.43 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.1 %
Operating Factor (OF) | [18 empty] | : | 84.67 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1343 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 63.62 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 701.66 | 642.99 |  |  |  | 711.60 |  | 687.90 | [8 empty] | 690.16 |  |  | 645.43 | [6 empty] | 592.80 |  | 329.81 |  |  |  | 0.00 |  |  | 354.57 |  |  | 674.99 | [9 empty] | 728.79 |  |  | 6760.71
EAF [%] |  |  |  |  | 99.93 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.05 |  |  | 97.09 | [6 empty] | 87.09 |  | 48.99 |  |  |  | 0.00 |  |  | 50.85 |  |  | 97.48 | [9 empty] | 100.00 |  |  | 81.64
UCF [%] |  |  |  |  | 99.93 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 99.88 | [6 empty] | 92.23 |  | 53.12 |  |  |  | 0.00 |  |  | 50.85 |  |  | 97.48 | [9 empty] | 100.00 |  |  | 82.74
LF [%] |  |  |  |  | 101.96 | 103.44 |  |  |  | 103.40 |  | 103.29 | [8 empty] | 100.28 |  |  | 96.91 | [6 empty] | 86.14 |  | 47.92 |  |  |  | 0.00 |  |  | 51.52 |  |  | 101.35 | [9 empty] | 105.90 |  |  | 83.43
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 94.35 |  | 57.80 |  |  |  | 0.00 |  |  | 64.11 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 84.67
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 7.71 |  | 0.28 |  |  |  | 0.00 |  |  | 1.82 |  |  | 2.52 | [9 empty] | 0.00 |  |  | 1.14
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 7.71 |  | 0.15 |  |  |  | 0.00 |  |  | 0.94 |  |  | 2.52 | [9 empty] | 0.00 |  |  | 0.95
PUF [%] |  |  |  |  | 0.07 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.12 | [6 empty] | 0.05 |  | 46.73 |  |  |  | 100.00 |  |  | 48.21 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 16.30
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.95 |  |  | 2.79 | [6 empty] | 5.15 |  | 4.13 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.10
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 240918.76 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.45 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 77.34 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.04 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.34 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.62 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.16 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.53 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1986 |  |  |  | 6328.54 |  |  | 7574 |  |  |  | 925 | [10 empty] | 80.35 |  |  |  | 80.81 | [5 empty] | 80.28 |  |  | 88.06 |  |  |  | 12.66 |  | 11.71 | [8 empty] | 7.47 |  |  |  |  | 0.46
1987 |  |  |  | 6167.68 |  |  | 6704 |  |  |  | 1000 | [10 empty] | 72.29 |  |  |  | 72.43 | [5 empty] | 70.41 |  |  | 76.53 |  |  |  | 6.80 |  | 5.28 | [8 empty] | 22.29 |  |  |  |  | 0.14
1988 |  |  |  | 6653.03 |  |  | 7390 |  |  |  | 925 | [10 empty] | 81.73 |  |  |  | 81.73 | [5 empty] | 81.88 |  |  | 84.13 |  |  |  | 5.02 |  | 4.32 | [8 empty] | 13.95 |  |  |  |  | 0.01
1989 |  |  |  | 6131.81 |  |  | 6954 |  |  |  | 925 | [10 empty] | 75.98 |  |  |  | 76.02 | [5 empty] | 75.67 |  |  | 79.38 |  |  |  | 4.04 |  | 3.20 | [8 empty] | 20.78 |  |  |  |  | 0.05
1990 |  |  |  | 6050.02 |  |  | 6922 |  |  |  | 925 | [10 empty] | 73.62 |  |  |  | 73.71 | [5 empty] | 74.66 |  |  | 79.02 |  |  |  | 7.62 |  | 6.08 | [8 empty] | 20.21 |  |  |  |  | 0.09
1991 |  |  |  | 7356.07 |  |  | 8469 |  |  |  | 925 | [10 empty] | 90.30 |  |  |  | 92.54 | [5 empty] | 90.78 |  |  | 96.68 |  |  |  | 4.21 |  | 4.06 | [8 empty] | 3.40 |  |  |  |  | 2.24
1992 |  |  |  | 6117.37 |  |  | 7324 |  |  |  | 925 | [10 empty] | 75.44 |  |  |  | 75.44 | [5 empty] | 75.30 |  |  | 83.39 |  |  |  | 2.41 |  | 1.87 | [8 empty] | 22.69 |  |  |  |  | 0.00
1993 |  |  |  | 5638.27 |  |  | 6439 |  |  |  | 925 | [10 empty] | 70.98 |  |  |  | 71.72 | [5 empty] | 69.58 |  |  | 73.50 |  |  |  | 4.54 |  | 3.41 | [8 empty] | 24.87 |  |  |  |  | 0.74
1994 |  |  |  | 5369.44 |  |  | 6255 |  |  |  | 925 | [10 empty] | 66.98 |  |  |  | 71.55 | [5 empty] | 66.26 |  |  | 71.40 |  |  |  | 1.27 |  | 0.92 | [8 empty] | 27.53 |  |  |  |  | 4.57
1995 |  |  |  | 6207.48 |  |  | 7001 |  |  |  | 925 | [10 empty] | 77.02 |  |  |  | 78.61 | [5 empty] | 76.61 |  |  | 79.92 |  |  |  | 3.36 |  | 2.74 | [8 empty] | 18.66 |  |  |  |  | 1.58
1996 |  |  |  | 6590.19 |  |  | 7373 |  |  |  | 925 | [10 empty] | 80.16 |  |  |  | 81.40 | [5 empty] | 81.11 |  |  | 83.94 |  |  |  | 3.23 |  | 2.71 | [8 empty] | 15.89 |  |  |  |  | 1.23
1997 |  |  |  | 5971.68 |  |  | 6664 |  |  |  | 925 | [10 empty] | 73.05 |  |  |  | 73.87 | [5 empty] | 73.70 |  |  | 76.07 |  |  |  | 2.70 |  | 2.05 | [8 empty] | 24.08 |  |  |  |  | 0.82
1998 |  |  |  | 6641.43 |  |  | 7751 |  |  |  | 925 | [10 empty] | 82.33 |  |  |  | 86.66 | [5 empty] | 81.96 |  |  | 88.48 |  |  |  | 1.46 |  | 1.29 | [8 empty] | 12.05 |  |  |  |  | 4.34
1999 |  |  |  | 5895.38 |  |  | 6595 |  |  |  | 925 | [10 empty] | 72.77 |  |  |  | 74.17 | [5 empty] | 72.76 |  |  | 75.29 |  |  |  | 1.02 |  | 0.77 | [8 empty] | 25.06 |  |  |  |  | 1.40
2000 |  |  |  | 6778.77 |  |  | 7423 |  |  |  | 925 | [10 empty] | 82.81 |  |  |  | 83.47 | [5 empty] | 83.43 |  |  | 84.51 |  |  |  | 0.59 |  | 0.50 | [8 empty] | 16.03 |  |  |  |  | 0.66
2001 |  |  |  | 6671.63 |  |  | 7281 |  |  |  | 925 | [10 empty] | 81.52 |  |  |  | 82.20 | [5 empty] | 82.34 |  |  | 83.12 |  |  |  | 0.81 |  | 0.67 | [8 empty] | 17.13 |  |  |  |  | 0.68
2002 |  |  |  | 5530.98 |  |  | 6094 |  |  |  | 925 | [10 empty] | 67.61 |  |  |  | 68.31 | [5 empty] | 68.26 |  |  | 69.57 |  |  |  | 1.54 |  | 1.07 | [8 empty] | 30.62 |  |  |  |  | 0.71
2003 |  |  |  | 6233.39 |  |  | 6802 |  |  |  | 925 | [10 empty] | 75.84 |  |  |  | 77.26 | [5 empty] | 76.93 |  |  | 77.65 |  |  |  | 0.27 |  | 0.21 | [8 empty] | 22.54 |  |  |  |  | 1.42
2004 |  |  |  | 5422.93 |  |  | 6005 |  |  |  | 925 | [10 empty] | 66.70 |  |  |  | 68.02 | [5 empty] | 66.74 |  |  | 68.36 |  |  |  | 0.27 |  | 0.18 | [8 empty] | 31.80 |  |  |  |  | 1.32
2005 |  |  |  | 7081.14 |  |  | 7858 |  |  |  | 925 | [10 empty] | 87.15 |  |  |  | 89.43 | [5 empty] | 87.38 |  |  | 89.69 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.57 |  |  |  |  | 2.28
2006 |  |  |  | 3636.44 |  |  | 4115 |  |  |  | 925 | [10 empty] | 44.24 |  |  |  | 44.77 | [5 empty] | 44.88 |  |  | 46.97 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 55.23 |  |  |  |  | 0.53
2007 |  |  |  | 7426.50 |  |  | 8298 |  |  |  | 925 | [10 empty] | 91.23 |  |  |  | 94.27 | [5 empty] | 91.65 |  |  | 94.73 |  |  |  | 0.19 |  | 0.18 | [8 empty] | 5.54 |  |  |  |  | 3.04
2008 |  |  |  | 6052.40 |  |  | 6580 |  |  |  | 925 | [10 empty] | 73.94 |  |  |  | 74.87 | [5 empty] | 74.49 |  |  | 74.91 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 25.13 |  |  |  |  | 0.93
2009 |  |  |  | 4184.28 |  |  | 4786 |  |  |  | 925 | [10 empty] | 52.34 |  |  |  | 52.46 | [5 empty] | 51.64 |  |  | 54.63 |  |  |  | 1.38 |  | 0.73 | [8 empty] | 46.81 |  |  |  |  | 0.12
2010 |  |  |  | 7557.08 |  |  | 8109 |  |  |  | 925 | [10 empty] | 91.31 |  |  |  | 91.65 | [5 empty] | 93.26 |  |  | 92.57 |  |  |  | 2.88 |  | 2.72 | [8 empty] | 5.62 |  |  |  |  | 0.35
2011 |  |  |  | 5500.69 |  |  | 5729 |  |  |  | 925 | [10 empty] | 64.46 |  |  |  | 64.51 | [5 empty] | 67.89 |  |  | 65.41 |  |  |  | 4.61 |  | 3.12 | [8 empty] | 32.37 |  |  |  |  | 0.05
2012 |  |  |  | 7470.41 |  |  | 8144 |  |  |  | 925 | [10 empty] | 89.18 |  |  |  | 89.36 | [5 empty] | 91.94 |  |  | 92.71 |  |  |  | 2.11 |  | 1.93 | [8 empty] | 8.72 |  |  |  |  | 0.18
2013 |  |  |  | 6213.89 |  |  | 6807 |  |  |  | 925 | [10 empty] | 74.33 |  |  |  | 74.78 | [5 empty] | 76.69 |  |  | 77.71 |  |  |  | 1.12 |  | 0.85 | [8 empty] | 24.37 |  |  |  |  | 0.46
2014 |  |  |  | 7517.80 |  |  | 8201 |  |  |  | 925 | [10 empty] | 89.67 |  |  |  | 90.11 | [5 empty] | 92.78 |  |  | 93.62 |  |  |  | 2.44 |  | 2.26 | [8 empty] | 7.64 |  |  |  |  | 0.44
2015 |  |  |  | 6745.34 |  |  | 7348 |  |  |  | 925 | [10 empty] | 81.17 |  |  |  | 82.83 | [5 empty] | 83.24 |  |  | 83.88 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 17.11 |  |  |  |  | 1.67
2016 |  |  |  | 7420.59 |  |  | 8055 |  |  |  | 925 | [10 empty] | 88.67 |  |  |  | 90.08 | [5 empty] | 91.33 |  |  | 91.70 |  |  |  | 0.76 |  | 0.69 | [8 empty] | 9.23 |  |  |  |  | 1.40
2017 |  |  |  | 6940.86 |  |  | 7471 |  |  |  | 925 | [10 empty] | 83.55 |  |  |  | 83.71 | [5 empty] | 85.66 |  |  | 85.29 |  |  |  | 2.08 |  | 1.78 | [8 empty] | 14.52 |  |  |  |  | 0.15
2018 |  |  |  | 7117.30 |  |  | 7645 |  |  |  | 925 | [10 empty] | 85.95 |  |  |  | 86.70 | [5 empty] | 87.84 |  |  | 87.27 |  |  |  | 3.14 |  | 2.81 | [8 empty] | 10.49 |  |  |  |  | 0.75
2019 |  |  |  | 6538.38 |  |  | 7095 |  |  |  | 925 | [10 empty] | 79.38 |  |  |  | 80.03 | [5 empty] | 80.69 |  |  | 80.99 |  |  |  | 2.71 |  | 2.99 | [8 empty] | 16.98 |  |  |  |  | 0.65
2020 |  |  |  | 7277.83 |  |  | 7991 |  |  |  | 925 | [10 empty] | 88.64 |  |  |  | 89.46 | [5 empty] | 89.57 |  |  | 90.97 |  |  |  | 0.62 |  | 0.56 | [8 empty] | 9.98 |  |  |  |  | 0.81
2021 |  |  |  | 6292.87 |  |  | 6865 |  |  |  | 925 | [10 empty] | 76.86 |  |  |  | 77.33 | [5 empty] | 77.66 |  |  | 78.37 |  |  |  | 1.79 |  | 1.41 | [8 empty] | 21.26 |  |  |  |  | 0.47
2022 |  |  |  | 5672.23 |  |  | 6628 |  |  |  | 925 | [10 empty] | 68.23 |  |  |  | 68.49 | [5 empty] | 70.00 |  |  | 75.66 |  |  |  | 0.11 |  | 2.17 | [8 empty] | 29.34 |  |  |  |  | 0.26
2023 |  |  |  | 6760.71 |  |  | 7417 |  |  |  | 925 | [10 empty] | 81.64 |  |  |  | 82.74 | [5 empty] | 83.43 |  |  | 84.67 |  |  |  | 1.14 |  | 0.95 | [8 empty] | 16.30 |  |  |  |  | 1.10
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1986 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 42 | [14 empty] | 69
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1301 | [14 empty] | 1182
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 372
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 72
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [39 empty] | 5
Subtotal | [22 empty] | 1301 |  |  |  | 42 | [10 empty] | 1626 |  |  |  | 79 | [11 empty] | 1
Total | [22 empty] | 1343 | [14 empty] | 1706
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1986 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 8
12. |  |  | Reactor I&C Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 13
16. |  |  | Steam generation systems | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [19 empty] | 42 | [14 empty] | 7
33. |  |  | Circulating Water System | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 22
Total | [22 empty] | 42 | [14 empty] | 69
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-May, October-December. Additional electricity generation amounted to 148610 MWh. The unit was in the intermediate maintenance outage from 2023.08.18 to 2023.10.12. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD 2-1
2023 Operating Experience
RU-163 | [8 empty] | LENINGRAD 2-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-491 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-10-25
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-03-09
Gross electrical power | [12 empty] | : |  |  | 1188 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-10-29
Reference unit power (net) | [12 empty] | : |  |  | 1101 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 4690.9 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 44.41 %
Energy Availability Factor (EAF) | [18 empty] | : | 49.18 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 39.72 %
Unit Capability Factor (UCF) | [18 empty] | : | 49.71 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.57 %
Load Factor (LF) | [18 empty] | : | 48.64 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.53 %
Operating Factor (OF) | [18 empty] | : | 50.19 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 4363 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 814.96 | 92.13 |  |  |  | 374.30 |  | 498.52 | [8 empty] | 343.67 |  |  | 785.06 | [6 empty] | 489.10 |  | 0.00 |  |  |  | 183.12 |  |  | 820.42 |  |  | 289.61 | [9 empty] | 0.00 |  |  | 4690.90
EAF [%] |  |  |  |  | 99.05 | 13.23 |  |  |  | 47.26 |  | 64.33 | [8 empty] | 44.21 |  |  | 98.47 | [6 empty] | 60.32 |  | 0.01 |  |  |  | 24.26 |  |  | 99.49 |  |  | 36.95 | [9 empty] | 0.01 |  |  | 49.18
UCF [%] |  |  |  |  | 100.00 | 14.31 |  |  |  | 47.33 |  | 64.53 | [8 empty] | 44.64 |  |  | 100.00 | [6 empty] | 61.41 |  | 0.01 |  |  |  | 24.72 |  |  | 100.00 |  |  | 37.09 | [9 empty] | 0.01 |  |  | 49.71
LF [%] |  |  |  |  | 99.49 | 12.45 |  |  |  | 45.69 |  | 62.89 | [8 empty] | 41.95 |  |  | 99.03 | [6 empty] | 59.71 |  | 0.00 |  |  |  | 23.10 |  |  | 100.16 |  |  | 36.53 | [9 empty] | 0.00 |  |  | 48.64
OF [%] |  |  |  |  | 100.00 | 14.43 |  |  |  | 54.03 |  | 64.58 | [8 empty] | 42.61 |  |  | 100.00 | [6 empty] | 61.42 |  | 0.00 |  |  |  | 25.56 |  |  | 100.00 |  |  | 37.08 | [9 empty] | 0.00 |  |  | 50.19
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 10.68 |  | 35.47 | [8 empty] | 55.36 |  |  | 0.00 | [6 empty] | 38.59 |  | 99.99 |  |  |  | 75.28 |  |  | 0.00 |  |  | 62.91 | [9 empty] | 99.99 |  |  | 44.41
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 5.66 |  | 35.47 | [8 empty] | 55.36 |  |  | 0.00 | [6 empty] | 38.59 |  | 99.99 |  |  |  | 75.28 |  |  | 0.00 |  |  | 62.91 | [9 empty] | 99.99 |  |  | 39.72
PUF [%] |  |  |  |  | 0.00 | 85.69 |  |  |  | 47.01 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.57
XUF [%] |  |  |  |  | 0.95 | 1.07 |  |  |  | 0.07 |  | 0.20 | [8 empty] | 0.43 |  |  | 1.53 | [6 empty] | 1.10 |  | 0.00 |  |  |  | 0.46 |  |  | 0.51 |  |  | 0.13 | [9 empty] | 0.00 |  |  | 0.53
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 38016.72 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 14.77 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.74 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 13.51 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.75 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.74 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.22 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.01 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 75.15 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 2344.91 |  |  | 3078 |  |  |  | 1085 | [10 empty] | 23.75 |  |  |  | 23.75 | [5 empty] | 20.26 |  |  | 25.14 |  |  |  | 76.25 |  | 76.25 | [8 empty] | 0.00 |  |  |  |  | 0.00
2019 |  |  |  | 7137.13 |  |  | 6666 |  |  |  | 1101 | [10 empty] | 74.35 |  |  |  | 74.93 | [5 empty] | 74.00 |  |  | 76.10 |  |  |  | 8.67 |  | 9.99 | [8 empty] | 15.09 |  |  |  |  | 0.57
2020 |  |  |  | 7530.82 |  |  | 7037 |  |  |  | 1101 | [10 empty] | 82.64 |  |  |  | 83.44 | [5 empty] | 77.87 |  |  | 80.11 |  |  |  | 0.18 |  | 0.15 | [8 empty] | 16.41 |  |  |  |  | 0.80
2021 |  |  |  | 8598.45 |  |  | 8324 |  |  |  | 1101 | [10 empty] | 90.52 |  |  |  | 92.65 | [5 empty] | 89.15 |  |  | 95.02 |  |  |  | 3.11 |  | 2.98 | [8 empty] | 4.38 |  |  |  |  | 2.12
2022 |  |  |  | 7714.52 |  |  | 7241 |  |  |  | 1101 | [10 empty] | 80.22 |  |  |  | 81.40 | [5 empty] | 79.99 |  |  | 82.66 |  |  |  | 5.16 |  | 4.42 | [8 empty] | 14.17 |  |  |  |  | 1.18
2023 |  |  |  | 4690.90 |  |  | 4397 |  |  |  | 1101 | [10 empty] | 49.18 |  |  |  | 49.71 | [5 empty] | 48.64 |  |  | 50.19 |  |  |  | 44.41 |  | 39.72 | [8 empty] | 10.57 |  |  |  |  | 0.53
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2018 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 3450 | [14 empty] | 1203
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 918 | [14 empty] | 948
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 47
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 62
Subtotal | [22 empty] | 918 |  |  |  | 3450 | [10 empty] | 995 |  |  |  | 1203 | [11 empty] | 62
Total | [22 empty] | 4368 | [14 empty] | 2260
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2018 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [19 empty] | 196 | [14 empty] | 72
31. |  |  | Turbine and auxiliaries | [19 empty] | 1569 | [14 empty] | 393
32. |  |  | Feedwater and Main Steam System | [34 empty] | 95
33. |  |  | Circulating Water System | [34 empty] | 5
41. |  |  | Main Generator Systems | [19 empty] | 1685 | [14 empty] | 498
42. |  |  | Electrical Power Supply Systems | [34 empty] | 1
Total | [22 empty] | 3450 | [14 empty] | 1064
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Federal Tariffs Service. The unit was in the intermediate maintenance outage from 2023.02.05 to 2023.03.15. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD 2-2
2023 Operating Experience
RU-164 | [8 empty] | LENINGRAD 2-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-491 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-04-15
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-10-22
Gross electrical power | [12 empty] | : |  |  | 1188 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-03-18
Reference unit power (net) | [12 empty] | : |  |  | 1101 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8555.51 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 6.13 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.29 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 6.22 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.89 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 3.89 %
Load Factor (LF) | [18 empty] | : | 88.71 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.59 %
Operating Factor (OF) | [18 empty] | : | 90.24 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 855 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 399.75 | 696.38 |  |  |  | 719.92 |  | 789.38 | [8 empty] | 641.02 |  |  | 779.31 | [6 empty] | 523.41 |  | 792.55 |  |  |  | 767.77 |  |  | 791.12 |  |  | 787.35 | [9 empty] | 867.57 |  |  | 8555.51
EAF [%] |  |  |  |  | 49.65 | 93.73 |  |  |  | 87.86 |  | 99.29 | [8 empty] | 78.80 |  |  | 97.75 | [6 empty] | 64.89 |  | 96.47 |  |  |  | 97.22 |  |  | 98.69 |  |  | 98.85 | [9 empty] | 98.14 |  |  | 88.29
UCF [%] |  |  |  |  | 50.11 | 95.05 |  |  |  | 88.78 |  | 100.00 | [8 empty] | 79.90 |  |  | 100.00 | [6 empty] | 66.64 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.89
LF [%] |  |  |  |  | 48.80 | 94.12 |  |  |  | 87.89 |  | 99.58 | [8 empty] | 78.26 |  |  | 98.31 | [6 empty] | 63.90 |  | 96.75 |  |  |  | 96.85 |  |  | 96.58 |  |  | 99.32 | [9 empty] | 105.91 |  |  | 88.71
OF [%] |  |  |  |  | 50.81 | 96.13 |  |  |  | 89.52 |  | 100.00 | [8 empty] | 81.05 |  |  | 100.00 | [6 empty] | 67.20 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 90.24
FLR [%] |  |  |  |  | 0.00 | 4.95 |  |  |  | 11.22 |  | 0.00 | [8 empty] | 20.10 |  |  | 0.00 | [6 empty] | 33.36 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.13
UCL [%] |  |  |  |  | 4.09 | 4.95 |  |  |  | 11.22 |  | 0.00 | [8 empty] | 20.10 |  |  | 0.00 | [6 empty] | 33.36 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 6.22
PUF [%] |  |  |  |  | 45.80 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 3.89
XUF [%] |  |  |  |  | 0.46 | 1.31 |  |  |  | 0.92 |  | 0.71 | [8 empty] | 1.10 |  |  | 2.25 | [6 empty] | 1.74 |  | 3.53 |  |  |  | 2.78 |  |  | 1.31 |  |  | 1.15 | [9 empty] | 1.86 |  |  | 1.59
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 25087.26 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.53 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.46 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.28 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.1 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.62 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.82 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.65 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.54 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2021 |  |  |  | 8361.90 |  |  | 7935 |  |  |  | 1101 | [10 empty] | 88.43 |  |  |  | 90.96 | [5 empty] | 88.87 |  |  | 91.67 |  |  |  | 2.03 |  | 1.88 | [8 empty] | 7.16 |  |  |  |  | 2.53
2022 |  |  |  | 7510.31 |  |  | 6919 |  |  |  | 1101 | [10 empty] | 77.62 |  |  |  | 78.66 | [5 empty] | 77.87 |  |  | 78.98 |  |  |  | 1.74 |  | 1.39 | [8 empty] | 19.95 |  |  |  |  | 1.04
2023 |  |  |  | 8555.51 |  |  | 7905 |  |  |  | 1101 | [10 empty] | 88.29 |  |  |  | 89.89 | [5 empty] | 88.71 |  |  | 90.24 |  |  |  | 6.13 |  | 6.22 | [8 empty] | 3.89 |  |  |  |  | 1.59
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2021 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 505 | [14 empty] | 267
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 336 | [14 empty] | 816
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 104
Z. |  | Other | [24 empty] | 30 | [14 empty] | 11
Subtotal | [22 empty] | 336 |  |  |  | 535 | [10 empty] | 920 |  |  |  | 278
Total | [22 empty] | 871 | [14 empty] | 1198
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2021 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 127 | [14 empty] | 42
15. |  |  | Reactor Cooling Systems | [34 empty] | 40
16. |  |  | Steam generation systems | [19 empty] | 37 | [14 empty] | 12
31. |  |  | Turbine and auxiliaries | [19 empty] | 41 | [14 empty] | 26
41. |  |  | Main Generator Systems | [19 empty] | 301 | [14 empty] | 122
42. |  |  | Electrical Power Supply Systems | [34 empty] | 2
Total | [22 empty] | 506 | [14 empty] | 244
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. The unit was in the intermediate maintenance outage from 2023.01.01 to 2023.01.15. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD-3
2023 Operating Experience
RU-34 | [8 empty] | LENINGRAD-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-12-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1979-12-07
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-06-29
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 211 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6419.76 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.04 %
Energy Availability Factor (EAF) | [18 empty] | : | 78.53 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.03 %
Unit Capability Factor (UCF) | [18 empty] | : | 78.64 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 21.33 %
Load Factor (LF) | [18 empty] | : | 79.23 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.11 %
Operating Factor (OF) | [18 empty] | : | 79.63 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1784 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 69.19 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 701.41 | 632.93 |  |  |  | 696.82 |  | 526.41 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 432.85 |  | 684.48 |  |  |  | 655.46 |  |  | 703.50 |  |  | 680.90 | [9 empty] | 705.00 |  |  | 6419.76
EAF [%] |  |  |  |  | 99.67 | 100.00 |  |  |  | 99.99 |  | 79.67 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 64.60 |  | 99.38 |  |  |  | 99.96 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.53
UCF [%] |  |  |  |  | 99.67 | 100.00 |  |  |  | 99.99 |  | 79.67 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 65.25 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 78.64
LF [%] |  |  |  |  | 101.92 | 101.82 |  |  |  | 101.25 |  | 79.04 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 62.90 |  | 99.46 |  |  |  | 98.42 |  |  | 102.22 |  |  | 102.24 | [9 empty] | 102.44 |  |  | 79.23
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 83.33 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 73.12 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 79.63
FLR [%] |  |  |  |  | 0.33 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.04
UCL [%] |  |  |  |  | 0.33 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.01 |  | 20.33 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 34.75 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 21.33
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.65 |  | 0.62 |  |  |  | 0.04 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.11
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 259763.95 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.59 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 73.78 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.76 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 74.6 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 22.64 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 72.82 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.82 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 76.51 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 5345.39 |  |  | 7504 |  |  |  | 925 | [10 empty] | 81.59 |  |  |  | 81.61 | [5 empty] | 80.55 |  |  | 90.94 |  |  |  | 10.86 |  | 9.95 | [8 empty] | 8.45 |  |  |  |  | 0.02
1981 |  |  |  | 6553.56 |  |  | 7528 |  |  |  | 925 | [10 empty] | 81.35 |  |  |  | 81.66 | [5 empty] | 80.88 |  |  | 85.94 |  |  |  | 9.31 |  | 8.38 | [8 empty] | 9.96 |  |  |  |  | 0.32
1982 |  |  |  | 6413.26 |  |  | 7448 |  |  |  | 925 | [10 empty] | 80.27 |  |  |  | 80.80 | [5 empty] | 79.15 |  |  | 85.02 |  |  |  | 7.18 |  | 6.25 | [8 empty] | 12.95 |  |  |  |  | 0.53
1983 |  |  |  | 5708.44 |  |  | 6809 |  |  |  | 925 | [10 empty] | 70.90 |  |  |  | 71.30 | [5 empty] | 70.45 |  |  | 77.73 |  |  |  | 7.88 |  | 6.10 | [8 empty] | 22.61 |  |  |  |  | 0.39
1984 |  |  |  | 7214.95 |  |  | 8060 |  |  |  | 925 | [10 empty] | 89.22 |  |  |  | 89.76 | [5 empty] | 88.80 |  |  | 91.76 |  |  |  | 1.88 |  | 1.72 | [8 empty] | 8.52 |  |  |  |  | 0.55
1985 |  |  |  | 6831.90 |  |  | 7835 |  |  |  | 925 | [10 empty] | 84.94 |  |  |  | 85.42 | [5 empty] | 84.31 |  |  | 89.44 |  |  |  | 5.45 |  | 4.92 | [8 empty] | 9.67 |  |  |  |  | 0.47
1986 |  |  |  | 6890.93 |  |  | 7935 |  |  |  | 925 | [10 empty] | 85.89 |  |  |  | 86.44 | [5 empty] | 85.04 |  |  | 90.58 |  |  |  | 3.36 |  | 3.01 | [8 empty] | 10.55 |  |  |  |  | 0.55
1987 |  |  |  | 6010.31 |  |  | 6362 |  |  |  | 1000 | [10 empty] | 69.36 |  |  |  | 70.37 | [5 empty] | 68.61 |  |  | 72.63 |  |  |  | 1.12 |  | 0.79 | [8 empty] | 28.83 |  |  |  |  | 1.01
1988 |  |  |  | 6951.74 |  |  | 7885 |  |  |  | 925 | [10 empty] | 86.53 |  |  |  | 86.53 | [5 empty] | 85.56 |  |  | 89.77 |  |  |  | 1.44 |  | 1.26 | [8 empty] | 12.21 |  |  |  |  | 0.00
1989 |  |  |  | 6938.14 |  |  | 7455 |  |  |  | 925 | [10 empty] | 85.86 |  |  |  | 86.23 | [5 empty] | 85.62 |  |  | 85.10 |  |  |  | 0.97 |  | 0.84 | [8 empty] | 12.93 |  |  |  |  | 0.37
1990 |  |  |  | 7531.93 |  |  | 8280 |  |  |  | 925 | [10 empty] | 92.35 |  |  |  | 92.96 | [5 empty] | 92.95 |  |  | 94.52 |  |  |  | 1.36 |  | 1.28 | [8 empty] | 5.76 |  |  |  |  | 0.61
1991 |  |  |  | 6506.60 |  |  | 7197 |  |  |  | 925 | [10 empty] | 80.59 |  |  |  | 80.59 | [5 empty] | 80.30 |  |  | 82.16 |  |  |  | 1.25 |  | 1.02 | [8 empty] | 18.39 |  |  |  |  | 0.00
1992 |  |  |  | 5516.63 |  |  | 6122 |  |  |  | 925 | [10 empty] | 68.39 |  |  |  | 68.49 | [5 empty] | 67.90 |  |  | 69.70 |  |  |  | 2.92 |  | 2.06 | [8 empty] | 29.45 |  |  |  |  | 0.09
1993 |  |  |  | 7143.82 |  |  | 7966 |  |  |  | 925 | [10 empty] | 88.90 |  |  |  | 90.14 | [5 empty] | 88.16 |  |  | 90.94 |  |  |  | 0.56 |  | 0.51 | [8 empty] | 9.35 |  |  |  |  | 1.24
1994 |  |  |  | 6631.82 |  |  | 8135 |  |  |  | 925 | [10 empty] | 91.04 |  |  |  | 92.42 | [5 empty] | 81.84 |  |  | 92.87 |  |  |  | 0.26 |  | 0.24 | [8 empty] | 7.34 |  |  |  |  | 1.39
1995 |  |  |  | 3585.96 |  |  | 4332 |  |  |  | 925 | [10 empty] | 46.53 |  |  |  | 49.40 | [5 empty] | 44.25 |  |  | 49.45 |  |  |  | 0.44 |  | 0.22 | [8 empty] | 50.38 |  |  |  |  | 2.87
1996 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1997 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
1998 |  |  |  | 1386.50 |  |  | 1610 |  |  |  | 925 | [10 empty] | 17.41 |  |  |  | 17.49 | [5 empty] | 17.11 |  |  | 18.38 |  |  |  | 4.00 |  | 0.73 | [8 empty] | 81.78 |  |  |  |  | 0.08
1999 |  |  |  | 7853.14 |  |  | 8701 |  |  |  | 925 | [10 empty] | 97.08 |  |  |  | 99.66 | [5 empty] | 96.92 |  |  | 99.33 |  |  |  | 0.34 |  | 0.34 | [8 empty] | 0.00 |  |  |  |  | 2.58
2000 |  |  |  | 6352.80 |  |  | 7169 |  |  |  | 925 | [10 empty] | 78.25 |  |  |  | 79.64 | [5 empty] | 78.19 |  |  | 81.61 |  |  |  | 1.83 |  | 1.49 | [8 empty] | 18.87 |  |  |  |  | 1.39
2001 |  |  |  | 6173.49 |  |  | 7007 |  |  |  | 925 | [10 empty] | 76.58 |  |  |  | 78.92 | [5 empty] | 76.19 |  |  | 79.99 |  |  |  | 0.19 |  | 0.15 | [8 empty] | 20.93 |  |  |  |  | 2.34
2002 |  |  |  | 2514.75 |  |  | 3332 |  |  |  | 925 | [10 empty] | 31.88 |  |  |  | 33.60 | [5 empty] | 31.03 |  |  | 38.04 |  |  |  | 17.29 |  | 7.02 | [8 empty] | 59.38 |  |  |  |  | 1.72
2003 |  |  |  | 6729.17 |  |  | 8100 |  |  |  | 925 | [10 empty] | 84.54 |  |  |  | 86.65 | [5 empty] | 83.05 |  |  | 92.47 |  |  |  | 6.00 |  | 5.53 | [8 empty] | 7.82 |  |  |  |  | 2.11
2004 |  |  |  | 6909.08 |  |  | 8426 |  |  |  | 925 | [10 empty] | 86.47 |  |  |  | 90.86 | [5 empty] | 85.03 |  |  | 95.92 |  |  |  | 5.04 |  | 4.82 | [8 empty] | 4.31 |  |  |  |  | 4.40
2005 |  |  |  | 4447.28 |  |  | 5397 |  |  |  | 925 | [10 empty] | 61.10 |  |  |  | 61.46 | [5 empty] | 54.88 |  |  | 61.60 |  |  |  | 2.72 |  | 1.72 | [8 empty] | 36.83 |  |  |  |  | 0.36
2006 |  |  |  | 7332.11 |  |  | 8274 |  |  |  | 925 | [10 empty] | 89.86 |  |  |  | 89.86 | [5 empty] | 90.49 |  |  | 94.45 |  |  |  | 2.22 |  | 4.89 | [8 empty] | 5.25 |  |  |  |  | 0.00
2007 |  |  |  | 3755.96 |  |  | 4820 |  |  |  | 925 | [10 empty] | 47.04 |  |  |  | 54.08 | [5 empty] | 46.35 |  |  | 55.02 |  |  |  | 0.24 |  | 0.13 | [8 empty] | 45.78 |  |  |  |  | 7.04
2008 |  |  |  | 5013.64 |  |  | 5632 |  |  |  | 925 | [10 empty] | 62.68 |  |  |  | 62.71 | [5 empty] | 61.70 |  |  | 64.12 |  |  |  | 1.64 |  | 7.69 | [8 empty] | 29.60 |  |  |  |  | 0.03
2009 |  |  |  | 5336.12 |  |  | 6209 |  |  |  | 925 | [10 empty] | 70.38 |  |  |  | 70.65 | [5 empty] | 65.85 |  |  | 70.88 |  |  |  | 3.40 |  | 22.58 | [8 empty] | 6.78 |  |  |  |  | 0.26
2010 |  |  |  | 7303.22 |  |  | 8261 |  |  |  | 925 | [10 empty] | 92.58 |  |  |  | 92.88 | [5 empty] | 90.13 |  |  | 94.30 |  |  |  | 1.27 |  | 1.19 | [8 empty] | 5.93 |  |  |  |  | 0.29
2011 |  |  |  | 6803.29 |  |  | 7548 |  |  |  | 925 | [10 empty] | 83.65 |  |  |  | 83.81 | [5 empty] | 83.97 |  |  | 86.17 |  |  |  | 0.47 |  | 1.73 | [8 empty] | 14.46 |  |  |  |  | 0.15
2012 |  |  |  | 7401.44 |  |  | 8115 |  |  |  | 925 | [10 empty] | 91.56 |  |  |  | 91.65 | [5 empty] | 91.09 |  |  | 92.38 |  |  |  | 2.66 |  | 2.51 | [8 empty] | 5.84 |  |  |  |  | 0.10
2013 |  |  |  | 6892.27 |  |  | 7446 |  |  |  | 925 | [10 empty] | 83.65 |  |  |  | 83.95 | [5 empty] | 85.06 |  |  | 85.00 |  |  |  | 1.79 |  | 1.55 | [8 empty] | 14.50 |  |  |  |  | 0.30
2014 |  |  |  | 7199.40 |  |  | 8229 |  |  |  | 925 | [10 empty] | 89.69 |  |  |  | 90.10 | [5 empty] | 88.84 |  |  | 93.93 |  |  |  | 1.79 |  | 4.75 | [8 empty] | 5.15 |  |  |  |  | 0.41
2015 |  |  |  | 6817.12 |  |  | 7628 |  |  |  | 925 | [10 empty] | 86.76 |  |  |  | 86.85 | [5 empty] | 84.13 |  |  | 87.08 |  |  |  | 2.01 |  | 1.78 | [8 empty] | 11.37 |  |  |  |  | 0.09
2016 |  |  |  | 7024.91 |  |  | 7879 |  |  |  | 925 | [10 empty] | 87.77 |  |  |  | 87.94 | [5 empty] | 86.46 |  |  | 89.70 |  |  |  | 2.71 |  | 2.45 | [8 empty] | 9.62 |  |  |  |  | 0.16
2017 |  |  |  | 6786.43 |  |  | 7460 |  |  |  | 925 | [10 empty] | 84.94 |  |  |  | 84.96 | [5 empty] | 83.75 |  |  | 85.16 |  |  |  | 1.87 |  | 1.62 | [8 empty] | 13.42 |  |  |  |  | 0.03
2018 |  |  |  | 5801.48 |  |  | 6257 |  |  |  | 925 | [10 empty] | 72.16 |  |  |  | 72.21 | [5 empty] | 71.60 |  |  | 71.43 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 27.77 |  |  |  |  | 0.05
2019 |  |  |  | 6890.81 |  |  | 7642 |  |  |  | 925 | [10 empty] | 84.69 |  |  |  | 84.85 | [5 empty] | 85.04 |  |  | 87.24 |  |  |  | 0.65 |  | 0.56 | [8 empty] | 14.59 |  |  |  |  | 0.16
2020 |  |  |  | 5765.23 |  |  | 6269 |  |  |  | 925 | [10 empty] | 70.51 |  |  |  | 70.53 | [5 empty] | 70.95 |  |  | 71.37 |  |  |  | 1.02 |  | 0.72 | [8 empty] | 28.75 |  |  |  |  | 0.01
2021 |  |  |  | 5763.58 |  |  | 6496 |  |  |  | 925 | [10 empty] | 72.24 |  |  |  | 72.94 | [5 empty] | 71.13 |  |  | 74.16 |  |  |  | 0.80 |  | 0.59 | [8 empty] | 26.47 |  |  |  |  | 0.70
2022 |  |  |  | 6944.66 |  |  | 7526 |  |  |  | 925 | [10 empty] | 84.93 |  |  |  | 85.20 | [5 empty] | 85.70 |  |  | 85.91 |  |  |  | 0.14 |  | 0.12 | [8 empty] | 14.68 |  |  |  |  | 0.26
2023 |  |  |  | 6419.76 |  |  | 6976 |  |  |  | 925 | [10 empty] | 78.53 |  |  |  | 78.64 | [5 empty] | 79.23 |  |  | 79.63 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 21.33 |  |  |  |  | 0.11
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1980 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 97
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1785 | [14 empty] | 849
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 877
E. |  | Testing of plant systems or components | [35 empty] | 1 |  |  |  | 16
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 121
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 74
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 3
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 12
L. |  | Human factor related | [39 empty] | 3
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 1785 | [14 empty] | 1922 |  |  |  | 117 | [11 empty] | 16
Total | [22 empty] | 1785 | [14 empty] | 2055
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1980 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 9
12. |  |  | Reactor I&C Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 6
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 6
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 51
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
33. |  |  | Circulating Water System | [34 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 15
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 12
Total | [37 empty] | 116
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-April, July-December. Additional electricity generation amounted to 107503 MWh. The unit was in the intermediate maintenance outage from 2023.04.25 to 2023.07.09. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## LENINGRAD-4
2023 Operating Experience
RU-35 | [8 empty] | LENINGRAD-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-02-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-02-09
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-08-29
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 211 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6049.67 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.88 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.49 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.22 %
Unit Capability Factor (UCF) | [18 empty] | : | 74.7 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 23.08 %
Load Factor (LF) | [18 empty] | : | 74.66 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.21 %
Operating Factor (OF) | [18 empty] | : | 75.92 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2109 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 60.52 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 369.68 | 0.00 |  |  |  | 0.00 |  | 425.65 | [8 empty] | 701.22 |  |  | 674.61 | [6 empty] | 668.94 |  | 617.21 |  |  |  | 549.50 |  |  | 670.91 |  |  | 673.98 | [9 empty] | 697.97 |  |  | 6049.67
EAF [%] |  |  |  |  | 52.35 | 0.00 |  |  |  | 0.00 |  | 65.08 | [8 empty] | 100.00 |  |  | 99.82 | [6 empty] | 98.86 |  | 90.29 |  |  |  | 85.54 |  |  | 96.47 |  |  | 99.98 | [9 empty] | 100.00 |  |  | 74.49
UCF [%] |  |  |  |  | 52.35 | 0.00 |  |  |  | 0.00 |  | 65.08 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 90.97 |  |  |  | 85.92 |  |  | 96.56 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 74.70
LF [%] |  |  |  |  | 53.72 | 0.00 |  |  |  | 0.00 |  | 63.91 | [8 empty] | 101.89 |  |  | 101.29 | [6 empty] | 97.20 |  | 89.68 |  |  |  | 82.51 |  |  | 97.49 |  |  | 101.20 | [9 empty] | 101.42 |  |  | 74.66
OF [%] |  |  |  |  | 54.84 | 0.00 |  |  |  | 0.00 |  | 71.81 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 90.99 |  |  |  | 87.92 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 75.92
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 9.03 |  |  |  | 14.08 |  |  | 3.44 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.88
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 9.03 |  |  |  | 14.08 |  |  | 3.44 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.22
PUF [%] |  |  |  |  | 47.65 | 100.00 |  |  |  | 100.00 |  | 34.92 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 23.08
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.18 | [6 empty] | 1.14 |  | 0.67 |  |  |  | 0.38 |  |  | 0.09 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 0.21
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 250407.22 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.94 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 75.02 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.94 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.9 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 21.15 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.25 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.88 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.61 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 3931.27 |  |  | 6151 |  |  |  | 925 | [10 empty] | 76.82 |  |  |  | 76.83 | [5 empty] | 76.06 |  |  | 83.41 |  |  |  | 12.21 |  | 10.69 | [8 empty] | 12.48 |  |  |  |  | 0.01
1982 |  |  |  | 6715.19 |  |  | 7609 |  |  |  | 925 | [10 empty] | 83.59 |  |  |  | 83.72 | [5 empty] | 82.87 |  |  | 86.86 |  |  |  | 4.43 |  | 3.88 | [8 empty] | 12.40 |  |  |  |  | 0.13
1983 |  |  |  | 6844.23 |  |  | 8159 |  |  |  | 925 | [10 empty] | 85.33 |  |  |  | 86.12 | [5 empty] | 84.47 |  |  | 93.14 |  |  |  | 6.80 |  | 6.29 | [8 empty] | 7.59 |  |  |  |  | 0.79
1984 |  |  |  | 6126.32 |  |  | 6803 |  |  |  | 925 | [10 empty] | 74.43 |  |  |  | 74.94 | [5 empty] | 75.40 |  |  | 77.45 |  |  |  | 3.19 |  | 2.47 | [8 empty] | 22.59 |  |  |  |  | 0.52
1985 |  |  |  | 7335.31 |  |  | 8309 |  |  |  | 925 | [10 empty] | 90.92 |  |  |  | 91.18 | [5 empty] | 90.53 |  |  | 94.85 |  |  |  | 3.29 |  | 3.10 | [8 empty] | 5.72 |  |  |  |  | 0.26
1986 |  |  |  | 7060.95 |  |  | 7826 |  |  |  | 925 | [10 empty] | 87.65 |  |  |  | 88.69 | [5 empty] | 87.14 |  |  | 89.34 |  |  |  | 0.49 |  | 0.44 | [8 empty] | 10.87 |  |  |  |  | 1.04
1987 |  |  |  | 7319.23 |  |  | 7530 |  |  |  | 1000 | [10 empty] | 84.15 |  |  |  | 85.01 | [5 empty] | 83.55 |  |  | 85.96 |  |  |  | 2.18 |  | 1.90 | [8 empty] | 13.09 |  |  |  |  | 0.86
1988 |  |  |  | 6050.44 |  |  | 6667 |  |  |  | 925 | [10 empty] | 74.82 |  |  |  | 74.82 | [5 empty] | 74.47 |  |  | 75.90 |  |  |  | 0.72 |  | 0.54 | [8 empty] | 24.64 |  |  |  |  | 0.00
1989 |  |  |  | 7409.69 |  |  | 8185 |  |  |  | 925 | [10 empty] | 91.46 |  |  |  | 91.89 | [5 empty] | 91.44 |  |  | 93.44 |  |  |  | 2.23 |  | 2.10 | [8 empty] | 6.01 |  |  |  |  | 0.43
1990 |  |  |  | 7762.56 |  |  | 8588 |  |  |  | 925 | [10 empty] | 95.38 |  |  |  | 96.06 | [5 empty] | 95.80 |  |  | 98.04 |  |  |  | 2.33 |  | 2.29 | [8 empty] | 1.65 |  |  |  |  | 0.68
1991 |  |  |  | 6130.70 |  |  | 6870 |  |  |  | 925 | [10 empty] | 76.14 |  |  |  | 76.77 | [5 empty] | 75.66 |  |  | 78.42 |  |  |  | 1.77 |  | 1.38 | [8 empty] | 21.85 |  |  |  |  | 0.62
1992 |  |  |  | 5618.11 |  |  | 6617 |  |  |  | 925 | [10 empty] | 70.29 |  |  |  | 70.79 | [5 empty] | 69.15 |  |  | 75.34 |  |  |  | 4.30 |  | 3.18 | [8 empty] | 26.02 |  |  |  |  | 0.51
1993 |  |  |  | 6735.70 |  |  | 7762 |  |  |  | 925 | [10 empty] | 85.27 |  |  |  | 87.61 | [5 empty] | 83.13 |  |  | 88.61 |  |  |  | 1.54 |  | 1.37 | [8 empty] | 11.02 |  |  |  |  | 2.34
1994 |  |  |  | 6167.07 |  |  | 7340 |  |  |  | 925 | [10 empty] | 82.08 |  |  |  | 83.16 | [5 empty] | 76.11 |  |  | 83.79 |  |  |  | 1.33 |  | 1.12 | [8 empty] | 15.72 |  |  |  |  | 1.07
1995 |  |  |  | 6140.97 |  |  | 7270 |  |  |  | 925 | [10 empty] | 82.96 |  |  |  | 86.06 | [5 empty] | 75.79 |  |  | 82.99 |  |  |  | 0.29 |  | 0.25 | [8 empty] | 13.69 |  |  |  |  | 3.11
1996 |  |  |  | 7079.69 |  |  | 8048 |  |  |  | 925 | [10 empty] | 88.30 |  |  |  | 88.78 | [5 empty] | 87.13 |  |  | 91.62 |  |  |  | 4.63 |  | 4.31 | [8 empty] | 6.91 |  |  |  |  | 0.47
1997 |  |  |  | 7644.68 |  |  | 8760 |  |  |  | 925 | [10 empty] | 95.95 |  |  |  | 98.19 | [5 empty] | 94.34 |  |  | 100.00 |  |  |  | 1.81 |  | 1.81 | [8 empty] | 0.00 |  |  |  |  | 2.24
1998 |  |  |  | 3681.98 |  |  | 4341 |  |  |  | 925 | [10 empty] | 45.98 |  |  |  | 47.31 | [5 empty] | 45.44 |  |  | 49.55 |  |  |  | 2.11 |  | 1.02 | [8 empty] | 51.68 |  |  |  |  | 1.32
1999 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2000 |  |  |  | 0.00 |  |  | 0 |  |  |  | 925 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 100.00 |  |  |  |  | 0.00
2001 |  |  |  | 3585.73 |  |  | 4387 |  |  |  | 925 | [10 empty] | 44.56 |  |  |  | 45.54 | [5 empty] | 44.25 |  |  | 50.08 |  |  |  | 23.52 |  | 14.00 | [8 empty] | 40.46 |  |  |  |  | 0.98
2002 |  |  |  | 7528.53 |  |  | 8760 |  |  |  | 925 | [10 empty] | 93.93 |  |  |  | 97.55 | [5 empty] | 92.91 |  |  | 100.00 |  |  |  | 2.45 |  | 2.45 | [8 empty] | 0.00 |  |  |  |  | 3.62
2003 |  |  |  | 1957.16 |  |  | 2399 |  |  |  | 925 | [10 empty] | 24.69 |  |  |  | 26.03 | [5 empty] | 24.15 |  |  | 27.39 |  |  |  | 2.58 |  | 0.69 | [8 empty] | 73.28 |  |  |  |  | 1.35
2004 |  |  |  | 7232.18 |  |  | 8243 |  |  |  | 925 | [10 empty] | 89.58 |  |  |  | 92.27 | [5 empty] | 89.01 |  |  | 93.84 |  |  |  | 3.43 |  | 3.28 | [8 empty] | 4.45 |  |  |  |  | 2.70
2005 |  |  |  | 6730.12 |  |  | 7838 |  |  |  | 925 | [10 empty] | 83.76 |  |  |  | 89.33 | [5 empty] | 83.05 |  |  | 89.46 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 10.57 |  |  |  |  | 5.57
2006 |  |  |  | 5611.94 |  |  | 6197 |  |  |  | 925 | [10 empty] | 69.36 |  |  |  | 69.36 | [5 empty] | 69.26 |  |  | 70.74 |  |  |  | 0.80 |  | 1.36 | [8 empty] | 29.29 |  |  |  |  | 0.00
2007 |  |  |  | 4827.43 |  |  | 5713 |  |  |  | 925 | [10 empty] | 59.73 |  |  |  | 64.85 | [5 empty] | 59.58 |  |  | 65.22 |  |  |  | 3.84 |  | 18.24 | [8 empty] | 16.91 |  |  |  |  | 5.11
2008 |  |  |  | 7526.25 |  |  | 8714 |  |  |  | 925 | [10 empty] | 94.69 |  |  |  | 94.90 | [5 empty] | 92.63 |  |  | 99.20 |  |  |  | 2.93 |  | 2.86 | [8 empty] | 2.24 |  |  |  |  | 0.22
2009 |  |  |  | 4052.83 |  |  | 4695 |  |  |  | 925 | [10 empty] | 53.23 |  |  |  | 53.37 | [5 empty] | 50.02 |  |  | 53.60 |  |  |  | 4.90 |  | 2.75 | [8 empty] | 43.88 |  |  |  |  | 0.14
2010 |  |  |  | 5222.37 |  |  | 5798 |  |  |  | 925 | [10 empty] | 64.04 |  |  |  | 64.18 | [5 empty] | 64.45 |  |  | 66.19 |  |  |  | 3.64 |  | 9.60 | [8 empty] | 26.21 |  |  |  |  | 0.14
2011 |  |  |  | 6589.79 |  |  | 7177 |  |  |  | 925 | [10 empty] | 80.76 |  |  |  | 81.01 | [5 empty] | 81.33 |  |  | 81.94 |  |  |  | 3.53 |  | 4.93 | [8 empty] | 14.06 |  |  |  |  | 0.25
2012 |  |  |  | 7559.92 |  |  | 8254 |  |  |  | 925 | [10 empty] | 92.28 |  |  |  | 92.30 | [5 empty] | 93.04 |  |  | 93.97 |  |  |  | 0.23 |  | 0.52 | [8 empty] | 7.18 |  |  |  |  | 0.02
2013 |  |  |  | 6992.92 |  |  | 7739 |  |  |  | 925 | [10 empty] | 85.84 |  |  |  | 85.93 | [5 empty] | 86.30 |  |  | 88.34 |  |  |  | 2.97 |  | 2.63 | [8 empty] | 11.43 |  |  |  |  | 0.09
2014 |  |  |  | 6942.49 |  |  | 7665 |  |  |  | 925 | [10 empty] | 85.92 |  |  |  | 86.00 | [5 empty] | 85.67 |  |  | 87.49 |  |  |  | 2.03 |  | 2.77 | [8 empty] | 11.23 |  |  |  |  | 0.08
2015 |  |  |  | 6617.16 |  |  | 7414 |  |  |  | 925 | [10 empty] | 85.58 |  |  |  | 85.60 | [5 empty] | 81.66 |  |  | 84.63 |  |  |  | 2.97 |  | 2.62 | [8 empty] | 11.78 |  |  |  |  | 0.02
2016 |  |  |  | 6912.04 |  |  | 7660 |  |  |  | 925 | [10 empty] | 85.43 |  |  |  | 85.45 | [5 empty] | 85.07 |  |  | 87.20 |  |  |  | 0.85 |  | 0.73 | [8 empty] | 13.82 |  |  |  |  | 0.01
2017 |  |  |  | 6846.75 |  |  | 7873 |  |  |  | 925 | [10 empty] | 85.57 |  |  |  | 85.58 | [5 empty] | 84.50 |  |  | 89.87 |  |  |  | 4.04 |  | 4.04 | [8 empty] | 10.39 |  |  |  |  | 0.01
2018 |  |  |  | 6951.25 |  |  | 7499 |  |  |  | 925 | [10 empty] | 84.68 |  |  |  | 84.83 | [5 empty] | 85.79 |  |  | 85.61 |  |  |  | 4.62 |  | 4.11 | [8 empty] | 11.06 |  |  |  |  | 0.15
2019 |  |  |  | 6265.79 |  |  | 6730 |  |  |  | 925 | [10 empty] | 75.83 |  |  |  | 75.83 | [5 empty] | 77.33 |  |  | 76.83 |  |  |  | 0.31 |  | 0.24 | [8 empty] | 23.94 |  |  |  |  | 0.00
2020 |  |  |  | 6842.29 |  |  | 7486 |  |  |  | 925 | [10 empty] | 84.44 |  |  |  | 84.44 | [5 empty] | 84.21 |  |  | 85.22 |  |  |  | 0.42 |  | 0.35 | [8 empty] | 15.20 |  |  |  |  | 0.01
2021 |  |  |  | 5789.70 |  |  | 6585 |  |  |  | 925 | [10 empty] | 72.99 |  |  |  | 73.22 | [5 empty] | 71.45 |  |  | 75.17 |  |  |  | 3.83 |  | 2.91 | [8 empty] | 23.87 |  |  |  |  | 0.23
2022 |  |  |  | 6839.10 |  |  | 7399 |  |  |  | 925 | [10 empty] | 83.47 |  |  |  | 83.51 | [5 empty] | 84.40 |  |  | 84.46 |  |  |  | 0.41 |  | 0.34 | [8 empty] | 16.15 |  |  |  |  | 0.05
2023 |  |  |  | 6049.67 |  |  | 6651 |  |  |  | 925 | [10 empty] | 74.49 |  |  |  | 74.70 | [5 empty] | 74.66 |  |  | 75.92 |  |  |  | 2.88 |  | 2.22 | [8 empty] | 23.08 |  |  |  |  | 0.21
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1981 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 155 | [14 empty] | 87
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1958 | [14 empty] | 1350
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 199
E. |  | Testing of plant systems or components | [39 empty] | 0
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 150
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 95 |  |  |  | 33
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 10
L. |  | Human factor related | [39 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 0
Z. |  | Other | [39 empty] | 18 | [11 empty] | 1
Subtotal | [22 empty] | 1958 |  |  |  | 155 | [10 empty] | 1794 |  |  |  | 139 | [11 empty] | 12
Total | [22 empty] | 2113 | [14 empty] | 1945
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1981 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [19 empty] | 155 | [14 empty] | 24
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 18
16. |  |  | Steam generation systems | [34 empty] | 10
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
33. |  |  | Circulating Water System | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 9
Total | [22 empty] | 155 | [14 empty] | 88
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January, April-December. Additional electricity generation amounted to 74711 MWh. The unit was in the unit overhaul from 2023.01.17 to 2023.04.09. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH 2-1
2023 Operating Experience
RU-161 | [8 empty] | NOVOVORONEZH 2-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-392M | [11 empty] | Construction Date | [15 empty] | : |  |  | 2008-06-24
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2016-08-05
Gross electrical power | [12 empty] | : |  |  | 1180 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2017-02-27
Reference unit power (net) | [12 empty] | : |  |  | 1100 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 7 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6950.52 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 3.35 %
Energy Availability Factor (EAF) | [18 empty] | : | 72.63 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.71 %
Unit Capability Factor (UCF) | [18 empty] | : | 75.62 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 16.66 %
Load Factor (LF) | [18 empty] | : | 72.13 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.99 %
Operating Factor (OF) | [18 empty] | : | 76.22 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2083 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 694.30 | 746.36 |  |  |  | 801.40 |  | 782.09 | [8 empty] | 798.20 |  |  | 766.82 | [6 empty] | 677.83 |  | 652.11 |  |  |  | 744.22 |  |  | 2.04 |  |  | 46.52 | [9 empty] | 238.63 |  |  | 6950.51
EAF [%] |  |  |  |  | 85.30 | 100.00 |  |  |  | 97.96 |  | 98.89 | [8 empty] | 97.56 |  |  | 96.77 | [6 empty] | 83.92 |  | 81.09 |  |  |  | 94.44 |  |  | 0.25 |  |  | 7.92 | [9 empty] | 30.39 |  |  | 72.63
UCF [%] |  |  |  |  | 85.30 | 100.00 |  |  |  | 97.96 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 92.46 |  | 97.06 |  |  |  | 98.06 |  |  | 0.25 |  |  | 8.00 | [9 empty] | 30.88 |  |  | 75.62
LF [%] |  |  |  |  | 84.84 | 100.97 |  |  |  | 97.92 |  | 98.75 | [8 empty] | 97.53 |  |  | 96.82 | [6 empty] | 82.82 |  | 79.68 |  |  |  | 93.97 |  |  | 0.25 |  |  | 5.87 | [9 empty] | 29.16 |  |  | 72.13
OF [%] |  |  |  |  | 86.56 | 100.00 |  |  |  | 98.52 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 92.74 |  | 97.58 |  |  |  | 98.61 |  |  | 0.54 |  |  | 8.89 | [9 empty] | 33.60 |  |  | 76.22
FLR [%] |  |  |  |  | 14.70 | 0.00 |  |  |  | 2.04 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 7.54 |  | 2.94 |  |  |  | 1.94 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 5.52 |  |  | 3.35
UCL [%] |  |  |  |  | 14.70 | 0.00 |  |  |  | 2.04 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 7.54 |  | 2.94 |  |  |  | 1.94 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 61.72 |  |  | 7.71
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 99.75 |  |  | 92.00 | [9 empty] | 7.40 |  |  | 16.66
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 1.11 | [8 empty] | 2.44 |  |  | 3.23 | [6 empty] | 8.54 |  | 15.97 |  |  |  | 3.63 |  |  | 0.00 |  |  | 0.08 | [9 empty] | 0.49 |  |  | 2.99
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 51061.15 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.2 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.21 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.25 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.39 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 14.35 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.9 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.18 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.35 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2017 |  |  |  | 5620.47 |  |  | 6226 |  |  |  | 1114 | [10 empty] | 62.35 |  |  |  | 65.08 | [5 empty] | 60.87 |  |  | 75.08 |  |  |  | 19.08 |  | 15.34 | [8 empty] | 19.58 |  |  |  |  | 2.73
2018 |  |  |  | 7746.87 |  |  | 7378 |  |  |  | 1114 | [10 empty] | 81.34 |  |  |  | 83.60 | [5 empty] | 79.38 |  |  | 84.22 |  |  |  | 5.56 |  | 4.92 | [8 empty] | 11.47 |  |  |  |  | 2.27
2019 |  |  |  | 7186.30 |  |  | 6885 |  |  |  | 1100 | [10 empty] | 76.74 |  |  |  | 77.97 | [5 empty] | 74.58 |  |  | 78.60 |  |  |  | 1.81 |  | 1.44 | [8 empty] | 20.59 |  |  |  |  | 1.22
2020 |  |  |  | 7602.46 |  |  | 7465 |  |  |  | 1100 | [10 empty] | 80.29 |  |  |  | 82.00 | [5 empty] | 78.68 |  |  | 84.98 |  |  |  | 3.44 |  | 4.32 | [8 empty] | 13.67 |  |  |  |  | 1.71
2021 |  |  |  | 7523.13 |  |  | 6953 |  |  |  | 1100 | [10 empty] | 78.81 |  |  |  | 80.41 | [5 empty] | 78.07 |  |  | 79.37 |  |  |  | 4.37 |  | 11.39 | [8 empty] | 8.19 |  |  |  |  | 1.60
2022 |  |  |  | 7558.04 |  |  | 7279 |  |  |  | 1100 | [10 empty] | 79.16 |  |  |  | 81.98 | [5 empty] | 78.44 |  |  | 83.09 |  |  |  | 7.76 |  | 6.89 | [8 empty] | 11.13 |  |  |  |  | 2.81
2023 |  |  |  | 6950.52 |  |  | 6677 |  |  |  | 1100 | [10 empty] | 72.63 |  |  |  | 75.62 | [5 empty] | 72.13 |  |  | 76.22 |  |  |  | 3.35 |  | 7.71 | [8 empty] | 16.66 |  |  |  |  | 2.99
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2017 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 195 | [14 empty] | 319
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1444 | [14 empty] | 1247
Z. |  | Other | [24 empty] | 446 | [14 empty] | 164
Subtotal | [22 empty] | 1444 |  |  |  | 641 | [10 empty] | 1247 |  |  |  | 483
Total | [22 empty] | 2085 | [14 empty] | 1730
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2017 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
14. |  |  | Safety Systems | [34 empty] | 18
16. |  |  | Steam generation systems | [34 empty] | 3
31. |  |  | Turbine and auxiliaries | [34 empty] | 65
32. |  |  | Feedwater and Main Steam System | [34 empty] | 56
33. |  |  | Circulating Water System | [34 empty] | 31
41. |  |  | Main Generator Systems | [19 empty] | 195 | [14 empty] | 139
Total | [22 empty] | 195 | [14 empty] | 312
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-March. Additional electricity generation amounted to 12179 MWh. The unit was in the unit overhaul from 2023.10.01 to 2023.11.15. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH 2-2
2023 Operating Experience
RU-162 | [8 empty] | NOVOVORONEZH 2-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-392M | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-07-12
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2019-05-01
Gross electrical power | [12 empty] | : |  |  | 1181 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2019-10-31
Reference unit power (net) | [12 empty] | : |  |  | 1101 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 4 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8377.15 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.15 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.43 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.82 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.59 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 9.59 %
Load Factor (LF) | [18 empty] | : | 86.86 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.17 %
Operating Factor (OF) | [18 empty] | : | 88.66 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 993 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 827.09 | 748.18 |  |  |  | 820.26 |  | 603.18 | [8 empty] | 0.83 |  |  | 763.08 | [6 empty] | 777.00 |  | 765.44 |  |  |  | 769.33 |  |  | 804.38 |  |  | 783.43 | [9 empty] | 714.94 |  |  | 8377.15
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 99.47 |  | 75.97 | [8 empty] | 0.13 |  |  | 95.89 | [6 empty] | 94.56 |  | 93.25 |  |  |  | 96.61 |  |  | 97.73 |  |  | 98.32 | [9 empty] | 87.20 |  |  | 86.43
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 76.95 | [8 empty] | 0.13 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 87.86 |  |  | 88.59
LF [%] |  |  |  |  | 100.97 | 101.12 |  |  |  | 100.14 |  | 76.09 | [8 empty] | 0.10 |  |  | 96.26 | [6 empty] | 94.86 |  | 93.44 |  |  |  | 97.05 |  |  | 98.20 |  |  | 98.83 | [9 empty] | 87.28 |  |  | 86.86
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 77.22 | [8 empty] | 0.27 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 88.31 |  |  | 88.66
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 12.14 |  |  | 1.15
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.27 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 12.14 |  |  | 1.82
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 23.05 | [8 empty] | 90.60 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 9.59
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.53 |  | 0.98 | [8 empty] | 0.00 |  |  | 4.11 | [6 empty] | 5.44 |  | 6.75 |  |  |  | 3.39 |  |  | 2.27 |  |  | 1.68 | [9 empty] | 0.67 |  |  | 2.17
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 34760.4 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.97 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.73 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.3 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.88 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.82 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.93 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.14 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.17 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2019 |  |  |  | 3557.06 |  |  | 4222 |  |  |  | 1101 | [10 empty] | 85.48 |  |  |  | 85.48 | [5 empty] | 83.47 |  |  | 88.25 |  |  |  | 13.57 |  | 13.43 | [8 empty] | 1.09 |  |  |  |  | 0.00
2020 |  |  |  | 7602.61 |  |  | 7367 |  |  |  | 1101 | [10 empty] | 81.50 |  |  |  | 83.68 | [5 empty] | 78.61 |  |  | 83.87 |  |  |  | 3.46 |  | 3.00 | [8 empty] | 13.32 |  |  |  |  | 2.18
2021 |  |  |  | 7348.32 |  |  | 6953 |  |  |  | 1101 | [10 empty] | 76.69 |  |  |  | 79.28 | [5 empty] | 76.19 |  |  | 79.37 |  |  |  | 0.15 |  | 2.40 | [8 empty] | 18.33 |  |  |  |  | 2.59
2022 |  |  |  | 7875.32 |  |  | 7368 |  |  |  | 1101 | [10 empty] | 81.69 |  |  |  | 83.70 | [5 empty] | 81.65 |  |  | 84.11 |  |  |  | 4.89 |  | 4.30 | [8 empty] | 12.00 |  |  |  |  | 2.01
2023 |  |  |  | 8377.15 |  |  | 7767 |  |  |  | 1101 | [10 empty] | 86.43 |  |  |  | 88.59 | [5 empty] | 86.86 |  |  | 88.66 |  |  |  | 1.15 |  | 1.82 | [8 empty] | 9.59 |  |  |  |  | 2.17
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2019 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 87 | [14 empty] | 213
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 837 | [14 empty] | 1113
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [24 empty] | 70 | [14 empty] | 85
Subtotal | [22 empty] | 837 |  |  |  | 157 | [10 empty] | 1113 |  |  |  | 303
Total | [22 empty] | 994 | [14 empty] | 1416
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2019 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 8
15. |  |  | Reactor Cooling Systems | [34 empty] | 44
31. |  |  | Turbine and auxiliaries | [34 empty] | 38
32. |  |  | Feedwater and Main Steam System | [34 empty] | 66
33. |  |  | Circulating Water System | [34 empty] | 11
35. |  |  | All other I&C Systems | [34 empty] | 7
41. |  |  | Main Generator Systems | [19 empty] | 87 | [14 empty] | 19
42. |  |  | Electrical Power Supply Systems | [34 empty] | 3
Total | [22 empty] | 87 | [14 empty] | 196
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-February. Additional electricity generation amounted to 5099 MWh. The unit was in the intermediate maintenance outage from 2023.04.24 to 2023.05.29. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH-4
2023 Operating Experience
RU-11 | [8 empty] | NOVOVORONEZH-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-179 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1967-07-01
Thermal power | [12 empty] | : |  |  | 1375 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1972-12-28
Gross electrical power | [12 empty] | : |  |  | 417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1973-03-24
Reference unit power (net) | [12 empty] | : |  |  | 385 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 51 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 12.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 295.8
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 6
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28600 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 2.88 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 4.4
| Active core height/length [m] | [13 empty] | : |  |  | 2.5 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 349 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.1 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 73 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 4
| Number of external reactor coolant loops | [13 empty] | : |  |  | 6 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 3055.96 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 6.18 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.16 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 6.67 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.76 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.57 %
Load Factor (LF) | [18 empty] | : | 90.61 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.59 %
Operating Factor (OF) | [18 empty] | : | 91.34 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 759 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 73.07 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 44.39 | 267.40 |  |  |  | 291.19 |  | 278.96 | [8 empty] | 284.67 |  |  | 205.64 | [6 empty] | 276.18 |  | 276.62 |  |  |  | 275.60 |  |  | 289.47 |  |  | 283.81 | [9 empty] | 282.05 |  |  | 3055.96
EAF [%] |  |  |  |  | 18.02 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.87 |  |  | 75.45 | [6 empty] | 97.04 |  | 96.95 |  |  |  | 99.94 |  |  | 99.80 |  |  | 100.00 | [9 empty] | 96.32 |  |  | 90.16
UCF [%] |  |  |  |  | 18.02 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 76.26 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 99.80 |  |  | 100.00 | [9 empty] | 96.32 |  |  | 90.76
LF [%] |  |  |  |  | 15.50 | 103.35 |  |  |  | 101.66 |  | 100.63 | [8 empty] | 99.38 |  |  | 74.18 | [6 empty] | 96.42 |  | 96.57 |  |  |  | 99.42 |  |  | 101.06 |  |  | 102.38 | [9 empty] | 98.47 |  |  | 90.61
OF [%] |  |  |  |  | 23.12 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 74.03 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.34
FLR [%] |  |  |  |  | 70.75 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 23.74 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.20 |  |  | 0.00 | [9 empty] | 3.68 |  |  | 6.18
UCL [%] |  |  |  |  | 51.72 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 23.74 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.20 |  |  | 0.00 | [9 empty] | 3.68 |  |  | 6.67
PUF [%] |  |  |  |  | 30.26 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.57
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.13 |  |  | 0.82 | [6 empty] | 2.96 |  | 3.05 |  |  |  | 0.06 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.59
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 134400.54 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.35 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.16 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.7 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 79.46 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 16.84 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.06 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.3 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.69 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1973 |  |  |  | 2570.51 |  |  | 8072 |  |  |  | 385 | [10 empty] | 84.20 |  |  |  | 84.20 | [5 empty] | 84.95 |  |  | 93.15 |  |  |  | 14.82 |  | 14.65 | [8 empty] | 1.15 |  |  |  |  | 0.00
1974 |  |  |  | 2411.84 |  |  | 7159 |  |  |  | 385 | [10 empty] | 71.28 |  |  |  | 71.28 | [5 empty] | 71.51 |  |  | 81.72 |  |  |  | 15.90 |  | 13.48 | [8 empty] | 15.24 |  |  |  |  | 0.00
1975 |  |  |  | 2644.87 |  |  | 7950 |  |  |  | 385 | [10 empty] | 75.64 |  |  |  | 75.64 | [5 empty] | 78.42 |  |  | 90.75 |  |  |  | 9.17 |  | 7.63 | [8 empty] | 16.73 |  |  |  |  | 0.00
1976 |  |  |  | 2924.13 |  |  | 7963 |  |  |  | 385 | [10 empty] | 84.48 |  |  |  | 84.48 | [5 empty] | 86.47 |  |  | 90.65 |  |  |  | 4.63 |  | 4.10 | [8 empty] | 11.42 |  |  |  |  | 0.00
1977 |  |  |  | 2822.95 |  |  | 7637 |  |  |  | 385 | [10 empty] | 81.34 |  |  |  | 81.34 | [5 empty] | 83.70 |  |  | 87.18 |  |  |  | 4.88 |  | 4.17 | [8 empty] | 14.49 |  |  |  |  | 0.00
1978 |  |  |  | 2658.54 |  |  | 7388 |  |  |  | 385 | [10 empty] | 78.18 |  |  |  | 78.18 | [5 empty] | 78.83 |  |  | 84.34 |  |  |  | 3.70 |  | 3.00 | [8 empty] | 18.82 |  |  |  |  | 0.00
1979 |  |  |  | 2442.24 |  |  | 6888 |  |  |  | 385 | [10 empty] | 72.44 |  |  |  | 72.44 | [5 empty] | 72.41 |  |  | 78.63 |  |  |  | 8.70 |  | 6.90 | [8 empty] | 20.66 |  |  |  |  | 0.00
1980 |  |  |  | 2842.93 |  |  | 7690 |  |  |  | 385 | [10 empty] | 84.08 |  |  |  | 84.08 | [5 empty] | 84.06 |  |  | 87.55 |  |  |  | 3.15 |  | 2.74 | [8 empty] | 13.18 |  |  |  |  | 0.00
1981 |  |  |  | 3019.87 |  |  | 8278 |  |  |  | 385 | [10 empty] | 90.03 |  |  |  | 90.03 | [5 empty] | 89.55 |  |  | 94.51 |  |  |  | 4.32 |  | 4.06 | [8 empty] | 5.91 |  |  |  |  | 0.00
1982 |  |  |  | 2797.51 |  |  | 8278 |  |  |  | 385 | [10 empty] | 83.88 |  |  |  | 83.88 | [5 empty] | 82.95 |  |  | 94.50 |  |  |  | 9.47 |  | 8.78 | [8 empty] | 7.35 |  |  |  |  | 0.00
1983 |  |  |  | 2950.30 |  |  | 8216 |  |  |  | 385 | [10 empty] | 89.15 |  |  |  | 89.15 | [5 empty] | 87.48 |  |  | 93.79 |  |  |  | 3.80 |  | 3.52 | [8 empty] | 7.33 |  |  |  |  | 0.00
1984 |  |  |  | 2974.10 |  |  | 7982 |  |  |  | 385 | [10 empty] | 87.89 |  |  |  | 87.89 | [5 empty] | 87.94 |  |  | 90.87 |  |  |  | 3.16 |  | 2.87 | [8 empty] | 9.24 |  |  |  |  | 0.00
1985 |  |  |  | 3097.87 |  |  | 8250 |  |  |  | 385 | [10 empty] | 91.30 |  |  |  | 91.30 | [5 empty] | 91.85 |  |  | 94.18 |  |  |  | 2.71 |  | 2.54 | [8 empty] | 6.16 |  |  |  |  | 0.00
1986 |  |  |  | 2792.21 |  |  | 7688 |  |  |  | 385 | [10 empty] | 82.62 |  |  |  | 82.62 | [5 empty] | 82.79 |  |  | 87.76 |  |  |  | 5.57 |  | 4.88 | [8 empty] | 12.51 |  |  |  |  | 0.00
1987 |  |  |  | 3262.68 |  |  | 8252 |  |  |  | 417 | [10 empty] | 91.72 |  |  |  | 91.72 | [5 empty] | 89.32 |  |  | 94.20 |  |  |  | 0.15 |  | 0.14 | [8 empty] | 8.14 |  |  |  |  | 0.00
1988 |  |  |  | 2529.37 |  |  | 7152 |  |  |  | 385 | [10 empty] | 79.97 |  |  |  | 79.97 | [5 empty] | 74.79 |  |  | 81.42 |  |  |  | 1.21 |  | 0.98 | [8 empty] | 19.05 |  |  |  |  | 0.00
1989 |  |  |  | 2710.26 |  |  | 8357 |  |  |  | 385 | [10 empty] | 90.16 |  |  |  | 90.19 | [5 empty] | 80.36 |  |  | 95.40 |  |  |  | 5.71 |  | 5.46 | [8 empty] | 4.35 |  |  |  |  | 0.04
1990 |  |  |  | 2244.69 |  |  | 6622 |  |  |  | 385 | [10 empty] | 69.63 |  |  |  | 70.55 | [5 empty] | 66.56 |  |  | 75.59 |  |  |  | 11.28 |  | 8.97 | [8 empty] | 20.48 |  |  |  |  | 0.92
1991 |  |  |  | 1827.62 |  |  | 5540 |  |  |  | 385 | [10 empty] | 57.96 |  |  |  | 58.24 | [5 empty] | 54.19 |  |  | 63.24 |  |  |  | 9.28 |  | 5.96 | [8 empty] | 35.80 |  |  |  |  | 0.28
1992 |  |  |  | 2853.44 |  |  | 8163 |  |  |  | 385 | [10 empty] | 82.38 |  |  |  | 87.35 | [5 empty] | 84.38 |  |  | 92.94 |  |  |  | 6.01 |  | 5.58 | [8 empty] | 7.07 |  |  |  |  | 4.97
1993 |  |  |  | 2613.71 |  |  | 7204 |  |  |  | 385 | [10 empty] | 76.60 |  |  |  | 79.73 | [5 empty] | 77.50 |  |  | 82.24 |  |  |  | 2.64 |  | 2.16 | [8 empty] | 18.11 |  |  |  |  | 3.13
1994 |  |  |  | 1954.27 |  |  | 6033 |  |  |  | 385 | [10 empty] | 56.65 |  |  |  | 66.91 | [5 empty] | 57.95 |  |  | 68.87 |  |  |  | 2.79 |  | 1.92 | [8 empty] | 31.17 |  |  |  |  | 10.26
1995 |  |  |  | 2119.99 |  |  | 5818 |  |  |  | 385 | [10 empty] | 62.15 |  |  |  | 65.50 | [5 empty] | 62.86 |  |  | 66.42 |  |  |  | 0.64 |  | 0.42 | [8 empty] | 34.08 |  |  |  |  | 3.35
1996 |  |  |  | 3080.28 |  |  | 8362 |  |  |  | 385 | [10 empty] | 90.38 |  |  |  | 93.78 | [5 empty] | 91.08 |  |  | 95.20 |  |  |  | 1.08 |  | 1.02 | [8 empty] | 5.20 |  |  |  |  | 3.40
1997 |  |  |  | 2235.48 |  |  | 6690 |  |  |  | 385 | [10 empty] | 66.98 |  |  |  | 70.29 | [5 empty] | 66.28 |  |  | 76.37 |  |  |  | 0.76 |  | 0.54 | [8 empty] | 29.17 |  |  |  |  | 3.30
1998 |  |  |  | 2714.87 |  |  | 7366 |  |  |  | 385 | [10 empty] | 80.18 |  |  |  | 83.16 | [5 empty] | 80.50 |  |  | 84.09 |  |  |  | 0.98 |  | 0.82 | [8 empty] | 16.02 |  |  |  |  | 2.98
1999 |  |  |  | 1791.48 |  |  | 4927 |  |  |  | 385 | [10 empty] | 53.21 |  |  |  | 54.93 | [5 empty] | 53.12 |  |  | 56.24 |  |  |  | 17.55 |  | 11.69 | [8 empty] | 33.38 |  |  |  |  | 1.72
2000 |  |  |  | 2474.25 |  |  | 6784 |  |  |  | 385 | [10 empty] | 73.08 |  |  |  | 74.64 | [5 empty] | 73.16 |  |  | 77.23 |  |  |  | 3.12 |  | 2.40 | [8 empty] | 22.96 |  |  |  |  | 1.56
2001 |  |  |  | 2655.95 |  |  | 7173 |  |  |  | 385 | [10 empty] | 79.22 |  |  |  | 80.72 | [5 empty] | 78.75 |  |  | 81.88 |  |  |  | 1.24 |  | 1.01 | [8 empty] | 18.26 |  |  |  |  | 1.51
2002 |  |  |  | 2184.85 |  |  | 5857 |  |  |  | 385 | [10 empty] | 64.21 |  |  |  | 65.37 | [5 empty] | 64.78 |  |  | 66.86 |  |  |  | 4.51 |  | 3.09 | [8 empty] | 31.55 |  |  |  |  | 1.15
2003 |  |  |  | 2583.05 |  |  | 6950 |  |  |  | 385 | [10 empty] | 76.75 |  |  |  | 78.78 | [5 empty] | 76.59 |  |  | 79.34 |  |  |  | 1.32 |  | 1.05 | [8 empty] | 20.17 |  |  |  |  | 2.02
2004 |  |  |  | 2714.01 |  |  | 7685 |  |  |  | 385 | [10 empty] | 80.75 |  |  |  | 83.75 | [5 empty] | 80.25 |  |  | 87.49 |  |  |  | 4.90 |  | 4.32 | [8 empty] | 11.94 |  |  |  |  | 2.99
2005 |  |  |  | 2433.38 |  |  | 7228 |  |  |  | 385 | [10 empty] | 73.09 |  |  |  | 75.27 | [5 empty] | 72.15 |  |  | 82.51 |  |  |  | 12.96 |  | 11.20 | [8 empty] | 13.53 |  |  |  |  | 2.18
2006 |  |  |  | 2575.08 |  |  | 7636 |  |  |  | 385 | [10 empty] | 76.49 |  |  |  | 81.29 | [5 empty] | 76.35 |  |  | 87.17 |  |  |  | 8.30 |  | 7.36 | [8 empty] | 11.36 |  |  |  |  | 4.79
2007 |  |  |  | 2290.27 |  |  | 6488 |  |  |  | 385 | [10 empty] | 67.88 |  |  |  | 69.12 | [5 empty] | 67.91 |  |  | 74.06 |  |  |  | 8.19 |  | 9.08 | [8 empty] | 21.80 |  |  |  |  | 1.24
2008 |  |  |  | 2876.30 |  |  | 7464 |  |  |  | 385 | [10 empty] | 83.37 |  |  |  | 84.02 | [5 empty] | 85.05 |  |  | 84.97 |  |  |  | 3.95 |  | 3.45 | [8 empty] | 12.53 |  |  |  |  | 0.65
2009 |  |  |  | 2931.78 |  |  | 7580 |  |  |  | 385 | [10 empty] | 85.23 |  |  |  | 86.31 | [5 empty] | 86.93 |  |  | 86.53 |  |  |  | 0.01 |  | 0.78 | [8 empty] | 12.91 |  |  |  |  | 1.08
2010 |  |  |  | 2928.70 |  |  | 7727 |  |  |  | 385 | [10 empty] | 85.82 |  |  |  | 87.48 | [5 empty] | 86.84 |  |  | 88.21 |  |  |  | 3.36 |  | 3.04 | [8 empty] | 9.48 |  |  |  |  | 1.66
2011 |  |  |  | 2707.55 |  |  | 7263 |  |  |  | 385 | [10 empty] | 80.64 |  |  |  | 82.08 | [5 empty] | 80.29 |  |  | 82.92 |  |  |  | 1.69 |  | 1.41 | [8 empty] | 16.51 |  |  |  |  | 1.44
2012 |  |  |  | 2944.86 |  |  | 7707 |  |  |  | 385 | [10 empty] | 87.14 |  |  |  | 87.87 | [5 empty] | 87.08 |  |  | 87.74 |  |  |  | 1.22 |  | 1.09 | [8 empty] | 11.04 |  |  |  |  | 0.73
2013 |  |  |  | 3038.98 |  |  | 7929 |  |  |  | 385 | [10 empty] | 89.36 |  |  |  | 90.36 | [5 empty] | 90.11 |  |  | 90.51 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.63 |  |  |  |  | 1.00
2014 |  |  |  | 3061.07 |  |  | 7932 |  |  |  | 385 | [10 empty] | 89.26 |  |  |  | 90.33 | [5 empty] | 90.75 |  |  | 90.54 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 9.56 |  |  |  |  | 1.07
2015 |  |  |  | 2704.38 |  |  | 7085 |  |  |  | 385 | [10 empty] | 79.59 |  |  |  | 80.43 | [5 empty] | 80.19 |  |  | 80.88 |  |  |  | 0.45 |  | 0.36 | [8 empty] | 19.21 |  |  |  |  | 0.83
2016 |  |  |  | 2959.49 |  |  | 7783 |  |  |  | 385 | [10 empty] | 87.26 |  |  |  | 88.31 | [5 empty] | 87.51 |  |  | 88.60 |  |  |  | 2.91 |  | 2.65 | [8 empty] | 9.04 |  |  |  |  | 1.05
2017 |  |  |  | 3148.86 |  |  | 8259 |  |  |  | 385 | [10 empty] | 92.54 |  |  |  | 93.92 | [5 empty] | 93.37 |  |  | 94.28 |  |  |  | 0.37 |  | 0.35 | [8 empty] | 5.73 |  |  |  |  | 1.38
2018 |  |  |  | 8.92 |  |  | 73 |  |  |  | 385 | [10 empty] | 0.43 |  |  |  | 0.43 | [5 empty] | 0.26 |  |  | 0.83 |  |  |  | 47.79 |  | 0.39 | [8 empty] | 99.18 |  |  |  |  | 0.00
2019 |  |  |  | 2994.94 |  |  | 7654 |  |  |  | 385 | [10 empty] | 86.23 |  |  |  | 86.33 | [5 empty] | 88.80 |  |  | 87.37 |  |  |  | 3.00 |  | 2.67 | [8 empty] | 11.01 |  |  |  |  | 0.09
2020 |  |  |  | 2945.24 |  |  | 7956 |  |  |  | 385 | [10 empty] | 89.27 |  |  |  | 90.40 | [5 empty] | 87.09 |  |  | 90.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.60 |  |  |  |  | 1.13
2021 |  |  |  | 3020.99 |  |  | 7951 |  |  |  | 385 | [10 empty] | 89.69 |  |  |  | 90.51 | [5 empty] | 89.57 |  |  | 90.76 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 9.46 |  |  |  |  | 0.82
2022 |  |  |  | 2199.85 |  |  | 5716 |  |  |  | 385 | [10 empty] | 64.37 |  |  |  | 65.15 | [5 empty] | 65.23 |  |  | 65.25 |  |  |  | 0.13 |  | 0.09 | [8 empty] | 34.76 |  |  |  |  | 0.78
2023 |  |  |  | 3055.96 |  |  | 8001 |  |  |  | 385 | [10 empty] | 90.16 |  |  |  | 90.76 | [5 empty] | 90.61 |  |  | 91.34 |  |  |  | 6.18 |  | 6.67 | [8 empty] | 2.57 |  |  |  |  | 0.59
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1973 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 553 | [14 empty] | 76
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 186 | [14 empty] | 1243
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 87
E. |  | Testing of plant systems or components | [35 empty] | 11
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 53
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 8
L. |  | Human factor related | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 8
Z. |  | Other | [35 empty] | 2 |  |  |  | 13
Subtotal | [22 empty] | 186 |  |  |  | 553 | [10 empty] | 1396 |  |  |  | 99 | [11 empty] | 8
Total | [22 empty] | 739 | [14 empty] | 1503
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1973 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 7
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 4
16. |  |  | Steam generation systems | [19 empty] | 530 | [14 empty] | 41
31. |  |  | Turbine and auxiliaries | [19 empty] | 23 | [14 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 0
35. |  |  | All other I&C Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 0
Total | [22 empty] | 553 | [14 empty] | 79
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-April, October-December. Additional electricity generation amounted to 39248 MWh. The unit was in the unit overhaul from 2023.01.01 to 2023.01.08. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## NOVOVORONEZH-5
2023 Operating Experience
RU-20 | [8 empty] | NOVOVORONEZH-5 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-187 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-03-01
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-05-31
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-02-20
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 324
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.5
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 109 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH / PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6729.72 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.44 %
Energy Availability Factor (EAF) | [18 empty] | : | 81.27 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.99 %
Unit Capability Factor (UCF) | [18 empty] | : | 81.94 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.07 %
Load Factor (LF) | [18 empty] | : | 80.87 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.67 %
Operating Factor (OF) | [18 empty] | : | 83.71 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1427 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 0 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 695.91 | 642.88 |  |  |  | 709.92 |  | 680.25 | [8 empty] | 674.22 |  |  | 624.25 | [6 empty] | 204.35 |  | 0.00 |  |  |  | 411.56 |  |  | 697.35 |  |  | 681.36 | [9 empty] | 707.68 |  |  | 6729.73
EAF [%] |  |  |  |  | 99.16 | 100.00 |  |  |  | 100.00 |  | 99.94 | [8 empty] | 95.98 |  |  | 92.10 | [6 empty] | 29.99 |  | 0.00 |  |  |  | 61.66 |  |  | 99.12 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.27
UCF [%] |  |  |  |  | 99.60 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 97.79 |  |  | 94.08 | [6 empty] | 31.92 |  | 0.00 |  |  |  | 62.90 |  |  | 99.71 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 81.94
LF [%] |  |  |  |  | 98.46 | 100.70 |  |  |  | 100.44 |  | 99.45 | [8 empty] | 95.39 |  |  | 91.27 | [6 empty] | 28.91 |  | 0.00 |  |  |  | 60.17 |  |  | 98.66 |  |  | 99.61 | [9 empty] | 100.12 |  |  | 80.87
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 36.29 |  | 0.00 |  |  |  | 70.97 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 83.71
FLR [%] |  |  |  |  | 0.40 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.21 |  |  | 5.92 | [6 empty] | 10.80 |  | 0.00 |  |  |  | 2.51 |  |  | 0.29 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.44
UCL [%] |  |  |  |  | 0.40 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.21 |  |  | 5.92 | [6 empty] | 3.87 |  | 0.00 |  |  |  | 23.45 |  |  | 0.29 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.99
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 64.21 |  | 100.00 |  |  |  | 13.65 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 15.07
XUF [%] |  |  |  |  | 0.45 | 0.00 |  |  |  | 0.00 |  | 0.06 | [8 empty] | 1.81 |  |  | 1.97 | [6 empty] | 1.93 |  | 0.00 |  |  |  | 1.24 |  |  | 0.59 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.67
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 235853.65 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 11.18 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 67.81 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 10.58 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 68.63 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 20.79 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 67.58 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.82 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 74.44 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 4639.79 |  |  | 6929 |  |  |  | 950 | [10 empty] | 56.62 |  |  |  | 56.62 | [5 empty] | 56.10 |  |  | 77.77 |  |  |  | 28.48 |  | 22.54 | [8 empty] | 20.83 |  |  |  |  | 0.00
1982 |  |  |  | 5042.84 |  |  | 6631 |  |  |  | 950 | [10 empty] | 60.89 |  |  |  | 60.89 | [5 empty] | 60.60 |  |  | 75.70 |  |  |  | 25.30 |  | 20.62 | [8 empty] | 18.49 |  |  |  |  | 0.00
1983 |  |  |  | 6607.53 |  |  | 7716 |  |  |  | 950 | [10 empty] | 79.53 |  |  |  | 79.53 | [5 empty] | 79.40 |  |  | 88.08 |  |  |  | 7.92 |  | 6.84 | [8 empty] | 13.64 |  |  |  |  | 0.00
1984 |  |  |  | 6979.64 |  |  | 7742 |  |  |  | 950 | [10 empty] | 83.42 |  |  |  | 83.42 | [5 empty] | 83.64 |  |  | 88.14 |  |  |  | 5.18 |  | 4.56 | [8 empty] | 12.02 |  |  |  |  | 0.00
1985 |  |  |  | 6894.29 |  |  | 7979 |  |  |  | 950 | [10 empty] | 83.12 |  |  |  | 83.12 | [5 empty] | 82.84 |  |  | 91.08 |  |  |  | 8.96 |  | 8.18 | [8 empty] | 8.69 |  |  |  |  | 0.00
1986 |  |  |  | 5523.75 |  |  | 6806 |  |  |  | 950 | [10 empty] | 65.91 |  |  |  | 65.96 | [5 empty] | 66.38 |  |  | 77.69 |  |  |  | 17.36 |  | 13.86 | [8 empty] | 20.18 |  |  |  |  | 0.04
1987 |  |  |  | 7052.70 |  |  | 7399 |  |  |  | 1000 | [10 empty] | 81.79 |  |  |  | 81.79 | [5 empty] | 80.51 |  |  | 84.46 |  |  |  | 2.68 |  | 2.26 | [8 empty] | 15.96 |  |  |  |  | 0.00
1988 |  |  |  | 3017.85 |  |  | 3439 |  |  |  | 950 | [10 empty] | 36.51 |  |  |  | 36.51 | [5 empty] | 36.16 |  |  | 39.15 |  |  |  | 59.88 |  | 54.50 | [8 empty] | 8.98 |  |  |  |  | 0.00
1989 |  |  |  | 3308.95 |  |  | 3778 |  |  |  | 950 | [10 empty] | 40.88 |  |  |  | 40.88 | [5 empty] | 39.76 |  |  | 43.13 |  |  |  | 25.41 |  | 13.93 | [8 empty] | 45.19 |  |  |  |  | 0.00
1990 |  |  |  | 3913.28 |  |  | 4715 |  |  |  | 950 | [10 empty] | 47.63 |  |  |  | 47.72 | [5 empty] | 47.02 |  |  | 53.82 |  |  |  | 15.35 |  | 8.66 | [8 empty] | 43.62 |  |  |  |  | 0.09
1991 |  |  |  | 5878.22 |  |  | 6996 |  |  |  | 950 | [10 empty] | 71.54 |  |  |  | 71.54 | [5 empty] | 70.63 |  |  | 79.86 |  |  |  | 19.86 |  | 17.72 | [8 empty] | 10.74 |  |  |  |  | 0.00
1992 |  |  |  | 3752.83 |  |  | 5244 |  |  |  | 950 | [10 empty] | 45.70 |  |  |  | 45.89 | [5 empty] | 44.98 |  |  | 59.71 |  |  |  | 8.71 |  | 4.38 | [8 empty] | 49.73 |  |  |  |  | 0.20
1993 |  |  |  | 5935.41 |  |  | 7448 |  |  |  | 950 | [10 empty] | 72.55 |  |  |  | 73.79 | [5 empty] | 71.32 |  |  | 85.02 |  |  |  | 10.42 |  | 8.59 | [8 empty] | 17.62 |  |  |  |  | 1.24
1994 |  |  |  | 2281.89 |  |  | 4288 |  |  |  | 950 | [10 empty] | 28.94 |  |  |  | 33.19 | [5 empty] | 27.42 |  |  | 48.95 |  |  |  | 50.98 |  | 34.51 | [8 empty] | 32.29 |  |  |  |  | 4.26
1995 |  |  |  | 4753.72 |  |  | 6670 |  |  |  | 950 | [10 empty] | 57.46 |  |  |  | 63.87 | [5 empty] | 57.12 |  |  | 76.14 |  |  |  | 14.52 |  | 10.85 | [8 empty] | 25.28 |  |  |  |  | 6.41
1996 |  |  |  | 3861.84 |  |  | 4759 |  |  |  | 950 | [10 empty] | 46.71 |  |  |  | 46.71 | [5 empty] | 46.28 |  |  | 54.18 |  |  |  | 15.10 |  | 8.31 | [8 empty] | 44.98 |  |  |  |  | 0.00
1997 |  |  |  | 5949.25 |  |  | 6854 |  |  |  | 950 | [10 empty] | 71.37 |  |  |  | 71.69 | [5 empty] | 71.49 |  |  | 78.24 |  |  |  | 7.84 |  | 6.10 | [8 empty] | 22.21 |  |  |  |  | 0.33
1998 |  |  |  | 3771.78 |  |  | 4457 |  |  |  | 950 | [10 empty] | 44.89 |  |  |  | 45.48 | [5 empty] | 45.32 |  |  | 50.88 |  |  |  | 28.35 |  | 17.99 | [8 empty] | 36.52 |  |  |  |  | 0.60
1999 |  |  |  | 4845.42 |  |  | 6062 |  |  |  | 950 | [10 empty] | 58.73 |  |  |  | 61.16 | [5 empty] | 58.22 |  |  | 69.20 |  |  |  | 17.37 |  | 12.86 | [8 empty] | 25.99 |  |  |  |  | 2.43
2000 |  |  |  | 5278.64 |  |  | 6479 |  |  |  | 950 | [10 empty] | 63.54 |  |  |  | 65.56 | [5 empty] | 63.26 |  |  | 73.76 |  |  |  | 7.30 |  | 5.17 | [8 empty] | 29.27 |  |  |  |  | 2.02
2001 |  |  |  | 5984.59 |  |  | 7508 |  |  |  | 950 | [10 empty] | 72.26 |  |  |  | 73.22 | [5 empty] | 71.91 |  |  | 85.71 |  |  |  | 6.60 |  | 5.17 | [8 empty] | 21.61 |  |  |  |  | 0.96
2002 |  |  |  | 6762.21 |  |  | 7430 |  |  |  | 950 | [10 empty] | 80.68 |  |  |  | 83.14 | [5 empty] | 81.26 |  |  | 84.82 |  |  |  | 1.95 |  | 1.65 | [8 empty] | 15.21 |  |  |  |  | 2.45
2003 |  |  |  | 6951.21 |  |  | 7507 |  |  |  | 950 | [10 empty] | 83.05 |  |  |  | 84.51 | [5 empty] | 83.53 |  |  | 85.70 |  |  |  | 0.93 |  | 0.79 | [8 empty] | 14.70 |  |  |  |  | 1.46
2004 |  |  |  | 3610.61 |  |  | 4032 |  |  |  | 950 | [10 empty] | 43.13 |  |  |  | 43.61 | [5 empty] | 43.27 |  |  | 45.90 |  |  |  | 44.15 |  | 34.48 | [8 empty] | 21.91 |  |  |  |  | 0.48
2005 |  |  |  | 2544.26 |  |  | 2861 |  |  |  | 950 | [10 empty] | 30.60 |  |  |  | 31.42 | [5 empty] | 30.57 |  |  | 32.66 |  |  |  | 0.00 |  | 68.58 | [8 empty] | 0.00 |  |  |  |  | 0.82
2006 |  |  |  | 7264.41 |  |  | 7762 |  |  |  | 950 | [10 empty] | 86.70 |  |  |  | 87.75 | [5 empty] | 87.29 |  |  | 88.61 |  |  |  | 0.61 |  | 0.54 | [8 empty] | 11.71 |  |  |  |  | 1.05
2007 |  |  |  | 6556.27 |  |  | 7140 |  |  |  | 950 | [10 empty] | 78.48 |  |  |  | 79.84 | [5 empty] | 78.78 |  |  | 81.51 |  |  |  | 7.10 |  | 7.85 | [8 empty] | 12.31 |  |  |  |  | 1.36
2008 |  |  |  | 7285.18 |  |  | 7718 |  |  |  | 950 | [10 empty] | 86.89 |  |  |  | 87.00 | [5 empty] | 87.30 |  |  | 87.86 |  |  |  | 0.51 |  | 0.44 | [8 empty] | 12.56 |  |  |  |  | 0.11
2009 |  |  |  | 6518.11 |  |  | 6865 |  |  |  | 950 | [10 empty] | 77.59 |  |  |  | 77.86 | [5 empty] | 78.32 |  |  | 78.37 |  |  |  | 4.04 |  | 3.28 | [8 empty] | 18.86 |  |  |  |  | 0.27
2010 |  |  |  | 5585.30 |  |  | 6404 |  |  |  | 950 | [10 empty] | 66.98 |  |  |  | 69.12 | [5 empty] | 67.11 |  |  | 73.11 |  |  |  | 5.83 |  | 4.28 | [8 empty] | 26.61 |  |  |  |  | 2.13
2011 |  |  |  | 2085.77 |  |  | 2422 |  |  |  | 950 | [10 empty] | 25.11 |  |  |  | 25.11 | [5 empty] | 25.07 |  |  | 27.65 |  |  |  | 7.01 |  | 7.99 | [8 empty] | 66.90 |  |  |  |  | 0.00
2012 |  |  |  | 7014.58 |  |  | 7457 |  |  |  | 950 | [10 empty] | 83.60 |  |  |  | 83.72 | [5 empty] | 84.06 |  |  | 84.89 |  |  |  | 1.80 |  | 2.89 | [8 empty] | 13.38 |  |  |  |  | 0.13
2013 |  |  |  | 7205.36 |  |  | 7773 |  |  |  | 950 | [10 empty] | 85.97 |  |  |  | 86.24 | [5 empty] | 86.58 |  |  | 88.73 |  |  |  | 1.20 |  | 1.23 | [8 empty] | 12.54 |  |  |  |  | 0.27
2014 |  |  |  | 6193.58 |  |  | 7712 |  |  |  | 950 | [10 empty] | 74.39 |  |  |  | 74.40 | [5 empty] | 74.42 |  |  | 88.03 |  |  |  | 11.44 |  | 9.61 | [8 empty] | 15.99 |  |  |  |  | 0.01
2015 |  |  |  | 6209.76 |  |  | 7120 |  |  |  | 950 | [10 empty] | 74.34 |  |  |  | 74.50 | [5 empty] | 74.62 |  |  | 81.28 |  |  |  | 8.43 |  | 7.73 | [8 empty] | 17.77 |  |  |  |  | 0.16
2016 |  |  |  | 7191.83 |  |  | 7777 |  |  |  | 950 | [10 empty] | 85.94 |  |  |  | 86.18 | [5 empty] | 86.18 |  |  | 88.54 |  |  |  | 1.73 |  | 1.85 | [8 empty] | 11.97 |  |  |  |  | 0.24
2017 |  |  |  | 6560.03 |  |  | 7811 |  |  |  | 950 | [10 empty] | 78.87 |  |  |  | 79.36 | [5 empty] | 78.83 |  |  | 89.17 |  |  |  | 0.60 |  | 0.48 | [8 empty] | 20.16 |  |  |  |  | 0.49
2018 |  |  |  | 7134.80 |  |  | 7766 |  |  |  | 950 | [10 empty] | 86.22 |  |  |  | 87.70 | [5 empty] | 85.73 |  |  | 88.65 |  |  |  | 0.99 |  | 2.46 | [8 empty] | 9.84 |  |  |  |  | 1.48
2019 |  |  |  | 6092.49 |  |  | 6806 |  |  |  | 950 | [10 empty] | 74.19 |  |  |  | 74.67 | [5 empty] | 73.21 |  |  | 77.69 |  |  |  | 8.33 |  | 6.79 | [8 empty] | 18.54 |  |  |  |  | 0.49
2020 |  |  |  | 6787.87 |  |  | 7483 |  |  |  | 950 | [10 empty] | 83.89 |  |  |  | 84.60 | [5 empty] | 81.34 |  |  | 85.19 |  |  |  | 2.96 |  | 2.84 | [8 empty] | 12.56 |  |  |  |  | 0.71
2021 |  |  |  | 7227.84 |  |  | 7774 |  |  |  | 950 | [10 empty] | 87.16 |  |  |  | 87.84 | [5 empty] | 86.85 |  |  | 88.74 |  |  |  | 0.45 |  | 0.77 | [8 empty] | 11.40 |  |  |  |  | 0.68
2022 |  |  |  | 7312.92 |  |  | 7908 |  |  |  | 950 | [10 empty] | 88.52 |  |  |  | 89.62 | [5 empty] | 87.87 |  |  | 90.27 |  |  |  | 0.16 |  | 0.14 | [8 empty] | 10.24 |  |  |  |  | 1.10
2023 |  |  |  | 6729.73 |  |  | 7333 |  |  |  | 950 | [10 empty] | 81.27 |  |  |  | 81.94 | [5 empty] | 80.87 |  |  | 83.71 |  |  |  | 1.44 |  | 2.99 | [8 empty] | 15.07 |  |  |  |  | 0.67
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1981 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 22 | [14 empty] | 583
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1314 | [14 empty] | 1420
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 287
L. |  | Human factor related | [39 empty] | 2
Z. |  | Other | [24 empty] | 91 | [14 empty] | 12
Subtotal | [22 empty] | 1314 |  |  |  | 113 | [10 empty] | 1707 |  |  |  | 597
Total | [22 empty] | 1427 | [14 empty] | 2304
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1981 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 224
12. |  |  | Reactor I&C Systems | [34 empty] | 18
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 2
15. |  |  | Reactor Cooling Systems | [34 empty] | 48
16. |  |  | Steam generation systems | [34 empty] | 203
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [19 empty] | 113 | [14 empty] | 15
32. |  |  | Feedwater and Main Steam System | [34 empty] | 6
34. |  |  | Miscellaneous Systems | [34 empty] | 6
35. |  |  | All other I&C Systems | [34 empty] | 5
41. |  |  | Main Generator Systems | [34 empty] | 46
42. |  |  | Electrical Power Supply Systems | [34 empty] | 4
Total | [22 empty] | 113 | [14 empty] | 583
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. The unit was in the overhaul from 2023.07.12 to 2023.09.05. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-1
2023 Operating Experience
RU-59 | [8 empty] | ROSTOV-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1981-09-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2001-03-30
Gross electrical power | [12 empty] | : |  |  | 1041 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2001-12-25
Reference unit power (net) | [12 empty] | : |  |  | 989 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 22 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 16
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 6993.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.39 %
Energy Availability Factor (EAF) | [18 empty] | : | 79.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 1.52 %
Unit Capability Factor (UCF) | [18 empty] | : | 79.95 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 18.53 %
Load Factor (LF) | [18 empty] | : | 80.72 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.67 %
Operating Factor (OF) | [18 empty] | : | 80.03 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1749 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 765.57 | 690.00 |  |  |  | 459.70 |  | 0.00 | [8 empty] | 0.00 |  |  | 652.26 | [6 empty] | 729.23 |  | 723.02 |  |  |  | 713.39 |  |  | 759.12 |  |  | 740.56 | [9 empty] | 760.56 |  |  | 6993.42
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 63.14 |  | 1.10 | [8 empty] | 1.10 |  |  | 91.42 | [6 empty] | 98.91 |  | 98.49 |  |  |  | 98.82 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.52 |  |  | 79.28
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 68.28 |  | 1.10 | [8 empty] | 1.10 |  |  | 91.57 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 98.85 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.52 |  |  | 79.95
LF [%] |  |  |  |  | 104.04 | 103.82 |  |  |  | 62.48 |  | 0.00 | [8 empty] | 0.00 |  |  | 91.60 | [6 empty] | 99.11 |  | 98.26 |  |  |  | 100.18 |  |  | 103.17 |  |  | 104.00 | [9 empty] | 103.36 |  |  | 80.72
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 68.28 |  | 0.00 | [8 empty] | 0.00 |  |  | 93.19 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.03
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.28 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 1.15 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.48 |  |  | 0.39
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.57 |  |  | 7.01 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 1.15 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.48 |  |  | 1.52
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 31.72 |  | 98.90 | [8 empty] | 89.33 |  |  | 1.42 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 18.53
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 5.15 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.15 | [6 empty] | 1.09 |  | 1.51 |  |  |  | 0.04 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.67
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 171664.95 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.09 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 88.04 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.26 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 88.42 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.33 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.03 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.38 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.71 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2001 |  |  |  | Data not provided
2002 |  |  |  | 7176.18 |  |  | 7543 |  |  |  | 950 | [10 empty] | 84.06 |  |  |  | 85.51 | [5 empty] | 86.23 |  |  | 86.11 |  |  |  | 1.33 |  | 1.16 | [8 empty] | 13.33 |  |  |  |  | 1.45
2003 |  |  |  | 6973.93 |  |  | 7154 |  |  |  | 950 | [10 empty] | 81.33 |  |  |  | 82.56 | [5 empty] | 83.80 |  |  | 81.67 |  |  |  | 2.81 |  | 2.39 | [8 empty] | 15.05 |  |  |  |  | 1.23
2004 |  |  |  | 7439.31 |  |  | 7766 |  |  |  | 950 | [10 empty] | 87.75 |  |  |  | 87.96 | [5 empty] | 89.15 |  |  | 88.41 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 11.87 |  |  |  |  | 0.21
2005 |  |  |  | 7232.86 |  |  | 7628 |  |  |  | 950 | [10 empty] | 85.85 |  |  |  | 86.87 | [5 empty] | 86.90 |  |  | 87.07 |  |  |  | 0.60 |  | 0.52 | [8 empty] | 12.60 |  |  |  |  | 1.02
2006 |  |  |  | 7216.42 |  |  | 7386 |  |  |  | 950 | [10 empty] | 83.82 |  |  |  | 84.19 | [5 empty] | 86.71 |  |  | 84.32 |  |  |  | 0.29 |  | 3.46 | [8 empty] | 12.35 |  |  |  |  | 0.38
2007 |  |  |  | 7309.44 |  |  | 7536 |  |  |  | 950 | [10 empty] | 85.28 |  |  |  | 85.48 | [5 empty] | 87.83 |  |  | 86.03 |  |  |  | 0.55 |  | 0.47 | [8 empty] | 14.04 |  |  |  |  | 0.20
2008 |  |  |  | 7745.73 |  |  | 7799 |  |  |  | 950 | [10 empty] | 88.53 |  |  |  | 88.56 | [5 empty] | 92.82 |  |  | 88.79 |  |  |  | 1.00 |  | 0.89 | [8 empty] | 10.54 |  |  |  |  | 0.03
2009 |  |  |  | 7927.02 |  |  | 7916 |  |  |  | 950 | [10 empty] | 90.27 |  |  |  | 90.29 | [5 empty] | 95.25 |  |  | 90.37 |  |  |  | 0.52 |  | 0.47 | [8 empty] | 9.25 |  |  |  |  | 0.01
2010 |  |  |  | 7398.47 |  |  | 7828 |  |  |  | 950 | [10 empty] | 88.60 |  |  |  | 88.91 | [5 empty] | 88.90 |  |  | 89.36 |  |  |  | 2.23 |  | 2.02 | [8 empty] | 9.06 |  |  |  |  | 0.32
2011 |  |  |  | 7695.35 |  |  | 7736 |  |  |  | 950 | [10 empty] | 88.24 |  |  |  | 88.24 | [5 empty] | 92.48 |  |  | 88.32 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 11.68 |  |  |  |  | 0.00
2012 |  |  |  | 7569.03 |  |  | 7614 |  |  |  | 950 | [10 empty] | 86.42 |  |  |  | 86.51 | [5 empty] | 90.70 |  |  | 86.68 |  |  |  | 0.10 |  | 1.40 | [8 empty] | 12.09 |  |  |  |  | 0.09
2013 |  |  |  | 8557.12 |  |  | 8618 |  |  |  | 950 | [10 empty] | 98.15 |  |  |  | 98.15 | [5 empty] | 102.83 |  |  | 98.38 |  |  |  | 1.85 |  | 1.85 | [8 empty] | 0.00 |  |  |  |  | 0.00
2014 |  |  |  | 7227.67 |  |  | 7498 |  |  |  | 950 | [10 empty] | 85.13 |  |  |  | 85.37 | [5 empty] | 86.84 |  |  | 85.58 |  |  |  | 1.82 |  | 1.58 | [8 empty] | 13.05 |  |  |  |  | 0.25
2015 |  |  |  | 6713.50 |  |  | 6980 |  |  |  | 950 | [10 empty] | 76.83 |  |  |  | 76.83 | [5 empty] | 80.67 |  |  | 79.68 |  |  |  | 7.21 |  | 5.97 | [8 empty] | 17.21 |  |  |  |  | 0.00
2016 |  |  |  | 8833.60 |  |  | 8753 |  |  |  | 950 | [10 empty] | 99.63 |  |  |  | 99.63 | [5 empty] | 105.86 |  |  | 99.65 |  |  |  | 0.37 |  | 0.37 | [8 empty] | 0.00 |  |  |  |  | 0.00
2017 |  |  |  | 7840.38 |  |  | 7825 |  |  |  | 950 | [10 empty] | 89.24 |  |  |  | 89.24 | [5 empty] | 94.21 |  |  | 89.33 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 10.76 |  |  |  |  | 0.00
2018 |  |  |  | 7609.90 |  |  | 7719 |  |  |  | 950 | [10 empty] | 87.71 |  |  |  | 87.98 | [5 empty] | 91.44 |  |  | 88.12 |  |  |  | 0.74 |  | 1.07 | [8 empty] | 10.95 |  |  |  |  | 0.27
2019 |  |  |  | 8620.25 |  |  | 8723 |  |  |  | 950 | [10 empty] | 99.49 |  |  |  | 99.52 | [5 empty] | 103.58 |  |  | 99.58 |  |  |  | 0.48 |  | 0.48 | [8 empty] | 0.00 |  |  |  |  | 0.03
2020 |  |  |  | 7443.25 |  |  | 7689 |  |  |  | 950 | [10 empty] | 86.60 |  |  |  | 87.29 | [5 empty] | 89.20 |  |  | 87.53 |  |  |  | 0.96 |  | 0.85 | [8 empty] | 11.86 |  |  |  |  | 0.68
2021 |  |  |  | 7416.99 |  |  | 7622 |  |  |  | 989 | [10 empty] | 85.73 |  |  |  | 87.04 | [5 empty] | 85.61 |  |  | 87.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.96 |  |  |  |  | 1.31
2022 |  |  |  | 8753.70 |  |  | 8728 |  |  |  | 989 | [10 empty] | 98.87 |  |  |  | 99.02 | [5 empty] | 101.04 |  |  | 99.63 |  |  |  | 0.98 |  | 0.98 | [8 empty] | 0.00 |  |  |  |  | 0.14
2023 |  |  |  | 6993.42 |  |  | 7011 |  |  |  | 989 | [10 empty] | 79.28 |  |  |  | 79.95 | [5 empty] | 80.72 |  |  | 80.03 |  |  |  | 0.39 |  | 1.52 | [8 empty] | 18.53 |  |  |  |  | 0.67
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2001 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 121 | [14 empty] | 85
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1629 | [14 empty] | 890
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 6
E. |  | Testing of plant systems or components | [39 empty] | 2
L. |  | Human factor related | [39 empty] | 3
Subtotal | [22 empty] | 1629 |  |  |  | 121 | [10 empty] | 896 |  |  |  | 90
Total | [22 empty] | 1750 | [14 empty] | 986
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2001 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 3
14. |  |  | Safety Systems | [34 empty] | 2
16. |  |  | Steam generation systems | [34 empty] | 31
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 1
33. |  |  | Circulating Water System | [34 empty] | 3
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [19 empty] | 13 | [14 empty] | 28
42. |  |  | Electrical Power Supply Systems | [19 empty] | 108 | [14 empty] | 19
Total | [22 empty] | 121 | [14 empty] | 89
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-March, June, September-December. Additional electricity generation amounted to 127515 MWh. The unit was in theoverhaul outage from 2023.03.22 to 2023.06.02. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-2
2023 Operating Experience
RU-62 | [8 empty] | ROSTOV-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | FAEA (Federal Atomic Energy Agency)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1983-05-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2010-03-18
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2010-12-10
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 13 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 0.7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 4
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 30 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 40000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.16 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6
| Active core height/length [m] | [13 empty] | : |  |  | 3.53 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 163 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 61 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7978.3 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.55 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.06 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.93 %
Load Factor (LF) | [18 empty] | : | 95.87 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.51 %
Operating Factor (OF) | [18 empty] | : | 91.15 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 775 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 724.65 | 203.03 |  |  |  | 391.54 |  | 735.85 | [8 empty] | 752.60 |  |  | 714.06 | [6 empty] | 730.02 |  | 732.82 |  |  |  | 725.44 |  |  | 760.17 |  |  | 740.65 | [9 empty] | 767.47 |  |  | 7978.31
EAF [%] |  |  |  |  | 97.33 | 32.29 |  |  |  | 52.60 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 90.55
UCF [%] |  |  |  |  | 100.00 | 35.93 |  |  |  | 52.60 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.99 |  |  | 91.06
LF [%] |  |  |  |  | 102.53 | 31.80 |  |  |  | 55.40 |  | 107.58 | [8 empty] | 106.48 |  |  | 104.39 | [6 empty] | 103.28 |  | 103.68 |  |  |  | 106.06 |  |  | 107.55 |  |  | 108.28 | [9 empty] | 108.58 |  |  | 95.87
OF [%] |  |  |  |  | 100.00 | 36.31 |  |  |  | 53.36 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.15
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.33 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 0.02
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.17 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.01 |  |  | 0.02
PUF [%] |  |  |  |  | 0.00 | 64.07 |  |  |  | 47.23 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.93
XUF [%] |  |  |  |  | 2.67 | 3.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.51
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 105284.27 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.49 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.88 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.35 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 90.2 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.44 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 93.31 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.32 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.44 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2010 |  |  |  | 4303.76 |  |  | 6133 |  |  |  | 950 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 97.93 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2011 |  |  |  | 7368.43 |  |  | 7944 |  |  |  | 950 | [10 empty] | 89.41 |  |  |  | 90.23 | [5 empty] | 88.55 |  |  | 90.70 |  |  |  | 0.63 |  | 0.58 | [8 empty] | 9.19 |  |  |  |  | 0.82
2012 |  |  |  | 7433.18 |  |  | 7781 |  |  |  | 950 | [10 empty] | 87.61 |  |  |  | 87.79 | [5 empty] | 89.08 |  |  | 88.58 |  |  |  | 1.30 |  | 1.16 | [8 empty] | 11.05 |  |  |  |  | 0.18
2013 |  |  |  | 7832.67 |  |  | 8151 |  |  |  | 950 | [10 empty] | 92.80 |  |  |  | 92.80 | [5 empty] | 94.12 |  |  | 93.05 |  |  |  | 0.55 |  | 0.51 | [8 empty] | 6.69 |  |  |  |  | 0.00
2014 |  |  |  | 7741.45 |  |  | 8018 |  |  |  | 950 | [10 empty] | 91.20 |  |  |  | 91.29 | [5 empty] | 93.01 |  |  | 91.52 |  |  |  | 0.26 |  | 0.24 | [8 empty] | 8.47 |  |  |  |  | 0.09
2015 |  |  |  | 7525.83 |  |  | 7610 |  |  |  | 950 | [10 empty] | 86.39 |  |  |  | 86.41 | [5 empty] | 90.43 |  |  | 86.87 |  |  |  | 1.26 |  | 1.11 | [8 empty] | 12.48 |  |  |  |  | 0.03
2016 |  |  |  | 7890.03 |  |  | 7974 |  |  |  | 950 | [10 empty] | 90.15 |  |  |  | 90.69 | [5 empty] | 94.55 |  |  | 90.78 |  |  |  | 1.44 |  | 1.33 | [8 empty] | 7.98 |  |  |  |  | 0.54
2017 |  |  |  | 7734.15 |  |  | 7755 |  |  |  | 950 | [10 empty] | 88.29 |  |  |  | 88.31 | [5 empty] | 92.94 |  |  | 88.53 |  |  |  | 11.64 |  | 11.63 | [8 empty] | 0.06 |  |  |  |  | 0.01
2018 |  |  |  | 6666.68 |  |  | 6845 |  |  |  | 950 | [10 empty] | 76.80 |  |  |  | 77.90 | [5 empty] | 80.11 |  |  | 78.14 |  |  |  | 12.50 |  | 11.13 | [8 empty] | 10.98 |  |  |  |  | 1.09
2019 |  |  |  | 8662.06 |  |  | 8650 |  |  |  | 950 | [10 empty] | 98.71 |  |  |  | 98.72 | [5 empty] | 104.09 |  |  | 98.74 |  |  |  | 1.28 |  | 1.28 | [8 empty] | 0.00 |  |  |  |  | 0.01
2020 |  |  |  | 7864.15 |  |  | 7982 |  |  |  | 950 | [10 empty] | 90.61 |  |  |  | 90.79 | [5 empty] | 94.24 |  |  | 90.87 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 9.21 |  |  |  |  | 0.18
2021 |  |  |  | 7418.56 |  |  | 7532 |  |  |  | 950 | [10 empty] | 85.14 |  |  |  | 85.85 | [5 empty] | 89.14 |  |  | 85.98 |  |  |  | 1.31 |  | 1.79 | [8 empty] | 12.36 |  |  |  |  | 0.71
2022 |  |  |  | 8865.36 |  |  | 8760 |  |  |  | 950 | [10 empty] | 99.97 |  |  |  | 99.97 | [5 empty] | 106.53 |  |  | 100.00 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 0.00 |  |  |  |  | 0.00
2023 |  |  |  | 7978.31 |  |  | 7985 |  |  |  | 950 | [10 empty] | 90.55 |  |  |  | 91.06 | [5 empty] | 95.87 |  |  | 91.15 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 8.93 |  |  |  |  | 0.51
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2010 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 188
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 776 | [14 empty] | 598
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 44
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
Z. |  | Other | [39 empty] | 4
Subtotal | [22 empty] | 776 | [14 empty] | 642 |  |  |  | 192 | [11 empty] | 1
Total | [22 empty] | 776 | [14 empty] | 835
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2010 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 7
15. |  |  | Reactor Cooling Systems | [34 empty] | 5
16. |  |  | Steam generation systems | [34 empty] | 10
31. |  |  | Turbine and auxiliaries | [34 empty] | 35
41. |  |  | Main Generator Systems | [34 empty] | 79
42. |  |  | Electrical Power Supply Systems | [34 empty] | 42
Total | [37 empty] | 178
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January, March-December. Additional electricity generation amounted to 410474 MWh. The unit was in the intermediate maintenance outage from 2023.02.11 to 2023.03.15. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-3
2023 Operating Experience
RU-63 | [8 empty] | ROSTOV-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2009-09-15
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2014-12-27
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2015-09-17
Reference unit power (net) | [12 empty] | : |  |  | 950 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 9 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7755.53 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.38 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.69 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.34 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.69 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.97 %
Load Factor (LF) | [18 empty] | : | 93.19 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0 %
Operating Factor (OF) | [18 empty] | : | 88.85 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 977 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 455.92 |  |  |  | 750.58 |  | 719.25 | [8 empty] | 730.41 |  |  | 713.51 | [6 empty] | 734.47 |  | 728.19 |  |  |  | 718.69 |  |  | 751.38 |  |  | 705.07 | [9 empty] | 748.07 |  |  | 7755.53
EAF [%] |  |  |  |  | 0.00 | 67.68 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.54 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 97.04 | [9 empty] | 99.31 |  |  | 88.69
UCF [%] |  |  |  |  | 0.00 | 67.68 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.54 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 97.04 | [9 empty] | 99.31 |  |  | 88.69
LF [%] |  |  |  |  | 0.00 | 71.42 |  |  |  | 106.19 |  | 105.15 | [8 empty] | 103.34 |  |  | 104.31 | [6 empty] | 103.91 |  | 103.03 |  |  |  | 105.07 |  |  | 106.31 |  |  | 103.08 | [9 empty] | 105.84 |  |  | 93.19
OF [%] |  |  |  |  | 0.00 | 68.01 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 97.50 | [9 empty] | 100.00 |  |  | 88.85
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.46 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.96 | [9 empty] | 0.69 |  |  | 0.38
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.46 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 2.96 | [9 empty] | 0.69 |  |  | 0.34
PUF [%] |  |  |  |  | 100.00 | 32.32 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.97
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 63776.23 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.41 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 86.21 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.47 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.04 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.49 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 88.53 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.83 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 87.82 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2015 |  |  |  | 5132.22 |  |  | 7040 |  |  |  | 950 | [10 empty] | 99.65 |  |  |  | 99.65 | [5 empty] | 104.56 |  |  | 100.00 |  |  |  | 0.35 |  | 0.35 | [8 empty] | 0.00 |  |  |  |  | 0.00
2016 |  |  |  | 6110.00 |  |  | 6728 |  |  |  | 950 | [10 empty] | 71.98 |  |  |  | 73.43 | [5 empty] | 73.22 |  |  | 76.59 |  |  |  | 5.40 |  | 14.24 | [8 empty] | 12.33 |  |  |  |  | 1.45
2017 |  |  |  | 6422.53 |  |  | 6888 |  |  |  | 950 | [10 empty] | 76.35 |  |  |  | 77.80 | [5 empty] | 77.18 |  |  | 78.63 |  |  |  | 3.24 |  | 2.60 | [8 empty] | 19.60 |  |  |  |  | 1.45
2018 |  |  |  | 7709.57 |  |  | 7962 |  |  |  | 950 | [10 empty] | 90.24 |  |  |  | 90.77 | [5 empty] | 92.64 |  |  | 90.89 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 8.95 |  |  |  |  | 0.53
2019 |  |  |  | 7360.63 |  |  | 7848 |  |  |  | 950 | [10 empty] | 87.53 |  |  |  | 89.97 | [5 empty] | 88.45 |  |  | 89.59 |  |  |  | 0.71 |  | 0.64 | [8 empty] | 9.39 |  |  |  |  | 2.44
2020 |  |  |  | 7651.88 |  |  | 8081 |  |  |  | 950 | [10 empty] | 89.89 |  |  |  | 90.36 | [5 empty] | 91.70 |  |  | 92.00 |  |  |  | 1.38 |  | 1.26 | [8 empty] | 8.38 |  |  |  |  | 0.47
2021 |  |  |  | 7615.55 |  |  | 8010 |  |  |  | 950 | [10 empty] | 90.16 |  |  |  | 90.67 | [5 empty] | 91.51 |  |  | 91.44 |  |  |  | 0.97 |  | 0.89 | [8 empty] | 8.45 |  |  |  |  | 0.51
2022 |  |  |  | 8018.57 |  |  | 8016 |  |  |  | 950 | [10 empty] | 91.52 |  |  |  | 91.52 | [5 empty] | 96.35 |  |  | 91.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.48 |  |  |  |  | 0.00
2023 |  |  |  | 7755.53 |  |  | 7783 |  |  |  | 950 | [10 empty] | 88.69 |  |  |  | 88.69 | [5 empty] | 93.19 |  |  | 88.85 |  |  |  | 0.38 |  | 0.34 | [8 empty] | 10.97 |  |  |  |  | 0.00
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2015 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 19 | [14 empty] | 156
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 959 | [14 empty] | 695
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 12
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 203
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 8
Subtotal | [22 empty] | 959 |  |  |  | 19 | [10 empty] | 910 |  |  |  | 156 | [11 empty] | 8
Total | [22 empty] | 978 | [14 empty] | 1074
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2015 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
15. |  |  | Reactor Cooling Systems | [34 empty] | 22
16. |  |  | Steam generation systems | [34 empty] | 2
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 12
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
33. |  |  | Circulating Water System | [34 empty] | 1
41. |  |  | Main Generator Systems | [19 empty] | 19 | [14 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 100
Total | [22 empty] | 19 | [14 empty] | 143
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in February-December. Additional electricity generation amounted to 455149 MWh. The unit was in the overhaul outage from 2023.01.01 to 2023.02.09. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## ROSTOV-4
2023 Operating Experience
RU-64 | [8 empty] | ROSTOV-4 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | AEM (Atomenergomash)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / VVER V-320 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2010-06-16
Thermal power | [12 empty] | : |  |  | 3000 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2018-02-02
Gross electrical power | [12 empty] | : |  |  | 1030 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2018-09-28
Reference unit power (net) | [12 empty] | : |  |  | 979 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 5 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | - | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | - | [11 empty] | Number of SG | [15 empty] | : |  |  | -
| Refuelling type | [13 empty] | : |  |  | - | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | - | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | -
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | -
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | - | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | -
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | - | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | - | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 8450.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 97.92 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 100 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 0 %
Load Factor (LF) | [18 empty] | : | 98.54 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.08 %
Operating Factor (OF) | [18 empty] | : | 100 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 0 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 754.76 | 680.96 |  |  |  | 744.99 |  | 714.77 | [8 empty] | 726.93 |  |  | 687.04 | [6 empty] | 665.83 |  | 623.54 |  |  |  | 684.11 |  |  | 722.58 |  |  | 706.04 | [9 empty] | 739.13 |  |  | 8450.68
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.76 |  |  | 98.34 | [6 empty] | 92.61 |  | 87.23 |  |  |  | 98.08 |  |  | 99.54 |  |  | 99.89 | [9 empty] | 99.90 |  |  | 97.92
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
LF [%] |  |  |  |  | 103.62 | 103.51 |  |  |  | 102.28 |  | 101.40 | [8 empty] | 99.80 |  |  | 97.47 | [6 empty] | 91.41 |  | 85.61 |  |  |  | 97.05 |  |  | 99.20 |  |  | 100.17 | [9 empty] | 101.48 |  |  | 98.54
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 100.00
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.24 |  |  | 1.66 | [6 empty] | 7.39 |  | 12.77 |  |  |  | 1.92 |  |  | 0.46 |  |  | 0.11 | [9 empty] | 0.10 |  |  | 2.08
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 44626.9 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.92 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.44 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.87 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 93.03 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 6.1 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 91.53 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.59 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 93.23 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2018 |  |  |  | 5681.92 |  |  | 6556 |  |  |  | 950 | [10 empty] | 99.97 |  |  |  | 99.99 | [5 empty] | 103.76 |  |  | 100.00 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 0.00 |  |  |  |  | 0.01
2019 |  |  |  | 7430.57 |  |  | 7751 |  |  |  | 979 | [10 empty] | 87.01 |  |  |  | 88.29 | [5 empty] | 86.64 |  |  | 88.48 |  |  |  | 0.40 |  | 0.35 | [8 empty] | 11.36 |  |  |  |  | 1.28
2020 |  |  |  | 8066.50 |  |  | 8573 |  |  |  | 979 | [10 empty] | 94.86 |  |  |  | 97.45 | [5 empty] | 93.80 |  |  | 97.60 |  |  |  | 2.50 |  | 2.50 | [8 empty] | 0.05 |  |  |  |  | 2.58
2021 |  |  |  | 7521.96 |  |  | 7862 |  |  |  | 979 | [10 empty] | 88.05 |  |  |  | 89.52 | [5 empty] | 87.71 |  |  | 89.75 |  |  |  | 0.91 |  | 0.82 | [8 empty] | 9.66 |  |  |  |  | 1.47
2022 |  |  |  | 7542.06 |  |  | 7761 |  |  |  | 979 | [10 empty] | 87.28 |  |  |  | 88.19 | [5 empty] | 87.94 |  |  | 88.60 |  |  |  | 0.98 |  | 0.87 | [8 empty] | 10.94 |  |  |  |  | 0.91
2023 |  |  |  | 8450.68 |  |  | 8760 |  |  |  | 979 | [10 empty] | 97.92 |  |  |  | 100.00 | [5 empty] | 98.54 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 2.08
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2018 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 67
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 555
L. |  | Human factor related | [39 empty] | 2
Subtotal | [37 empty] | 555 |  |  |  | 69
Total | [22 empty] | 0 | [14 empty] | 624
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2018 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
16. |  |  | Steam generation systems | [34 empty] | 18
31. |  |  | Turbine and auxiliaries | [34 empty] | 11
32. |  |  | Feedwater and Main Steam System | [34 empty] | 38
33. |  |  | Circulating Water System | [34 empty] | 2
Total | [37 empty] | 69
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-June, October-December. Additional electricity generation amounted to 122728 MWh. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## SMOLENSK-1
2023 Operating Experience
RU-23 | [8 empty] | SMOLENSK-1 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-10-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-12-09
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-09-30
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 175 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | PH / DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5689.02 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.03 %
Energy Availability Factor (EAF) | [18 empty] | : | 67.72 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 67.85 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 32.13 %
Load Factor (LF) | [18 empty] | : | 70.21 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.13 %
Operating Factor (OF) | [18 empty] | : | 70.24 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 2607 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 63.68 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 728.79 | 656.66 |  |  |  | 729.25 |  | 688.63 | [8 empty] | 686.58 |  |  | 285.99 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 499.95 |  |  | 677.57 | [9 empty] | 735.59 |  |  | 5689.02
EAF [%] |  |  |  |  | 99.72 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 98.97 |  |  | 44.11 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 72.08 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 67.72
UCF [%] |  |  |  |  | 99.72 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 99.89 |  |  | 44.77 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 72.08 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 67.85
LF [%] |  |  |  |  | 105.90 | 105.64 |  |  |  | 105.96 |  | 103.40 | [8 empty] | 99.76 |  |  | 42.94 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 72.65 |  |  | 101.74 | [9 empty] | 106.89 |  |  | 70.21
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 46.94 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 97.72 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 70.24
FLR [%] |  |  |  |  | 0.28 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
UCL [%] |  |  |  |  | 0.28 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.02
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.11 |  |  | 55.23 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 27.92 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 32.13
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.92 |  |  | 0.65 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.13
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 247123.06 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.44 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 74.14 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.01 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 75.8 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 22.19 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 74.87 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.66 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 77.31 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 4744.20 |  |  | 7223 |  |  |  | 925 | [10 empty] | 99.64 |  |  |  | 99.64 | [5 empty] | 100.76 |  |  | 99.86 |  |  |  | 0.36 |  | 0.36 | [8 empty] | 0.00 |  |  |  |  | 0.00
1984 |  |  |  | 6921.35 |  |  | 7830 |  |  |  | 925 | [10 empty] | 84.23 |  |  |  | 84.23 | [5 empty] | 85.18 |  |  | 89.14 |  |  |  | 2.64 |  | 2.28 | [8 empty] | 13.49 |  |  |  |  | 0.00
1985 |  |  |  | 5850.24 |  |  | 6806 |  |  |  | 925 | [10 empty] | 72.40 |  |  |  | 74.87 | [5 empty] | 72.20 |  |  | 77.69 |  |  |  | 1.52 |  | 1.15 | [8 empty] | 23.97 |  |  |  |  | 2.47
1986 |  |  |  | 3039.75 |  |  | 3472 |  |  |  | 925 | [10 empty] | 37.79 |  |  |  | 37.79 | [5 empty] | 37.51 |  |  | 39.63 |  |  |  | 0.05 |  | 0.02 | [8 empty] | 62.20 |  |  |  |  | 0.00
1987 |  |  |  | 7445.76 |  |  | 7620 |  |  |  | 1000 | [10 empty] | 86.72 |  |  |  | 86.72 | [5 empty] | 85.00 |  |  | 86.99 |  |  |  | 2.08 |  | 1.84 | [8 empty] | 11.44 |  |  |  |  | 0.00
1988 |  |  |  | 6695.59 |  |  | 7288 |  |  |  | 925 | [10 empty] | 81.89 |  |  |  | 81.89 | [5 empty] | 82.41 |  |  | 82.97 |  |  |  | 0.44 |  | 0.36 | [8 empty] | 17.75 |  |  |  |  | 0.00
1989 |  |  |  | 6506.46 |  |  | 7177 |  |  |  | 925 | [10 empty] | 79.32 |  |  |  | 79.70 | [5 empty] | 80.30 |  |  | 81.93 |  |  |  | 6.44 |  | 5.49 | [8 empty] | 14.82 |  |  |  |  | 0.38
1990 |  |  |  | 6227.84 |  |  | 6851 |  |  |  | 925 | [10 empty] | 76.14 |  |  |  | 76.59 | [5 empty] | 76.86 |  |  | 78.21 |  |  |  | 3.90 |  | 3.11 | [8 empty] | 20.30 |  |  |  |  | 0.45
1991 |  |  |  | 6693.92 |  |  | 7252 |  |  |  | 925 | [10 empty] | 81.29 |  |  |  | 81.29 | [5 empty] | 82.61 |  |  | 82.79 |  |  |  | 3.68 |  | 3.11 | [8 empty] | 15.60 |  |  |  |  | 0.00
1992 |  |  |  | 6849.38 |  |  | 7563 |  |  |  | 925 | [10 empty] | 83.69 |  |  |  | 83.69 | [5 empty] | 84.31 |  |  | 86.11 |  |  |  | 2.55 |  | 2.19 | [8 empty] | 14.12 |  |  |  |  | 0.00
1993 |  |  |  | 6290.56 |  |  | 6993 |  |  |  | 925 | [10 empty] | 78.01 |  |  |  | 78.41 | [5 empty] | 77.63 |  |  | 79.83 |  |  |  | 0.38 |  | 0.30 | [8 empty] | 21.29 |  |  |  |  | 0.40
1994 |  |  |  | 4217.84 |  |  | 6286 |  |  |  | 925 | [10 empty] | 57.81 |  |  |  | 71.04 | [5 empty] | 52.05 |  |  | 71.76 |  |  |  | 0.20 |  | 0.14 | [8 empty] | 28.82 |  |  |  |  | 13.23
1995 |  |  |  | 5002.47 |  |  | 6390 |  |  |  | 925 | [10 empty] | 62.97 |  |  |  | 77.35 | [5 empty] | 61.74 |  |  | 72.95 |  |  |  | 1.91 |  | 1.50 | [8 empty] | 21.15 |  |  |  |  | 14.38
1996 |  |  |  | 5666.43 |  |  | 6604 |  |  |  | 925 | [10 empty] | 71.56 |  |  |  | 71.73 | [5 empty] | 69.74 |  |  | 75.18 |  |  |  | 1.05 |  | 0.76 | [8 empty] | 27.51 |  |  |  |  | 0.17
1997 |  |  |  | 4674.51 |  |  | 5366 |  |  |  | 925 | [10 empty] | 57.82 |  |  |  | 59.14 | [5 empty] | 57.69 |  |  | 61.26 |  |  |  | 2.88 |  | 1.75 | [8 empty] | 39.11 |  |  |  |  | 1.32
1998 |  |  |  | 3554.08 |  |  | 5411 |  |  |  | 925 | [10 empty] | 45.04 |  |  |  | 58.85 | [5 empty] | 43.86 |  |  | 61.77 |  |  |  | 3.49 |  | 2.13 | [8 empty] | 39.02 |  |  |  |  | 13.81
1999 |  |  |  | 6478.89 |  |  | 7417 |  |  |  | 925 | [10 empty] | 80.06 |  |  |  | 83.51 | [5 empty] | 79.96 |  |  | 84.67 |  |  |  | 3.29 |  | 2.84 | [8 empty] | 13.65 |  |  |  |  | 3.45
2000 |  |  |  | 5228.48 |  |  | 5738 |  |  |  | 925 | [10 empty] | 63.83 |  |  |  | 64.36 | [5 empty] | 64.35 |  |  | 65.32 |  |  |  | 0.06 |  | 0.04 | [8 empty] | 35.60 |  |  |  |  | 0.53
2001 |  |  |  | 5165.12 |  |  | 5940 |  |  |  | 925 | [10 empty] | 63.24 |  |  |  | 67.43 | [5 empty] | 63.74 |  |  | 67.81 |  |  |  | 2.61 |  | 1.81 | [8 empty] | 30.76 |  |  |  |  | 4.19
2002 |  |  |  | 6866.73 |  |  | 7587 |  |  |  | 925 | [10 empty] | 83.69 |  |  |  | 85.10 | [5 empty] | 84.74 |  |  | 86.61 |  |  |  | 2.59 |  | 2.26 | [8 empty] | 12.64 |  |  |  |  | 1.41
2003 |  |  |  | 6711.76 |  |  | 7533 |  |  |  | 925 | [10 empty] | 82.90 |  |  |  | 84.38 | [5 empty] | 82.83 |  |  | 85.99 |  |  |  | 3.18 |  | 2.77 | [8 empty] | 12.85 |  |  |  |  | 1.48
2004 |  |  |  | 2337.12 |  |  | 2592 |  |  |  | 925 | [10 empty] | 28.50 |  |  |  | 29.09 | [5 empty] | 28.76 |  |  | 29.51 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 70.91 |  |  |  |  | 0.59
2005 |  |  |  | 7354.10 |  |  | 8414 |  |  |  | 925 | [10 empty] | 90.63 |  |  |  | 94.66 | [5 empty] | 90.75 |  |  | 96.04 |  |  |  | 0.80 |  | 0.76 | [8 empty] | 4.58 |  |  |  |  | 4.03
2006 |  |  |  | 5417.08 |  |  | 6021 |  |  |  | 925 | [10 empty] | 67.09 |  |  |  | 67.09 | [5 empty] | 66.85 |  |  | 68.73 |  |  |  | 1.33 |  | 3.79 | [8 empty] | 29.12 |  |  |  |  | 0.00
2007 |  |  |  | 6569.65 |  |  | 7138 |  |  |  | 925 | [10 empty] | 80.25 |  |  |  | 80.82 | [5 empty] | 81.08 |  |  | 81.48 |  |  |  | 0.20 |  | 0.16 | [8 empty] | 19.02 |  |  |  |  | 0.57
2008 |  |  |  | 7794.93 |  |  | 8430 |  |  |  | 925 | [10 empty] | 94.94 |  |  |  | 95.19 | [5 empty] | 95.94 |  |  | 95.97 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 4.79 |  |  |  |  | 0.25
2009 |  |  |  | 6122.29 |  |  | 6974 |  |  |  | 925 | [10 empty] | 77.32 |  |  |  | 77.60 | [5 empty] | 75.56 |  |  | 79.61 |  |  |  | 12.28 |  | 10.86 | [8 empty] | 11.54 |  |  |  |  | 0.28
2010 |  |  |  | 4896.26 |  |  | 5424 |  |  |  | 925 | [10 empty] | 61.10 |  |  |  | 61.75 | [5 empty] | 60.43 |  |  | 61.92 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 38.24 |  |  |  |  | 0.65
2011 |  |  |  | 5444.54 |  |  | 5899 |  |  |  | 925 | [10 empty] | 65.97 |  |  |  | 66.24 | [5 empty] | 67.20 |  |  | 67.35 |  |  |  | 0.05 |  | 0.03 | [8 empty] | 33.73 |  |  |  |  | 0.27
2012 |  |  |  | 6306.76 |  |  | 6741 |  |  |  | 925 | [10 empty] | 75.88 |  |  |  | 76.32 | [5 empty] | 77.62 |  |  | 76.74 |  |  |  | 1.76 |  | 1.37 | [8 empty] | 22.31 |  |  |  |  | 0.45
2013 |  |  |  | 7775.27 |  |  | 8267 |  |  |  | 925 | [10 empty] | 93.47 |  |  |  | 93.80 | [5 empty] | 95.96 |  |  | 94.37 |  |  |  | 3.63 |  | 3.53 | [8 empty] | 2.67 |  |  |  |  | 0.34
2014 |  |  |  | 7330.99 |  |  | 7691 |  |  |  | 925 | [10 empty] | 87.06 |  |  |  | 87.27 | [5 empty] | 90.46 |  |  | 87.79 |  |  |  | 0.92 |  | 0.83 | [8 empty] | 11.89 |  |  |  |  | 0.21
2015 |  |  |  | 7050.99 |  |  | 7394 |  |  |  | 925 | [10 empty] | 83.24 |  |  |  | 83.37 | [5 empty] | 87.02 |  |  | 84.41 |  |  |  | 2.18 |  | 1.86 | [8 empty] | 14.77 |  |  |  |  | 0.14
2016 |  |  |  | 6746.07 |  |  | 7003 |  |  |  | 925 | [10 empty] | 79.38 |  |  |  | 79.45 | [5 empty] | 83.03 |  |  | 79.72 |  |  |  | 0.15 |  | 0.12 | [8 empty] | 20.42 |  |  |  |  | 0.07
2017 |  |  |  | 6710.68 |  |  | 7720 |  |  |  | 925 | [10 empty] | 80.35 |  |  |  | 80.44 | [5 empty] | 82.82 |  |  | 88.13 |  |  |  | 9.47 |  | 8.41 | [8 empty] | 11.15 |  |  |  |  | 0.08
2018 |  |  |  | 6788.06 |  |  | 7256 |  |  |  | 925 | [10 empty] | 80.82 |  |  |  | 80.92 | [5 empty] | 83.77 |  |  | 82.83 |  |  |  | 4.80 |  | 4.08 | [8 empty] | 15.00 |  |  |  |  | 0.10
2019 |  |  |  | 6373.86 |  |  | 6673 |  |  |  | 925 | [10 empty] | 75.51 |  |  |  | 75.51 | [5 empty] | 78.66 |  |  | 76.18 |  |  |  | 0.54 |  | 2.32 | [8 empty] | 22.17 |  |  |  |  | 0.00
2020 |  |  |  | 6155.00 |  |  | 6930 |  |  |  | 925 | [10 empty] | 73.88 |  |  |  | 73.96 | [5 empty] | 75.75 |  |  | 78.89 |  |  |  | 0.51 |  | 0.38 | [8 empty] | 25.66 |  |  |  |  | 0.08
2021 |  |  |  | 7267.29 |  |  | 7736 |  |  |  | 925 | [10 empty] | 86.52 |  |  |  | 87.17 | [5 empty] | 89.69 |  |  | 88.31 |  |  |  | 3.27 |  | 2.94 | [8 empty] | 9.89 |  |  |  |  | 0.66
2022 |  |  |  | 6594.48 |  |  | 7001 |  |  |  | 925 | [10 empty] | 78.31 |  |  |  | 78.56 | [5 empty] | 81.38 |  |  | 79.92 |  |  |  | 4.46 |  | 3.67 | [8 empty] | 17.78 |  |  |  |  | 0.24
2023 |  |  |  | 5689.02 |  |  | 6153 |  |  |  | 925 | [10 empty] | 67.72 |  |  |  | 67.85 | [5 empty] | 70.21 |  |  | 70.24 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 32.13 |  |  |  |  | 0.13
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1983 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 102
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 2607 | [14 empty] | 1218
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 265
E. |  | Testing of plant systems or components | [35 empty] | 19
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 255
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 4
L. |  | Human factor related | [39 empty] | 1
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 11
Subtotal | [22 empty] | 2607 | [14 empty] | 1757 |  |  |  | 103 | [11 empty] | 15
Total | [22 empty] | 2607 | [14 empty] | 1875
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1983 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 20
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 12
14. |  |  | Safety Systems | [34 empty] | 13
15. |  |  | Reactor Cooling Systems | [34 empty] | 22
16. |  |  | Steam generation systems | [34 empty] | 0
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 0
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
34. |  |  | Miscellaneous Systems | [34 empty] | 5
42. |  |  | Electrical Power Supply Systems | [34 empty] | 7
Total | [37 empty] | 104
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-June, October-December. Additional electricity generation amounted to 200803 MWh. The unit was in the routine maintenance from 2023.06.15 to 2023.10.01. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## SMOLENSK-2
2023 Operating Experience
RU-24 | [8 empty] | SMOLENSK-2 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1976-06-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-05-31
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-07-02
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 175 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | PH / DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7182.68 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.43 %
Energy Availability Factor (EAF) | [18 empty] | : | 86.63 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.17 %
Unit Capability Factor (UCF) | [18 empty] | : | 86.91 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.92 %
Load Factor (LF) | [18 empty] | : | 88.64 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.29 %
Operating Factor (OF) | [18 empty] | : | 88 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1051 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 58.29 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 708.51 | 652.54 |  |  |  | 723.47 |  | 141.57 | [8 empty] | 316.94 |  |  | 522.21 | [6 empty] | 685.12 |  | 679.57 |  |  |  | 662.99 |  |  | 704.36 |  |  | 678.83 | [9 empty] | 706.56 |  |  | 7182.68
EAF [%] |  |  |  |  | 97.36 | 100.00 |  |  |  | 100.00 |  | 21.91 | [8 empty] | 47.04 |  |  | 78.72 | [6 empty] | 98.93 |  | 98.50 |  |  |  | 99.12 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 97.73 |  |  | 86.63
UCF [%] |  |  |  |  | 97.36 | 100.00 |  |  |  | 100.00 |  | 21.91 | [8 empty] | 47.06 |  |  | 79.13 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.53 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 97.73 |  |  | 86.91
LF [%] |  |  |  |  | 102.95 | 104.98 |  |  |  | 105.13 |  | 21.26 | [8 empty] | 46.05 |  |  | 78.41 | [6 empty] | 99.55 |  | 98.75 |  |  |  | 99.55 |  |  | 102.35 |  |  | 101.93 | [9 empty] | 102.67 |  |  | 88.64
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 23.75 | [8 empty] | 50.54 |  |  | 81.39 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.00
FLR [%] |  |  |  |  | 2.64 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 20.87 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.43 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 2.27 |  |  | 2.43
UCL [%] |  |  |  |  | 2.64 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 20.87 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.43 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 2.27 |  |  | 2.17
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 78.09 | [8 empty] | 52.94 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.04 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.92
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.01 |  |  | 0.41 | [6 empty] | 1.07 |  | 1.50 |  |  |  | 0.41 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.29
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 240742.14 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.73 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 76.3 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 2.35 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 78.06 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 19.59 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 76.94 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.75 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 80.08 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 3623.94 |  |  | 4593 |  |  |  | 925 | [10 empty] | 81.32 |  |  |  | 90.61 | [5 empty] | 80.97 |  |  | 91.89 |  |  |  | 6.31 |  | 6.10 | [8 empty] | 3.29 |  |  |  |  | 9.28
1986 |  |  |  | 6667.30 |  |  | 7442 |  |  |  | 925 | [10 empty] | 82.57 |  |  |  | 82.57 | [5 empty] | 82.28 |  |  | 84.95 |  |  |  | 1.56 |  | 1.31 | [8 empty] | 16.12 |  |  |  |  | 0.00
1987 |  |  |  | 6364.93 |  |  | 6707 |  |  |  | 1000 | [10 empty] | 74.52 |  |  |  | 74.52 | [5 empty] | 72.66 |  |  | 76.56 |  |  |  | 4.46 |  | 3.48 | [8 empty] | 22.01 |  |  |  |  | 0.00
1988 |  |  |  | 6757.16 |  |  | 7594 |  |  |  | 925 | [10 empty] | 83.49 |  |  |  | 83.55 | [5 empty] | 83.16 |  |  | 86.45 |  |  |  | 1.83 |  | 1.56 | [8 empty] | 14.89 |  |  |  |  | 0.06
1989 |  |  |  | 6627.33 |  |  | 7336 |  |  |  | 925 | [10 empty] | 81.50 |  |  |  | 81.85 | [5 empty] | 81.79 |  |  | 83.74 |  |  |  | 2.69 |  | 2.26 | [8 empty] | 15.88 |  |  |  |  | 0.36
1990 |  |  |  | 6710.59 |  |  | 7453 |  |  |  | 925 | [10 empty] | 82.52 |  |  |  | 82.97 | [5 empty] | 82.82 |  |  | 85.08 |  |  |  | 5.48 |  | 4.81 | [8 empty] | 12.22 |  |  |  |  | 0.45
1991 |  |  |  | 5796.72 |  |  | 6495 |  |  |  | 925 | [10 empty] | 71.36 |  |  |  | 71.36 | [5 empty] | 71.54 |  |  | 74.14 |  |  |  | 3.36 |  | 2.48 | [8 empty] | 26.16 |  |  |  |  | 0.00
1992 |  |  |  | 6731.61 |  |  | 7472 |  |  |  | 925 | [10 empty] | 82.63 |  |  |  | 83.90 | [5 empty] | 82.86 |  |  | 85.07 |  |  |  | 1.14 |  | 0.96 | [8 empty] | 15.13 |  |  |  |  | 1.28
1993 |  |  |  | 6634.11 |  |  | 7492 |  |  |  | 925 | [10 empty] | 82.69 |  |  |  | 84.90 | [5 empty] | 81.87 |  |  | 85.53 |  |  |  | 0.29 |  | 0.25 | [8 empty] | 14.86 |  |  |  |  | 2.21
1994 |  |  |  | 5259.83 |  |  | 7044 |  |  |  | 925 | [10 empty] | 66.56 |  |  |  | 80.25 | [5 empty] | 64.91 |  |  | 80.41 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 19.73 |  |  |  |  | 13.69
1995 |  |  |  | 5337.40 |  |  | 6738 |  |  |  | 925 | [10 empty] | 66.84 |  |  |  | 80.32 | [5 empty] | 65.87 |  |  | 76.92 |  |  |  | 0.26 |  | 0.21 | [8 empty] | 19.47 |  |  |  |  | 13.49
1996 |  |  |  | 6127.71 |  |  | 7010 |  |  |  | 925 | [10 empty] | 77.82 |  |  |  | 79.09 | [5 empty] | 75.42 |  |  | 79.80 |  |  |  | 0.89 |  | 0.71 | [8 empty] | 20.20 |  |  |  |  | 1.27
1997 |  |  |  | 4991.02 |  |  | 5642 |  |  |  | 925 | [10 empty] | 61.57 |  |  |  | 61.70 | [5 empty] | 61.59 |  |  | 64.41 |  |  |  | 4.41 |  | 2.84 | [8 empty] | 35.46 |  |  |  |  | 0.13
1998 |  |  |  | 5297.02 |  |  | 6576 |  |  |  | 925 | [10 empty] | 65.58 |  |  |  | 73.88 | [5 empty] | 65.37 |  |  | 75.07 |  |  |  | 1.37 |  | 1.03 | [8 empty] | 25.09 |  |  |  |  | 8.30
1999 |  |  |  | 5362.50 |  |  | 6090 |  |  |  | 925 | [10 empty] | 66.03 |  |  |  | 69.14 | [5 empty] | 66.18 |  |  | 69.52 |  |  |  | 0.12 |  | 0.09 | [8 empty] | 30.78 |  |  |  |  | 3.11
2000 |  |  |  | 6566.15 |  |  | 7108 |  |  |  | 925 | [10 empty] | 80.10 |  |  |  | 80.54 | [5 empty] | 80.81 |  |  | 80.92 |  |  |  | 3.91 |  | 3.28 | [8 empty] | 16.19 |  |  |  |  | 0.44
2001 |  |  |  | 6457.64 |  |  | 7537 |  |  |  | 925 | [10 empty] | 78.96 |  |  |  | 81.02 | [5 empty] | 79.69 |  |  | 86.04 |  |  |  | 6.08 |  | 5.25 | [8 empty] | 13.73 |  |  |  |  | 2.06
2002 |  |  |  | 3431.09 |  |  | 3890 |  |  |  | 925 | [10 empty] | 41.69 |  |  |  | 43.60 | [5 empty] | 42.34 |  |  | 44.41 |  |  |  | 1.66 |  | 0.74 | [8 empty] | 55.66 |  |  |  |  | 1.91
2003 |  |  |  | 6438.59 |  |  | 7734 |  |  |  | 925 | [10 empty] | 79.13 |  |  |  | 81.42 | [5 empty] | 79.46 |  |  | 88.29 |  |  |  | 8.45 |  | 7.52 | [8 empty] | 11.06 |  |  |  |  | 2.29
2004 |  |  |  | 7480.14 |  |  | 8312 |  |  |  | 925 | [10 empty] | 90.85 |  |  |  | 93.66 | [5 empty] | 92.06 |  |  | 94.63 |  |  |  | 0.62 |  | 0.59 | [8 empty] | 5.75 |  |  |  |  | 2.80
2005 |  |  |  | 3053.40 |  |  | 3734 |  |  |  | 925 | [10 empty] | 37.72 |  |  |  | 41.71 | [5 empty] | 37.68 |  |  | 42.63 |  |  |  | 0.42 |  | 0.17 | [8 empty] | 58.11 |  |  |  |  | 4.00
2006 |  |  |  | 7623.87 |  |  | 8306 |  |  |  | 925 | [10 empty] | 93.15 |  |  |  | 93.15 | [5 empty] | 94.09 |  |  | 94.82 |  |  |  | 0.16 |  | 1.27 | [8 empty] | 5.58 |  |  |  |  | 0.00
2007 |  |  |  | 4096.43 |  |  | 4878 |  |  |  | 925 | [10 empty] | 49.68 |  |  |  | 50.76 | [5 empty] | 50.55 |  |  | 55.68 |  |  |  | 2.50 |  | 1.30 | [8 empty] | 47.94 |  |  |  |  | 1.08
2008 |  |  |  | 6718.76 |  |  | 7823 |  |  |  | 925 | [10 empty] | 83.20 |  |  |  | 83.66 | [5 empty] | 82.69 |  |  | 89.06 |  |  |  | 1.71 |  | 1.46 | [8 empty] | 14.89 |  |  |  |  | 0.46
2009 |  |  |  | 7668.41 |  |  | 8279 |  |  |  | 925 | [10 empty] | 93.84 |  |  |  | 94.10 | [5 empty] | 94.64 |  |  | 94.51 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 5.82 |  |  |  |  | 0.26
2010 |  |  |  | 6651.23 |  |  | 7626 |  |  |  | 925 | [10 empty] | 82.04 |  |  |  | 82.31 | [5 empty] | 82.08 |  |  | 87.05 |  |  |  | 0.56 |  | 0.46 | [8 empty] | 17.23 |  |  |  |  | 0.27
2011 |  |  |  | 7328.17 |  |  | 8314 |  |  |  | 925 | [10 empty] | 89.65 |  |  |  | 90.28 | [5 empty] | 90.45 |  |  | 94.92 |  |  |  | 3.58 |  | 3.36 | [8 empty] | 6.36 |  |  |  |  | 0.63
2012 |  |  |  | 6802.21 |  |  | 7767 |  |  |  | 925 | [10 empty] | 85.94 |  |  |  | 86.34 | [5 empty] | 83.72 |  |  | 88.42 |  |  |  | 3.24 |  | 2.89 | [8 empty] | 10.76 |  |  |  |  | 0.41
2013 |  |  |  | 2630.28 |  |  | 3045 |  |  |  | 925 | [10 empty] | 32.61 |  |  |  | 32.62 | [5 empty] | 32.46 |  |  | 34.76 |  |  |  | 5.82 |  | 2.02 | [8 empty] | 65.36 |  |  |  |  | 0.01
2014 |  |  |  | 7821.17 |  |  | 8524 |  |  |  | 925 | [10 empty] | 94.28 |  |  |  | 94.57 | [5 empty] | 96.51 |  |  | 97.29 |  |  |  | 1.89 |  | 1.82 | [8 empty] | 3.61 |  |  |  |  | 0.29
2015 |  |  |  | 7404.36 |  |  | 7809 |  |  |  | 925 | [10 empty] | 87.61 |  |  |  | 87.79 | [5 empty] | 91.38 |  |  | 89.14 |  |  |  | 1.26 |  | 1.12 | [8 empty] | 11.09 |  |  |  |  | 0.17
2016 |  |  |  | 6910.57 |  |  | 7360 |  |  |  | 925 | [10 empty] | 82.20 |  |  |  | 82.32 | [5 empty] | 85.05 |  |  | 83.79 |  |  |  | 11.12 |  | 10.30 | [8 empty] | 7.39 |  |  |  |  | 0.12
2017 |  |  |  | 6307.00 |  |  | 6734 |  |  |  | 925 | [10 empty] | 74.22 |  |  |  | 74.29 | [5 empty] | 77.84 |  |  | 76.87 |  |  |  | 5.42 |  | 4.26 | [8 empty] | 21.45 |  |  |  |  | 0.07
2018 |  |  |  | 7352.87 |  |  | 7772 |  |  |  | 925 | [10 empty] | 87.37 |  |  |  | 87.42 | [5 empty] | 90.74 |  |  | 88.72 |  |  |  | 3.77 |  | 3.43 | [8 empty] | 9.16 |  |  |  |  | 0.05
2019 |  |  |  | 5918.57 |  |  | 6573 |  |  |  | 925 | [10 empty] | 70.29 |  |  |  | 70.31 | [5 empty] | 73.04 |  |  | 75.03 |  |  |  | 7.33 |  | 5.56 | [8 empty] | 24.13 |  |  |  |  | 0.03
2020 |  |  |  | 7313.92 |  |  | 7838 |  |  |  | 925 | [10 empty] | 87.74 |  |  |  | 87.86 | [5 empty] | 90.02 |  |  | 89.23 |  |  |  | 0.86 |  | 0.76 | [8 empty] | 11.38 |  |  |  |  | 0.11
2021 |  |  |  | 6939.32 |  |  | 7444 |  |  |  | 925 | [10 empty] | 83.12 |  |  |  | 83.80 | [5 empty] | 85.64 |  |  | 84.98 |  |  |  | 0.39 |  | 0.33 | [8 empty] | 15.87 |  |  |  |  | 0.68
2022 |  |  |  | 6641.85 |  |  | 7002 |  |  |  | 925 | [10 empty] | 79.30 |  |  |  | 79.46 | [5 empty] | 81.97 |  |  | 79.93 |  |  |  | 0.06 |  | 5.34 | [8 empty] | 15.21 |  |  |  |  | 0.16
2023 |  |  |  | 7182.68 |  |  | 7709 |  |  |  | 925 | [10 empty] | 86.63 |  |  |  | 86.91 | [5 empty] | 88.64 |  |  | 88.00 |  |  |  | 2.43 |  | 2.17 | [8 empty] | 10.92 |  |  |  |  | 0.29
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 134 | [14 empty] | 95
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 917 | [14 empty] | 1025
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 250
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 125
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 229
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 10
L. |  | Human factor related | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 9
Z. |  | Other | [39 empty] | 2
Subtotal | [22 empty] | 917 |  |  |  | 134 | [10 empty] | 1629 |  |  |  | 99 | [11 empty] | 19
Total | [22 empty] | 1051 | [14 empty] | 1747
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 16
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 5
14. |  |  | Safety Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [19 empty] | 134 | [14 empty] | 37
16. |  |  | Steam generation systems | [34 empty] | 1
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 5
32. |  |  | Feedwater and Main Steam System | [34 empty] | 8
34. |  |  | Miscellaneous Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 13
Total | [22 empty] | 134 | [14 empty] | 97
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-June, September-December. Additional electricity generation amounted to 162578 MWh. The unit was in the routine maintenance from 2023.04.08 to 2023.05.16. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.

## SMOLENSK-3
2023 Operating Experience
RU-67 | [8 empty] | SMOLENSK-3 | [26 empty] | RUSSIA
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Owner | [7 empty] | : | REA (Joint Stock Company 'Concern Rosenergoatom')
Reactor Supplier | [7 empty] | : | AEM (Atomenergomash)
Turbine Supplier | [7 empty] | : | KTF (Kharkiv Turbine Factory)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | LWGR / RBMK-1000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1984-05-01
Thermal power | [12 empty] | : |  |  | 3200 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1990-01-17
Gross electrical power | [12 empty] | : |  |  | 1000 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1990-10-12
Reference unit power (net) | [12 empty] | : |  |  | 925 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 33 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 284
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | ON-line | [11 empty] | Containment type | [15 empty] | : |  |  | Confinement
| Moderator material | [13 empty] | : |  |  | GRAPHITE | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | - | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 22200 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 11.8 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.59
| Active core height/length [m] | [13 empty] | : |  |  | 7 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 1661 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.5 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 175 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | PH / DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7227.81 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.89 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.06 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.78 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.1 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.12 %
Load Factor (LF) | [18 empty] | : | 89.2 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.03 %
Operating Factor (OF) | [18 empty] | : | 88.77 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 984 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 47.28 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 725.43 | 235.53 |  |  |  | 78.70 |  | 701.17 | [8 empty] | 699.78 |  |  | 670.99 | [6 empty] | 695.84 |  | 636.70 |  |  |  | 676.29 |  |  | 714.29 |  |  | 662.44 | [9 empty] | 730.66 |  |  | 7227.81
EAF [%] |  |  |  |  | 100.00 | 37.69 |  |  |  | 14.03 |  | 99.54 | [8 empty] | 97.82 |  |  | 99.82 | [6 empty] | 99.92 |  | 92.84 |  |  |  | 99.97 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.06
UCF [%] |  |  |  |  | 100.00 | 37.69 |  |  |  | 14.03 |  | 99.54 | [8 empty] | 97.82 |  |  | 99.90 | [6 empty] | 99.96 |  | 93.09 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.10
LF [%] |  |  |  |  | 105.41 | 37.89 |  |  |  | 11.44 |  | 105.28 | [8 empty] | 101.68 |  |  | 100.75 | [6 empty] | 101.11 |  | 92.52 |  |  |  | 101.54 |  |  | 103.79 |  |  | 99.47 | [9 empty] | 106.17 |  |  | 89.20
OF [%] |  |  |  |  | 100.00 | 39.73 |  |  |  | 27.69 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 94.49 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.77
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.18 |  |  | 0.10 | [6 empty] | 0.00 |  | 6.91 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.89
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.18 |  |  | 0.10 | [6 empty] | 0.00 |  | 6.91 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.78
PUF [%] |  |  |  |  | 0.00 | 62.31 |  |  |  | 85.97 |  | 0.46 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.04 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.12
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.09 | [6 empty] | 0.04 |  | 0.25 |  |  |  | 0.03 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.03
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 219914.21 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.24 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 79.29 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.92 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.76 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 17.32 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.54 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.47 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 81.55 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1990 |  |  |  | 4570.76 |  |  | 6767 |  |  |  | 925 | [10 empty] | 99.06 |  |  |  | 99.06 | [5 empty] | 101.20 |  |  | 100.00 |  |  |  | 0.62 |  | 0.62 | [8 empty] | 0.32 |  |  |  |  | 0.00
1991 |  |  |  | 6561.74 |  |  | 7338 |  |  |  | 925 | [10 empty] | 80.87 |  |  |  | 80.87 | [5 empty] | 80.98 |  |  | 83.77 |  |  |  | 3.91 |  | 3.29 | [8 empty] | 15.84 |  |  |  |  | 0.00
1992 |  |  |  | 6866.56 |  |  | 7515 |  |  |  | 925 | [10 empty] | 83.90 |  |  |  | 83.92 | [5 empty] | 84.52 |  |  | 85.56 |  |  |  | 6.83 |  | 6.15 | [8 empty] | 9.93 |  |  |  |  | 0.03
1993 |  |  |  | 6595.99 |  |  | 7419 |  |  |  | 925 | [10 empty] | 81.42 |  |  |  | 82.61 | [5 empty] | 81.40 |  |  | 84.69 |  |  |  | 1.76 |  | 1.48 | [8 empty] | 15.91 |  |  |  |  | 1.19
1994 |  |  |  | 5513.66 |  |  | 6701 |  |  |  | 925 | [10 empty] | 72.50 |  |  |  | 82.28 | [5 empty] | 68.04 |  |  | 76.50 |  |  |  | 0.43 |  | 0.35 | [8 empty] | 17.37 |  |  |  |  | 9.78
1995 |  |  |  | 5090.97 |  |  | 5844 |  |  |  | 925 | [10 empty] | 63.17 |  |  |  | 78.19 | [5 empty] | 62.83 |  |  | 66.71 |  |  |  | 1.13 |  | 0.89 | [8 empty] | 20.92 |  |  |  |  | 15.02
1996 |  |  |  | 6496.64 |  |  | 7268 |  |  |  | 925 | [10 empty] | 80.83 |  |  |  | 82.16 | [5 empty] | 79.96 |  |  | 82.74 |  |  |  | 7.42 |  | 6.58 | [8 empty] | 11.25 |  |  |  |  | 1.34
1997 |  |  |  | 5559.27 |  |  | 6469 |  |  |  | 925 | [10 empty] | 69.32 |  |  |  | 69.32 | [5 empty] | 68.61 |  |  | 73.85 |  |  |  | 6.03 |  | 4.45 | [8 empty] | 26.23 |  |  |  |  | 0.00
1998 |  |  |  | 4575.89 |  |  | 6162 |  |  |  | 925 | [10 empty] | 57.53 |  |  |  | 68.95 | [5 empty] | 56.47 |  |  | 70.34 |  |  |  | 3.48 |  | 2.49 | [8 empty] | 28.56 |  |  |  |  | 11.42
1999 |  |  |  | 6410.98 |  |  | 7063 |  |  |  | 925 | [10 empty] | 78.19 |  |  |  | 79.31 | [5 empty] | 79.12 |  |  | 80.63 |  |  |  | 0.39 |  | 0.31 | [8 empty] | 20.38 |  |  |  |  | 1.12
2000 |  |  |  | 6970.48 |  |  | 7542 |  |  |  | 925 | [10 empty] | 84.58 |  |  |  | 84.70 | [5 empty] | 85.79 |  |  | 85.86 |  |  |  | 2.37 |  | 2.06 | [8 empty] | 13.24 |  |  |  |  | 0.12
2001 |  |  |  | 6951.72 |  |  | 7823 |  |  |  | 925 | [10 empty] | 85.39 |  |  |  | 87.30 | [5 empty] | 85.79 |  |  | 89.30 |  |  |  | 0.15 |  | 0.13 | [8 empty] | 12.57 |  |  |  |  | 1.91
2002 |  |  |  | 7204.90 |  |  | 7831 |  |  |  | 925 | [10 empty] | 87.67 |  |  |  | 88.71 | [5 empty] | 88.92 |  |  | 89.39 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 11.02 |  |  |  |  | 1.03
2003 |  |  |  | 7038.23 |  |  | 7697 |  |  |  | 925 | [10 empty] | 86.26 |  |  |  | 87.09 | [5 empty] | 86.86 |  |  | 87.87 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 12.73 |  |  |  |  | 0.82
2004 |  |  |  | 7085.74 |  |  | 7765 |  |  |  | 925 | [10 empty] | 86.88 |  |  |  | 87.86 | [5 empty] | 87.21 |  |  | 88.40 |  |  |  | 0.00 |  | 0.08 | [8 empty] | 12.05 |  |  |  |  | 0.99
2005 |  |  |  | 7303.68 |  |  | 8192 |  |  |  | 925 | [10 empty] | 90.36 |  |  |  | 93.06 | [5 empty] | 90.14 |  |  | 93.52 |  |  |  | 1.07 |  | 1.01 | [8 empty] | 5.93 |  |  |  |  | 2.70
2006 |  |  |  | 4942.96 |  |  | 5631 |  |  |  | 925 | [10 empty] | 60.71 |  |  |  | 60.71 | [5 empty] | 61.00 |  |  | 64.28 |  |  |  | 4.39 |  | 3.15 | [8 empty] | 36.14 |  |  |  |  | 0.00
2007 |  |  |  | 7566.25 |  |  | 8247 |  |  |  | 925 | [10 empty] | 92.46 |  |  |  | 93.15 | [5 empty] | 93.38 |  |  | 94.14 |  |  |  | 1.48 |  | 1.40 | [8 empty] | 5.44 |  |  |  |  | 0.70
2008 |  |  |  | 5093.44 |  |  | 5396 |  |  |  | 925 | [10 empty] | 61.23 |  |  |  | 61.29 | [5 empty] | 62.69 |  |  | 61.43 |  |  |  | 0.07 |  | 0.04 | [8 empty] | 38.67 |  |  |  |  | 0.06
2009 |  |  |  | 6082.98 |  |  | 6706 |  |  |  | 925 | [10 empty] | 74.30 |  |  |  | 74.31 | [5 empty] | 75.07 |  |  | 76.55 |  |  |  | 1.66 |  | 1.26 | [8 empty] | 24.44 |  |  |  |  | 0.00
2010 |  |  |  | 7738.82 |  |  | 8233 |  |  |  | 925 | [10 empty] | 93.55 |  |  |  | 93.71 | [5 empty] | 95.51 |  |  | 93.98 |  |  |  | 0.12 |  | 0.38 | [8 empty] | 5.91 |  |  |  |  | 0.16
2011 |  |  |  | 6241.79 |  |  | 6579 |  |  |  | 925 | [10 empty] | 73.98 |  |  |  | 74.01 | [5 empty] | 77.04 |  |  | 75.11 |  |  |  | 0.15 |  | 0.11 | [8 empty] | 25.88 |  |  |  |  | 0.03
2012 |  |  |  | 5845.23 |  |  | 6279 |  |  |  | 925 | [10 empty] | 70.62 |  |  |  | 70.62 | [5 empty] | 71.94 |  |  | 71.48 |  |  |  | 7.04 |  | 5.35 | [8 empty] | 24.03 |  |  |  |  | 0.00
2013 |  |  |  | 7942.17 |  |  | 8471 |  |  |  | 925 | [10 empty] | 95.12 |  |  |  | 95.19 | [5 empty] | 98.02 |  |  | 96.70 |  |  |  | 2.12 |  | 2.06 | [8 empty] | 2.75 |  |  |  |  | 0.07
2014 |  |  |  | 6894.49 |  |  | 7219 |  |  |  | 925 | [10 empty] | 81.72 |  |  |  | 81.82 | [5 empty] | 85.08 |  |  | 82.40 |  |  |  | 0.30 |  | 0.24 | [8 empty] | 17.94 |  |  |  |  | 0.10
2015 |  |  |  | 8079.91 |  |  | 8364 |  |  |  | 925 | [10 empty] | 95.01 |  |  |  | 95.01 | [5 empty] | 99.71 |  |  | 95.48 |  |  |  | 0.33 |  | 0.31 | [8 empty] | 4.67 |  |  |  |  | 0.00
2016 |  |  |  | 7116.59 |  |  | 7352 |  |  |  | 925 | [10 empty] | 83.34 |  |  |  | 83.35 | [5 empty] | 87.59 |  |  | 83.70 |  |  |  | 2.89 |  | 2.48 | [8 empty] | 14.17 |  |  |  |  | 0.02
2017 |  |  |  | 7946.26 |  |  | 8266 |  |  |  | 925 | [10 empty] | 93.42 |  |  |  | 93.49 | [5 empty] | 98.07 |  |  | 94.36 |  |  |  | 0.12 |  | 0.11 | [8 empty] | 6.40 |  |  |  |  | 0.06
2018 |  |  |  | 3494.62 |  |  | 3601 |  |  |  | 925 | [10 empty] | 40.84 |  |  |  | 40.84 | [5 empty] | 43.13 |  |  | 41.11 |  |  |  | 0.66 |  | 1.09 | [8 empty] | 58.07 |  |  |  |  | 0.00
2019 |  |  |  | 6207.98 |  |  | 6723 |  |  |  | 925 | [10 empty] | 74.43 |  |  |  | 74.46 | [5 empty] | 76.61 |  |  | 76.75 |  |  |  | 5.25 |  | 4.90 | [8 empty] | 20.64 |  |  |  |  | 0.03
2020 |  |  |  | 6927.47 |  |  | 7624 |  |  |  | 925 | [10 empty] | 83.21 |  |  |  | 83.22 | [5 empty] | 85.26 |  |  | 86.79 |  |  |  | 0.35 |  | 0.29 | [8 empty] | 16.49 |  |  |  |  | 0.00
2021 |  |  |  | 7044.34 |  |  | 7418 |  |  |  | 925 | [10 empty] | 83.94 |  |  |  | 84.13 | [5 empty] | 86.93 |  |  | 84.68 |  |  |  | 0.02 |  | 0.01 | [8 empty] | 15.85 |  |  |  |  | 0.19
2022 |  |  |  | 6464.67 |  |  | 6991 |  |  |  | 925 | [10 empty] | 77.70 |  |  |  | 77.76 | [5 empty] | 79.78 |  |  | 79.81 |  |  |  | 11.48 |  | 10.09 | [8 empty] | 12.15 |  |  |  |  | 0.06
2023 |  |  |  | 7227.81 |  |  | 7776 |  |  |  | 925 | [10 empty] | 87.06 |  |  |  | 87.10 | [5 empty] | 89.20 |  |  | 88.77 |  |  |  | 0.89 |  | 0.78 | [8 empty] | 12.12 |  |  |  |  | 0.03
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1990 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 41 | [14 empty] | 92
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 943 | [14 empty] | 1012
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 238
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 162
G. |  | Major backfitting, refurbishment or upgrading activities without refuelling | [35 empty] | 94
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 1
L. |  | Human factor related | [39 empty] | 2
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [51 empty] | 48
Z. |  | Other | [39 empty] | 16
Subtotal | [22 empty] | 943 |  |  |  | 41 | [10 empty] | 1506 |  |  |  | 110 | [11 empty] | 49
Total | [22 empty] | 984 | [14 empty] | 1665
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1990 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 13
12. |  |  | Reactor I&C Systems | [34 empty] | 12
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 8
16. |  |  | Steam generation systems | [34 empty] | 27
31. |  |  | Turbine and auxiliaries | [34 empty] | 8
32. |  |  | Feedwater and Main Steam System | [34 empty] | 4
34. |  |  | Miscellaneous Systems | [34 empty] | 4
35. |  |  | All other I&C Systems | [34 empty] | 3
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [19 empty] | 41 | [14 empty] | 8
Total | [22 empty] | 41 | [14 empty] | 92
Highlights (2023)
The Russian NPPs are operating in the baseload mode agreed with the Russia's Federal Energy Commission. Unit operation at power level above installed capacity took place in January-February, April-December. Additional electricity generation amounted to 236885 MWh. The unit was in the intermediate maintenance outage from 2023.02.12 to 2023.03.23. Radionuclides content in the monitored environmental objects in the plant vicinity was on the level of average background values typical for the European part of the Russian Federation.