## FORSMARK-1
2023 Operating Experience
SE-9 | [8 empty] | FORSMARK-1 | [26 empty] | SWEDEN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FKA (FORSMARK KRAFTGRUPP AB)
Owner | [7 empty] | : | FKA (FORSMARK KRAFTGRUPP AB)
Reactor Supplier | [7 empty] | : | ABB ATOM (ABB ATOM (formerly ASEA-ATOM))
Turbine Supplier | [7 empty] | : | STAL (STAL-LAVAL)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / AA-III, BWR-2500 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-06-01
Thermal power | [12 empty] | : |  |  | 3075 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-06-06
Gross electrical power | [12 empty] | : |  |  | 1078 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1980-12-10
Reference unit power (net) | [12 empty] | : |  |  | 1040 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.55
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.60 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 17 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 48000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.51 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.35
| Active core height/length [m] | [13 empty] | : |  |  | 3.68 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 21.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 676 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 161 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7813.5 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.39 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.2 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.01 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.92 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.07 %
Load Factor (LF) | [18 empty] | : | 85.76 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.72 %
Operating Factor (OF) | [18 empty] | : | 92.79 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 632 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 753.51 | 678.12 |  |  |  | 752.62 |  | 679.00 | [8 empty] | 157.53 |  |  | 705.98 | [6 empty] | 733.58 |  | 726.03 |  |  |  | 517.25 |  |  | 639.08 |  |  | 726.09 | [9 empty] | 744.72 |  |  | 7813.50
EAF [%] |  |  |  |  | 99.99 | 99.58 |  |  |  | 100.00 |  | 99.08 | [8 empty] | 20.80 |  |  | 94.81 | [6 empty] | 97.40 |  | 97.93 |  |  |  | 86.74 |  |  | 99.79 |  |  | 99.56 | [9 empty] | 100.00 |  |  | 91.20
UCF [%] |  |  |  |  | 99.99 | 99.58 |  |  |  | 100.00 |  | 99.08 | [8 empty] | 20.84 |  |  | 97.19 | [6 empty] | 100.00 |  | 99.55 |  |  |  | 88.52 |  |  | 100.00 |  |  | 99.56 | [9 empty] | 100.00 |  |  | 91.92
LF [%] |  |  |  |  | 97.38 | 97.03 |  |  |  | 97.40 |  | 90.68 | [8 empty] | 20.36 |  |  | 94.28 | [6 empty] | 94.81 |  | 93.83 |  |  |  | 69.08 |  |  | 82.48 |  |  | 96.97 | [9 empty] | 96.25 |  |  | 85.76
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 96.67 | [8 empty] | 27.15 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 90.83 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 92.79
FLR [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.92 | [8 empty] | 13.22 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 11.48 |  |  | 0.00 |  |  | 0.11 | [9 empty] | 0.00 |  |  | 1.39
UCL [%] |  |  |  |  | 0.01 | 0.00 |  |  |  | 0.00 |  | 0.92 | [8 empty] | 11.51 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 11.48 |  |  | 0.00 |  |  | 0.11 | [9 empty] | 0.00 |  |  | 2.01
PUF [%] |  |  |  |  | 0.00 | 0.42 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 67.65 |  |  | 2.81 | [6 empty] | 0.00 |  | 0.45 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.34 | [9 empty] | 0.00 |  |  | 6.07
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.04 |  |  | 2.38 | [6 empty] | 2.60 |  | 1.62 |  |  |  | 1.77 |  |  | 0.21 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.72
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 303249.26 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.76 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 84.68 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.61 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 86.64 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.75 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.96 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.96 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.93 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1980 |  |  |  | 2200.90 |  |  | 5016 |  |  |  | 928 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 100.00 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1981 |  |  |  | 6063.70 |  |  | 7305 |  |  |  | 900 | [10 empty] | 76.91 |  |  |  | 76.91 | [5 empty] | 76.91 |  |  | 83.39 |  |  |  | 8.70 |  | 7.33 | [8 empty] | 15.76 |  |  |  |  | 0.00
1982 |  |  |  | 5548.10 |  |  | 7131 |  |  |  | 900 | [10 empty] | 70.37 |  |  |  | 70.37 | [5 empty] | 70.37 |  |  | 81.40 |  |  |  | 18.09 |  | 15.54 | [8 empty] | 14.09 |  |  |  |  | 0.00
1983 |  |  |  | 5926.00 |  |  | 8095 |  |  |  | 900 | [10 empty] | 75.17 |  |  |  | 75.17 | [5 empty] | 75.16 |  |  | 92.41 |  |  |  | 15.95 |  | 14.26 | [8 empty] | 10.57 |  |  |  |  | 0.00
1984 |  |  |  | 6461.80 |  |  | 8207 |  |  |  | 900 | [10 empty] | 91.90 |  |  |  | 91.90 | [5 empty] | 81.74 |  |  | 93.43 |  |  |  | 1.77 |  | 1.65 | [8 empty] | 6.45 |  |  |  |  | 0.00
1985 |  |  |  | 5587.57 |  |  | 7773 |  |  |  | 900 | [10 empty] | 79.42 |  |  |  | 79.42 | [5 empty] | 70.87 |  |  | 88.73 |  |  |  | 1.82 |  | 1.48 | [8 empty] | 19.10 |  |  |  |  | 0.00
1986 |  |  |  | 7317.15 |  |  | 8303 |  |  |  | 954 | [10 empty] | 89.83 |  |  |  | 89.83 | [5 empty] | 87.53 |  |  | 94.78 |  |  |  | 0.94 |  | 0.85 | [8 empty] | 9.31 |  |  |  |  | 0.00
1987 |  |  |  | 6493.39 |  |  | 8291 |  |  |  | 970 | [10 empty] | 79.45 |  |  |  | 79.45 | [5 empty] | 76.42 |  |  | 94.65 |  |  |  | 0.29 |  | 0.23 | [8 empty] | 20.32 |  |  |  |  | 0.00
1988 |  |  |  | 6852.84 |  |  | 7739 |  |  |  | 970 | [10 empty] | 81.84 |  |  |  | 81.84 | [5 empty] | 80.43 |  |  | 88.10 |  |  |  | 5.18 |  | 4.48 | [8 empty] | 13.68 |  |  |  |  | 0.00
1989 |  |  |  | 6138.64 |  |  | 7907 |  |  |  | 969 | [10 empty] | 85.46 |  |  |  | 85.46 | [5 empty] | 72.30 |  |  | 90.26 |  |  |  | 2.53 |  | 2.22 | [8 empty] | 12.32 |  |  |  |  | 0.00
1990 |  |  |  | 6257.49 |  |  | 7885 |  |  |  | 972 | [10 empty] | 85.83 |  |  |  | 85.83 | [5 empty] | 73.49 |  |  | 90.01 |  |  |  | 3.25 |  | 2.89 | [8 empty] | 11.28 |  |  |  |  | 0.00
1991 |  |  |  | 7487.58 |  |  | 8122 |  |  |  | 968 | [10 empty] | 88.26 |  |  |  | 90.58 | [5 empty] | 88.30 |  |  | 92.72 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 9.32 |  |  |  |  | 2.32
1992 |  |  |  | 6833.64 |  |  | 8175 |  |  |  | 968 | [10 empty] | 80.28 |  |  |  | 85.22 | [5 empty] | 80.36 |  |  | 93.06 |  |  |  | 4.53 |  | 4.04 | [8 empty] | 10.73 |  |  |  |  | 4.94
1993 |  |  |  | 7022.83 |  |  | 8010 |  |  |  | 968 | [10 empty] | 82.73 |  |  |  | 91.93 | [5 empty] | 82.81 |  |  | 91.43 |  |  |  | 1.46 |  | 1.36 | [8 empty] | 6.70 |  |  |  |  | 9.20
1994 |  |  |  | 7398.21 |  |  | 8109 |  |  |  | 968 | [10 empty] | 87.02 |  |  |  | 91.35 | [5 empty] | 87.25 |  |  | 92.57 |  |  |  | 1.31 |  | 1.21 | [8 empty] | 7.44 |  |  |  |  | 4.33
1995 |  |  |  | 7325.18 |  |  | 8173 |  |  |  | 968 | [10 empty] | 86.19 |  |  |  | 91.29 | [5 empty] | 86.39 |  |  | 93.30 |  |  |  | 2.45 |  | 2.29 | [8 empty] | 6.42 |  |  |  |  | 5.11
1996 |  |  |  | 7311.38 |  |  | 8412 |  |  |  | 968 | [10 empty] | 86.42 |  |  |  | 95.27 | [5 empty] | 85.99 |  |  | 95.77 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 4.70 |  |  |  |  | 8.84
1997 |  |  |  | 5402.87 |  |  | 6255 |  |  |  | 968 | [10 empty] | 64.57 |  |  |  | 64.57 | [5 empty] | 63.54 |  |  | 71.21 |  |  |  | 0.55 |  | 0.36 | [8 empty] | 35.08 |  |  |  |  | 0.00
1998 |  |  |  | 7307.70 |  |  | 8265 |  |  |  | 968 | [10 empty] | 93.64 |  |  |  | 93.64 | [5 empty] | 86.18 |  |  | 94.35 |  |  |  | 1.28 |  | 1.21 | [8 empty] | 5.14 |  |  |  |  | 0.00
1999 |  |  |  | 7582.73 |  |  | 8420 |  |  |  | 968 | [10 empty] | 96.29 |  |  |  | 96.69 | [5 empty] | 89.42 |  |  | 96.12 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 3.27 |  |  |  |  | 0.40
2000 |  |  |  | 5730.82 |  |  | 7202 |  |  |  | 968 | [10 empty] | 67.39 |  |  |  | 85.94 | [5 empty] | 67.40 |  |  | 81.99 |  |  |  | 0.24 |  | 0.21 | [8 empty] | 13.86 |  |  |  |  | 18.55
2001 |  |  |  | 7286.12 |  |  | 8482 |  |  |  | 968 | [10 empty] | 86.25 |  |  |  | 94.77 | [5 empty] | 85.92 |  |  | 96.83 |  |  |  | 0.84 |  | 0.80 | [8 empty] | 4.43 |  |  |  |  | 8.51
2002 |  |  |  | 7143.77 |  |  | 7978 |  |  |  | 961 | [10 empty] | 86.02 |  |  |  | 90.04 | [5 empty] | 84.86 |  |  | 91.07 |  |  |  | 4.69 |  | 4.43 | [8 empty] | 5.53 |  |  |  |  | 4.02
2003 |  |  |  | 7456.00 |  |  | 8093 |  |  |  | 961 | [10 empty] | 88.49 |  |  |  | 88.49 | [5 empty] | 88.56 |  |  | 92.38 |  |  |  | 0.52 |  | 1.36 | [8 empty] | 10.15 |  |  |  |  | 0.00
2004 |  |  |  | 8032.28 |  |  | 8555 |  |  |  | 961 | [10 empty] | 95.65 |  |  |  | 97.52 | [5 empty] | 95.15 |  |  | 97.39 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 2.45 |  |  |  |  | 1.87
2005 |  |  |  | 7291.06 |  |  | 7648 |  |  |  | 1011 | [10 empty] | 84.38 |  |  |  | 85.43 | [5 empty] | 85.13 |  |  | 87.31 |  |  |  | 2.45 |  | 2.15 | [8 empty] | 12.43 |  |  |  |  | 1.05
2006 |  |  |  | 6683.92 |  |  | 6806 |  |  |  | 995 | [10 empty] | 75.43 |  |  |  | 76.50 | [5 empty] | 75.47 |  |  | 77.69 |  |  |  | 21.61 |  | 21.09 | [8 empty] | 2.40 |  |  |  |  | 1.07
2007 |  |  |  | 6961.43 |  |  | 7204 |  |  |  | 987 | [10 empty] | 80.38 |  |  |  | 81.12 | [5 empty] | 80.52 |  |  | 82.24 |  |  |  | 14.03 |  | 13.23 | [8 empty] | 5.65 |  |  |  |  | 0.74
2008 |  |  |  | 6973.66 |  |  | 7442 |  |  |  | 978 | [10 empty] | 80.76 |  |  |  | 81.41 | [5 empty] | 81.10 |  |  | 84.71 |  |  |  | 3.25 |  | 4.51 | [8 empty] | 14.07 |  |  |  |  | 0.65
2009 |  |  |  | 7555.38 |  |  | 8029 |  |  |  | 978 | [10 empty] | 87.90 |  |  |  | 88.35 | [5 empty] | 88.19 |  |  | 91.66 |  |  |  | 4.80 |  | 4.88 | [8 empty] | 6.77 |  |  |  |  | 0.46
2010 |  |  |  | 7993.61 |  |  | 8283 |  |  |  | 978 | [10 empty] | 92.83 |  |  |  | 93.38 | [5 empty] | 93.30 |  |  | 94.55 |  |  |  | 0.09 |  | 0.49 | [8 empty] | 6.13 |  |  |  |  | 0.55
2011 |  |  |  | 6776.59 |  |  | 7005 |  |  |  | 984 | [10 empty] | 78.44 |  |  |  | 79.22 | [5 empty] | 79.02 |  |  | 79.97 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 20.76 |  |  |  |  | 0.77
2012 |  |  |  | 7615.92 |  |  | 7938 |  |  |  | 984 | [10 empty] | 87.69 |  |  |  | 88.16 | [5 empty] | 88.11 |  |  | 90.37 |  |  |  | 2.25 |  | 2.03 | [8 empty] | 9.80 |  |  |  |  | 0.48
2013 |  |  |  | 7539.63 |  |  | 7782 |  |  |  | 984 | [10 empty] | 87.12 |  |  |  | 87.78 | [5 empty] | 87.47 |  |  | 88.84 |  |  |  | 2.02 |  | 5.00 | [8 empty] | 7.23 |  |  |  |  | 0.66
2014 |  |  |  | 8085.96 |  |  | 8307 |  |  |  | 984 | [10 empty] | 93.54 |  |  |  | 94.41 | [5 empty] | 93.81 |  |  | 94.83 |  |  |  | 0.05 |  | 0.05 | [8 empty] | 5.54 |  |  |  |  | 0.87
2015 |  |  |  | 6570.19 |  |  | 7153 |  |  |  | 984 | [10 empty] | 79.10 |  |  |  | 79.76 | [5 empty] | 76.22 |  |  | 81.66 |  |  |  | 8.82 |  | 8.49 | [8 empty] | 11.75 |  |  |  |  | 0.66
2016 |  |  |  | 8214.31 |  |  | 8421 |  |  |  | 984 | [10 empty] | 94.49 |  |  |  | 95.40 | [5 empty] | 95.04 |  |  | 95.87 |  |  |  | 0.04 |  | 0.04 | [8 empty] | 4.56 |  |  |  |  | 0.91
2017 |  |  |  | 7623.46 |  |  | 7994 |  |  |  | 984 | [10 empty] | 87.85 |  |  |  | 89.45 | [5 empty] | 88.44 |  |  | 91.26 |  |  |  | 1.34 |  | 2.03 | [8 empty] | 8.52 |  |  |  |  | 1.60
2018 |  |  |  | 8087.58 |  |  | 8448 |  |  |  | 986 | [10 empty] | 93.30 |  |  |  | 94.76 | [5 empty] | 93.70 |  |  | 96.44 |  |  |  | 1.36 |  | 1.30 | [8 empty] | 3.94 |  |  |  |  | 1.46
2019 |  |  |  | 7432.93 |  |  | 7699 |  |  |  | 990 | [10 empty] | 85.54 |  |  |  | 86.35 | [5 empty] | 85.87 |  |  | 87.89 |  |  |  | 2.06 |  | 1.81 | [8 empty] | 11.83 |  |  |  |  | 0.81
2020 |  |  |  | 6410.35 |  |  | 7652 |  |  |  | 990 | [10 empty] | 78.29 |  |  |  | 79.04 | [5 empty] | 73.71 |  |  | 87.11 |  |  |  | 11.72 |  | 10.49 | [8 empty] | 10.46 |  |  |  |  | 0.76
2021 |  |  |  | 7935.93 |  |  | 8295 |  |  |  | 990 | [10 empty] | 91.17 |  |  |  | 92.33 | [5 empty] | 91.51 |  |  | 94.69 |  |  |  | 1.86 |  | 1.75 | [8 empty] | 5.92 |  |  |  |  | 1.16
2022 |  |  |  | 7253.90 |  |  | 7775 |  |  |  | 1040 | [10 empty] | 82.88 |  |  |  | 83.64 | [5 empty] | 82.94 |  |  | 88.76 |  |  |  | 6.45 |  | 6.29 | [8 empty] | 10.07 |  |  |  |  | 0.75
2023 |  |  |  | 7813.50 |  |  | 8128 |  |  |  | 1040 | [10 empty] | 91.20 |  |  |  | 91.92 | [5 empty] | 85.76 |  |  | 92.79 |  |  |  | 1.39 |  | 2.01 | [8 empty] | 6.07 |  |  |  |  | 0.72
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1980 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 128 | [14 empty] | 144
B. |  | Refuelling without maintenance | [35 empty] | 8
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 480 | [14 empty] | 665
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 1
E. |  | Testing of plant systems or components | [35 empty] | 3
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 23
H. |  | Nuclear regulatory requirements | [39 empty] | 6
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 24 | [19 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 10
L. |  | Human factor related | [39 empty] | 26
P. |  | Fire | [39 empty] | 0
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 5
Subtotal | [22 empty] | 480 |  |  |  | 128 | [6 empty] | 24 |  |  |  | 700 |  |  |  | 181 | [11 empty] | 12
Total | [22 empty] | 632 | [14 empty] | 893
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1980 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 62 | [14 empty] | 47
12. |  |  | Reactor I&C Systems | [34 empty] | 13
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 17
14. |  |  | Safety Systems | [34 empty] | 29
15. |  |  | Reactor Cooling Systems | [19 empty] | 66 | [14 empty] | 11
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [34 empty] | 8
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 1
41. |  |  | Main Generator Systems | [34 empty] | 3
42. |  |  | Electrical Power Supply Systems | [34 empty] | 41
Total | [22 empty] | 128 | [14 empty] | 174
Highlights (2023)
Annual outage in May.

## FORSMARK-2
2023 Operating Experience
SE-11 | [8 empty] | FORSMARK-2 | [26 empty] | SWEDEN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FKA (FORSMARK KRAFTGRUPP AB)
Owner | [7 empty] | : | FKA (FORSMARK KRAFTGRUPP AB)
Reactor Supplier | [7 empty] | : | ABB ATOM (ABB ATOM (formerly ASEA-ATOM))
Turbine Supplier | [7 empty] | : | STAL (STAL-LAVAL)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / AA-III, BWR-2500 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1975-01-01
Thermal power | [12 empty] | : |  |  | 3253 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1981-01-26
Gross electrical power | [12 empty] | : |  |  | 1160 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-07-07
Reference unit power (net) | [12 empty] | : |  |  | 1121 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 42 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.55
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.60 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 48000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.51 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.35
| Active core height/length [m] | [13 empty] | : |  |  | 3.68 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 21.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 676 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 4
| Number of control rod assemblies | [13 empty] | : |  |  | 161 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7354.48 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 9.92 %
Energy Availability Factor (EAF) | [18 empty] | : | 76.36 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 9.52 %
Unit Capability Factor (UCF) | [18 empty] | : | 76.88 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 13.6 %
Load Factor (LF) | [18 empty] | : | 74.89 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.51 %
Operating Factor (OF) | [18 empty] | : | 85.68 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1254 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 835.15 | 730.76 |  |  |  | 838.73 |  | 708.17 | [8 empty] | 688.67 |  |  | 723.38 | [6 empty] | 679.53 |  | 361.48 |  |  |  | 28.16 |  |  | 164.84 |  |  | 796.39 | [9 empty] | 799.24 |  |  | 7354.48
EAF [%] |  |  |  |  | 99.37 | 96.26 |  |  |  | 99.94 |  | 99.94 | [8 empty] | 85.97 |  |  | 90.07 | [6 empty] | 85.18 |  | 43.34 |  |  |  | 3.49 |  |  | 19.71 |  |  | 98.40 | [9 empty] | 96.30 |  |  | 76.36
UCF [%] |  |  |  |  | 99.37 | 96.26 |  |  |  | 99.94 |  | 99.94 | [8 empty] | 85.97 |  |  | 92.68 | [6 empty] | 87.75 |  | 44.15 |  |  |  | 3.61 |  |  | 19.71 |  |  | 98.40 | [9 empty] | 96.30 |  |  | 76.88
LF [%] |  |  |  |  | 100.13 | 97.01 |  |  |  | 100.70 |  | 87.74 | [8 empty] | 82.57 |  |  | 89.62 | [6 empty] | 81.48 |  | 43.34 |  |  |  | 3.49 |  |  | 19.74 |  |  | 98.67 | [9 empty] | 95.83 |  |  | 74.89
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 89.72 | [8 empty] | 86.83 |  |  | 99.17 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 8.61 |  |  | 43.89 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.68
FLR [%] |  |  |  |  | 0.00 | 3.69 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 13.99 |  |  | 7.23 | [6 empty] | 12.18 |  | 55.85 |  |  |  | 50.66 |  |  | 0.00 |  |  | 0.06 | [9 empty] | 3.70 |  |  | 9.92
UCL [%] |  |  |  |  | 0.00 | 3.69 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 13.99 |  |  | 7.22 | [6 empty] | 12.17 |  | 55.85 |  |  |  | 3.71 |  |  | 12.44 |  |  | 0.06 | [9 empty] | 3.70 |  |  | 9.52
PUF [%] |  |  |  |  | 0.63 | 0.05 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 0.04 |  |  | 0.10 | [6 empty] | 0.08 |  | 0.00 |  |  |  | 92.68 |  |  | 67.85 |  |  | 1.55 | [9 empty] | 0.00 |  |  | 13.60
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 2.61 | [6 empty] | 2.57 |  | 0.81 |  |  |  | 0.12 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.51
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 301755.26 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.48 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.84 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.95 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.41 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.81 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.22 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 2870.70 |  |  | 3977 |  |  |  | 900 | [10 empty] | 72.23 |  |  |  | 72.23 | [5 empty] | 72.23 |  |  | 90.06 |  |  |  | 22.48 |  | 20.94 | [8 empty] | 6.83 |  |  |  |  | 0.00
1982 |  |  |  | 5316.40 |  |  | 6076 |  |  |  | 900 | [10 empty] | 67.40 |  |  |  | 67.40 | [5 empty] | 67.43 |  |  | 69.36 |  |  |  | 24.62 |  | 22.01 | [8 empty] | 10.58 |  |  |  |  | 0.00
1983 |  |  |  | 5484.40 |  |  | 7879 |  |  |  | 900 | [10 empty] | 69.56 |  |  |  | 69.56 | [5 empty] | 69.56 |  |  | 89.94 |  |  |  | 19.21 |  | 16.54 | [8 empty] | 13.89 |  |  |  |  | 0.00
1984 |  |  |  | 5911.73 |  |  | 7442 |  |  |  | 900 | [10 empty] | 82.56 |  |  |  | 82.57 | [5 empty] | 74.78 |  |  | 84.72 |  |  |  | 7.71 |  | 6.90 | [8 empty] | 10.53 |  |  |  |  | 0.01
1985 |  |  |  | 5735.38 |  |  | 8048 |  |  |  | 900 | [10 empty] | 83.81 |  |  |  | 83.81 | [5 empty] | 72.75 |  |  | 91.87 |  |  |  | 4.41 |  | 3.87 | [8 empty] | 12.32 |  |  |  |  | 0.00
1986 |  |  |  | 6987.86 |  |  | 8231 |  |  |  | 938 | [10 empty] | 86.54 |  |  |  | 86.54 | [5 empty] | 84.99 |  |  | 93.96 |  |  |  | 2.06 |  | 1.82 | [8 empty] | 11.64 |  |  |  |  | 0.00
1987 |  |  |  | 6553.84 |  |  | 8190 |  |  |  | 949 | [10 empty] | 85.48 |  |  |  | 85.48 | [5 empty] | 78.84 |  |  | 93.49 |  |  |  | 1.47 |  | 1.27 | [8 empty] | 13.25 |  |  |  |  | 0.00
1988 |  |  |  | 6976.19 |  |  | 8032 |  |  |  | 963 | [10 empty] | 83.19 |  |  |  | 83.19 | [5 empty] | 82.47 |  |  | 91.44 |  |  |  | 4.17 |  | 3.62 | [8 empty] | 13.19 |  |  |  |  | 0.00
1989 |  |  |  | 5943.42 |  |  | 8222 |  |  |  | 964 | [10 empty] | 90.02 |  |  |  | 90.02 | [5 empty] | 70.36 |  |  | 93.86 |  |  |  | 1.11 |  | 1.01 | [8 empty] | 8.96 |  |  |  |  | 0.00
1990 |  |  |  | 6426.24 |  |  | 8119 |  |  |  | 972 | [10 empty] | 88.64 |  |  |  | 88.64 | [5 empty] | 75.47 |  |  | 92.68 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 11.18 |  |  |  |  | 0.00
1991 |  |  |  | 7155.18 |  |  | 8084 |  |  |  | 969 | [10 empty] | 84.19 |  |  |  | 85.78 | [5 empty] | 84.29 |  |  | 92.28 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 14.20 |  |  |  |  | 1.58
1992 |  |  |  | 6748.91 |  |  | 8294 |  |  |  | 969 | [10 empty] | 79.22 |  |  |  | 86.22 | [5 empty] | 79.29 |  |  | 94.42 |  |  |  | 2.04 |  | 1.79 | [8 empty] | 11.98 |  |  |  |  | 7.00
1993 |  |  |  | 6715.51 |  |  | 7684 |  |  |  | 969 | [10 empty] | 79.14 |  |  |  | 88.82 | [5 empty] | 79.11 |  |  | 87.72 |  |  |  | 0.30 |  | 0.27 | [8 empty] | 10.91 |  |  |  |  | 9.68
1994 |  |  |  | 7679.45 |  |  | 8194 |  |  |  | 969 | [10 empty] | 90.44 |  |  |  | 92.53 | [5 empty] | 90.47 |  |  | 93.54 |  |  |  | 0.94 |  | 0.88 | [8 empty] | 6.60 |  |  |  |  | 2.08
1995 |  |  |  | 7149.21 |  |  | 8144 |  |  |  | 969 | [10 empty] | 84.14 |  |  |  | 91.61 | [5 empty] | 84.21 |  |  | 92.96 |  |  |  | 1.27 |  | 1.18 | [8 empty] | 7.21 |  |  |  |  | 7.47
1996 |  |  |  | 7348.24 |  |  | 8135 |  |  |  | 969 | [10 empty] | 86.21 |  |  |  | 91.24 | [5 empty] | 86.32 |  |  | 92.60 |  |  |  | 2.72 |  | 2.55 | [8 empty] | 6.20 |  |  |  |  | 5.03
1997 |  |  |  | 7325.29 |  |  | 7927 |  |  |  | 969 | [10 empty] | 87.44 |  |  |  | 87.44 | [5 empty] | 86.06 |  |  | 90.24 |  |  |  | 2.57 |  | 2.31 | [8 empty] | 10.25 |  |  |  |  | 0.00
1998 |  |  |  | 7198.57 |  |  | 8240 |  |  |  | 969 | [10 empty] | 91.87 |  |  |  | 92.09 | [5 empty] | 84.80 |  |  | 94.06 |  |  |  | 3.00 |  | 2.84 | [8 empty] | 5.06 |  |  |  |  | 0.22
1999 |  |  |  | 7292.27 |  |  | 8117 |  |  |  | 964 | [10 empty] | 91.75 |  |  |  | 91.75 | [5 empty] | 86.02 |  |  | 92.66 |  |  |  | 1.27 |  | 1.18 | [8 empty] | 7.07 |  |  |  |  | 0.00
2000 |  |  |  | 5428.10 |  |  | 6939 |  |  |  | 964 | [10 empty] | 66.32 |  |  |  | 79.62 | [5 empty] | 64.10 |  |  | 79.00 |  |  |  | 6.00 |  | 5.08 | [8 empty] | 15.30 |  |  |  |  | 13.30
2001 |  |  |  | 7399.55 |  |  | 8321 |  |  |  | 964 | [10 empty] | 88.83 |  |  |  | 92.34 | [5 empty] | 87.62 |  |  | 94.99 |  |  |  | 3.87 |  | 3.71 | [8 empty] | 3.95 |  |  |  |  | 3.51
2002 |  |  |  | 6823.89 |  |  | 8155 |  |  |  | 959 | [10 empty] | 82.20 |  |  |  | 89.92 | [5 empty] | 81.02 |  |  | 93.09 |  |  |  | 3.82 |  | 3.57 | [8 empty] | 6.51 |  |  |  |  | 7.72
2003 |  |  |  | 7303.88 |  |  | 7916 |  |  |  | 954 | [10 empty] | 87.06 |  |  |  | 87.06 | [5 empty] | 87.05 |  |  | 90.35 |  |  |  | 0.86 |  | 1.91 | [8 empty] | 11.03 |  |  |  |  | 0.00
2004 |  |  |  | 7982.20 |  |  | 8529 |  |  |  | 954 | [10 empty] | 95.21 |  |  |  | 96.92 | [5 empty] | 95.25 |  |  | 97.10 |  |  |  | 0.12 |  | 0.12 | [8 empty] | 2.96 |  |  |  |  | 1.71
2005 |  |  |  | 7790.11 |  |  | 8348 |  |  |  | 951 | [10 empty] | 93.68 |  |  |  | 94.64 | [5 empty] | 93.51 |  |  | 95.30 |  |  |  | 1.78 |  | 1.72 | [8 empty] | 3.64 |  |  |  |  | 0.96
2006 |  |  |  | 6011.87 |  |  | 6426 |  |  |  | 951 | [10 empty] | 72.49 |  |  |  | 73.11 | [5 empty] | 72.16 |  |  | 73.36 |  |  |  | 18.80 |  | 16.93 | [8 empty] | 9.97 |  |  |  |  | 0.61
2007 |  |  |  | 7470.12 |  |  | 7750 |  |  |  | 1000 | [10 empty] | 85.03 |  |  |  | 85.67 | [5 empty] | 85.27 |  |  | 88.46 |  |  |  | 8.07 |  | 8.39 | [8 empty] | 5.94 |  |  |  |  | 0.64
2008 |  |  |  | 6920.12 |  |  | 7342 |  |  |  | 990 | [10 empty] | 79.18 |  |  |  | 79.68 | [5 empty] | 79.45 |  |  | 83.58 |  |  |  | 11.44 |  | 10.30 | [8 empty] | 10.02 |  |  |  |  | 0.51
2009 |  |  |  | 5530.68 |  |  | 5902 |  |  |  | 990 | [10 empty] | 63.57 |  |  |  | 64.13 | [5 empty] | 63.77 |  |  | 67.37 |  |  |  | 5.11 |  | 20.46 | [8 empty] | 15.42 |  |  |  |  | 0.56
2010 |  |  |  | 3334.15 |  |  | 7635 |  |  |  | 990 | [10 empty] | 38.26 |  |  |  | 38.58 | [5 empty] | 38.45 |  |  | 87.16 |  |  |  | 54.60 |  | 48.30 | [8 empty] | 13.11 |  |  |  |  | 0.32
2011 |  |  |  | 8161.59 |  |  | 8259 |  |  |  | 996 | [10 empty] | 93.23 |  |  |  | 93.92 | [5 empty] | 93.82 |  |  | 94.28 |  |  |  | 0.07 |  | 0.07 | [8 empty] | 6.01 |  |  |  |  | 0.68
2012 |  |  |  | 7464.89 |  |  | 7747 |  |  |  | 996 | [10 empty] | 84.98 |  |  |  | 85.66 | [5 empty] | 85.32 |  |  | 88.19 |  |  |  | 3.91 |  | 4.46 | [8 empty] | 9.88 |  |  |  |  | 0.67
2013 |  |  |  | 8697.94 |  |  | 8239 |  |  |  | 1120 | [10 empty] | 91.22 |  |  |  | 91.85 | [5 empty] | 91.14 |  |  | 94.05 |  |  |  | 1.06 |  | 2.39 | [8 empty] | 5.76 |  |  |  |  | 0.64
2014 |  |  |  | 8796.40 |  |  | 7991 |  |  |  | 1120 | [10 empty] | 89.39 |  |  |  | 90.15 | [5 empty] | 89.66 |  |  | 91.22 |  |  |  | 0.35 |  | 2.60 | [8 empty] | 7.25 |  |  |  |  | 0.76
2015 |  |  |  | 8933.60 |  |  | 8107 |  |  |  | 1120 | [10 empty] | 91.07 |  |  |  | 91.82 | [5 empty] | 91.06 |  |  | 92.55 |  |  |  | 0.06 |  | 3.18 | [8 empty] | 5.00 |  |  |  |  | 0.75
2016 |  |  |  | 7362.92 |  |  | 6927 |  |  |  | 1120 | [10 empty] | 74.53 |  |  |  | 75.21 | [5 empty] | 74.84 |  |  | 78.86 |  |  |  | 3.12 |  | 12.84 | [8 empty] | 11.95 |  |  |  |  | 0.68
2017 |  |  |  | 8063.69 |  |  | 7721 |  |  |  | 1120 | [10 empty] | 81.92 |  |  |  | 87.02 | [5 empty] | 82.19 |  |  | 88.14 |  |  |  | 0.63 |  | 1.05 | [8 empty] | 11.93 |  |  |  |  | 5.10
2018 |  |  |  | 8562.30 |  |  | 7890 |  |  |  | 1116 | [10 empty] | 87.17 |  |  |  | 88.38 | [5 empty] | 87.48 |  |  | 90.07 |  |  |  | 2.05 |  | 2.36 | [8 empty] | 9.26 |  |  |  |  | 1.21
2019 |  |  |  | 8470.86 |  |  | 8183 |  |  |  | 1118 | [10 empty] | 86.33 |  |  |  | 87.28 | [5 empty] | 86.49 |  |  | 93.41 |  |  |  | 5.94 |  | 6.11 | [8 empty] | 6.61 |  |  |  |  | 0.95
2020 |  |  |  | 7535.29 |  |  | 7356 |  |  |  | 1118 | [10 empty] | 80.28 |  |  |  | 80.90 | [5 empty] | 76.73 |  |  | 83.74 |  |  |  | 6.91 |  | 6.00 | [8 empty] | 13.10 |  |  |  |  | 0.69
2021 |  |  |  | 8620.49 |  |  | 7943 |  |  |  | 1118 | [10 empty] | 87.48 |  |  |  | 88.46 | [5 empty] | 88.02 |  |  | 90.67 |  |  |  | 3.68 |  | 3.38 | [8 empty] | 8.16 |  |  |  |  | 0.98
2022 |  |  |  | 8998.04 |  |  | 8254 |  |  |  | 1121 | [10 empty] | 92.53 |  |  |  | 93.35 | [5 empty] | 91.63 |  |  | 94.22 |  |  |  | 0.33 |  | 0.55 | [8 empty] | 6.09 |  |  |  |  | 0.83
2023 |  |  |  | 7354.48 |  |  | 7506 |  |  |  | 1121 | [10 empty] | 76.36 |  |  |  | 76.88 | [5 empty] | 74.89 |  |  | 85.68 |  |  |  | 9.92 |  | 9.52 | [8 empty] | 13.60 |  |  |  |  | 0.51
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1981 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 199 | [14 empty] | 210
B. |  | Refuelling without maintenance | [35 empty] | 4
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 982 | [14 empty] | 600 |  |  |  | 8
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 47
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 33
H. |  | Nuclear regulatory requirements | [39 empty] | 19
J. |  | Grid limitation, failure or grid unavailability | [31 empty] | 75 | [19 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 12
L. |  | Human factor related | [39 empty] | 16
P. |  | Fire | [39 empty] | 3
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [35 empty] | 3 |  |  |  | 6
Z. |  | Other | [39 empty] | 1
Subtotal | [22 empty] | 982 |  |  |  | 199 | [6 empty] | 75 |  |  |  | 687 |  |  |  | 263 | [11 empty] | 14
Total | [22 empty] | 1256 | [14 empty] | 964
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1981 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 94 | [14 empty] | 81
12. |  |  | Reactor I&C Systems | [19 empty] | 105 | [14 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 6
14. |  |  | Safety Systems | [34 empty] | 38
15. |  |  | Reactor Cooling Systems | [34 empty] | 13
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 52
32. |  |  | Feedwater and Main Steam System | [34 empty] | 5
34. |  |  | Miscellaneous Systems | [34 empty] | 13
41. |  |  | Main Generator Systems | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [34 empty] | 43
Total | [22 empty] | 199 | [14 empty] | 258
Highlights (2023)
Annual outage in September and October 2023 Half power due to earth fault in generator, in July - September (G21) and in December - (G22).

## FORSMARK-3
2023 Operating Experience
SE-14 | [8 empty] | FORSMARK-3 | [26 empty] | SWEDEN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | FKA (FORSMARK KRAFTGRUPP AB)
Owner | [7 empty] | : | FKA (FORSMARK KRAFTGRUPP AB)
Reactor Supplier | [7 empty] | : | ABB ATOM (ABB ATOM (formerly ASEA-ATOM))
Turbine Supplier | [7 empty] | : | STAL (STAL-LAVAL)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / AA-IV, BWR-3000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1979-01-01
Thermal power | [12 empty] | : |  |  | 3300 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-03-05
Gross electrical power | [12 empty] | : |  |  | 1208 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-08-18
Reference unit power (net) | [12 empty] | : |  |  | 1172 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.6
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3.65 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 48000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 1
| Active core diameter [m] | [13 empty] | : |  |  | 4.6 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.97
| Active core height/length [m] | [13 empty] | : |  |  | 3.68 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 25
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 700 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 19 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 6
| Number of control rod assemblies | [13 empty] | : |  |  | 169 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | NA | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 9170.91 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.88 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.67 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.83 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.23 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 5.94 %
Load Factor (LF) | [18 empty] | : | 89.33 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.55 %
Operating Factor (OF) | [18 empty] | : | 93.87 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 537 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 885.73 | 800.49 |  |  |  | 884.62 |  | 852.79 | [8 empty] | 843.61 |  |  | 743.22 | [6 empty] | 268.35 |  | 821.53 |  |  |  | 686.74 |  |  | 744.04 |  |  | 760.43 | [9 empty] | 879.34 |  |  | 9170.91
EAF [%] |  |  |  |  | 99.76 | 99.81 |  |  |  | 99.79 |  | 99.87 | [8 empty] | 99.94 |  |  | 88.80 | [6 empty] | 30.77 |  | 97.14 |  |  |  | 96.56 |  |  | 99.50 |  |  | 89.68 | [9 empty] | 99.51 |  |  | 91.67
UCF [%] |  |  |  |  | 99.76 | 99.81 |  |  |  | 99.79 |  | 99.89 | [8 empty] | 99.94 |  |  | 99.76 | [6 empty] | 32.43 |  | 99.70 |  |  |  | 99.71 |  |  | 99.90 |  |  | 89.68 | [9 empty] | 99.51 |  |  | 93.23
LF [%] |  |  |  |  | 101.58 | 101.64 |  |  |  | 101.59 |  | 101.06 | [8 empty] | 96.75 |  |  | 88.08 | [6 empty] | 30.77 |  | 94.22 |  |  |  | 81.38 |  |  | 85.21 |  |  | 90.12 | [9 empty] | 100.85 |  |  | 89.33
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 36.02 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 91.53 | [9 empty] | 100.00 |  |  | 93.87
FLR [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 10.04 | [9 empty] | 0.08 |  |  | 0.88
UCL [%] |  |  |  |  | 0.02 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 10.01 | [9 empty] | 0.08 |  |  | 0.83
PUF [%] |  |  |  |  | 0.22 | 0.19 |  |  |  | 0.21 |  | 0.11 | [8 empty] | 0.06 |  |  | 0.24 | [6 empty] | 67.57 |  | 0.30 |  |  |  | 0.29 |  |  | 0.10 |  |  | 0.31 | [9 empty] | 0.41 |  |  | 5.94
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.01 | [8 empty] | 0.00 |  |  | 10.95 | [6 empty] | 1.66 |  | 2.56 |  |  |  | 3.15 |  |  | 0.40 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.55
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 329957.89 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.26 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 85.73 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.19 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.79 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.02 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 84.54 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.06 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 89.51 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 4155.51 |  |  | 4803 |  |  |  | 1068 | [10 empty] | 95.52 |  |  |  | 95.52 | [5 empty] | 86.55 |  |  | 96.82 |  |  |  | 4.15 |  | 4.14 | [8 empty] | 0.35 |  |  |  |  | 0.00
1986 |  |  |  | 8069.60 |  |  | 7983 |  |  |  | 1060 | [10 empty] | 88.36 |  |  |  | 88.36 | [5 empty] | 86.90 |  |  | 91.13 |  |  |  | 3.39 |  | 3.11 | [8 empty] | 8.54 |  |  |  |  | 0.00
1987 |  |  |  | 7038.90 |  |  | 7866 |  |  |  | 1063 | [10 empty] | 77.86 |  |  |  | 77.86 | [5 empty] | 75.59 |  |  | 89.79 |  |  |  | 2.25 |  | 1.79 | [8 empty] | 20.35 |  |  |  |  | 0.00
1988 |  |  |  | 7462.87 |  |  | 7807 |  |  |  | 1068 | [10 empty] | 80.40 |  |  |  | 80.40 | [5 empty] | 79.55 |  |  | 88.88 |  |  |  | 4.38 |  | 3.69 | [8 empty] | 15.91 |  |  |  |  | 0.00
1989 |  |  |  | 7367.20 |  |  | 7792 |  |  |  | 1118 | [10 empty] | 85.77 |  |  |  | 85.77 | [5 empty] | 75.16 |  |  | 88.95 |  |  |  | 0.79 |  | 0.68 | [8 empty] | 13.55 |  |  |  |  | 0.00
1990 |  |  |  | 7942.08 |  |  | 8165 |  |  |  | 1150 | [10 empty] | 80.07 |  |  |  | 91.32 | [5 empty] | 78.84 |  |  | 93.21 |  |  |  | 1.97 |  | 1.84 | [8 empty] | 6.84 |  |  |  |  | 11.26
1991 |  |  |  | 8665.07 |  |  | 8325 |  |  |  | 1155 | [10 empty] | 85.61 |  |  |  | 87.47 | [5 empty] | 85.64 |  |  | 95.03 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 12.53 |  |  |  |  | 1.86
1992 |  |  |  | 8176.17 |  |  | 7963 |  |  |  | 1197 | [10 empty] | 81.18 |  |  |  | 89.45 | [5 empty] | 77.76 |  |  | 90.65 |  |  |  | 0.50 |  | 0.45 | [8 empty] | 10.10 |  |  |  |  | 8.27
1993 |  |  |  | 8457.86 |  |  | 8251 |  |  |  | 1158 | [10 empty] | 83.40 |  |  |  | 93.17 | [5 empty] | 83.38 |  |  | 94.19 |  |  |  | 1.43 |  | 1.35 | [8 empty] | 5.48 |  |  |  |  | 9.77
1994 |  |  |  | 9228.82 |  |  | 8277 |  |  |  | 1158 | [10 empty] | 90.92 |  |  |  | 93.42 | [5 empty] | 90.98 |  |  | 94.49 |  |  |  | 0.65 |  | 0.61 | [8 empty] | 5.97 |  |  |  |  | 2.50
1995 |  |  |  | 8930.86 |  |  | 8250 |  |  |  | 1158 | [10 empty] | 88.19 |  |  |  | 92.77 | [5 empty] | 88.04 |  |  | 94.18 |  |  |  | 1.84 |  | 1.74 | [8 empty] | 5.49 |  |  |  |  | 4.58
1996 |  |  |  | 8819.19 |  |  | 8008 |  |  |  | 1158 | [10 empty] | 86.71 |  |  |  | 89.09 | [5 empty] | 86.70 |  |  | 91.17 |  |  |  | 1.42 |  | 1.29 | [8 empty] | 9.63 |  |  |  |  | 2.38
1997 |  |  |  | 8955.24 |  |  | 8004 |  |  |  | 1158 | [10 empty] | 89.94 |  |  |  | 89.94 | [5 empty] | 88.04 |  |  | 91.12 |  |  |  | 1.20 |  | 1.09 | [8 empty] | 8.97 |  |  |  |  | 0.00
1998 |  |  |  | 8960.71 |  |  | 8227 |  |  |  | 1158 | [10 empty] | 93.75 |  |  |  | 93.92 | [5 empty] | 88.33 |  |  | 93.92 |  |  |  | 0.50 |  | 0.48 | [8 empty] | 5.60 |  |  |  |  | 0.17
1999 |  |  |  | 8825.52 |  |  | 8005 |  |  |  | 1155 | [10 empty] | 90.95 |  |  |  | 91.14 | [5 empty] | 87.08 |  |  | 91.38 |  |  |  | 1.57 |  | 1.46 | [8 empty] | 7.41 |  |  |  |  | 0.18
2000 |  |  |  | 7933.87 |  |  | 8038 |  |  |  | 1155 | [10 empty] | 87.71 |  |  |  | 94.92 | [5 empty] | 78.07 |  |  | 91.51 |  |  |  | 0.69 |  | 0.66 | [8 empty] | 4.43 |  |  |  |  | 7.21
2001 |  |  |  | 8182.42 |  |  | 7585 |  |  |  | 1155 | [10 empty] | 81.77 |  |  |  | 86.23 | [5 empty] | 80.87 |  |  | 86.59 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 13.71 |  |  |  |  | 4.46
2002 |  |  |  | 9079.36 |  |  | 8450 |  |  |  | 1158 | [10 empty] | 91.22 |  |  |  | 94.96 | [5 empty] | 89.50 |  |  | 96.46 |  |  |  | 1.85 |  | 1.79 | [8 empty] | 3.24 |  |  |  |  | 3.74
2003 |  |  |  | 9100.31 |  |  | 8507 |  |  |  | 1155 | [10 empty] | 89.93 |  |  |  | 89.93 | [5 empty] | 89.94 |  |  | 97.11 |  |  |  | 0.02 |  | 1.50 | [8 empty] | 8.57 |  |  |  |  | 0.00
2004 |  |  |  | 8973.49 |  |  | 7920 |  |  |  | 1185 | [10 empty] | 87.68 |  |  |  | 89.39 | [5 empty] | 87.69 |  |  | 90.16 |  |  |  | 0.42 |  | 0.38 | [8 empty] | 10.23 |  |  |  |  | 1.71
2005 |  |  |  | 9868.82 |  |  | 8491 |  |  |  | 1190 | [10 empty] | 94.57 |  |  |  | 96.23 | [5 empty] | 94.73 |  |  | 96.93 |  |  |  | 0.08 |  | 0.08 | [8 empty] | 3.68 |  |  |  |  | 1.66
2006 |  |  |  | 9600.51 |  |  | 8323 |  |  |  | 1170 | [10 empty] | 92.39 |  |  |  | 94.61 | [5 empty] | 92.23 |  |  | 95.01 |  |  |  | 2.12 |  | 2.05 | [8 empty] | 3.34 |  |  |  |  | 2.22
2007 |  |  |  | 8992.59 |  |  | 7770 |  |  |  | 1170 | [10 empty] | 87.26 |  |  |  | 88.24 | [5 empty] | 87.74 |  |  | 88.70 |  |  |  | 0.11 |  | 1.19 | [8 empty] | 10.57 |  |  |  |  | 0.98
2008 |  |  |  | 7109.80 |  |  | 6185 |  |  |  | 1170 | [10 empty] | 68.84 |  |  |  | 69.71 | [5 empty] | 69.18 |  |  | 70.41 |  |  |  | 2.42 |  | 20.59 | [8 empty] | 9.70 |  |  |  |  | 0.86
2009 |  |  |  | 8815.50 |  |  | 7624 |  |  |  | 1170 | [10 empty] | 85.49 |  |  |  | 86.01 | [5 empty] | 86.01 |  |  | 87.03 |  |  |  | 5.03 |  | 5.11 | [8 empty] | 8.88 |  |  |  |  | 0.52
2010 |  |  |  | 8320.23 |  |  | 7317 |  |  |  | 1170 | [10 empty] | 80.61 |  |  |  | 81.44 | [5 empty] | 81.18 |  |  | 83.53 |  |  |  | 5.16 |  | 4.43 | [8 empty] | 14.13 |  |  |  |  | 0.83
2011 |  |  |  | 8691.28 |  |  | 7515 |  |  |  | 1170 | [10 empty] | 84.34 |  |  |  | 85.36 | [5 empty] | 84.80 |  |  | 85.79 |  |  |  | 2.71 |  | 2.37 | [8 empty] | 12.27 |  |  |  |  | 1.01
2012 |  |  |  | 9520.47 |  |  | 8212 |  |  |  | 1170 | [10 empty] | 92.14 |  |  |  | 93.00 | [5 empty] | 92.64 |  |  | 93.49 |  |  |  | 1.32 |  | 1.25 | [8 empty] | 5.75 |  |  |  |  | 0.86
2013 |  |  |  | 9021.75 |  |  | 7830 |  |  |  | 1170 | [10 empty] | 87.63 |  |  |  | 88.60 | [5 empty] | 88.02 |  |  | 89.38 |  |  |  | 0.53 |  | 0.47 | [8 empty] | 10.94 |  |  |  |  | 0.96
2014 |  |  |  | 8471.77 |  |  | 7326 |  |  |  | 1170 | [10 empty] | 82.30 |  |  |  | 83.08 | [5 empty] | 82.66 |  |  | 83.63 |  |  |  | 2.08 |  | 2.59 | [8 empty] | 14.33 |  |  |  |  | 0.78
2015 |  |  |  | 5662.11 |  |  | 5200 |  |  |  | 1167 | [10 empty] | 57.40 |  |  |  | 57.84 | [5 empty] | 55.39 |  |  | 59.36 |  |  |  | 3.65 |  | 23.22 | [8 empty] | 18.94 |  |  |  |  | 0.44
2016 |  |  |  | 8439.79 |  |  | 7373 |  |  |  | 1167 | [10 empty] | 81.89 |  |  |  | 82.79 | [5 empty] | 82.33 |  |  | 83.94 |  |  |  | 7.71 |  | 6.92 | [8 empty] | 10.29 |  |  |  |  | 0.89
2017 |  |  |  | 8842.13 |  |  | 7764 |  |  |  | 1167 | [10 empty] | 86.18 |  |  |  | 87.48 | [5 empty] | 86.49 |  |  | 88.63 |  |  |  | 12.48 |  | 12.47 | [8 empty] | 0.05 |  |  |  |  | 1.29
2018 |  |  |  | 8357.50 |  |  | 7345 |  |  |  | 1159 | [10 empty] | 81.28 |  |  |  | 82.12 | [5 empty] | 82.08 |  |  | 83.85 |  |  |  | 7.86 |  | 7.01 | [8 empty] | 10.87 |  |  |  |  | 0.84
2019 |  |  |  | 9465.61 |  |  | 8197 |  |  |  | 1172 | [10 empty] | 91.53 |  |  |  | 92.65 | [5 empty] | 92.20 |  |  | 93.57 |  |  |  | 2.68 |  | 3.02 | [8 empty] | 4.33 |  |  |  |  | 1.12
2020 |  |  |  | 8864.05 |  |  | 7917 |  |  |  | 1172 | [10 empty] | 88.29 |  |  |  | 89.12 | [5 empty] | 86.10 |  |  | 90.13 |  |  |  | 3.36 |  | 3.10 | [8 empty] | 7.78 |  |  |  |  | 0.83
2021 |  |  |  | 9022.92 |  |  | 7786 |  |  |  | 1172 | [10 empty] | 87.17 |  |  |  | 88.52 | [5 empty] | 87.89 |  |  | 88.88 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 11.42 |  |  |  |  | 1.35
2022 |  |  |  | 9379.92 |  |  | 8153 |  |  |  | 1172 | [10 empty] | 91.30 |  |  |  | 92.57 | [5 empty] | 91.36 |  |  | 93.07 |  |  |  | 0.10 |  | 0.10 | [8 empty] | 7.34 |  |  |  |  | 1.27
2023 |  |  |  | 9170.91 |  |  | 8223 |  |  |  | 1172 | [10 empty] | 91.67 |  |  |  | 93.23 | [5 empty] | 89.33 |  |  | 93.87 |  |  |  | 0.88 |  | 0.83 | [8 empty] | 5.94 |  |  |  |  | 1.55
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 61 | [14 empty] | 201
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 477 | [14 empty] | 675
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 1
E. |  | Testing of plant systems or components | [35 empty] | 3 |  |  |  | 2
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 7
H. |  | Nuclear regulatory requirements | [39 empty] | 8
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 5
L. |  | Human factor related | [39 empty] | 18
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [39 empty] | 2
Z. |  | Other | [39 empty] | 0 | [11 empty] | 1
Subtotal | [22 empty] | 477 |  |  |  | 61 | [10 empty] | 686 |  |  |  | 231 | [11 empty] | 6
Total | [22 empty] | 538 | [14 empty] | 923
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 52
12. |  |  | Reactor I&C Systems | [34 empty] | 59
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 9
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 5
31. |  |  | Turbine and auxiliaries | [34 empty] | 19
32. |  |  | Feedwater and Main Steam System | [34 empty] | 2
41. |  |  | Main Generator Systems | [19 empty] | 61 | [14 empty] | 55
42. |  |  | Electrical Power Supply Systems | [34 empty] | 24
Total | [22 empty] | 61 | [14 empty] | 228
Highlights (2023)
Annual outage in July 2023.

## OSKARSHAMN-3
2023 Operating Experience
SE-12 | [8 empty] | OSKARSHAMN-3 | [26 empty] | SWEDEN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | OKG (OKG AKTIEBOLAG)
Owner | [7 empty] | : | OKG (OKG AKTIEBOLAG)
Reactor Supplier | [7 empty] | : | ABB ATOM (ABB ATOM (formerly ASEA-ATOM))
Turbine Supplier | [7 empty] | : | STAL (STAL-LAVAL)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / AA-IV, BWR-3000 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1980-05-01
Thermal power | [12 empty] | : |  |  | 3900 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1985-03-03
Gross electrical power | [12 empty] | : |  |  | 1450 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1985-08-15
Reference unit power (net) | [12 empty] | : |  |  | 1400 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 38 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 288
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 6
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 3 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 20 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 32000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 4.6 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.7
| Active core height/length [m] | [13 empty] | : |  |  | 3.68 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 20.5
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 700 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 14.0 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 169 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 4 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 4
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 9177.85 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 8.62 %
Energy Availability Factor (EAF) | [18 empty] | : | 74.79 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 7.96 %
Unit Capability Factor (UCF) | [18 empty] | : | 76.39 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 15.65 %
Load Factor (LF) | [18 empty] | : | 74.84 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.6 %
Operating Factor (OF) | [18 empty] | : | 80.92 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1671 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1028.64 | 928.42 |  |  |  | 748.91 |  | 468.56 | [8 empty] | 0.00 |  |  | 519.23 | [6 empty] | 863.85 |  | 709.24 |  |  |  | 895.60 |  |  | 1021.05 |  |  | 965.84 | [9 empty] | 1028.50 |  |  | 9177.85
EAF [%] |  |  |  |  | 98.76 | 98.68 |  |  |  | 71.86 |  | 46.48 | [8 empty] | 0.00 |  |  | 51.31 | [6 empty] | 82.93 |  | 67.92 |  |  |  | 88.85 |  |  | 97.90 |  |  | 95.82 | [9 empty] | 98.74 |  |  | 74.79
UCF [%] |  |  |  |  | 99.69 | 99.66 |  |  |  | 72.91 |  | 48.01 | [8 empty] | 0.00 |  |  | 54.95 | [6 empty] | 84.64 |  | 69.44 |  |  |  | 91.88 |  |  | 99.80 |  |  | 97.72 | [9 empty] | 99.75 |  |  | 76.39
LF [%] |  |  |  |  | 98.76 | 98.68 |  |  |  | 72.00 |  | 46.48 | [8 empty] | 0.00 |  |  | 51.51 | [6 empty] | 82.93 |  | 68.09 |  |  |  | 88.85 |  |  | 97.90 |  |  | 95.82 | [9 empty] | 98.74 |  |  | 74.84
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 77.52 |  | 48.89 | [8 empty] | 0.00 |  |  | 60.97 | [6 empty] | 100.00 |  | 85.08 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 80.92
FLR [%] |  |  |  |  | 0.31 | 0.34 |  |  |  | 27.09 |  | 1.79 | [8 empty] | 0.00 |  |  | 2.78 | [6 empty] | 15.36 |  | 30.56 |  |  |  | 8.12 |  |  | 0.20 |  |  | 0.66 | [9 empty] | 0.25 |  |  | 8.62
UCL [%] |  |  |  |  | 0.31 | 0.34 |  |  |  | 27.09 |  | 0.88 | [8 empty] | 0.00 |  |  | 10.74 | [6 empty] | 15.36 |  | 30.56 |  |  |  | 8.12 |  |  | 0.20 |  |  | 0.65 | [9 empty] | 0.25 |  |  | 7.96
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 51.11 | [8 empty] | 100.00 |  |  | 34.31 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 1.63 | [9 empty] | 0.00 |  |  | 15.65
XUF [%] |  |  |  |  | 0.94 | 0.98 |  |  |  | 1.05 |  | 1.53 | [8 empty] | 0.00 |  |  | 3.65 | [6 empty] | 1.71 |  | 1.53 |  |  |  | 3.03 |  |  | 1.91 |  |  | 1.90 | [9 empty] | 1.01 |  |  | 1.60
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 325618.82 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 5.92 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.98 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 8.56 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 82.26 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.18 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.4 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.28 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.04 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1985 |  |  |  | 3848.48 |  |  | 4706 |  |  |  | 1055 | [10 empty] | 92.98 |  |  |  | 92.98 | [5 empty] | 79.25 |  |  | 93.38 |  |  |  | 7.02 |  | 7.02 | [8 empty] | 0.00 |  |  |  |  | 0.00
1986 |  |  |  | 8386.93 |  |  | 8111 |  |  |  | 1060 | [10 empty] | 91.91 |  |  |  | 91.91 | [5 empty] | 90.39 |  |  | 92.59 |  |  |  | 2.32 |  | 2.18 | [8 empty] | 5.91 |  |  |  |  | 0.00
1987 |  |  |  | 7057.96 |  |  | 7988 |  |  |  | 1065 | [10 empty] | 89.40 |  |  |  | 89.64 | [5 empty] | 75.65 |  |  | 91.19 |  |  |  | 4.29 |  | 4.02 | [8 empty] | 6.34 |  |  |  |  | 0.24
1988 |  |  |  | 7311.93 |  |  | 7457 |  |  |  | 1060 | [10 empty] | 83.60 |  |  |  | 83.89 | [5 empty] | 78.44 |  |  | 84.89 |  |  |  | 9.70 |  | 9.01 | [8 empty] | 7.11 |  |  |  |  | 0.29
1989 |  |  |  | 7788.21 |  |  | 8241 |  |  |  | 1035 | [10 empty] | 92.77 |  |  |  | 93.12 | [5 empty] | 84.38 |  |  | 94.08 |  |  |  | 0.86 |  | 0.81 | [8 empty] | 6.07 |  |  |  |  | 0.36
1990 |  |  |  | 7640.22 |  |  | 7781 |  |  |  | 1060 | [10 empty] | 83.25 |  |  |  | 84.13 | [5 empty] | 83.16 |  |  | 88.82 |  |  |  | 4.65 |  | 4.10 | [8 empty] | 11.76 |  |  |  |  | 0.88
1991 |  |  |  | 8935.78 |  |  | 8183 |  |  |  | 1160 | [10 empty] | 90.92 |  |  |  | 91.57 | [5 empty] | 87.94 |  |  | 93.41 |  |  |  | 1.13 |  | 1.05 | [8 empty] | 7.38 |  |  |  |  | 0.65
1992 |  |  |  | 8270.64 |  |  | 7903 |  |  |  | 1160 | [10 empty] | 89.45 |  |  |  | 90.08 | [5 empty] | 81.17 |  |  | 89.97 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 9.86 |  |  |  |  | 0.63
1993 |  |  |  | 8339.49 |  |  | 8026 |  |  |  | 1160 | [10 empty] | 90.86 |  |  |  | 91.71 | [5 empty] | 82.07 |  |  | 91.62 |  |  |  | 1.83 |  | 1.71 | [8 empty] | 6.58 |  |  |  |  | 0.85
1994 |  |  |  | 8480.44 |  |  | 7878 |  |  |  | 1160 | [10 empty] | 88.39 |  |  |  | 89.09 | [5 empty] | 83.46 |  |  | 89.93 |  |  |  | 0.75 |  | 0.67 | [8 empty] | 10.24 |  |  |  |  | 0.70
1995 |  |  |  | 8828.15 |  |  | 7957 |  |  |  | 1160 | [10 empty] | 87.55 |  |  |  | 89.79 | [5 empty] | 86.88 |  |  | 90.83 |  |  |  | 2.60 |  | 2.39 | [8 empty] | 7.82 |  |  |  |  | 2.24
1996 |  |  |  | 8518.40 |  |  | 7543 |  |  |  | 1153 | [10 empty] | 84.55 |  |  |  | 85.14 | [5 empty] | 84.10 |  |  | 85.86 |  |  |  | 1.62 |  | 1.40 | [8 empty] | 13.46 |  |  |  |  | 0.59
1997 |  |  |  | 8970.42 |  |  | 8042 |  |  |  | 1155 | [10 empty] | 89.79 |  |  |  | 90.95 | [5 empty] | 88.65 |  |  | 91.79 |  |  |  | 0.50 |  | 0.45 | [8 empty] | 8.59 |  |  |  |  | 1.16
1998 |  |  |  | 8032.25 |  |  | 7914 |  |  |  | 1155 | [10 empty] | 88.68 |  |  |  | 89.33 | [5 empty] | 79.39 |  |  | 90.34 |  |  |  | 2.89 |  | 2.66 | [8 empty] | 8.01 |  |  |  |  | 0.65
1999 |  |  |  | 8516.73 |  |  | 7850 |  |  |  | 1155 | [10 empty] | 88.91 |  |  |  | 89.72 | [5 empty] | 84.17 |  |  | 89.60 |  |  |  | 0.34 |  | 0.30 | [8 empty] | 9.98 |  |  |  |  | 0.81
2000 |  |  |  | 7219.13 |  |  | 8075 |  |  |  | 1155 | [10 empty] | 91.20 |  |  |  | 91.20 | [5 empty] | 71.16 |  |  | 91.93 |  |  |  | 4.10 |  | 3.90 | [8 empty] | 4.91 |  |  |  |  | 0.00
2001 |  |  |  | 9051.96 |  |  | 8170 |  |  |  | 1155 | [10 empty] | 91.80 |  |  |  | 92.56 | [5 empty] | 89.47 |  |  | 93.26 |  |  |  | 2.74 |  | 2.61 | [8 empty] | 4.83 |  |  |  |  | 0.76
2002 |  |  |  | 8883.98 |  |  | 8140 |  |  |  | 1155 | [10 empty] | 92.24 |  |  |  | 92.24 | [5 empty] | 87.80 |  |  | 92.91 |  |  |  | 2.05 |  | 1.93 | [8 empty] | 5.82 |  |  |  |  | 0.00
2003 |  |  |  | 7678.01 |  |  | 6871 |  |  |  | 1155 | [10 empty] | 76.19 |  |  |  | 77.96 | [5 empty] | 75.89 |  |  | 78.44 |  |  |  | 16.30 |  | 15.52 | [8 empty] | 6.52 |  |  |  |  | 1.77
2004 |  |  |  | 9318.51 |  |  | 8236 |  |  |  | 1149 | [10 empty] | 92.44 |  |  |  | 93.04 | [5 empty] | 92.32 |  |  | 93.75 |  |  |  | 1.12 |  | 1.05 | [8 empty] | 5.90 |  |  |  |  | 0.61
2005 |  |  |  | 8573.43 |  |  | 7671 |  |  |  | 1149 | [10 empty] | 86.17 |  |  |  | 86.72 | [5 empty] | 85.18 |  |  | 87.57 |  |  |  | 5.08 |  | 4.65 | [8 empty] | 8.64 |  |  |  |  | 0.55
2006 |  |  |  | 9522.49 |  |  | 8467 |  |  |  | 1149 | [10 empty] | 94.94 |  |  |  | 96.29 | [5 empty] | 94.60 |  |  | 96.64 |  |  |  | 0.18 |  | 0.29 | [8 empty] | 3.42 |  |  |  |  | 1.36
2007 |  |  |  | 8829.23 |  |  | 7965 |  |  |  | 1150 | [10 empty] | 87.82 |  |  |  | 89.56 | [5 empty] | 87.63 |  |  | 90.91 |  |  |  | 4.57 |  | 4.50 | [8 empty] | 5.94 |  |  |  |  | 1.75
2008 |  |  |  | 7100.89 |  |  | 6424 |  |  |  | 1152 | [10 empty] | 70.43 |  |  |  | 71.36 | [5 empty] | 70.23 |  |  | 73.13 |  |  |  | 3.22 |  | 20.73 | [8 empty] | 7.91 |  |  |  |  | 0.93
2009 |  |  |  | 1684.68 |  |  | 1795 |  |  |  | 1152 | [10 empty] | 16.76 |  |  |  | 16.82 | [5 empty] | 16.70 |  |  | 20.49 |  |  |  | 5.39 |  | 54.69 | [8 empty] | 28.48 |  |  |  |  | 0.06
2010 |  |  |  | 3841.75 |  |  | 4783 |  |  |  | 1400 | [10 empty] | 31.57 |  |  |  | 31.96 | [5 empty] | 31.33 |  |  | 54.60 |  |  |  | 48.60 |  | 50.26 | [8 empty] | 17.78 |  |  |  |  | 0.39
2011 |  |  |  | 8337.26 |  |  | 7313 |  |  |  | 1400 | [10 empty] | 69.08 |  |  |  | 70.41 | [5 empty] | 67.98 |  |  | 83.48 |  |  |  | 16.29 |  | 21.24 | [8 empty] | 8.35 |  |  |  |  | 1.33
2012 |  |  |  | 8438.86 |  |  | 6571 |  |  |  | 1400 | [10 empty] | 69.15 |  |  |  | 70.08 | [5 empty] | 68.62 |  |  | 74.81 |  |  |  | 17.19 |  | 21.04 | [8 empty] | 8.88 |  |  |  |  | 0.93
2013 |  |  |  | 9439.44 |  |  | 7186 |  |  |  | 1400 | [10 empty] | 77.59 |  |  |  | 78.85 | [5 empty] | 76.97 |  |  | 82.03 |  |  |  | 14.89 |  | 14.07 | [8 empty] | 7.08 |  |  |  |  | 1.26
2014 |  |  |  | 9215.46 |  |  | 7083 |  |  |  | 1400 | [10 empty] | 75.14 |  |  |  | 77.29 | [5 empty] | 75.14 |  |  | 80.86 |  |  |  | 3.78 |  | 5.98 | [8 empty] | 16.73 |  |  |  |  | 2.15
2015 |  |  |  | 9668.25 |  |  | 7480 |  |  |  | 1400 | [10 empty] | 79.13 |  |  |  | 81.16 | [5 empty] | 78.83 |  |  | 85.39 |  |  |  | 13.23 |  | 12.48 | [8 empty] | 6.37 |  |  |  |  | 2.03
2016 |  |  |  | 10265.41 |  |  | 7736 |  |  |  | 1400 | [10 empty] | 83.47 |  |  |  | 85.27 | [5 empty] | 83.47 |  |  | 88.07 |  |  |  | 6.41 |  | 7.33 | [8 empty] | 7.40 |  |  |  |  | 1.80
2017 |  |  |  | 9387.81 |  |  | 6996 |  |  |  | 1400 | [10 empty] | 76.55 |  |  |  | 78.20 | [5 empty] | 76.55 |  |  | 79.86 |  |  |  | 5.30 |  | 8.37 | [8 empty] | 13.44 |  |  |  |  | 1.65
2018 |  |  |  | 10688.89 |  |  | 7913 |  |  |  | 1400 | [10 empty] | 87.32 |  |  |  | 89.26 | [5 empty] | 87.16 |  |  | 90.33 |  |  |  | 2.79 |  | 3.00 | [8 empty] | 7.75 |  |  |  |  | 1.93
2019 |  |  |  | 10976.04 |  |  | 8135 |  |  |  | 1400 | [10 empty] | 89.50 |  |  |  | 91.78 | [5 empty] | 89.50 |  |  | 92.87 |  |  |  | 0.77 |  | 1.35 | [8 empty] | 6.86 |  |  |  |  | 2.29
2020 |  |  |  | 7988.94 |  |  | 6081 |  |  |  | 1400 | [10 empty] | 64.97 |  |  |  | 71.99 | [5 empty] | 64.97 |  |  | 69.24 |  |  |  | 4.23 |  | 9.78 | [8 empty] | 18.23 |  |  |  |  | 7.02
2021 |  |  |  | 10989.44 |  |  | 8118 |  |  |  | 1400 | [10 empty] | 89.63 |  |  |  | 91.83 | [5 empty] | 89.62 |  |  | 92.68 |  |  |  | 0.25 |  | 3.17 | [8 empty] | 5.01 |  |  |  |  | 2.20
2022 |  |  |  | 10414.56 |  |  | 7785 |  |  |  | 1400 | [10 empty] | 84.91 |  |  |  | 86.98 | [5 empty] | 84.92 |  |  | 88.87 |  |  |  | 6.60 |  | 6.15 | [8 empty] | 6.86 |  |  |  |  | 2.08
2023 |  |  |  | 9177.85 |  |  | 7089 |  |  |  | 1400 | [10 empty] | 74.79 |  |  |  | 76.39 | [5 empty] | 74.84 |  |  | 80.92 |  |  |  | 8.62 |  | 7.96 | [8 empty] | 15.65 |  |  |  |  | 1.60
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1985 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 199 | [14 empty] | 470
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1327 | [14 empty] | 654 |  |  |  | 17
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 22 |  |  |  | 0
E. |  | Testing of plant systems or components | [35 empty] | 1
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 57
H. |  | Nuclear regulatory requirements | [39 empty] | 31
L. |  | Human factor related | [39 empty] | 18
R. |  | External restrictions on supply and services (lack of funds due to delayed payments from customers, disputes in fuel industries, fuel-rationing, labour strike outside the plant , spare part delivery problems etc.) | [39 empty] | 15
S. |  | Fuel management limitation (including high flux tilt, stretch out or coast-down operation) | [24 empty] | 66 | [14 empty] | 2
Z. |  | Other | [24 empty] | 62 | [14 empty] | 16 | [11 empty] | 13
Subtotal | [22 empty] | 1327 |  |  |  | 327 | [10 empty] | 734 |  |  |  | 569 | [11 empty] | 13
Total | [22 empty] | 1654 | [14 empty] | 1316
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1985 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 168 | [14 empty] | 121
12. |  |  | Reactor I&C Systems | [34 empty] | 10
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 14
14. |  |  | Safety Systems | [34 empty] | 21
15. |  |  | Reactor Cooling Systems | [34 empty] | 21
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 226
32. |  |  | Feedwater and Main Steam System | [19 empty] | 31 | [14 empty] | 71
33. |  |  | Circulating Water System | [34 empty] | 2
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [34 empty] | 16
42. |  |  | Electrical Power Supply Systems | [34 empty] | 8
Total | [22 empty] | 199 | [14 empty] | 513

## RINGHALS-3
2023 Operating Experience
SE-7 | [8 empty] | RINGHALS-3 | [26 empty] | SWEDEN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | RAB (Ringhals AB)
Owner | [7 empty] | : | RAB (Ringhals AB)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | STAL (STAL-LAVAL)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1972-09-01
Thermal power | [12 empty] | : |  |  | 3135 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1980-09-07
Gross electrical power | [12 empty] | : |  |  | 1128 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1981-09-09
Reference unit power (net) | [12 empty] | : |  |  | 1081 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 43 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.51
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.65
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.75
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7694.6 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 1.35 %
Energy Availability Factor (EAF) | [18 empty] | : | 80.47 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 8.14 %
Unit Capability Factor (UCF) | [18 empty] | : | 85.06 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 6.8 %
Load Factor (LF) | [18 empty] | : | 81.47 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 4.59 %
Operating Factor (OF) | [18 empty] | : | 85.65 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1257 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 808.54 | 730.82 |  |  |  | 808.09 |  | 774.05 | [8 empty] | 648.94 |  |  | 0.00 | [6 empty] | 286.86 |  | 726.20 |  |  |  | 676.73 |  |  | 661.22 |  |  | 771.82 | [9 empty] | 801.33 |  |  | 7694.60
EAF [%] |  |  |  |  | 99.91 | 99.84 |  |  |  | 99.96 |  | 98.98 | [8 empty] | 80.06 |  |  | 0.00 | [6 empty] | 34.78 |  | 89.28 |  |  |  | 85.93 |  |  | 81.22 |  |  | 98.15 | [9 empty] | 98.61 |  |  | 80.47
UCF [%] |  |  |  |  | 99.99 | 99.99 |  |  |  | 99.99 |  | 99.91 | [8 empty] | 96.77 |  |  | 0.00 | [6 empty] | 37.30 |  | 96.76 |  |  |  | 99.98 |  |  | 90.61 |  |  | 99.98 | [9 empty] | 99.98 |  |  | 85.06
LF [%] |  |  |  |  | 101.19 | 101.26 |  |  |  | 101.13 |  | 100.10 | [8 empty] | 81.21 |  |  | 0.00 | [6 empty] | 35.67 |  | 90.29 |  |  |  | 86.95 |  |  | 82.21 |  |  | 99.16 | [9 empty] | 99.64 |  |  | 81.47
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 97.18 |  |  | 0.00 | [6 empty] | 41.40 |  | 100.00 |  |  |  | 100.00 |  |  | 89.25 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 85.65
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.08 | [8 empty] | 0.03 |  |  | 0.00 | [6 empty] | 2.69 |  | 3.22 |  |  |  | 0.00 |  |  | 9.36 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.35
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.08 | [8 empty] | 0.03 |  |  | 23.50 | [6 empty] | 60.22 |  | 3.22 |  |  |  | 0.00 |  |  | 9.36 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 8.14
PUF [%] |  |  |  |  | 0.01 | 0.01 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 3.20 |  |  | 76.50 | [6 empty] | 2.49 |  | 0.02 |  |  |  | 0.02 |  |  | 0.03 |  |  | 0.02 | [9 empty] | 0.02 |  |  | 6.80
XUF [%] |  |  |  |  | 0.08 | 0.15 |  |  |  | 0.03 |  | 0.93 | [8 empty] | 16.71 |  |  | 0.00 | [6 empty] | 2.51 |  | 7.48 |  |  |  | 14.05 |  |  | 9.39 |  |  | 1.84 | [9 empty] | 1.36 |  |  | 4.59
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 280487.03 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 6.88 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 78.52 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.77 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 80.56 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.67 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 77.07 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.03 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 84.44 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1981 |  |  |  | 2859.20 |  |  | 4560 |  |  |  | 920 | [10 empty] | 26.75 |  |  |  | 26.75 | [5 empty] | 26.77 |  |  | 29.51 |  |  |  | 73.25 |  | 73.25 | [8 empty] | 0.00 |  |  |  |  | 0.00
1982 |  |  |  | 1251.60 |  |  | 3680 |  |  |  | 915 | [10 empty] | 15.62 |  |  |  | 15.62 | [5 empty] | 15.61 |  |  | 42.01 |  |  |  | 73.78 |  | 43.95 | [8 empty] | 40.43 |  |  |  |  | 0.00
1983 |  |  |  | 2909.90 |  |  | 5886 |  |  |  | 867 | [10 empty] | 38.25 |  |  |  | 38.25 | [5 empty] | 38.24 |  |  | 67.19 |  |  |  | 46.42 |  | 33.13 | [8 empty] | 28.63 |  |  |  |  | 0.00
1984 |  |  |  | 5346.56 |  |  | 6450 |  |  |  | 915 | [10 empty] | 72.44 |  |  |  | 72.44 | [5 empty] | 66.52 |  |  | 73.43 |  |  |  | 15.69 |  | 13.48 | [8 empty] | 14.07 |  |  |  |  | 0.00
1985 |  |  |  | 6090.25 |  |  | 7580 |  |  |  | 915 | [10 empty] | 84.79 |  |  |  | 84.79 | [5 empty] | 75.98 |  |  | 86.53 |  |  |  | 1.48 |  | 1.27 | [8 empty] | 13.94 |  |  |  |  | 0.00
1986 |  |  |  | 6233.87 |  |  | 7026 |  |  |  | 915 | [10 empty] | 78.79 |  |  |  | 78.79 | [5 empty] | 77.77 |  |  | 80.21 |  |  |  | 2.40 |  | 1.94 | [8 empty] | 19.28 |  |  |  |  | 0.00
1987 |  |  |  | 6169.21 |  |  | 7485 |  |  |  | 915 | [10 empty] | 83.09 |  |  |  | 83.09 | [5 empty] | 76.97 |  |  | 85.45 |  |  |  | 5.67 |  | 4.99 | [8 empty] | 11.92 |  |  |  |  | 0.00
1988 |  |  |  | 6151.17 |  |  | 7645 |  |  |  | 915 | [10 empty] | 77.14 |  |  |  | 77.14 | [5 empty] | 76.53 |  |  | 87.03 |  |  |  | 8.53 |  | 7.19 | [8 empty] | 15.67 |  |  |  |  | 0.00
1989 |  |  |  | 5829.68 |  |  | 7757 |  |  |  | 915 | [10 empty] | 82.60 |  |  |  | 82.60 | [5 empty] | 72.73 |  |  | 88.55 |  |  |  | 10.37 |  | 9.56 | [8 empty] | 7.84 |  |  |  |  | 0.00
1990 |  |  |  | 5871.27 |  |  | 7855 |  |  |  | 915 | [10 empty] | 74.05 |  |  |  | 74.18 | [5 empty] | 73.25 |  |  | 89.67 |  |  |  | 18.98 |  | 17.38 | [8 empty] | 8.44 |  |  |  |  | 0.13
1991 |  |  |  | 5923.60 |  |  | 8007 |  |  |  | 915 | [10 empty] | 75.66 |  |  |  | 75.66 | [5 empty] | 73.90 |  |  | 91.40 |  |  |  | 14.25 |  | 12.57 | [8 empty] | 11.77 |  |  |  |  | 0.00
1992 |  |  |  | 5622.12 |  |  | 7941 |  |  |  | 915 | [10 empty] | 82.27 |  |  |  | 82.33 | [5 empty] | 69.95 |  |  | 90.40 |  |  |  | 3.55 |  | 3.03 | [8 empty] | 14.64 |  |  |  |  | 0.06
1993 |  |  |  | 6685.76 |  |  | 7964 |  |  |  | 915 | [10 empty] | 89.81 |  |  |  | 89.81 | [5 empty] | 83.41 |  |  | 90.91 |  |  |  | 2.84 |  | 2.62 | [8 empty] | 7.57 |  |  |  |  | 0.00
1994 |  |  |  | 6873.37 |  |  | 8097 |  |  |  | 918 | [10 empty] | 86.13 |  |  |  | 86.13 | [5 empty] | 85.47 |  |  | 92.43 |  |  |  | 0.58 |  | 0.50 | [8 empty] | 13.37 |  |  |  |  | 0.00
1995 |  |  |  | 4873.56 |  |  | 6040 |  |  |  | 918 | [10 empty] | 60.66 |  |  |  | 60.66 | [5 empty] | 60.60 |  |  | 68.95 |  |  |  | 14.30 |  | 10.12 | [8 empty] | 29.22 |  |  |  |  | 0.00
1996 |  |  |  | 6816.76 |  |  | 8166 |  |  |  | 910 | [10 empty] | 87.31 |  |  |  | 92.49 | [5 empty] | 85.28 |  |  | 92.96 |  |  |  | 0.60 |  | 0.56 | [8 empty] | 6.95 |  |  |  |  | 5.18
1997 |  |  |  | 6581.42 |  |  | 8107 |  |  |  | 910 | [10 empty] | 81.73 |  |  |  | 85.50 | [5 empty] | 82.55 |  |  | 92.54 |  |  |  | 8.04 |  | 7.53 | [8 empty] | 6.97 |  |  |  |  | 3.77
1998 |  |  |  | 6382.65 |  |  | 8008 |  |  |  | 915 | [10 empty] | 81.30 |  |  |  | 90.17 | [5 empty] | 79.63 |  |  | 91.42 |  |  |  | 2.57 |  | 2.38 | [8 empty] | 7.45 |  |  |  |  | 8.87
1999 |  |  |  | 6975.98 |  |  | 7899 |  |  |  | 911 | [10 empty] | 88.02 |  |  |  | 90.01 | [5 empty] | 87.41 |  |  | 90.17 |  |  |  | 0.37 |  | 0.34 | [8 empty] | 9.65 |  |  |  |  | 1.99
2000 |  |  |  | 6165.84 |  |  | 7966 |  |  |  | 911 | [10 empty] | 89.53 |  |  |  | 92.26 | [5 empty] | 77.05 |  |  | 90.69 |  |  |  | 0.69 |  | 0.65 | [8 empty] | 7.09 |  |  |  |  | 2.73
2001 |  |  |  | 6285.26 |  |  | 7942 |  |  |  | 911 | [10 empty] | 79.44 |  |  |  | 88.58 | [5 empty] | 78.76 |  |  | 90.66 |  |  |  | 2.41 |  | 2.19 | [8 empty] | 9.23 |  |  |  |  | 9.15
2002 |  |  |  | 6890.61 |  |  | 7930 |  |  |  | 915 | [10 empty] | 88.77 |  |  |  | 90.83 | [5 empty] | 85.97 |  |  | 90.53 |  |  |  | 0.85 |  | 0.78 | [8 empty] | 8.39 |  |  |  |  | 2.06
2003 |  |  |  | 6714.60 |  |  | 7475 |  |  |  | 915 | [10 empty] | 84.43 |  |  |  | 85.29 | [5 empty] | 83.77 |  |  | 85.33 |  |  |  | 0.41 |  | 0.35 | [8 empty] | 14.37 |  |  |  |  | 0.86
2004 |  |  |  | 7497.90 |  |  | 8295 |  |  |  | 915 | [10 empty] | 93.86 |  |  |  | 93.98 | [5 empty] | 93.29 |  |  | 94.43 |  |  |  | 1.65 |  | 1.58 | [8 empty] | 4.44 |  |  |  |  | 0.11
2005 |  |  |  | 7181.56 |  |  | 8075 |  |  |  | 915 | [10 empty] | 90.51 |  |  |  | 91.19 | [5 empty] | 89.60 |  |  | 92.18 |  |  |  | 1.20 |  | 2.19 | [8 empty] | 6.63 |  |  |  |  | 0.68
2006 |  |  |  | 6570.84 |  |  | 7249 |  |  |  | 1045 | [10 empty] | 74.97 |  |  |  | 81.77 | [5 empty] | 76.42 |  |  | 82.75 |  |  |  | 8.85 |  | 10.06 | [8 empty] | 8.16 |  |  |  |  | 6.80
2007 |  |  |  | 5990.80 |  |  | 6565 |  |  |  | 1045 | [10 empty] | 64.27 |  |  |  | 67.04 | [5 empty] | 65.44 |  |  | 74.94 |  |  |  | 12.79 |  | 22.60 | [8 empty] | 10.36 |  |  |  |  | 2.78
2008 |  |  |  | 7599.80 |  |  | 7980 |  |  |  | 985 | [10 empty] | 87.79 |  |  |  | 89.22 | [5 empty] | 87.84 |  |  | 90.85 |  |  |  | 3.48 |  | 4.26 | [8 empty] | 6.52 |  |  |  |  | 1.43
2009 |  |  |  | 8102.89 |  |  | 8093 |  |  |  | 1044 | [10 empty] | 89.73 |  |  |  | 91.37 | [5 empty] | 89.85 |  |  | 92.39 |  |  |  | 2.34 |  | 2.81 | [8 empty] | 5.82 |  |  |  |  | 1.64
2010 |  |  |  | 7605.45 |  |  | 7590 |  |  |  | 1051 | [10 empty] | 81.87 |  |  |  | 84.02 | [5 empty] | 82.61 |  |  | 86.64 |  |  |  | 1.60 |  | 4.14 | [8 empty] | 11.84 |  |  |  |  | 2.16
2011 |  |  |  | 7141.61 |  |  | 7032 |  |  |  | 1057 | [10 empty] | 77.21 |  |  |  | 79.48 | [5 empty] | 77.13 |  |  | 80.27 |  |  |  | 12.93 |  | 12.98 | [8 empty] | 7.54 |  |  |  |  | 2.28
2012 |  |  |  | 8327.82 |  |  | 8088 |  |  |  | 1064 | [10 empty] | 89.17 |  |  |  | 91.41 | [5 empty] | 89.59 |  |  | 92.08 |  |  |  | 0.10 |  | 0.12 | [8 empty] | 8.47 |  |  |  |  | 2.24
2013 |  |  |  | 6949.96 |  |  | 6852 |  |  |  | 1064 | [10 empty] | 73.84 |  |  |  | 76.99 | [5 empty] | 74.57 |  |  | 78.22 |  |  |  | 1.74 |  | 1.59 | [8 empty] | 21.41 |  |  |  |  | 3.15
2014 |  |  |  | 8099.92 |  |  | 7887 |  |  |  | 1062 | [10 empty] | 86.23 |  |  |  | 88.68 | [5 empty] | 86.97 |  |  | 90.03 |  |  |  | 1.09 |  | 0.98 | [8 empty] | 10.35 |  |  |  |  | 2.44
2015 |  |  |  | 7753.27 |  |  | 7853 |  |  |  | 1063 | [10 empty] | 82.47 |  |  |  | 86.55 | [5 empty] | 83.26 |  |  | 89.65 |  |  |  | 2.73 |  | 4.47 | [8 empty] | 8.98 |  |  |  |  | 4.08
2016 |  |  |  | 7437.54 |  |  | 7106 |  |  |  | 1065 | [10 empty] | 78.91 |  |  |  | 80.36 | [5 empty] | 79.64 |  |  | 80.90 |  |  |  | 0.16 |  | 0.44 | [8 empty] | 19.20 |  |  |  |  | 1.45
2017 |  |  |  | 7988.55 |  |  | 8027 |  |  |  | 1065 | [10 empty] | 84.88 |  |  |  | 87.54 | [5 empty] | 85.63 |  |  | 91.63 |  |  |  | 5.76 |  | 5.35 | [8 empty] | 7.11 |  |  |  |  | 2.66
2018 |  |  |  | 8144.41 |  |  | 7821 |  |  |  | 1062 | [10 empty] | 86.48 |  |  |  | 88.80 | [5 empty] | 87.54 |  |  | 89.28 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 11.12 |  |  |  |  | 2.32
2019 |  |  |  | 8212.36 |  |  | 8107 |  |  |  | 1062 | [10 empty] | 87.05 |  |  |  | 91.10 | [5 empty] | 88.28 |  |  | 92.55 |  |  |  | 2.20 |  | 2.05 | [8 empty] | 6.85 |  |  |  |  | 4.05
2020 |  |  |  | 5522.53 |  |  | 5452 |  |  |  | 1072 | [10 empty] | 63.08 |  |  |  | 64.61 | [5 empty] | 58.97 |  |  | 62.07 |  |  |  | 6.80 |  | 23.32 | [8 empty] | 12.07 |  |  |  |  | 1.53
2021 |  |  |  | 6623.06 |  |  | 6214 |  |  |  | 1072 | [10 empty] | 69.06 |  |  |  | 70.28 | [5 empty] | 70.53 |  |  | 70.94 |  |  |  | 1.04 |  | 21.80 | [8 empty] | 7.92 |  |  |  |  | 1.23
2022 |  |  |  | 8151.85 |  |  | 7780 |  |  |  | 1074 | [10 empty] | 85.63 |  |  |  | 87.70 | [5 empty] | 86.65 |  |  | 88.81 |  |  |  | 2.40 |  | 2.16 | [8 empty] | 10.14 |  |  |  |  | 2.08
2023 |  |  |  | 7694.60 |  |  | 7503 |  |  |  | 1081 | [10 empty] | 80.47 |  |  |  | 85.06 | [5 empty] | 81.47 |  |  | 85.65 |  |  |  | 1.35 |  | 8.14 | [8 empty] | 6.80 |  |  |  |  | 4.59
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1981 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 622 | [14 empty] | 363
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 576 | [14 empty] | 753 |  |  |  | 15
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 179
E. |  | Testing of plant systems or components | [35 empty] | 4 |  |  |  | 1
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 2
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 12
L. |  | Human factor related | [24 empty] | 45 | [14 empty] | 14
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 1
Z. |  | Other | [39 empty] | 13
Subtotal | [22 empty] | 576 |  |  |  | 667 | [10 empty] | 936 |  |  |  | 406 | [11 empty] | 15
Total | [22 empty] | 1243 | [14 empty] | 1357
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1981 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 19 | [14 empty] | 27
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [19 empty] | 20 | [14 empty] | 8
14. |  |  | Safety Systems | [19 empty] | 217 | [14 empty] | 54
15. |  |  | Reactor Cooling Systems | [19 empty] | 230 | [14 empty] | 43
16. |  |  | Steam generation systems | [34 empty] | 107
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 0
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 30
31. |  |  | Turbine and auxiliaries | [34 empty] | 33
32. |  |  | Feedwater and Main Steam System | [34 empty] | 26
34. |  |  | Miscellaneous Systems | [19 empty] | 57 | [14 empty] | 1
35. |  |  | All other I&C Systems | [34 empty] | 0
41. |  |  | Main Generator Systems | [19 empty] | 20 | [14 empty] | 14
42. |  |  | Electrical Power Supply Systems | [19 empty] | 58 | [14 empty] | 26
Total | [22 empty] | 621 | [14 empty] | 376

## RINGHALS-4
2023 Operating Experience
SE-10 | [8 empty] | RINGHALS-4 | [26 empty] | SWEDEN
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | RAB (Ringhals AB)
Owner | [7 empty] | : | RAB (Ringhals AB)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | STAL (STAL-LAVAL)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 3LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-11-01
Thermal power | [12 empty] | : |  |  | 3300 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1982-06-23
Gross electrical power | [12 empty] | : |  |  | 1178 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1983-11-21
Reference unit power (net) | [12 empty] | : |  |  | 1130 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 41 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.51
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 322
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 4.65
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 46000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 3.04 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.75
| Active core height/length [m] | [13 empty] | : |  |  | 3.66 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 157 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 18.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 24 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 5436.26 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 4.79 %
Energy Availability Factor (EAF) | [18 empty] | : | 54.24 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 23.3 %
Unit Capability Factor (UCF) | [18 empty] | : | 56.54 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 20.16 %
Load Factor (LF) | [18 empty] | : | 54.92 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 2.3 %
Operating Factor (OF) | [18 empty] | : | 59.32 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 3564 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.61 |  | 699.51 | [8 empty] | 819.00 |  |  | 771.32 | [6 empty] | 793.05 |  | 26.09 |  |  |  | 82.22 |  |  | 797.77 |  |  | 745.72 | [9 empty] | 700.97 |  |  | 5436.26
EAF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.07 |  | 84.91 | [8 empty] | 96.35 |  |  | 93.74 | [6 empty] | 93.27 |  | 2.29 |  |  |  | 9.43 |  |  | 94.09 |  |  | 90.86 | [9 empty] | 82.60 |  |  | 54.24
UCF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.07 |  | 87.12 | [8 empty] | 99.97 |  |  | 99.98 | [6 empty] | 99.77 |  | 2.72 |  |  |  | 10.83 |  |  | 98.00 |  |  | 93.46 | [9 empty] | 83.17 |  |  | 56.54
LF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.07 |  | 85.98 | [8 empty] | 97.42 |  |  | 94.80 | [6 empty] | 94.33 |  | 3.10 |  |  |  | 10.11 |  |  | 94.89 |  |  | 91.66 | [9 empty] | 83.38 |  |  | 54.92
OF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.54 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 3.63 |  |  |  | 20.83 |  |  | 100.00 |  |  | 93.61 | [9 empty] | 89.92 |  |  | 59.32
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 6.46 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.22 |  | 0.00 |  |  |  | 18.10 |  |  | 1.96 |  |  | 6.52 | [9 empty] | 16.83 |  |  | 4.79
UCL [%] |  |  |  |  | 0.00 | 100.00 |  |  |  | 99.46 |  | 6.01 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.22 |  | 0.00 |  |  |  | 55.22 |  |  | 1.96 |  |  | 6.52 | [9 empty] | 16.83 |  |  | 23.30
PUF [%] |  |  |  |  | 100.00 | 0.00 |  |  |  | 0.47 |  | 6.87 | [8 empty] | 0.03 |  |  | 0.02 | [6 empty] | 0.01 |  | 97.28 |  |  |  | 33.96 |  |  | 0.04 |  |  | 0.02 | [9 empty] | 0.00 |  |  | 20.16
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 2.20 | [8 empty] | 3.62 |  |  | 6.24 | [6 empty] | 6.50 |  | 0.43 |  |  |  | 1.40 |  |  | 3.91 |  |  | 2.60 | [9 empty] | 0.57 |  |  | 2.30
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 269532.21 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 3.69 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.51 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 5.67 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 83.76 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 10.57 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 78.92 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 2.25 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 85.83 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1983 |  |  |  | 2653.10 |  |  | 4122 |  |  |  | 915 | [10 empty] | 56.37 |  |  |  | 56.37 | [5 empty] | 56.38 |  |  | 74.60 |  |  |  | 24.02 |  | 17.82 | [8 empty] | 25.81 |  |  |  |  | 0.00
1984 |  |  |  | 5987.71 |  |  | 7517 |  |  |  | 915 | [10 empty] | 82.17 |  |  |  | 82.26 | [5 empty] | 74.50 |  |  | 85.58 |  |  |  | 9.40 |  | 8.53 | [8 empty] | 9.21 |  |  |  |  | 0.09
1985 |  |  |  | 5923.72 |  |  | 7755 |  |  |  | 915 | [10 empty] | 87.92 |  |  |  | 87.92 | [5 empty] | 73.90 |  |  | 88.53 |  |  |  | 1.75 |  | 1.56 | [8 empty] | 10.51 |  |  |  |  | 0.00
1986 |  |  |  | 5619.26 |  |  | 6839 |  |  |  | 915 | [10 empty] | 70.67 |  |  |  | 70.67 | [5 empty] | 70.11 |  |  | 78.07 |  |  |  | 9.98 |  | 7.83 | [8 empty] | 21.50 |  |  |  |  | 0.00
1987 |  |  |  | 5665.94 |  |  | 7827 |  |  |  | 915 | [10 empty] | 88.21 |  |  |  | 88.21 | [5 empty] | 70.69 |  |  | 89.35 |  |  |  | 1.44 |  | 1.29 | [8 empty] | 10.50 |  |  |  |  | 0.00
1988 |  |  |  | 6641.73 |  |  | 7945 |  |  |  | 915 | [10 empty] | 83.43 |  |  |  | 83.43 | [5 empty] | 82.64 |  |  | 90.45 |  |  |  | 0.68 |  | 0.57 | [8 empty] | 16.00 |  |  |  |  | 0.00
1989 |  |  |  | 5536.82 |  |  | 7624 |  |  |  | 915 | [10 empty] | 85.79 |  |  |  | 85.79 | [5 empty] | 69.08 |  |  | 87.03 |  |  |  | 6.32 |  | 5.79 | [8 empty] | 8.42 |  |  |  |  | 0.00
1990 |  |  |  | 6467.30 |  |  | 8080 |  |  |  | 915 | [10 empty] | 89.11 |  |  |  | 89.11 | [5 empty] | 80.69 |  |  | 92.24 |  |  |  | 0.88 |  | 0.79 | [8 empty] | 10.10 |  |  |  |  | 0.00
1991 |  |  |  | 6916.15 |  |  | 8041 |  |  |  | 915 | [10 empty] | 85.85 |  |  |  | 85.85 | [5 empty] | 86.29 |  |  | 91.79 |  |  |  | 0.64 |  | 0.55 | [8 empty] | 13.59 |  |  |  |  | 0.00
1992 |  |  |  | 6432.41 |  |  | 8156 |  |  |  | 915 | [10 empty] | 90.03 |  |  |  | 90.09 | [5 empty] | 80.03 |  |  | 92.85 |  |  |  | 1.18 |  | 1.08 | [8 empty] | 8.83 |  |  |  |  | 0.06
1993 |  |  |  | 6342.34 |  |  | 7906 |  |  |  | 915 | [10 empty] | 88.75 |  |  |  | 88.75 | [5 empty] | 79.13 |  |  | 90.25 |  |  |  | 2.67 |  | 2.44 | [8 empty] | 8.81 |  |  |  |  | 0.00
1994 |  |  |  | 6234.70 |  |  | 7476 |  |  |  | 914 | [10 empty] | 84.84 |  |  |  | 84.84 | [5 empty] | 77.87 |  |  | 85.34 |  |  |  | 7.04 |  | 6.43 | [8 empty] | 8.74 |  |  |  |  | 0.00
1995 |  |  |  | 6251.70 |  |  | 7684 |  |  |  | 912 | [10 empty] | 80.60 |  |  |  | 88.39 | [5 empty] | 78.25 |  |  | 87.72 |  |  |  | 4.14 |  | 3.81 | [8 empty] | 7.79 |  |  |  |  | 7.79
1996 |  |  |  | 6426.77 |  |  | 8067 |  |  |  | 912 | [10 empty] | 79.62 |  |  |  | 91.83 | [5 empty] | 80.22 |  |  | 91.84 |  |  |  | 0.63 |  | 0.58 | [8 empty] | 7.58 |  |  |  |  | 12.21
1997 |  |  |  | 6372.26 |  |  | 7665 |  |  |  | 912 | [10 empty] | 78.83 |  |  |  | 87.03 | [5 empty] | 79.75 |  |  | 87.49 |  |  |  | 1.27 |  | 2.53 | [8 empty] | 10.44 |  |  |  |  | 8.20
1998 |  |  |  | 6809.80 |  |  | 8146 |  |  |  | 915 | [10 empty] | 86.52 |  |  |  | 92.52 | [5 empty] | 84.96 |  |  | 92.99 |  |  |  | 0.71 |  | 0.66 | [8 empty] | 6.82 |  |  |  |  | 6.00
1999 |  |  |  | 6986.83 |  |  | 8042 |  |  |  | 907 | [10 empty] | 88.63 |  |  |  | 91.73 | [5 empty] | 87.94 |  |  | 91.80 |  |  |  | 1.42 |  | 1.33 | [8 empty] | 6.94 |  |  |  |  | 3.11
2000 |  |  |  | 4060.71 |  |  | 5898 |  |  |  | 907 | [10 empty] | 63.43 |  |  |  | 66.52 | [5 empty] | 50.97 |  |  | 67.14 |  |  |  | 25.24 |  | 22.46 | [8 empty] | 11.01 |  |  |  |  | 3.10
2001 |  |  |  | 6623.98 |  |  | 7758 |  |  |  | 909 | [10 empty] | 86.51 |  |  |  | 88.38 | [5 empty] | 83.19 |  |  | 88.56 |  |  |  | 3.12 |  | 2.85 | [8 empty] | 8.77 |  |  |  |  | 1.88
2002 |  |  |  | 5942.20 |  |  | 7056 |  |  |  | 915 | [10 empty] | 75.53 |  |  |  | 80.25 | [5 empty] | 74.13 |  |  | 80.55 |  |  |  | 5.38 |  | 4.57 | [8 empty] | 15.19 |  |  |  |  | 4.72
2003 |  |  |  | 6996.51 |  |  | 7843 |  |  |  | 915 | [10 empty] | 88.86 |  |  |  | 89.19 | [5 empty] | 87.29 |  |  | 89.53 |  |  |  | 0.68 |  | 3.47 | [8 empty] | 7.34 |  |  |  |  | 0.33
2004 |  |  |  | 7209.61 |  |  | 8092 |  |  |  | 915 | [10 empty] | 92.10 |  |  |  | 92.10 | [5 empty] | 89.70 |  |  | 92.12 |  |  |  | 1.15 |  | 1.45 | [8 empty] | 6.45 |  |  |  |  | 0.00
2005 |  |  |  | 7129.78 |  |  | 8073 |  |  |  | 915 | [10 empty] | 91.36 |  |  |  | 91.46 | [5 empty] | 88.95 |  |  | 92.16 |  |  |  | 0.30 |  | 1.97 | [8 empty] | 6.57 |  |  |  |  | 0.11
2006 |  |  |  | 7092.37 |  |  | 8054 |  |  |  | 907 | [10 empty] | 88.68 |  |  |  | 91.15 | [5 empty] | 89.26 |  |  | 91.94 |  |  |  | 1.55 |  | 2.13 | [8 empty] | 6.72 |  |  |  |  | 2.48
2007 |  |  |  | 7192.87 |  |  | 8126 |  |  |  | 907 | [10 empty] | 89.43 |  |  |  | 91.03 | [5 empty] | 90.53 |  |  | 92.76 |  |  |  | 1.45 |  | 2.26 | [8 empty] | 6.71 |  |  |  |  | 1.60
2008 |  |  |  | 7331.95 |  |  | 8046 |  |  |  | 935 | [10 empty] | 88.97 |  |  |  | 91.12 | [5 empty] | 89.27 |  |  | 91.60 |  |  |  | 0.87 |  | 1.43 | [8 empty] | 7.46 |  |  |  |  | 2.15
2009 |  |  |  | 7467.66 |  |  | 8165 |  |  |  | 936 | [10 empty] | 90.24 |  |  |  | 92.81 | [5 empty] | 91.08 |  |  | 93.21 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.19 |  |  |  |  | 2.57
2010 |  |  |  | 7229.47 |  |  | 7948 |  |  |  | 935 | [10 empty] | 87.33 |  |  |  | 89.57 | [5 empty] | 88.27 |  |  | 90.73 |  |  |  | 0.96 |  | 1.84 | [8 empty] | 8.59 |  |  |  |  | 2.23
2011 |  |  |  | 4102.44 |  |  | 4678 |  |  |  | 945 | [10 empty] | 50.12 |  |  |  | 50.68 | [5 empty] | 49.56 |  |  | 53.40 |  |  |  | 4.24 |  | 14.34 | [8 empty] | 34.98 |  |  |  |  | 0.57
2012 |  |  |  | 6963.03 |  |  | 7541 |  |  |  | 940 | [10 empty] | 83.57 |  |  |  | 85.49 | [5 empty] | 83.96 |  |  | 85.85 |  |  |  | 0.95 |  | 6.20 | [8 empty] | 8.30 |  |  |  |  | 1.92
2013 |  |  |  | 7379.26 |  |  | 8054 |  |  |  | 940 | [10 empty] | 88.85 |  |  |  | 91.38 | [5 empty] | 89.61 |  |  | 91.94 |  |  |  | 0.33 |  | 0.47 | [8 empty] | 8.15 |  |  |  |  | 2.53
2014 |  |  |  | 6740.44 |  |  | 7396 |  |  |  | 938 | [10 empty] | 81.47 |  |  |  | 83.99 | [5 empty] | 81.93 |  |  | 84.43 |  |  |  | 0.80 |  | 0.68 | [8 empty] | 15.33 |  |  |  |  | 2.52
2015 |  |  |  | 7604.79 |  |  | 7215 |  |  |  | 1115 | [10 empty] | 78.03 |  |  |  | 80.73 | [5 empty] | 78.92 |  |  | 82.36 |  |  |  | 9.62 |  | 8.63 | [8 empty] | 10.63 |  |  |  |  | 2.70
2016 |  |  |  | 8331.54 |  |  | 7862 |  |  |  | 1106 | [10 empty] | 84.63 |  |  |  | 86.92 | [5 empty] | 84.92 |  |  | 89.50 |  |  |  | 3.98 |  | 3.60 | [8 empty] | 9.48 |  |  |  |  | 2.28
2017 |  |  |  | 8265.10 |  |  | 7664 |  |  |  | 1106 | [10 empty] | 84.84 |  |  |  | 86.88 | [5 empty] | 85.31 |  |  | 87.49 |  |  |  | 1.02 |  | 0.89 | [8 empty] | 12.22 |  |  |  |  | 2.04
2018 |  |  |  | 8702.45 |  |  | 8273 |  |  |  | 1102 | [10 empty] | 89.78 |  |  |  | 93.43 | [5 empty] | 90.08 |  |  | 94.44 |  |  |  | 1.07 |  | 1.01 | [8 empty] | 5.56 |  |  |  |  | 3.65
2019 |  |  |  | 8008.02 |  |  | 7627 |  |  |  | 1117 | [10 empty] | 81.90 |  |  |  | 86.23 | [5 empty] | 82.67 |  |  | 87.07 |  |  |  | 0.36 |  | 4.31 | [8 empty] | 9.46 |  |  |  |  | 4.33
2020 |  |  |  | 6285.45 |  |  | 6739 |  |  |  | 1130 | [10 empty] | 64.86 |  |  |  | 66.92 | [5 empty] | 63.32 |  |  | 76.72 |  |  |  | 23.55 |  | 22.69 | [8 empty] | 10.39 |  |  |  |  | 2.06
2021 |  |  |  | 8234.53 |  |  | 7649 |  |  |  | 1130 | [10 empty] | 82.12 |  |  |  | 84.58 | [5 empty] | 83.19 |  |  | 87.32 |  |  |  | 2.71 |  | 3.14 | [8 empty] | 12.28 |  |  |  |  | 2.45
2022 |  |  |  | 5819.96 |  |  | 5318 |  |  |  | 1130 | [10 empty] | 58.19 |  |  |  | 59.97 | [5 empty] | 58.79 |  |  | 60.71 |  |  |  | 0.00 |  | 34.20 | [8 empty] | 5.83 |  |  |  |  | 1.78
2023 |  |  |  | 5436.26 |  |  | 5196 |  |  |  | 1130 | [10 empty] | 54.24 |  |  |  | 56.54 | [5 empty] | 54.92 |  |  | 59.32 |  |  |  | 4.79 |  | 23.30 | [8 empty] | 20.16 |  |  |  |  | 2.30
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1983 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 1913 | [14 empty] | 325 | [11 empty] | 1
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1656 | [14 empty] | 862 |  |  |  | 1
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 150
E. |  | Testing of plant systems or components | [35 empty] | 28 |  |  |  | 13
H. |  | Nuclear regulatory requirements | [39 empty] | 2
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 17
Z. |  | Other | [35 empty] | 1 |  |  |  | 11
Subtotal | [22 empty] | 1656 |  |  |  | 1913 | [10 empty] | 1041 |  |  |  | 369 | [11 empty] | 1
Total | [22 empty] | 3569 | [14 empty] | 1411
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1983 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 379 | [14 empty] | 75
12. |  |  | Reactor I&C Systems | [34 empty] | 4
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 14
14. |  |  | Safety Systems | [34 empty] | 17
15. |  |  | Reactor Cooling Systems | [19 empty] | 1412 | [14 empty] | 160
16. |  |  | Steam generation systems | [34 empty] | 29
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 8
32. |  |  | Feedwater and Main Steam System | [19 empty] | 122 | [14 empty] | 25
41. |  |  | Main Generator Systems | [34 empty] | 2
42. |  |  | Electrical Power Supply Systems | [34 empty] | 0
Total | [22 empty] | 1913 | [14 empty] | 335