## BEZNAU-1
2023 Operating Experience
CH-1 | [8 empty] | BEZNAU-1 | [26 empty] | SWITZERLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | Axpo AG (Kernkraftwerk Beznau CH-5312 Döttingen)
Owner | [7 empty] | : | Axpo AG (Kernkraftwerk Beznau CH-5312 Döttingen)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1965-09-01
Thermal power | [12 empty] | : |  |  | 1130 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1969-07-17
Gross electrical power | [12 empty] | : |  |  | 380 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1969-12-09
Reference unit power (net) | [12 empty] | : |  |  | 365 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 54 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.3
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 313
| Fuel material | [13 empty] | : |  |  | UO2/MOX | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.68 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 17 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 42000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.45 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.3
| Active core height/length [m] | [13 empty] | : |  |  | 3.05 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 15
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.7 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 17 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2937.08 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 2.4 %
Energy Availability Factor (EAF) | [18 empty] | : | 91.52 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 2.81 %
Unit Capability Factor (UCF) | [18 empty] | : | 93.14 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 4.05 %
Load Factor (LF) | [18 empty] | : | 91.86 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.62 %
Operating Factor (OF) | [18 empty] | : | 95.63 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 383 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 49.33 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 273.78 | 247.18 |  |  |  | 273.15 |  | 264.18 | [8 empty] | 133.31 |  |  | 185.77 | [6 empty] | 251.25 |  | 244.66 |  |  |  | 256.69 |  |  | 269.52 |  |  | 264.05 | [9 empty] | 273.53 |  |  | 2937.08
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 49.09 |  |  | 70.69 | [6 empty] | 92.52 |  | 90.09 |  |  |  | 97.67 |  |  | 99.11 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.52
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 49.61 |  |  | 72.55 | [6 empty] | 96.19 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 93.14
LF [%] |  |  |  |  | 100.82 | 100.78 |  |  |  | 100.72 |  | 100.52 | [8 empty] | 49.09 |  |  | 70.69 | [6 empty] | 92.52 |  | 90.09 |  |  |  | 97.67 |  |  | 99.11 |  |  | 100.48 | [9 empty] | 100.73 |  |  | 91.86
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 49.73 |  |  | 98.75 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 95.63
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 24.77 | [6 empty] | 3.81 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.40
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 4.97 |  |  | 25.13 | [6 empty] | 3.81 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.81
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 45.41 |  |  | 2.32 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 4.05
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.52 |  |  | 1.86 | [6 empty] | 3.67 |  | 9.91 |  |  |  | 2.33 |  |  | 0.89 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.62
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 272182.39 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.64 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 80.83 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 7.35 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.15 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.49 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 80.44 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.32 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 82.39 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1969 |  |  |  | Data not provided
1970 |  |  |  | 1947.00 |  |  | 5917 |  |  |  | 364 | [10 empty] | 61.05 |  |  |  | 61.05 | [5 empty] | 61.06 |  |  | 67.55 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 38.95 |  |  |  |  | 0.00
1971 |  |  |  | 1700.50 |  |  | 5123 |  |  |  | 364 | [10 empty] | 58.99 |  |  |  | 58.99 | [5 empty] | 53.33 |  |  | 58.48 |  |  |  | 27.48 |  | 22.35 | [8 empty] | 18.66 |  |  |  |  | 0.00
1972 |  |  |  | 1402.90 |  |  | 5391 |  |  |  | 280 | [10 empty] | 61.32 |  |  |  | 61.32 | [5 empty] | 57.04 |  |  | 61.37 |  |  |  | 38.68 |  | 38.68 | [8 empty] | 0.00 |  |  |  |  | 0.00
1973 |  |  |  | 1655.00 |  |  | 6654 |  |  |  | 350 | [10 empty] | 71.57 |  |  |  | 71.57 | [5 empty] | 53.98 |  |  | 75.96 |  |  |  | 8.53 |  | 6.67 | [8 empty] | 21.76 |  |  |  |  | 0.00
1974 |  |  |  | 2346.70 |  |  | 7177 |  |  |  | 350 | [10 empty] | 78.10 |  |  |  | 78.10 | [5 empty] | 76.54 |  |  | 81.93 |  |  |  | 2.77 |  | 2.22 | [8 empty] | 19.67 |  |  |  |  | 0.00
1975 |  |  |  | 2490.90 |  |  | 7490 |  |  |  | 350 | [10 empty] | 81.22 |  |  |  | 81.22 | [5 empty] | 81.24 |  |  | 85.50 |  |  |  | 5.62 |  | 4.83 | [8 empty] | 13.95 |  |  |  |  | 0.00
1976 |  |  |  | 2548.10 |  |  | 7530 |  |  |  | 350 | [10 empty] | 83.46 |  |  |  | 83.46 | [5 empty] | 82.88 |  |  | 85.72 |  |  |  | 0.65 |  | 0.55 | [8 empty] | 15.99 |  |  |  |  | 0.00
1977 |  |  |  | 2596.30 |  |  | 7592 |  |  |  | 350 | [10 empty] | 85.21 |  |  |  | 85.21 | [5 empty] | 84.68 |  |  | 86.67 |  |  |  | 2.68 |  | 2.34 | [8 empty] | 12.44 |  |  |  |  | 0.00
1978 |  |  |  | 2761.90 |  |  | 8031 |  |  |  | 350 | [10 empty] | 89.46 |  |  |  | 89.46 | [5 empty] | 90.08 |  |  | 91.68 |  |  |  | 0.13 |  | 0.12 | [8 empty] | 10.42 |  |  |  |  | 0.00
1979 |  |  |  | 2658.80 |  |  | 7746 |  |  |  | 350 | [10 empty] | 86.11 |  |  |  | 86.11 | [5 empty] | 86.72 |  |  | 88.42 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 13.88 |  |  |  |  | 0.00
1980 |  |  |  | 2650.50 |  |  | 7682 |  |  |  | 350 | [10 empty] | 85.69 |  |  |  | 85.69 | [5 empty] | 86.21 |  |  | 87.45 |  |  |  | 4.56 |  | 4.09 | [8 empty] | 10.21 |  |  |  |  | 0.00
1981 |  |  |  | 2569.70 |  |  | 7486 |  |  |  | 350 | [10 empty] | 83.46 |  |  |  | 83.46 | [5 empty] | 83.81 |  |  | 85.46 |  |  |  | 5.43 |  | 4.79 | [8 empty] | 11.74 |  |  |  |  | 0.00
1982 |  |  |  | 2566.90 |  |  | 7553 |  |  |  | 350 | [10 empty] | 83.52 |  |  |  | 83.52 | [5 empty] | 83.72 |  |  | 86.22 |  |  |  | 3.14 |  | 2.71 | [8 empty] | 13.77 |  |  |  |  | 0.00
1983 |  |  |  | 2551.70 |  |  | 7546 |  |  |  | 350 | [10 empty] | 83.49 |  |  |  | 83.49 | [5 empty] | 83.23 |  |  | 86.14 |  |  |  | 0.64 |  | 0.54 | [8 empty] | 15.97 |  |  |  |  | 0.00
1984 |  |  |  | 2732.94 |  |  | 8001 |  |  |  | 350 | [10 empty] | 88.85 |  |  |  | 88.85 | [5 empty] | 88.89 |  |  | 91.09 |  |  |  | 0.29 |  | 0.26 | [8 empty] | 10.89 |  |  |  |  | 0.00
1985 |  |  |  | 2634.26 |  |  | 7906 |  |  |  | 350 | [10 empty] | 86.01 |  |  |  | 86.01 | [5 empty] | 85.92 |  |  | 90.25 |  |  |  | 4.17 |  | 3.74 | [8 empty] | 10.25 |  |  |  |  | 0.00
1986 |  |  |  | 2496.27 |  |  | 7403 |  |  |  | 350 | [10 empty] | 81.60 |  |  |  | 81.60 | [5 empty] | 81.42 |  |  | 84.51 |  |  |  | 9.03 |  | 8.10 | [8 empty] | 10.30 |  |  |  |  | 0.00
1987 |  |  |  | 2486.26 |  |  | 7256 |  |  |  | 350 | [10 empty] | 80.71 |  |  |  | 80.71 | [5 empty] | 81.09 |  |  | 82.83 |  |  |  | 1.90 |  | 1.56 | [8 empty] | 17.73 |  |  |  |  | 0.00
1988 |  |  |  | 2566.55 |  |  | 7499 |  |  |  | 350 | [10 empty] | 82.97 |  |  |  | 82.97 | [5 empty] | 83.48 |  |  | 85.37 |  |  |  | 1.56 |  | 1.32 | [8 empty] | 15.72 |  |  |  |  | 0.00
1989 |  |  |  | 2433.15 |  |  | 7062 |  |  |  | 350 | [10 empty] | 78.65 |  |  |  | 78.65 | [5 empty] | 79.36 |  |  | 80.62 |  |  |  | 7.30 |  | 6.19 | [8 empty] | 15.16 |  |  |  |  | 0.00
1990 |  |  |  | 2562.48 |  |  | 7506 |  |  |  | 350 | [10 empty] | 84.38 |  |  |  | 84.38 | [5 empty] | 83.58 |  |  | 85.68 |  |  |  | 0.41 |  | 0.34 | [8 empty] | 15.28 |  |  |  |  | 0.00
1991 |  |  |  | 2495.26 |  |  | 7430 |  |  |  | 350 | [10 empty] | 83.48 |  |  |  | 83.48 | [5 empty] | 81.38 |  |  | 84.82 |  |  |  | 1.61 |  | 1.36 | [8 empty] | 15.16 |  |  |  |  | 0.00
1992 |  |  |  | 2477.39 |  |  | 7303 |  |  |  | 350 | [10 empty] | 81.70 |  |  |  | 81.70 | [5 empty] | 80.58 |  |  | 83.14 |  |  |  | 0.71 |  | 0.58 | [8 empty] | 17.71 |  |  |  |  | 0.00
1993 |  |  |  | 2158.43 |  |  | 6241 |  |  |  | 350 | [10 empty] | 69.37 |  |  |  | 69.88 | [5 empty] | 70.40 |  |  | 71.24 |  |  |  | 1.02 |  | 0.72 | [8 empty] | 29.39 |  |  |  |  | 0.52
1994 |  |  |  | 2686.88 |  |  | 7610 |  |  |  | 350 | [10 empty] | 85.05 |  |  |  | 86.19 | [5 empty] | 87.63 |  |  | 86.87 |  |  |  | 0.35 |  | 0.30 | [8 empty] | 13.51 |  |  |  |  | 1.13
1995 |  |  |  | 2850.46 |  |  | 7993 |  |  |  | 350 | [10 empty] | 90.15 |  |  |  | 90.48 | [5 empty] | 92.97 |  |  | 91.24 |  |  |  | 0.32 |  | 0.29 | [8 empty] | 9.23 |  |  |  |  | 0.33
1996 |  |  |  | 2753.18 |  |  | 7704 |  |  |  | 353 | [10 empty] | 86.81 |  |  |  | 87.45 | [5 empty] | 88.60 |  |  | 87.70 |  |  |  | 0.35 |  | 0.31 | [8 empty] | 12.24 |  |  |  |  | 0.64
1997 |  |  |  | 2708.21 |  |  | 7731 |  |  |  | 365 | [10 empty] | 85.12 |  |  |  | 87.46 | [5 empty] | 84.70 |  |  | 88.25 |  |  |  | 0.18 |  | 0.16 | [8 empty] | 12.38 |  |  |  |  | 2.35
1998 |  |  |  | 3183.13 |  |  | 8760 |  |  |  | 365 | [10 empty] | 99.84 |  |  |  | 99.89 | [5 empty] | 99.55 |  |  | 100.00 |  |  |  | 0.06 |  | 0.06 | [8 empty] | 0.05 |  |  |  |  | 0.06
1999 |  |  |  | 2841.27 |  |  | 8074 |  |  |  | 365 | [10 empty] | 88.60 |  |  |  | 91.33 | [5 empty] | 88.86 |  |  | 92.17 |  |  |  | 0.15 |  | 0.13 | [8 empty] | 8.54 |  |  |  |  | 2.72
2000 |  |  |  | 2539.20 |  |  | 7113 |  |  |  | 365 | [10 empty] | 78.30 |  |  |  | 79.22 | [5 empty] | 79.20 |  |  | 80.98 |  |  |  | 0.46 |  | 0.36 | [8 empty] | 20.41 |  |  |  |  | 0.92
2001 |  |  |  | 3090.18 |  |  | 8504 |  |  |  | 365 | [10 empty] | 96.76 |  |  |  | 96.76 | [5 empty] | 96.65 |  |  | 97.08 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.24 |  |  |  |  | 0.00
2002 |  |  |  | 2908.78 |  |  | 8000 |  |  |  | 365 | [10 empty] | 91.03 |  |  |  | 91.26 | [5 empty] | 90.97 |  |  | 91.32 |  |  |  | 0.03 |  | 0.89 | [8 empty] | 7.85 |  |  |  |  | 0.23
2003 |  |  |  | 3061.76 |  |  | 8494 |  |  |  | 365 | [10 empty] | 96.18 |  |  |  | 96.92 | [5 empty] | 95.76 |  |  | 96.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.08 |  |  |  |  | 0.74
2004 |  |  |  | 2801.17 |  |  | 7758 |  |  |  | 365 | [10 empty] | 87.44 |  |  |  | 87.53 | [5 empty] | 87.36 |  |  | 88.31 |  |  |  | 0.37 |  | 1.15 | [8 empty] | 11.32 |  |  |  |  | 0.09
2005 |  |  |  | 3095.96 |  |  | 8491 |  |  |  | 365 | [10 empty] | 96.64 |  |  |  | 96.67 | [5 empty] | 96.82 |  |  | 96.92 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 3.32 |  |  |  |  | 0.03
2006 |  |  |  | 2950.68 |  |  | 8114 |  |  |  | 365 | [10 empty] | 92.19 |  |  |  | 92.35 | [5 empty] | 92.28 |  |  | 92.63 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 7.65 |  |  |  |  | 0.15
2007 |  |  |  | 3081.34 |  |  | 8486 |  |  |  | 365 | [10 empty] | 96.67 |  |  |  | 96.70 | [5 empty] | 96.37 |  |  | 96.87 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.30 |  |  |  |  | 0.03
2008 |  |  |  | 2956.58 |  |  | 8143 |  |  |  | 365 | [10 empty] | 92.45 |  |  |  | 92.45 | [5 empty] | 92.22 |  |  | 92.70 |  |  |  | 0.11 |  | 0.10 | [8 empty] | 7.44 |  |  |  |  | 0.00
2009 |  |  |  | 3067.33 |  |  | 8460 |  |  |  | 365 | [10 empty] | 96.27 |  |  |  | 96.30 | [5 empty] | 95.93 |  |  | 96.58 |  |  |  | 0.57 |  | 0.68 | [8 empty] | 3.02 |  |  |  |  | 0.03
2010 |  |  |  | 2673.99 |  |  | 7347 |  |  |  | 365 | [10 empty] | 83.66 |  |  |  | 83.66 | [5 empty] | 83.63 |  |  | 83.87 |  |  |  | 0.04 |  | 1.13 | [8 empty] | 15.21 |  |  |  |  | 0.00
2011 |  |  |  | 3067.13 |  |  | 8458 |  |  |  | 365 | [10 empty] | 96.42 |  |  |  | 96.42 | [5 empty] | 95.93 |  |  | 96.55 |  |  |  | 0.00 |  | 0.02 | [8 empty] | 3.56 |  |  |  |  | 0.00
2012 |  |  |  | 2724.73 |  |  | 7508 |  |  |  | 365 | [10 empty] | 85.26 |  |  |  | 85.26 | [5 empty] | 84.98 |  |  | 85.47 |  |  |  | 0.02 |  | 1.32 | [8 empty] | 13.42 |  |  |  |  | 0.00
2013 |  |  |  | 3078.45 |  |  | 8473 |  |  |  | 365 | [10 empty] | 96.59 |  |  |  | 96.59 | [5 empty] | 96.28 |  |  | 96.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.41 |  |  |  |  | 0.00
2014 |  |  |  | 2920.61 |  |  | 8047 |  |  |  | 365 | [10 empty] | 91.64 |  |  |  | 91.64 | [5 empty] | 91.34 |  |  | 91.86 |  |  |  | 4.87 |  | 4.88 | [8 empty] | 3.48 |  |  |  |  | 0.00
2015 |  |  |  | 628.54 |  |  | 1715 |  |  |  | 365 | [10 empty] | 19.56 |  |  |  | 19.56 | [5 empty] | 19.66 |  |  | 19.58 |  |  |  | 0.00 |  | 47.99 | [8 empty] | 32.46 |  |  |  |  | 0.00
2016 |  |  |  | 0.00 |  |  | 0 |  |  |  | 365 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 94.81 | [8 empty] | 5.19 |  |  |  |  | 0.00
2017 |  |  |  | 0.00 |  |  | 0 |  |  |  | 365 | [10 empty] | 0.00 |  |  |  | 0.00 | [5 empty] | 0.00 |  |  | 0.00 |  |  |  | 0.00 |  | 100.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
2018 |  |  |  | 2483.69 |  |  | 6897 |  |  |  | 365 | [10 empty] | 77.34 |  |  |  | 78.25 | [5 empty] | 77.68 |  |  | 78.73 |  |  |  | 0.42 |  | 21.75 | [8 empty] | 0.00 |  |  |  |  | 0.91
2019 |  |  |  | 2854.84 |  |  | 7851 |  |  |  | 365 | [10 empty] | 88.65 |  |  |  | 89.60 | [5 empty] | 89.29 |  |  | 89.62 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.40 |  |  |  |  | 0.95
2020 |  |  |  | 2784.66 |  |  | 7661 |  |  |  | 365 | [10 empty] | 86.25 |  |  |  | 87.02 | [5 empty] | 86.85 |  |  | 87.22 |  |  |  | 3.61 |  | 3.26 | [8 empty] | 9.71 |  |  |  |  | 0.78
2021 |  |  |  | 3071.24 |  |  | 8449 |  |  |  | 365 | [10 empty] | 95.64 |  |  |  | 96.21 | [5 empty] | 96.05 |  |  | 96.45 |  |  |  | 0.09 |  | 0.08 | [8 empty] | 3.71 |  |  |  |  | 0.57
2022 |  |  |  | 2564.59 |  |  | 7244 |  |  |  | 365 | [10 empty] | 79.92 |  |  |  | 82.35 | [5 empty] | 80.21 |  |  | 82.69 |  |  |  | 0.21 |  | 2.68 | [8 empty] | 14.97 |  |  |  |  | 2.43
2023 |  |  |  | 2937.08 |  |  | 8377 |  |  |  | 365 | [10 empty] | 91.52 |  |  |  | 93.14 | [5 empty] | 91.86 |  |  | 95.63 |  |  |  | 2.40 |  | 2.81 | [8 empty] | 4.05 |  |  |  |  | 1.62
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1969 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 46 | [14 empty] | 191
B. |  | Refuelling without maintenance | [20 empty] | 337 | [14 empty] | 44
C. |  | Inspection, maintenance or repair combined with refuelling | [35 empty] | 783
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 13
E. |  | Testing of plant systems or components | [39 empty] | 0
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 62
H. |  | Nuclear regulatory requirements | [39 empty] | 437
L. |  | Human factor related | [39 empty] | 0
N. |  | Environmental conditions (lack of cooling water due to dry weather, cooling water temperature limits, flood, storm, lightning, etc.) | [51 empty] | 2
Subtotal | [22 empty] | 337 |  |  |  | 46 | [10 empty] | 902 |  |  |  | 628 | [11 empty] | 2
Total | [22 empty] | 383 | [14 empty] | 1532
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1969 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 46 | [14 empty] | 454
12. |  |  | Reactor I&C Systems | [34 empty] | 67
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 9
14. |  |  | Safety Systems | [34 empty] | 3
15. |  |  | Reactor Cooling Systems | [34 empty] | 12
16. |  |  | Steam generation systems | [34 empty] | 66
21. |  |  | Fuel Handling and Storage Facilities | [34 empty] | 0
31. |  |  | Turbine and auxiliaries | [34 empty] | 2
32. |  |  | Feedwater and Main Steam System | [34 empty] | 9
35. |  |  | All other I&C Systems | [34 empty] | 0
42. |  |  | Electrical Power Supply Systems | [34 empty] | 5
Total | [22 empty] | 46 | [14 empty] | 627
Highlights (2023)
Plant refuelling outage Shutdown TG 12 due to leak in feedwater system

## BEZNAU-2
2023 Operating Experience
CH-3 | [8 empty] | BEZNAU-2 | [26 empty] | SWITZERLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | Axpo AG (Kernkraftwerk Beznau CH-5312 Döttingen)
Owner | [7 empty] | : | Axpo AG (Kernkraftwerk Beznau CH-5312 Döttingen)
Reactor Supplier | [7 empty] | : | WH (WESTINGHOUSE ELECTRIC CORPORATION)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / WH 2LP | [11 empty] | Construction Date | [15 empty] | : |  |  | 1968-01-01
Thermal power | [12 empty] | : |  |  | 1130 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1971-10-23
Gross electrical power | [12 empty] | : |  |  | 380 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1972-03-04
Reference unit power (net) | [12 empty] | : |  |  | 365 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 52 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.5
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 313
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.31
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 4.68 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 2
| Part of the core refuelled [%] | [13 empty] | : |  |  | 17 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 42000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 2
| Active core diameter [m] | [13 empty] | : |  |  | 2.45 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 5.3
| Active core height/length [m] | [13 empty] | : |  |  | 3.05 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 121 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | River (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 16.7 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 2
| Number of control rod assemblies | [13 empty] | : |  |  | 25 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 1
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 3
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | DH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 2804.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.31 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.65 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.34 %
Unit Capability Factor (UCF) | [18 empty] | : | 88.69 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.97 %
Load Factor (LF) | [18 empty] | : | 87.71 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.04 %
Operating Factor (OF) | [18 empty] | : | 89.26 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 941 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 2.83 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 271.79 | 245.46 |  |  |  | 271.40 |  | 261.89 | [8 empty] | 269.20 |  |  | 254.81 | [6 empty] | 259.35 |  | 27.57 |  |  |  | 138.16 |  |  | 269.15 |  |  | 263.17 | [9 empty] | 272.45 |  |  | 2804.42
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.65 | [8 empty] | 99.13 |  |  | 96.96 | [6 empty] | 95.50 |  | 10.15 |  |  |  | 52.57 |  |  | 98.98 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 87.65
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 10.94 |  |  |  | 54.45 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.69
LF [%] |  |  |  |  | 100.09 | 100.07 |  |  |  | 100.08 |  | 99.65 | [8 empty] | 99.13 |  |  | 96.96 | [6 empty] | 95.50 |  | 10.15 |  |  |  | 52.57 |  |  | 98.98 |  |  | 100.14 | [9 empty] | 100.33 |  |  | 87.71
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 11.16 |  |  |  | 61.11 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 89.26
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 5.86 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.31
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 4.08 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.34
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 89.06 |  |  |  | 41.47 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 10.97
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.35 | [8 empty] | 0.87 |  |  | 3.04 | [6 empty] | 4.50 |  | 0.79 |  |  |  | 1.87 |  |  | 1.02 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 1.04
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 286421.08 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.11 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 87.6 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 1.14 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 87.84 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.02 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 87.83 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.25 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 88.86 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1972 |  |  |  | 2618.50 |  |  | 7624 |  |  |  | 364 | [10 empty] | 83.06 |  |  |  | 83.06 | [5 empty] | 82.10 |  |  | 84.20 |  |  |  | 9.60 |  | 8.82 | [8 empty] | 8.12 |  |  |  |  | 0.00
1973 |  |  |  | 2220.70 |  |  | 7042 |  |  |  | 350 | [10 empty] | 78.45 |  |  |  | 78.45 | [5 empty] | 72.43 |  |  | 80.39 |  |  |  | 1.91 |  | 1.53 | [8 empty] | 20.02 |  |  |  |  | 0.00
1974 |  |  |  | 2527.80 |  |  | 7607 |  |  |  | 350 | [10 empty] | 83.53 |  |  |  | 83.53 | [5 empty] | 82.45 |  |  | 86.84 |  |  |  | 0.65 |  | 0.55 | [8 empty] | 15.92 |  |  |  |  | 0.00
1975 |  |  |  | 2547.00 |  |  | 7503 |  |  |  | 350 | [10 empty] | 83.05 |  |  |  | 83.05 | [5 empty] | 83.07 |  |  | 85.65 |  |  |  | 3.98 |  | 3.45 | [8 empty] | 13.50 |  |  |  |  | 0.00
1976 |  |  |  | 2652.20 |  |  | 7777 |  |  |  | 350 | [10 empty] | 86.62 |  |  |  | 86.62 | [5 empty] | 86.27 |  |  | 88.54 |  |  |  | 0.29 |  | 0.25 | [8 empty] | 13.13 |  |  |  |  | 0.00
1977 |  |  |  | 2690.90 |  |  | 7758 |  |  |  | 350 | [10 empty] | 85.55 |  |  |  | 85.55 | [5 empty] | 87.77 |  |  | 88.56 |  |  |  | 0.67 |  | 0.58 | [8 empty] | 13.87 |  |  |  |  | 0.00
1978 |  |  |  | 2753.10 |  |  | 7888 |  |  |  | 350 | [10 empty] | 86.69 |  |  |  | 86.69 | [5 empty] | 89.79 |  |  | 90.05 |  |  |  | 3.14 |  | 2.81 | [8 empty] | 10.49 |  |  |  |  | 0.00
1979 |  |  |  | 2700.00 |  |  | 7835 |  |  |  | 350 | [10 empty] | 86.70 |  |  |  | 86.70 | [5 empty] | 88.06 |  |  | 89.44 |  |  |  | 2.84 |  | 2.54 | [8 empty] | 10.77 |  |  |  |  | 0.00
1980 |  |  |  | 2559.00 |  |  | 7279 |  |  |  | 350 | [10 empty] | 81.05 |  |  |  | 81.05 | [5 empty] | 83.24 |  |  | 82.87 |  |  |  | 6.13 |  | 5.29 | [8 empty] | 13.66 |  |  |  |  | 0.00
1981 |  |  |  | 2768.80 |  |  | 7868 |  |  |  | 350 | [10 empty] | 88.77 |  |  |  | 88.77 | [5 empty] | 90.31 |  |  | 89.82 |  |  |  | 0.13 |  | 0.11 | [8 empty] | 11.12 |  |  |  |  | 0.00
1982 |  |  |  | 2722.10 |  |  | 7811 |  |  |  | 350 | [10 empty] | 87.58 |  |  |  | 87.58 | [5 empty] | 88.78 |  |  | 89.17 |  |  |  | 0.25 |  | 0.22 | [8 empty] | 12.20 |  |  |  |  | 0.00
1983 |  |  |  | 2790.50 |  |  | 7977 |  |  |  | 350 | [10 empty] | 89.60 |  |  |  | 89.60 | [5 empty] | 91.01 |  |  | 91.06 |  |  |  | 0.70 |  | 0.63 | [8 empty] | 9.77 |  |  |  |  | 0.00
1984 |  |  |  | 2724.21 |  |  | 7874 |  |  |  | 350 | [10 empty] | 87.54 |  |  |  | 87.54 | [5 empty] | 88.61 |  |  | 89.64 |  |  |  | 0.19 |  | 0.17 | [8 empty] | 12.29 |  |  |  |  | 0.00
1985 |  |  |  | 2629.06 |  |  | 7647 |  |  |  | 350 | [10 empty] | 84.95 |  |  |  | 84.95 | [5 empty] | 85.75 |  |  | 87.29 |  |  |  | 2.99 |  | 2.62 | [8 empty] | 12.44 |  |  |  |  | 0.00
1986 |  |  |  | 2769.81 |  |  | 7983 |  |  |  | 350 | [10 empty] | 90.18 |  |  |  | 90.18 | [5 empty] | 90.34 |  |  | 91.13 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 9.76 |  |  |  |  | 0.00
1987 |  |  |  | 2527.62 |  |  | 7535 |  |  |  | 350 | [10 empty] | 82.38 |  |  |  | 82.38 | [5 empty] | 82.44 |  |  | 86.02 |  |  |  | 2.34 |  | 1.98 | [8 empty] | 15.64 |  |  |  |  | 0.00
1988 |  |  |  | 2630.19 |  |  | 7604 |  |  |  | 350 | [10 empty] | 84.53 |  |  |  | 84.53 | [5 empty] | 85.55 |  |  | 86.57 |  |  |  | 0.57 |  | 0.49 | [8 empty] | 14.98 |  |  |  |  | 0.00
1989 |  |  |  | 2643.34 |  |  | 7614 |  |  |  | 350 | [10 empty] | 85.11 |  |  |  | 85.11 | [5 empty] | 86.21 |  |  | 86.92 |  |  |  | 0.65 |  | 0.55 | [8 empty] | 14.34 |  |  |  |  | 0.00
1990 |  |  |  | 2636.07 |  |  | 7568 |  |  |  | 350 | [10 empty] | 85.25 |  |  |  | 85.25 | [5 empty] | 85.98 |  |  | 86.39 |  |  |  | 0.23 |  | 0.20 | [8 empty] | 14.55 |  |  |  |  | 0.00
1991 |  |  |  | 2619.53 |  |  | 7551 |  |  |  | 350 | [10 empty] | 84.48 |  |  |  | 84.48 | [5 empty] | 85.44 |  |  | 86.20 |  |  |  | 0.37 |  | 0.31 | [8 empty] | 15.21 |  |  |  |  | 0.00
1992 |  |  |  | 2375.90 |  |  | 6836 |  |  |  | 350 | [10 empty] | 76.26 |  |  |  | 76.26 | [5 empty] | 77.28 |  |  | 77.82 |  |  |  | 0.19 |  | 0.15 | [8 empty] | 23.60 |  |  |  |  | 0.00
1993 |  |  |  | 2650.93 |  |  | 7517 |  |  |  | 350 | [10 empty] | 84.86 |  |  |  | 85.09 | [5 empty] | 86.46 |  |  | 85.81 |  |  |  | 0.25 |  | 0.21 | [8 empty] | 14.70 |  |  |  |  | 0.23
1994 |  |  |  | 3062.80 |  |  | 8710 |  |  |  | 350 | [10 empty] | 98.78 |  |  |  | 98.94 | [5 empty] | 99.90 |  |  | 99.43 |  |  |  | 1.01 |  | 1.01 | [8 empty] | 0.05 |  |  |  |  | 0.16
1995 |  |  |  | 2560.94 |  |  | 7247 |  |  |  | 350 | [10 empty] | 82.58 |  |  |  | 82.72 | [5 empty] | 83.53 |  |  | 82.73 |  |  |  | 0.41 |  | 0.34 | [8 empty] | 16.94 |  |  |  |  | 0.14
1996 |  |  |  | 2754.10 |  |  | 7912 |  |  |  | 351 | [10 empty] | 87.91 |  |  |  | 88.51 | [5 empty] | 89.13 |  |  | 90.07 |  |  |  | 0.80 |  | 0.71 | [8 empty] | 10.78 |  |  |  |  | 0.60
1997 |  |  |  | 3090.24 |  |  | 8732 |  |  |  | 357 | [10 empty] | 99.54 |  |  |  | 99.54 | [5 empty] | 98.81 |  |  | 99.68 |  |  |  | 0.18 |  | 0.18 | [8 empty] | 0.28 |  |  |  |  | 0.01
1998 |  |  |  | 2717.82 |  |  | 7755 |  |  |  | 357 | [10 empty] | 87.26 |  |  |  | 87.76 | [5 empty] | 86.91 |  |  | 88.53 |  |  |  | 0.44 |  | 0.38 | [8 empty] | 11.85 |  |  |  |  | 0.50
1999 |  |  |  | 2217.19 |  |  | 6322 |  |  |  | 357 | [10 empty] | 70.28 |  |  |  | 70.68 | [5 empty] | 70.90 |  |  | 72.17 |  |  |  | 3.67 |  | 2.69 | [8 empty] | 26.62 |  |  |  |  | 0.41
2000 |  |  |  | 3071.03 |  |  | 8499 |  |  |  | 365 | [10 empty] | 96.20 |  |  |  | 96.20 | [5 empty] | 95.79 |  |  | 96.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.80 |  |  |  |  | 0.00
2001 |  |  |  | 2568.68 |  |  | 7107 |  |  |  | 365 | [10 empty] | 80.67 |  |  |  | 80.68 | [5 empty] | 80.34 |  |  | 81.13 |  |  |  | 0.33 |  | 0.27 | [8 empty] | 19.05 |  |  |  |  | 0.01
2002 |  |  |  | 3012.01 |  |  | 8292 |  |  |  | 365 | [10 empty] | 94.62 |  |  |  | 94.63 | [5 empty] | 94.20 |  |  | 94.66 |  |  |  | 0.26 |  | 1.98 | [8 empty] | 3.39 |  |  |  |  | 0.00
2003 |  |  |  | 2920.29 |  |  | 8070 |  |  |  | 365 | [10 empty] | 91.85 |  |  |  | 92.05 | [5 empty] | 91.33 |  |  | 92.12 |  |  |  | 0.79 |  | 0.74 | [8 empty] | 7.21 |  |  |  |  | 0.20
2004 |  |  |  | 3099.37 |  |  | 8556 |  |  |  | 365 | [10 empty] | 97.02 |  |  |  | 97.02 | [5 empty] | 96.66 |  |  | 97.39 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.98 |  |  |  |  | 0.00
2005 |  |  |  | 2801.02 |  |  | 7728 |  |  |  | 365 | [10 empty] | 87.84 |  |  |  | 87.95 | [5 empty] | 87.60 |  |  | 88.22 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 12.03 |  |  |  |  | 0.11
2006 |  |  |  | 3073.23 |  |  | 8517 |  |  |  | 365 | [10 empty] | 96.80 |  |  |  | 97.06 | [5 empty] | 96.12 |  |  | 97.23 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.94 |  |  |  |  | 0.26
2007 |  |  |  | 2911.65 |  |  | 8063 |  |  |  | 365 | [10 empty] | 91.46 |  |  |  | 91.48 | [5 empty] | 91.06 |  |  | 92.04 |  |  |  | 0.15 |  | 0.41 | [8 empty] | 8.11 |  |  |  |  | 0.02
2008 |  |  |  | 3073.36 |  |  | 8505 |  |  |  | 365 | [10 empty] | 96.25 |  |  |  | 96.25 | [5 empty] | 95.86 |  |  | 96.82 |  |  |  | 0.52 |  | 0.51 | [8 empty] | 3.25 |  |  |  |  | 0.00
2009 |  |  |  | 2758.47 |  |  | 7615 |  |  |  | 365 | [10 empty] | 86.56 |  |  |  | 86.67 | [5 empty] | 86.27 |  |  | 86.93 |  |  |  | 0.52 |  | 0.45 | [8 empty] | 12.88 |  |  |  |  | 0.10
2010 |  |  |  | 2856.53 |  |  | 7865 |  |  |  | 365 | [10 empty] | 89.59 |  |  |  | 89.59 | [5 empty] | 89.34 |  |  | 89.78 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.41 |  |  |  |  | 0.00
2011 |  |  |  | 2739.21 |  |  | 7564 |  |  |  | 365 | [10 empty] | 86.11 |  |  |  | 86.11 | [5 empty] | 85.67 |  |  | 86.35 |  |  |  | 0.00 |  | 1.68 | [8 empty] | 12.21 |  |  |  |  | 0.00
2012 |  |  |  | 2793.97 |  |  | 7715 |  |  |  | 365 | [10 empty] | 87.65 |  |  |  | 87.65 | [5 empty] | 87.14 |  |  | 87.83 |  |  |  | 6.98 |  | 9.01 | [8 empty] | 3.33 |  |  |  |  | 0.00
2013 |  |  |  | 2892.03 |  |  | 7968 |  |  |  | 365 | [10 empty] | 90.82 |  |  |  | 90.82 | [5 empty] | 90.45 |  |  | 90.96 |  |  |  | 0.00 |  | 0.18 | [8 empty] | 9.00 |  |  |  |  | 0.00
2014 |  |  |  | 3053.52 |  |  | 8433 |  |  |  | 365 | [10 empty] | 95.99 |  |  |  | 95.99 | [5 empty] | 95.50 |  |  | 96.27 |  |  |  | 0.13 |  | 0.13 | [8 empty] | 3.89 |  |  |  |  | 0.00
2015 |  |  |  | 2023.36 |  |  | 5611 |  |  |  | 365 | [10 empty] | 63.18 |  |  |  | 63.87 | [5 empty] | 63.28 |  |  | 64.05 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 36.13 |  |  |  |  | 0.68
2016 |  |  |  | 3048.37 |  |  | 8474 |  |  |  | 365 | [10 empty] | 94.49 |  |  |  | 96.27 | [5 empty] | 95.08 |  |  | 96.47 |  |  |  | 0.00 |  | 0.13 | [8 empty] | 3.60 |  |  |  |  | 1.78
2017 |  |  |  | 2813.62 |  |  | 7735 |  |  |  | 365 | [10 empty] | 87.42 |  |  |  | 87.75 | [5 empty] | 88.00 |  |  | 88.30 |  |  |  | 1.18 |  | 1.94 | [8 empty] | 10.31 |  |  |  |  | 0.33
2018 |  |  |  | 3057.41 |  |  | 8445 |  |  |  | 365 | [10 empty] | 95.26 |  |  |  | 96.28 | [5 empty] | 95.62 |  |  | 96.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 3.72 |  |  |  |  | 1.02
2019 |  |  |  | 2827.27 |  |  | 7790 |  |  |  | 365 | [10 empty] | 88.01 |  |  |  | 88.73 | [5 empty] | 88.42 |  |  | 88.93 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 11.22 |  |  |  |  | 0.72
2020 |  |  |  | 2956.04 |  |  | 8175 |  |  |  | 365 | [10 empty] | 91.92 |  |  |  | 92.83 | [5 empty] | 92.20 |  |  | 93.07 |  |  |  | 3.52 |  | 3.54 | [8 empty] | 3.63 |  |  |  |  | 0.91
2021 |  |  |  | 2850.23 |  |  | 7871 |  |  |  | 365 | [10 empty] | 89.08 |  |  |  | 89.69 | [5 empty] | 89.14 |  |  | 89.85 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.31 |  |  |  |  | 0.61
2022 |  |  |  | 2974.93 |  |  | 8406 |  |  |  | 365 | [10 empty] | 93.02 |  |  |  | 95.78 | [5 empty] | 93.04 |  |  | 95.96 |  |  |  | 0.21 |  | 0.21 | [8 empty] | 4.02 |  |  |  |  | 2.75
2023 |  |  |  | 2804.42 |  |  | 7819 |  |  |  | 365 | [10 empty] | 87.65 |  |  |  | 88.69 | [5 empty] | 87.71 |  |  | 89.26 |  |  |  | 0.31 |  | 0.34 | [8 empty] | 10.97 |  |  |  |  | 1.04
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1972 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 5 | [14 empty] | 90
B. |  | Refuelling without maintenance | [35 empty] | 58
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 936 | [14 empty] | 749
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 28
F. |  | Major backfitting, refurbishment or upgrading activities with refuelling | [35 empty] | 61
K. |  | Load-following (frequency control, reserve shutdown due to reduced energy demand, reactive power) | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 1
Subtotal | [22 empty] | 936 |  |  |  | 5 | [10 empty] | 896 |  |  |  | 91 | [11 empty] | 0
Total | [22 empty] | 941 | [14 empty] | 987
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1972 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [19 empty] | 5 | [14 empty] | 5
12. |  |  | Reactor I&C Systems | [34 empty] | 7
13. |  |  | Reactor Auxiliary Systems | [34 empty] | 1
14. |  |  | Safety Systems | [34 empty] | 1
15. |  |  | Reactor Cooling Systems | [34 empty] | 22
16. |  |  | Steam generation systems | [34 empty] | 19
17. |  |  | Safety I&C Systems (excluding reactor I&C) | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 10
32. |  |  | Feedwater and Main Steam System | [34 empty] | 3
33. |  |  | Circulating Water System | [34 empty] | 3
34. |  |  | Miscellaneous Systems | [34 empty] | 8
35. |  |  | All other I&C Systems | [34 empty] | 1
42. |  |  | Electrical Power Supply Systems | [34 empty] | 9
Total | [22 empty] | 5 | [14 empty] | 90
Highlights (2023)
Plant refuelling outage

## GOESGEN
2023 Operating Experience
CH-4 | [8 empty] | GOESGEN | [26 empty] | SWITZERLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KKG (KERNKRAFTWERK GÖSGEN-DÄNIKEN AG)
Owner | [7 empty] | : | KKG (KERNKRAFTWERK GÖSGEN-DÄNIKEN AG)
Reactor Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Turbine Supplier | [7 empty] | : | KWU (KRAFTWERK UNION, AG)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / PWR 3 Loop | [11 empty] | Construction Date | [15 empty] | : |  |  | 1973-12-01
Thermal power | [12 empty] | : |  |  | 3002 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1979-02-02
Gross electrical power | [12 empty] | : |  |  | 1060 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1979-11-01
Reference unit power (net) | [12 empty] | : |  |  | 1010 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 44 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.3
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 324.5
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 3
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Double
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 5
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 25 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 52000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.24 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.65
| Active core height/length [m] | [13 empty] | : |  |  | 3.58 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 177 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 22.6 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 36 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 3 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 6
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | PH
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 7973.07 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.06 %
Energy Availability Factor (EAF) | [18 empty] | : | 90.28 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.05 %
Unit Capability Factor (UCF) | [18 empty] | : | 91.61 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.34 %
Load Factor (LF) | [18 empty] | : | 90.11 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.34 %
Operating Factor (OF) | [18 empty] | : | 91.98 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 703 hours
Equivalent non-electrical energy generated (NEG) | [18 empty] | : | 22.72 GW(e).h
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 748.00 | 675.45 |  |  |  | 745.01 |  | 720.85 | [8 empty] | 620.38 |  |  | 100.77 | [6 empty] | 727.54 |  | 724.12 |  |  |  | 706.57 |  |  | 739.02 |  |  | 718.75 | [9 empty] | 746.60 |  |  | 7973.07
EAF [%] |  |  |  |  | 98.95 | 98.95 |  |  |  | 99.02 |  | 99.00 | [8 empty] | 83.49 |  |  | 15.05 | [6 empty] | 97.09 |  | 96.76 |  |  |  | 97.46 |  |  | 99.05 |  |  | 98.68 | [9 empty] | 99.00 |  |  | 90.28
UCF [%] |  |  |  |  | 99.96 | 99.97 |  |  |  | 99.97 |  | 99.98 | [8 empty] | 84.22 |  |  | 15.11 | [6 empty] | 99.97 |  | 99.63 |  |  |  | 99.98 |  |  | 99.98 |  |  | 99.74 | [9 empty] | 99.98 |  |  | 91.61
LF [%] |  |  |  |  | 99.54 | 99.52 |  |  |  | 99.14 |  | 99.13 | [8 empty] | 82.56 |  |  | 13.86 | [6 empty] | 96.82 |  | 96.36 |  |  |  | 97.16 |  |  | 98.21 |  |  | 98.84 | [9 empty] | 99.36 |  |  | 90.11
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 84.54 |  |  | 18.33 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.98
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.35 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.24 | [9 empty] | 0.00 |  |  | 0.06
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.01 |  | 0.35 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.24 | [9 empty] | 0.00 |  |  | 0.05
PUF [%] |  |  |  |  | 0.04 | 0.03 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 15.78 |  |  | 84.89 | [6 empty] | 0.02 |  | 0.02 |  |  |  | 0.02 |  |  | 0.02 |  |  | 0.02 | [9 empty] | 0.02 |  |  | 8.34
XUF [%] |  |  |  |  | 1.01 | 1.03 |  |  |  | 0.96 |  | 0.98 | [8 empty] | 0.73 |  |  | 0.06 | [6 empty] | 2.88 |  | 2.87 |  |  |  | 2.52 |  |  | 0.93 |  |  | 1.06 | [9 empty] | 0.98 |  |  | 1.34
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 329212.12 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 1.04 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 89.03 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.95 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 89.86 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 9.19 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 89.36 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.84 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 90.73 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1979 |  |  |  | 3398.70 |  |  | 4724 |  |  |  | 924 | [10 empty] | 93.20 |  |  |  | 93.20 | [5 empty] | 93.22 |  |  | 97.13 |  |  |  | 6.80 |  | 6.80 | [8 empty] | 0.00 |  |  |  |  | 0.00
1980 |  |  |  | 5935.70 |  |  | 6819 |  |  |  | 920 | [10 empty] | 73.47 |  |  |  | 73.47 | [5 empty] | 73.45 |  |  | 77.63 |  |  |  | 9.11 |  | 7.37 | [8 empty] | 19.16 |  |  |  |  | 0.00
1981 |  |  |  | 6527.60 |  |  | 7523 |  |  |  | 920 | [10 empty] | 80.66 |  |  |  | 80.66 | [5 empty] | 81.00 |  |  | 85.88 |  |  |  | 0.87 |  | 0.71 | [8 empty] | 18.64 |  |  |  |  | 0.00
1982 |  |  |  | 6436.10 |  |  | 7665 |  |  |  | 920 | [10 empty] | 79.81 |  |  |  | 79.81 | [5 empty] | 79.86 |  |  | 87.50 |  |  |  | 5.99 |  | 5.08 | [8 empty] | 15.10 |  |  |  |  | 0.00
1983 |  |  |  | 6891.60 |  |  | 7790 |  |  |  | 920 | [10 empty] | 86.17 |  |  |  | 86.17 | [5 empty] | 85.51 |  |  | 88.93 |  |  |  | 2.77 |  | 2.46 | [8 empty] | 11.38 |  |  |  |  | 0.00
1984 |  |  |  | 7134.78 |  |  | 8015 |  |  |  | 900 | [10 empty] | 89.85 |  |  |  | 90.60 | [5 empty] | 90.25 |  |  | 91.25 |  |  |  | 0.54 |  | 0.50 | [8 empty] | 8.91 |  |  |  |  | 0.75
1985 |  |  |  | 6747.72 |  |  | 7789 |  |  |  | 909 | [10 empty] | 84.62 |  |  |  | 85.68 | [5 empty] | 84.74 |  |  | 88.92 |  |  |  | 3.31 |  | 2.93 | [8 empty] | 11.39 |  |  |  |  | 1.06
1986 |  |  |  | 6754.54 |  |  | 7386 |  |  |  | 941 | [10 empty] | 82.76 |  |  |  | 84.14 | [5 empty] | 81.94 |  |  | 84.32 |  |  |  | 0.03 |  | 0.02 | [8 empty] | 15.83 |  |  |  |  | 1.38
1987 |  |  |  | 6910.34 |  |  | 7521 |  |  |  | 935 | [10 empty] | 84.39 |  |  |  | 85.18 | [5 empty] | 84.37 |  |  | 85.86 |  |  |  | 0.19 |  | 0.16 | [8 empty] | 14.66 |  |  |  |  | 0.79
1988 |  |  |  | 6858.97 |  |  | 7476 |  |  |  | 936 | [10 empty] | 83.36 |  |  |  | 84.71 | [5 empty] | 83.42 |  |  | 85.11 |  |  |  | 0.11 |  | 0.09 | [8 empty] | 15.20 |  |  |  |  | 1.35
1989 |  |  |  | 6878.68 |  |  | 7514 |  |  |  | 931 | [10 empty] | 84.31 |  |  |  | 85.40 | [5 empty] | 84.34 |  |  | 85.78 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 14.58 |  |  |  |  | 1.08
1990 |  |  |  | 7131.49 |  |  | 7983 |  |  |  | 929 | [10 empty] | 87.61 |  |  |  | 89.42 | [5 empty] | 87.63 |  |  | 91.13 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 10.55 |  |  |  |  | 1.81
1991 |  |  |  | 7141.94 |  |  | 7918 |  |  |  | 925 | [10 empty] | 88.08 |  |  |  | 89.68 | [5 empty] | 88.14 |  |  | 90.39 |  |  |  | 0.32 |  | 0.29 | [8 empty] | 10.02 |  |  |  |  | 1.61
1992 |  |  |  | 7406.91 |  |  | 8107 |  |  |  | 934 | [10 empty] | 90.16 |  |  |  | 92.11 | [5 empty] | 90.23 |  |  | 92.29 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 7.85 |  |  |  |  | 1.95
1993 |  |  |  | 7408.12 |  |  | 8075 |  |  |  | 950 | [10 empty] | 88.93 |  |  |  | 89.26 | [5 empty] | 89.02 |  |  | 92.18 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 10.74 |  |  |  |  | 0.34
1994 |  |  |  | 7661.09 |  |  | 8102 |  |  |  | 947 | [10 empty] | 91.07 |  |  |  | 92.13 | [5 empty] | 92.35 |  |  | 92.49 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.87 |  |  |  |  | 1.06
1995 |  |  |  | 7820.85 |  |  | 8109 |  |  |  | 971 | [10 empty] | 91.07 |  |  |  | 91.77 | [5 empty] | 91.95 |  |  | 92.57 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 8.23 |  |  |  |  | 0.70
1996 |  |  |  | 7928.35 |  |  | 8204 |  |  |  | 986 | [10 empty] | 91.54 |  |  |  | 93.40 | [5 empty] | 91.54 |  |  | 93.40 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.60 |  |  |  |  | 1.86
1997 |  |  |  | 7967.77 |  |  | 8189 |  |  |  | 986 | [10 empty] | 91.55 |  |  |  | 93.48 | [5 empty] | 92.25 |  |  | 93.48 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.52 |  |  |  |  | 1.93
1998 |  |  |  | 7839.73 |  |  | 8179 |  |  |  | 986 | [10 empty] | 90.77 |  |  |  | 93.18 | [5 empty] | 90.77 |  |  | 93.37 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.82 |  |  |  |  | 2.42
1999 |  |  |  | 7533.93 |  |  | 7887 |  |  |  | 970 | [10 empty] | 88.75 |  |  |  | 89.93 | [5 empty] | 88.66 |  |  | 90.03 |  |  |  | 1.27 |  | 1.16 | [8 empty] | 8.91 |  |  |  |  | 1.18
2000 |  |  |  | 7804.26 |  |  | 8089 |  |  |  | 970 | [10 empty] | 91.66 |  |  |  | 92.02 | [5 empty] | 91.59 |  |  | 92.09 |  |  |  | 0.43 |  | 0.40 | [8 empty] | 7.58 |  |  |  |  | 0.36
2001 |  |  |  | 7870.47 |  |  | 8206 |  |  |  | 970 | [10 empty] | 92.64 |  |  |  | 93.50 | [5 empty] | 92.61 |  |  | 93.67 |  |  |  | 0.36 |  | 0.34 | [8 empty] | 6.15 |  |  |  |  | 0.86
2002 |  |  |  | 7853.30 |  |  | 8154 |  |  |  | 970 | [10 empty] | 92.34 |  |  |  | 92.89 | [5 empty] | 92.42 |  |  | 93.08 |  |  |  | 1.55 |  | 1.46 | [8 empty] | 5.64 |  |  |  |  | 0.56
2003 |  |  |  | 7988.68 |  |  | 8291 |  |  |  | 970 | [10 empty] | 93.88 |  |  |  | 94.46 | [5 empty] | 94.02 |  |  | 94.65 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 5.53 |  |  |  |  | 0.58
2004 |  |  |  | 8015.60 |  |  | 8300 |  |  |  | 970 | [10 empty] | 93.79 |  |  |  | 94.31 | [5 empty] | 94.07 |  |  | 94.49 |  |  |  | 0.24 |  | 0.23 | [8 empty] | 5.46 |  |  |  |  | 0.52
2005 |  |  |  | 7588.23 |  |  | 7754 |  |  |  | 970 | [10 empty] | 87.99 |  |  |  | 88.38 | [5 empty] | 89.30 |  |  | 88.52 |  |  |  | 0.14 |  | 0.12 | [8 empty] | 11.50 |  |  |  |  | 0.39
2006 |  |  |  | 8099.10 |  |  | 8230 |  |  |  | 970 | [10 empty] | 93.59 |  |  |  | 93.74 | [5 empty] | 95.31 |  |  | 93.95 |  |  |  | 0.10 |  | 0.10 | [8 empty] | 6.17 |  |  |  |  | 0.15
2007 |  |  |  | 8158.91 |  |  | 8313 |  |  |  | 970 | [10 empty] | 94.64 |  |  |  | 94.77 | [5 empty] | 96.02 |  |  | 94.90 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 5.23 |  |  |  |  | 0.13
2008 |  |  |  | 7964.01 |  |  | 8148 |  |  |  | 970 | [10 empty] | 92.19 |  |  |  | 92.63 | [5 empty] | 93.47 |  |  | 92.76 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.37 |  |  |  |  | 0.44
2009 |  |  |  | 8072.42 |  |  | 8267 |  |  |  | 970 | [10 empty] | 93.96 |  |  |  | 94.18 | [5 empty] | 95.00 |  |  | 94.37 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 5.81 |  |  |  |  | 0.23
2010 |  |  |  | 8029.09 |  |  | 8220 |  |  |  | 970 | [10 empty] | 93.11 |  |  |  | 93.21 | [5 empty] | 94.49 |  |  | 93.84 |  |  |  | 0.01 |  | 0.00 | [8 empty] | 6.78 |  |  |  |  | 0.10
2011 |  |  |  | 7910.31 |  |  | 8122 |  |  |  | 970 | [10 empty] | 91.95 |  |  |  | 92.02 | [5 empty] | 93.09 |  |  | 92.72 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.98 |  |  |  |  | 0.07
2012 |  |  |  | 8073.93 |  |  | 8281 |  |  |  | 985 | [10 empty] | 93.12 |  |  |  | 93.35 | [5 empty] | 93.32 |  |  | 94.27 |  |  |  | 0.51 |  | 0.48 | [8 empty] | 6.17 |  |  |  |  | 0.23
2013 |  |  |  | 6410.20 |  |  | 6491 |  |  |  | 985 | [10 empty] | 73.39 |  |  |  | 73.43 | [5 empty] | 74.29 |  |  | 74.10 |  |  |  | 12.09 |  | 10.09 | [8 empty] | 16.47 |  |  |  |  | 0.04
2014 |  |  |  | 8021.58 |  |  | 8029 |  |  |  | 1010 | [10 empty] | 90.80 |  |  |  | 91.11 | [5 empty] | 91.79 |  |  | 91.66 |  |  |  | 0.13 |  | 0.12 | [8 empty] | 8.77 |  |  |  |  | 0.31
2015 |  |  |  | 7971.20 |  |  | 7980 |  |  |  | 1010 | [10 empty] | 90.34 |  |  |  | 90.65 | [5 empty] | 90.09 |  |  | 91.10 |  |  |  | 0.69 |  | 0.63 | [8 empty] | 8.72 |  |  |  |  | 0.31
2016 |  |  |  | 8233.25 |  |  | 8232 |  |  |  | 1010 | [10 empty] | 92.63 |  |  |  | 93.32 | [5 empty] | 92.80 |  |  | 93.72 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 6.61 |  |  |  |  | 0.69
2017 |  |  |  | 8154.30 |  |  | 8148 |  |  |  | 1010 | [10 empty] | 92.01 |  |  |  | 92.66 | [5 empty] | 92.16 |  |  | 93.01 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 7.33 |  |  |  |  | 0.65
2018 |  |  |  | 8172.01 |  |  | 8244 |  |  |  | 1010 | [10 empty] | 92.14 |  |  |  | 93.77 | [5 empty] | 92.36 |  |  | 94.11 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 6.23 |  |  |  |  | 1.63
2019 |  |  |  | 7743.07 |  |  | 7835 |  |  |  | 1010 | [10 empty] | 87.36 |  |  |  | 89.00 | [5 empty] | 87.52 |  |  | 89.44 |  |  |  | 5.34 |  | 5.02 | [8 empty] | 5.97 |  |  |  |  | 1.64
2020 |  |  |  | 8249.56 |  |  | 8360 |  |  |  | 1010 | [10 empty] | 92.94 |  |  |  | 94.52 | [5 empty] | 92.99 |  |  | 95.17 |  |  |  | 0.40 |  | 0.38 | [8 empty] | 5.10 |  |  |  |  | 1.58
2021 |  |  |  | 7819.83 |  |  | 7900 |  |  |  | 1010 | [10 empty] | 88.25 |  |  |  | 89.59 | [5 empty] | 88.38 |  |  | 90.18 |  |  |  | 0.85 |  | 0.77 | [8 empty] | 9.64 |  |  |  |  | 1.34
2022 |  |  |  | 7886.66 |  |  | 7968 |  |  |  | 1010 | [10 empty] | 89.15 |  |  |  | 90.56 | [5 empty] | 89.14 |  |  | 90.96 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.44 |  |  |  |  | 1.41
2023 |  |  |  | 7973.07 |  |  | 8058 |  |  |  | 1010 | [10 empty] | 90.28 |  |  |  | 91.61 | [5 empty] | 90.11 |  |  | 91.98 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 8.34 |  |  |  |  | 1.34
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1979 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 55
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 705 | [14 empty] | 757
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 0
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 0
J. |  | Grid limitation, failure or grid unavailability | [51 empty] | 0
L. |  | Human factor related | [39 empty] | 0
Subtotal | [22 empty] | 705 | [14 empty] | 757 |  |  |  | 55 | [11 empty] | 0
Total | [22 empty] | 705 | [14 empty] | 812
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1979 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 3
12. |  |  | Reactor I&C Systems | [34 empty] | 0
15. |  |  | Reactor Cooling Systems | [34 empty] | 0
16. |  |  | Steam generation systems | [34 empty] | 1
31. |  |  | Turbine and auxiliaries | [34 empty] | 3
32. |  |  | Feedwater and Main Steam System | [34 empty] | 16
41. |  |  | Main Generator Systems | [34 empty] | 22
42. |  |  | Electrical Power Supply Systems | [34 empty] | 9
Total | [37 empty] | 54
Highlights (2023)
26.08.2023: Power reduction to 50 % due to a unplanned closed turbine valve. 20.11.2023: Power reduction to 30 % due to a unplanned trip of a reactor coolant pump.

## LEIBSTADT
2023 Operating Experience
CH-5 | [8 empty] | LEIBSTADT | [26 empty] | SWITZERLAND
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | KKL (KERNKRAFTWERK LEIBSTADT)
Owner | [7 empty] | : | KKL (KERNKRAFTWERK LEIBSTADT)
Reactor Supplier | [7 empty] | : | GETSCO (GENERAL ELECTRIC TECHNICAL SERVICES CO.)
Turbine Supplier | [7 empty] | : | BBC (BROWN BOVERI ET CIE)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | BWR / BWR-6 | [11 empty] | Construction Date | [15 empty] | : |  |  | 1974-01-01
Thermal power | [12 empty] | : |  |  | 3600 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 1984-05-24
Gross electrical power | [12 empty] | : |  |  | 1275 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 1984-12-15
Reference unit power (net) | [12 empty] | : |  |  | 1233 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 39 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 7.31
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 286
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | NA
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | -
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 12 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 18 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 3000
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 43000 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | 4.38 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.76
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 648 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Cooling towers
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 13.3 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | 211 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | -
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 9689.42 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.61 %
Energy Availability Factor (EAF) | [18 empty] | : | 89.7 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.56 %
Unit Capability Factor (UCF) | [18 empty] | : | 90.81 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 8.63 %
Load Factor (LF) | [18 empty] | : | 89.71 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 1.11 %
Operating Factor (OF) | [18 empty] | : | 91.51 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 744 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 915.69 | 824.29 |  |  |  | 909.20 |  | 878.21 | [8 empty] | 6.51 |  |  | 795.45 | [6 empty] | 891.43 |  | 890.68 |  |  |  | 864.86 |  |  | 909.39 |  |  | 885.36 | [9 empty] | 918.34 |  |  | 9689.42
EAF [%] |  |  |  |  | 99.82 | 99.48 |  |  |  | 99.24 |  | 98.92 | [8 empty] | 0.71 |  |  | 89.60 | [6 empty] | 97.17 |  | 97.09 |  |  |  | 97.42 |  |  | 99.00 |  |  | 99.73 | [9 empty] | 100.00 |  |  | 89.70
UCF [%] |  |  |  |  | 100.00 | 99.80 |  |  |  | 99.88 |  | 99.84 | [8 empty] | 0.72 |  |  | 91.68 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 99.81 |  |  | 100.00 |  |  | 99.76 | [9 empty] | 100.00 |  |  | 90.81
LF [%] |  |  |  |  | 99.82 | 99.48 |  |  |  | 99.24 |  | 98.92 | [8 empty] | 0.71 |  |  | 89.60 | [6 empty] | 97.17 |  | 97.09 |  |  |  | 97.42 |  |  | 99.00 |  |  | 99.73 | [9 empty] | 100.11 |  |  | 89.71
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 3.09 |  |  | 96.81 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 91.51
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 6.90 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.61
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 6.80 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.56
PUF [%] |  |  |  |  | 0.00 | 0.20 |  |  |  | 0.12 |  | 0.16 | [8 empty] | 99.28 |  |  | 1.52 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.19 |  |  | 0.00 |  |  | 0.24 | [9 empty] | 0.00 |  |  | 8.63
XUF [%] |  |  |  |  | 0.18 | 0.32 |  |  |  | 0.63 |  | 0.91 | [8 empty] | 0.01 |  |  | 2.08 | [6 empty] | 2.83 |  | 2.91 |  |  |  | 2.39 |  |  | 1.00 |  |  | 0.03 | [9 empty] | 0.00 |  |  | 1.11
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 317764.41 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 2.23 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 82.41 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 3.12 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 84 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 12.88 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 82.56 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 1.58 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 86.06 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
1984 |  |  |  | 2.21 |  |  | 3361 |  |  |  | 1030 | [10 empty] | 100.00 |  |  |  | 100.00 | [5 empty] | 0.09 |  |  | 100.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  |  |  | 0.00
1985 |  |  |  | 6769.30 |  |  | 7233 |  |  |  | 951 | [10 empty] | 80.12 |  |  |  | 80.12 | [5 empty] | 81.24 |  |  | 82.57 |  |  |  | 1.82 |  | 1.48 | [8 empty] | 18.40 |  |  |  |  | 0.00
1986 |  |  |  | 7209.23 |  |  | 7668 |  |  |  | 957 | [10 empty] | 83.24 |  |  |  | 83.24 | [5 empty] | 85.91 |  |  | 87.53 |  |  |  | 1.10 |  | 0.93 | [8 empty] | 15.83 |  |  |  |  | 0.00
1987 |  |  |  | 7376.42 |  |  | 7917 |  |  |  | 990 | [10 empty] | 85.24 |  |  |  | 85.24 | [5 empty] | 85.06 |  |  | 90.38 |  |  |  | 0.50 |  | 0.43 | [8 empty] | 14.33 |  |  |  |  | 0.00
1988 |  |  |  | 7003.53 |  |  | 7536 |  |  |  | 990 | [10 empty] | 79.99 |  |  |  | 79.99 | [5 empty] | 80.54 |  |  | 85.79 |  |  |  | 1.29 |  | 1.05 | [8 empty] | 18.96 |  |  |  |  | 0.00
1989 |  |  |  | 7364.21 |  |  | 7671 |  |  |  | 990 | [10 empty] | 85.52 |  |  |  | 85.52 | [5 empty] | 84.92 |  |  | 87.57 |  |  |  | 1.37 |  | 1.19 | [8 empty] | 13.29 |  |  |  |  | 0.00
1990 |  |  |  | 7596.23 |  |  | 7905 |  |  |  | 990 | [10 empty] | 89.85 |  |  |  | 89.85 | [5 empty] | 87.59 |  |  | 90.24 |  |  |  | 0.44 |  | 0.40 | [8 empty] | 9.75 |  |  |  |  | 0.00
1991 |  |  |  | 7060.30 |  |  | 7580 |  |  |  | 990 | [10 empty] | 81.27 |  |  |  | 86.01 | [5 empty] | 81.41 |  |  | 86.53 |  |  |  | 0.56 |  | 0.48 | [8 empty] | 13.51 |  |  |  |  | 4.74
1992 |  |  |  | 7537.62 |  |  | 7986 |  |  |  | 990 | [10 empty] | 86.44 |  |  |  | 90.38 | [5 empty] | 86.68 |  |  | 90.92 |  |  |  | 0.60 |  | 0.55 | [8 empty] | 9.08 |  |  |  |  | 3.93
1993 |  |  |  | 7338.05 |  |  | 7898 |  |  |  | 990 | [10 empty] | 84.38 |  |  |  | 89.14 | [5 empty] | 84.61 |  |  | 90.16 |  |  |  | 0.46 |  | 0.41 | [8 empty] | 10.44 |  |  |  |  | 4.76
1994 |  |  |  | 6988.22 |  |  | 7108 |  |  |  | 1003 | [10 empty] | 79.42 |  |  |  | 81.37 | [5 empty] | 79.51 |  |  | 81.14 |  |  |  | 1.34 |  | 1.10 | [8 empty] | 17.53 |  |  |  |  | 1.95
1995 |  |  |  | 7673.83 |  |  | 7819 |  |  |  | 1030 | [10 empty] | 84.18 |  |  |  | 89.07 | [5 empty] | 85.05 |  |  | 89.26 |  |  |  | 1.53 |  | 1.38 | [8 empty] | 9.55 |  |  |  |  | 4.89
1996 |  |  |  | 7705.13 |  |  | 7734 |  |  |  | 1030 | [10 empty] | 84.75 |  |  |  | 87.58 | [5 empty] | 85.16 |  |  | 88.05 |  |  |  | 0.17 |  | 0.15 | [8 empty] | 12.26 |  |  |  |  | 2.83
1997 |  |  |  | 7762.50 |  |  | 7830 |  |  |  | 1030 | [10 empty] | 86.20 |  |  |  | 89.23 | [5 empty] | 86.03 |  |  | 89.38 |  |  |  | 0.69 |  | 0.62 | [8 empty] | 10.15 |  |  |  |  | 3.03
1998 |  |  |  | 8046.20 |  |  | 8102 |  |  |  | 1030 | [10 empty] | 88.21 |  |  |  | 92.35 | [5 empty] | 89.18 |  |  | 92.49 |  |  |  | 0.03 |  | 0.03 | [8 empty] | 7.62 |  |  |  |  | 4.14
1999 |  |  |  | 8319.99 |  |  | 8126 |  |  |  | 1080 | [10 empty] | 86.82 |  |  |  | 91.82 | [5 empty] | 87.94 |  |  | 92.76 |  |  |  | 0.01 |  | 0.01 | [8 empty] | 8.17 |  |  |  |  | 5.00
2000 |  |  |  | 8823.19 |  |  | 8159 |  |  |  | 1115 | [10 empty] | 89.48 |  |  |  | 92.32 | [5 empty] | 90.09 |  |  | 92.88 |  |  |  | 0.50 |  | 0.47 | [8 empty] | 7.21 |  |  |  |  | 2.84
2001 |  |  |  | 9089.77 |  |  | 8187 |  |  |  | 1115 | [10 empty] | 90.38 |  |  |  | 91.17 | [5 empty] | 93.06 |  |  | 93.46 |  |  |  | 0.22 |  | 0.20 | [8 empty] | 8.63 |  |  |  |  | 0.78
2002 |  |  |  | 9173.83 |  |  | 8250 |  |  |  | 1115 | [10 empty] | 90.83 |  |  |  | 91.47 | [5 empty] | 93.92 |  |  | 94.18 |  |  |  | 1.83 |  | 1.71 | [8 empty] | 6.83 |  |  |  |  | 0.64
2003 |  |  |  | 9309.34 |  |  | 8204 |  |  |  | 1165 | [10 empty] | 90.08 |  |  |  | 90.92 | [5 empty] | 91.21 |  |  | 93.64 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 9.08 |  |  |  |  | 0.84
2004 |  |  |  | 8692.04 |  |  | 7633 |  |  |  | 1165 | [10 empty] | 84.89 |  |  |  | 85.74 | [5 empty] | 84.94 |  |  | 86.90 |  |  |  | 1.33 |  | 1.16 | [8 empty] | 13.10 |  |  |  |  | 0.86
2005 |  |  |  | 5768.08 |  |  | 5004 |  |  |  | 1165 | [10 empty] | 56.34 |  |  |  | 56.51 | [5 empty] | 56.51 |  |  | 57.12 |  |  |  | 41.21 |  | 39.61 | [8 empty] | 3.88 |  |  |  |  | 0.17
2006 |  |  |  | 9367.04 |  |  | 8206 |  |  |  | 1165 | [10 empty] | 91.70 |  |  |  | 92.72 | [5 empty] | 91.79 |  |  | 93.68 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 7.26 |  |  |  |  | 1.02
2007 |  |  |  | 9436.80 |  |  | 8276 |  |  |  | 1165 | [10 empty] | 93.23 |  |  |  | 93.43 | [5 empty] | 92.46 |  |  | 94.46 |  |  |  | 1.09 |  | 1.03 | [8 empty] | 5.55 |  |  |  |  | 0.20
2008 |  |  |  | 9307.65 |  |  | 8119 |  |  |  | 1165 | [10 empty] | 90.72 |  |  |  | 91.86 | [5 empty] | 90.95 |  |  | 92.43 |  |  |  | 0.07 |  | 0.06 | [8 empty] | 8.07 |  |  |  |  | 1.14
2009 |  |  |  | 9385.05 |  |  | 8203 |  |  |  | 1165 | [10 empty] | 91.69 |  |  |  | 93.12 | [5 empty] | 91.96 |  |  | 93.64 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 6.85 |  |  |  |  | 1.42
2010 |  |  |  | 8774.54 |  |  | 7640 |  |  |  | 1165 | [10 empty] | 85.14 |  |  |  | 86.14 | [5 empty] | 85.98 |  |  | 87.21 |  |  |  | 0.30 |  | 0.26 | [8 empty] | 13.60 |  |  |  |  | 1.00
2011 |  |  |  | 9481.35 |  |  | 8094 |  |  |  | 1190 | [10 empty] | 90.71 |  |  |  | 91.56 | [5 empty] | 90.95 |  |  | 92.40 |  |  |  | 0.22 |  | 0.21 | [8 empty] | 8.24 |  |  |  |  | 0.84
2012 |  |  |  | 7881.30 |  |  | 6746 |  |  |  | 1190 | [10 empty] | 74.92 |  |  |  | 75.92 | [5 empty] | 75.40 |  |  | 76.80 |  |  |  | 0.13 |  | 9.82 | [8 empty] | 14.26 |  |  |  |  | 1.00
2013 |  |  |  | 9691.67 |  |  | 8150 |  |  |  | 1220 | [10 empty] | 90.59 |  |  |  | 92.15 | [5 empty] | 90.68 |  |  | 93.04 |  |  |  | 0.20 |  | 0.18 | [8 empty] | 7.66 |  |  |  |  | 1.56
2014 |  |  |  | 9457.60 |  |  | 7970 |  |  |  | 1220 | [10 empty] | 88.49 |  |  |  | 90.08 | [5 empty] | 88.49 |  |  | 90.98 |  |  |  | 0.51 |  | 0.46 | [8 empty] | 9.46 |  |  |  |  | 1.59
2015 |  |  |  | 8598.52 |  |  | 7322 |  |  |  | 1220 | [10 empty] | 80.45 |  |  |  | 82.39 | [5 empty] | 80.45 |  |  | 83.57 |  |  |  | 7.57 |  | 6.75 | [8 empty] | 10.87 |  |  |  |  | 1.94
2016 |  |  |  | 6075.41 |  |  | 5147 |  |  |  | 1220 | [10 empty] | 57.01 |  |  |  | 58.19 | [5 empty] | 56.70 |  |  | 58.60 |  |  |  | 0.00 |  | 33.33 | [8 empty] | 8.48 |  |  |  |  | 1.18
2017 |  |  |  | 5618.75 |  |  | 5347 |  |  |  | 1220 | [10 empty] | 52.86 |  |  |  | 54.52 | [5 empty] | 52.57 |  |  | 61.04 |  |  |  | 0.65 |  | 0.36 | [8 empty] | 45.13 |  |  |  |  | 1.66
2018 |  |  |  | 7812.96 |  |  | 7658 |  |  |  | 1220 | [10 empty] | 73.11 |  |  |  | 74.43 | [5 empty] | 73.11 |  |  | 87.42 |  |  |  | 6.86 |  | 5.48 | [8 empty] | 20.09 |  |  |  |  | 1.32
2019 |  |  |  | 8819.52 |  |  | 7792 |  |  |  | 1220 | [10 empty] | 82.54 |  |  |  | 84.38 | [5 empty] | 82.52 |  |  | 88.95 |  |  |  | 3.67 |  | 3.22 | [8 empty] | 12.40 |  |  |  |  | 1.84
2020 |  |  |  | 9058.71 |  |  | 7727 |  |  |  | 1220 | [10 empty] | 84.53 |  |  |  | 86.02 | [5 empty] | 84.53 |  |  | 87.97 |  |  |  | 0.04 |  | 0.03 | [8 empty] | 13.95 |  |  |  |  | 1.49
2021 |  |  |  | 4851.90 |  |  | 4102 |  |  |  | 1220 | [10 empty] | 45.03 |  |  |  | 45.80 | [5 empty] | 45.40 |  |  | 46.83 |  |  |  | 0.74 |  | 0.34 | [8 empty] | 53.86 |  |  |  |  | 0.40
2022 |  |  |  | 9753.38 |  |  | 8048 |  |  |  | 1233 | [10 empty] | 90.28 |  |  |  | 91.23 | [5 empty] | 90.30 |  |  | 91.87 |  |  |  | 0.26 |  | 0.24 | [8 empty] | 8.53 |  |  |  |  | 0.95
2023 |  |  |  | 9689.42 |  |  | 8016 |  |  |  | 1233 | [10 empty] | 89.70 |  |  |  | 90.81 | [5 empty] | 89.71 |  |  | 91.51 |  |  |  | 0.61 |  | 0.56 | [8 empty] | 8.63 |  |  |  |  | 1.11
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 1984 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [24 empty] | 23 | [14 empty] | 255
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 720 | [14 empty] | 910
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 11
E. |  | Testing of plant systems or components | [35 empty] | 0 |  |  |  | 1
H. |  | Nuclear regulatory requirements | [39 empty] | 1
L. |  | Human factor related | [39 empty] | 5
Z. |  | Other | [35 empty] | 2
Subtotal | [22 empty] | 720 |  |  |  | 23 | [10 empty] | 923 |  |  |  | 262
Total | [22 empty] | 743 | [14 empty] | 1185
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 1984 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 99
12. |  |  | Reactor I&C Systems | [34 empty] | 4
14. |  |  | Safety Systems | [34 empty] | 11
15. |  |  | Reactor Cooling Systems | [34 empty] | 3
16. |  |  | Steam generation systems | [34 empty] | 2
31. |  |  | Turbine and auxiliaries | [19 empty] | 23 | [14 empty] | 19
32. |  |  | Feedwater and Main Steam System | [34 empty] | 7
34. |  |  | Miscellaneous Systems | [34 empty] | 2
35. |  |  | All other I&C Systems | [34 empty] | 2
41. |  |  | Main Generator Systems | [34 empty] | 111
Total | [22 empty] | 23 | [14 empty] | 260