## BARAKAH-1
2023 Operating Experience
AE-01 | [8 empty] | BARAKAH-1 | [26 empty] | UNITED ARAB EMIRATES
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NAWAH (Nawah Energy Company)
Owner | [7 empty] | : | ENEC (Emirates Nuclear Energy Corporation)
Reactor Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Turbine Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / APR-1400 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2012-07-19
Thermal power | [12 empty] | : |  |  | 3983 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2020-08-19
Gross electrical power | [12 empty] | : |  |  | 1417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2021-04-01
Reference unit power (net) | [12 empty] | : |  |  | 1337 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 3 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.513
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.414
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.66 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28914 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.647 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.629
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 47.572 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 81 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 3
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 10488.13 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.06 %
Energy Availability Factor (EAF) | [18 empty] | : | 88.87 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.05 %
Unit Capability Factor (UCF) | [18 empty] | : | 89.66 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 10.29 %
Load Factor (LF) | [18 empty] | : | 89.55 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.79 %
Operating Factor (OF) | [18 empty] | : | 90.25 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 854 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1019.19 | 917.05 |  |  |  | 1008.43 |  | 968.90 | [8 empty] | 985.59 |  |  | 948.84 | [6 empty] | 969.77 |  | 967.32 |  |  |  | 869.56 |  |  | 0.00 |  |  | 826.71 | [9 empty] | 1006.78 |  |  | 10488.13
EAF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.98 | [8 empty] | 99.08 |  |  | 98.57 | [6 empty] | 97.49 |  | 97.24 |  |  |  | 90.33 |  |  | 0.00 |  |  | 85.42 | [9 empty] | 100.00 |  |  | 88.87
UCF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 99.98 | [8 empty] | 99.40 |  |  | 99.99 | [6 empty] | 99.91 |  | 99.80 |  |  |  | 93.09 |  |  | 0.00 |  |  | 85.42 | [9 empty] | 100.00 |  |  | 89.66
LF [%] |  |  |  |  | 102.46 | 102.07 |  |  |  | 101.38 |  | 100.65 | [8 empty] | 99.08 |  |  | 98.57 | [6 empty] | 97.49 |  | 97.24 |  |  |  | 90.33 |  |  | 0.00 |  |  | 85.88 | [9 empty] | 101.21 |  |  | 89.55
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 93.61 |  |  | 0.00 |  |  | 91.11 | [9 empty] | 100.00 |  |  | 90.25
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.06 |  |  | 0.01 | [6 empty] | 0.09 |  | 0.20 |  |  |  | 0.27 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.06
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.06 |  |  | 0.01 | [6 empty] | 0.09 |  | 0.20 |  |  |  | 0.25 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.05
PUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.02 | [8 empty] | 0.54 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 6.65 |  |  | 100.00 |  |  | 14.58 | [9 empty] | 0.00 |  |  | 10.29
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.32 |  |  | 1.43 | [6 empty] | 2.42 |  | 2.56 |  |  |  | 2.76 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.79
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 29172.82 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 4.66 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 81.11 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 6.81 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 81.65 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 11.53 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 81.4 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.54 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 83.88 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2021 |  |  |  | 8926.09 |  |  | 6763 |  |  |  | 1417 | [10 empty] | 85.44 |  |  |  | 85.98 | [5 empty] | 85.49 |  |  | 91.77 |  |  |  | 13.54 |  | 13.47 | [8 empty] | 0.55 |  |  |  |  | 0.54
2022 |  |  |  | 8196.79 |  |  | 6269 |  |  |  | 1337 | [10 empty] | 69.89 |  |  |  | 70.18 | [5 empty] | 69.99 |  |  | 71.56 |  |  |  | 0.53 |  | 8.26 | [8 empty] | 21.55 |  |  |  |  | 0.30
2023 |  |  |  | 10488.13 |  |  | 7906 |  |  |  | 1337 | [10 empty] | 88.87 |  |  |  | 89.66 | [5 empty] | 89.55 |  |  | 90.25 |  |  |  | 0.06 |  | 0.05 | [8 empty] | 10.29 |  |  |  |  | 0.79
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2021 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 302
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 854 | [14 empty] | 835
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 441
Z. |  | Other | [39 empty] | 463
Subtotal | [22 empty] | 854 | [14 empty] | 1276 |  |  |  | 765
Total | [22 empty] | 854 | [14 empty] | 2041
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2021 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
12. |  |  | Reactor I&C Systems | [34 empty] | 154
33. |  |  | Circulating Water System | [34 empty] | 123
Total | [37 empty] | 277

## BARAKAH-2
2023 Operating Experience
AE-02 | [8 empty] | BARAKAH-2 | [26 empty] | UNITED ARAB EMIRATES
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NAWAH (Nawah Energy Company)
Owner | [7 empty] | : | ENEC (Emirates Nuclear Energy Corporation)
Reactor Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Turbine Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / APR-1400 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2013-04-15
Thermal power | [12 empty] | : |  |  | 3983 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2021-09-14
Gross electrical power | [12 empty] | : |  |  | 1417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2022-03-24
Reference unit power (net) | [12 empty] | : |  |  | 1337 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 2 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | 15.513
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | 323.9
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | 0.414
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | 2.66 | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | 33.3 | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28914 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | 3
| Active core diameter [m] | [13 empty] | : |  |  | 3.647 | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | 6.629
| Active core height/length [m] | [13 empty] | : |  |  | 3.81 | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | 27
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | 241 | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | 17.9 | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | 3
| Number of control rod assemblies | [13 empty] | : |  |  | 81 | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | 2
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 10274.57 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0.02 %
Energy Availability Factor (EAF) | [18 empty] | : | 87.12 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0.02 %
Unit Capability Factor (UCF) | [18 empty] | : | 87.59 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 12.39 %
Load Factor (LF) | [18 empty] | : | 87.73 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.48 %
Operating Factor (OF) | [18 empty] | : | 88.16 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 1037 hours
Annual Summary
[5 empty] | Jan | Feb |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h |  |  |  |  | 1001.43 | 902.30 |  |  |  | 64.06 |  | 452.11 | [8 empty] | 1007.13 |  |  | 966.08 | [6 empty] | 987.66 |  | 952.15 |  |  |  | 950.77 |  |  | 995.98 |  |  | 978.47 | [9 empty] | 1016.44 |  |  | 10274.57
EAF [%] |  |  |  |  | 99.97 | 99.91 |  |  |  | 6.41 |  | 46.69 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 99.29 |  | 95.72 |  |  |  | 98.77 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.80 |  |  | 87.12
UCF [%] |  |  |  |  | 99.97 | 99.91 |  |  |  | 6.41 |  | 46.69 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 99.96 |  |  |  | 99.44 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 99.80 |  |  | 87.59
LF [%] |  |  |  |  | 100.67 | 100.43 |  |  |  | 6.44 |  | 46.97 | [8 empty] | 101.25 |  |  | 100.36 | [6 empty] | 99.29 |  | 95.72 |  |  |  | 98.77 |  |  | 100.13 |  |  | 101.64 | [9 empty] | 102.18 |  |  | 87.73
OF [%] |  |  |  |  | 100.00 | 100.00 |  |  |  | 6.85 |  | 52.22 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 100.00 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 88.16
FLR [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.20 |  |  | 0.02
UCL [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.20 |  |  | 0.02
PUF [%] |  |  |  |  | 0.03 | 0.09 |  |  |  | 93.59 |  | 53.31 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.04 |  |  |  | 0.56 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 12.39
XUF [%] |  |  |  |  | 0.00 | 0.00 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.71 |  | 4.24 |  |  |  | 0.67 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.48
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 21388.89 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0.29 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 91.98 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0.27 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 92.54 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 7.19 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 92.19 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.56 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 93.25 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2022 |  |  |  | 9914.13 |  |  | 7723 |  |  |  | 1337 | [10 empty] | 98.44 |  |  |  | 99.11 | [5 empty] | 98.12 |  |  | 100.00 |  |  |  | 0.61 |  | 0.61 | [8 empty] | 0.28 |  |  |  |  | 0.67
2023 |  |  |  | 10274.57 |  |  | 7723 |  |  |  | 1337 | [10 empty] | 87.12 |  |  |  | 87.59 | [5 empty] | 87.73 |  |  | 88.16 |  |  |  | 0.02 |  | 0.02 | [8 empty] | 12.39 |  |  |  |  | 0.48
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2022 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 353
C. |  | Inspection, maintenance or repair combined with refuelling | [20 empty] | 1037 | [14 empty] | 593
D. |  | Inspection, maintenance or repair without refuelling | [35 empty] | 559
Subtotal | [22 empty] | 1037 | [14 empty] | 1152 |  |  |  | 353
Total | [22 empty] | 1037 | [14 empty] | 1505
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2022 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 25
15. |  |  | Reactor Cooling Systems | [34 empty] | 129
31. |  |  | Turbine and auxiliaries | [34 empty] | 111
Total | [37 empty] | 265

## BARAKAH-3
2023 Operating Experience
AE-03 | [8 empty] | BARAKAH-3 | [26 empty] | UNITED ARAB EMIRATES
Status at end of year | [7 empty] | : | Operational
Operator | [7 empty] | : | NAWAH (Nawah Energy Company)
Owner | [7 empty] | : | ENEC (Emirates Nuclear Energy Corporation)
Reactor Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Turbine Supplier | [7 empty] | : | KEPCO (Korea Electric Power Corporation)
Reactor Unit Details | [27 empty] | Key Dates
Reactor type and model | [12 empty] | : |  |  | PWR / APR-1400 | [11 empty] | Construction Date | [15 empty] | : |  |  | 2014-09-24
Thermal power | [12 empty] | : |  |  | 3983 | [8 empty] | MWth |  |  | Grid Date | [15 empty] | : |  |  | 2022-10-08
Gross electrical power | [12 empty] | : |  |  | 1417 | [8 empty] | MWe |  |  | Commercial Date | [15 empty] | : |  |  | 2023-02-24
Reference unit power (net) | [12 empty] | : |  |  | 1337 | [8 empty] | MWe |  |  | Age at end of year | [15 empty] | : |  |  | 1 years
Design Characteristics
| Primary Systems | [28 empty] | Operating coolant pressure [MPa] | [15 empty] | : |  |  | -
| Reactor vessel centreline orientation | [13 empty] | : |  |  | Vertical | [11 empty] | Reactor outlet temperature [°C] | [15 empty] | : |  |  | -
| Fuel material | [13 empty] | : |  |  | UO2 | [11 empty] | Number of SG | [15 empty] | : |  |  | 2
| Refuelling type | [13 empty] | : |  |  | OFF-line | [11 empty] | Containment type | [15 empty] | : |  |  | Single
| Moderator material | [13 empty] | : |  |  | H2O | [11 empty] | Containment design pressure [MPa] | [15 empty] | : |  |  | -
| Average fuel enrichment [% of U235] | [13 empty] | : |  |  | - | [11 empty] | Secondary systems
| Refuelling frequency [month] | [13 empty] | : |  |  | 18 | [11 empty] | Number of turbine-generators per unit/reactor | [15 empty] | : |  |  | 1
| Part of the core refuelled [%] | [13 empty] | : |  |  | - | [11 empty] | Turbine speed [rpm] | [15 empty] | : |  |  | 1500
| Average discharge burnup [MWd/t] | [13 empty] | : |  |  | 28914 | [11 empty] | Number of LP cylinders per turbine | [15 empty] | : |  |  | -
| Active core diameter [m] | [13 empty] | : |  |  | - | [11 empty] | HP cylinder inlet steam pressure [MPa] | [15 empty] | : |  |  | -
| Active core height/length [m] | [13 empty] | : |  |  | - | [11 empty] | Output voltage [kV] | [15 empty] | : |  |  | -
| Number of fissile fuel assemblies/bundles | [13 empty] | : |  |  | - | [11 empty] | Primary means of condenser cooling | [15 empty] | : |  |  | Sea (once-through)
| Fuel linear heat generation rate [kW/m] | [13 empty] | : |  |  | - | [11 empty] | Number of main condensate pumps | [15 empty] | : |  |  | -
| Number of control rod assemblies | [13 empty] | : |  |  | - | [11 empty] | Number of FW pumps for full power operation | [15 empty] | : |  |  | -
| Number of external reactor coolant loops | [13 empty] | : |  |  | 2 | [11 empty] | Number of on-site safety related diesel generators | [15 empty] | : |  |  | 2
| Coolant type | [13 empty] | : |  |  | H2O | [11 empty] | Non-electrical applications | [15 empty] | : |  |  | none
Annual Production Results (2023)
Net Energy Production | [18 empty] | : | 10442.83 GW(e).h | [8 empty] | Forced Loss Rate (FLR) | [15 empty] | : |  |  | 0 %
Energy Availability Factor (EAF) | [18 empty] | : | 96.83 % | [8 empty] | Unplanned Capability Loss Factor (UCL) | [15 empty] | : |  |  | 0 %
Unit Capability Factor (UCF) | [18 empty] | : | 97.36 % | [8 empty] | Planned Unavailability Factor (PUF) | [15 empty] | : |  |  | 2.64 %
Load Factor (LF) | [18 empty] | : | 97.68 % | [8 empty] | Externally cause unavailability (XUF) | [15 empty] | : |  |  | 0.53 %
Operating Factor (OF) | [18 empty] | : | 97.7 % | [8 empty] | Total off-line time | [15 empty] | : |  |  | 895 hours
Annual Summary
[5 empty] | Feb | Jan |  |  |  | Mar |  | Apr | [8 empty] | May |  |  | Jun | [6 empty] | Jul |  | Aug |  |  |  | Sep |  |  | Oct |  |  | Nov | [9 empty] | Dec |  |  | Annual
GW(e)-h | [9 empty] | 1018.35 |  | 983.89 | [8 empty] | 995.67 |  |  | 960.24 | [6 empty] | 983.14 |  | 975.41 |  |  |  | 947.26 |  |  | 735.80 |  |  | 970.83 | [9 empty] | 1020.34 |  |  | 9590.95
EAF [%] | [9 empty] | 100.00 |  | 100.00 | [8 empty] | 99.61 |  |  | 99.75 | [6 empty] | 98.83 |  | 98.06 |  |  |  | 98.40 |  |  | 73.97 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 96.83
UCF [%] | [9 empty] | 100.00 |  | 100.00 | [8 empty] | 99.61 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 74.30 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.36
LF [%] | [9 empty] | 102.38 |  | 102.21 | [8 empty] | 100.09 |  |  | 99.75 | [6 empty] | 98.83 |  | 98.06 |  |  |  | 98.40 |  |  | 73.97 |  |  | 100.85 | [9 empty] | 102.57 |  |  | 97.68
OF [%] | [9 empty] | 100.00 |  | 100.00 | [8 empty] | 100.00 |  |  | 100.00 | [6 empty] | 100.00 |  | 100.00 |  |  |  | 100.00 |  |  | 77.28 |  |  | 100.00 | [9 empty] | 100.00 |  |  | 97.70
FLR [%] | [9 empty] | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
UCL [%] | [9 empty] | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 0.00 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.00
PUF [%] | [9 empty] | 0.00 |  | 0.00 | [8 empty] | 0.39 |  |  | 0.00 | [6 empty] | 0.00 |  | 0.00 |  |  |  | 0.00 |  |  | 25.70 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 2.64
XUF [%] | [9 empty] | 0.00 |  | 0.00 | [8 empty] | 0.00 |  |  | 0.25 | [6 empty] | 1.17 |  | 1.94 |  |  |  | 1.60 |  |  | 0.33 |  |  | 0.00 | [9 empty] | 0.00 |  |  | 0.53
Historical Summary
Lifetime energy generation | [13 empty] | : |  |  | 11632.36 GW(e).h | [11 empty] | Cumulative Forced Loss Rate (FLR) | [21 empty] | : | 0 %
Cumulative Energy Availability Factor (EAF) | [13 empty] | : |  |  | 96.83 % | [11 empty] | Cumulative Unplanned Capability Loss Factor (UCL) | [21 empty] | : | 0 %
Cumulative Unit Capability Factor (UCF) | [13 empty] | : |  |  | 97.36 % | [11 empty] | Cumulative Planned Unavailability Factor (PUF) | [21 empty] | : | 2.64 %
Cumulative Load Factor (LF) | [13 empty] | : |  |  | 97.68 % | [11 empty] | Cumulative Externally cause unavailability (XUF) | [21 empty] | : | 0.53 %
Cumulative Operating Factor (OF) | [13 empty] | : |  |  | 97.7 %
Electricity Production (net) [GWh]
Performance for Years of Commercial Operation
Year |  |  |  | Energy |  |  | Time Online |  |  |  | Reference Unit Power | [10 empty] | EAF |  |  |  | UCF | [5 empty] | LF |  |  | OF |  |  |  | FLR |  | UCL | [8 empty] | PUF |  |  |  |  | XUF
|  |  |  | [GW-h] |  |  | [Hours] |  |  |  | [MW] | [10 empty] | [%] |  |  |  | [%] | [5 empty] | [%] |  |  | [%] |  |  |  | [%] |  | [%] | [8 empty] | [%] |  |  |  |  | [%]
2023 |  |  |  | 10442.83 |  |  | 7865 |  |  |  | 1337 | [10 empty] | 96.83 |  |  |  | 97.36 | [5 empty] | 97.68 |  |  | 97.70 |  |  |  | 0.00 |  | 0.00 | [8 empty] | 2.64 |  |  |  |  | 0.53
Key Factors in Last 20 Years [%]
Energy Losses by Type
Full Outages, Analysis by Cause
[23 empty] | 2023 | [14 empty] | 2023 to 2023
Outage Cause | [22 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
[23 empty] | Planned |  |  |  | Unplanned | [6 empty] | External |  |  |  | Planned |  |  |  | Unplanned | [11 empty] | External
A. |  | Plant equipment problem/failure | [39 empty] | 100
D. |  | Inspection, maintenance or repair without refuelling | [20 empty] | 169 | [14 empty] | 203
E. |  | Testing of plant systems or components | [20 empty] | 726 | [14 empty] | 1176
Subtotal | [22 empty] | 895 | [14 empty] | 1379 |  |  |  | 100
Total | [22 empty] | 895 | [14 empty] | 1479
Equipment Related Unplanned Full Outages, Analysis by System
System | [22 empty] | 2023 | [14 empty] | 2023 to 2023
[23 empty] | Hours Lost | [14 empty] | Average hours lost per reactor-year
11. |  |  | Reactor and Accessories | [34 empty] | 66
Total | [37 empty] | 66